## Summary
Input data
PV Panel
[14 empty] | individual | Phase 1
| district | Phase I | Phase II | Source | [9 empty] | Parameter | Duplex | Terrace | Innov. Hub | Source
| Installed capacity (kW) | 1001 | 3077 | Solar Assessment by Wood plus own assumption |  |  |  | Capacity (kW) Phase I | Capacity (kW) per unit for Phase I | Total Area (m2) | Phase 1+2 | Source |  | Installed capacity (kW) | 5.0227 | 6.2308 | 228 | Solar Assessment by Wood
| Inclination of PV (°) | 15 |  | Solar Assessment by Wood |  |  | Duplex | 221 | 5.0227 | 1650 | 3375 | Solar Assessment by Wood plus own assumption |  | Inclination of PV (°) | 15 |  |  | Solar Assessment by Wood
| Orientation of PV | South |  | Solar Assessment by Wood |  |  | Terrace | 162 | 6.2308 | 1200 | 3323.0769 |  |  | Orientation of PV | South |  |  | Solar Assessment by Wood
| Ambient temperature | Online Database connected through energyPRO |  |  |  |  | Innov. Hub | 228 | 228 | 1680 | 1680 |  |  | Ambient temperature | Online Database connected through energyPRO
| Solar radiation | Online Database connected through energyPRO |  |  |  |  | Car Park | 390 | 390 | 2870 | 8610 |  |  | Solar radiation | Online Database connected through energyPRO
| Maximum power (kW) | 0.33 |  | Solar Assessment by Wood |  |  | SUM | 1001 |  | 7400 | 8378.0769 |  |  | Maximum power (kW) | 0.33 |  |  | Solar Assessment by Wood
| Temperature coefficient of power (%/°C) | -0.041 |  | Canadian Solar |  |  | Flat |  |  |  | 1840 | own assumption |  | Temperature coefficient of power (%/°C) | -0.041 |  |  | Canadian Solar
| NOCT (°C) | 45 |  | Canadian Solar |  |  | Work Live |  |  |  | 1300 |  |  | NOCT (°C) | 45 |  |  | Canadian Solar
[7 empty] | Leisure |  |  |  | 1424
[7 empty] | Religious |  |  |  | 96
[7 empty] | Spec Office |  |  |  | 960
[7 empty] | SUM Phase I + II |  |  |  | 22608.0769
[7 empty] | 80% coverage |  |  |  | 18086.4615 |  |  | 1.94 | 1 panel area | Solar Assessment by Wood
[7 empty] | number of panels |  |  |  | 9322.9183 |  |  | 0.33 | capacity of 1 PV
[7 empty] | Installed capacity |  |  |  | 3076.563
Wind Data
Source
| Wind speed | Online Database connected through energyPRO
| Measure Height (m) | 100 | obtained from Findhorn example from ESRU Library (source: Andrew Lyden)
| Hub Height (m) | 23
| Hellmann exponent | 0
Source
| Wind speed [m/s] | Power [kW] | Power Modified [kW] | obtained from Findhorn example from ESRU Library (source: Andrew Lyden)
| 0 | 0 | 0
| 3 | 2 | 6.4
| 3 | 2 | 6.4
| 4 | 2.5 | 8
| 5 | 5 | 16
| 6 | 15 | 48
| 7 | 20 | 64
| 8 | 30 | 96
| 9 | 37 | 118.4
| 10 | 45 | 144
| 11 | 52.5 | 168.32
| 12 | 60 | 192
| 13 | 67 | 214.4
| 14 | 72 | 230.4
| 15 | 75 | 240
| 16 | 80 | 256
| 17 | 82 | 262.4
| 18 | 83 | 265.6
| 19 | 83 | 265.6
| 20 | 83 | 265.6
| 55 | 83 | 265.6
Heat Pump
| district | ASHP |  | WSHP |  | GSHP |  |  |  | individual | ASHP |  |  | Source | GSHP |  |  | Source
|  | Phase 1 | Source | Phase 1 | Source | Phase 1 | Source |  |  |  | Duplex | Terrace | Innovation Hub |  | Duplex | Terrace | Innovation Hub
| Electr. Capacity (kW) | 172 | calculated with COP | 134.375 | calculated with COP | 148.2759 | calculated with COP |  |  | Electr. capacity (kW) | 0.24 | 0.24 | 68 | calculated with COP | 0.17 | 0.21 | 59 | calculated with COP
| Max. Heat capacity (kW) | 430 | Peak demand from heating profile (before downsizing) | 430 | Peak demand from profile (before downsizing) | 430 | Peak demand from heating profile (before downsizing) |  |  | Heat capacity (kW) | 0.6 | 0.6 | 170 | Heat needed to meet demand | 0.5 | 0.6 | 170 | Heat needed to meet demand
| COP | 2.5 | Energy Saving Trust (2013). The heat is on: heat pump field trials phase 2 | 3.2 | Star Refrigeration http://www.star-ref.co.uk/smart-thinking/how-to-choose-an-efficient-heat-pump-large-scale-heat-pumps-and-district-heating-making-the-right-choice.aspx | 2.9 | Energy Saving Trust (2013). The heat is on: heat pump field trials phase 2 |  |  | COP | 2.5 | 2.5 | 2.5 | Energy Saving Trust (2013). The heat is on: heat pump field trials phase 2 | 2.9 | 2.9 | 2.9 | Energy Saving Trust (2013). The heat is on: heat pump field trials phase 2
| Heated from (°C) | 35 | Cibse journal https://www.cibsejournal.com/cpd/modules/2010-02/ | 55 |  | 35 | Forkers, http://www.forkers.com/filestore/pdf/a%20guide%20to%20ground%20source%20heating.pdf |  |  | Heated from (°C) | 35 | 35 | 35 | Cibse journal https://www.cibsejournal.com/cpd/modules/2010-02/ | 35 | 35 | 35 | Forkers, http://www.forkers.com/filestore/pdf/a%20guide%20to%20ground%20source%20heating.pdf
| Heated to (°C) | 60 |  | 75 |  | 65 |  |  |  | Heated to (°C) | 60 | 60 | 60 |  | 50 | 50 | 50
| Heat source cooled from (°C) | 10 | own assumption | 8 |  | 12 |  |  |  | Heat source cooled from (°C) | 10 | 10 | 10 | own assumption | 12 | 12 | 12
| Cooled to (°C) | 5 |  | 5 |  | 0 |  |  |  | Cooled to (°C) | 5 | 5 | 5 |  | 0 | 0 | 0
| Actual temperatures: Heat source cooled from (°C) | T() | own assumption, ASHP are dependent from ambient temperature (cools down around 2 degrees) | 8 |  | 12 |  |  |  | Actual temperatures (°C) | From T() to T()-2 | From T() to T()-2 | From T() to T()-2 | own assumption, ASHP are dependent from ambient temperature (cools down around 2 degrees) | 12 to 0 | 12 to 0 | 12 to 0
| Actual temperatures: Cooled to (°C) | T()-2 |  | 5 |  | 0
Solar Thermal
Phase 1
| Parameter | Base | Source |  | Building Name | Total Area (m2)
| Total area of collectors (m2) | 5920 | Solar Assessment by Wood + own assumption |  | Innovation Centre | 1680
| Inclination of solar collector (°) | 15 | Solar Assessment by Wood + own assumption |  | Residential Duplex | 1650
| Orientation of solar collector | South | Solar Assessment by Wood |  | Residential Terrace | 1200
| Ambient temperature | Online Database connected through energyPRO |  |  | Car Park | 2870
| Solar radiation | Online Database connected through energyPRO |  |  | Total | 7400
| Start efficiency | 0.717 | Apricus, https://www.energymatters.com.au/images/apricus/Brochure.pdf + own assumption |  | 80% coverage | 5920
| Loss coefficient (W/m2 °C) | 1.6
| Loss coefficient (W/m2 °C) | 0.0085
| Incidence angle modifier - coefficient | 4
Electric boiler (only individual)
|  | Phase 1 |  |  | Source
|  | Duplex | Terrace | Innovation Hub
| Electrical Consumption (kW) | 2.1 | 2 | 160 | Energy.GOV https://www.energy.gov/energysaver/home-heating-systems/furnaces-and-boilers
| Heat Output (kW) | 2.1 | 2 | 160 | Peak demand from heating profile
Absorption Chiller
Source
| Heating Consumption (kW) | 128 | calculated with COP
| Cooling Supply (kW) | 90 | Peak demand from profile
| COP | 0.7 | Hitachi Ltd, http://www.nedo.go.jp/content/100874854.pdf
Electric Chiller
Source
| Electric Consumption (kW) | 75 | calculated with COP
| Cooling Supply (kW) | 90 | Peak demand from profile
| COP | 1.2 | Ref-wiki, http://www.ref-wiki.com/technical-information/162-chillers/32888-hvac-absorption-chillers-vs-electric-chillers.html
Battery
|  | District | Source
| Parameter | Base | own assumption
| Max. capacity (MWh) | 10
| Efficiency | 85%
Thermal Storage
|  | District | Source
| Parameter | Base | own assumption
| Volume (m3) | 10
| Temperature in top (°C) | 90
| Temperature in bottom (°C) | 50
Cold Store
| Parameter | Innovation Hub | Source
| Volume (m3) | 50 | own assumption
| Temperature in top (°C) | 10
| Temperature in bottom (°C) | 5