## Welcome
Welcome to the biomass feasibility tool
This tool was developed by Lucas Lira, Panagiotis Seferis and Radek Kaczorowski for a MSc group project at the University of Strathclyde. The work was supported by David Palmer of the Campbell Palmer Partnership Ltd who provided industrial supervision for the project.
Disclaimer
Whilst all reasonable steps have been taken to ensure that the information used to produce this calculator is correct, you should be aware that it may not produce representative results in every case. Accordingly, no liability can be accepted by either the University of Strathclyde or the Campbell Palmer Partnership Ltd should the use of the calculator result in errors or omissions in designs or calculations based on results obtained from the calculator. Any person makes use of this calculator at their own risk and designers should, in every case, carry out their own calculations from first principles in order to underwrite the accuracy of the information they supply.
This tool is FREEWARE and is distributed free of charge by the University of Strathclyde and the Campbell Palmer Partnership Ltd.
Click here to start
Click here to access our web page

## Main Menu
. .
. .
[6 empty] | . . |  | . .
[6 empty] | . . |  | . .
| . . | [6 empty] | . .
. .
[7 empty] | Fuel Selected | . .
[7 empty] | Woodchip1 | . .
Pellet1
| . . |  | . .
| . . |  | . .
| Location | East Scotland |  | Boiler Capacity
| Kind of Input | Automatic Calculation |  | 30 | kW
|  |  | . . |  |  | . . |  | . .
USER GUIDE |  |  | . . |  |  | . . |  | . .
[5 empty] | Fuel Selected |  | Woodchip1
[5 empty] | Storage Selected |  | Square Silo Sloping Floor

## Heat Demand Model
AUXILIAR TABLES - Heat Demand Calculation
ENERGY DEMAND
[14 empty] | Design Heat Losses (kW/m2) without HWS |  |  |  |  | Design Heat Losses (kW) |  |  |  |  | Design Heat Losses (kW) with HWS
|  |  |  | RETURN TO MAIN MENU | [10 empty] | North Scotland | East Scotland | West Scotland |  |  | North Scotland | East Scotland | West Scotland |  |  | North Scotland | East Scotland | West Scotland
[8 empty] | Peak Heat Loads baseds on defined OAT | [5 empty] | January | 0.039172 | 0.039709 | 0.037996 |  | January | 31.3374 | 31.7673 | 30.397 |  | January | 32.1374 | 32.5673 | 31.197
Basic Dimensions |  | External surface (m2) | Volume (m3) | Number of floors | Temperature | T (°C) |  | Max. Heat Load(kW/m2) | Max. Heat Load(kW) |  | Efficiency |  |  | February | 0.039424 | 0.039575 | 0.037828 |  | February | 31.5389 | 31.6598 | 30.2627 |  | February | 32.3389 | 32.4598 | 31.0627
Length (m) | 40 | 360 | 2400 | 1 | Internal | 21 |  | 0.054109 | 43.2872 |  | 0.75 |  |  | March | 0.037425 | 0.037358 | 0.035948 |  | March | 29.9403 | 29.8866 | 28.7581 |  | March | 30.7403 | 30.6866 | 29.5581
Width (m) | 20 |  |  | Floor Area (A) | Ground | 0 | [7 empty] | April | 0.034017 | 0.033832 | 0.032656 |  | April | 27.2133 | 27.0655 | 26.1252 |  | April | 28.0133 | 27.8655 | 26.9252
Height (m) | 3 |  |  | 800 | OAT | -5 |  | DEGREE DAYS C.F AND HWS DATA, CLICK HERE | [5 empty] | May | 0.029903 | 0.029097 | 0.027871 |  | May | 23.9221 | 23.2773 | 22.2966 |  | May | 24.7221 | 24.0773 | 23.0966
Number of air changes N (h-1) | 1 | [12 empty] | June | 0.02604 | 0.024915 | 0.024109 |  | June | 20.8323 | 19.9323 | 19.2875 |  | June | 21.6323 | 20.7323 | 20.0875
[5 empty] | Heating Period | Hours | Correction Factor | Days in a week | Correction Factor | Type of Heating | Correction Factor | Total Correction Factor |  | July | 0.023169 | 0.021926 | 0.021372 |  | July | 18.5352 | 17.5411 | 17.0978 |  | July | 19.3352 | 18.3411 | 17.8978
Building Components |  |  |  |  | Summer | 4 | 0.8 | 7 | 1 | Intermittent-responsive plant | 0.7 | 0.56 |  | August | 0.023203 | 0.022094 | 0.021372 |  | August | 18.5621 | 17.6755 | 17.0978 |  | August | 19.3621 | 18.4755 | 17.8978
|  | Surface (m2) | U (W/m2k) | Heat Transfer per Floor Area | Winter | 12 | 1.12 | 7 | 1 | Intermittent-responsive plant | 0.7 | 0.784 |  | September | 0.025654 | 0.024983 | 0.024042 |  | September | 20.5234 | 19.986 | 19.2338 |  | September | 21.3234 | 20.786 | 20.0338
Walls |  |  |  |  | Spring/Autunm | 8 | 1 | 7 | 1 | Intermittent-responsive plant | 0.7 | 0.7 |  | October | 0.031011 | 0.03086 | 0.029533 |  | October | 24.8087 | 24.6878 | 23.6265 |  | October | 25.6087 | 25.4878 | 24.4265
Additional wall surface | [13 empty] | November | 0.035662 | 0.035998 | 0.034235 |  | November | 28.5298 | 28.7984 | 27.3879 |  | November | 29.3298 | 29.5984 | 28.1879
Total wall surface |  | 248.85 | 0.3 | 0.093319 |  | Number | kW per unit | Total (kW) | Total (kWh) | Total (kW/m2) | Total (kWh/m2) |  |  | December | 0.039306 | 0.039558 | 0.038013 |  | December | 31.4449 | 31.6464 | 30.4105 |  | December | 32.2449 | 32.4464 | 31.2105
[5 empty] | Occupants | 30 | 0.13 | 3.9
|  | Surface (m2) | U (W/m2k) | Heat Transfer per Floor Area | Pcs | 10 | 0.075 | 0.75
Windows |  |  |  |  | Lighting (kW/m2) | 0.01 | 8 | 0.08
[5 empty] | Solar gains |  |  |  | 1404 |  | 13
Glazing Percentage (%) |  | 30 | [5 empty] | 4.73 | 2463.52 | 0.0059125 | 3.0794
[14 empty] | Monthly Energy Demand (kWh/m2) | [5 empty] | Monthly Energy Demand (kWh/m2) - With correction factors | [5 empty] | Monthly Energy Demand (kWh/m2) - With correction factors & HWS & CHG
[15 empty] | West Scotland | East Scotland | N. West Scotland | N. East Scotland |  |  | West Scotland | East Scotland | N. West Scotland | N. East Scotland |  |  | West Scotland | East Scotland | N. West Scotland | N. East Scotland
Total surface |  | 108 | 2.8 | 0.378 | DHL and Monthly Energy Demand |  | *Please, select the apropriate location and the calculation option | [6 empty] | January | 18.1846 | 18.6161 | 16.8903 | 18.59 |  | January | 14.2567 | 14.595 | 13.242 | 14.5745 |  | January | 26.5511 | 27.0022 | 25.1981 | 26.9749
[5 empty] | East Scotland | Automatic Calculation | [7 empty] | February | 16.2774 | 16.4123 | 15.6369 | 16.7501 |  | February | 12.7615 | 12.8672 | 12.2594 | 13.1321 |  | February | 24.5574 | 24.6984 | 23.8879 | 25.0515
|  | Surface (m2) | U (W/m2k) | Heat Transfer per Floor Area | [9 empty] | March | 16.0193 | 16.0222 | 16.2281 | 16.4977 |  | March | 11.2135 | 11.2156 | 11.3597 | 11.5484 |  | March | 22.4935 | 22.4962 | 22.6884 | 22.94
Doors | [6 empty] | Design Heat Losses + HWS (kW) | Monthly Energy Demand (kWh) | TEMPERATURE DATA CLICK HERE |  |  |  |  | April | 12.8735 | 13.3091 | 13.5043 | 13.8392 |  | April | 9.0115 | 9.3164 | 9.453 | 9.6874 |  | April | 19.5574 | 19.9639 | 20.1462 | 20.4587
Length |  | 0.75 |  |  |  | January | 32.5673 | 21601.7358 | [5 empty] | May | 9.3902 | 10.3852 | 11.4897 | 10.7826 |  | May | 6.5731 | 7.2697 | 8.0428 | 7.5478 |  | May | 16.3063 | 17.235 | 18.2658 | 17.6059
Height |  | 2.1 |  |  |  | February | 32.4598 | 19758.7368 | [5 empty] | June | 5.6338 | 6.0381 | 7.5907 | 6.5786 |  | June | 3.1549 | 3.3813 | 4.2508 | 3.684 |  | June | 11.7487 | 12.0506 | 13.2099 | 12.4542
Number of doors |  | 2 |  |  |  | March | 30.6866 | 17996.9622 | [5 empty] | July | 3.6845 | 3.9662 | 5.3768 | 4.0836 |  | July | 2.0633 | 2.2211 | 3.011 | 2.2868 |  | July | 8.736 | 8.736 | 8.736 | 8.736
Additional door surface | [5 empty] | April | 27.8655 | 15971.1496 | [5 empty] | August | 3.9012 | 3.9435 | 4.6915 | 4.1476 |  | August | 2.1847 | 2.2084 | 2.6272 | 2.3226 |  | August | 8.736 | 8.736 | 8.736 | 8.736
Total surface |  | 3.15 | 2 | 0.007875 |  | May | 24.0773 | 13788.0163 | [5 empty] | September | 6.3744 | 6.2875 | 6.6355 | 6.6993 |  | September | 4.4621 | 4.4012 | 4.6449 | 4.6895 |  | September | 13.4915 | 13.4105 | 13.7353 | 13.7949
[6 empty] | June | 20.7323 | 9640.479 | [5 empty] | October | 10.8453 | 10.5141 | 10.6654 | 11.0712 |  | October | 7.5917 | 7.3599 | 7.4658 | 7.7498 |  | October | 17.6644 | 17.3553 | 17.4965 | 17.8752
|  | Surface (m2) | U (W/m2k) | Heat Transfer per Floor Area |  | July | 18.3411 | 6988.8 | [5 empty] | November | 14.9186 | 14.973 | 13.5978 | 15.133 |  | November | 10.443 | 10.4811 | 9.5185 | 10.5931 |  | November | 21.4662 | 21.5169 | 20.2334 | 21.6663
Rooftop | [5 empty] | August | 18.4755 | 6988.8 | [5 empty] | December | 18.611 | 18.9031 | 16.6598 | 18.8881 |  | December | 14.591 | 14.82 | 13.0613 | 14.8083 |  | December | 26.9968 | 27.3022 | 24.9571 | 27.2865
Additional surface | [5 empty] | September | 20.786 | 10728.372
Total surface |  | 800 | 0.2 | 0.2 |  | October | 25.4878 | 13884.2259
[6 empty] | November | 29.5984 | 17213.5499
|  | Surface (m2) | U (W/m2k) | Heat Transfer per Floor Area |  | December | 32.4464 | 21841.7335
Floor
Additional surface | [13 empty] | Monthly Energy Demand (kWh) - With correction factors | [5 empty] | Monthly Energy Demand (kWh) - With correction factors & HWS & CHG
Total surface |  | 800 | 0.45 | 0.45 | [10 empty] | West Scotland | East Scotland | N. West Scotland | N. East Scotland |  |  | West Scotland | East Scotland | N. West Scotland | N. East Scotland
[14 empty] | January | 11405.3681 | 11676.0219 | 10593.6078 | 11659.6312 |  | January | 21240.8641 | 21601.7358 | 20158.5171 | 21579.8816
Ventilation Heat loss | [13 empty] | February | 10209.1808 | 10293.7726 | 9807.4806 | 10505.6403 |  | February | 19645.9477 | 19758.7368 | 19110.3475 | 20041.227
|  |  |  | 1 | [9 empty] | March | 8970.7907 | 8972.4417 | 9087.7599 | 9238.7194 |  | March | 17994.761 | 17996.9622 | 18150.7199 | 18351.9992
[14 empty] | April | 7209.1848 | 7453.0822 | 7562.4283 | 7749.9265 |  | April | 15645.953 | 15971.1496 | 16116.9444 | 16366.942
Hot water supply | [13 empty] | May | 5258.5027 | 5815.7323 | 6434.2103 | 6038.2589 |  | May | 13045.0436 | 13788.0163 | 14612.6537 | 14084.7185
[14 empty] | June | 2523.9436 | 2705.0792 | 3400.6488 | 2947.2289 |  | June | 9398.9648 | 9640.479 | 10567.905 | 9963.3452
Building Data |  |  | HWS provision (W/m2) | kWh/m2 | [9 empty] | July | 1650.638 | 1776.8714 | 2408.806 | 1829.4729 |  | July | 6988.8 | 6988.8 | 6988.8 | 6988.8
No of working weeks/year |  | 52 | [11 empty] | August | 1747.7344 | 1766.7013 | 2101.7983 | 1858.1115 |  | August | 6988.8 | 6988.8 | 6988.8 | 6988.8
No of working days/week |  | 7 | FALSE | [10 empty] | September | 3569.6433 | 3520.999 | 3715.9007 | 3751.6306 |  | September | 10793.231 | 10728.372 | 10988.241 | 11035.8807
Building type |  | Shop 6 day week | 1 | 8.736 | [9 empty] | October | 6073.3604 | 5887.8894 | 5972.6313 | 6199.851 |  | October | 14131.5206 | 13884.2259 | 13997.2151 | 14300.1746
[14 empty] | November | 8354.4289 | 8384.8824 | 7614.7623 | 8474.4936 |  | November | 17172.9452 | 17213.5499 | 16186.7231 | 17333.0314
Mean Power (kW) | 0.8 | [12 empty] | December | 11672.8143 | 11856.0201 | 10449.0005 | 11846.6375 |  | December | 21597.4591 | 21841.7335 | 19965.7073 | 21829.2233
Mean Monthly Consumption (kWh) | 6988.8

## User Input
| USER DEFINED HEAT DEMAND |  |  |  |  | BACK TO HEAT DEMAND CALCULATOR
Kind of input | Design heat losses + HWS
Energy consumption
Monthly Energy Demand (kWh) - With correction factors |  |  |  |  | Design heat losses(kW)
| North Scotland | East Scotland | West Scotland |  |  | North Scotland | East Scotland | West Scotland
January |  |  |  |  | January | 0 | 0 | 0
February |  |  |  |  | February | 0 | 0 | 0
March |  |  |  |  | March | 0 | 0 | 0
April |  |  |  |  | April | 0 | 0 | 0
May |  |  |  |  | May | 0 | 0 | 0
June |  |  |  |  | June | 0 | 0 | 0
July |  |  |  |  | July | 0 | 0 | 0
August |  |  |  |  | August | 0 | 0 | 0
September |  |  |  |  | September | 0 | 0 | 0
October |  |  |  |  | October | 0 | 0 | 0
November |  |  |  |  | November | 0 | 0 | 0
December |  |  |  |  | December | 0 | 0 | 0
Design heat losses + HWS
[5 empty] | Working days (per week) | 7
Internal temperature |  | 21 |  |  | Working weeks (per year) | 52
HWS (kW) |  |  |  |  | Monthly HWS energy demand (kWh) | 0
Design heat losses(kW) |  |  |  |  | Space heating monthly energy demand (kWh) - With correction factors
| North Scotland | East Scotland | West Scotland |  |  | North Scotland | East Scotland | West Scotland
January |  |  |  |  | January | 0 | 0 | 0
February |  |  |  |  | February | 0 | 0 | 0
March |  |  |  |  | March | 0 | 0 | 0
April |  |  |  |  | April | 0 | 0 | 0
May |  |  |  |  | May | 0 | 0 | 0
June |  |  |  |  | June | 0 | 0 | 0
July |  |  |  |  | July | 0 | 0 | 0
August |  |  |  |  | August | 0 | 0 | 0
September |  |  |  |  | September | 0 | 0 | 0
October |  |  |  |  | October | 0 | 0 | 0
November |  |  |  |  | November | 0 | 0 | 0
December |  |  |  |  | December | 0 | 0 | 0
Energy Consump option tables |  |  |  |  | Design heat losses option tables
| Selected Design Heat Losses | Selected Energy Demand |  |  | Selected Design Heat Losses | Selected Energy Demand
January | 0 | 0 |  | January | 0 | 0
February | 0 | 0 |  | February | 0 | 0
March | 0 | 0 |  | March | 0 | 0
April | 0 | 0 |  | April | 0 | 0
May | 0 | 0 |  | May | 0 | 0
June | 0 | 0 |  | June | 0 | 0
July | 0 | 0 |  | July | 0 | 0
August | 0 | 0 |  | August | 0 | 0
September | 0 | 0 |  | September | 0 | 0
October | 0 | 0 |  | October | 0 | 0
November | 0 | 0 |  | November | 0 | 0
December | 0 | 0 |  | December | 0 | 0
Selected Table
Auxiliar Table
| Selected Design Heat Losses | Selected Energy Demand
January | 0 | 0 |  |  | Office - 5 or 6 day week
February | 0 | 0 |  |  | Shop - 6 day week
March | 0 | 0 |  |  | Factories - 5 day single shift
April | 0 | 0 |  |  | Factories - 6 day single shift
May | 0 | 0 |  |  | Factories - 7 day multiple shift
June | 0 | 0 |  |  | Warehouse
July | 0 | 0 |  |  | Residential
August | 0 | 0 |  |  | Hotels
September | 0 | 0 |  |  | Hospitals
October | 0 | 0 |  |  | Education
November | 0 | 0
December | 0 | 0

## Temperature Data Scotland
| TEMPERATURE VARIATION - SCOTLAND |  |  |  |  | RETURN TO HEAT DEMAND CALCULATOR
Source - http://www.metoffice.gov.uk
Mean Temperature 2007 |  |  |  | Mean Temperature 2006 |  |  |  | Mean Temperature 2005 |  |  |  | Mean Temperature 2004 |  |  |  | Mean Temperature 2003 |  |  |  | Mean Temperature 2002 |  |  |  | Mean Temperature 2001 |  |  |  | Mean Temperature 2000 |  |  |  | Mean Temperature 1999 |  |  |  | Mean Temperature 1998
| North Scotland | East Scotland | West Scotland |  | North Scotland | East Scotland | West Scotland |  | North Scotland | East Scotland | West Scotland |  | North Scotland | East Scotland | West Scotland |  | North Scotland | East Scotland | West Scotland |  | North Scotland | East Scotland | West Scotland |  | North Scotland | East Scotland | West Scotland |  | North Scotland | East Scotland | West Scotland |  | North Scotland | East Scotland | West Scotland |  | North Scotland | East Scotland | West Scotland
January | 4.4 | 4.3 | 5.4 | January | 3.5 | 2.8 | 3.7 | January | 4.2 | 4.1 | 4.9 | January | 3.1 | 2.9 | 4.2 | January | 2.6 | 2.5 | 3.2 | January | 4.4 | 3.3 | 5 | January | 1 | 1.1 | 2.1 | January | 3.9 | 3.4 | 4.1 | January | 2.8 | 2.6 | 3.6 | January | 3.1 | 2.8 | 3.8
February | 3.9 | 3.7 | 4.6 | February | 2.9 | 2.5 | 3.7 | February | 2.7 | 2.7 | 3.7 | February | 2.8 | 2.9 | 3.8 | February | 2.9 | 1.9 | 3.1 | February | 3 | 3.3 | 4.6 | February | 1.7 | 1.5 | 2.8 | February | 3.2 | 3.3 | 4.3 | February | 2.3 | 2.5 | 3.7 | February | 6.1 | 6.3 | 6.7
March | 5 | 5 | 5.6 | March | 2.1 | 2.1 | 3.3 | March | 5.3 | 5.3 | 6.1 | March | 4.7 | 4.4 | 5.2 | March | 5.7 | 5.4 | 5.9 | March | 4.7 | 4.7 | 5.7 | March | 2.3 | 2 | 3.2 | March | 5.1 | 5.5 | 6.1 | March | 4.3 | 4.6 | 5.2 | March | 4.2 | 4.8 | 5.9
April | 8.6 | 8.9 | 9.3 | April | 5.3 | 5.7 | 6.3 | April | 6.4 | 6.4 | 7.2 | April | 7.2 | 7.3 | 7.9 | April | 8.1 | 7.5 | 8.6 | April | 7 | 6.8 | 7.4 | April | 5.2 | 5.3 | 5.9 | April | 4.9 | 5.3 | 6 | April | 6.6 | 6.9 | 7.5 | April | 4.4 | 4.7 | 5.7
May | 8.2 | 8.8 | 9.7 | May | 8.3 | 8.7 | 9.7 | May | 7.7 | 8.4 | 8.9 | May | 9.3 | 10 | 10.4 | May | 8.7 | 9.4 | 9.6 | May | 9.3 | 9.5 | 10 | May | 9.8 | 10.1 | 10.9 | May | 9 | 9.1 | 10.2 | May | 8.9 | 9.4 | 10.4 | May | 9 | 9.6 | 10.5
June | 11.3 | 11.7 | 13 | June | 12.2 | 12.9 | 13.1 | June | 11.7 | 12.7 | 13 | June | 11.4 | 12.4 | 12.6 | June | 12.7 | 13.1 | 13.3 | June | 11.8 | 11.9 | 12.2 | June | 10.2 | 10.9 | 11.3 | June | 10.1 | 10.7 | 11.6 | June | 10.1 | 10.9 | 11.3 | June | 9.7 | 10.7 | 11.3
July | 12.3 | 12.9 | 13.3 | July | 15.1 | 16 | 16 | July | 12.8 | 13.8 | 14 | July | 12.4 | 12.8 | 13.3 | July | 14.5 | 15 | 15.1 | July | 12.2 | 12.8 | 12.9 | July | 12.4 | 13.4 | 13.7 | July | 12 | 12.5 | 13.4 | July | 13.1 | 14.1 | 14.5 | July | 11.5 | 12.4 | 12.8
August | 12 | 12.7 | 13.2 | August | 12 | 13.6 | 13.7 | August | 12.7 | 13.3 | 13.6 | August | 14 | 14.3 | 15.2 | August | 14 | 14.5 | 14.8 | August | 13.5 | 14.3 | 14.5 | August | 12.7 | 13.2 | 13.5 | August | 12.8 | 13.5 | 13.9 | August | 12.4 | 12.6 | 13.5 | August | 12 | 12.7 | 13.1
September | 10.1 | 10.8 | 11.3 | September | 13 | 13.3 | 13.6 | September | 11.5 | 12.1 | 12.6 | September | 11.2 | 11.7 | 12.3 | September | 11.2 | 11.4 | 11.9 | September | 11.6 | 11.6 | 12.2 | September | 10.3 | 10.7 | 11.5 | September | 11.3 | 11.5 | 12.3 | September | 11.8 | 12.6 | 13 | September | 11.5 | 11.8 | 12.4
October | 9.3 | 8.9 | 9.8 | October | 9.4 | 9.8 | 10.7 | October | 9.5 | 9.5 | 10.4 | October | 7.4 | 7.7 | 8.2 | October | 6.4 | 6.8 | 7.4 | October | 6.7 | 6.5 | 7.4 | October | 10.3 | 10.7 | 11.3 | October | 8 | 7.6 | 8.3 | October | 8.3 | 8.3 | 9.1 | October | 6.3 | 6.7 | 7.8
November | 5.7 | 5.7 | 6.7 | November | 5.9 | 5.8 | 6.8 | November | 4.8 | 4.2 | 5.2 | November | 5.8 | 5.6 | 6.8 | November | 6.1 | 6 | 7.1 | November | 6.1 | 5.7 | 6.8 | November | 5.7 | 5.6 | 6.7 | November | 4.1 | 4.1 | 5 | November | 5.6 | 5.5 | 6.2 | November | 4.1 | 3.7 | 5.1
December | 3.3 | 2.3 | 4.1 | December | 4.4 | 3.5 | 5.2 | December | 3.1 | 4.1 | 3.8 | December | 3.7 | 5 | 4.6 | December | 3.1 | 2.8 | 3.9 | December | 3.3 | 3.5 | 3.9 | December | 2.5 | 1.8 | 3.1 | December | 3 | 2.9 | 3.8 | December | 1.7 | 1.4 | 2.8 | December | 4.1 | 3.4 | 4.7
Average Mean Temperature 1998 - 2007
| North Scotland | East Scotland | West Scotland
January | 3.3 | 2.98 | 4
February | 3.15 | 3.06 | 4.1
March | 4.34 | 4.38 | 5.22
April | 6.37 | 6.48 | 7.18
May | 8.82 | 9.3 | 10.03
June | 11.12 | 11.79 | 12.27
July | 12.83 | 13.57 | 13.9
August | 12.81 | 13.47 | 13.9
September | 11.35 | 11.75 | 12.31
October | 8.16 | 8.25 | 9.04
November | 5.39 | 5.19 | 6.24
December | 3.22 | 3.07 | 3.99
Mean Annual | 7.5717 | 7.7742 | 8.515

## Degree days C.F and HWS
Standard Degree Days- Scotland
RETURN TO HEAT DEMAND CALCULATION
Degree Days and Ventilation Factor
| Table 1 |  |  |  | Table 2
| Location | Ventilation factor | Choice |  | Standard Degree Days in UK for the last 20 years (averages for 2007)
| North & Middlands | 29 | 28.5 |  |  | West Scotland | East Scotland | N. West Scotland | N. East Scotland | North Scotland
| Northern Ireland | 26.5 |  |  | January | 339 | 352 | 318 | 350 | 334
| Scotland | 28.5 |  |  | February | 303 | 310 | 295 | 316 | 305.5
| South East & Wales | 27 |  |  | March | 293 | 297 | 301 | 306 | 303.5
| South West | 25 |  |  | April | 227 | 238 | 242 | 248 | 245
| Source - CIBSE guide |  |  |  | May | 154 | 174 | 195 | 183 | 189
[5 empty] | June | 85 | 93 | 120 | 104 | 112
[5 empty] | July | 51 | 56 | 79 | 60 | 69.5
[5 empty] | August | 54 | 56 | 69 | 61 | 65
[5 empty] | September | 96 | 97 | 104 | 105 | 104.5
[5 empty] | October | 183 | 181 | 184 | 191 | 187.5
[5 empty] | November | 268 | 274 | 248 | 276 | 262
[5 empty] | December | 347 | 357 | 314 | 356 | 335
Source - MetOffice
Correction Factors - Source: CIBSE guide
| occupied period (days) | Correction Factor |  | Occupied Period (hours) | Correction Factor |  | Type of Heating | Correction Factor
| 5 | 0.8 |  | 4 | 0.8 |  | Continuous | 1
| 7 | 1 |  | 8 | 1 |  | Intermittent-responsive plant | 0.7
|  |  |  | 12 | 1.12 |  | Intermittent-plant with long time lag | 0.85
|  |  |  | 16 | 1.22
HWS - McMullan, R. "Environmental Science in Building" . 6th edition
HWS provision in W/m2 of floor
| Building Type | HWS (W/m2)
| Office - 5 or 6 day week | 2
| Shop - 6 day week | 1
| Factories - 5 day single shift | 9
| Factories - 6 day single shift | 11
| Factories - 7 day multiple shift | 12
| Warehouse | 1
| Residential | 17.5
| Hotels | 8
| Hospitals | 29
| Education | 2

## Woodchip
| FUEL DATA - WOODCHIP | [9 empty] | INPUTS ARE IN WHITE BOXES
DO NOT OVERWRITE ANY OTHER CELLS
Select Option
| Moisture content* | Kind of wood | Ash content (%) |  | Fuel density |  | Calorific value |  |  | Price per tonne (GBP) | Transport cost per tonne per mile (GBP) | Distance (Miles) | Total cost
|  |  | dry basis | as received | kg/m3 | kWh/m3 | MJ/kg |  | kWh/kg |  |  |  | (GBP per kWh)
Woodchip1 | M20 | Hard Wood | A0.7 | 0.56 | 325 | 1364.2417 | 15.1116 |  | 4.1977 | 45 | 0.4 | 25 | 0.013103
| 20 |  | 0.7
Woodchip2 | M20 | Hard Wood | A0.7 | 0.56 | 325 | 1364.2417 | 15.1116 |  | 4.1977 | 45 | 0.4 | 25 | 0.013103
| 20 |  | 0.7
WoodChip3 | M20 | Hard Wood | A0.7 | 0.56 | 325 | 1364.2417 | 15.1116 |  | 4.1977 | 45 | 0.4 | 25 | 0.013103
| 20 |  | 0.7
| *For better performance, try to use the limits values defined by CEN/TS 14961:2005 | [11 empty] | RETURN TO MAIN MENU
Default net calorific value (HHV) for dry wood taken is (MJ/kg) | [5 empty] | Default dry bulk density (kg/m3)
| Soft Wood - 18.5 |  | Hard Wood - 19.5 |  |  |  |  | Soft Wood - 195 |  | Hard Wood - 260
Other Values | [5 empty] | Other Values
| Woodchip1 | Woodchip2 | WoodChip3 |  |  |  | Woodchip1 |  | Woodchip2 | WoodChip3
| - | - | - |  |  |  | - |  | - | -
Source: Smith, K.R.; Kaltschmitt, M.; Thrän, D. 2001 "Renewable Energy from Biomass" | [5 empty] | Source:UBET Unified Bioenergy Terminology
*When dealing with the fuel supplier, following the CEN/TS 14961:2005, the specifications of the fuel properties are given as bellow
| Moisture (M) |  |  |  |  | Ash content (dry basis)
M20 | Moisture ≤ 20% |  | Dried |  |  | A0.7 | Ash content ≤ 0.7%
M30 | Moisture ≤ 30% |  | Suitable for storage |  |  | A1.5 | Ash content ≤ 1.5%
M40 | Moisture ≤ 40% |  | Limited for storage |  |  | A3.0 | Ash content ≤ 3.0%
M55 | Moisture ≤ 55% |  |  |  |  | A6.0 | Ash content ≤ 6.0%
M65 | Moisture ≤ 65% |  |  |  |  | A10.0 | Ash content ≤ 10.0%

## Pellet
| FUEL DATA - PELLETS | [6 empty] | INPUTS ARE IN WHITE BOXES
DO NOT OVERWRITE ANY OTHER CELLS
| Moisture content* |  | Ash content (%) |  | Fuel density |  | Calorific value |  | Price per tonne delivered (GBP) | Total cost
|  |  | dry basis | as received | kg/m3 | kWh/m3 | MJ/kg | kWh/kg |  | (GBP per kWh)
Pellet1 | M10 |  | A0.7 | 0.63 | 777.7778 | 3836.1296 | 17.7558 | 4.9322 | 130 | 0.026358
| 10 |  | 0.7
Pellet2 | M10 |  | A0.7 | 0.63 | 777.7778 | 3836.1296 | 17.7558 | 4.9322 | 130 | 0.026358
| 10 |  | 0.7
Pellet3 | M10 |  | A0.7 | 0.63 | 777.7778 | 3836.1296 | 17.7558 | 4.9322 | 130 | 0.026358
| 10 |  | 0.7
| *For better performance, try to use the limits values defined by CEN/TS 14961:2005 | [8 empty] | RETURN TO MAIN MENU
Base Net Calorific Value (HHV) for dry wood taken is (MJ/kg) | [5 empty] | Dry Bulk density taken is (kg/m3)
| Pellet1 | Pellet2 | Pellet3 |  |  |  | Pellet1 | Pellet2 | Pellet3
| 20 | 20 | 20 |  |  |  | 700 | 700 | 700
*density of pellet is typically between 600 and 700 kg/m3 (1)
1 - Physical Characterisation and chemical composition of densified biomass fuels with regard to their combustion behaviour. Published in: Proceedings of the 1st World Conference on Pellets
*When dealing with the fuel supplier, following the CEN/TS 14961:2005, the specifications of the fuel properties are given as bellow
| Moisture (M) |  |  | Ash Content (dry basis)
M10 | Moisture ≤ 10% |  |  | A0.7 | Ash content ≤ 0.7%
M15 | Moisture ≤ 15% |  |  | A1.5 | Ash content ≤ 1.5%
M20 | Moisture ≤ 20% |  |  | A3.0 | Ash content ≤ 3.0%
|  |  |  | A6.0 | Ash content ≤ 6.0%
|  |  |  | A6.0+ | Ash content ≥6.0%

## Boiler
|  | BOILER SIZING |  |  |  | INPUTS ARE IN WHITE BOXES
DO NOT OVERWRITE ANY OTHER CELLS
| Number of boilers |  | 1
|  | select option | [5 empty] | select option
| Main Boiler | Automatic |  |  |  |  | Not in Use | Automatic
| Boiler capacity |  | 30 |  | kW |  |  |  | 0
Ignore this line
| Turn-down ratio |  | 3 | : 1 |  | 0.33333 |  |  | 3 | : 1
| Boiler efficiency |  | 80 |  | % |  |  |  | 80
| Minimum power output |  | 10 |  | kW
RETURN TO MAIN MENU
| Final system capacity |  | 30 |  | kW |  | Power to be supplied by secondary source* |  | 13.2872 |  | kW
| New build capital cost ** |  | 12300 |  | GBP
*includes peak demand at defined OAT
Load Profile kW
|  | Load Profile |  | Mean Load
| January | 32.5673 |  | 26.127
| February | 32.4598
| March | 30.6866
| April | 27.8655
| May | 24.0773
| June | 20.7323
| July | 18.3411
| August | 18.4755
| September | 20.786
| October | 25.4878
| November | 29.5984
| December | 32.4464
| Mean Energy Consumed (kWh) | [6 empty] | Fuel Consumption Data
|  | January | 27002.1698
|  | February | 24698.4211
|  | March | 22496.2028
|  | April | 19963.937
|  | May | 17235.0204
|  | June | 12050.5987
|  | July | 8736
|  | August | 8736
|  | September | 13410.465
|  | October | 17355.2824
|  | November | 21516.9373
|  | December | 27302.1669
|  | Total | 220503.2013
**Reference: Biomass sector review for the Carbon Trust for the Carbon Trust
Auxiliary Tables - main boiler sizing | [9 empty] | Auxiliary Table -Selects Value for auto or defined
Main boiler
[10 empty] | Working Power |  | 30
[5 empty] | Mean Value for graph |  |  | Boiler Cap. |  | Secondary Boiler
|  | Mean Load |  |  | 26.127 |  |  | 30 |  | Working Power |  | 0
Mean |  | 26.127 |  |  | 26.127 |  |  | 30
Min |  | 18.3411 |  |  | 26.127 |  |  | 30 |  | Min Capacity |  | 0
Max1 |  | 55.0234 |  |  | 26.127 |  |  | 30
Max defined |  | 32.5673 |  |  | 26.127 |  |  | 30
Max defined corrected |  | 30 |  |  | 26.127 |  |  | 30
Min defined |  | 10 |  |  | 26.127 |  |  | 30 |  | Efficiency
[5 empty] | 26.127 |  |  | 30 |  | 80
[5 empty] | 26.127 |  |  | 30
Power to be suplied by a sec boiler |  |  | 2.5673 |  | 26.127 |  |  | 30
[5 empty] | 26.127 |  |  | 30
[5 empty] | 26.127 |  |  | 30
Secondary Boiler
Capacity to be supplied |  |  | 0 |  |  |  | New
Max Capacity |  |  | 0 |  |  | Boiler Cap |  | 0
0
0
0
System minimum Output | [7 empty] | 0
Matrix | [7 empty] | 0
Min. Boiler 1 | 10 | [6 empty] | 0
Min. Boiler 2 | [7 empty] | 0
Minimum | 10 | [6 empty] | 0
| 10 | [6 empty] | 0
| 10 | [6 empty] | 0
| 10 | [6 empty] | 0
10
10
10
10
10
10
10
10
Capital Cost
Power out | Base Value
30000 | 360
5000 | 225
300 | 410 | 500
Boiler 1 | 12300
Boiler 2 | 0
auxiliar energy Demand

## Fuel Comparator and Consumption
FUEL COST AND CONSUMPTION
Fuel Price Comparator
The selected biomass fuels will be used at further calculations
BACK TO MAIN MENU
|  |  | Fuel |  |  | Typical price* (pence per kWh)
|  |  | Woodchip1 |  |  | 1.3103
|  |  | Pellet1 |  |  | 2.6358 | User Input |  |  |  |  | Pay back period
|  |  | Heating Oil |  |  | 3.75 | [5 empty] | Kind of Fuel
|  |  | LPG | 19 kg propane |  | 8.26 | [5 empty] | Against
|  |  |  | 47 kg propane |  | 6.76 | [5 empty] | Savings per year |  |  | #REF!
|  |  |  | LPG Domestic |  | 4.68
|  |  |  | LPG Commercial |  | 3.51 | [5 empty] | Payback Period |  |  | #REF!
|  |  | Electricity |  |  | 10
|  |  | Mains Gas |  |  | 3 | [6 empty] | Auxiliary Box
|  |  | Coal | house coal |  | 2.57 | [6 empty] | Woodchip1 |  | Pellet1
|  |  |  | Coalite |  | 4.09 | [6 empty] | Woodchip2 |  | Pellet2
|  |  | values in p/kWh | [9 empty] | WoodChip3 |  | Pellet3
|  |  | Select source |  | Woodenergy
|  | * Source: | [10 empty] | For the storage system
|  |  | Woodenergy | [9 empty] | 1364.2417 | 325
|  |  | SAP 2005 | [9 empty] | 3836.1296 | 777.7778
Fuel Consumption and Monthly Cost
Woodchips | [12 empty] | Selected Consumption
6.4327
| Woodchip1 |  |  | Woodchip2 |  |  | WoodChip3 | [5 empty] | 5.8838
Month | Consumption Tonnes | Cost - British Pounds |  | Consumption Tonnes |  | Cost - British Pounds | Consumption Tonnes | Cost - British Pounds |  |  |  |  | 5.3592
January | 6.4327 | 353.7964 |  | 6.4327 |  | 353.7964 | 6.4327 | 353.7964 |  |  |  |  | 4.756
February | 5.8838 | 323.6115 |  | 5.8838 |  | 323.6115 | 5.8838 | 323.6115 |  |  |  |  | 4.1059
March | 5.3592 | 294.7569 |  | 5.3592 |  | 294.7569 | 5.3592 | 294.7569 |  |  |  |  | 2.8708
April | 4.756 | 261.5778 |  | 4.756 |  | 261.5778 | 4.756 | 261.5778 |  |  |  |  | 2.0812
May | 4.1059 | 225.8222 |  | 4.1059 |  | 225.8222 | 4.1059 | 225.8222 |  |  |  |  | 2.0812
June | 2.8708 | 157.8932 |  | 2.8708 |  | 157.8932 | 2.8708 | 157.8932 |  |  |  |  | 3.1947
July | 2.0812 | 114.4636 |  | 2.0812 |  | 114.4636 | 2.0812 | 114.4636 | Monthly | Wood Consumption - tonnes | Woodchip2 |  | 4.1345
August | 2.0812 | 114.4636 |  | 2.0812 |  | 114.4636 | 2.0812 | 114.4636 |  |  |  |  | 5.1259
September | 3.1947 | 175.7108 |  | 3.1947 |  | 175.7108 | 3.1947 | 175.7108 |  |  |  |  | 6.5041
October | 4.1345 | 227.3979 |  | 4.1345 |  | 227.3979 | 4.1345 | 227.3979
November | 5.1259 | 281.926 |  | 5.1259 |  | 281.926 | 5.1259 | 281.926
December | 6.5041 | 357.7271 |  | 6.5041 |  | 357.7271 | 6.5041 | 357.7271
TOTAL | 52.5299 | 2889.147 |  | 52.5299 |  | 2889.147 | 52.5299 | 2889.147
Back to woodchip fuel data
Back to boiler sizing
Wood pellets | [12 empty] | Selected Consumption
711.712
| Pellet1 |  |  | Pellet2 |  |  | Pellet3 | [5 empty] | 650.9907
Month | Consumption Tonnes | Cost - British Pounds |  | Consumption Tonnes |  | Cost - British Pounds | Consumption Tonnes | Cost - British Pounds |  |  |  |  | 592.9456
January | 5.4747 | 711.712 |  | 5.4747 |  | 711.712 | 5.4747 | 711.712 |  |  |  |  | 526.2012
February | 5.0076 | 650.9907 |  | 5.0076 |  | 650.9907 | 5.0076 | 650.9907 |  |  |  |  | 454.2735
March | 4.5611 | 592.9456 |  | 4.5611 |  | 592.9456 | 4.5611 | 592.9456 |  |  |  |  | 317.6247
April | 4.0477 | 526.2012 |  | 4.0477 |  | 526.2012 | 4.0477 | 526.2012 |  |  |  |  | 230.2599
May | 3.4944 | 454.2735 |  | 3.4944 |  | 454.2735 | 3.4944 | 454.2735 |  |  |  |  | 230.2599
June | 2.4433 | 317.6247 |  | 2.4433 |  | 317.6247 | 2.4433 | 317.6247 |  |  |  |  | 353.4675
July | 1.7712 | 230.2599 |  | 1.7712 |  | 230.2599 | 1.7712 | 230.2599 | Monthly | Fuel Cost - GBP | Pellet1 |  | 457.4433
August | 1.7712 | 230.2599 |  | 1.7712 |  | 230.2599 | 1.7712 | 230.2599 |  |  |  |  | 567.1345
September | 2.719 | 353.4675 |  | 2.719 |  | 353.4675 | 2.719 | 353.4675 |  |  |  |  | 719.6192
October | 3.5188 | 457.4433 |  | 3.5188 |  | 457.4433 | 3.5188 | 457.4433
November | 4.3626 | 567.1345 |  | 4.3626 |  | 567.1345 | 4.3626 | 567.1345
December | 5.5355 | 719.6192 |  | 5.5355 |  | 719.6192 | 5.5355 | 719.6192
TOTAL | 44.7072 | 5811.9318 |  | 44.7072 |  | 5811.9318 | 44.7072 | 5811.9318
Back to Pellet fuel data
Back to boiler sizing

## Storage options
STORAGE OPTIONS
Selected Storage Option |  |  |  |  | Storage type | Depth | Width/ Diameter | Length | Fall angle to the horizontal | Exit diameter | Extractor angle | Storage capacity
Square Silo Sloping Floor |  | Woodchip1 |  |  |  | m | m | m | degrees | m | degrees | m3
[5 empty] | Square silo sloping floor | 2 | 2 | 2 | N/A | N/A | 37 | 4.9858
Storage capacity (tonnes) |  | 1.6204
Cost per delivery |  | 89.1209 |  |  | Walking floor | 1 | 2 | 2 | N/A | N/A | N/A | 4
|  | BACK TO MAIN MENU |  |  | Gravity hopper | 1 | 1 | N/A | 40 | 0.5 | N/A | 0.88151
Woodchip Storage
[5 empty] | Average fuel consumption | Month
[6 empty] | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Fuel | Fuel density | Storage type | Storage capacity | Cost per delivery | kg/month | 6432.6617 | 5883.8452 | 5359.2161 | 4755.9605 | 4105.8573 | 2870.7851 | 2081.1562 | 2081.1562 | 3194.7427 | 4134.507 | 5125.9281 | 6504.1293
| kg/m3 |  | Tonnes | GBP | kg/hour | 8.6461 | 8.6782 | 7.2032 | 6.6055 | 5.5186 | 3.9872 | 2.7973 | 2.7973 | 4.4371 | 5.5571 | 7.1193 | 8.7421
Woodchip1 | 325 | Square silo sloping floor | 1.6204 | 89.1209 | Storage capacity (days) | 7.8089 | 7.7799 | 9.373 | 10.2212 | 12.2342 | 16.9331 | 24.1365 | 24.1365 | 15.2161 | 12.1494 | 9.4834 | 7.7231
|  | Walking floor | 1.3 | 71.5 |  | 6.2649 | 6.2417 | 7.5198 | 8.2002 | 9.8152 | 13.5851 | 19.3642 | 19.3642 | 12.2076 | 9.7472 | 7.6084 | 6.1961
Wood Pellet Storage
[5 empty] | Average fuel consumption | Month Jan: Month
[6 empty] | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Fuel | Fuel density | Storage type | Storage capacity | Cost per delivery | kg/month | 5474.7075 | 5007.6209 | 4561.1197 | 4047.7012 | 3494.4116 | 2443.2667 | 1771.2297 | 1771.2297 | 2718.9805 | 3518.7948 | 4362.573 | 5535.5321
| kg/m3 |  | Tonnes | GBP | kg/hour | 7.3585 | 7.3859 | 6.1305 | 5.6218 | 4.6968 | 3.3934 | 2.3807 | 2.3807 | 3.7764 | 4.7296 | 6.0591 | 7.4402
Pellet1 | 777.7778 | Square silo sloping floor | 3.8778 | 504.1181 | Storage capacity (days) | 21.9578 | 21.8764 | 26.356 | 28.741 | 34.4014 | 47.6145 | 67.8697 | 67.8697 | 42.7862 | 34.1631 | 26.6666 | 21.7166
|  | Walking floor | 3.1111 | 404.4444 |  | 17.6164 | 17.551 | 21.1449 | 23.0584 | 27.5996 | 38.2002 | 54.4506 | 54.4506 | 34.3266 | 27.4084 | 21.3941 | 17.4228
|  | Gravity hopper | 0.68562 | 89.1301 |  | 3.8822 | 3.8678 | 4.6598 | 5.0815 | 6.0823 | 8.4184 | 11.9996 | 11.9996 | 7.5648 | 6.0402 | 4.7148 | 3.8396
Auxiliary Table | kg | cost | Storage Capacity
Woodchip1 | 52529.9455 | 2889.147
Pellet1 | 44707.1675 | 6828.8929

## Thermal Buffer
Thermal Buffer
RETURN TO MAIN MENU
| Inputs | [10 empty] | Auxiliar boiler data
HWS
|  | Number of hours of stored hot water |  |  |  | 2 |  | Start-up energy requested |  |  |  | Auxiliar boiler power (kW) | 13.2872
|  | Temperature drop through heating circuit |  |  |  | 11 |  | Fuel moisture content |  |  | 20 | HWS mean demand (kW) | 0.8
|  | Energy stored (kWh) |  |  |  | 1.6 |  | Start up energy (kWh) |  |  | 15 | Start up period using A. Boiler (h) | 1.1289
|  | Buffer utilization |  | HWS supply | [7 empty] | *depending of the control configuration, the auxiliar boiler may
be used to supply hot water during summer or energy for
|  | Total energy stored (kWh) |  | 1.6 | [7 empty] | the start-up process
Requested Capacity
|  | Storage capacity requested (L) |  |  |  | 124.6753
|  | Total water volume (m3) |  |  |  | 0.12468
|  | Number of tanks |  |  |  | 2
|  | Buffer volume incl. insulation (m3) |  |  |  | 0.10909 |  | (*) (**)
*just indicative value, may vary with manufacturer
**value for each tank
Illustrative buffer dimensions (individual)
|  | Proportion between diameter and height (D/H) | [5 empty] | 0.6 | *
|  | Diameter | 0.4368 | m
|  | Height | 0.728 | m
*the proportion usually varies around 0.4, depending of the manufacturer
Inputs
Calculation Method
Auxiliar Boiler
| Thermal Lining | [5 empty] | Sizing |  | 37402.5974 |  |  | 13.2872
| Fuel Moisture Content |  |  | 20 |  |  | Circuit Temperature Drop |  |  |  | 11 | 0.8
| Requested Energy (kWh) |  |  | 200
[7 empty] | HWS Capacity |  |  |  | 6.8571
| HWS (kWh) |  |  | 280
| Number of hours water supply |  |  | 4
auxiliary Table
Defining Fuel Moisture Content
Kind Of Fuel
20
Moisture Content of Fuel -Pellet |  |  |  |  | Moisture Content of Fuel -Woodchip
10 |  |  |  |  | 20
Pellet1 |  | 10 |  |  | Woodchip1 |  | 20
Pellet2 |  | 10 |  |  | Woodchip2 |  | 20
Pellet3 |  | 10 |  |  | WoodChip3 |  | 20

## Funding
Funding Schemes at Scotland
RETURN TO MAIN MENU
Name |  | Requirements | Grant Value |  | Information
Low Carbon Buildings Program Phase 2 |  | Public Sector - schools, hospitals, housing associations, local authorities and charitable bodies | Up to 30% of installation costs. |  | http://www.lowcarbonbuildingsphase2.org.uk/
Boilers up to 50 kW
Low Carbon Buildings Program Phase 1 |  | Residential Building | Up to 30% of the installation costs or 1,500 pounds. The lowest value |  | http://www.lowcarbonbuildings.org.uk
You must have insulated the whole of the loft of the property to meet current building regulations e.g. 270mm of mineral wool loft insulation or suitable alternative; You must have installed cavity wall insulation throughout the property where practicable (i.e. where the property does have cavity walls); You must use low energy light bulbs in appropriate light fittings in all the main rooms (i.e. kitchen, hallway and all main living rooms) in the property; You must have installed basic controls for your central heating system (if any), including controls that ensure your boiler only operates when there is a demand for heat and a programmer or timer for the property as a whole.
Highland and Island Enterprises |  | Communities in the Highlands and Islands | Funding is divided into 4 phases, each one with its own funding values |  | http://www.hie.co.uk/community-investment.html
Community associations, enterprises, development trusts and groups
|  |  | Start Up | Up to 2,000 Pounds
|  |  | Feasibility | Up to 15,000 Pounds
|  |  | Pre-Planning | Up to 50,000 Pounds
|  |  | Pos-Planning | Up to 200,000 Pounds
Energy Saving Trust - Communities |  | The basic premise is that applicants must be Scotland based, legally constituted, non-profit distributing community groups: | The grant is divided into two categories: |  | http://www.energysavingtrust.org.uk/schri/community/grant.cfm#eligible
Technical assistance funding: available to support non-capital projects, such as feasibility or scooping studies and capacity building within a community. The maximum grant is £10,000.
local/national voluntary, non-profit and charitable organisations
local rural partnerships
local authorities
|  | housing associations | Capital grants: contribute to the capital costs of a project. The maximum grant is £100,000.
local enterprise companies
companies limited by guarantee
Universities and schools
Energy Saving Trust - Householders |  | The system must be designed, installed and commissioned by an approved installer using approved system components | Funding for householders is set at 30% of the installed cost of a renewable measure up to £4,000 |  | http://www.energysavingtrust.org.uk/schri/household/grant.cfm
Bio-energy Capital Grants Scheme |  | Round 3 of the Bio-energy Capital Grants Scheme was launched in December 2006 with a 10 week application window which closed in March 2007. \ | The minimum award limit was £25,000 and the maximum single award was £1m. Higher awards were possible for multiple or bundled applications. |  | http://www.defra.gov.uk/farm/crops/industrial/energy/capital-grants.htm
Defra intends to run further rounds of the scheme. The details are likely to be broadly similar to round 3.
The round was open to applications from the industrial, commercial and community sectors. "Community" included local authorities, schools, etc. There was no targeting of any particular technology or sector.
ScottishPower Green Energy Trust |  | The ScottishPower Green Energy Trust supports the development of small scale community based environmental and educational renewable energy projects. | The Trust provides up to 50 per cent of the project cost, up to a maximum of £25,000. |  | http://freight.quix.co.uk/Default.aspx
The Trust does not support applications that will benefit only private companies, individual or government bodies.
Environmental Transformation Fund |  | The domestic ETF brings together Defra’s and BERR’s existing low carbon technology funding programmes together with a number of new investments to begin in 2008/09 | On 21 February 2008 Hilary Benn announced the first set of new schemes to be funded from Defra’s element of the domestic ETF |  | http://www.defra.gov.uk/environment/climatechange/uk/energy/fund/
47.4m for the Carbon Trust’s technology programmes in 2008/09
The Environmental Transformation Fund itself will not be open for funding requests. Instead, schemes funded by the ETF, such as those operated by the Carbon Trust and BERR, will be publicised via their websites and in the usual ways when funding becomes available.
£10m in 2008/09 for new rounds of the Bio-energy Capital Grants and Bio-energy Infrastructure Schemes
Around £10m over three years for projects that demonstrate the potential of anaerobic digestion technologies at commercial scale

## WoodChip CO2 calculator
Estimate of Carbon Emissions from the Production of Woodchips
[5 empty] | Assumes drying at roadside only |  |  |  | CREATED BY CAMPBELL PALMER
|  |  | CV |  | INPUTS ARE IN WHITE BOXES
Moisture Content at Felling | 60 | % IMC | 1666 |  | DO NOT OVERWRITE ANY OTHER CELLS
Moisture Content after drying at roadside | 20 | % FMC | 4006
Return to main menu
Harvesting
| tonnes/hr | Mean HP of equipment | kWh / tonne wood | litres diesel / tonne wood @ IMC | kg CO2 / tonne wood @ IMC | CO2 / tonne wood corrected to FMC
Felling | 5 | 10 | 1.492 | 0.15071 | 0.373 | 0.8969
Removal to Roadside
(Insert appropriate data) | tonnes/hr | Mean HP of equipment | kWh / tonne wood | litres diesel / tonne wood @ IMC | kg CO2 / tonne wood @ IMC | CO2 / tonne wood corrected to FMC
Skyline, Skidder or Forwarder | 5 | 200 | 29.84 | 3.0141 | 7.46 | 17.938
Transport to Depot
| tonnes / load | Mean mpg | Return Distance Miles | Fuel Used litres | Energy Used kWh | kWh / tonne wood | kg CO2 / tonne wood @ FMC
Haulage | 20 | 15 | 100 | 30.4667 | 301.62 | 15.081 | 3.7702
Chipping
| tonnes / hour | Mean HP of chipper |  |  |  | kWh / tonne wood | kg CO2 / tonne wood @ FMC | Density of Woodchips kg/m3
Conversion to Woodchips | 10 | 200 |  |  |  | 14.92 | 3.73 | 187.5
Delivery of Woodchips
| tonnes / load | Mean mpg | Return Distance Miles | Fuel Used litres | Energy Used kWh | kWh / tonne wood | kg CO2 / tonne wood @ FMC
Haulage to end user | 3.75 | 18 | 60 | 15.2333 | 150.81 | 40.216 | 10.054
Results
| Total carbon emissions/tonne of woodchips |  |  |  | 36.3892 | kgCO2/tonne wood
| kg CO2 / kWh energy in woodchips |  |  |  | 0.0090837 | kgCO2/kWh

## Results
RESULTS
| Boiler System Data |  |  |  | Fuel Data and Saving
| BUILDING HEAT DEMAND |  | 32.5673 | kW | SELECTED FUEL TYPE | Woodchip1
| BIOMASS BOILER SIZE |  | 30 | kW | COST PER kWh DELIVERED | 0.013103 | GBP
| BOILER INSTALATION COST |  | 12300 | GBP | SELECT SECONDARY FUEL | Mains Gas |  | SELECT
| SECONDARY HEAT SOURCE |  | 13.2872 | kW * | COST OF kWh SECONDARY | 0.03 | GBP
| *based on a peak demand of |  | 43.2872 | kW | ANNUAL SAVINGS | 3725.949 | GBP
| Storage and Consumption |  |  |  | Fuel Storage and Buffer Volumes
| STORAGE TYPE |  | Square Silo Sloping Floor |  | STORAGE SYSTEM VOLUME | 8 | m3
| FUEL STORAGE CAPACITY |  | 1.6204 | tonnes | BUFFERS OCCUPIED VOLUME | 0.21818 | m3
| *based on winter consumption |  | 7.8089 | days*
| FUEL CONSUMPTION (YEAR) |  | 52.5299 | tonnes
| FUEL COST (YEAR) |  | 2889.147 | GBP
RETURN TO MAIN MENU
Auxiliary Table
Consumption Table |  |  |  | FUEL TYPES AND COSTS
6.4327 | January |  |  | Heating Oil
5.8838 | February |  |  | 19 kg propane
5.3592 | March |  |  | 47 kg propane
4.756 | April |  |  | LPG Domestic
4.1059 | May |  |  | LPG Commercial
2.8708 | June |  |  | Electricity
2.0812 | July |  |  | Mains Gas
2.0812 | August |  |  | house coal
3.1947 | September |  |  | Coalite
4.1345 | October
5.1259 | November |  |  | Cost of selected source
6.5041 | December |  |  | 3
3