## Hydro
Small Scale Hydro | [13 empty] | ξ υ
Calculation Basis: | [13 empty] | ξ υ
1) First step is to find a site that has the required combination of head and flow rate
A comprehensive estimate of potential sites and their power in each catchment area has been estimated in Reference (2)
Q = flow rate; H = head; L = length of pipe from head to turbine; D= pipe diameter
| Power = | η(tot) *ρ *g* Q *H
| Efficiency η(tot) = | η(trans) * η(turb) * η(gen) | [5 empty] | Pipe roughness (1) |  |  | Friction coefficient (1)
| Losses = | ρ * Q^3 *32 f *L /(π^2 *D^5) |  | =(1- η(trans))* ρ *g* Q *H | [5 empty] | ξ (mm) | For turbulent flow, Re>10^6
[9 empty] | PVC | 0 | ξ/D | f
2) Actual flow rate of catchment area must be enough to leave at least 5% of the flow untouched | [8 empty] | Asbestos cement | 0.012 | 0.0001 | 0.0027
[9 empty] | New steel | 0.1 | 0.0004 | 0.004
3) Having found a site at a given H and Q, estimate the length of pipe L needed from source to turbine site | [8 empty] | Smooth concrete | 0.4 | 0.001 | 0.0049
| the pipe diamater may be estimated as follows: | [9 empty] | 0.004 | 0.007
[11 empty] | 0.01 | 0.009
| L/D^5 = | (1- η(trans))* g*H * π^2 / (32 f * Q^2) |  |  | = Z | [5 empty] | 0.02 | 0.012
| Reynolds No: | Re = | u*D / υ | = 4*Q / π *D *υ | [6 empty] | 0.04 | 0.017
Pipe friction coefficient is a function of relative roughness (ξ/D) & Re
Inputs:
|  | Flow |  |  |  | Demand |  |  |  | Pipe friction coefficient
|  | ρ at 15C= | 999.001 | kg/m3 |  | IT power | 1 | 250 | kW |  | Material: | steel
|  | g = | 9.81 | m/s2 |  | Fixed Infrastructure | 0.25 | 62.5 | kW |  | Pipe roughness ξ: | 0.1 | mm
|  | Transmission efficiency η(trans) = | 0.85 |  |  | Cooling | 0.03 | 7.5 | kW |  | Pipe diameter D: | 1 | m
|  | Turbine efficiency η(turb) = | 0.8 |  |  | TOTAL | 1.28 | 320 | kW |  | ξ / D = | 0.0001
|  | Generation efficincy η(gen) = | 0.95 |  |  | Tier 1 availability |  | 99.67%
|  | Friction coefficient (start) f = | 0.003
|  | % water unused at min flow period: | 5%
Calculations:
|  | η(tot) = | 0.646 |  |  |  | Q*H = | 50.5455 | m4/s
|  | kinematic viscosity at 15C υ = | 1.1371e-06 | kg/ms |  | Actual min flow | Qact | 53.0728 | / H m3/sec
Calculator for head and flow rate combinations, together with pipe length & diameter
H | Qact | Z | L | L/ Z | D | Re | ξ / D | check for f - reset if necc | Comments
m | m3 | m-4 | m |  | m |  |  | necc
5 | 10.6146 | 6.7136 | 500 | 74.4757 | 2.3681 | 5018761.5331 | 4.2228e-05 | 0.002
5 | 10.6146 | 6.7136 | 1000 | 148.9515 | 2.7203 | 4369085.6797 | 3.6761e-05
10 | 5.3073 | 53.7088 | 500 | 9.3095 | 1.5624 | 3803509.9995 | 6.4005e-05 | 0.0027
10 | 5.3073 | 53.7088 | 1000 | 18.6189 | 1.7947 | 3311147.7726 | 5.572e-05
15 | 3.5382 | 181.2671 | 500 | 2.7584 | 1.225 | 3234059.8945 | 8.1634e-05 | 0.0027
15 | 3.5382 | 181.2671 | 1000 | 5.5167 | 1.4071 | 2815412.6629 | 7.1066e-05
20 | 2.6536 | 429.6701 | 500 | 1.1637 | 1.0308 | 2882521.5586 | 9.7014e-05 | 0.003
20 | 2.6536 | 429.6701 | 1000 | 2.3274 | 1.1841 | 2509380.7665 | 8.4455e-05
20 | 2.6536 | 429.6701 | 1500 | 3.4911 | 1.2841 | 2313919.8578 | 7.7877e-05
30 | 1.7691 | 1450.1365 | 500 | 0.3448 | 0.80819 | 2450959.0796 | 0.00012373 | 0.003
30 | 1.7691 | 1450.1365 | 1000 | 0.68959 | 0.92836 | 2133683.8074 | 0.00010772
30 | 1.7691 | 1450.1365 | 1500 | 1.0344 | 1.0068 | 1967486.7194 | 9.9326e-05
40 | 1.3268 | 3437.3606 | 500 | 0.14546 | 0.68006 | 2184542.8398 | 0.00014705 | 0.003
40 | 1.3268 | 3437.3606 | 1000 | 0.29092 | 0.78119 | 1901754.9998 | 0.00012801
40 | 1.3268 | 3437.3606 | 1500 | 0.43638 | 0.84718 | 1753623.331 | 0.00011804
50 | 1.0615 | 6713.5949 | 500 | 0.074476 | 0.59484 | 1998004.9536 | 0.00016811 | 0.003 |  |  | ξ/D | f
50 | 1.0615 | 6713.5949 | 1000 | 0.14895 | 0.6833 | 1739364.3378 | 0.00014635 |  | Example |  | 0.0001 | 0.0027
50 | 1.0615 | 6713.5949 | 1500 | 0.22343 | 0.74102 | 1603881.6169 | 0.00013495 |  |  |  | 0.0004 | 0.004
60 | 0.88455 | 11601.092 | 500 | 0.043099 | 0.53321 | 1857479.6404 | 0.00018755 | 0.003 |  |  | 0.001 | 0.0049
60 | 0.88455 | 11601.092 | 1000 | 0.086199 | 0.61249 | 1617029.9473 | 0.00016327 |  |  |  | 0.004 | 0.007
60 | 0.88455 | 11601.092 | 1500 | 0.1293 | 0.66423 | 1491076.1075 | 0.00015055 |  |  |  | 0.01 | 0.009
75 | 0.70764 | 22658.3828 | 500 | 0.022067 | 0.46639 | 1698869.6468 | 0.00021441 | 0.003 |  |  | 0.02 | 0.012
75 | 0.70764 | 22658.3828 | 1000 | 0.044134 | 0.53574 | 1478951.928 | 0.00018666 |  |  |  | 0.04 | 0.017
75 | 0.70764 | 22658.3828 | 1500 | 0.066201 | 0.581 | 1363753.2735 | 0.00017212
100 | 0.53073 | 53708.7593 | 500 | 0.0093095 | 0.39245 | 1514204.6041 | 0.00025481 | 0.003
100 | 0.53073 | 53708.7593 | 1000 | 0.018619 | 0.45081 | 1318191.671 | 0.00022182
100 | 0.53073 | 53708.7593 | 1500 | 0.027928 | 0.48889 | 1215514.9687 | 0.00020455
100 | 0.53073 | 53708.7593 | 2000 | 0.037238 | 0.51784 | 1147552.5018 | 0.00019311
150 | 0.35382 | 181267.0625 | 500 | 0.0027584 | 0.3077 | 1287502.434 | 0.00032499 | 0.0035
150 | 0.35382 | 181267.0625 | 1000 | 0.0055167 | 0.35346 | 1120835.9692 | 0.00028292
150 | 0.35382 | 181267.0625 | 1500 | 0.0082751 | 0.38331 | 1033531.7146 | 0.00026088
150 | 0.35382 | 181267.0625 | 2000 | 0.011033 | 0.40602 | 975744.3843 | 0.0002463
200 | 0.26536 | 429670.0741 | 500 | 0.0011637 | 0.25892 | 1147552.5018 | 0.00038622 | 0.004
200 | 0.26536 | 429670.0741 | 1000 | 0.0023274 | 0.29742 | 999002.4768 | 0.00033622
200 | 0.26536 | 429670.0741 | 1500 | 0.0034911 | 0.32255 | 921188.0875 | 0.00031003
200 | 0.26536 | 429670.0741 | 2000 | 0.0046547 | 0.34165 | 869682.1689 | 0.0002927
Mechanical Availability
Calculator for head and flow rate combinations, together with pipe length & diameter Qact: Hydroelectric equipment is robust and maintenance intervals are 5years +; Calculator for head and flow rate combinations, together with pipe length & diameter ξ / D: 5 | years
Calculator for head and flow rate combinations, together with pipe length & diameter Qact: Maintenance period can be low if replacement parts are available; Calculator for head and flow rate combinations, together with pipe length & diameter ξ / D: 2 | weeks
| Availability = 1 - (maintenance period)/(maintenance interval) | [5 empty] | 99.23%
Calculator for head and flow rate combinations, together with pipe length & diameter Qact: Standby generation still required, on average; Calculator for head and flow rate combinations, together with pipe length & diameter ξ / D: 2.8077 | days per year
However, planned maintenance intervals may be fitted in with planned replacement of IT equipment
Availability of Resource
From Scottish Hydrowpoer Resource Study (Source (2)) Appendix 4
| Area |  | Catchment area ref | Total no of schemes | Total power potential MW | No. Financially viable on grid
| Shetland |  | 311 | 308 | 6.1 | 0
| Orkney |  | 310 | 68 | 0.9 | 0
| E Caithness |  | 1 | 109 | 5.8 | 1
| N Caithness |  | 97 | 63 | 9.5 | 0
| E Sutherland |  | 2 | 375 | 38.4 | 6
| N Sutherland |  | 96 | 746 | 58.3 | 11
| NW Coastal |  | 95 | 1568 | 126 | 61
| L Shin / Dornoch |  | 3 | 649 | 60.7 | 9
| E Ross |  | 4 | 1014 | 93.9 | 19
| W Ross |  | 94 | 936 | 76 | 48
| Kintail |  | 93 | 1978 | 164.7 | 70
| Inverness and West |  | 5 | 797 | 98 | 37
| Loch Ness |  | 6 | 1049 | 119.3 | 44
| Skye |  | 303 | 1640 | 63.6 | 26
| Lewis& Harrris |  | 302 | 828 | 28.8 | 6
| Uists |  | 305 | 23 | 0.2 | 0
Total sites in Scotland (Source (2), pg 22)
| Power band |  | no of schemes | Total power MW
| 100kW-500kW |  | 537 | 150.4
| 500kW - 1MW |  | 300 | 193.2
| 1MW - 5 MW |  | 170 | 276.6
Conclusions
If sufficient resoucre is available within reasonable distance of the data centre,
this is a good soucre of power as it is constant power. simple technology, high availability
and relatively modest cost
If the plant is not conencted to the grid, it may still be finacially viable for this purpose
Specifics of where indivudal potential schemes are located resoucre are commercially available from (3):
Hydrobot® model
Unlikely to be scalable at specific location

## Data Sources
Dat Sources
(1) | Twidell, J; Weir, T: Renewable Energy Resources, 2nd ed, Taylor & Francis (2006), pg 38
(3) | Scottish Hydropower Resource Study Final Report 2008; For Scottish Government by Nick Forrest Associates /SIS Tech/ Black & Veatch; 26th August 2008
(2) | Nick Forrest Associates: http://www.nickforrestassoc.co.uk/