## Sizing Sheet
Table 1 |  |  |  | Formula Used:
COP considered | 3 |  |  | Land Area Required (m2) = [ heated floor area(m2) * builiding heat loss (W/m2) * (COP - 1) / COP / Energy extractable per m of ground pipe (W/m) * Spacing between Trenches (m) ]
Energy extractable per m of ground pipe | 20 | W/m |  | Source: http://www.dimplex.co.uk/assets/product_instructions/Dx_heat_pump_fact_sheet_Read-Only.pdf
Spacing between Trenches | 0.75 | m
Table 2
Building heat loss W/m2
Building Floor Area |  | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70 | 75 | 80 | 85 | 90 | 95 | 100
100 | Land Area Required (m2) | 50 | 62.5 | 75 | 87.5 | 100 | 112.5 | 125 | 137.5 | 150 | 162.5 | 175 | 187.5 | 200 | 212.5 | 225 | 237.5 | 250
150 |  | 75 | 93.75 | 112.5 | 131.25 | 150 | 168.75 | 187.5 | 206.25 | 225 | 243.75 | 262.5 | 281.25 | 300 | 318.75 | 337.5 | 356.25 | 375
200 |  | 100 | 125 | 150 | 175 | 200 | 225 | 250 | 275 | 300 | 325 | 350 | 375 | 400 | 425 | 450 | 475 | 500
250 |  | 125 | 156.25 | 187.5 | 218.75 | 250 | 281.25 | 312.5 | 343.75 | 375 | 406.25 | 437.5 | 468.75 | 500 | 531.25 | 562.5 | 593.75 | 625
300 |  | 150 | 187.5 | 225 | 262.5 | 300 | 337.5 | 375 | 412.5 | 450 | 487.5 | 525 | 562.5 | 600 | 637.5 | 675 | 712.5 | 750
350 |  | 175 | 218.75 | 262.5 | 306.25 | 350 | 393.75 | 437.5 | 481.25 | 525 | 568.75 | 612.5 | 656.25 | 700 | 743.75 | 787.5 | 831.25 | 875
400 |  | 200 | 250 | 300 | 350 | 400 | 450 | 500 | 550 | 600 | 650 | 700 | 750 | 800 | 850 | 900 | 950 | 1000
Step 1: Building heat load in kWhr/m2/annum is taken from HEM for a dwelling
Step 2: That value is divided by 8.76 to obtain the heat loss in W/m2 (8760 hrs in a year / conversion factor of 1000 from kW to W)
Step 3a: Table 1 is filled setting energy extractable as minimum of 3
Step 3b: Energy extractable is set to a maximum possible value for a given locale
Step 3c: Spacing between trenches is kept to a minimum possible
Step 4: The land area corresponding to the heated floor area of building on the left of the table and the building heat loss in W/m2 is read
Step 5: The space available obtained using freemaptools which calculates area is then compared against this value
Step 6: If it fails to meet these criteria, the proposed space is screened out and is not suitable for horizontal GSHP application