## User Guide
All boxes in blue, user is to input data as follows:

## Demand
DISTRICT AND DEMAND DEFINITION
District Name ----> | District 1 |  |  |  | District 2 |  |  |  | District 3
Housing Age band: | Property Type: |  |  |  | Property Type: |  |  |  | Property Type:
| Flat | Terrace | Semi-Detatched | Detatched | Flat | Terrace | Semi-Detatched | Detatched | Flat | Terrace | Semi-Detatched | Detatched
Pre 1917
1918 - 1938
1939 - 1959
1960 - 1975
1976 - 1982
1983 - 1989
1990 - 1999
Post 2000
Other Buildings in District: | Total Floor Area (m^2) |  |  |  | Total Floor Area (m^2) |  |  |  | Total Floor Area (m^2)
Churches
Community Hall
Hospital
Library
Office
Retail
School
Sports Centre
Supermarket
Swimming pool centre
University
[9 empty] | District 1 | District 2 | District 3
[8 empty] | Demand kWhr/year | 0 | 0 | 0
[8 empty] | Region | West Scotland | West Scotland | West Scotland
Additional/ Specific Demands kWhr/year
[8 empty] | Total Demand kWhr/yr | 0 | 0 | 0

## Cost
COSTS
| District 1 |  |  |  | District 2 |  |  |  | District 3
| Boiler | CHP | Electricity | Renewable Electricity | Boiler | CHP | Electricity | Renewable Electricity | Boiler | CHP | Electricity | Renewable Electricity
Energy supplied to system (kWh/yr) ------> | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inputs - Energy Prices
Estimated buy price of fuel (p/kWh energy supplied) | 3.07 | 3.07 | 10.44 | 10.44 | 3.07 | 3.07 | 10.44 | 10.44 | 3.07 | 3.07 | 10.44 | 10.44
User input buy price of fuel (p/kWh energy supplied) | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sell price of energy (p/kWh) | 5 | 8 | 14 | 12 | 5 | 8 | 14 | 12 | 5 | 8 | 14 | 12
Inputs - Finances
Required repayment period (years) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Interest on loan (%/100) | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06
Inputs - Maintenance Costs
Estimated maintenance costs/year (£/kW) | 3 | #N/A | 0.5 | 0.5 | 3 | #N/A | 0.5 | 0.5 | 3 | #N/A | 0.5 | 0.5
User input cost to maintain system/year (£/kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Outputs:
Gross profit (£/year) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net expenditure on fuel (£/year) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net profit (£/year) | 0 | #N/A | 0 | 0 | 0 | #N/A | 0 | 0 | 0 | #N/A | 0 | 0
Maximum capital input possible (£k) | 0 | #N/A | 0 | 0 | 0 | #N/A | 0 | 0 | 0 | #N/A | 0 | 0

## Emissions
EMISSIONS
District Heating Energy Source:
District | Pollutant | Natural Gas | Biomass - Woodchips* | Biomass - Woodchips (Actual)** | Electrical Grid (Current Energy Mix) | Electrical Grid (100% Wind Power) | CHP
District 1 | CO2 (kg) | 0 | 0 | 0 | 0 | 0 | 0
| CH4 (kg) | 0 | 0 | 0 | 0 | 0 | 0
| N2O (kg) | 0 | 0 | 0 | 0 | 0 | 0
District 2 | CO2 (kg) | 0 | 0 | 0 | 0 | 0 | 0
| CH4 (kg) | 0 | 0 | 0 | 0 | 0 | 0
| N2O (kg) | 0 | 0 | 0 | 0 | 0 | 0
District 3 | CO2 (kg) | 0 | 0 | 0 | 0 | 0 | 0
| CH4 (kg) | 0 | 0 | 0 | 0 | 0 | 0
| N2O (kg) | 0 | 0 | 0 | 0 | 0 | 0
|  |  | CO2(kg/kWh) | CH4(kg/kWh) | N2O(kg/kWh)
|  | Natural Gas | 0.20435 | 0.00027 | 0.00011
|  | Woodchip | 1e-09 | 0.000245 | 0.0001225
|  | Woodchip (Actual Combustion) | 0.354 | 0.00024548 | 0.00012274
|  | Electricty Grid (Current) | 0.58982 | 0.00026 | 0.00317
|  | Electricity (100% Wind Power) | 0.00525 | 0 | 0
2012 Guidelines to Defra / DECC's GHG Conversion Factors for Company Reporting
Produced by AEA for the Department of Energy and Climate Change (DECC) and the Department for Environment, Food and Rural Affairs (Defra)
Direct emissions of methane (CH4) and nitrous oxide (N2O), which are not absorbed in the biomass growth phase are not currently available.
http://www.epa.gov/climateleadership/documents/emission-factors.pdf
*"Biomass - Woodchips" Direct emissions of CO2 are set to 0 for biomass,since for this case it assumed all biomass material is regrown
**''Biomass - Woochips (Actual)'' Actual emissions from combustion of biomass fuel without considering regrowth.
Natural Gas
Electrical Grid (Current Energy Mix)
Electrical Grid (100% Wind Power)
CHP

## Efficiencies
EFFICIENCIES
Source |  | Transmission |  | Storage |  | Hardware
Grid Electricity | 1 | Wires | 1 | Thermal Storage Water Tank 35degC | 0 | Conventional Radiator | 0 | [5 empty] | 1
Boiler | 0 | Pipes | 0 | Thermal Storage Water Tank 75degC | 0 | Electrical Heater | 0 | [5 empty] | 2
CHP | 0 |  |  | PCM Storage Heater | 0 | Ground Source Heat Pump 3.4 | 1 | [5 empty] | 3
|  |  |  | Battery | 0 | Ground Source Heat Pump 1.68 | 0 | [5 empty] | 4
5
6
| A |  | D |  |  |  | N | Total |  |  |  |  | 7
Energy | 0.37 |  | 0.99 |  | 1 |  | 3.4 | 124.5% |  |  |  |  | 8
Exergy | 0.373 |  | 1 |  | 1 |  | 0.72 | 26.86% |  |  |  |  | 9
10
Boiler/CHP Fuel
Fossil Fuels
Grid Electricity Type
Non-Thermal Renewables | [7 empty] | Energy Efficiency | Exergy Efficiency | Energy Index | Exergy Index | District
[8 empty] | 124.5% | 26.86% | 10 | 8 | District 3
Heat pump COPs must be considered by user to properly assess energy

## Output Matrix
OUTPUT MATRIX
Criteria | Weighting (%) | District 1 |  |  |  | District 2 |  |  |  | District 3
|  | Boiler | CHP | Electricity | Renewable Electricity | Boiler | CHP | Electricity | Renewable Electricity | Boiler | CHP | Electricity | Renewable Electricity
Cost | 21.1039 | 3 | 5 | 6 | 4 | 3 | 5 | 6 | 4 | 3 | 5 | 6 | 4
Energy Efficiency | 15.5844 | 6 | 6 | 2 | 10 | 6 | 6 | 2 | 10 | 6 | 6 | 2 | 10
Exergy Efficiency | 6.8182 | 3 | 4 | 5 | 8 | 3 | 4 | 5 | 8 | 3 | 3 | 5 | 8
Emissions | 9.0909 | 6 | 5 | 3 | 10 | 6 | 5 | 3 | 10 | 6 | 5 | 3 | 10
Impacts | 15.2597 | 8 | 9 | 5 | 8 | 8 | 9 | 5 | 8 | 8 | 9 | 5 | 8
End User Cost | 12.6623 | 8 | 10 | 3 | 3 | 8 | 10 | 3 | 3 | 8 | 10 | 3 | 3
Income + Subsidies | 19.4805 | 7 | 8 | 5 | 7 | 7 | 8 | 5 | 7 | 7 | 8 | 5 | 7
Average |  | 5.9156 | 6.9156 | 4.3084 | 6.8214 | 5.9156 | 6.9156 | 4.3084 | 6.8214 | 5.9156 | 6.8474 | 4.3084 | 6.8214

## ExergyData (hidden)
Label | Technology | Energy Efficency Ƞ | Exergy Efficiency Ψ |  |  |  |  | Boiler Energy Types | Energy Mix
F | Thermal Energy Store, Water Tank (fluid heat exchanger) (35degC) | 83% | 27% |  |  |  |  | Fossil Fuels | Current (~fossil fuel)
G | Thermal Energy Store, Water Tank (fluid heat exchanger) (75degC) | 83% | 73% |  |  |  |  | Biofuel | 50:50 mix
A | Fossil Fuel Electricity Generation | 37% | 37.3% | [5 empty] | No Fossil, Combustion Based
L | Fossil Fuel Electricity to Heat | 95% | 16.6% | [5 empty] | Non-Thermal Renewables
N | GSHP System (COP 3.4) Product exergy/Fuel exergy | 340% | 72% |  | exergy | 26.86%
O | GSHP System (COP 1.68) Product exergy/Fuel exergy | 168% | 59.77% |  | energy | 124.5% | index | 8
B | Fuel Based District boiler | 85% | 30.9% |  |  |  | Non-Thermal Renewables
D | Wires | 99% | 100% |  |  |  | Exergy | Fossil Index | BioFuel | 50/50 | Thermal Renew | Renew
E | Pipe Losses | 95% | 74% |  |  |  | 2.7% | 1 | 3 | 2 | 3 | 4
I | Battery | 80% | 50% |  |  |  | 5.4% | 2 | 4 | 3 | 4 | 5
H | PCM material | 90% | 60% |  |  |  | 8.1% | 2 | 4 | 3 | 4 | 5
C | CHP Unit | 92% | 43% |  |  |  | 10.8% | 3 | 5 | 4 | 5 | 6
K | Radiator | 97% | 74% |  |  |  | 13.5% | 3 | 5 | 4 | 5 | 6
[7 empty] | 16.2% | 4 | 6 | 5 | 6 | 7
[7 empty] | 18.9% | 4 | 6 | 5 | 6 | 7
[7 empty] | 21.6% | 5 | 7 | 6 | 7 | 8
[7 empty] | 24.3% | 5 | 7 | 6 | 7 | 8
[7 empty] | 27% | 6 | 8 | 7 | 8 | 9
District 1
District 2
District 3
[7 empty] | Energy | Fossil Index | BioFuel | 50/50 | Thermal Renew | Renew
[7 empty] | 25% | 1 | 3 | 2 | 3 | 5
[7 empty] | 30% | 2 | 4 | 3 | 4 | 6
[7 empty] | 35% | 3 | 5 | 4 | 5 | 7
[7 empty] | 40% | 4 | 6 | 5 | 6 | 8
[7 empty] | 60% | 6 | 7 | 6 | 7 | 9
[7 empty] | 70% | 7 | 8 | 7 | 8 | 9
[7 empty] | 90% | 8 | 9 | 8 | 9 | 10
[7 empty] | 100% | 8 | 10 | 9 | 10 | 10
[7 empty] | energy | 124.5%
[7 empty] | Index | 10

## Cost Data (hidden)
Electricity | Size kWh | Cost p/kWh |  |  | Gas | Size kWh | Cost p/kWh
Very Small | 0 | 10.44 |  |  | Very Small | 0 | 3.07
Small | 20000 | 8.78 |  |  | Small | 278000 | 2.42
Small/Medium | 500000 | 7.81 |  |  | Medium | 2778000 | 2.13
Medium | 2000000 | 7.05 |  |  | Large | 27778000 | 1.92
Large | 20000000 | 6.83 |  |  | Very Large | 277778000 | 1.7
Very Large | 70000000 | 6.58
Extra Large | 150000000 | 7.18
Boiler | Maintenance £/kW
Natural Gas | 3
Biomass | 15
CHP | Size kWe | Maintenance £/kWe | Size kWth | Maintenance £/kWth
Small | 500 | 80 | 2500 | 16
Large | 2000 | 48 | 10000 | 9.6

## Demand Data (hidden)
| Single Dwelling Heat and Hot water requirement/year (Kwh) | [8 empty] | Dist1 House | Single Dwelling Heat and Hot water requirement/year (Kwh) | [8 empty] | Dist2 House
| Age band | Flat |  | Terrace |  | Semi-Detatched |  | Detatched |  |  | Age band | Flat |  | Terrace |  | Semi-Detatched |  | Detatched
| Pre 1917 | 10581 | 0 | 16042 | 0 | 20476 | 0 | 30714 | 0 | 0 | Pre 1917 | 10581 | 0 | 16042 | 0 | 20476 | 0 | 30714 | 0 | 0
| 1918 - 1938 | 9755 | 0 | 14640 | 0 | 18652 | 0 | 27977 | 0 | 0 | 1918 - 1938 | 9755 | 0 | 14640 | 0 | 18652 | 0 | 27977 | 0 | 0
| 1939 - 1959 | 8994 | 0 | 13182 | 0 | 16688 | 0 | 25033 | 0 | 0 | 1939 - 1959 | 8994 | 0 | 13182 | 0 | 16688 | 0 | 25033 | 0 | 0
| 1960 - 1975 | 8653 | 0 | 12710 | 0 | 16065 | 0 | 24098 | 0 | 0 | 1960 - 1975 | 8653 | 0 | 12710 | 0 | 16065 | 0 | 24098 | 0 | 0
| 1976 - 1982 | 8101 | 0 | 11740 | 0 | 14749 | 0 | 22123 | 0 | 0 | 1976 - 1982 | 8101 | 0 | 11740 | 0 | 14749 | 0 | 22123 | 0 | 0
| 1983 - 1989 | 8331 | 0 | 11989 | 0 | 15072 | 0 | 22608 | 0 | 0 | 1983 - 1989 | 8331 | 0 | 11989 | 0 | 15072 | 0 | 22608 | 0 | 0
| 1990 - 1999 | 6828 | 0 | 9479 | 0 | 11728 | 0 | 17592 | 0 | 0 | 1990 - 1999 | 6828 | 0 | 9479 | 0 | 11728 | 0 | 17592 | 0 | 0
| Post 2000 | 6218 | 0 | 8371 | 0 | 10306 | 0 | 15459 | 0 | 0 | Post 2000 | 6218 | 0 | 8371 | 0 | 10306 | 0 | 15459 | 0 | 0
[10 empty] | 0 | [9 empty] | 0
Weather correction factors by region
| Region | Difference (%) | [8 empty] | Single Dwelling Heat and Hot water requirement/year (Kwh) | [8 empty] | Dist3 House
| Thames | 0.85 | [8 empty] | Age band | Flat |  | Terrace |  | Semi-Detatched |  | Detatched
| South East England | 1 | [8 empty] | Pre 1917 | 10581 | 0 | 16042 | 0 | 20476 | 0 | 30714 | 0 | 0
| Southern England | 0.95 | [8 empty] | 1918 - 1938 | 9755 | 0 | 14640 | 0 | 18652 | 0 | 27977 | 0 | 0
| South West England | 0.82 | [8 empty] | 1939 - 1959 | 8994 | 0 | 13182 | 0 | 16688 | 0 | 25033 | 0 | 0
| Severn | 0.88 | [8 empty] | 1960 - 1975 | 8653 | 0 | 12710 | 0 | 16065 | 0 | 24098 | 0 | 0
| Midlands | 1.03 | [8 empty] | 1976 - 1982 | 8101 | 0 | 11740 | 0 | 14749 | 0 | 22123 | 0 | 0
| West Pennines | 1.01 | [8 empty] | 1983 - 1989 | 8331 | 0 | 11989 | 0 | 15072 | 0 | 22608 | 0 | 0
| NW England / SW Scotland | 1.13 | [8 empty] | 1990 - 1999 | 6828 | 0 | 9479 | 0 | 11728 | 0 | 17592 | 0 | 0
| Borders | 1.12 | [8 empty] | Post 2000 | 6218 | 0 | 8371 | 0 | 10306 | 0 | 15459 | 0 | 0
| North East England | 1.11 | [17 empty] | 0
| East Pennines | 1.02
| East Anglia | 1.04
| West Scotland | 1.12
| East Scotland | 1.12
| North East England | 1.12
| Wales | 0.97
| Northern Ireland | 1.07 | [10 empty] | g/mmbtu | kg/mmbtu | kg/kWh
| North West Scotland | 1.12 | [9 empty] | ch4 | 7.2 | 0.072 | 0.00024548
[12 empty] | n2o | 3.6 | 0.036 | 0.00012274
http://www.cse.org.uk/thesource/download/assessing-the-heat-demand-of-a-whole-community-exercise-planlocal-80
https://www.gov.uk/government/uploads/system/uploads/attachment_data/file/379052/EED_regs_-_benchmark_heat_demand_paper_-_261114_.pdf
http://shrinkthatfootprint.com/how-much-heating-energy-do-you-use
| Other building heat and hot water requirement/year (Kwh/m2) |  | dist1 | dist2 | dist3
| Churches | 150 | 0 | 0 | 0
| Community Hall | 174 | 0 | 0 | 0
| Hospital | 410 | 0 | 0 | 0
| Library | 185 | 0 | 0 | 0
| Office | 175 | 0 | 0 | 0
| Retail | 190 | 0 | 0 | 0
| School | 160 | 0 | 0 | 0
| Sports Centre | 400 | 0 | 0 | 0
| Supermarket | 260 | 0 | 0 | 0
| Swimming pool centre | 1100 | 0 | 0 | 0
| University | 200 | 0 | 0 | 0
|  |  | 0 | 0 | 0