## Raw Data
[6 empty] | Years In Hours | [8 empty] | Aquabuoy Performance Matrix | [12 empty] | Aquabuoy Power Output | [5 empty] | A | [8 empty] | Pelamis Power Output
Spain - Bay Of Bicay | North of Gijon |  |  |  |  | 43800 | [21 empty] | Spain - Bay Of Bicay |  |  | North of Gijon | [11 empty] | Spain - Bay Of Bicay |  |  | North of Gijon
|  | Tp (s) | [12 empty] | Aquabuoy |  | Tp (s) | [10 empty] | Aquabuoy |  | Tp (s) | [12 empty] | Aquabuoy |  | Tp (s)
[17 empty] | <=1.0 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | >10 |  |  | <=1.0 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | >10 | Total (KWh/(5*Annum)) |  |  |  | <=1.0 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | >10 | Total (KWh/(5*Annum))
|  | Hs (m) | <=1.0 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | >10 | Total (Hours) | Hs (m) | <=0.5 | [11 empty] | Hs (m) | <=0.5 | [11 empty] | 0 |  | Hs (m) | <=0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | <=0.5 |  |  |  |  | 41.61 | [5 empty] | 41.61 |  | 1 | Tp (s) 6: 6; Tp (s) 7: 8; Tp (s) 8: 11; Tp (s) 9: 12; Tp (s) 10: 11; Tp (s) >10: 5 |  | 1 | [5 empty] | 4407.156 | 3486.48 | 8802.486 | 8851.104 | 7453.446 | 4224.51 | 37225.182 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 11113.155 | 28408.023 | 28028.496 | 24393.096 | 25769.511 | 52711.6356 | 170423.9166
|  |  | 1 |  |  | 32.85 | 241.776 | 734.526 | 435.81 | 800.226 | 737.592 | 677.586 | 844.902 | 4505.268 |  | 1.5 | Tp (s) 6: 13; Tp (s) 7: 17; Tp (s) 8: 25; Tp (s) 9: 26; Tp (s) 10: 26; Tp (s) >10: 15.2 |  | 1.5 | [5 empty] | 10556.676 | 9538.326 | 23881.95 | 45403.956 | 51769.848 | 56090.28 | 197241.036 |  |  | 1.5 | 0 | 0 | 0 | 0 | 25985.664 | 32261.985 | 75944.601 | 150182.316 | 160287.414 | 252775.275 | 453919.3728 | 1151356.6278
|  |  | 1.5 |  |  |  | 286.452 | 812.052 | 561.078 | 955.278 | 1746.306 | 1991.148 | 3690.15 | 10042.464 |  | 2 | Tp (s) 6: 24; Tp (s) 7: 30; Tp (s) 8: 44; Tp (s) 9: 47; Tp (s) 10: 47; Tp (s) >10: 27.6 |  | 2 | [5 empty] | 13108.464 | 18356.58 | 21681 | 29190.948 | 48685.89 | 160515.0864 | 291537.9684 |  |  | 2 | 0 | 0 | 0 | 0 | 31132.602 | 62106.429 | 69970.5 | 94715.31 | 147611.475 | 706615.326 | 731868.3036 | 1844019.9456
|  |  | 2 |  |  |  | 47.742 | 546.186 | 611.886 | 492.75 | 621.084 | 1035.87 | 5815.764 | 9171.282 |  | 2.5 | Tp (s) 6: 37; Tp (s) 7: 47; Tp (s) 8: 69; Tp (s) 9: 73; Tp (s) 10: 73; Tp (s) >10: 43.2 |  | 2.5 | [5 empty] | 4083.912 | 16983.45 | 30886.884 | 32037.948 | 32677.428 | 220417.7184 | 337087.3404 |  |  | 2.5 | 0 | 0 | 0 | 0 | 9823.464 | 57454.65 | 99151.374 | 104452.488 | 99822.828 | 969429.78 | 863900.25 | 2204034.834
|  |  | 2.5 |  |  |  | 3.066 | 110.376 | 361.35 | 447.636 | 438.876 | 447.636 | 5102.262 | 6911.202 |  | 3 | Tp (s) 6: 54; Tp (s) 7: 68; Tp (s) 8: 99; Tp (s) 9: 106; Tp (s) 10: 106; Tp (s) >10: 62 |  | 3 | [5 empty] | 165.564 | 11585.976 | 34559.514 | 22796.148 | 30085.344 | 226942.692 | 326135.238 |  |  | 3 | 0 | 0 | 0 | 0 | 395.514 | 39017.478 | 111183.891 | 72259.488 | 86140.584 | 926072.598 | 831016.305 | 2066085.858
|  |  | 3 |  |  |  |  | 3.066 | 170.382 | 349.086 | 215.058 | 283.824 | 3660.366 | 4681.782 |  | 3.5 | Tp (s) 6: 93; Tp (s) 7: 135; Tp (s) 8: 152; Tp (s) 9: 126; Tp (s) 10: 126; Tp (s) >10: 70 |  | 3.5 | [5 empty] | 285.138 | 3252.15 | 18574.704 | 18432.792 | 21799.26 | 169059.24 | 231403.284 |  |  | 3.5 | 0 | 0 | 0 | 0 | 0 | 7516.08 | 51996.951 | 63198.144 | 67560.405 | 830805.408 | 662695.4016 | 1683772.3896
|  |  | 3.5 |  |  |  |  | 3.066 | 24.09 | 122.202 | 146.292 | 173.01 | 2415.132 | 2883.792 |  | 4 | Tp (s) 6: 122; Tp (s) 7: 176; Tp (s) 8: 198; Tp (s) 9: 164; Tp (s) 10: 164; Tp (s) >10: 100 |  | 4 | [5 empty] | 0 | 0 | 4769.82 | 20041.128 | 15659.376 | 163286.4 | 203756.724 |  |  | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 12550.89 | 65744.676 | 46500.708 | 663759.216 | 538396.608 | 1326952.098
|  |  | 4 | [6 empty] | 24.09 | 122.202 | 95.484 | 1632.864 | 1874.64 |  | 4.5 | Tp (s) 6: 223; Tp (s) 7: 250; Tp (s) 8: 239; Tp (s) 9: 173; Tp (s) 10: 173; Tp (s) >10: 115 |  | 4.5 | [5 empty] | 0 | 0 | 0 | 5683.05 | 13411.998 | 124615.38 | 143710.428 |  |  | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20958.3 | 44654.976 | 542347.806 | 412761.6516 | 1020722.7336
|  |  | 4.5 | [7 empty] | 32.85 | 77.526 | 1083.612 | 1193.988 |  | 5 | Tp (s) 6: 250; Tp (s) 7: 250; Tp (s) 8: 250; Tp (s) 9: 214; Tp (s) 10: 214; Tp (s) >10: 142 |  | 5 | [5 empty] | 0 | 0 | 0 | 1874.64 | 5717.652 | 103431.948 | 111024.24 |  |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6298.44 | 18128.163 | 423925.308 | 312576.4224 | 760928.3334
|  |  | 5 | [7 empty] | 8.76 | 26.718 | 728.394 | 763.872 |  | >5 | Tp (s) 6: 250; Tp (s) 7: 250; Tp (s) 8: 250; Tp (s) 9: 250; Tp (s) 10: 250; Tp (s) >10: 172 |  | >5 | [5 empty] | 0 | 0 | 0 | 766.5 | 4489.5 | 293735.064 | 298992.064 |  |  | >5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2299.5 | 13468.5 | 1250423.3364 | 1055861.3744 | 2322053.7108
|  |  | >5 | [7 empty] | 3.066 | 17.958 | 1707.762 | 1729.786 | [14 empty] | Total | [11 empty] | 2178113.5048 |  |  | Total | [11 empty] | 14550350.4474
|  |  | Total | [10 empty] | 43799.686
[41 empty] | 435622.701 | KWh/Annum | [13 empty] | 2910070.0895 | KWh/Annum
[7 empty] | 0.2475 | [33 empty] | 435.6227 | MWh/Annum | [13 empty] | 2910.0701 | MWh/Annum
Spain - Canary Islands | North of Santa Cruz De Tenerife | [13 empty] | Pelamis Performance Matrix | [12 empty] | Spain - Canary Islands |  |  | North of Santa Cruz De Tenerife | [11 empty] | Spain - Canary Islands |  |  | North of Santa Cruz De Tenerife
|  | Tp (s) | [12 empty] | Pelamis |  | Tp (s) <=1.0: Tp (s) | Aquabuoy |  | Tp (s) | [12 empty] | Aquabuoy |  | Tp (s)
[17 empty] | <=1.0 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | >10 |  |  | <=1.0 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | >10 | Total (KWh/(5*Annum)) |  |  |  | <=1.0 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | >10 | Total (KWh/(5*Annum))
|  | Hs (m) | <=1.0 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | >10 | Total (Hours) | Hs (m) | <=0.5 | [11 empty] | Hs (m) | <=0.5 | [11 empty] | 0 |  | Hs (m) | <=0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | <=0.5 |  |  |  |  | 0 | 17.958 |  |  | 6.132 |  | 24.09 |  | 1 | Tp (s) 6: 25.5; Tp (s) 7: 35.5; Tp (s) 8: 38; Tp (s) 9: 36; Tp (s) 10: 30.5; Tp (s) >10: 11.7 |  | 1 | [5 empty] | 1395.468 | 2694.576 | 4394.016 | 3794.832 | 2163.282 | 1342.47 | 15784.644 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 8588.961 | 14180.688 | 12016.968 | 7079.832 | 8189.067 | 20592.0936 | 70647.6096
|  |  | 1 |  |  | 0 | 8.76 | 232.578 | 336.822 | 399.456 | 316.236 | 196.662 | 268.494 | 1760.008 |  | 1.5 |  |  |  |  | 32 | 57.5 | 79.5 | 86 | 80.5 | 68.5 | 45.2 |  | 1.5 | [5 empty] | 9884.784 | 28138.434 | 50775.15 | 59172.048 | 49936.38 | 50777.5152 | 248684.3112 |  |  | 1.5 | 0 | 0 | 0 | 0 | 24331.776 | 95174.115 | 161464.977 | 195722.928 | 154610.715 | 228832.881 | 543008.5728 | 1403145.9648
|  |  | 1.5 |  |  |  | 29.784 | 760.368 | 1655.202 | 2031.006 | 2275.848 | 1920.63 | 3340.626 | 12013.464 |  | 2 |  |  |  |  | 57 | 101.5 | 142 | 152.5 | 142.5 | 121.5 | 79.8 |  | 2 | [5 empty] | 4078.656 | 36056.16 | 125325.816 | 63651.912 | 68263.176 | 186046.632 | 483422.352 |  |  | 2 | 0 | 0 | 0 | 0 | 9686.808 | 121990.008 | 404460.588 | 206530.14 | 206968.14 | 819009.63 | 1100091.8376 | 2868737.1516
|  |  | 2 |  |  |  | 17.958 | 169.944 | 1201.872 | 2848.314 | 1354.296 | 1452.408 | 6740.82 | 13785.612 |  | 2.5 |  |  |  |  | 89 | 159 | 221.5 | 238 | 223 | 190 | 125 |  | 2.5 | [5 empty] | 664.446 | 8275.572 | 105565.446 | 90134.706 | 41790.018 | 216463.104 | 462893.292 |  |  | 2.5 | 0 | 0 | 0 | 0 | 1598.262 | 27996.084 | 338880.381 | 293863.836 | 127659.918 | 952036.8 | 1067734.5 | 2809769.781
|  |  | 2.5 |  |  |  | 0 | 17.958 | 176.076 | 1529.934 | 1234.722 | 572.466 | 5010.72 | 8541.876 |  | 3 |  |  |  |  | 129 | 229 | 318.5 | 336 | 303.5 | 253 | 177.5 |  | 3 | [5 empty] | 165.564 | 3246.456 | 22157.982 | 93598.848 | 51860.076 | 169018.944 | 340047.87 |  |  | 3 | 0 | 0 | 0 | 0 | 395.514 | 10932.918 | 71286.033 | 296690.688 | 148486.161 | 689706.336 | 776206.08 | 1993703.73
|  |  | 3 |  |  |  |  | 3.066 | 47.742 | 223.818 | 883.008 | 489.246 | 2726.112 | 4372.992 |  | 3.5 | Tp (s) 6: 312; Tp (s) 7: 425.5; Tp (s) 8: 432; Tp (s) 9: 390.5; Tp (s) 10: 344; Tp (s) >10: 229.8 |  | 3.5 | [5 empty] | 0 | 827.82 | 11317.92 | 28587.384 | 31567.536 | 104182.68 | 176483.34 |  |  | 3.5 | 0 | 0 | 0 | 0 | 0 | 1913.184 | 31682.73 | 98013.888 | 97834.308 | 511983.456 | 470248.0128 | 1211675.5788
|  |  | 3.5 |  |  |  |  | 0 | 6.132 | 74.46 | 226.884 | 250.536 | 1488.324 | 2046.336 |  | 4 | Tp (s) 6: 462; Tp (s) 7: 521; Tp (s) 8: 538; Tp (s) 9: 487; Tp (s) 10: 406.5; Tp (s) >10: 287.2 |  | 4 | [5 empty] | 0 | 0 | 1734.48 | 7326.864 | 16665.024 | 60531.6 | 86257.968 |  |  | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 4563.96 | 24035.688 | 49486.992 | 246060.954 | 218377.6896 | 542525.2836
|  |  | 4 | [6 empty] | 8.76 | 44.676 | 101.616 | 605.316 | 760.368 |  | 4.5 | Tp (s) 6: 544; Tp (s) 7: 628.5; Tp (s) 8: 638; Tp (s) 9: 576; Tp (s) 10: 500.5; Tp (s) >10: 345.7 |  | 4.5 | [5 empty] | 0 | 0 | 0 | 1060.836 | 2045.898 | 29819.04 | 32925.774 |  |  | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3912.216 | 6811.776 | 129777.648 | 95846.7078 | 236348.3478
|  |  | 4.5 | [7 empty] | 6.132 | 11.826 | 259.296 | 277.254 |  | 5 | Tp (s) 6: 0; Tp (s) 7: 732.5; Tp (s) 8: 719; Tp (s) 9: 678.5; Tp (s) 10: 582; Tp (s) >10: 409.2 |  | 5 | [5 empty] | 0 | 0 | 0 | 0 | 656.124 | 14429.472 | 15085.596 |  |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2080.281 | 59140.512 | 42835.8744 | 104056.6674
|  |  | 5 | [7 empty] | 0 | 3.066 | 101.616 | 104.682 |  | >5 | Tp (s) 6: 0; Tp (s) 7: 750; Tp (s) 8: 750; Tp (s) 9: 750; Tp (s) 10: 732.2; Tp (s) >10: 610.4 |  | >5 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 19512.024 | 19513.024 |  |  | >5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83062.2324 | 69244.9968 | 152308.2292
|  |  | >5 | [7 empty] | 0 | 0 | 113.442 | 113.442 | [14 empty] | Total | [11 empty] | 1881098.1712 |  |  | Total | [11 empty] | 11392918.3438
|  |  | Total | [10 empty] | 43800.124
[41 empty] | 376219.6342 | KWh/Annum | [13 empty] | 2278583.6688 | KWh/Annum
1385.484
[6 empty] | Years In Hours | [34 empty] | 376.2196 | MWh/Annum | [13 empty] | 2278.5837 | MWh/Annum
43800
France - Brest | East of Brest | [26 empty] | France - Brest |  |  | East of Brest | [11 empty] | France - Brest |  |  | East of Brest
|  | Tp (s) | [25 empty] | Aquabuoy |  | Tp (s) | [12 empty] | Aquabuoy |  | Tp (s)
[30 empty] | <=1.0 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | >10 | Total (KWh/(5*Annum)) |  |  |  | <=1.0 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | >10 | Total (KWh/(5*Annum))
|  | Hs (m) | <=1.0 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | >10 | Total (Hours) | [13 empty] | Hs (m) | <=0.5 | [11 empty] | 0 |  | Hs (m) | <=0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | <=0.5 |  |  | 3.066 | 8.76 | 44.676 | 23.652 |  |  | 11.826 | 14.892 | 106.872 | [14 empty] | 1 | Tp (s) 6: 2967.012; Tp (s) 7: 2645.52; Tp (s) 8: 5930.958; Tp (s) 9: 5397.912; Tp (s) 10: 3372.6; Tp (s) >10: 1132.23 | 21446.232 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 8432.595 | 19140.819 | 17093.388 | 11037.6 | 6906.603 | 30214.6416 | 92825.6466
|  |  | 1 |  |  | 17.958 | 217.248 | 494.502 | 330.69 | 539.178 | 449.826 | 306.6 | 226.446 | 2582.448 | [14 empty] | 1.5 | Tp (s) 6: 10186.566; Tp (s) 7: 12963.486; Tp (s) 8: 22786.95; Tp (s) 9: 43285.788; Tp (s) 10: 40894.308; Tp (s) >10: 29606.3472 | 159723.4452 |  |  | 1.5 | 0 | 0 | 0 | 0 | 25074.624 | 43847.085 | 72462.501 | 143176.068 | 126615.069 | 133423.341 | 354080.076 | 898678.764
|  |  | 1.5 |  |  | 3.066 | 187.464 | 783.582 | 762.558 | 911.478 | 1664.838 | 1572.858 | 1947.786 | 7833.63 | [14 empty] | 2 | Tp (s) 6: 12509.28; Tp (s) 7: 22876.74; Tp (s) 8: 30661.752; Tp (s) 9: 45083.34; Tp (s) 10: 57949.59; Tp (s) >10: 128491.8552 | 297572.5572 |  |  | 2 | 0 | 0 | 0 | 0 | 29709.54 | 77399.637 | 98953.836 | 146281.05 | 175698.225 | 565643.493 | 707122.0044 | 1800807.7854
|  |  | 2 |  |  |  | 32.85 | 521.22 | 762.558 | 696.858 | 959.22 | 1232.97 | 4655.502 | 8861.178 | [14 empty] | 2.5 | Tp (s) 6: 3630.144; Tp (s) 7: 28985.088; Tp (s) 8: 55699.146; Tp (s) 9: 48056.922; Tp (s) 10: 51957.75; Tp (s) >10: 173321.856 | 361650.906 |  |  | 2.5 | 0 | 0 | 0 | 0 | 8731.968 | 98055.936 | 178802.331 | 156678.732 | 158720.25 | 762295.2 | 863024.25 | 2226308.667
|  |  | 2.5 |  |  |  | 0 | 98.112 | 616.704 | 807.234 | 658.314 | 711.75 | 4012.08 | 6904.194 | [14 empty] | 3 | Tp (s) 6: 473.04; Tp (s) 7: 8518.224; Tp (s) 8: 58365.252; Tp (s) 9: 48610.116; Tp (s) 10: 53995.764; Tp (s) >10: 222516.264 | 392478.66 |  |  | 3 | 0 | 0 | 0 | 0 | 1130.04 | 28686.372 | 187771.038 | 154084.896 | 154601.079 | 908009.916 | 937293.72 | 2371577.061
|  |  | 3 |  |  |  |  | 8.76 | 125.268 | 589.548 | 458.586 | 509.394 | 3588.972 | 5280.528 | [14 empty] | 3.5 | Tp (s) 6: 0; Tp (s) 7: 2424.33; Tp (s) 8: 34885.824; Tp (s) 9: 37914.156; Tp (s) 10: 40176.864; Tp (s) >10: 192452.82 | 307853.994 |  |  | 3.5 | 0 | 0 | 0 | 0 | 0 | 5602.896 | 97657.356 | 129991.392 | 124516.392 | 945768.144 | 831086.8668 | 2134623.0468
|  |  | 3.5 |  |  |  |  | 0 | 17.958 | 229.512 | 300.906 | 318.864 | 2749.326 | 3616.566 | [14 empty] | 4 | Tp (s) 6: 0; Tp (s) 7: 0; Tp (s) 8: 13008.6; Tp (s) 9: 28804.632; Tp (s) 10: 32755.392; Tp (s) >10: 212649 | 287217.624 |  |  | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 34229.7 | 94493.244 | 97267.536 | 864418.185 | 737402.0832 | 1827810.7482
|  |  | 4 | [6 empty] | 65.7 | 175.638 | 199.728 | 2126.49 | 2567.556 | [14 empty] | 4.5 | Tp (s) 6: 0; Tp (s) 7: 0; Tp (s) 8: 3559.188; Tp (s) 9: 14397.06; Tp (s) 10: 27278.64; Tp (s) >10: 189088.98 | 234323.868 |  |  | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 9359.622 | 53094.36 | 90823.68 | 822948.126 | 656845.2108 | 1633070.9988
|  |  | 4.5 | [6 empty] | 14.892 | 83.22 | 157.68 | 1644.252 | 1900.044 | [14 empty] | 5 | Tp (s) 6: 0; Tp (s) 7: 0; Tp (s) 8: 766.5; Tp (s) 9: 3843.012; Tp (s) 10: 16590.564; Tp (s) >10: 166623.084 | 187823.16 |  |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 2245.845 | 12911.802 | 52601.391 | 682919.964 | 520482.7584 | 1271161.7604
|  |  | 5 | [6 empty] | 3.066 | 17.958 | 77.526 | 1173.402 | 1271.952 | [14 empty] | >5 | Tp (s) 6: 0; Tp (s) 7: 0; Tp (s) 8: 0; Tp (s) 9: 1533; Tp (s) 10: 11935.5; Tp (s) >10: 485163.84 | 498633.34 |  |  | >5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4599 | 35806.5 | 2065331.184 | 1754652.1776 | 3860389.8616
|  |  | >5 | [7 empty] | 6.132 | 47.742 | 2820.72 | 2874.594 | [14 empty] | Total | [11 empty] | 2748723.7864 |  |  | Total | [11 empty] | 18117254.3398
|  |  | Total | [10 empty] | 43799.562
[41 empty] | 549744.7573 | KWh/Annum | [13 empty] | 3623450.868 | KWh/Annum
[6 empty] | Years In Hours | [34 empty] | 549.7448 | MWh/Annum | [13 empty] | 3623.4509 | MWh/Annum
43800
Scotland - Tiree | East of Tiree | [26 empty] | Scotland - Tiree |  | Tp (s) 2: East of Tiree |  |  | Scotland - Tiree |  |  | East of Tiree
|  | Tp (s) | [25 empty] | Aquabuoy |  | Tp (s) <=1.0: Tp (s) |  |  | Aquabuoy |  | Tp (s)
[30 empty] | <=1.0 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | >10 | Total (KWh/(5*Annum)) |  |  |  | <=1.0 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | >10 | Total (KWh/(5*Annum))
|  | Hs (m) | <=1.0 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | >10 | Total (Hours) | [13 empty] | Hs (m) | <=0.5 | [11 empty] | 0 |  | Hs (m) | <=0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | <=0.5 |  |  | 11.826 | 3.066 | 3.066 | 83.22 | 110.376 | 92.418 | 44.676 | 32.85 | 381.498 | [14 empty] | 1 | Tp (s) 6: 1429.632; Tp (s) 7: 2477.328; Tp (s) 8: 9077.112; Tp (s) 9: 14406.696; Tp (s) 10: 11958.276; Tp (s) >10: 4498.26 | 43847.304 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 7896.483 | 29294.316 | 45621.204 | 39136.176 | 27439.386 | 58758.6636 | 208146.2286
|  |  | 1 |  |  | 104.244 | 357.408 | 238.272 | 309.666 | 825.192 | 1200.558 | 1087.116 | 899.652 | 5022.108 | [14 empty] | 1.5 | Tp (s) 6: 8324.628; Tp (s) 7: 4914.36; Tp (s) 8: 15045.3; Tp (s) 9: 36396.048; Tp (s) 10: 48865.908; Tp (s) >10: 36443.7024 | 149989.9464 |  |  | 1.5 | 0 | 0 | 0 | 0 | 20491.392 | 16622.1 | 47844.054 | 120386.928 | 151296.369 | 164236.422 | 346347.8024 | 867225.0674
|  |  | 1.5 |  |  | 18.396 | 438 | 640.356 | 289.08 | 601.812 | 1399.848 | 1879.458 | 2397.612 | 7662.562 | [14 empty] | 2 | Tp (s) 6: 19657.44; Tp (s) 7: 13665.6; Tp (s) 8: 14030.016; Tp (s) 9: 29108.604; Tp (s) 10: 43951.11; Tp (s) >10: 93639.8448 | 214052.6148 |  |  | 2 | 0 | 0 | 0 | 0 | 46686.42 | 46235.28 | 45278.688 | 94448.13 | 133256.025 | 412218.882 | 528829.812 | 1306953.237
|  |  | 2 |  |  |  | 86.286 | 819.06 | 455.52 | 318.864 | 619.332 | 935.13 | 3392.748 | 6626.94 | [14 empty] | 2.5 | Tp (s) 6: 9804.63; Tp (s) 7: 34152.174; Tp (s) 8: 22606.056; Tp (s) 9: 25866.966; Tp (s) 10: 38049.06; Tp (s) >10: 140379.3504 | 270858.2364 |  |  | 2.5 | 0 | 0 | 0 | 0 | 23584.11 | 115536.078 | 72568.716 | 84333.396 | 116232.06 | 617409.18 | 682020.75 | 1711684.29
|  |  | 2.5 |  |  |  | 11.826 | 264.99 | 726.642 | 327.624 | 354.342 | 521.22 | 3249.522 | 5456.166 | [14 empty] | 3 | Tp (s) 6: 1277.208; Tp (s) 7: 24720.72; Tp (s) 8: 33605.55; Tp (s) 9: 30317.484; Tp (s) 10: 42620.904; Tp (s) >10: 192617.508 | 325159.374 |  |  | 3 | 0 | 0 | 0 | 0 | 3051.108 | 83250.66 | 108114.825 | 96100.704 | 122032.494 | 786003.702 | 804116.535 | 2002670.028
|  |  | 3 |  |  |  | 8.76 | 23.652 | 363.54 | 339.45 | 286.014 | 402.084 | 3106.734 | 4530.234 | [14 empty] | 3.5 | Tp (s) 6: 570.276; Tp (s) 7: 14486.85; Tp (s) 8: 58853.184; Tp (s) 9: 33775.056; Tp (s) 10: 37914.156; Tp (s) >10: 179728.92 | 325328.442 |  |  | 3.5 | 0 | 0 | 0 | 0 | 0 | 33480.72 | 164750.196 | 115800.192 | 117503.793 | 883239.264 | 836522.0964 | 2151296.2614
|  |  | 3.5 |  |  |  | 3.066 | 6.132 | 107.31 | 387.192 | 268.056 | 300.906 | 2567.556 | 3640.218 | [14 empty] | 4 | Tp (s) 6: 0; Tp (s) 7: 4702.368; Tp (s) 8: 45963.72; Tp (s) 9: 30313.104; Tp (s) 10: 35197.68; Tp (s) >10: 221321.4 | 337498.272 |  |  | 4 | 0 | 0 | 0 | 0 | 0 | 12343.716 | 120944.94 | 99441.768 | 104519.94 | 899671.491 | 824702.8416 | 2061624.6966
|  |  | 4 | [5 empty] | 26.718 | 232.14 | 184.836 | 214.62 | 2213.214 | 2871.528 | [14 empty] | 4.5 | Tp (s) 6: 683.718; Tp (s) 7: 0; Tp (s) 8: 13503.978; Tp (s) 9: 21671.364; Tp (s) 10: 23717.262; Tp (s) >10: 206567.37 | 266143.692 |  |  | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 35511.507 | 79920.984 | 78966.144 | 899017.119 | 732250.6776 | 1825666.4316
|  |  | 4.5 |  |  |  |  | 3.066 |  | 56.502 | 125.268 | 137.094 | 1796.238 | 2118.168 | [14 empty] | 5 | Tp (s) 6: 0; Tp (s) 7: 766.5; Tp (s) 8: 5256; Tp (s) 9: 33181.128; Tp (s) 10: 18465.204; Tp (s) >10: 166249.908 | 223918.74 |  |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 15400.08 | 111482.388 | 58545.051 | 681390.468 | 587693.8584 | 1454511.8454
|  |  | 5 | [5 empty] | 3.066 | 21.024 | 155.052 | 86.286 | 1170.774 | 1436.202 | [14 empty] | >5 | Tp (s) 6: 0; Tp (s) 7: 0; Tp (s) 8: 1533; Tp (s) 9: 13359; Tp (s) 10: 37996.5; Tp (s) >10: 660922.728 | 713812.228 |  |  | >5 | 0 | 0 | 0 | 0 | 0 | 0 | 4599 | 40077 | 113989.5 | 2813532.6828 | 2474639.7312 | 5446838.914
|  |  | >5 | [6 empty] | 6.132 | 53.436 | 151.986 | 3842.574 | 4054.128 | [14 empty] | Total | [11 empty] | 2870608.8496 |  |  | Total | [11 empty] | 19036617
|  |  | Total | [10 empty] | 43799.752
[41 empty] | 574121.7699 | KWh/Annum | [13 empty] | 3807323.4 | KWh/Annum
[41 empty] | 574.1218 | MWh/Annum | [13 empty] | 3807.3234 | MWh/Annum
Years In Hours
Scotland - North Uist | Southeast of Uist |  |  |  |  | 43800
[28 empty] | Scotland - North Uist |  | Tp (s) 2: Southeast of Uist |  |  | Scotland - North Uist |  |  | Southeast of Uist
|  | Tp (s) | [25 empty] | Aquabuoy |  | Tp (s) <=1.0: Tp (s) |  |  | Aquabuoy |  | Tp (s)
[30 empty] | <=1.0 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | >10 | Total (KWh/(5*Annum)) |  |  |  | <=1.0 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | >10 | Total (KWh/(5*Annum))
|  | Hs (m) | <=1.0 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | >10 | Total (Hours) | [13 empty] | Hs (m) | <=0.5 | [11 empty] | 0 |  | Hs (m) | <=0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | <=0.5 | [5 empty] | 14.892 | 0 | 0 | 0 | 0 | 14.892 | [14 empty] | 1 | Tp (s) 6: 1109.016; Tp (s) 7: 4264.368; Tp (s) 8: 7959.336; Tp (s) 9: 7579.152; Tp (s) 10: 3998.94; Tp (s) >10: 2054.22 | 26965.032 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 13592.673 | 25686.948 | 24000.648 | 13087.44 | 12530.742 | 33909.4782 | 122807.9292
|  |  | 1 |  |  |  | 50.808 | 184.836 | 533.046 | 723.576 | 631.596 | 363.54 | 410.844 | 2898.246 | [14 empty] | 1.5 | Tp (s) 6: 4532.424; Tp (s) 7: 7446; Tp (s) 8: 26586.6; Tp (s) 9: 49640.292; Tp (s) 10: 41122.068; Tp (s) >10: 21144.5376 | 150471.9216 |  |  | 1.5 | 0 | 0 | 0 | 0 | 11156.736 | 25185 | 84545.388 | 164194.812 | 127320.249 | 95289.528 | 309371.4904 | 817063.2034
|  |  | 1.5 |  |  | 3.066 | 110.376 | 348.648 | 438 | 1063.464 | 1909.242 | 1581.618 | 1391.088 | 6844.502 | [14 empty] | 2 | Tp (s) 6: 6359.76; Tp (s) 7: 18133.2; Tp (s) 8: 26730.264; Tp (s) 9: 52350.198; Tp (s) 10: 80079.54; Tp (s) >10: 69305.0904 | 252958.0524 |  |  | 2 | 0 | 0 | 0 | 0 | 15104.43 | 61350.66 | 86265.852 | 169859.685 | 242794.35 | 305093.061 | 543789.4392 | 1424257.4772
|  |  | 2 |  |  |  | 8.76 | 264.99 | 604.44 | 607.506 | 1113.834 | 1703.82 | 2511.054 | 6814.404 | [14 empty] | 2.5 | Tp (s) 6: 1879.896; Tp (s) 7: 20586; Tp (s) 8: 31037.994; Tp (s) 9: 49783.518; Tp (s) 10: 75234.822; Tp (s) >10: 134721.792 | 313244.022 |  |  | 2.5 | 0 | 0 | 0 | 0 | 4521.912 | 69642 | 99636.459 | 162307.908 | 229826.922 | 592526.4 | 721221.75 | 1879683.351
|  |  | 2.5 |  |  |  |  | 50.808 | 438 | 449.826 | 681.966 | 1030.614 | 3118.56 | 5769.774 | [14 empty] | 3 | Tp (s) 6: 331.128; Tp (s) 7: 6880.104; Tp (s) 8: 40413.384; Tp (s) 9: 58081.428; Tp (s) 10: 69131.292; Tp (s) >10: 193350.72 | 368188.056 |  |  | 3 | 0 | 0 | 0 | 0 | 791.028 | 23169.762 | 130016.796 | 184107.168 | 197937.237 | 788995.68 | 858071.565 | 2183089.236
|  |  | 3 |  |  |  |  | 6.132 | 101.178 | 408.216 | 547.938 | 652.182 | 3118.56 | 4834.206 | [14 empty] | 3.5 | Tp (s) 6: 0; Tp (s) 7: 3606.93; Tp (s) 8: 28095.072; Tp (s) 9: 55905.444; Tp (s) 10: 61920.936; Tp (s) >10: 196837.2 | 346365.582 |  |  | 3.5 | 0 | 0 | 0 | 0 | 0 | 8336.016 | 78647.718 | 191675.808 | 191905.758 | 967314.24 | 909696.3912 | 2347575.9312
|  |  | 3.5 |  |  |  |  | 0 | 26.718 | 184.836 | 443.694 | 491.436 | 2811.96 | 3958.644 | [14 empty] | 4 | Tp (s) 6: 0; Tp (s) 7: 539.616; Tp (s) 8: 14743.08; Tp (s) 9: 31749.744; Tp (s) 10: 59117.736; Tp (s) >10: 251981.4 | 358131.576 |  |  | 4 | 0 | 0 | 0 | 0 | 0 | 1416.492 | 38793.66 | 104154.648 | 175550.838 | 1024304.391 | 905084.952 | 2249304.981
|  |  | 4 |  |  |  |  | 0 | 3.066 | 74.46 | 193.596 | 360.474 | 2519.814 | 3151.41 | [14 empty] | 4.5 | Tp (s) 6: 0; Tp (s) 7: 766.5; Tp (s) 8: 2093.64; Tp (s) 9: 18034.212; Tp (s) 10: 49480.422; Tp (s) >10: 235681.23 | 306056.004 |  |  | 4.5 | 0 | 0 | 0 | 0 | 0 | 1667.904 | 5505.66 | 66507.672 | 164744.064 | 1025725.701 | 847478.7102 | 2111629.7112
|  |  | 4.5 |  |  |  |  | 0 | 3.066 | 8.76 | 104.244 | 286.014 | 2049.402 | 2451.486 | [14 empty] | 5 | Tp (s) 6: 0; Tp (s) 7: 0; Tp (s) 8: 0; Tp (s) 9: 7686.024; Tp (s) 10: 35711.892; Tp (s) >10: 246171.768 | 289569.684 |  |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25823.604 | 113226.723 | 1008957.528 | 792374.0616 | 1940381.9166
|  |  | 5 | [5 empty] | 0 | 0 | 35.916 | 166.878 | 1733.604 | 1936.398 | [14 empty] | >5 | Tp (s) 6: 0; Tp (s) 7: 0; Tp (s) 8: 766.5; Tp (s) 9: 2190; Tp (s) 10: 16425; Tp (s) >10: 868398.072 | 887780.572 |  |  | >5 | 0 | 0 | 0 | 0 | 0 | 0 | 2299.5 | 6570 | 49275 | 3696750.3972 | 3129125.2608 | 6884021.158
|  |  | >5 | [5 empty] | 0 | 3.066 | 8.76 | 65.7 | 5048.826 | 5126.352 | [14 empty] | Total | [11 empty] | 3299730.502 |  |  | Total | [11 empty] | 21959814.8948
|  |  | Total | [10 empty] | 43800.314
[41 empty] | 659946.1004 | KWh/Annum | [13 empty] | 4391962.979 | KWh/Annum
[41 empty] | 659.9461 | MWh/Annum | [13 empty] | 4391.963 | MWh/Annum

## Calculated Data
Wave Resources Data Sheet
Theoretical Power Check
Wave Site Power Curves
Power (kW) | Hz | Te | f=1/T | w=(2*pi)/T
0 | 0 | 1 | 1 | 6.2832
0.2453 | 0.5 | 2 | 0.5 | 3.1416
1.4718 | 1 | 3 | 0.33333 | 2.0944 |  |  |  |  | Power | 35.3236 | kW/m | Hmo = 3 | Te=8
4.4154 | 1.5 | 4 | 0.25 | 1.5708
9.8121 | 2 | 5 | 0.2 | 1.2566 |  |  |  |  | Average Power From Point Absorber | 37820.3364
18.3977 | 2.5 | 6 | 0.16667 | 1.0472 | [5 empty] | 37.8203 | KW/m
30.9081 | 3 | 7 | 0.14286 | 0.8976
48.0793 | 3.5 | 8 | 0.125 | 0.7854 |  |  |  |  | Average Power From Attenuator | 129831.6096
70.6471 | 4 | 9 | 0.11111 | 0.69813 | [5 empty] | 129.8316 | kW/m
99.3475 | 4.5 | 10 | 0.1 | 0.62832
134.9164 | 5 | 11 | 0.090909 | 0.5712 |  |  |  |  | Point Absorber | 659.9461 | MWh/Annum
178.0896 | 5.5 | 12 | 0.083333 | 0.5236 |  |  |  |  | Point Absorber | 574.1218 | MWh/Annum
229.6032 | 6 | 13 | 0.076923 | 0.48332 |  |  |  | 0 | Point Absorber | 376.2196 | MWh/Annum
290.1929 | 6.5 | 14 | 0.071429 | 0.4488
360.5947 | 7 | 15 | 0.066667 | 0.41888 |  |  |  |  | Point Absorber | 659.9461 | MWh/Annum
441.5446 | 7.5 | 16 | 0.0625 | 0.3927 |  |  |  |  | Attenuator | 4391.963 | MWh/Annum
533.7783 | 8 | 17 | 0.058824 | 0.3696
638.0319 | 8.5 | 18 | 0.055556 | 0.34907 |  |  |  |  | Point Absorber | 574.1218 | MWh/Annum
755.0412 | 9 | 19 | 0.052632 | 0.33069 |  |  |  |  | Attenuator | 3807.3234 | MWh/Annum
885.5422 | 9.5 | 20 | 0.05 | 0.31416
1030.2707 | 10 | 21 | 0.047619 | 0.2992 |  |  |  |  | Point Absorber | 376.2196 | MWh/Annum
1189.9626 | 10.5 | 22 | 0.045455 | 0.2856 |  |  |  |  | Attenuator | 2278.5837 | MWh/Annum
1365.3539 | 11 | 23 | 0.043478 | 0.27318
1557.1805 | 11.5 | 24 | 0.041667 | 0.2618 |  |  |  |  | Attenuator | 4391.963 | MWh/Annum
1766.1783 | 12 | 25 | 0.04 | 0.25133 |  |  |  |  | Attenuator | 3807.3234 | MWh/Annum
[9 empty] | Attenuator | 2278.5837 | MWh/Annum
Point Absorber |  |  |  |  | Attunuator
Float Diameter | 7 | meters | Water Density | 1.0025 | Overall Length | 150 | m |  | System Voltage | 415/690Vac 50/60Hz | 3-phase |  |  | Point Absorber With Power Limiter (250kW) |  |  |  |  | Attunuator With P-Limite (750kW) |  |  | Point Absorber With Power Limiter (250kW) | Attunuator With P-Limite (750kW)
Float Height | 4.8 | meters | gravity | 9.81 | Diameter | 3.5 | m |  | Transformer | 950 | 0
Displaced Volume | 185 | m^3 | i | 1 | Displacement | 700 | tones |  | Depth | 50 | m |  |  | Power Curves @ Te 1 |  |  |  |  | Power Curve @ Te 1
Accelerator Tube Diameter | 4.65 | meter |  |  | Nose | 5 | m |  | Current | 1 | knot |  |  | Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW)
Accelerator Tube Length | 30 | meter |  |  | Power Take off Units | 3 |  |  | Mooring System | compliant | slack moored |  |  | 0 | 0 | 435.2386 | -0.2898 | 42.8402 | 0 | 0 | Hz
Rated Absorbed Power | 273 | kW |  |  | Power Take off | 4 | (2 heave, 2 sway |  | Equivalent Gas Turbine - Fuel | 600 | tonnes/year |  |  | 2.4586 | 82.61 | 517.8487 | -0.3448 | 60.646 | 1.965e-08 | 0.5 | Hz
Significant Wave Height (At Rated Power) | 5 | meter |  |  | Power Smoothing/Storage | 0.1 | m/s |  | EGT - CO2 Emissions | 2000 | tonnes/year |  |  | 4.9173 | 165.22 | 600.4587 | -0.39981 | 81.5386 | 7.86e-08 | 1 | Hz
Average Wave Period (At Rated Power) | 7.5 | seconds |  |  | Working Pressure | 275 | bar | [6 empty] | 7.3759 | 247.83 | 683.0687 | -0.45481 | 105.5178 | 1.768e-07 | 1.5 | Hz
Waterplane Area | 33.6 | m^2 |  |  | Power Conversion | 2 | [7 empty] | 9.8345 | 330.44 | 765.6787 | -0.50982 | 132.5836 | 3.144e-07 | 2 | Hz
Float Draft hf | 8 | meters |  |  | Generator | 2 | 157kVa/125kW | [6 empty] | 12.2932 | 413.05 | 848.2887 | -0.56482 | 162.7362 | 4.912e-07 | 2.5 | Hz
Heave Stiffness (k) | 330.44 |  |  |  | Speed | 1500 | rpm | [6 empty] | 14.7518 | 495.6601 | 930.8987 | -0.61982 | 195.9754 | 7.074e-07 | 3 | Hz
Structeral Mass (Ms) | 33.684 |  |  |  | Overall Power Rating | 750 | kW | [6 empty] | 17.2104 | 578.2701 | 1013.5087 | -0.67483 | 232.3014 | 9.628e-07 | 3.5 | Hz
Added Mass (Ma) | 16.842 |  |  |  | Annual Output | 2.7 | GWh | [6 empty] | 19.669 | 660.8801 | 1096.1187 | -0.72983 | 250 | 1.258e-06 | 4 | Hz
Damping Ratio (ζ) | 0.1 |  |  |  | Nominal Wave Power | 55 | kW/m | [6 empty] | 22.1277 | 743.4901 | 1178.7287 | -0.78484 | 250 | 1.592e-06 | 4.5 | Hz
c | 25.8425 |  |  |  | Hydrostatic Power Limiting | 6.5 | m | [6 empty] | 24.5863 | 826.1001 | 1261.3387 | -0.83984 | 250 | 1.965e-06 | 5 | Hz
[5 empty] | Generator type |  | Asynchronous | [6 empty] | 27.0449 | 908.7101 | 1343.9488 | -0.89485 | 250 | 2.378e-06 | 5.5 | Hz
[14 empty] | 29.5036 | 991.3201 | 1426.5588 | -0.94985 | 250 | 2.829e-06 | 6 | Hz
[14 empty] | 31.9622 | 1073.9301 | 1509.1688 | -1.0049 | 250 | 3.321e-06 | 6.5 | Hz
Power Curves @ Te 1 |  |  |  |  | Power Curve @ Te 1 | [8 empty] | 34.4208 | 1156.5401 | 1591.7788 | -1.0599 | 250 | 3.851e-06 | 7 | Hz
Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW) | [8 empty] | 36.8795 | 1239.1502 | 1674.3888 | -1.1149 | 250 | 4.421e-06 | 7.5 | Hz
0 | 0 | 435.2386 | -0.2898 | 42.8402 | 0 | [8 empty] | 39.3381 | 1321.7602 | 1756.9988 | -1.1699 | 250 | 5.03e-06 | 8 | Hz
2.4586 | 82.61 | 517.8487 | -0.3448 | 60.646 | 1.965e-08 | [8 empty] | 41.7967 | 1404.3702 | 1839.6088 | -1.2249 | 250 | 5.679e-06 | 8.5 | Hz
4.9173 | 165.22 | 600.4587 | -0.39981 | 81.5386 | 7.86e-08 | [8 empty] | 44.2554 | 1486.9802 | 1922.2188 | -1.2799 | 250 | 6.366e-06 | 9 | Hz
7.3759 | 247.83 | 683.0687 | -0.45481 | 105.5178 | 1.768e-07 | [8 empty] | 46.714 | 1569.5902 | 2004.8288 | -1.3349 | 250 | 7.093e-06 | 9.5 | Hz
9.8345 | 330.44 | 765.6787 | -0.50982 | 132.5836 | 3.144e-07 | [8 empty] | 49.1726 | 1652.2002 | 2087.4388 | -1.3899 | 250 | 7.86e-06 | 10 | Hz
12.2932 | 413.05 | 848.2887 | -0.56482 | 162.7362 | 4.912e-07 | [8 empty] | 51.6313 | 1734.8102 | 2170.0489 | -1.4449 | 250 | 8.665e-06 | 10.5 | Hz
14.7518 | 495.6601 | 930.8987 | -0.61982 | 195.9754 | 7.074e-07 | [8 empty] | 54.0899 | 1817.4202 | 2252.6589 | -1.4999 | 250 | 9.51e-06 | 11 | Hz
17.2104 | 578.2701 | 1013.5087 | -0.67483 | 232.3014 | 9.628e-07 | [8 empty] | 56.5485 | 1900.0302 | 2335.2689 | -1.5549 | 250 | 1.039e-05 | 11.5 | Hz
19.669 | 660.8801 | 1096.1187 | -0.72983 | 271.714 | 1.258e-06 | [8 empty] | 59.0071 | 1982.6402 | 2417.8789 | -1.6099 | 250 | 1.132e-05 | 12 | Hz
22.1277 | 743.4901 | 1178.7287 | -0.78484 | 314.2133 | 1.592e-06
24.5863 | 826.1001 | 1261.3387 | -0.83984 | 359.7993 | 1.965e-06
27.0449 | 908.7101 | 1343.9488 | -0.89485 | 408.4719 | 2.378e-06 | 5.5 | Hz | [6 empty] | Power Curves @ Te 2 |  |  |  |  | Power Curve @ Te 2
29.5036 | 991.3201 | 1426.5588 | -0.94985 | 460.2313 | 2.829e-06 | [8 empty] | Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW)
31.9622 | 1073.9301 | 1509.1688 | -1.0049 | 515.0773 | 3.321e-06 | [8 empty] | 0 | 0 | 435.2386 | -5.0001 | 250 | 0 | 0 | Hz
34.4208 | 1156.5401 | 1591.7788 | -1.0599 | 573.01 | 3.851e-06 | [8 empty] | 2.4586 | 82.61 | 517.8487 | -5.9492 | 250 | 0.009 | 0.5 | Hz
36.8795 | 1239.1502 | 1674.3888 | -1.1149 | 634.0294 | 4.421e-06 | [8 empty] | 4.9173 | 165.22 | 600.4587 | -6.8982 | 250 | 0.035 | 1 | Hz
39.3381 | 1321.7602 | 1756.9988 | -1.1699 | 698.1355 | 5.03e-06 | [8 empty] | 7.3759 | 247.83 | 683.0687 | -7.8473 | 250 | 0.078 | 1.5 | Hz
41.7967 | 1404.3702 | 1839.6088 | -1.2249 | 765.3283 | 5.679e-06 | [8 empty] | 9.8345 | 330.44 | 765.6787 | -8.7963 | 250 | 0.139 | 2 | Hz
44.2554 | 1486.9802 | 1922.2188 | -1.2799 | 835.6077 | 6.366e-06 | [8 empty] | 12.2932 | 413.05 | 848.2887 | -9.7454 | 250 | 0.217 | 2.5 | Hz
46.714 | 1569.5902 | 2004.8288 | -1.3349 | 908.9739 | 7.093e-06 | [8 empty] | 14.7518 | 495.6601 | 930.8987 | -10.6944 | 250 | 0.313 | 3 | Hz
49.1726 | 1652.2002 | 2087.4388 | -1.3899 | 985.4267 | 7.86e-06 | [8 empty] | 17.2104 | 578.2701 | 1013.5087 | -11.6435 | 250 | 0.425 | 3.5 | Hz
51.6313 | 1734.8102 | 2170.0489 | -1.4449 | 1064.9662 | 8.665e-06 | [8 empty] | 19.669 | 660.8801 | 1096.1187 | -12.5925 | 250 | 0.556 | 4 | Hz
54.0899 | 1817.4202 | 2252.6589 | -1.4999 | 1147.5924 | 9.51e-06 | [8 empty] | 22.1277 | 743.4901 | 1178.7287 | -13.5416 | 250 | 0.703 | 4.5 | Hz
56.5485 | 1900.0302 | 2335.2689 | -1.5549 | 1233.3052 | 1.039e-05 | [8 empty] | 24.5863 | 826.1001 | 1261.3387 | -14.4906 | 250 | 0.868 | 5 | Hz
59.0071 | 1982.6402 | 2417.8789 | -1.6099 | 1322.1048 | 1.132e-05 | [8 empty] | 27.0449 | 908.7101 | 1343.9488 | -15.4397 | 250 | 1.051 | 5.5 | Hz
0 | 0 | 435.2386 | -0.2898 | 42.8402 | [9 empty] | 29.5036 | 991.3201 | 1426.5588 | -16.3887 | 250 | 1.25 | 6 | Hz
[14 empty] | 31.9622 | 1073.9301 | 1509.1688 | -17.3378 | 250 | 1.467 | 6.5 | Hz
Power Curves @ Te 2 |  |  |  |  | Power Curve @ Te 2 | [8 empty] | 34.4208 | 1156.5401 | 1591.7788 | -18.2868 | 250 | 1.702 | 7 | Hz
Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW) | [8 empty] | 36.8795 | 1239.1502 | 1674.3888 | -19.2359 | 250 | 1.954 | 7.5 | Hz
0 | 0 | 435.2386 | -5.0001 | 3188.3762 | 0 |  | Hz | [6 empty] | 39.3381 | 1321.7602 | 1756.9988 | -20.1849 | 250 | 2.223 | 8 | Hz
2.4586 | 82.61 | 517.8487 | -5.9492 | 4513.572 | 0.009 |  | Hz | [6 empty] | 41.7967 | 1404.3702 | 1839.6088 | -21.134 | 250 | 2.509 | 8.5 | Hz
4.9173 | 165.22 | 600.4587 | -6.8982 | 6068.4936 | 0.035 |  | Hz | [6 empty] | 44.2554 | 1486.9802 | 1922.2188 | -22.083 | 250 | 2.813 | 9 | Hz
7.3759 | 247.83 | 683.0687 | -7.8473 | 7853.1412 | 0.078 |  | Hz | [6 empty] | 46.714 | 1569.5902 | 2004.8288 | -23.0321 | 250 | 3.135 | 9.5 | Hz
9.8345 | 330.44 | 765.6787 | -8.7963 | 9867.5147 | 0.139 |  | Hz | [6 empty] | 49.1726 | 1652.2002 | 2087.4388 | -23.9811 | 250 | 3.473 | 10 | Hz
12.2932 | 413.05 | 848.2887 | -9.7454 | 12111.6141 | 0.217 |  | Hz | [6 empty] | 51.6313 | 1734.8102 | 2170.0489 | -24.9302 | 250 | 3.829 | 10.5 | Hz
14.7518 | 495.6601 | 930.8987 | -10.6944 | 14585.4394 | 0.313 |  | Hz | [6 empty] | 54.0899 | 1817.4202 | 2252.6589 | -25.8792 | 250 | 4.203 | 11 | Hz
17.2104 | 578.2701 | 1013.5087 | -11.6435 | 17288.9907 | 0.425 |  | Hz | [6 empty] | 56.5485 | 1900.0302 | 2335.2689 | -26.8283 | 250 | 4.593 | 11.5 | Hz
19.669 | 660.8801 | 1096.1187 | -12.5925 | 20222.2679 | 0.556 |  | Hz | [6 empty] | 59.0071 | 1982.6402 | 2417.8789 | -27.7773 | 250 | 5.002 | 12 | Hz
22.1277 | 743.4901 | 1178.7287 | -13.5416 | 23385.271 | 0.703 |  | Hz
24.5863 | 826.1001 | 1261.3387 | -14.4906 | 26778 | 0.868 |  | Hz
27.0449 | 908.7101 | 1343.9488 | -15.4397 | 30400.455 | 1.051 | 5.5 | Hz | [6 empty] | Power Curves @ Te 3 |  |  |  |  | Power Curve @ Te 3
29.5036 | 991.3201 | 1426.5588 | -16.3887 | 34252.6359 | 1.25 |  | Hz | [6 empty] | Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW)
31.9622 | 1073.9301 | 1509.1688 | -17.3378 | 38334.5427 | 1.467 |  | Hz | [6 empty] | 0 | 0 | 435.2386 | 2.6713 | 250 | 0 | 0 | Hz
34.4208 | 1156.5401 | 1591.7788 | -18.2868 | 42646.1754 | 1.702 |  | Hz | [6 empty] | 2.4586 | 82.61 | 517.8487 | 3.1783 | 250 | 0.125 | 0.5 | Hz
36.8795 | 1239.1502 | 1674.3888 | -19.2359 | 47187.5341 | 1.954 |  | Hz | [6 empty] | 4.9173 | 165.22 | 600.4587 | 3.6853 | 250 | 0.499 | 1 | Hz
39.3381 | 1321.7602 | 1756.9988 | -20.1849 | 51958.6187 | 2.223 |  | Hz | [6 empty] | 7.3759 | 247.83 | 683.0687 | 4.1923 | 250 | 1.122 | 1.5 | Hz
41.7967 | 1404.3702 | 1839.6088 | -21.134 | 56959.4292 | 2.509 |  | Hz | [6 empty] | 9.8345 | 330.44 | 765.6787 | 4.6994 | 250 | 1.995 | 2 | Hz
44.2554 | 1486.9802 | 1922.2188 | -22.083 | 62189.9656 | 2.813 |  | Hz | [6 empty] | 12.2932 | 413.05 | 848.2887 | 5.2064 | 250 | 3.117 | 2.5 | Hz
46.714 | 1569.5902 | 2004.8288 | -23.0321 | 67650.228 | 3.135 |  | Hz | [6 empty] | 14.7518 | 495.6601 | 930.8987 | 5.7134 | 250 | 4.489 | 3 | Hz
49.1726 | 1652.2002 | 2087.4388 | -23.9811 | 73340.2163 | 3.473 |  | Hz | [6 empty] | 17.2104 | 578.2701 | 1013.5087 | 6.2204 | 250 | 6.11 | 3.5 | Hz
51.6313 | 1734.8102 | 2170.0489 | -24.9302 | 79259.9305 | 3.829 |  | Hz | [6 empty] | 19.669 | 660.8801 | 1096.1187 | 6.7274 | 250 | 7.98 | 4 | Hz
54.0899 | 1817.4202 | 2252.6589 | -25.8792 | 85409.3706 | 4.203 |  | Hz | [6 empty] | 22.1277 | 743.4901 | 1178.7287 | 7.2345 | 250 | 10.1 | 4.5 | Hz
56.5485 | 1900.0302 | 2335.2689 | -26.8283 | 91788.5367 | 4.593 |  | Hz | [6 empty] | 24.5863 | 826.1001 | 1261.3387 | 7.7415 | 250 | 12.469 | 5 | Hz
59.0071 | 1982.6402 | 2417.8789 | -27.7773 | 98397.4287 | 5.002 |  | Hz | [6 empty] | 27.0449 | 908.7101 | 1343.9488 | 8.2485 | 250 | 15.088 | 5.5 | Hz
0 | 0 | 435.2386 | -5.0001 | 3188.3762 | [9 empty] | 29.5036 | 991.3201 | 1426.5588 | 8.7555 | 250 | 17.956 | 6 | Hz
[14 empty] | 31.9622 | 1073.9301 | 1509.1688 | 9.2625 | 250 | 21.073 | 6.5 | Hz
Power Curves @ Te 3 |  |  |  |  | Power Curve @ Te 3 | [8 empty] | 34.4208 | 1156.5401 | 1591.7788 | 9.7696 | 250 | 24.44 | 7 | Hz
Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW) | [8 empty] | 36.8795 | 1239.1502 | 1674.3888 | 10.2766 | 250 | 28.056 | 7.5 | Hz
0 | 0 | 435.2386 | 2.6713 | 404.4459 | 0 |  | Hz | [6 empty] | 39.3381 | 1321.7602 | 1756.9988 | 10.7836 | 250 | 31.922 | 8 | Hz
2.4586 | 82.61 | 517.8487 | 3.1783 | 572.5471 | 0.125 |  | Hz | [6 empty] | 41.7967 | 1404.3702 | 1839.6088 | 11.2906 | 250 | 36.037 | 8.5 | Hz
4.9173 | 165.22 | 600.4587 | 3.6853 | 769.789 | 0.499 |  | Hz | [6 empty] | 44.2554 | 1486.9802 | 1922.2188 | 11.7976 | 250 | 40.401 | 9 | Hz
7.3759 | 247.83 | 683.0687 | 4.1923 | 996.1718 | 1.122 |  | Hz | [6 empty] | 46.714 | 1569.5902 | 2004.8288 | 12.3047 | 250 | 45.015 | 9.5 | Hz
9.8345 | 330.44 | 765.6787 | 4.6994 | 1251.6952 | 1.995 |  | Hz | [6 empty] | 49.1726 | 1652.2002 | 2087.4388 | 12.8117 | 250 | 49.878 | 10 | Hz
12.2932 | 413.05 | 848.2887 | 5.2064 | 1536.3595 | 3.117 |  | Hz | [6 empty] | 51.6313 | 1734.8102 | 2170.0489 | 13.3187 | 250 | 54.99 | 10.5 | Hz
14.7518 | 495.6601 | 930.8987 | 5.7134 | 1850.1645 | 4.489 |  | Hz | [6 empty] | 54.0899 | 1817.4202 | 2252.6589 | 13.8257 | 250 | 60.352 | 11 | Hz
17.2104 | 578.2701 | 1013.5087 | 6.2204 | 2193.1102 | 6.11 |  | Hz | [6 empty] | 56.5485 | 1900.0302 | 2335.2689 | 14.3327 | 250 | 65.963 | 11.5 | Hz
19.669 | 660.8801 | 1096.1187 | 6.7274 | 2565.1967 | 7.98 |  | Hz | [6 empty] | 59.0071 | 1982.6402 | 2417.8789 | 14.8398 | 250 | 71.824 | 12 | Hz
22.1277 | 743.4901 | 1178.7287 | 7.2345 | 2966.424 | 10.1 |  | Hz
24.5863 | 826.1001 | 1261.3387 | 7.7415 | 3396.792 | 12.469 |  | Hz
27.0449 | 908.7101 | 1343.9488 | 8.2485 | 3856.3008 | 15.088 | 5.5 | Hz | [6 empty] | Power Curves @ Te 4 |  |  |  |  | Power Curve @ Te 4
29.5036 | 991.3201 | 1426.5588 | 8.7555 | 4344.9504 | 17.956 |  | Hz | [6 empty] | Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW)
31.9622 | 1073.9301 | 1509.1688 | 9.2625 | 4862.7407 | 21.073 |  | Hz | [6 empty] | 0 | 0 | 435.2386 | 1.7666 | 99.5037 | 0 | 0 | Hz
34.4208 | 1156.5401 | 1591.7788 | 9.7696 | 5409.6717 | 24.44 |  | Hz | [6 empty] | 2.4586 | 82.61 | 517.8487 | 2.102 | 140.8607 | 3.765 | 0.5 | Hz
36.8795 | 1239.1502 | 1674.3888 | 10.2766 | 5985.7435 | 28.056 |  | Hz | [6 empty] | 4.9173 | 165.22 | 600.4587 | 2.4373 | 189.3871 | 15.058 | 1 | Hz
39.3381 | 1321.7602 | 1756.9988 | 10.7836 | 6590.9561 | 31.922 |  | Hz | [6 empty] | 7.3759 | 247.83 | 683.0687 | 2.7726 | 245.0829 | 33.881 | 1.5 | Hz
41.7967 | 1404.3702 | 1839.6088 | 11.2906 | 7225.3094 | 36.037 |  | Hz | [6 empty] | 9.8345 | 330.44 | 765.6787 | 3.1079 | 250 | 60.233 | 2 | Hz
44.2554 | 1486.9802 | 1922.2188 | 11.7976 | 7888.8035 | 40.401 |  | Hz | [6 empty] | 12.2932 | 413.05 | 848.2887 | 3.4432 | 250 | 94.113 | 2.5 | Hz
46.714 | 1569.5902 | 2004.8288 | 12.3047 | 8581.4383 | 45.015 |  | Hz | [6 empty] | 14.7518 | 495.6601 | 930.8987 | 3.7785 | 250 | 135.523 | 3 | Hz
49.1726 | 1652.2002 | 2087.4388 | 12.8117 | 9303.2139 | 49.878 |  | Hz | [6 empty] | 17.2104 | 578.2701 | 1013.5087 | 4.1138 | 250 | 184.462 | 3.5 | Hz
51.6313 | 1734.8102 | 2170.0489 | 13.3187 | 10054.1303 | 54.99 |  | Hz | [6 empty] | 19.669 | 660.8801 | 1096.1187 | 4.4492 | 250 | 240.93 | 4 | Hz
54.0899 | 1817.4202 | 2252.6589 | 13.8257 | 10834.1874 | 60.352 |  | Hz | [6 empty] | 22.1277 | 743.4901 | 1178.7287 | 4.7845 | 250 | 304.927 | 4.5 | Hz
56.5485 | 1900.0302 | 2335.2689 | 14.3327 | 11643.3853 | 65.963 |  | Hz | [6 empty] | 24.5863 | 826.1001 | 1261.3387 | 5.1198 | 250 | 376.454 | 5 | Hz
59.0071 | 1982.6402 | 2417.8789 | 14.8398 | 12481.7239 | 71.824 |  | Hz | [6 empty] | 27.0449 | 908.7101 | 1343.9488 | 5.4551 | 250 | 455.509 | 5.5 | Hz
0 | 0 | 435.2386 | 2.6713 | 404.4459 | [9 empty] | 29.5036 | 991.3201 | 1426.5588 | 5.7904 | 250 | 542.093 | 6 | Hz
[14 empty] | 31.9622 | 1073.9301 | 1509.1688 | 6.1257 | 250 | 636.207 | 6.5 | Hz
Power Curves @ Te 4 |  |  |  |  | Power Curve @ Te 4 | [8 empty] | 34.4208 | 1156.5401 | 1591.7788 | 6.461 | 250 | 737.849 | 7 | Hz
Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW) | [8 empty] | 36.8795 | 1239.1502 | 1674.3888 | 6.7964 | 250 | 750 | 7.5 | Hz
0 | 0 | 435.2386 | 1.7666 | 99.5037 | 0 | [8 empty] | 39.3381 | 1321.7602 | 1756.9988 | 7.1317 | 250 | 750 | 8 | Hz
2.4586 | 82.61 | 517.8487 | 2.102 | 140.8607 | 3.765 | [8 empty] | 41.7967 | 1404.3702 | 1839.6088 | 7.467 | 250 | 750 | 8.5 | Hz
4.9173 | 165.22 | 600.4587 | 2.4373 | 189.3871 | 15.058 | [8 empty] | 44.2554 | 1486.9802 | 1922.2188 | 7.8023 | 250 | 750 | 9 | Hz
7.3759 | 247.83 | 683.0687 | 2.7726 | 245.0829 | 33.881 | [8 empty] | 46.714 | 1569.5902 | 2004.8288 | 8.1376 | 250 | 750 | 9.5 | Hz
9.8345 | 330.44 | 765.6787 | 3.1079 | 307.948 | 60.233 | [8 empty] | 49.1726 | 1652.2002 | 2087.4388 | 8.4729 | 250 | 750 | 10 | Hz
12.2932 | 413.05 | 848.2887 | 3.4432 | 377.9824 | 94.113 | [8 empty] | 51.6313 | 1734.8102 | 2170.0489 | 8.8083 | 250 | 750 | 10.5 | Hz
14.7518 | 495.6601 | 930.8987 | 3.7785 | 455.1862 | 135.523 | [8 empty] | 54.0899 | 1817.4202 | 2252.6589 | 9.1436 | 250 | 750 | 11 | Hz
17.2104 | 578.2701 | 1013.5087 | 4.1138 | 539.5593 | 184.462 | [8 empty] | 56.5485 | 1900.0302 | 2335.2689 | 9.4789 | 250 | 750 | 11.5 | Hz
19.669 | 660.8801 | 1096.1187 | 4.4492 | 631.1018 | 240.93 | [8 empty] | 59.0071 | 1982.6402 | 2417.8789 | 9.8142 | 250 | 750 | 12 | Hz
22.1277 | 743.4901 | 1178.7287 | 4.7845 | 729.8136 | 304.927
24.5863 | 826.1001 | 1261.3387 | 5.1198 | 835.6948 | 376.454
27.0449 | 908.7101 | 1343.9488 | 5.4551 | 948.7453 | 455.509 | 5.5 | Hz | [6 empty] | Power Curves @ Te 5 |  |  |  |  | Power Curve @ Te 5
29.5036 | 991.3201 | 1426.5588 | 5.7904 | 1068.9652 | 542.093 | [8 empty] | Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW)
31.9622 | 1073.9301 | 1509.1688 | 6.1257 | 1196.3544 | 636.207 | [8 empty] | 0 | 0 | 435.2386 | 1.5373 | 48.2187 | 0 | 0 | Hz
34.4208 | 1156.5401 | 1591.7788 | 6.461 | 1330.913 | 737.849 | [8 empty] | 2.4586 | 82.61 | 517.8487 | 1.829 | 68.26 | 15.145 | 0.5 | Hz
36.8795 | 1239.1502 | 1674.3888 | 6.7964 | 1472.6409 | 847.021 | [8 empty] | 4.9173 | 165.22 | 600.4587 | 2.1208 | 91.7755 | 60.581 | 1 | Hz
39.3381 | 1321.7602 | 1756.9988 | 7.1317 | 1621.5381 | 963.721 | [8 empty] | 7.3759 | 247.83 | 683.0687 | 2.4126 | 118.7652 | 136.308 | 1.5 | Hz
41.7967 | 1404.3702 | 1839.6088 | 7.467 | 1777.6047 | 1088 | [8 empty] | 9.8345 | 330.44 | 765.6787 | 2.7044 | 149.2291 | 242.324 | 2 | Hz
44.2554 | 1486.9802 | 1922.2188 | 7.8023 | 1940.8407 | 1220 | [8 empty] | 12.2932 | 413.05 | 848.2887 | 2.9961 | 183.1672 | 378.632 | 2.5 | Hz
46.714 | 1569.5902 | 2004.8288 | 8.1376 | 2111.246 | 1359 | [8 empty] | 14.7518 | 495.6601 | 930.8987 | 3.2879 | 220.5796 | 545.23 | 3 | Hz
49.1726 | 1652.2002 | 2087.4388 | 8.4729 | 2288.8206 | 1506 | [8 empty] | 17.2104 | 578.2701 | 1013.5087 | 3.5797 | 250 | 742.119 | 3.5 | Hz
51.6313 | 1734.8102 | 2170.0489 | 8.8083 | 2473.5646 | 1660 | [8 empty] | 19.669 | 660.8801 | 1096.1187 | 3.8715 | 250 | 750 | 4 | Hz
54.0899 | 1817.4202 | 2252.6589 | 9.1436 | 2665.4779 | 1822 | [8 empty] | 22.1277 | 743.4901 | 1178.7287 | 4.1632 | 250 | 750 | 4.5 | Hz
56.5485 | 1900.0302 | 2335.2689 | 9.4789 | 2864.5606 | 1991 | [8 empty] | 24.5863 | 826.1001 | 1261.3387 | 4.455 | 250 | 750 | 5 | Hz
59.0071 | 1982.6402 | 2417.8789 | 9.8142 | 3070.8126 | 2168 | [8 empty] | 27.0449 | 908.7101 | 1343.9488 | 4.7468 | 250 | 750 | 5.5 | Hz
0 | 0 | 435.2386 | 1.7666 | 99.5037 | [9 empty] | 29.5036 | 991.3201 | 1426.5588 | 5.0386 | 250 | 750 | 6 | Hz
[14 empty] | 31.9622 | 1073.9301 | 1509.1688 | 5.3304 | 250 | 750 | 6.5 | Hz
Power Curves @ Te 5 |  |  |  |  | Power Curve @ Te 5 | [8 empty] | 34.4208 | 1156.5401 | 1591.7788 | 5.6221 | 250 | 750 | 7 | Hz
Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW) | [8 empty] | 36.8795 | 1239.1502 | 1674.3888 | 5.9139 | 250 | 750 | 7.5 | Hz
0 | 0 | 435.2386 | 1.5373 | 48.2187 | 0 | [8 empty] | 39.3381 | 1321.7602 | 1756.9988 | 6.2057 | 250 | 750 | 8 | Hz
2.4586 | 82.61 | 517.8487 | 1.829 | 68.26 | 15.145 | [8 empty] | 41.7967 | 1404.3702 | 1839.6088 | 6.4975 | 250 | 750 | 8.5 | Hz
4.9173 | 165.22 | 600.4587 | 2.1208 | 91.7755 | 60.581 | [8 empty] | 44.2554 | 1486.9802 | 1922.2188 | 6.7892 | 250 | 750 | 9 | Hz
7.3759 | 247.83 | 683.0687 | 2.4126 | 118.7652 | 136.308 | [8 empty] | 46.714 | 1569.5902 | 2004.8288 | 7.081 | 250 | 750 | 9.5 | Hz
9.8345 | 330.44 | 765.6787 | 2.7044 | 149.2291 | 242.324 | [8 empty] | 49.1726 | 1652.2002 | 2087.4388 | 7.3728 | 250 | 750 | 10 | Hz
12.2932 | 413.05 | 848.2887 | 2.9961 | 183.1672 | 378.632 | [8 empty] | 51.6313 | 1734.8102 | 2170.0489 | 7.6646 | 250 | 750 | 10.5 | Hz
14.7518 | 495.6601 | 930.8987 | 3.2879 | 220.5796 | 545.23 | [8 empty] | 54.0899 | 1817.4202 | 2252.6589 | 7.9564 | 250 | 750 | 11 | Hz
17.2104 | 578.2701 | 1013.5087 | 3.5797 | 261.4661 | 742.119 | [8 empty] | 56.5485 | 1900.0302 | 2335.2689 | 8.2481 | 250 | 750 | 11.5 | Hz
19.669 | 660.8801 | 1096.1187 | 3.8715 | 305.8269 | 969.298 | [8 empty] | 59.0071 | 1982.6402 | 2417.8789 | 8.5399 | 250 | 750 | 12 | Hz
22.1277 | 743.4901 | 1178.7287 | 4.1632 | 353.6618 | 1227
24.5863 | 826.1001 | 1261.3387 | 4.455 | 404.971 | 1515
27.0449 | 908.7101 | 1343.9488 | 4.7468 | 459.7544 | 1833 | 5.5 | Hz | [6 empty] | Power Curves @ Te 6 |  |  |  |  | Power Curve @ Te 6
29.5036 | 991.3201 | 1426.5588 | 5.0386 | 518.0119 | 2181 | [8 empty] | Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW)
31.9622 | 1073.9301 | 1509.1688 | 5.3304 | 579.7437 | 2560 | [8 empty] | 0 | 0 | 435.2386 | 1.4407 | 29.4124 | 0 | 0 | Hz
34.4208 | 1156.5401 | 1591.7788 | 5.6221 | 644.9497 | 2968 | [8 empty] | 2.4586 | 82.61 | 517.8487 | 1.7142 | 41.6372 | 10.356 | 0.5 | Hz
36.8795 | 1239.1502 | 1674.3888 | 5.9139 | 713.6299 | 3408 | [8 empty] | 4.9173 | 165.22 | 600.4587 | 1.9877 | 55.9812 | 41.423 | 1 | Hz
39.3381 | 1321.7602 | 1756.9988 | 6.2057 | 785.7843 | 3877 | [8 empty] | 7.3759 | 247.83 | 683.0687 | 2.2611 | 72.4444 | 93.202 | 1.5 | Hz
41.7967 | 1404.3702 | 1839.6088 | 6.4975 | 861.413 | 4377 | [8 empty] | 9.8345 | 330.44 | 765.6787 | 2.5346 | 91.0268 | 165.692 | 2 | Hz
44.2554 | 1486.9802 | 1922.2188 | 6.7892 | 940.5158 | 4907 | [8 empty] | 12.2932 | 413.05 | 848.2887 | 2.808 | 111.7284 | 258.894 | 2.5 | Hz
46.714 | 1569.5902 | 2004.8288 | 7.081 | 1023.0928 | 5467 | [8 empty] | 14.7518 | 495.6601 | 930.8987 | 3.0815 | 134.5492 | 372.807 | 3 | Hz
49.1726 | 1652.2002 | 2087.4388 | 7.3728 | 1109.1441 | 6058 | [8 empty] | 17.2104 | 578.2701 | 1013.5087 | 3.3549 | 159.4891 | 507.431 | 3.5 | Hz
51.6313 | 1734.8102 | 2170.0489 | 7.6646 | 1198.6695 | 6679 | [8 empty] | 19.669 | 660.8801 | 1096.1187 | 3.6284 | 186.5483 | 662.768 | 4 | Hz
54.0899 | 1817.4202 | 2252.6589 | 7.9564 | 1291.6692 | 7330 | [8 empty] | 22.1277 | 743.4901 | 1178.7287 | 3.9019 | 215.7267 | 750 | 4.5 | Hz
56.5485 | 1900.0302 | 2335.2689 | 8.2481 | 1388.143 | 8012 | [8 empty] | 24.5863 | 826.1001 | 1261.3387 | 4.1753 | 247.0243 | 750 | 5 | Hz
59.0071 | 1982.6402 | 2417.8789 | 8.5399 | 1488.0911 | 8724 | [8 empty] | 27.0449 | 908.7101 | 1343.9488 | 4.4488 | 250 | 750 | 5.5 | Hz
0 | 0 | 435.2386 | 1.5373 | 48.2187 | [9 empty] | 29.5036 | 991.3201 | 1426.5588 | 4.7222 | 250 | 750 | 6 | Hz
[14 empty] | 31.9622 | 1073.9301 | 1509.1688 | 4.9957 | 250 | 750 | 6.5 | Hz
Power Curves @ Te 6 |  |  |  |  | Power Curve @ Te 6 | [8 empty] | 34.4208 | 1156.5401 | 1591.7788 | 5.2691 | 250 | 750 | 7 | Hz
Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW) | [8 empty] | 36.8795 | 1239.1502 | 1674.3888 | 5.5426 | 250 | 750 | 7.5 | Hz
0 | 0 | 435.2386 | 1.4407 | 29.4124 | 0 | [8 empty] | 39.3381 | 1321.7602 | 1756.9988 | 5.8161 | 250 | 750 | 8 | Hz
2.4586 | 82.61 | 517.8487 | 1.7142 | 41.6372 | 10.356 | [8 empty] | 41.7967 | 1404.3702 | 1839.6088 | 6.0895 | 250 | 750 | 8.5 | Hz
4.9173 | 165.22 | 600.4587 | 1.9877 | 55.9812 | 41.423 | [8 empty] | 44.2554 | 1486.9802 | 1922.2188 | 6.363 | 250 | 750 | 9 | Hz
7.3759 | 247.83 | 683.0687 | 2.2611 | 72.4444 | 93.202 | [8 empty] | 46.714 | 1569.5902 | 2004.8288 | 6.6364 | 250 | 750 | 9.5 | Hz
9.8345 | 330.44 | 765.6787 | 2.5346 | 91.0268 | 165.692 | [8 empty] | 49.1726 | 1652.2002 | 2087.4388 | 6.9099 | 250 | 750 | 10 | Hz
12.2932 | 413.05 | 848.2887 | 2.808 | 111.7284 | 258.894 | [8 empty] | 51.6313 | 1734.8102 | 2170.0489 | 7.1834 | 250 | 750 | 10.5 | Hz
14.7518 | 495.6601 | 930.8987 | 3.0815 | 134.5492 | 372.807 | [8 empty] | 54.0899 | 1817.4202 | 2252.6589 | 7.4568 | 250 | 750 | 11 | Hz
17.2104 | 578.2701 | 1013.5087 | 3.3549 | 159.4891 | 507.431 | [8 empty] | 56.5485 | 1900.0302 | 2335.2689 | 7.7303 | 250 | 750 | 11.5 | Hz
19.669 | 660.8801 | 1096.1187 | 3.6284 | 186.5483 | 662.768 | [8 empty] | 59.0071 | 1982.6402 | 2417.8789 | 8.0037 | 250 | 750 | 12 | Hz
22.1277 | 743.4901 | 1178.7287 | 3.9019 | 215.7267 | 838.815
24.5863 | 826.1001 | 1261.3387 | 4.1753 | 247.0243 | 1036
27.0449 | 908.7101 | 1343.9488 | 4.4488 | 280.441 | 1253 | 5.5 | Hz | [6 empty] | Power Curves @ Te 7 |  |  |  |  | Power Curve @ Te 7
29.5036 | 991.3201 | 1426.5588 | 4.7222 | 315.977 | 1491 | [8 empty] | Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW)
31.9622 | 1073.9301 | 1509.1688 | 4.9957 | 353.6322 | 1750 | [8 empty] | 0 | 0 | 435.2386 | 1.3909 | 20.1388 | 0 | 0 | Hz
34.4208 | 1156.5401 | 1591.7788 | 5.2691 | 393.4065 | 2030 | [8 empty] | 2.4586 | 82.61 | 517.8487 | 1.6548 | 28.5091 | 4.061 | 0.5 | Hz
36.8795 | 1239.1502 | 1674.3888 | 5.5426 | 435.3001 | 2330 | [8 empty] | 4.9173 | 165.22 | 600.4587 | 1.9188 | 38.3305 | 16.242 | 1 | Hz
39.3381 | 1321.7602 | 1756.9988 | 5.8161 | 479.3129 | 2651 | [8 empty] | 7.3759 | 247.83 | 683.0687 | 2.1828 | 49.6028 | 36.545 | 1.5 | Hz
41.7967 | 1404.3702 | 1839.6088 | 6.0895 | 525.4448 | 2993 | [8 empty] | 9.8345 | 330.44 | 765.6787 | 2.4468 | 62.3262 | 64.968 | 2 | Hz
44.2554 | 1486.9802 | 1922.2188 | 6.363 | 573.696 | 3355 | [8 empty] | 12.2932 | 413.05 | 848.2887 | 2.7108 | 76.5007 | 101.513 | 2.5 | Hz
46.714 | 1569.5902 | 2004.8288 | 6.6364 | 624.0663 | 3738 | [8 empty] | 14.7518 | 495.6601 | 930.8987 | 2.9748 | 92.1261 | 146.178 | 3 | Hz
49.1726 | 1652.2002 | 2087.4388 | 6.9099 | 676.5559 | 4142 | [8 empty] | 17.2104 | 578.2701 | 1013.5087 | 3.2388 | 109.2026 | 198.965 | 3.5 | Hz
51.6313 | 1734.8102 | 2170.0489 | 7.1834 | 731.1646 | 4567 | [8 empty] | 19.669 | 660.8801 | 1096.1187 | 3.5028 | 127.73 | 259.872 | 4 | Hz
54.0899 | 1817.4202 | 2252.6589 | 7.4568 | 787.8926 | 5012 | [8 empty] | 22.1277 | 743.4901 | 1178.7287 | 3.7668 | 147.7085 | 328.901 | 4.5 | Hz
56.5485 | 1900.0302 | 2335.2689 | 7.7303 | 846.7397 | 5478 | [8 empty] | 24.5863 | 826.1001 | 1261.3387 | 4.0308 | 169.138 | 406.051 | 5 | Hz
59.0071 | 1982.6402 | 2417.8789 | 8.0037 | 907.7061 | 5965 | [8 empty] | 27.0449 | 908.7101 | 1343.9488 | 4.2947 | 192.0186 | 491.321 | 5.5 | Hz
0 | 0 | 435.2386 | 1.4407 | 29.4124 | [9 empty] | 29.5036 | 991.3201 | 1426.5588 | 4.5587 | 216.3501 | 584.713 | 6 | Hz
[14 empty] | 31.9622 | 1073.9301 | 1509.1688 | 4.8227 | 242.1327 | 686.226 | 6.5 | Hz
Power Curves @ Te 7 |  |  |  |  | Power Curve @ Te 7 | [8 empty] | 34.4208 | 1156.5401 | 1591.7788 | 5.0867 | 250 | 750 | 7 | Hz
Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW) | [8 empty] | 36.8795 | 1239.1502 | 1674.3888 | 5.3507 | 250 | 750 | 7.5 | Hz
0 | 0 | 435.2386 | 1.3909 | 20.1388 | 0 | [8 empty] | 39.3381 | 1321.7602 | 1756.9988 | 5.6147 | 250 | 750 | 8 | Hz
2.4586 | 82.61 | 517.8487 | 1.6548 | 28.5091 | 4.061 | [8 empty] | 41.7967 | 1404.3702 | 1839.6088 | 5.8787 | 250 | 750 | 8.5 | Hz
4.9173 | 165.22 | 600.4587 | 1.9188 | 38.3305 | 16.242 | [8 empty] | 44.2554 | 1486.9802 | 1922.2188 | 6.1427 | 250 | 750 | 9 | Hz
7.3759 | 247.83 | 683.0687 | 2.1828 | 49.6028 | 36.545 | [8 empty] | 46.714 | 1569.5902 | 2004.8288 | 6.4067 | 250 | 750 | 9.5 | Hz
9.8345 | 330.44 | 765.6787 | 2.4468 | 62.3262 | 64.968 | [8 empty] | 49.1726 | 1652.2002 | 2087.4388 | 6.6707 | 250 | 750 | 10 | Hz
12.2932 | 413.05 | 848.2887 | 2.7108 | 76.5007 | 101.513 | [8 empty] | 51.6313 | 1734.8102 | 2170.0489 | 6.9347 | 250 | 750 | 10.5 | Hz
14.7518 | 495.6601 | 930.8987 | 2.9748 | 92.1261 | 146.178 | [8 empty] | 54.0899 | 1817.4202 | 2252.6589 | 7.1986 | 250 | 750 | 11 | Hz
17.2104 | 578.2701 | 1013.5087 | 3.2388 | 109.2026 | 198.965 | [8 empty] | 56.5485 | 1900.0302 | 2335.2689 | 7.4626 | 250 | 750 | 11.5 | Hz
19.669 | 660.8801 | 1096.1187 | 3.5028 | 127.73 | 259.872 | [8 empty] | 59.0071 | 1982.6402 | 2417.8789 | 7.7266 | 250 | 750 | 12 | Hz
22.1277 | 743.4901 | 1178.7287 | 3.7668 | 147.7085 | 328.901
24.5863 | 826.1001 | 1261.3387 | 4.0308 | 169.138 | 406.051
27.0449 | 908.7101 | 1343.9488 | 4.2947 | 192.0186 | 491.321 | 5.5 | Hz | [6 empty] | Power Curves @ Te 8 |  |  |  |  | Power Curve @ Te 8
29.5036 | 991.3201 | 1426.5588 | 4.5587 | 216.3501 | 584.713 | [8 empty] | Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW)
31.9622 | 1073.9301 | 1509.1688 | 4.8227 | 242.1327 | 686.226 | [8 empty] | 0 | 0 | 435.2386 | 1.362 | 14.7845 | 0 | 0 | Hz
34.4208 | 1156.5401 | 1591.7788 | 5.0867 | 269.3663 | 795.859 | [8 empty] | 2.4586 | 82.61 | 517.8487 | 1.6205 | 20.9295 | 1.417 | 0.5 | Hz
36.8795 | 1239.1502 | 1674.3888 | 5.3507 | 298.0509 | 913.614 | [8 empty] | 4.9173 | 165.22 | 600.4587 | 1.879 | 28.1396 | 5.669 | 1 | Hz
39.3381 | 1321.7602 | 1756.9988 | 5.6147 | 328.1865 | 1039 | [8 empty] | 7.3759 | 247.83 | 683.0687 | 2.1375 | 36.4151 | 12.755 | 1.5 | Hz
41.7967 | 1404.3702 | 1839.6088 | 5.8787 | 359.7732 | 1173 | [8 empty] | 9.8345 | 330.44 | 765.6787 | 2.396 | 45.7557 | 22.676 | 2 | Hz
44.2554 | 1486.9802 | 1922.2188 | 6.1427 | 392.8108 | 1316 | [8 empty] | 12.2932 | 413.05 | 848.2887 | 2.6545 | 56.1616 | 35.431 | 2.5 | Hz
46.714 | 1569.5902 | 2004.8288 | 6.4067 | 427.2995 | 1466 | [8 empty] | 14.7518 | 495.6601 | 930.8987 | 2.913 | 67.6328 | 51.021 | 3 | Hz
49.1726 | 1652.2002 | 2087.4388 | 6.6707 | 463.2392 | 1624 | [8 empty] | 17.2104 | 578.2701 | 1013.5087 | 3.1715 | 80.1692 | 69.445 | 3.5 | Hz
51.6313 | 1734.8102 | 2170.0489 | 6.9347 | 500.63 | 1791 | [8 empty] | 19.669 | 660.8801 | 1096.1187 | 3.43 | 93.7708 | 90.704 | 4 | Hz
54.0899 | 1817.4202 | 2252.6589 | 7.1986 | 539.4717 | 1965 | [8 empty] | 22.1277 | 743.4901 | 1178.7287 | 3.6885 | 108.4377 | 124.797 | 4.5 | Hz
56.5485 | 1900.0302 | 2335.2689 | 7.4626 | 579.7645 | 2148 | [8 empty] | 24.5863 | 826.1001 | 1261.3387 | 3.947 | 124.1698 | 141.724 | 5 | Hz
59.0071 | 1982.6402 | 2417.8789 | 7.7266 | 621.5082 | 2339 | [8 empty] | 27.0449 | 908.7101 | 1343.9488 | 4.2055 | 140.9671 | 171.486 | 5.5 | Hz
0 | 0 | 435.2386 | 1.3909 | 20.1388 | [9 empty] | 29.5036 | 991.3201 | 1426.5588 | 4.464 | 158.8297 | 204.083 | 6 | Hz
[14 empty] | 31.9622 | 1073.9301 | 1509.1688 | 4.7225 | 177.7575 | 239.514 | 6.5 | Hz
Power Curves @ Te 8 |  |  |  |  | Power Curve @ Te 8 | [8 empty] | 34.4208 | 1156.5401 | 1591.7788 | 4.981 | 197.7506 | 277.78 | 7 | Hz
Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW) | [8 empty] | 36.8795 | 1239.1502 | 1674.3888 | 5.2395 | 218.8089 | 318.88 | 7.5 | Hz
0 | 0 | 435.2386 | 1.362 | 14.7845 | 0 | [8 empty] | 39.3381 | 1321.7602 | 1756.9988 | 5.498 | 240.9325 | 362.814 | 8 | Hz
2.4586 | 82.61 | 517.8487 | 1.6205 | 20.9295 | 1.417 | [8 empty] | 41.7967 | 1404.3702 | 1839.6088 | 5.7565 | 250 | 409.583 | 8.5 | Hz
4.9173 | 165.22 | 600.4587 | 1.879 | 28.1396 | 5.669 | [8 empty] | 44.2554 | 1486.9802 | 1922.2188 | 6.015 | 250 | 459.187 | 9 | Hz
7.3759 | 247.83 | 683.0687 | 2.1375 | 36.4151 | 12.755 | [8 empty] | 46.714 | 1569.5902 | 2004.8288 | 6.2735 | 250 | 511.625 | 9.5 | Hz
9.8345 | 330.44 | 765.6787 | 2.396 | 45.7557 | 22.676 | [8 empty] | 49.1726 | 1652.2002 | 2087.4388 | 6.532 | 250 | 566.897 | 10 | Hz
12.2932 | 413.05 | 848.2887 | 2.6545 | 56.1616 | 35.431 | [8 empty] | 51.6313 | 1734.8102 | 2170.0489 | 6.7905 | 250 | 625.004 | 10.5 | Hz
14.7518 | 495.6601 | 930.8987 | 2.913 | 67.6328 | 51.021 | [8 empty] | 54.0899 | 1817.4202 | 2252.6589 | 7.049 | 250 | 685.946 | 11 | Hz
17.2104 | 578.2701 | 1013.5087 | 3.1715 | 80.1692 | 69.445 | [8 empty] | 56.5485 | 1900.0302 | 2335.2689 | 7.3075 | 250 | 749.722 | 11.5 | Hz
19.669 | 660.8801 | 1096.1187 | 3.43 | 93.7708 | 90.704 | [8 empty] | 59.0071 | 1982.6402 | 2417.8789 | 7.566 | 250 | 750 | 12 | Hz
22.1277 | 743.4901 | 1178.7287 | 3.6885 | 108.4377 | 124.797
24.5863 | 826.1001 | 1261.3387 | 3.947 | 124.1698 | 141.724
27.0449 | 908.7101 | 1343.9488 | 4.2055 | 140.9671 | 171.486 | 5.5 | Hz | [6 empty] | Power Curves @ Te 9 |  |  |  |  | Power Curve @ Te 9
29.5036 | 991.3201 | 1426.5588 | 4.464 | 158.8297 | 204.083 | [8 empty] | Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW)
31.9622 | 1073.9301 | 1509.1688 | 4.7225 | 177.7575 | 239.514 | [8 empty] | 0 | 0 | 435.2386 | 1.3439 | 11.3744 | 0 | 0 | Hz
34.4208 | 1156.5401 | 1591.7788 | 4.981 | 197.7506 | 277.78 | [8 empty] | 2.4586 | 82.61 | 517.8487 | 1.599 | 16.102 | 0.503 | 0.5 | Hz
36.8795 | 1239.1502 | 1674.3888 | 5.2395 | 218.8089 | 318.88 | [8 empty] | 4.9173 | 165.22 | 600.4587 | 1.8541 | 21.6492 | 2.011 | 1 | Hz
39.3381 | 1321.7602 | 1756.9988 | 5.498 | 240.9325 | 362.814 | [8 empty] | 7.3759 | 247.83 | 683.0687 | 2.1092 | 28.0159 | 4.526 | 1.5 | Hz
41.7967 | 1404.3702 | 1839.6088 | 5.7565 | 264.1213 | 409.583 | [8 empty] | 9.8345 | 330.44 | 765.6787 | 2.3643 | 35.2021 | 8.045 | 2 | Hz
44.2554 | 1486.9802 | 1922.2188 | 6.015 | 288.3753 | 459.187 | [8 empty] | 12.2932 | 413.05 | 848.2887 | 2.6193 | 43.2079 | 12.571 | 2.5 | Hz
46.714 | 1569.5902 | 2004.8288 | 6.2735 | 313.6946 | 511.625 | [8 empty] | 14.7518 | 495.6601 | 930.8987 | 2.8744 | 52.0332 | 18.102 | 3 | Hz
49.1726 | 1652.2002 | 2087.4388 | 6.532 | 340.0791 | 566.897 | [8 empty] | 17.2104 | 578.2701 | 1013.5087 | 3.1295 | 61.678 | 24.639 | 3.5 | Hz
51.6313 | 1734.8102 | 2170.0489 | 6.7905 | 367.5289 | 625.004 | [8 empty] | 19.669 | 660.8801 | 1096.1187 | 3.3846 | 72.1424 | 32.182 | 4 | Hz
54.0899 | 1817.4202 | 2252.6589 | 7.049 | 396.0439 | 685.946 | [8 empty] | 22.1277 | 743.4901 | 1178.7287 | 3.6397 | 83.4263 | 40.73 | 4.5 | Hz
56.5485 | 1900.0302 | 2335.2689 | 7.3075 | 425.6241 | 749.722 | [8 empty] | 24.5863 | 826.1001 | 1261.3387 | 3.8948 | 95.5298 | 50.284 | 5 | Hz
59.0071 | 1982.6402 | 2417.8789 | 7.566 | 456.2696 | 816.332 | [8 empty] | 27.0449 | 908.7101 | 1343.9488 | 4.1498 | 108.4528 | 60.844 | 5.5 | Hz
0 | 0 | 435.2386 | 1.362 | 14.7845 | [9 empty] | 29.5036 | 991.3201 | 1426.5588 | 4.4049 | 122.1954 | 72.409 | 6 | Hz
[14 empty] | 31.9622 | 1073.9301 | 1509.1688 | 4.66 | 136.7574 | 84.981 | 6.5 | Hz
Power Curves @ Te 9 |  |  |  |  | Power Curve @ Te 9 | [8 empty] | 34.4208 | 1156.5401 | 1591.7788 | 4.9151 | 152.1391 | 98.557 | 7 | Hz
Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW) | [8 empty] | 36.8795 | 1239.1502 | 1674.3888 | 5.1702 | 168.3403 | 113.14 | 7.5 | Hz
0 | 0 | 435.2386 | 1.3439 | 11.3744 | 0 | [8 empty] | 39.3381 | 1321.7602 | 1756.9988 | 5.4253 | 185.361 | 128.728 | 8 | Hz
2.4586 | 82.61 | 517.8487 | 1.599 | 16.102 | 0.503 | [8 empty] | 41.7967 | 1404.3702 | 1839.6088 | 5.6803 | 203.2012 | 145.322 | 8.5 | Hz
4.9173 | 165.22 | 600.4587 | 1.8541 | 21.6492 | 2.011 | [8 empty] | 44.2554 | 1486.9802 | 1922.2188 | 5.9354 | 221.861 | 162.921 | 9 | Hz
7.3759 | 247.83 | 683.0687 | 2.1092 | 28.0159 | 4.526 | [8 empty] | 46.714 | 1569.5902 | 2004.8288 | 6.1905 | 241.3404 | 181.526 | 9.5 | Hz
9.8345 | 330.44 | 765.6787 | 2.3643 | 35.2021 | 8.045 | [8 empty] | 49.1726 | 1652.2002 | 2087.4388 | 6.4456 | 250 | 201.137 | 10 | Hz
12.2932 | 413.05 | 848.2887 | 2.6193 | 43.2079 | 12.571 | [8 empty] | 51.6313 | 1734.8102 | 2170.0489 | 6.7007 | 250 | 221.754 | 10.5 | Hz
14.7518 | 495.6601 | 930.8987 | 2.8744 | 52.0332 | 18.102 | [8 empty] | 54.0899 | 1817.4202 | 2252.6589 | 6.9557 | 250 | 243.376 | 11 | Hz
17.2104 | 578.2701 | 1013.5087 | 3.1295 | 61.678 | 24.639 | [8 empty] | 56.5485 | 1900.0302 | 2335.2689 | 7.2108 | 250 | 266.004 | 11.5 | Hz
19.669 | 660.8801 | 1096.1187 | 3.3846 | 72.1424 | 32.182 | [8 empty] | 59.0071 | 1982.6402 | 2417.8789 | 7.4659 | 250 | 289.638 | 12 | Hz
22.1277 | 743.4901 | 1178.7287 | 3.6397 | 83.4263 | 40.73
24.5863 | 826.1001 | 1261.3387 | 3.8948 | 95.5298 | 50.284
27.0449 | 908.7101 | 1343.9488 | 4.1498 | 108.4528 | 60.844 | 5.5 | Hz | [6 empty] | Power Curves @ Te 10 |  |  |  |  | Power Curve @ Te 10
29.5036 | 991.3201 | 1426.5588 | 4.4049 | 122.1954 | 72.409 | [8 empty] | Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW)
31.9622 | 1073.9301 | 1509.1688 | 4.66 | 136.7574 | 84.981 | [8 empty] | 0 | 0 | 435.2386 | 1.3321 | 9.0519 | 0 | 0 | Hz
34.4208 | 1156.5401 | 1591.7788 | 4.9151 | 152.1391 | 98.557 | [8 empty] | 2.4586 | 82.61 | 517.8487 | 1.5849 | 12.8142 | 0.189 | 0.5 | Hz
36.8795 | 1239.1502 | 1674.3888 | 5.1702 | 168.3403 | 113.14 | [8 empty] | 4.9173 | 165.22 | 600.4587 | 1.8378 | 17.2286 | 0.756 | 1 | Hz
39.3381 | 1321.7602 | 1756.9988 | 5.4253 | 185.361 | 128.728 | [8 empty] | 7.3759 | 247.83 | 683.0687 | 2.0906 | 22.2953 | 1.7 | 1.5 | Hz
41.7967 | 1404.3702 | 1839.6088 | 5.6803 | 203.2012 | 145.322 | [8 empty] | 9.8345 | 330.44 | 765.6787 | 2.3435 | 28.0141 | 3.022 | 2 | Hz
44.2554 | 1486.9802 | 1922.2188 | 5.9354 | 221.861 | 162.921 | [8 empty] | 12.2932 | 413.05 | 848.2887 | 2.5963 | 34.3852 | 4.722 | 2.5 | Hz
46.714 | 1569.5902 | 2004.8288 | 6.1905 | 241.3404 | 181.526 | [8 empty] | 14.7518 | 495.6601 | 930.8987 | 2.8491 | 41.4085 | 6.8 | 3 | Hz
49.1726 | 1652.2002 | 2087.4388 | 6.4456 | 261.6392 | 201.137 | [8 empty] | 17.2104 | 578.2701 | 1013.5087 | 3.102 | 49.0839 | 9.256 | 3.5 | Hz
51.6313 | 1734.8102 | 2170.0489 | 6.7007 | 282.7577 | 221.754 | [8 empty] | 19.669 | 660.8801 | 1096.1187 | 3.3548 | 57.4116 | 12.089 | 4 | Hz
54.0899 | 1817.4202 | 2252.6589 | 6.9557 | 304.6956 | 243.376 | [8 empty] | 22.1277 | 743.4901 | 1178.7287 | 3.6076 | 66.3914 | 15.3 | 4.5 | Hz
56.5485 | 1900.0302 | 2335.2689 | 7.2108 | 327.4531 | 266.004 | [8 empty] | 24.5863 | 826.1001 | 1261.3387 | 3.8605 | 76.0235 | 18.889 | 5 | Hz
59.0071 | 1982.6402 | 2417.8789 | 7.4659 | 351.0302 | 289.638 | [8 empty] | 27.0449 | 908.7101 | 1343.9488 | 4.1133 | 86.3077 | 22.856 | 5.5 | Hz
0 | 0 | 435.2386 | 1.3439 | 11.3744 | [9 empty] | 29.5036 | 991.3201 | 1426.5588 | 4.3662 | 97.2442 | 27.2 | 6 | Hz
[14 empty] | 31.9622 | 1073.9301 | 1509.1688 | 4.619 | 108.8328 | 31.922 | 6.5 | Hz
Power Curves @ Te 10 |  |  |  |  | Power Curve @ Te 10 | [8 empty] | 34.4208 | 1156.5401 | 1591.7788 | 4.8718 | 121.0737 | 37.022 | 7 | Hz
Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW) | [8 empty] | 36.8795 | 1239.1502 | 1674.3888 | 5.1247 | 133.9667 | 42.5 | 7.5 | Hz
0 | 0 | 435.2386 | 1.3321 | 9.0519 | 0 |  | Hz | [6 empty] | 39.3381 | 1321.7602 | 1756.9988 | 5.3775 | 147.5119 | 48.356 | 8 | Hz
2.4586 | 82.61 | 517.8487 | 1.5849 | 12.8142 | 0.189 |  | Hz | [6 empty] | 41.7967 | 1404.3702 | 1839.6088 | 5.6304 | 161.7094 | 54.589 | 8.5 | Hz
4.9173 | 165.22 | 600.4587 | 1.8378 | 17.2286 | 0.756 |  | Hz | [6 empty] | 44.2554 | 1486.9802 | 1922.2188 | 5.8832 | 176.559 | 61.2 | 9 | Hz
7.3759 | 247.83 | 683.0687 | 2.0906 | 22.2953 | 1.7 |  | Hz | [6 empty] | 46.714 | 1569.5902 | 2004.8288 | 6.136 | 192.0609 | 68.189 | 9.5 | Hz
9.8345 | 330.44 | 765.6787 | 2.3435 | 28.0141 | 3.022 |  | Hz | [6 empty] | 49.1726 | 1652.2002 | 2087.4388 | 6.3889 | 208.2149 | 75.556 | 10 | Hz
12.2932 | 413.05 | 848.2887 | 2.5963 | 34.3852 | 4.722 |  | Hz | [6 empty] | 51.6313 | 1734.8102 | 2170.0489 | 6.6417 | 225.0211 | 83.3 | 10.5 | Hz
14.7518 | 495.6601 | 930.8987 | 2.8491 | 41.4085 | 6.8 |  | Hz | [6 empty] | 54.0899 | 1817.4202 | 2252.6589 | 6.8945 | 242.4795 | 91.422 | 11 | Hz
17.2104 | 578.2701 | 1013.5087 | 3.102 | 49.0839 | 9.256 |  | Hz | [6 empty] | 56.5485 | 1900.0302 | 2335.2689 | 7.1474 | 250 | 99.922 | 11.5 | Hz
19.669 | 660.8801 | 1096.1187 | 3.3548 | 57.4116 | 12.089 |  | Hz | [6 empty] | 59.0071 | 1982.6402 | 2417.8789 | 7.4002 | 250 | 108.8 | 12 | Hz
22.1277 | 743.4901 | 1178.7287 | 3.6076 | 66.3914 | 15.3 |  | Hz
24.5863 | 826.1001 | 1261.3387 | 3.8605 | 76.0235 | 18.889 |  | Hz
27.0449 | 908.7101 | 1343.9488 | 4.1133 | 86.3077 | 22.856 | 5.5 | Hz | [6 empty] | Power Curves @ Te 11 |  |  |  |  | Power Curve @ Te 11
29.5036 | 991.3201 | 1426.5588 | 4.3662 | 97.2442 | 27.2 |  | Hz | [6 empty] | Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW)
31.9622 | 1073.9301 | 1509.1688 | 4.619 | 108.8328 | 31.922 |  | Hz | [6 empty] | 0 | 0 | 435.2386 | 1.3241 | 7.3908 | 0 | 0 | Hz
34.4208 | 1156.5401 | 1591.7788 | 4.8718 | 121.0737 | 37.022 |  | Hz | [6 empty] | 2.4586 | 82.61 | 517.8487 | 1.5754 | 10.4626 | 0.076 | 0.5 | Hz
36.8795 | 1239.1502 | 1674.3888 | 5.1247 | 133.9667 | 42.5 |  | Hz | [6 empty] | 4.9173 | 165.22 | 600.4587 | 1.8267 | 14.067 | 0.304 | 1 | Hz
39.3381 | 1321.7602 | 1756.9988 | 5.3775 | 147.5119 | 48.356 |  | Hz | [6 empty] | 7.3759 | 247.83 | 683.0687 | 2.078 | 18.2039 | 0.683 | 1.5 | Hz
41.7967 | 1404.3702 | 1839.6088 | 5.6304 | 161.7094 | 54.589 |  | Hz | [6 empty] | 9.8345 | 330.44 | 765.6787 | 2.3293 | 22.8733 | 1.215 | 2 | Hz
44.2554 | 1486.9802 | 1922.2188 | 5.8832 | 176.559 | 61.2 |  | Hz | [6 empty] | 12.2932 | 413.05 | 848.2887 | 2.5806 | 28.0752 | 1.898 | 2.5 | Hz
46.714 | 1569.5902 | 2004.8288 | 6.136 | 192.0609 | 68.189 |  | Hz | [6 empty] | 14.7518 | 495.6601 | 930.8987 | 2.8319 | 33.8097 | 2.733 | 3 | Hz
49.1726 | 1652.2002 | 2087.4388 | 6.3889 | 208.2149 | 75.556 |  | Hz | [6 empty] | 17.2104 | 578.2701 | 1013.5087 | 3.0832 | 40.0766 | 3.719 | 3.5 | Hz
51.6313 | 1734.8102 | 2170.0489 | 6.6417 | 225.0211 | 83.3 |  | Hz | [6 empty] | 19.669 | 660.8801 | 1096.1187 | 3.3345 | 46.8761 | 4.858 | 4 | Hz
54.0899 | 1817.4202 | 2252.6589 | 6.8945 | 242.4795 | 91.422 |  | Hz | [6 empty] | 22.1277 | 743.4901 | 1178.7287 | 3.5859 | 54.208 | 6.148 | 4.5 | Hz
56.5485 | 1900.0302 | 2335.2689 | 7.1474 | 260.5902 | 99.922 |  | Hz | [6 empty] | 24.5863 | 826.1001 | 1261.3387 | 3.8372 | 62.0725 | 7.591 | 5 | Hz
59.0071 | 1982.6402 | 2417.8789 | 7.4002 | 279.353 | 108.8 |  | Hz | [6 empty] | 27.0449 | 908.7101 | 1343.9488 | 4.0885 | 70.4695 | 9.185 | 5.5 | Hz
0 | 0 | 435.2386 | 1.3321 | 9.0519 | [9 empty] | 29.5036 | 991.3201 | 1426.5588 | 4.3398 | 79.399 | 10.931 | 6 | Hz
[14 empty] | 31.9622 | 1073.9301 | 1509.1688 | 4.5911 | 88.8611 | 12.828 | 6.5 | Hz
Power Curves @ Te 11 |  |  |  |  | Power Curve @ Te 11 | [8 empty] | 34.4208 | 1156.5401 | 1591.7788 | 4.8424 | 98.8556 | 14.878 | 7 | Hz
Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW) | [8 empty] | 36.8795 | 1239.1502 | 1674.3888 | 5.0937 | 109.3827 | 17.079 | 7.5 | Hz
0 | 0 | 435.2386 | 1.3241 | 7.3908 | 0 | [8 empty] | 39.3381 | 1321.7602 | 1756.9988 | 5.345 | 120.4423 | 19.432 | 8 | Hz
2.4586 | 82.61 | 517.8487 | 1.5754 | 10.4626 | 0.076 | [8 empty] | 41.7967 | 1404.3702 | 1839.6088 | 5.5963 | 132.0343 | 21.937 | 8.5 | Hz
4.9173 | 165.22 | 600.4587 | 1.8267 | 14.067 | 0.304 | [8 empty] | 44.2554 | 1486.9802 | 1922.2188 | 5.8477 | 144.1589 | 24.594 | 9 | Hz
7.3759 | 247.83 | 683.0687 | 2.078 | 18.2039 | 0.683 | [8 empty] | 46.714 | 1569.5902 | 2004.8288 | 6.099 | 156.8161 | 27.402 | 9.5 | Hz
9.8345 | 330.44 | 765.6787 | 2.3293 | 22.8733 | 1.215 | [8 empty] | 49.1726 | 1652.2002 | 2087.4388 | 6.3503 | 170.0057 | 30.363 | 10 | Hz
12.2932 | 413.05 | 848.2887 | 2.5806 | 28.0752 | 1.898 | [8 empty] | 51.6313 | 1734.8102 | 2170.0489 | 6.6016 | 183.7278 | 33.475 | 10.5 | Hz
14.7518 | 495.6601 | 930.8987 | 2.8319 | 33.8097 | 2.733 | [8 empty] | 54.0899 | 1817.4202 | 2252.6589 | 6.8529 | 197.9825 | 36.739 | 11 | Hz
17.2104 | 578.2701 | 1013.5087 | 3.0832 | 40.0766 | 3.719 | [8 empty] | 56.5485 | 1900.0302 | 2335.2689 | 7.1042 | 212.7697 | 40.155 | 11.5 | Hz
19.669 | 660.8801 | 1096.1187 | 3.3345 | 46.8761 | 4.858 | [8 empty] | 59.0071 | 1982.6402 | 2417.8789 | 7.3555 | 228.0894 | 43.722 | 12 | Hz
22.1277 | 743.4901 | 1178.7287 | 3.5859 | 54.208 | 6.148
24.5863 | 826.1001 | 1261.3387 | 3.8372 | 62.0725 | 7.591
27.0449 | 908.7101 | 1343.9488 | 4.0885 | 70.4695 | 9.185 | 5.5 | Hz | [6 empty] | Power Curves @ Te 12 |  |  |  |  | Power Curve @ Te 12
29.5036 | 991.3201 | 1426.5588 | 4.3398 | 79.399 | 10.931 | [8 empty] | Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW)
31.9622 | 1073.9301 | 1509.1688 | 4.5911 | 88.8611 | 12.828 | [8 empty] | 0 | 0 | 435.2386 | 1.3184 | 6.1576 | 0 | 0 | Hz
34.4208 | 1156.5401 | 1591.7788 | 4.8424 | 98.8556 | 14.878 | [8 empty] | 2.4586 | 82.61 | 517.8487 | 1.5687 | 8.717 | 0.033 | 0.5 | Hz
36.8795 | 1239.1502 | 1674.3888 | 5.0937 | 109.3827 | 17.079 | [8 empty] | 4.9173 | 165.22 | 600.4587 | 1.8189 | 11.72 | 0.13 | 1 | Hz
39.3381 | 1321.7602 | 1756.9988 | 5.345 | 120.4423 | 19.432 | [8 empty] | 7.3759 | 247.83 | 683.0687 | 2.0692 | 15.1666 | 0.293 | 1.5 | Hz
41.7967 | 1404.3702 | 1839.6088 | 5.5963 | 132.0343 | 21.937 | [8 empty] | 9.8345 | 330.44 | 765.6787 | 2.3194 | 19.0569 | 0.521 | 2 | Hz
44.2554 | 1486.9802 | 1922.2188 | 5.8477 | 144.1589 | 24.594 | [8 empty] | 12.2932 | 413.05 | 848.2887 | 2.5696 | 23.3909 | 0.815 | 2.5 | Hz
46.714 | 1569.5902 | 2004.8288 | 6.099 | 156.8161 | 27.402 | [8 empty] | 14.7518 | 495.6601 | 930.8987 | 2.8199 | 28.1686 | 1.173 | 3 | Hz
49.1726 | 1652.2002 | 2087.4388 | 6.3503 | 170.0057 | 30.363 | [8 empty] | 17.2104 | 578.2701 | 1013.5087 | 3.0701 | 33.3899 | 1.597 | 3.5 | Hz
51.6313 | 1734.8102 | 2170.0489 | 6.6016 | 183.7278 | 33.475 | [8 empty] | 19.669 | 660.8801 | 1096.1187 | 3.3204 | 39.0548 | 2.086 | 4 | Hz
54.0899 | 1817.4202 | 2252.6589 | 6.8529 | 197.9825 | 36.739 | [8 empty] | 22.1277 | 743.4901 | 1178.7287 | 3.5706 | 45.1635 | 2.64 | 4.5 | Hz
56.5485 | 1900.0302 | 2335.2689 | 7.1042 | 212.7697 | 40.155 | [8 empty] | 24.5863 | 826.1001 | 1261.3387 | 3.8209 | 51.7158 | 3.259 | 5 | Hz
59.0071 | 1982.6402 | 2417.8789 | 7.3555 | 228.0894 | 43.722 | [8 empty] | 27.0449 | 908.7101 | 1343.9488 | 4.0711 | 58.7118 | 3.943 | 5.5 | Hz
0 | 0 | 435.2386 | 1.3241 | 7.3908 | [9 empty] | 29.5036 | 991.3201 | 1426.5588 | 4.3213 | 66.1514 | 4.693 | 6 | Hz
[14 empty] | 31.9622 | 1073.9301 | 1509.1688 | 4.5716 | 74.0347 | 5.508 | 6.5 | Hz
Power Curves @ Te 12 |  |  |  |  | Power Curve @ Te 12 | [8 empty] | 34.4208 | 1156.5401 | 1591.7788 | 4.8218 | 82.3617 | 6.388 | 7 | Hz
Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW) | [8 empty] | 36.8795 | 1239.1502 | 1674.3888 | 5.0721 | 91.1323 | 7.333 | 7.5 | Hz
0 | 0 | 435.2386 | 1.3184 | 6.1576 | 0 | [8 empty] | 39.3381 | 1321.7602 | 1756.9988 | 5.3223 | 100.3466 | 8.343 | 8 | Hz
2.4586 | 82.61 | 517.8487 | 1.5687 | 8.717 | 0.033 | [8 empty] | 41.7967 | 1404.3702 | 1839.6088 | 5.5726 | 110.0045 | 9.418 | 8.5 | Hz
4.9173 | 165.22 | 600.4587 | 1.8189 | 11.72 | 0.13 | [8 empty] | 44.2554 | 1486.9802 | 1922.2188 | 5.8228 | 120.1062 | 10.559 | 9 | Hz
7.3759 | 247.83 | 683.0687 | 2.0692 | 15.1666 | 0.293 | [8 empty] | 46.714 | 1569.5902 | 2004.8288 | 6.073 | 130.6515 | 11.765 | 9.5 | Hz
9.8345 | 330.44 | 765.6787 | 2.3194 | 19.0569 | 0.521 | [8 empty] | 49.1726 | 1652.2002 | 2087.4388 | 6.3233 | 141.6404 | 13.036 | 10 | Hz
12.2932 | 413.05 | 848.2887 | 2.5696 | 23.3909 | 0.815 | [8 empty] | 51.6313 | 1734.8102 | 2170.0489 | 6.5735 | 153.073 | 14.372 | 10.5 | Hz
14.7518 | 495.6601 | 930.8987 | 2.8199 | 28.1686 | 1.173 | [8 empty] | 54.0899 | 1817.4202 | 2252.6589 | 6.8238 | 164.9493 | 15.773 | 11 | Hz
17.2104 | 578.2701 | 1013.5087 | 3.0701 | 33.3899 | 1.597 | [8 empty] | 56.5485 | 1900.0302 | 2335.2689 | 7.074 | 177.2693 | 17.24 | 11.5 | Hz
19.669 | 660.8801 | 1096.1187 | 3.3204 | 39.0548 | 2.086 | [8 empty] | 59.0071 | 1982.6402 | 2417.8789 | 7.3243 | 190.0329 | 18.772 | 12 | Hz
22.1277 | 743.4901 | 1178.7287 | 3.5706 | 45.1635 | 2.64
24.5863 | 826.1001 | 1261.3387 | 3.8209 | 51.7158 | 3.259
27.0449 | 908.7101 | 1343.9488 | 4.0711 | 58.7118 | 3.943 | 5.5 | Hz | [6 empty] | Power Curves @ Te 13 |  |  |  |  | Power Curve @ Te 13
29.5036 | 991.3201 | 1426.5588 | 4.3213 | 66.1514 | 4.693 | [8 empty] | Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW)
31.9622 | 1073.9301 | 1509.1688 | 4.5716 | 74.0347 | 5.508 | [8 empty] | 0 | 0 | 435.2386 | 1.3144 | 5.2148 | 0 | 0 | Hz
34.4208 | 1156.5401 | 1591.7788 | 4.8218 | 82.3617 | 6.388 | [8 empty] | 2.4586 | 82.61 | 517.8487 | 1.5639 | 7.3823 | 0.015 | 0.5 | Hz
36.8795 | 1239.1502 | 1674.3888 | 5.0721 | 91.1323 | 7.333 | [8 empty] | 4.9173 | 165.22 | 600.4587 | 1.8134 | 9.9255 | 0.059 | 1 | Hz
39.3381 | 1321.7602 | 1756.9988 | 5.3223 | 100.3466 | 8.343 | [8 empty] | 7.3759 | 247.83 | 683.0687 | 2.0629 | 12.8444 | 0.134 | 1.5 | Hz
41.7967 | 1404.3702 | 1839.6088 | 5.5726 | 110.0045 | 9.418 | [8 empty] | 9.8345 | 330.44 | 765.6787 | 2.3123 | 16.1391 | 0.238 | 2 | Hz
44.2554 | 1486.9802 | 1922.2188 | 5.8228 | 120.1062 | 10.559 | [8 empty] | 12.2932 | 413.05 | 848.2887 | 2.5618 | 19.8095 | 0.372 | 2.5 | Hz
46.714 | 1569.5902 | 2004.8288 | 6.073 | 130.6515 | 11.765 | [8 empty] | 14.7518 | 495.6601 | 930.8987 | 2.8113 | 23.8557 | 0.535 | 3 | Hz
49.1726 | 1652.2002 | 2087.4388 | 6.3233 | 141.6404 | 13.036 | [8 empty] | 17.2104 | 578.2701 | 1013.5087 | 3.0608 | 28.2775 | 0.728 | 3.5 | Hz
51.6313 | 1734.8102 | 2170.0489 | 6.5735 | 153.073 | 14.372 | [8 empty] | 19.669 | 660.8801 | 1096.1187 | 3.3103 | 33.0751 | 0.951 | 4 | Hz
54.0899 | 1817.4202 | 2252.6589 | 6.8238 | 164.9493 | 15.773 | [8 empty] | 22.1277 | 743.4901 | 1178.7287 | 3.5597 | 38.2485 | 1.204 | 4.5 | Hz
56.5485 | 1900.0302 | 2335.2689 | 7.074 | 177.2693 | 17.24 | [8 empty] | 24.5863 | 826.1001 | 1261.3387 | 3.8092 | 43.7976 | 1.487 | 5 | Hz
59.0071 | 1982.6402 | 2417.8789 | 7.3243 | 190.0329 | 18.772 | [8 empty] | 27.0449 | 908.7101 | 1343.9488 | 4.0587 | 49.7224 | 1.799 | 5.5 | Hz
0 | 0 | 435.2386 | 1.3184 | 6.1576 | [9 empty] | 29.5036 | 991.3201 | 1426.5588 | 4.3082 | 56.0229 | 2.141 | 6 | Hz
[14 empty] | 31.9622 | 1073.9301 | 1509.1688 | 4.5577 | 62.6992 | 2.512 | 6.5 | Hz
Power Curves @ Te 13 |  |  |  |  | Power Curve @ Te 13 | [8 empty] | 34.4208 | 1156.5401 | 1591.7788 | 4.8071 | 69.7513 | 2.914 | 7 | Hz
Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW) | [8 empty] | 36.8795 | 1239.1502 | 1674.3888 | 5.0566 | 77.179 | 3.345 | 7.5 | Hz
0 | 0 | 435.2386 | 1.3144 | 5.2148 | 0 | [8 empty] | 39.3381 | 1321.7602 | 1756.9988 | 5.3061 | 84.9825 | 3.805 | 8 | Hz
2.4586 | 82.61 | 517.8487 | 1.5639 | 7.3823 | 0.015 | [8 empty] | 41.7967 | 1404.3702 | 1839.6088 | 5.5556 | 93.1617 | 4.296 | 8.5 | Hz
4.9173 | 165.22 | 600.4587 | 1.8134 | 9.9255 | 0.059 | [8 empty] | 44.2554 | 1486.9802 | 1922.2188 | 5.8051 | 101.7167 | 4.816 | 9 | Hz
7.3759 | 247.83 | 683.0687 | 2.0629 | 12.8444 | 0.134 | [8 empty] | 46.714 | 1569.5902 | 2004.8288 | 6.0546 | 110.6474 | 5.366 | 9.5 | Hz
9.8345 | 330.44 | 765.6787 | 2.3123 | 16.1391 | 0.238 | [8 empty] | 49.1726 | 1652.2002 | 2087.4388 | 6.304 | 119.9538 | 5.946 | 10 | Hz
12.2932 | 413.05 | 848.2887 | 2.5618 | 19.8095 | 0.372 | [8 empty] | 51.6313 | 1734.8102 | 2170.0489 | 6.5535 | 129.636 | 6.555 | 10.5 | Hz
14.7518 | 495.6601 | 930.8987 | 2.8113 | 23.8557 | 0.535 | [8 empty] | 54.0899 | 1817.4202 | 2252.6589 | 6.803 | 139.6939 | 7.195 | 11 | Hz
17.2104 | 578.2701 | 1013.5087 | 3.0608 | 28.2775 | 0.728 | [8 empty] | 56.5485 | 1900.0302 | 2335.2689 | 7.0525 | 150.1276 | 7.864 | 11.5 | Hz
19.669 | 660.8801 | 1096.1187 | 3.3103 | 33.0751 | 0.951 | [8 empty] | 59.0071 | 1982.6402 | 2417.8789 | 7.302 | 160.9369 | 8.562 | 12 | Hz
22.1277 | 743.4901 | 1178.7287 | 3.5597 | 38.2485 | 1.204
24.5863 | 826.1001 | 1261.3387 | 3.8092 | 43.7976 | 1.487
27.0449 | 908.7101 | 1343.9488 | 4.0587 | 49.7224 | 1.799 | 5.5 | Hz | [6 empty] | Power Curves @ Te 14 |  |  |  |  | Power Curve @ Te 14
29.5036 | 991.3201 | 1426.5588 | 4.3082 | 56.0229 | 2.141 | [8 empty] | Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW)
31.9622 | 1073.9301 | 1509.1688 | 4.5577 | 62.6992 | 2.512 | [8 empty] | 0 | 0 | 435.2386 | 1.3115 | 4.4766 | 0 | 0 | Hz
34.4208 | 1156.5401 | 1591.7788 | 4.8071 | 69.7513 | 2.914 | [8 empty] | 2.4586 | 82.61 | 517.8487 | 1.5604 | 6.3372 | 0.007 | 0.5 | Hz
36.8795 | 1239.1502 | 1674.3888 | 5.0566 | 77.179 | 3.345 | [8 empty] | 4.9173 | 165.22 | 600.4587 | 1.8094 | 8.5204 | 0.029 | 1 | Hz
39.3381 | 1321.7602 | 1756.9988 | 5.3061 | 84.9825 | 3.805 | [8 empty] | 7.3759 | 247.83 | 683.0687 | 2.0583 | 11.0261 | 0.064 | 1.5 | Hz
41.7967 | 1404.3702 | 1839.6088 | 5.5556 | 93.1617 | 4.296 | [8 empty] | 9.8345 | 330.44 | 765.6787 | 2.3072 | 13.8544 | 0.114 | 2 | Hz
44.2554 | 1486.9802 | 1922.2188 | 5.8051 | 101.7167 | 4.816 | [8 empty] | 12.2932 | 413.05 | 848.2887 | 2.5562 | 17.0052 | 0.179 | 2.5 | Hz
46.714 | 1569.5902 | 2004.8288 | 6.0546 | 110.6474 | 5.366 | [8 empty] | 14.7518 | 495.6601 | 930.8987 | 2.8051 | 20.4786 | 0.258 | 3 | Hz
49.1726 | 1652.2002 | 2087.4388 | 6.304 | 119.9538 | 5.946 | [8 empty] | 17.2104 | 578.2701 | 1013.5087 | 3.054 | 24.2745 | 0.351 | 3.5 | Hz
51.6313 | 1734.8102 | 2170.0489 | 6.5535 | 129.636 | 6.555 | [8 empty] | 19.669 | 660.8801 | 1096.1187 | 3.3029 | 28.3929 | 0.458 | 4 | Hz
54.0899 | 1817.4202 | 2252.6589 | 6.803 | 139.6939 | 7.195 | [8 empty] | 22.1277 | 743.4901 | 1178.7287 | 3.5519 | 32.8339 | 0.58 | 4.5 | Hz
56.5485 | 1900.0302 | 2335.2689 | 7.0525 | 150.1276 | 7.864 | [8 empty] | 24.5863 | 826.1001 | 1261.3387 | 3.8008 | 37.5974 | 0.716 | 5 | Hz
59.0071 | 1982.6402 | 2417.8789 | 7.302 | 160.9369 | 8.562 | [8 empty] | 27.0449 | 908.7101 | 1343.9488 | 4.0497 | 42.6835 | 0.866 | 5.5 | Hz
0 | 0 | 435.2386 | 1.3144 | 5.2148 | [9 empty] | 29.5036 | 991.3201 | 1426.5588 | 4.2987 | 48.0921 | 1.03 | 6 | Hz
[14 empty] | 31.9622 | 1073.9301 | 1509.1688 | 4.5476 | 53.8233 | 1.209 | 6.5 | Hz
Power Curves @ Te 14 |  |  |  |  | Power Curve @ Te 14 | [8 empty] | 34.4208 | 1156.5401 | 1591.7788 | 4.7965 | 59.877 | 1.403 | 7 | Hz
Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW) | [8 empty] | 36.8795 | 1239.1502 | 1674.3888 | 5.0455 | 66.2533 | 1.61 | 7.5 | Hz
0 | 0 | 435.2386 | 1.3115 | 4.4766 | 0 | [8 empty] | 39.3381 | 1321.7602 | 1756.9988 | 5.2944 | 72.9521 | 1.832 | 8 | Hz
2.4586 | 82.61 | 517.8487 | 1.5604 | 6.3372 | 0.007 | [8 empty] | 41.7967 | 1404.3702 | 1839.6088 | 5.5433 | 79.9734 | 2.068 | 8.5 | Hz
4.9173 | 165.22 | 600.4587 | 1.8094 | 8.5204 | 0.029 | [8 empty] | 44.2554 | 1486.9802 | 1922.2188 | 5.7922 | 87.3173 | 2.319 | 9 | Hz
7.3759 | 247.83 | 683.0687 | 2.0583 | 11.0261 | 0.064 | [8 empty] | 46.714 | 1569.5902 | 2004.8288 | 6.0412 | 94.9837 | 2.583 | 9.5 | Hz
9.8345 | 330.44 | 765.6787 | 2.3072 | 13.8544 | 0.114 | [8 empty] | 49.1726 | 1652.2002 | 2087.4388 | 6.2901 | 102.9727 | 2.862 | 10 | Hz
12.2932 | 413.05 | 848.2887 | 2.5562 | 17.0052 | 0.179 | [8 empty] | 51.6313 | 1734.8102 | 2170.0489 | 6.539 | 111.2842 | 3.156 | 10.5 | Hz
14.7518 | 495.6601 | 930.8987 | 2.8051 | 20.4786 | 0.258 | [8 empty] | 54.0899 | 1817.4202 | 2252.6589 | 6.788 | 119.9183 | 3.464 | 11 | Hz
17.2104 | 578.2701 | 1013.5087 | 3.054 | 24.2745 | 0.351 | [8 empty] | 56.5485 | 1900.0302 | 2335.2689 | 7.0369 | 128.8749 | 3.786 | 11.5 | Hz
19.669 | 660.8801 | 1096.1187 | 3.3029 | 28.3929 | 0.458 | [8 empty] | 59.0071 | 1982.6402 | 2417.8789 | 7.2858 | 138.1541 | 4.122 | 12 | Hz
22.1277 | 743.4901 | 1178.7287 | 3.5519 | 32.8339 | 0.58
24.5863 | 826.1001 | 1261.3387 | 3.8008 | 37.5974 | 0.716
27.0449 | 908.7101 | 1343.9488 | 4.0497 | 42.6835 | 0.866 | 5.5 | Hz | [6 empty] | Power Curves @ Te 15 |  |  |  |  | Power Curve @ Te 15
29.5036 | 991.3201 | 1426.5588 | 4.2987 | 48.0921 | 1.03 | [8 empty] | Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW)
31.9622 | 1073.9301 | 1509.1688 | 4.5476 | 53.8233 | 1.209 | [8 empty] | 0 | 0 | 435.2386 | 1.3094 | 3.887 | 0 | 0 | Hz
34.4208 | 1156.5401 | 1591.7788 | 4.7965 | 59.877 | 1.403 | [8 empty] | 2.4586 | 82.61 | 517.8487 | 1.5579 | 5.5026 | 0.004 | 0.5 | Hz
36.8795 | 1239.1502 | 1674.3888 | 5.0455 | 66.2533 | 1.61 | [8 empty] | 4.9173 | 165.22 | 600.4587 | 1.8064 | 7.3982 | 0.014 | 1 | Hz
39.3381 | 1321.7602 | 1756.9988 | 5.2944 | 72.9521 | 1.832 | [8 empty] | 7.3759 | 247.83 | 683.0687 | 2.055 | 9.5739 | 0.033 | 1.5 | Hz
41.7967 | 1404.3702 | 1839.6088 | 5.5433 | 79.9734 | 2.068 | [8 empty] | 9.8345 | 330.44 | 765.6787 | 2.3035 | 12.0297 | 0.058 | 2 | Hz
44.2554 | 1486.9802 | 1922.2188 | 5.7922 | 87.3173 | 2.319 | [8 empty] | 12.2932 | 413.05 | 848.2887 | 2.552 | 14.7655 | 0.09 | 2.5 | Hz
46.714 | 1569.5902 | 2004.8288 | 6.0412 | 94.9837 | 2.583 | [8 empty] | 14.7518 | 495.6601 | 930.8987 | 2.8005 | 17.7814 | 0.13 | 3 | Hz
49.1726 | 1652.2002 | 2087.4388 | 6.2901 | 102.9727 | 2.862 | [8 empty] | 17.2104 | 578.2701 | 1013.5087 | 3.0491 | 21.0773 | 0.177 | 3.5 | Hz
51.6313 | 1734.8102 | 2170.0489 | 6.539 | 111.2842 | 3.156 | [8 empty] | 19.669 | 660.8801 | 1096.1187 | 3.2976 | 24.6533 | 0.231 | 4 | Hz
54.0899 | 1817.4202 | 2252.6589 | 6.788 | 119.9183 | 3.464 | [8 empty] | 22.1277 | 743.4901 | 1178.7287 | 3.5461 | 28.5094 | 0.293 | 4.5 | Hz
56.5485 | 1900.0302 | 2335.2689 | 7.0369 | 128.8749 | 3.786 | [8 empty] | 24.5863 | 826.1001 | 1261.3387 | 3.7946 | 32.6455 | 0.361 | 5 | Hz
59.0071 | 1982.6402 | 2417.8789 | 7.2858 | 138.1541 | 4.122 | [8 empty] | 27.0449 | 908.7101 | 1343.9488 | 4.0432 | 37.0617 | 0.437 | 5.5 | Hz
0 | 0 | 435.2386 | 1.3115 | 4.4766 | [9 empty] | 29.5036 | 991.3201 | 1426.5588 | 4.2917 | 41.758 | 0.52 | 6 | Hz
[14 empty] | 31.9622 | 1073.9301 | 1509.1688 | 4.5402 | 46.7343 | 0.611 | 6.5 | Hz
Power Curves @ Te 15 |  |  |  |  | Power Curve @ Te 15 | [8 empty] | 34.4208 | 1156.5401 | 1591.7788 | 4.7888 | 51.9907 | 0.708 | 7 | Hz
Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW) | [8 empty] | 36.8795 | 1239.1502 | 1674.3888 | 5.0373 | 57.5271 | 0.813 | 7.5 | Hz
0 | 0 | 435.2386 | 1.3094 | 3.887 | 0 | [8 empty] | 39.3381 | 1321.7602 | 1756.9988 | 5.2858 | 63.3436 | 0.925 | 8 | Hz
2.4586 | 82.61 | 517.8487 | 1.5579 | 5.5026 | 0.004 | [8 empty] | 41.7967 | 1404.3702 | 1839.6088 | 5.5343 | 69.4402 | 1.044 | 8.5 | Hz
4.9173 | 165.22 | 600.4587 | 1.8064 | 7.3982 | 0.014 | [8 empty] | 44.2554 | 1486.9802 | 1922.2188 | 5.7829 | 75.8168 | 1.171 | 9 | Hz
7.3759 | 247.83 | 683.0687 | 2.055 | 9.5739 | 0.033 | [8 empty] | 46.714 | 1569.5902 | 2004.8288 | 6.0314 | 82.4735 | 1.304 | 9.5 | Hz
9.8345 | 330.44 | 765.6787 | 2.3035 | 12.0297 | 0.058 | [8 empty] | 49.1726 | 1652.2002 | 2087.4388 | 6.2799 | 89.4103 | 1.445 | 10 | Hz
12.2932 | 413.05 | 848.2887 | 2.552 | 14.7655 | 0.09 | [8 empty] | 51.6313 | 1734.8102 | 2170.0489 | 6.5284 | 96.6271 | 1.593 | 10.5 | Hz
14.7518 | 495.6601 | 930.8987 | 2.8005 | 17.7814 | 0.13 | [8 empty] | 54.0899 | 1817.4202 | 2252.6589 | 6.777 | 104.124 | 1.749 | 11 | Hz
17.2104 | 578.2701 | 1013.5087 | 3.0491 | 21.0773 | 0.177 | [8 empty] | 56.5485 | 1900.0302 | 2335.2689 | 7.0255 | 111.9009 | 1.911 | 11.5 | Hz
19.669 | 660.8801 | 1096.1187 | 3.2976 | 24.6533 | 0.231 | [8 empty] | 59.0071 | 1982.6402 | 2417.8789 | 7.274 | 119.9579 | 2.081 | 12 | Hz
22.1277 | 743.4901 | 1178.7287 | 3.5461 | 28.5094 | 0.293
24.5863 | 826.1001 | 1261.3387 | 3.7946 | 32.6455 | 0.361
27.0449 | 908.7101 | 1343.9488 | 4.0432 | 37.0617 | 0.437 | 5.5 | Hz | [6 empty] | Power Curves @ Te 16 |  |  |  |  | Power Curve @ Te 16
29.5036 | 991.3201 | 1426.5588 | 4.2917 | 41.758 | 0.52 | [8 empty] | Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW)
31.9622 | 1073.9301 | 1509.1688 | 4.5402 | 46.7343 | 0.611 | [8 empty] | 0 | 0 | 435.2386 | 1.3078 | 3.4082 | 0 | 0 | Hz
34.4208 | 1156.5401 | 1591.7788 | 4.7888 | 51.9907 | 0.708 | [8 empty] | 2.4586 | 82.61 | 517.8487 | 1.5561 | 4.8247 | 0.002 | 0.5 | Hz
36.8795 | 1239.1502 | 1674.3888 | 5.0373 | 57.5271 | 0.813 | [8 empty] | 4.9173 | 165.22 | 600.4587 | 1.8043 | 6.4868 | 0.008 | 1 | Hz
39.3381 | 1321.7602 | 1756.9988 | 5.2858 | 63.3436 | 0.925 | [8 empty] | 7.3759 | 247.83 | 683.0687 | 2.0525 | 8.3945 | 0.017 | 1.5 | Hz
41.7967 | 1404.3702 | 1839.6088 | 5.5343 | 69.4402 | 1.044 | [8 empty] | 9.8345 | 330.44 | 765.6787 | 2.3007 | 10.5477 | 0.03 | 2 | Hz
44.2554 | 1486.9802 | 1922.2188 | 5.7829 | 75.8168 | 1.171 | [8 empty] | 12.2932 | 413.05 | 848.2887 | 2.549 | 12.9465 | 0.048 | 2.5 | Hz
46.714 | 1569.5902 | 2004.8288 | 6.0314 | 82.4735 | 1.304 | [8 empty] | 14.7518 | 495.6601 | 930.8987 | 2.7972 | 15.5909 | 0.069 | 3 | Hz
49.1726 | 1652.2002 | 2087.4388 | 6.2799 | 89.4103 | 1.445 | [8 empty] | 17.2104 | 578.2701 | 1013.5087 | 3.0454 | 18.4808 | 0.093 | 3.5 | Hz
51.6313 | 1734.8102 | 2170.0489 | 6.5284 | 96.6271 | 1.593 | [8 empty] | 19.669 | 660.8801 | 1096.1187 | 3.2937 | 21.6163 | 0.122 | 4 | Hz
54.0899 | 1817.4202 | 2252.6589 | 6.777 | 104.124 | 1.749 | [8 empty] | 22.1277 | 743.4901 | 1178.7287 | 3.5419 | 24.9973 | 0.1154 | 4.5 | Hz
56.5485 | 1900.0302 | 2335.2689 | 7.0255 | 111.9009 | 1.911 | [8 empty] | 24.5863 | 826.1001 | 1261.3387 | 3.7901 | 28.6239 | 0.19 | 5 | Hz
59.0071 | 1982.6402 | 2417.8789 | 7.274 | 119.9579 | 2.081 | [8 empty] | 27.0449 | 908.7101 | 1343.9488 | 4.0383 | 32.4961 | 0.23 | 5.5 | Hz
0 | 0 | 435.2386 | 1.3094 | 3.887 | [9 empty] | 29.5036 | 991.3201 | 1426.5588 | 4.2866 | 36.6138 | 0.274 | 6 | Hz
[14 empty] | 31.9622 | 1073.9301 | 1509.1688 | 4.5348 | 40.9771 | 0.322 | 6.5 | Hz
Power Curves @ Te 16 |  |  |  |  | Power Curve @ Te 16 | [8 empty] | 34.4208 | 1156.5401 | 1591.7788 | 4.783 | 45.586 | 0.373 | 7 | Hz
Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW) | [8 empty] | 36.8795 | 1239.1502 | 1674.3888 | 5.0313 | 50.4404 | 0.428 | 7.5 | Hz
0 | 0 | 435.2386 | 1.3078 | 3.4082 | 0 | [8 empty] | 39.3381 | 1321.7602 | 1756.9988 | 5.2795 | 55.5404 | 0.487 | 8 | Hz
2.4586 | 82.61 | 517.8487 | 1.5561 | 4.8247 | 0.002 | [8 empty] | 41.7967 | 1404.3702 | 1839.6088 | 5.5277 | 60.8859 | 0.55 | 8.5 | Hz
4.9173 | 165.22 | 600.4587 | 1.8043 | 6.4868 | 0.008 | [8 empty] | 44.2554 | 1486.9802 | 1922.2188 | 5.776 | 66.477 | 0.617 | 9 | Hz
7.3759 | 247.83 | 683.0687 | 2.0525 | 8.3945 | 0.017 | [8 empty] | 46.714 | 1569.5902 | 2004.8288 | 6.0242 | 72.3137 | 0.687 | 9.5 | Hz
9.8345 | 330.44 | 765.6787 | 2.3007 | 10.5477 | 0.03 | [8 empty] | 49.1726 | 1652.2002 | 2087.4388 | 6.2724 | 78.3959 | 0.761 | 10 | Hz
12.2932 | 413.05 | 848.2887 | 2.549 | 12.9465 | 0.048 | [8 empty] | 51.6313 | 1734.8102 | 2170.0489 | 6.5206 | 84.7237 | 0.839 | 10.5 | Hz
14.7518 | 495.6601 | 930.8987 | 2.7972 | 15.5909 | 0.069 | [8 empty] | 54.0899 | 1817.4202 | 2252.6589 | 6.7689 | 91.297 | 0.921 | 11 | Hz
17.2104 | 578.2701 | 1013.5087 | 3.0454 | 18.4808 | 0.093 | [8 empty] | 56.5485 | 1900.0302 | 2335.2689 | 7.0171 | 98.1159 | 1.007 | 11.5 | Hz
19.669 | 660.8801 | 1096.1187 | 3.2937 | 21.6163 | 0.122 | [8 empty] | 59.0071 | 1982.6402 | 2417.8789 | 7.2653 | 105.1804 | 1.096 | 12 | Hz
22.1277 | 743.4901 | 1178.7287 | 3.5419 | 24.9973 | 1.154
24.5863 | 826.1001 | 1261.3387 | 3.7901 | 28.6239 | 0.19
27.0449 | 908.7101 | 1343.9488 | 4.0383 | 32.4961 | 0.23 | 5.5 | Hz | [6 empty] | Power Curves @ Te 17 |  |  |  |  | Power Curve @ Te 17
29.5036 | 991.3201 | 1426.5588 | 4.2866 | 36.6138 | 0.274 | [8 empty] | Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW)
31.9622 | 1073.9301 | 1509.1688 | 4.5348 | 40.9771 | 0.322 | [8 empty] | 0 | 0 | 435.2386 | 1.3067 | 3.0137 | 0 | 0 | Hz
34.4208 | 1156.5401 | 1591.7788 | 4.783 | 45.586 | 0.373 | [8 empty] | 2.4586 | 82.61 | 517.8487 | 1.5547 | 4.2663 | 0.001 | 0.5 | Hz
36.8795 | 1239.1502 | 1674.3888 | 5.0313 | 50.4404 | 0.428 | [8 empty] | 4.9173 | 165.22 | 600.4587 | 1.8027 | 5.736 | 0.004 | 1 | Hz
39.3381 | 1321.7602 | 1756.9988 | 5.2795 | 55.5404 | 0.487 | [8 empty] | 7.3759 | 247.83 | 683.0687 | 2.0507 | 7.4229 | 0.009 | 1.5 | Hz
41.7967 | 1404.3702 | 1839.6088 | 5.5277 | 60.8859 | 0.55 | [8 empty] | 9.8345 | 330.44 | 765.6787 | 2.2987 | 9.3269 | 0.017 | 2 | Hz
44.2554 | 1486.9802 | 1922.2188 | 5.776 | 66.477 | 0.617 | [8 empty] | 12.2932 | 413.05 | 848.2887 | 2.5467 | 11.4481 | 0.026 | 2.5 | Hz
46.714 | 1569.5902 | 2004.8288 | 6.0242 | 72.3137 | 0.687 | [8 empty] | 14.7518 | 495.6601 | 930.8987 | 2.7947 | 13.7863 | 0.037 | 3 | Hz
49.1726 | 1652.2002 | 2087.4388 | 6.2724 | 78.3959 | 0.761 | [8 empty] | 17.2104 | 578.2701 | 1013.5087 | 3.0428 | 16.3418 | 0.051 | 3.5 | Hz
51.6313 | 1734.8102 | 2170.0489 | 6.5206 | 84.7237 | 0.839 | [8 empty] | 19.669 | 660.8801 | 1096.1187 | 3.2908 | 19.1143 | 0.067 | 4 | Hz
54.0899 | 1817.4202 | 2252.6589 | 6.7689 | 91.297 | 0.921 | [8 empty] | 22.1277 | 743.4901 | 1178.7287 | 3.5388 | 22.1041 | 0.084 | 4.5 | Hz
56.5485 | 1900.0302 | 2335.2689 | 7.0171 | 98.1159 | 1.007 | [8 empty] | 24.5863 | 826.1001 | 1261.3387 | 3.7868 | 25.3109 | 0.104 | 5 | Hz
59.0071 | 1982.6402 | 2417.8789 | 7.2653 | 105.1804 | 1.096 | [8 empty] | 27.0449 | 908.7101 | 1343.9488 | 4.0348 | 28.7349 | 0.126 | 5.5 | Hz
0 | 0 | 435.2386 | 1.3078 | 3.4082 | [9 empty] | 29.5036 | 991.3201 | 1426.5588 | 4.2828 | 32.376 | 0.15 | 6 | Hz
[14 empty] | 31.9622 | 1073.9301 | 1509.1688 | 4.5308 | 36.2343 | 0.176 | 6.5 | Hz
Power Curves @ Te 17 |  |  |  |  | Power Curve @ Te 17 | [8 empty] | 34.4208 | 1156.5401 | 1591.7788 | 4.7788 | 40.3097 | 0.204 | 7 | Hz
Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW) | [8 empty] | 36.8795 | 1239.1502 | 1674.3888 | 5.0268 | 44.6023 | 0.234 | 7.5 | Hz
0 | 0 | 435.2386 | 1.3067 | 3.0137 | 0 | [8 empty] | 39.3381 | 1321.7602 | 1756.9988 | 5.2749 | 49.1119 | 0.267 | 8 | Hz
2.4586 | 82.61 | 517.8487 | 1.5547 | 4.2663 | 0.001 | [8 empty] | 41.7967 | 1404.3702 | 1839.6088 | 5.5229 | 53.8388 | 0.301 | 8.5 | Hz
4.9173 | 165.22 | 600.4587 | 1.8027 | 5.736 | 0.004 | [8 empty] | 44.2554 | 1486.9802 | 1922.2188 | 5.7709 | 58.7827 | 0.337 | 9 | Hz
7.3759 | 247.83 | 683.0687 | 2.0507 | 7.4229 | 0.009 | [8 empty] | 46.714 | 1569.5902 | 2004.8288 | 6.0189 | 63.9438 | 0.376 | 9.5 | Hz
9.8345 | 330.44 | 765.6787 | 2.2987 | 9.3269 | 0.017 | [8 empty] | 49.1726 | 1652.2002 | 2087.4388 | 6.2669 | 69.3221 | 0.416 | 10 | Hz
12.2932 | 413.05 | 848.2887 | 2.5467 | 11.4481 | 0.026 | [8 empty] | 51.6313 | 1734.8102 | 2170.0489 | 6.5149 | 74.9175 | 0.459 | 10.5 | Hz
14.7518 | 495.6601 | 930.8987 | 2.7947 | 13.7863 | 0.037 | [8 empty] | 54.0899 | 1817.4202 | 2252.6589 | 6.7629 | 80.73 | 0.504 | 11 | Hz
17.2104 | 578.2701 | 1013.5087 | 3.0428 | 16.3418 | 0.051 | [8 empty] | 56.5485 | 1900.0302 | 2335.2689 | 7.0109 | 86.7597 | 0.551 | 11.5 | Hz
19.669 | 660.8801 | 1096.1187 | 3.2908 | 19.1143 | 0.067 | [8 empty] | 59.0071 | 1982.6402 | 2417.8789 | 7.2589 | 93.0065 | 0.6 | 12 | Hz
22.1277 | 743.4901 | 1178.7287 | 3.5388 | 22.1041 | 0.084
24.5863 | 826.1001 | 1261.3387 | 3.7868 | 25.3109 | 0.104
27.0449 | 908.7101 | 1343.9488 | 4.0348 | 28.7349 | 0.126 | 5.5 | Hz | [6 empty] | Power Curves @ Te 18 |  |  |  |  | Power Curve @ Te 18
29.5036 | 991.3201 | 1426.5588 | 4.2828 | 32.376 | 0.15 | [8 empty] | Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW)
31.9622 | 1073.9301 | 1509.1688 | 4.5308 | 36.2343 | 0.176 | [8 empty] | 0 | 0 | 435.2386 | 1.3058 | 2.6847 | 0 | 0 | Hz
34.4208 | 1156.5401 | 1591.7788 | 4.7788 | 40.3097 | 0.204 | [8 empty] | 2.4586 | 82.61 | 517.8487 | 1.5537 | 3.8005 | 0.0005891 | 0.5 | Hz
36.8795 | 1239.1502 | 1674.3888 | 5.0268 | 44.6023 | 0.234 | [8 empty] | 4.9173 | 165.22 | 600.4587 | 1.8015 | 5.1098 | 0.002 | 1 | Hz
39.3381 | 1321.7602 | 1756.9988 | 5.2749 | 49.1119 | 0.267 | [8 empty] | 7.3759 | 247.83 | 683.0687 | 2.0494 | 6.6125 | 0.005 | 1.5 | Hz
41.7967 | 1404.3702 | 1839.6088 | 5.5229 | 53.8388 | 0.301 | [8 empty] | 9.8345 | 330.44 | 765.6787 | 2.2972 | 8.3086 | 0.009 | 2 | Hz
44.2554 | 1486.9802 | 1922.2188 | 5.7709 | 58.7827 | 0.337 | [8 empty] | 12.2932 | 413.05 | 848.2887 | 2.5451 | 10.1982 | 0.015 | 2.5 | Hz
46.714 | 1569.5902 | 2004.8288 | 6.0189 | 63.9438 | 0.376 | [8 empty] | 14.7518 | 495.6601 | 930.8987 | 2.7929 | 12.2812 | 0.021 | 3 | Hz
49.1726 | 1652.2002 | 2087.4388 | 6.2669 | 69.3221 | 0.416 | [8 empty] | 17.2104 | 578.2701 | 1013.5087 | 3.0408 | 14.5577 | 0.029 | 3.5 | Hz
51.6313 | 1734.8102 | 2170.0489 | 6.5149 | 74.9175 | 0.459 | [8 empty] | 19.669 | 660.8801 | 1096.1187 | 3.2886 | 17.0275 | 0.038 | 4 | Hz
54.0899 | 1817.4202 | 2252.6589 | 6.7629 | 80.73 | 0.504 | [8 empty] | 22.1277 | 743.4901 | 1178.7287 | 3.5365 | 19.6908 | 0.048 | 4.5 | Hz
56.5485 | 1900.0302 | 2335.2689 | 7.0109 | 86.7597 | 0.551 | [8 empty] | 24.5863 | 826.1001 | 1261.3387 | 3.7843 | 22.5476 | 0.059 | 5 | Hz
59.0071 | 1982.6402 | 2417.8789 | 7.2589 | 93.0065 | 0.6 | [8 empty] | 27.0449 | 908.7101 | 1343.9488 | 4.0322 | 25.5978 | 0.071 | 5.5 | Hz
0 | 0 | 435.2386 | 1.3067 | 3.0137 | [9 empty] | 29.5036 | 991.3201 | 1426.5588 | 4.28 | 28.8414 | 0.085 | 6 | Hz
[14 empty] | 31.9622 | 1073.9301 | 1509.1688 | 4.5279 | 32.2784 | 0.1 | 6.5 | Hz
Power Curves @ Te 18 |  |  |  |  | Power Curve @ Te 18 | [8 empty] | 34.4208 | 1156.5401 | 1591.7788 | 4.7758 | 35.9089 | 0.115 | 7 | Hz
Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW) | [8 empty] | 36.8795 | 1239.1502 | 1674.3888 | 5.0236 | 39.7328 | 0.133 | 7.5 | Hz
0 | 0 | 435.2386 | 1.3058 | 2.6847 | 0 | [8 empty] | 39.3381 | 1321.7602 | 1756.9988 | 5.2715 | 43.7502 | 0.151 | 8 | Hz
2.4586 | 82.61 | 517.8487 | 1.5537 | 3.8005 | 0.0005891 | [8 empty] | 41.7967 | 1404.3702 | 1839.6088 | 5.5193 | 47.9609 | 0.17 | 8.5 | Hz
4.9173 | 165.22 | 600.4587 | 1.8015 | 5.1098 | 0.002 | [8 empty] | 44.2554 | 1486.9802 | 1922.2188 | 5.7672 | 52.3651 | 0.191 | 9 | Hz
7.3759 | 247.83 | 683.0687 | 2.0494 | 6.6125 | 0.005 | [8 empty] | 46.714 | 1569.5902 | 2004.8288 | 6.015 | 56.9628 | 0.213 | 9.5 | Hz
9.8345 | 330.44 | 765.6787 | 2.2972 | 8.3086 | 0.009 | [8 empty] | 49.1726 | 1652.2002 | 2087.4388 | 6.2629 | 61.7539 | 0.236 | 10 | Hz
12.2932 | 413.05 | 848.2887 | 2.5451 | 10.1982 | 0.015 | [8 empty] | 51.6313 | 1734.8102 | 2170.0489 | 6.5107 | 66.7384 | 0.26 | 10.5 | Hz
14.7518 | 495.6601 | 930.8987 | 2.7929 | 12.2812 | 0.021 | [8 empty] | 54.0899 | 1817.4202 | 2252.6589 | 6.7586 | 71.9163 | 0.285 | 11 | Hz
17.2104 | 578.2701 | 1013.5087 | 3.0408 | 14.5577 | 0.029 | [8 empty] | 56.5485 | 1900.0302 | 2335.2689 | 7.0064 | 77.2877 | 0.312 | 11.5 | Hz
19.669 | 660.8801 | 1096.1187 | 3.2886 | 17.0275 | 0.038 | [8 empty] | 59.0071 | 1982.6402 | 2417.8789 | 7.2543 | 82.8525 | 0.339 | 12 | Hz
22.1277 | 743.4901 | 1178.7287 | 3.5365 | 19.6908 | 0.048
24.5863 | 826.1001 | 1261.3387 | 3.7843 | 22.5476 | 0.059
27.0449 | 908.7101 | 1343.9488 | 4.0322 | 25.5978 | 0.071 | 5.5 | Hz | [6 empty] | Power Curves @ Te 19 |  |  |  |  | Power Curve @ Te 19
29.5036 | 991.3201 | 1426.5588 | 4.28 | 28.8414 | 0.085 | [8 empty] | Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW)
31.9622 | 1073.9301 | 1509.1688 | 4.5279 | 32.2784 | 0.1 | [8 empty] | 0 | 0 | 435.2386 | 1.3052 | 2.4073 | 0 | 0 | Hz
34.4208 | 1156.5401 | 1591.7788 | 4.7758 | 35.9089 | 0.115 | [8 empty] | 2.4586 | 82.61 | 517.8487 | 1.553 | 3.4078 | 0.0003436 | 0.5 | Hz
36.8795 | 1239.1502 | 1674.3888 | 5.0236 | 39.7328 | 0.133 | [8 empty] | 4.9173 | 165.22 | 600.4587 | 1.8007 | 4.5818 | 0.001 | 1 | Hz
39.3381 | 1321.7602 | 1756.9988 | 5.2715 | 43.7502 | 0.151 | [8 empty] | 7.3759 | 247.83 | 683.0687 | 2.0484 | 5.9292 | 0.003 | 1.5 | Hz
41.7967 | 1404.3702 | 1839.6088 | 5.5193 | 47.9609 | 0.17 | [8 empty] | 9.8345 | 330.44 | 765.6787 | 2.2962 | 7.4501 | 0.005 | 2 | Hz
44.2554 | 1486.9802 | 1922.2188 | 5.7672 | 52.3651 | 0.191 | [8 empty] | 12.2932 | 413.05 | 848.2887 | 2.5439 | 9.1444 | 0.009 | 2.5 | Hz
46.714 | 1569.5902 | 2004.8288 | 6.015 | 56.9628 | 0.213 | [8 empty] | 14.7518 | 495.6601 | 930.8987 | 2.7916 | 11.0122 | 0.012 | 3 | Hz
49.1726 | 1652.2002 | 2087.4388 | 6.2629 | 61.7539 | 0.236 | [8 empty] | 17.2104 | 578.2701 | 1013.5087 | 3.0394 | 13.0534 | 0.017 | 3.5 | Hz
51.6313 | 1734.8102 | 2170.0489 | 6.5107 | 66.7384 | 0.26 | [8 empty] | 19.669 | 660.8801 | 1096.1187 | 3.2871 | 15.268 | 0.022 | 4 | Hz
54.0899 | 1817.4202 | 2252.6589 | 6.7586 | 71.9163 | 0.285 | [8 empty] | 22.1277 | 743.4901 | 1178.7287 | 3.5348 | 17.6561 | 0.028 | 4.5 | Hz
56.5485 | 1900.0302 | 2335.2689 | 7.0064 | 77.2877 | 0.312 | [8 empty] | 24.5863 | 826.1001 | 1261.3387 | 3.7826 | 20.2177 | 0.034 | 5 | Hz
59.0071 | 1982.6402 | 2417.8789 | 7.2543 | 82.8525 | 0.339 | [8 empty] | 27.0449 | 908.7101 | 1343.9488 | 4.0303 | 22.9527 | 0.042 | 5.5 | Hz
0 | 0 | 435.2386 | 1.3058 | 2.6847 | [9 empty] | 29.5036 | 991.3201 | 1426.5588 | 4.278 | 25.8611 | 0.049 | 6 | Hz
[14 empty] | 31.9622 | 1073.9301 | 1509.1688 | 4.5258 | 28.943 | 0.058 | 6.5 | Hz
Power Curves @ Te 19 |  |  |  |  | Power Curve @ Te 19 | [8 empty] | 34.4208 | 1156.5401 | 1591.7788 | 4.7735 | 32.1983 | 0.067 | 7 | Hz
Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW) | [8 empty] | 36.8795 | 1239.1502 | 1674.3888 | 5.0213 | 35.6271 | 0.077 | 7.5 | Hz
0 | 0 | 435.2386 | 1.3052 | 2.4073 | 0 | [8 empty] | 39.3381 | 1321.7602 | 1756.9988 | 5.269 | 39.2293 | 0.088 | 8 | Hz
2.4586 | 82.61 | 517.8487 | 1.553 | 3.4078 | 0.0003436 | [8 empty] | 41.7967 | 1404.3702 | 1839.6088 | 5.5167 | 43.0049 | 0.099 | 8.5 | Hz
4.9173 | 165.22 | 600.4587 | 1.8007 | 4.5818 | 0.001 | [8 empty] | 44.2554 | 1486.9802 | 1922.2188 | 5.7645 | 46.9541 | 0.111 | 9 | Hz
7.3759 | 247.83 | 683.0687 | 2.0484 | 5.9292 | 0.003 | [8 empty] | 46.714 | 1569.5902 | 2004.8288 | 6.0122 | 51.0766 | 0.124 | 9.5 | Hz
9.8345 | 330.44 | 765.6787 | 2.2962 | 7.4501 | 0.005 | [8 empty] | 49.1726 | 1652.2002 | 2087.4388 | 6.2599 | 55.3726 | 0.137 | 10 | Hz
12.2932 | 413.05 | 848.2887 | 2.5439 | 9.1444 | 0.009 | [8 empty] | 51.6313 | 1734.8102 | 2170.0489 | 6.5077 | 59.842 | 0.152 | 10.5 | Hz
14.7518 | 495.6601 | 930.8987 | 2.7916 | 11.0122 | 0.012 | [8 empty] | 54.0899 | 1817.4202 | 2252.6589 | 6.7554 | 64.4849 | 0.166 | 11 | Hz
17.2104 | 578.2701 | 1013.5087 | 3.0394 | 13.0534 | 0.017 | [8 empty] | 56.5485 | 1900.0302 | 2335.2689 | 7.0031 | 69.3013 | 0.182 | 11.5 | Hz
19.669 | 660.8801 | 1096.1187 | 3.2871 | 15.268 | 0.022 | [8 empty] | 59.0071 | 1982.6402 | 2417.8789 | 7.2509 | 74.2911 | 0.198 | 12 | Hz
22.1277 | 743.4901 | 1178.7287 | 3.5348 | 17.6561 | 0.028
24.5863 | 826.1001 | 1261.3387 | 3.7826 | 20.2177 | 0.034
27.0449 | 908.7101 | 1343.9488 | 4.0303 | 22.9527 | 0.042 | 5.5 | Hz | [6 empty] | Power Curves @ Te 20 |  |  |  |  | Power Curve @ Te 20
29.5036 | 991.3201 | 1426.5588 | 4.278 | 25.8611 | 0.049 | [8 empty] | Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW)
31.9622 | 1073.9301 | 1509.1688 | 4.5258 | 28.943 | 0.058 | [8 empty] | 0 | 0 | 435.2386 | 1.3048 | 2.1711 | 0 | 0 | Hz
34.4208 | 1156.5401 | 1591.7788 | 4.7735 | 32.1983 | 0.067 | [8 empty] | 2.4586 | 82.61 | 517.8487 | 1.5524 | 3.0735 | 0.000206 | 0.5 | Hz
36.8795 | 1239.1502 | 1674.3888 | 5.0213 | 35.6271 | 0.077 | [8 empty] | 4.9173 | 165.22 | 600.4587 | 1.8001 | 4.1323 | 0.0008238 | 1 | Hz
39.3381 | 1321.7602 | 1756.9988 | 5.269 | 39.2293 | 0.088 | [8 empty] | 7.3759 | 247.83 | 683.0687 | 2.0477 | 5.3475 | 0.002 | 1.5 | Hz
41.7967 | 1404.3702 | 1839.6088 | 5.5167 | 43.0049 | 0.099 | [8 empty] | 9.8345 | 330.44 | 765.6787 | 2.2954 | 6.7192 | 0.003 | 2 | Hz
44.2554 | 1486.9802 | 1922.2188 | 5.7645 | 46.9541 | 0.111 | [8 empty] | 12.2932 | 413.05 | 848.2887 | 2.543 | 8.2473 | 0.005 | 2.5 | Hz
46.714 | 1569.5902 | 2004.8288 | 6.0122 | 51.0766 | 0.124 | [8 empty] | 14.7518 | 495.6601 | 930.8987 | 2.7907 | 9.9318 | 0.007 | 3 | Hz
49.1726 | 1652.2002 | 2087.4388 | 6.2599 | 55.3726 | 0.137 | [8 empty] | 17.2104 | 578.2701 | 1013.5087 | 3.0384 | 11.7728 | 0.01 | 3.5 | Hz
51.6313 | 1734.8102 | 2170.0489 | 6.5077 | 59.842 | 0.152 | [8 empty] | 19.669 | 660.8801 | 1096.1187 | 3.286 | 13.7702 | 0.013 | 4 | Hz
54.0899 | 1817.4202 | 2252.6589 | 6.7554 | 64.4849 | 0.166 | [8 empty] | 22.1277 | 743.4901 | 1178.7287 | 3.5337 | 15.924 | 0.017 | 4.5 | Hz
56.5485 | 1900.0302 | 2335.2689 | 7.0031 | 69.3013 | 0.182 | [8 empty] | 24.5863 | 826.1001 | 1261.3387 | 3.7813 | 18.2343 | 0.021 | 5 | Hz
59.0071 | 1982.6402 | 2417.8789 | 7.2509 | 74.2911 | 0.198 | [8 empty] | 27.0449 | 908.7101 | 1343.9488 | 4.029 | 20.7009 | 0.025 | 5.5 | Hz
0 | 0 | 435.2386 | 1.3052 | 2.4073 | [9 empty] | 29.5036 | 991.3201 | 1426.5588 | 4.2766 | 23.324 | 0.03 | 6 | Hz
[14 empty] | 31.9622 | 1073.9301 | 1509.1688 | 4.5243 | 26.1036 | 0.035 | 6.5 | Hz
Power Curves @ Te 20 |  |  |  |  | Power Curve @ Te 20 | [8 empty] | 34.4208 | 1156.5401 | 1591.7788 | 4.7719 | 29.0395 | 0.04 | 7 | Hz
Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW) | [8 empty] | 36.8795 | 1239.1502 | 1674.3888 | 5.0196 | 32.1319 | 0.046 | 7.5 | Hz
0 | 0 | 435.2386 | 1.3048 | 2.1711 | 0 | [8 empty] | 39.3381 | 1321.7602 | 1756.9988 | 5.2672 | 35.3808 | 0.053 | 8 | Hz
2.4586 | 82.61 | 517.8487 | 1.5524 | 3.0735 | 0.000206 | [8 empty] | 41.7967 | 1404.3702 | 1839.6088 | 5.5149 | 38.786 | 0.06 | 8.5 | Hz
4.9173 | 165.22 | 600.4587 | 1.8001 | 4.1323 | 0.0008238 | [8 empty] | 44.2554 | 1486.9802 | 1922.2188 | 5.7625 | 42.3477 | 0.067 | 9 | Hz
7.3759 | 247.83 | 683.0687 | 2.0477 | 5.3475 | 0.002 | [8 empty] | 46.714 | 1569.5902 | 2004.8288 | 6.0102 | 46.0658 | 0.074 | 9.5 | Hz
9.8345 | 330.44 | 765.6787 | 2.2954 | 6.7192 | 0.003 | [8 empty] | 49.1726 | 1652.2002 | 2087.4388 | 6.2578 | 49.9404 | 0.082 | 10 | Hz
12.2932 | 413.05 | 848.2887 | 2.543 | 8.2473 | 0.005 | [8 empty] | 51.6313 | 1734.8102 | 2170.0489 | 6.5055 | 53.9714 | 0.091 | 10.5 | Hz
14.7518 | 495.6601 | 930.8987 | 2.7907 | 9.9318 | 0.007 | [8 empty] | 54.0899 | 1817.4202 | 2252.6589 | 6.7531 | 58.1588 | 0.1 | 11 | Hz
17.2104 | 578.2701 | 1013.5087 | 3.0384 | 11.7728 | 0.01 | [8 empty] | 56.5485 | 1900.0302 | 2335.2689 | 7.0008 | 62.5026 | 0.109 | 11.5 | Hz
19.669 | 660.8801 | 1096.1187 | 3.286 | 13.7702 | 0.013 | [8 empty] | 59.0071 | 1982.6402 | 2417.8789 | 7.2484 | 67.0029 | 0.119 | 12 | Hz
22.1277 | 743.4901 | 1178.7287 | 3.5337 | 15.924 | 0.017
24.5863 | 826.1001 | 1261.3387 | 3.7813 | 18.2343 | 0.021
27.0449 | 908.7101 | 1343.9488 | 4.029 | 20.7009 | 0.025 | 5.5 | Hz | [6 empty] | Power Curves @ Te 21 |  |  |  |  | Power Curve @ Te 21
29.5036 | 991.3201 | 1426.5588 | 4.2766 | 23.324 | 0.03 | [8 empty] | Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW)
31.9622 | 1073.9301 | 1509.1688 | 4.5243 | 26.1036 | 0.035 | [8 empty] | 0 | 0 | 435.2386 | 1.3045 | 1.9683 | 0 | 0 | Hz
34.4208 | 1156.5401 | 1591.7788 | 4.7719 | 29.0395 | 0.04 | [8 empty] | 2.4586 | 82.61 | 517.8487 | 1.5521 | 2.7864 | 0.0001266 | 0.5 | Hz
36.8795 | 1239.1502 | 1674.3888 | 5.0196 | 32.1319 | 0.046 | [8 empty] | 4.9173 | 165.22 | 600.4587 | 1.7997 | 3.7464 | 0.0005062 | 1 | Hz
39.3381 | 1321.7602 | 1756.9988 | 5.2672 | 35.3808 | 0.053 | [8 empty] | 7.3759 | 247.83 | 683.0687 | 2.0473 | 4.8481 | 0.001 | 1.5 | Hz
41.7967 | 1404.3702 | 1839.6088 | 5.5149 | 38.786 | 0.06 | [8 empty] | 9.8345 | 330.44 | 765.6787 | 2.2949 | 6.0917 | 0.002 | 2 | Hz
44.2554 | 1486.9802 | 1922.2188 | 5.7625 | 42.3477 | 0.067 | [8 empty] | 12.2932 | 413.05 | 848.2887 | 2.5425 | 7.4771 | 0.003 | 2.5 | Hz
46.714 | 1569.5902 | 2004.8288 | 6.0102 | 46.0658 | 0.074 | [8 empty] | 14.7518 | 495.6601 | 930.8987 | 2.7901 | 9.0043 | 0.005 | 3 | Hz
49.1726 | 1652.2002 | 2087.4388 | 6.2578 | 49.9404 | 0.082 | [8 empty] | 17.2104 | 578.2701 | 1013.5087 | 3.0376 | 10.6733 | 0.006 | 3.5 | Hz
51.6313 | 1734.8102 | 2170.0489 | 6.5055 | 53.9714 | 0.091 | [8 empty] | 19.669 | 660.8801 | 1096.1187 | 3.2852 | 12.4842 | 0.008 | 4 | Hz
54.0899 | 1817.4202 | 2252.6589 | 6.7531 | 58.1588 | 0.1 | [8 empty] | 22.1277 | 743.4901 | 1178.7287 | 3.5328 | 14.4369 | 0.01 | 4.5 | Hz
56.5485 | 1900.0302 | 2335.2689 | 7.0008 | 62.5026 | 0.109 | [8 empty] | 24.5863 | 826.1001 | 1261.3387 | 3.7804 | 16.5314 | 0.013 | 5 | Hz
59.0071 | 1982.6402 | 2417.8789 | 7.2484 | 67.0029 | 0.119 | [8 empty] | 27.0449 | 908.7101 | 1343.9488 | 4.028 | 18.7677 | 0.015 | 5.5 | Hz
0 | 0 | 435.2386 | 1.3048 | 2.1711 | [9 empty] | 29.5036 | 991.3201 | 1426.5588 | 4.2756 | 21.1458 | 0.018 | 6 | Hz
[14 empty] | 31.9622 | 1073.9301 | 1509.1688 | 4.5232 | 23.6658 | 0.021 | 6.5 | Hz
Power Curves @ Te 21 |  |  |  |  | Power Curve @ Te 21 | [8 empty] | 34.4208 | 1156.5401 | 1591.7788 | 4.7708 | 26.3276 | 0.025 | 7 | Hz
Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW) | [8 empty] | 36.8795 | 1239.1502 | 1674.3888 | 5.0184 | 29.1312 | 0.028 | 7.5 | Hz
0 | 0 | 435.2386 | 1.3045 | 1.9683 | 0 | [8 empty] | 39.3381 | 1321.7602 | 1756.9988 | 5.266 | 32.0766 | 0.032 | 8 | Hz
2.4586 | 82.61 | 517.8487 | 1.5521 | 2.7864 | 0.0001266 | [8 empty] | 41.7967 | 1404.3702 | 1839.6088 | 5.5136 | 35.1638 | 0.037 | 8.5 | Hz
4.9173 | 165.22 | 600.4587 | 1.7997 | 3.7464 | 0.0005062 | [8 empty] | 44.2554 | 1486.9802 | 1922.2188 | 5.7612 | 38.3929 | 0.041 | 9 | Hz
7.3759 | 247.83 | 683.0687 | 2.0473 | 4.8481 | 0.001 | [8 empty] | 46.714 | 1569.5902 | 2004.8288 | 6.0088 | 41.7638 | 0.046 | 9.5 | Hz
9.8345 | 330.44 | 765.6787 | 2.2949 | 6.0917 | 0.002 | [8 empty] | 49.1726 | 1652.2002 | 2087.4388 | 6.2564 | 45.2765 | 0.051 | 10 | Hz
12.2932 | 413.05 | 848.2887 | 2.5425 | 7.4771 | 0.003 | [8 empty] | 51.6313 | 1734.8102 | 2170.0489 | 6.504 | 48.931 | 0.056 | 10.5 | Hz
14.7518 | 495.6601 | 930.8987 | 2.7901 | 9.0043 | 0.005 | [8 empty] | 54.0899 | 1817.4202 | 2252.6589 | 6.7516 | 52.7274 | 0.061 | 11 | Hz
17.2104 | 578.2701 | 1013.5087 | 3.0376 | 10.6733 | 0.006 | [8 empty] | 56.5485 | 1900.0302 | 2335.2689 | 6.9992 | 56.6655 | 0.067 | 11.5 | Hz
19.669 | 660.8801 | 1096.1187 | 3.2852 | 12.4842 | 0.008 | [8 empty] | 59.0071 | 1982.6402 | 2417.8789 | 7.2468 | 60.7455 | 0.073 | 12 | Hz
22.1277 | 743.4901 | 1178.7287 | 3.5328 | 14.4369 | 0.01
24.5863 | 826.1001 | 1261.3387 | 3.7804 | 16.5314 | 0.013
27.0449 | 908.7101 | 1343.9488 | 4.028 | 18.7677 | 0.015 | 5.5 | Hz | [6 empty] | Power Curves @ Te 22 |  |  |  |  | Power Curve @ Te 22
29.5036 | 991.3201 | 1426.5588 | 4.2756 | 21.1458 | 0.018 | [8 empty] | Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW)
31.9622 | 1073.9301 | 1509.1688 | 4.5232 | 23.6658 | 0.021 | [8 empty] | 0 | 0 | 435.2386 | 1.3043 | 1.7929 | 0 | 0 | Hz
34.4208 | 1156.5401 | 1591.7788 | 4.7708 | 26.3276 | 0.025 | [8 empty] | 2.4586 | 82.61 | 517.8487 | 1.5518 | 2.5381 | 7.953e-05 | 0.5 | Hz
36.8795 | 1239.1502 | 1674.3888 | 5.0184 | 29.1312 | 0.028 | [8 empty] | 4.9173 | 165.22 | 600.4587 | 1.7994 | 3.4125 | 0.0003181 | 1 | Hz
39.3381 | 1321.7602 | 1756.9988 | 5.266 | 32.0766 | 0.032 | [8 empty] | 7.3759 | 247.83 | 683.0687 | 2.047 | 4.4161 | 0.0007157 | 1.5 | Hz
41.7967 | 1404.3702 | 1839.6088 | 5.5136 | 35.1638 | 0.037 | [8 empty] | 9.8345 | 330.44 | 765.6787 | 2.2945 | 5.5488 | 0.001 | 2 | Hz
44.2554 | 1486.9802 | 1922.2188 | 5.7612 | 38.3929 | 0.041 | [8 empty] | 12.2932 | 413.05 | 848.2887 | 2.5421 | 6.8107 | 0.002 | 2.5 | Hz
46.714 | 1569.5902 | 2004.8288 | 6.0088 | 41.7638 | 0.046 | [8 empty] | 14.7518 | 495.6601 | 930.8987 | 2.7896 | 8.2019 | 0.003 | 3 | Hz
49.1726 | 1652.2002 | 2087.4388 | 6.2564 | 45.2765 | 0.051 | [8 empty] | 17.2104 | 578.2701 | 1013.5087 | 3.0372 | 9.7222 | 0.004 | 3.5 | Hz
51.6313 | 1734.8102 | 2170.0489 | 6.504 | 48.931 | 0.056 | [8 empty] | 19.669 | 660.8801 | 1096.1187 | 3.2847 | 11.3716 | 0.005 | 4 | Hz
54.0899 | 1817.4202 | 2252.6589 | 6.7516 | 52.7274 | 0.061 | [8 empty] | 22.1277 | 743.4901 | 1178.7287 | 3.5323 | 13.1503 | 0.006 | 4.5 | Hz
56.5485 | 1900.0302 | 2335.2689 | 6.9992 | 56.6655 | 0.067 | [8 empty] | 24.5863 | 826.1001 | 1261.3387 | 3.7799 | 15.0581 | 0.008 | 5 | Hz
59.0071 | 1982.6402 | 2417.8789 | 7.2468 | 60.7455 | 0.073 | [8 empty] | 27.0449 | 908.7101 | 1343.9488 | 4.0274 | 17.0951 | 0.01 | 5.5 | Hz
0 | 0 | 435.2386 | 1.3045 | 1.9683 | [9 empty] | 29.5036 | 991.3201 | 1426.5588 | 4.275 | 19.2613 | 0.011 | 6 | Hz
[14 empty] | 31.9622 | 1073.9301 | 1509.1688 | 4.5225 | 21.5567 | 0.013 | 6.5 | Hz
Power Curves @ Te 22 |  |  |  |  | Power Curve @ Te 22 | [8 empty] | 34.4208 | 1156.5401 | 1591.7788 | 4.7701 | 23.9813 | 0.016 | 7 | Hz
Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW) | [8 empty] | 36.8795 | 1239.1502 | 1674.3888 | 5.0177 | 26.5351 | 0.018 | 7.5 | Hz
0 | 0 | 435.2386 | 1.3043 | 1.7929 | 0 | [8 empty] | 39.3381 | 1321.7602 | 1756.9988 | 5.2652 | 29.218 | 0.02 | 8 | Hz
2.4586 | 82.61 | 517.8487 | 1.5518 | 2.5381 | 7.953e-05 | [8 empty] | 41.7967 | 1404.3702 | 1839.6088 | 5.5128 | 32.0301 | 0.023 | 8.5 | Hz
4.9173 | 165.22 | 600.4587 | 1.7994 | 3.4125 | 0.0003181 | [8 empty] | 44.2554 | 1486.9802 | 1922.2188 | 5.7603 | 34.9714 | 0.026 | 9 | Hz
7.3759 | 247.83 | 683.0687 | 2.047 | 4.4161 | 0.0007157 | [8 empty] | 46.714 | 1569.5902 | 2004.8288 | 6.0079 | 38.0419 | 0.029 | 9.5 | Hz
9.8345 | 330.44 | 765.6787 | 2.2945 | 5.5488 | 0.001 | [8 empty] | 49.1726 | 1652.2002 | 2087.4388 | 6.2554 | 41.2415 | 0.032 | 10 | Hz
12.2932 | 413.05 | 848.2887 | 2.5421 | 6.8107 | 0.002 | [8 empty] | 51.6313 | 1734.8102 | 2170.0489 | 6.503 | 44.5704 | 0.035 | 10.5 | Hz
14.7518 | 495.6601 | 930.8987 | 2.7896 | 8.2019 | 0.003 | [8 empty] | 54.0899 | 1817.4202 | 2252.6589 | 6.7506 | 48.0284 | 0.038 | 11 | Hz
17.2104 | 578.2701 | 1013.5087 | 3.0372 | 9.7222 | 0.004 | [8 empty] | 56.5485 | 1900.0302 | 2335.2689 | 6.9981 | 51.6156 | 0.042 | 11.5 | Hz
19.669 | 660.8801 | 1096.1187 | 3.2847 | 11.3716 | 0.005 | [8 empty] | 59.0071 | 1982.6402 | 2417.8789 | 7.2457 | 55.332 | 0.046 | 12 | Hz
22.1277 | 743.4901 | 1178.7287 | 3.5323 | 13.1503 | 0.006
24.5863 | 826.1001 | 1261.3387 | 3.7799 | 15.0581 | 0.008
27.0449 | 908.7101 | 1343.9488 | 4.0274 | 17.0951 | 0.01 | 5.5 | Hz | [6 empty] | Power Curves @ Te 23 |  |  |  |  | Power Curve @ Te 23
29.5036 | 991.3201 | 1426.5588 | 4.275 | 19.2613 | 0.011 | [8 empty] | Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW)
31.9622 | 1073.9301 | 1509.1688 | 4.5225 | 21.5567 | 0.013 | [8 empty] | 0 | 0 | 435.2386 | 1.3042 | 1.6401 | 0 | 0 | Hz
34.4208 | 1156.5401 | 1591.7788 | 4.7701 | 23.9813 | 0.016 | [8 empty] | 2.4586 | 82.61 | 517.8487 | 1.5517 | 2.3218 | 5.101e-05 | 0.5 | Hz
36.8795 | 1239.1502 | 1674.3888 | 5.0177 | 26.5351 | 0.018 | [8 empty] | 4.9173 | 165.22 | 600.4587 | 1.7992 | 3.1217 | 0.0002041 | 1 | Hz
39.3381 | 1321.7602 | 1756.9988 | 5.2652 | 29.218 | 0.02 | [8 empty] | 7.3759 | 247.83 | 683.0687 | 2.0468 | 4.0397 | 0.0004591 | 1.5 | Hz
41.7967 | 1404.3702 | 1839.6088 | 5.5128 | 32.0301 | 0.023 | [8 empty] | 9.8345 | 330.44 | 765.6787 | 2.2943 | 5.0759 | 0.0008162 | 2 | Hz
44.2554 | 1486.9802 | 1922.2188 | 5.7603 | 34.9714 | 0.026 | [8 empty] | 12.2932 | 413.05 | 848.2887 | 2.5418 | 6.2303 | 0.001 | 2.5 | Hz
46.714 | 1569.5902 | 2004.8288 | 6.0079 | 38.0419 | 0.029 | [8 empty] | 14.7518 | 495.6601 | 930.8987 | 2.7894 | 7.5028 | 0.002 | 3 | Hz
49.1726 | 1652.2002 | 2087.4388 | 6.2554 | 41.2415 | 0.032 | [8 empty] | 17.2104 | 578.2701 | 1013.5087 | 3.0369 | 8.8935 | 0.002 | 3.5 | Hz
51.6313 | 1734.8102 | 2170.0489 | 6.503 | 44.5704 | 0.035 | [8 empty] | 19.669 | 660.8801 | 1096.1187 | 3.2845 | 10.4024 | 0.003 | 4 | Hz
54.0899 | 1817.4202 | 2252.6589 | 6.7506 | 48.0284 | 0.038 | [8 empty] | 22.1277 | 743.4901 | 1178.7287 | 3.532 | 12.0295 | 0.004 | 4.5 | Hz
56.5485 | 1900.0302 | 2335.2689 | 6.9981 | 51.6156 | 0.042 | [8 empty] | 24.5863 | 826.1001 | 1261.3387 | 3.7795 | 13.7747 | 0.005 | 5 | Hz
59.0071 | 1982.6402 | 2417.8789 | 7.2457 | 55.332 | 0.046 | [8 empty] | 27.0449 | 908.7101 | 1343.9488 | 4.0271 | 15.6381 | 0.006 | 5.5 | Hz
0 | 0 | 435.2386 | 1.3043 | 1.7929 | [9 empty] | 29.5036 | 991.3201 | 1426.5588 | 4.2746 | 17.6197 | 0.007 | 6 | Hz
[14 empty] | 31.9622 | 1073.9301 | 1509.1688 | 4.5221 | 19.7195 | 0.009 | 6.5 | Hz
Power Curves @ Te 23 |  |  |  |  | Power Curve @ Te 23 | [8 empty] | 34.4208 | 1156.5401 | 1591.7788 | 4.7697 | 21.9374 | 0.01 | 7 | Hz
Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW) | [8 empty] | 36.8795 | 1239.1502 | 1674.3888 | 5.0172 | 24.2735 | 0.011 | 7.5 | Hz
0 | 0 | 435.2386 | 1.3042 | 1.6401 | 0 | [8 empty] | 39.3381 | 1321.7602 | 1756.9988 | 5.2647 | 26.7278 | 0.013 | 8 | Hz
2.4586 | 82.61 | 517.8487 | 1.5517 | 2.3218 | 5.101e-05 | [8 empty] | 41.7967 | 1404.3702 | 1839.6088 | 5.5123 | 29.3002 | 0.015 | 8.5 | Hz
4.9173 | 165.22 | 600.4587 | 1.7992 | 3.1217 | 0.0002041 | [8 empty] | 44.2554 | 1486.9802 | 1922.2188 | 5.7598 | 31.9908 | 0.017 | 9 | Hz
7.3759 | 247.83 | 683.0687 | 2.0468 | 4.0397 | 0.0004591 | [8 empty] | 46.714 | 1569.5902 | 2004.8288 | 6.0074 | 34.7996 | 0.018 | 9.5 | Hz
9.8345 | 330.44 | 765.6787 | 2.2943 | 5.0759 | 0.0008162 | [8 empty] | 49.1726 | 1652.2002 | 2087.4388 | 6.2549 | 37.7266 | 0.02 | 10 | Hz
12.2932 | 413.05 | 848.2887 | 2.5418 | 6.2303 | 0.001 | [8 empty] | 51.6313 | 1734.8102 | 2170.0489 | 6.5024 | 40.7717 | 0.022 | 10.5 | Hz
14.7518 | 495.6601 | 930.8987 | 2.7894 | 7.5028 | 0.002 | [8 empty] | 54.0899 | 1817.4202 | 2252.6589 | 6.75 | 43.935 | 0.025 | 11 | Hz
17.2104 | 578.2701 | 1013.5087 | 3.0369 | 8.8935 | 0.002 | [8 empty] | 56.5485 | 1900.0302 | 2335.2689 | 6.9975 | 47.2165 | 0.027 | 11.5 | Hz
19.669 | 660.8801 | 1096.1187 | 3.2845 | 10.4024 | 0.003 | [8 empty] | 59.0071 | 1982.6402 | 2417.8789 | 7.245 | 50.6161 | 0.029 | 12 | Hz
22.1277 | 743.4901 | 1178.7287 | 3.532 | 12.0295 | 0.004
24.5863 | 826.1001 | 1261.3387 | 3.7795 | 13.7747 | 0.005
27.0449 | 908.7101 | 1343.9488 | 4.0271 | 15.6381 | 0.006 | 5.5 | Hz | [6 empty] | Power Curves @ Te 24 |  |  |  |  | Power Curve @ Te 24
29.5036 | 991.3201 | 1426.5588 | 4.2746 | 17.6197 | 0.007 | [8 empty] | Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW)
31.9622 | 1073.9301 | 1509.1688 | 4.5221 | 19.7195 | 0.009 | [8 empty] | 0 | 0 | 435.2386 | 1.3041 | 1.5062 | 0 | 0 | Hz
34.4208 | 1156.5401 | 1591.7788 | 4.7697 | 21.9374 | 0.01 | [8 empty] | 2.4586 | 82.61 | 517.8487 | 1.5516 | 2.1322 | 3.335e-05 | 0.5 | Hz
36.8795 | 1239.1502 | 1674.3888 | 5.0172 | 24.2735 | 0.011 | [8 empty] | 4.9173 | 165.22 | 600.4587 | 1.7992 | 2.8667 | 0.0001334 | 1 | Hz
39.3381 | 1321.7602 | 1756.9988 | 5.2647 | 26.7278 | 0.013 | [8 empty] | 7.3759 | 247.83 | 683.0687 | 2.0467 | 3.7098 | 0.0003001 | 1.5 | Hz
41.7967 | 1404.3702 | 1839.6088 | 5.5123 | 29.3002 | 0.015 | [8 empty] | 9.8345 | 330.44 | 765.6787 | 2.2942 | 4.6613 | 0.0005336 | 2 | Hz
44.2554 | 1486.9802 | 1922.2188 | 5.7598 | 31.9908 | 0.017 | [8 empty] | 12.2932 | 413.05 | 848.2887 | 2.5417 | 5.7214 | 0.0008337 | 2.5 | Hz
46.714 | 1569.5902 | 2004.8288 | 6.0074 | 34.7996 | 0.018 | [8 empty] | 14.7518 | 495.6601 | 930.8987 | 2.7893 | 6.8901 | 0.001 | 3 | Hz
49.1726 | 1652.2002 | 2087.4388 | 6.2549 | 37.7266 | 0.02 | [8 empty] | 17.2104 | 578.2701 | 1013.5087 | 3.0368 | 8.1672 | 0.002 | 3.5 | Hz
51.6313 | 1734.8102 | 2170.0489 | 6.5024 | 40.7717 | 0.022 | [8 empty] | 19.669 | 660.8801 | 1096.1187 | 3.2843 | 9.5529 | 0.002 | 4 | Hz
54.0899 | 1817.4202 | 2252.6589 | 6.75 | 43.935 | 0.025 | [8 empty] | 22.1277 | 743.4901 | 1178.7287 | 3.5318 | 11.047 | 0.003 | 4.5 | Hz
56.5485 | 1900.0302 | 2335.2689 | 6.9975 | 47.2165 | 0.027 | [8 empty] | 24.5863 | 826.1001 | 1261.3387 | 3.7794 | 12.6497 | 0.003 | 5 | Hz
59.0071 | 1982.6402 | 2417.8789 | 7.245 | 50.6161 | 0.029 | [8 empty] | 27.0449 | 908.7101 | 1343.9488 | 4.0269 | 14.361 | 0.004 | 5.5 | Hz
0 | 0 | 435.2386 | 1.3042 | 1.6401 | [9 empty] | 29.5036 | 991.3201 | 1426.5588 | 4.2744 | 16.1807 | 0.005 | 6 | Hz
[14 empty] | 31.9622 | 1073.9301 | 1509.1688 | 4.522 | 18.109 | 0.006 | 6.5 | Hz
Power Curves @ Te 24 |  |  |  |  | Power Curve @ Te 24 | [8 empty] | 34.4208 | 1156.5401 | 1591.7788 | 4.7695 | 20.1457 | 0.007 | 7 | Hz
Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW) | [8 empty] | 36.8795 | 1239.1502 | 1674.3888 | 5.017 | 22.291 | 0.008 | 7.5 | Hz
0 | 0 | 435.2386 | 1.3041 | 1.5062 | 0 | [8 empty] | 39.3381 | 1321.7602 | 1756.9988 | 5.2645 | 24.5449 | 0.009 | 8 | Hz
2.4586 | 82.61 | 517.8487 | 1.5516 | 2.1322 | 3.335e-05 | [8 empty] | 41.7967 | 1404.3702 | 1839.6088 | 5.5121 | 26.9072 | 0.01 | 8.5 | Hz
4.9173 | 165.22 | 600.4587 | 1.7992 | 2.8667 | 0.0001334 | [8 empty] | 44.2554 | 1486.9802 | 1922.2188 | 5.7596 | 29.3781 | 0.011 | 9 | Hz
7.3759 | 247.83 | 683.0687 | 2.0467 | 3.7098 | 0.0003001 | [8 empty] | 46.714 | 1569.5902 | 2004.8288 | 6.0071 | 31.9575 | 0.012 | 9.5 | Hz
9.8345 | 330.44 | 765.6787 | 2.2942 | 4.6613 | 0.0005336 | [8 empty] | 49.1726 | 1652.2002 | 2087.4388 | 6.2546 | 34.6454 | 0.013 | 10 | Hz
12.2932 | 413.05 | 848.2887 | 2.5417 | 5.7214 | 0.0008337 | [8 empty] | 51.6313 | 1734.8102 | 2170.0489 | 6.5022 | 37.4418 | 0.015 | 10.5 | Hz
14.7518 | 495.6601 | 930.8987 | 2.7893 | 6.8901 | 0.001 | [8 empty] | 54.0899 | 1817.4202 | 2252.6589 | 6.7497 | 40.3468 | 0.016 | 11 | Hz
17.2104 | 578.2701 | 1013.5087 | 3.0368 | 8.1672 | 0.002 | [8 empty] | 56.5485 | 1900.0302 | 2335.2689 | 6.9972 | 43.3602 | 0.018 | 11.5 | Hz
19.669 | 660.8801 | 1096.1187 | 3.2843 | 9.5529 | 0.002 | [8 empty] | 59.0071 | 1982.6402 | 2417.8789 | 7.2447 | 46.4822 | 0.019 | 12 | Hz
22.1277 | 743.4901 | 1178.7287 | 3.5318 | 11.047 | 0.003
24.5863 | 826.1001 | 1261.3387 | 3.7794 | 12.6497 | 0.003
27.0449 | 908.7101 | 1343.9488 | 4.0269 | 14.361 | 0.004 | 5.5 | Hz | [6 empty] | Power Curves @ Te 25 |  |  |  |  | Power Curve @ Te 25
29.5036 | 991.3201 | 1426.5588 | 4.2744 | 16.1807 | 0.005 | [8 empty] | Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW)
31.9622 | 1073.9301 | 1509.1688 | 4.522 | 18.109 | 0.006 | [8 empty] | 0 | 0 | 435.2386 | 1.3041 | 1.3881 | 0 | 0 | Hz
34.4208 | 1156.5401 | 1591.7788 | 4.7695 | 20.1457 | 0.007 | [8 empty] | 2.4586 | 82.61 | 517.8487 | 1.5516 | 1.965 | 2.218e-05 | 0.5 | Hz
36.8795 | 1239.1502 | 1674.3888 | 5.017 | 22.291 | 0.008 | [8 empty] | 4.9173 | 165.22 | 600.4587 | 1.7992 | 2.6419 | 8.872e-05 | 1 | Hz
39.3381 | 1321.7602 | 1756.9988 | 5.2645 | 24.5449 | 0.009 | [8 empty] | 7.3759 | 247.83 | 683.0687 | 2.0467 | 3.4189 | 0.0001996 | 1.5 | Hz
41.7967 | 1404.3702 | 1839.6088 | 5.5121 | 26.9072 | 0.01 | [8 empty] | 9.8345 | 330.44 | 765.6787 | 2.2942 | 4.2959 | 0.0003549 | 2 | Hz
44.2554 | 1486.9802 | 1922.2188 | 5.7596 | 29.3781 | 0.011 | [8 empty] | 12.2932 | 413.05 | 848.2887 | 2.5417 | 5.2728 | 0.0005545 | 2.5 | Hz
46.714 | 1569.5902 | 2004.8288 | 6.0071 | 31.9575 | 0.012 | [8 empty] | 14.7518 | 495.6601 | 930.8987 | 2.7893 | 6.3498 | 0.0007985 | 3 | Hz
49.1726 | 1652.2002 | 2087.4388 | 6.2546 | 34.6454 | 0.013 | [8 empty] | 17.2104 | 578.2701 | 1013.5087 | 3.0368 | 7.5268 | 0.001 | 3.5 | Hz
51.6313 | 1734.8102 | 2170.0489 | 6.5022 | 37.4418 | 0.015 | [8 empty] | 19.669 | 660.8801 | 1096.1187 | 3.2843 | 8.8039 | 0.001 | 4 | Hz
54.0899 | 1817.4202 | 2252.6589 | 6.7497 | 40.3468 | 0.016 | [8 empty] | 22.1277 | 743.4901 | 1178.7287 | 3.5318 | 10.1809 | 0.002 | 4.5 | Hz
56.5485 | 1900.0302 | 2335.2689 | 6.9972 | 43.3602 | 0.018 | [8 empty] | 24.5863 | 826.1001 | 1261.3387 | 3.7794 | 11.6579 | 0.002 | 5 | Hz
59.0071 | 1982.6402 | 2417.8789 | 7.2447 | 46.4822 | 0.019 | [8 empty] | 27.0449 | 908.7101 | 1343.9488 | 4.0269 | 13.235 | 0.003 | 5.5 | Hz
0 | 0 | 435.2386 | 1.3041 | 1.5062 | [9 empty] | 29.5036 | 991.3201 | 1426.5588 | 4.2744 | 14.912 | 0.003 | 6 | Hz
[14 empty] | 31.9622 | 1073.9301 | 1509.1688 | 4.5219 | 16.6891 | 0.004 | 6.5 | Hz
Power Curves @ Te 25 |  |  |  |  | Power Curve @ Te 25 | [8 empty] | 34.4208 | 1156.5401 | 1591.7788 | 4.7695 | 18.5662 | 0.004 | 7 | Hz
Dynamic Pressure (Pdyn) | Froude Kyrlov | Force | heave Displacement (z) | Power (kW) | Power (kW) | [8 empty] | 36.8795 | 1239.1502 | 1674.3888 | 5.017 | 20.5433 | 0.005 | 7.5 | Hz
0 | 0 | 435.2386 | 1.3041 | 1.3881 | 0 | [8 empty] | 39.3381 | 1321.7602 | 1756.9988 | 5.2645 | 22.6204 | 0.006 | 8 | Hz
2.4586 | 82.61 | 517.8487 | 1.5516 | 1.965 | 2.218e-05 | [8 empty] | 41.7967 | 1404.3702 | 1839.6088 | 5.512 | 24.7976 | 0.006 | 8.5 | Hz
4.9173 | 165.22 | 600.4587 | 1.7992 | 2.6419 | 8.872e-05 | [8 empty] | 44.2554 | 1486.9802 | 1922.2188 | 5.7596 | 27.0747 | 0.007 | 9 | Hz
7.3759 | 247.83 | 683.0687 | 2.0467 | 3.4189 | 0.0001996 | [8 empty] | 46.714 | 1569.5902 | 2004.8288 | 6.0071 | 29.4519 | 0.008 | 9.5 | Hz
9.8345 | 330.44 | 765.6787 | 2.2942 | 4.2959 | 0.0003549 | [8 empty] | 49.1726 | 1652.2002 | 2087.4388 | 6.2546 | 31.929 | 0.009 | 10 | Hz
12.2932 | 413.05 | 848.2887 | 2.5417 | 5.2728 | 0.0005545 | [8 empty] | 51.6313 | 1734.8102 | 2170.0489 | 6.5021 | 34.5062 | 0.01 | 10.5 | Hz
14.7518 | 495.6601 | 930.8987 | 2.7893 | 6.3498 | 0.0007985 | [8 empty] | 54.0899 | 1817.4202 | 2252.6589 | 6.7497 | 37.1834 | 0.011 | 11 | Hz
17.2104 | 578.2701 | 1013.5087 | 3.0368 | 7.5268 | 0.001 | [8 empty] | 56.5485 | 1900.0302 | 2335.2689 | 6.9972 | 39.9606 | 0.012 | 11.5 | Hz
19.669 | 660.8801 | 1096.1187 | 3.2843 | 8.8039 | 0.001 | [8 empty] | 59.0071 | 1982.6402 | 2417.8789 | 7.2447 | 42.8378 | 0.013 | 12 | Hz
22.1277 | 743.4901 | 1178.7287 | 3.5318 | 10.1809 | 0.002
24.5863 | 826.1001 | 1261.3387 | 3.7794 | 11.6579 | 0.002
27.0449 | 908.7101 | 1343.9488 | 4.0269 | 13.235 | 0.003 | 5.5 | Hz
29.5036 | 991.3201 | 1426.5588 | 4.2744 | 14.912 | 0.003
31.9622 | 1073.9301 | 1509.1688 | 4.5219 | 16.6891 | 0.004
34.4208 | 1156.5401 | 1591.7788 | 4.7695 | 18.5662 | 0.004
36.8795 | 1239.1502 | 1674.3888 | 5.017 | 20.5433 | 0.005
39.3381 | 1321.7602 | 1756.9988 | 5.2645 | 22.6204 | 0.006
41.7967 | 1404.3702 | 1839.6088 | 5.512 | 24.7976 | 0.006
44.2554 | 1486.9802 | 1922.2188 | 5.7596 | 27.0747 | 0.007
46.714 | 1569.5902 | 2004.8288 | 6.0071 | 29.4519 | 0.008
49.1726 | 1652.2002 | 2087.4388 | 6.2546 | 31.929 | 0.009
51.6313 | 1734.8102 | 2170.0489 | 6.5021 | 34.5062 | 0.01
54.0899 | 1817.4202 | 2252.6589 | 6.7497 | 37.1834 | 0.011
56.5485 | 1900.0302 | 2335.2689 | 6.9972 | 39.9606 | 0.012
59.0071 | 1982.6402 | 2417.8789 | 7.2447 | 42.8378 | 0.013
0 | 0 | 435.2386 | 1.3041 | 1.3881