## Sheet1
Examples of possible breakdown of losses across electrolyser and fuel cell system
Included: electrolyser, fuel cell and power electronics losses. Excluded: energy used in compression of hydrogen.
Electrolyser |  |  | An ideal, "no-losses" electrolyser | [5 empty] | Real system 1: good current equipment | [5 empty] | Real system 2: best current equipment (lab) | [5 empty] | Future equipment, current aims | [5 empty] | Aspirational future equipment *exceeds current aims
Where | what | notes | Power electronics efficiencies, % | losses in powering auxiliary equipment, % | current efficeincy, % | overvoltage required, or cell voltage, V | efficiency relative to G, free energy voltage, 1.23V | efficiency relative to H, thermoneutral voltage, 1.48V | Power electronics efficiencies, % | losses in powering auxiliary equipment, % | current efficiency, % | overvoltage required, or cell voltage, V | efficiency relative to G, free energy voltage 1.23V | efficiency, relative to H, thermoneutral voltage 1.48V | Power electronics efficiencies, % | losses in powering auxiliary equipment, % | current efficiency, % | overvoltage required, or cell voltage, V | efficiency relative to G, free energy voltage 1.23V | efficiency relative to H, thermoneutral voltage 1.48V | Power electronics efficiencies, % | losses in powering auxiliary equipment, % | current efficiency, % | overvoltage required, or cell voltage V | efficiency relative to G, free energy voltage 1.23V | efficiency relative to H, thermoneutral voltage 1.48V | Power electronics efficiencies, % | losses in powering auxiliary equipment, % | current efficiency, % | overvoltage required, or cell voltage V | efficiency relative to G, free energy voltage 1.23V | efficiency relative to H, thermoneutral voltage 1.48V
electrolyser, stack | TΔS, the difference between free energy voltage (1.23V) and thermoneutral voltage (1.48V) | some authors incorporate this part of voltage drop in with "activation polarisation". In practice, this is the minimum overvoltage needed to obtain any significant current at ambient temperatures. |  |  |  | 0.25 | [5 empty] | 0.25 | [5 empty] | 0.25 | [5 empty] | 0.25 | [5 empty] | 0.25
| Activation polarisation at electrodes: the necessary overvoltage to start chemical reaction | Even at open circuit an overvoltage is needed to start the reaction. This is the dominant voltage drop at low currents. A higher overvoltage is needed at the cathode because the kintetics of the oxygen reaction are slower than the hydrogen reaction, even with catalysts. |  |  |  | 0 | [5 empty] | 0.27 | [5 empty] | 0.15 | [5 empty] | 0.15 | [5 empty] | 0
| Ohmic polarisation - resistance of electrolyte | voltage drop increases linearly with current (Ohm's law). It is assumed here that the cell will operate at maximum design current, so ohmic polarisation will be significant. The resistance of the electrolyte is normally greater than of the electrodes, but both contribute. |  |  |  | 0 | [5 empty] | 0.15 | [5 empty] | 0.1 | [5 empty] | 0.1 | [5 empty] | 0.05
| Ohmic polarisation - electrode resistance |  |  |  |  | 0 | [5 empty] | 0.07 | [5 empty] | 0.05 | [5 empty] | 0.05 | [5 empty] | 0.03
| Concentration polarisation (depletion of reactants near electrode) | becomes more significant at high current densities. It is assumed that the electrolyser will run at a high current density, but within the equipment's design limit, and so only a small voltage drop occur. |  |  |  | 0 | [5 empty] | 0.1 | [5 empty] | 0.05 | [5 empty] | 0.01 | [5 empty] | 0.01
| total voltage drop, V, above free energy voltage |  |  |  |  | 0.25 | [5 empty] | 0.84 | [5 empty] | 0.6 | [5 empty] | 0.56 | [5 empty] | 0.34
| actual cell voltage, V |  |  |  |  | 1.48 | [5 empty] | 2.07 | [5 empty] | 1.83 | [5 empty] | 1.79 | [5 empty] | 1.57
| voltage efficiency ε v, = reference voltage / actual voltage | [5 empty] | 83.11% | 100% |  |  |  |  | 59.42% | 71.5% |  |  |  |  | 67.21% | 80.87% |  |  |  |  | 68.72% | 82.68% |  |  |  |  | 78.34% | 94.27%
| Faradaic efficiency ε f (hydrogen "escapes" into electrolyte and its chemical energy is lost) | can be significant at low power inputs. It is assumed here the electrolyser will always operate at rated capacity, so "near to one" is a deemed to be a reasonable assumption. |  |  | 100% | [5 empty] | 98% | [5 empty] | 98% | [5 empty] | 98% | [5 empty] | 99%
| total stack efficiency, ε stack = ε v * ε f | [5 empty] | 83.11% | 100% |  |  |  |  | 58.23% | 70.07% |  |  |  |  | 65.87% | 79.26% |  |  |  |  | 67.34% | 81.03% |  |  |  |  | 77.56% | 93.32%
electrolyser - auxiliary equipment | proportion of electricity needed to power auxiliary kit, L aux |  |  | 0% | [5 empty] | 15% | [5 empty] | 10% | [5 empty] | 5% | [5 empty] | 5%
overall electrolyser efficiency | ε electro = ε stack * (1- L aux) | [5 empty] | 83.11% | 100% |  |  |  |  | 49.5% | 59.56% |  |  |  |  | 59.28% | 71.33% |  |  |  |  | 63.97% | 76.98% |  |  |  |  | 73.68% | 88.66%
Fuel Cell |  |  |  | Ideal "no-losses" fuel cell |  |  |  |  | Real system 1, good current equipment | [5 empty] | Real system 2: best current equipment (lab) | [5 empty] | future equipment, current aims | [5 empty] | Aspirational future equipment *exceeds current aims
Where | what |  | Power electronics efficiencies, % | losses in powering auxiliary equipment, % | current efficiency, % | voltage loss, V | efficiency relative to G, free energy voltage, 1.22 V | overall voltage efficiency relative to H, thermoneutral voltage, 1.47 V | Power electronics efficiencies, % | losses in powering auxiliary equipment | current efficiency | voltage loss, V | efficiency relative to G, free energy voltage, 1.22 V | efficiency, relative to H, thermoneutral voltage, 1.47 V | Power electronics efficiencies, % | losses in powering auxiliary equipment | current efficiency | voltage loss, V | efficiency relative to G, free energy voltage, 1.22 V | efficiency, relative to H, thermoneutral voltage, 1.47 V | Power electronics efficiencies, % | losses in powering auxiliary equipment | current efficiency | voltage loss, V | efficiency relative to G, free energy voltage, 1.22 V | efficiency, relative to H, thermoneutral voltage, 1.47 V | Power electronics efficiencies, % | losses in powering auxiliary equipment | current efficiency | voltage loss, V | efficiency relative to G, free energy voltage, 1.22 V | efficiency, relative to H, thermoneutral voltage, 1.47 V
fuel cell, stack | Activation polarisation at the electrodes: the necessary overvoltage to start chemical reaction |  |  |  |  | 0 | [5 empty] | 0.2 | [5 empty] | 0.15 | [5 empty] | 0.15 | [5 empty] | 0.02
| Ohmic polarisation (resistance of electrolyte) |  |  |  |  | 0 | [5 empty] | 0.15 | [5 empty] | 0.1 | [5 empty] | 0.1 | [5 empty] | 0.05
| Ohmic polarisation (resistance of electrodes) |  |  |  |  | 0 | [5 empty] | 0.1 | [5 empty] | 0.05 | [5 empty] | 0.05 | [5 empty] | 0.03
| Concentration polarisation (depletion of reactants near electrode) |  |  |  |  | 0 | [5 empty] | 0.1 | [5 empty] | 0.05 | [5 empty] | 0.02 | [5 empty] | 0.01
| total voltage drop below free energy voltage |  |  |  |  | 0 | [5 empty] | 0.55 | [5 empty] | 0.35 | [5 empty] | 0.32 | [5 empty] | 0.11
| actual cell voltage, V |  |  |  |  | 1.22 | [5 empty] | 0.67 | [5 empty] | 0.87 | [5 empty] | 0.9 | [5 empty] | 1.11
| voltage efficiency ε v, = reference voltage / actual voltage | [5 empty] | 100% | 82.99% |  |  |  |  | 54.92% | 45.58% |  |  |  |  | 71.31% | 59.18% |  |  |  |  | 73.77% | 61.22% |  |  |  |  | 90.98% | 75.51%
| Faradaic efficiency ε f (hydrogen "escapes" into electrolyte and its chemical energy is lost) |  |  |  | 0% | [5 empty] | 98% | [5 empty] | 98% | [5 empty] | 99% | [5 empty] | 99%
| total stack efficiency, ε stack = ε v * ε f | [5 empty] | 100% | 82.99% |  |  |  |  | 53.82% | 44.67% |  |  |  |  | 69.89% | 58% |  |  |  |  | 73.03% | 60.61% |  |  |  |  | 90.07% | 74.76%
fuel cell - auxiliary equipment | proportion of electricity needed to power auxiiliary kit, L aux |  |  | 0% | [5 empty] | 15% | [5 empty] | 10% | [5 empty] | 5% | [5 empty] | 5%
overall fuel cell efficiency | ε fuelcell = ε stack * (1-L aux) | [5 empty] | 100% | 82.99% |  |  |  |  | 45.75% | 37.97% |  |  |  |  | 62.9% | 52.2% |  |  |  |  | 69.38% | 57.58% |  |  |  |  | 85.57% | 71.02%
Round trip: combination of electrolyser and fuel cell |  |  | Round trip: an ideal, "no-losses" electrolyser & fuel cell | [5 empty] | Round trip: real system 1: good current equipment | [5 empty] | Round trip: real system 2: best current equipment | [5 empty] | Round trip: future system | [5 empty] | Round trip: aspirational future system
[7 empty] | efficiency relative to G | efficiency relative to H |  |  |  |  | efficiency relative to G | efficiency relative to H |  |  |  |  | efficiency relative to G | efficiency relative to H |  |  |  |  | efficiency relative to G | efficiency relative to H |  |  |  |  | efficiency relative to G | efficiency relative to H
round trip efficiency | ε roundtrip net | [5 empty] | 83.11% | 82.99% |  |  |  |  | 22.64% | 22.61% |  |  |  |  | 37.29% | 37.23% |  |  |  |  | 44.39% | 44.32% |  |  |  |  | 63.05% | 62.96%
= ε electro * ε fuelcell
Round trip including power electronics |  |  | Round trip: an ideal, "no-losses" system, inc. PE | [5 empty] | Round trip: real system 1, good current equipment, inc. PE | [5 empty] | Round trip: real system 2: best current equipment, inc. PE | [5 empty] | Round trip: future system, inc. PE | [5 empty] | Round trip: aspirational future system, inc. PE
|  |  | Power electronics efficiencies, % |  |  |  | efficiency relative to G | efficiency relative to H | Power electronics efficiencies, % |  |  |  | efficiency relative to G | efficiency relative to H | Power electronics efficiencies, % |  |  |  | efficiency relative to G | efficiency relative to H | Power electronics efficiencies, % |  |  |  | efficiency relative to G | efficiency relative to H | Power electronics efficiencies, % |  |  |  | efficiency relative to G | efficiency relative to H
Power electronic efficiency | input to electrolyser, η PE in |  | 100% | [5 empty] | 95% | [5 empty] | 97% | [5 empty] | 98% | [5 empty] | 98%
| output from fuel cell, η PE out |  | 100% | [5 empty] | 95% | [5 empty] | 97% | [5 empty] | NA * | *use comon bus connection |  |  |  |  | NA * | *use comon bus connection
Round trip | ε roundtrip total | [5 empty] | 83.11% | 82.99% |  |  |  |  | 20.44% | 20.41% |  |  |  |  | 35.08% | 35.03% |  |  |  |  | 43.5% | 43.44% |  |  |  |  | 61.79% | 61.7%
= ε roundtrip net *η PE in*η PE out