## Slide 1: HAPI Combined Wind and Hydro Power Generation in the Nile
THET THIN ZAR LWIN NIKOLAOS NTAVARINOS ZLATINA PASEVA GERASIMOS PETRATOS

## Slide 2: Contents
Introduction of HAPI concept
1
Conclusions and future work
5
Location
2
Financial analysis
4
Technical insight
3

## Slide 3: Introduction of HAPI concept
Hybrid system of wind and current turbines
Floating structure in the river
Introduction of HAPI Location Technical insight Financial analysis Conclusions and future work
3
[windpowerengineering.com]
[alternative-energy-news.info]

## Slide 4: Aims and objectives
Aims
Investigation of the feasibility of HAPI
      Objectives
      Selection of appropriate location
      System configuration
      Hydrostatic analysis
      Calculation of dynamic loads
      Grid connection
      Financial analysis
4
Introduction of HAPI Location Technical insight Financial analysis Conclusions and future work
4

## Slide 5: Location
Breakdown of selection factors
Water depth, river width
Hydrographical factors
1
-Water stream velocity
-Wind speed
Adequate conditions
2
Navigable channel, human activities
Favorable spatial characteristics
3
5
Introduction of HAPI Location Technical insight Financial analysis Conclusions and future work
5

## Slide 6: Location
6
Selected location: River Nile, Egypt
Al Balyana
HAPI platform
Introduction of HAPI Location Technical insight Financial analysis Conclusions and future work
6

## Slide 7
450 m
Location
Enough width
Depth = 10m
Navigation Channel: 100m
Depth: 10m
Introduction of HAPI Location Technical insight Financial analysis Conclusions and future work

## Slide 8
4
Maximize power output
3
Shallow waters
2
Low stream velocity
5
Legislation
1
Shallow waters
8
Challenges
4
System layout
3
Optimise power output
Introduction of HAPI Location Technical insight Financial analysis Conclusions and future work
8

## Slide 9: System configuration
HAWT
100kW
Position: centre of the platform
4 x 5kW . Distance to each other: 18m
Bottom clearance: 4-5m
9
Wind turbine
River Current Turbines
Introduction of HAPI Location Technical insight Financial analysis Conclusions and future work
9

## Slide 10: Energy Output
Wind profile
Mean wind speed: 6.6 m/s
CF = 41%
360 MWh/year
10
[Windfinder.com]
Wind direction distribution throughout a year
Wind exceedance curve
Introduction of HAPI Location Technical insight Financial analysis Conclusions and future work
10
Notes: satisfaction of local communities needs

## Slide 11: Energy Output
River current profile
60 MWh/year
CF = 35%
Mean current speed: 0.8m/s
11
Contour of stream velocity in a cross-section
Introduction of HAPI Location Technical insight Financial analysis Conclusions and future work
11
[ N.M. Eshra, 2014]
Notes: satisfaction of local communities needs

## Slide 12: Energy Output
12
Total energy output
360+60 = 420 MWh/year
100 typical households
Egypt- Electric Power consumption – kWh per capita
Introduction of HAPI Location Technical insight Financial analysis Conclusions and future work
12
Notes: satisfaction of local communities needs

## Slide 13: Mooring lines
Spread mooring system
Catenary shape
Nominal diameter: 50mm
Break load = 2,700 kN
Normal operation
Touchdown point
Anchored
end
Fairlead
Suspended line length
riverbed
13
Line tension ≈ 40 kN
7m
23m
Depth = 10m
Introduction of HAPI Location Technical insight Financial analysis Conclusions and future work

## Slide 14: Mooring lines
14
Introduction of HAPI Location Technical insight Financial analysis Conclusions and future work

## Slide 15: Hydrostatic Analysis
W- Total weight of the structure Fb- Buoyancy force
The most important Parameters for Stability:
Heel (Starboard Port)
Trim (Fore Aft)
Draught
GM - Metacentric Height
GZ curve
Stable Equilibrium: Total Weight = Buoyancy
15
Introduction of HAPI Location Technical insight Financial analysis Conclusions and future work
15

## Slide 16: Hydrostatic analysis
16
Platform Dimensions | 
Length | 23 m
Beam | 23 m
Height | 3 m
Design Draught | 0.8 m
Added Ballast | 
Total Number of Tanks | 8
Material | Concrete (2080 kg/m3)
Tank Length | 5 m
Tank Beam | 11.5 m
Tank Height | 0.2 m
Quantity | 99%
Operational Draught | 1.16 m
Introduction of HAPI Location Technical insight Financial analysis Conclusions and future work
16

## Slide 17: Hydrostatic analysis
IMO and DNV regulations for floating
pontoons/ barge:
17
Initial GM has to be greater than 0.35m
Freeboard not less than 0.3m
Trim angle to not exceed 10°
Results | 
Draft Amidships | 1.17m
Freeboard | 1.83m
Heel | 0.0°
Trim (+ve by stern) | 0.003m
Trim angle (+ve by stern) | 0.0064°
GMt corrected | 53.789m
GML | 53.789m
Introduction of HAPI Location Technical insight Financial analysis Conclusions and future work
17

## Slide 18: Hydrostatic analysis
18
Initial GMT has to be greater than 0.35m
GZ curve to vanish after 35°
~54m
~80°
Introduction of HAPI Location Technical insight Financial analysis Conclusions and future work
18

## Slide 19: Loading
Dynamic loads
Fwind
Fcurrent
waterline
Wind force = 20kN
Mechanical loads
Bending moment = 53kN∙m
Current force = 15kN
19
Introduction of HAPI Location Technical insight Financial analysis Conclusions and future work
19
Notes: Flap rise at the root of each blade

## Slide 20
20
Introduction of HAPI Location Technical insight Financial analysis Conclusions and future work
20

## Slide 21: Grid connection
21
21
Introduction of HAPI Location Technical insight Financial analysis Conclusions and future work
21

## Slide 22: Grid connection
Riverbed Cables
Distance to the shore: 150m
Dynamic cables: Class three-core XLPE, double wire armor
Twisting and bending forces
Repetitive wear from riverbed
Usage of intermediate buoy
22
Introduction of HAPI Location Technical insight Financial analysis Conclusions and future work
22

## Slide 23: Grid connection
Weak grid → Frequent interruptions
✔ Steady state voltage
✔ Regulation of flicker values
✔ Harmonics within the limits
23
Introduction of HAPI Location Technical insight Financial analysis Conclusions and future work
23

## Slide 24: Financial analysis
Levelised Cost Of Energy (LCOE)
Payback Period
Sensitivity analysis
24
Introduction of HAPI Location Technical insight Financial analysis Conclusions and future work
24

## Slide 25: Financial analysis
Annual O&M Cost
Wind Turbine OPEX
Current Turbines OPEX
LCOE ( £/MWh )
25
Introduction of HAPI Location Technical insight Financial analysis Conclusions and future work
25

## Slide 26: Financial analysis
20 Years Life-time
LCOE= £0.14 p/kWh
Strike Price= £0.16 p/kWh
Slightly expensive for the Local Egyptian households
2020 Target 20% from Renewable Energy
12% from Wind Power
Government Subsidies
Cooperation with other countries
26
Introduction of HAPI Location Technical insight Financial analysis Conclusions and future work
26

## Slide 27: Payback Period
27
Introduction of HAPI Location Technical insight Financial analysis Conclusions and future work
27

## Slide 28: Sensitivity analysis
Wind Turbine Capacity Factor River Current Turbine Capacity Factor
28
Introduction of HAPI Location Technical insight Financial analysis Conclusions and future work
28

## Slide 29: Environmental Impact
Figure: Features of aquaculture production
Fish farming changes
  in areas
  behavior and nature of freshwater fish
29
Introduction of HAPI Location Technical insight Financial analysis Conclusions and future work
29
Notes: Production of 1 kg fish needs around 25 m^3 of water or 12 m^2 of land.
Compared with other hydropower station, the effect on water discharges could be negligible.

## Slide 30: Environmental Impact
Potential impact
  Fish swimming behavior
  Stuck with 1.7m in radius
  Restrict fish movement
Subsequent effect
  Morphological traits
  Habitat connectivity
  Migration routes
Possible mitigation
  Fish-friendly turbine for large array farm
  Width of gaps for large fish to pass through
  Investigation on rotor avoidance zone
30
Introduction of HAPI Location Technical insight Financial analysis Conclusions and future work
30
Notes: Morphological traits: swimming style, size and body shape

## Slide 31: Conclusions
So, what are the outcomes?
Limitation in large scale implementation
Feasible design for river applications
Stable construction under normal operation conditions
Cost-effective with a typical payback period
31
31
Introduction of HAPI Location Technical insight Financial analysis Conclusions and future work
31

## Slide 32: Future Work
Structural analysis
Potential expansion by building arrays
Development of onshore storage techniques
32
32
Introduction of HAPI Location Technical insight Financial analysis Conclusions and future work
32
Notes: (to get more power)
(to make it dispatchable source)
(technological enhancements + more efficient layout)

## Slide 33
Thank you for your attention!
Any Questions?
Thank you for your attention!
Any questions?