## README
This spreadsheet has been set up to evaluate a suitable CHP unit for a small NHS hospital. Demand data for the hospital has been specified along with data regarding the CHP unit performance. The spreadsheet allows you to examine the effect of three variables on CHP performance: 1 - the CHP unit maximum electrical power output, 2 - the fuel type (gas or diesel), and 3 - whether the unit can be throttled. Throttling is the ability to increase or reduce the output of the unit to meet demand. A unit which cannot throttle must switch off when the electrical demand falls below its rated power output. Power cannot be exported from the CHP unit to the grid, so the maximum unit size is limited to the maximum power demand. The CHP unit also includes a mechanism to dump any excess heat that it produces so that it can maintain electrical supply during times of low heat demand; try to keep the heat dumped to a minimum, as this is a waste of energy. The spreadsheet has four pages. The building demand data sheet shows the heat and power consumption for the building for typical days in summer winter and spring/autumn along with seasonal and yearly heat and power demands. The CHP fuel and emissions data sheet shows the CHP unit performance characteristics along with fuel financial and environmental information. The input data sheet shows the three parameters you can change. The results from these changes are displayed in the results sheet, which shows a range of environmental and financial parameters. You can analyse different combinations of CHP unit size, fuel type and engine management (throttling or non-throttling). Some example cases you could explore are: 1. A diesel unit supplying base heat demand with no throttling; 2. A gas unit supplying base power demand with no throttling; 3. A gas unit sized to meet peak power demand which can be throttled; You can also edit the spreadsheet - e.g. changing the load profile, altering the heat/power ratio formula.

## Input Data
You can change the following design variables
Variables
Enter Unit Size kWe: | 300
Throttling? (yes/no) | no
Fuel (gas or diesel) | gas
300
no
gas

## Results
CHP Financial/Environmental Results
Cost £ |  | Maintenance £ Per kWh
191746.3031 |  | 0.012783
Seasonal/Annual Results
| Power | Heat | Ave Load | Fuel | Efficiency | Fuel Cost | Saving | Saving Tonnes | Dumped Heat
| MWh | MWh | % | MWh | % | £ '000 | £ '000 | CO2 | MWh
Summer | 301.125 | 698.0851 | 45.8333 | 1251.9748 | 58.2466 | 12.5197 | 17.0933 | 24.2447 | 31.1121
Transition | 766.5 | 1776.9438 | 58.3333 | 3186.8449 | 63.2229 | 31.8684 | 43.3247 | 61.7138 | 101.5487
Winter | 657 | 1523.0947 | 100 | 2731.5814 | 79.8107 | 27.3158 | 37.8579 | 52.8975 | 0
Yearly Total | 1724.625 | 3998.1235 | 65.625 | 7170.4011 | 66.1258 | 71.704 | 98.2758 | 138.856 | 132.6607
Payback period (years) |  | 1.9511
Graphs for Typical Days
Graphs for Yearly Totals
Summer | Power kW | Heat kW | Loading % | Fuel kW | Efficiency % | Fuel £ | Saving £ | Saving CO2 kg | Excess Heat kW | Transition | Power kW | Heat kW | Loading % | Fuel kW | Efficiency % | Fuel £ | Saving £ | Saving CO2 kg | Excess Heat kW | Winter | Power kW | Heat kW | Loading % | Fuel kW | Efficiency % | Fuel £ | Saving £ | Saving CO2 kg | Excess Heat kW
1 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 1 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 16.4942 | 24.1541 | 95.477 | 1 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0
2 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 2 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0
3 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 3 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0
4 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 4 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0
5 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0 | 5 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0 | 5 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0
6 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0 | 6 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0 | 6 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0
7 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0 | 7 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0 | 7 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0
8 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0 | 8 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0 | 8 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0
9 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 9 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0
10 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 10 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0
11 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 11 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0
12 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 15.2492 | 24.1541 | 245.477 | 12 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 15.0832 | 24.1541 | 265.477 | 12 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0
13 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 16.4942 | 24.1541 | 95.477 | 13 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 13 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0
14 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 14 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0
15 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 15 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0
16 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 16 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0 | 16 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0
17 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0 | 17 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0 | 17 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0
18 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0 | 18 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0 | 18 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0
19 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0 | 19 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0 | 19 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0
20 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0 | 20 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0 | 20 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0
21 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0 | 21 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0 | 21 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0
22 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 22 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0 | 22 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0
23 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 23 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 15.6642 | 24.1541 | 195.477 | 23 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0
24 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 24 | 300 | 695.477 | 100 | 1247.2974 | 79.8107 | 12.473 | 17.2867 | 24.1541 | 0
Daily | 3300 | 7650.2472 | 45.8333 | 13720.2717 | 58.2466 | 137.2027 | 187.3238 | 265.6953 | 340.954 | Daily | 4200 | 9736.6783 | 58.3333 | 17462.164 | 63.2229 | 174.6216 | 237.3954 | 338.1577 | 556.4311 | Daily | 7200 | 16691.4485 | 100 | 29935.1383 | 79.8107 | 299.3514 | 414.8808 | 579.6989 | 0
Sesonal | 301125 | 698085.0604 | 45.8333 | 1251974.7939 | 58.2466 | 12519.7479 | 17093.297 | 24244.7006 | 31112.0564 | Sesonal | 766500 | 1776943.7901 | 58.3333 | 3186844.93 | 63.2229 | 31868.4493 | 43324.6694 | 61713.7834 | 101548.6693 | Sesonal | 657000 | 1523094.6772 | 100 | 2731581.3686 | 79.8107 | 27315.8137 | 37857.8772 | 52897.5286 | 0

## Building Demand Data
Demand data for a small hospital
| Typical Summer Day |  |  |  | Typical Transition (spring/autumn) Day |  |  |  | Typical Winter Day
| Time | Heat | Power |  | Time | Heat | Power |  | Time | Heat | Power
Summer | 1 | 400 | 270 | Transition | 1 | 600 | 310 | Winter | 1 | 1000 | 589
Hourly | 2 | 410 | 265 | Hourly | 2 | 500 | 300 | Hourly | 2 | 1010 | 570
Heat and | 3 | 420 | 290 | Heat and | 3 | 550 | 290 | Heat and | 3 | 1050 | 551
Power | 4 | 350 | 300 | Power | 4 | 560 | 300 | Power | 4 | 1100 | 570
kW | 5 | 700 | 320 | kW | 5 | 800 | 320 | kW | 5 | 2400 | 608
| 6 | 850 | 450 |  | 6 | 950 | 450 |  | 6 | 1700 | 1500
| 7 | 1020 | 600 |  | 7 | 1050 | 600 |  | 7 | 1900 | 1600
| 8 | 1050 | 320 |  | 8 | 1200 | 320 |  | 8 | 2010 | 1700
| 9 | 750 | 270 |  | 9 | 1000 | 270 |  | 9 | 1900 | 1200
| 10 | 420 | 200 |  | 10 | 740 | 200 |  | 10 | 1600 | 600
| 11 | 350 | 210 |  | 11 | 450 | 210 |  | 11 | 1550 | 600
| 12 | 450 | 400 |  | 12 | 430 | 400 |  | 12 | 1700 | 760
| 13 | 600 | 470 |  | 13 | 700 | 270 |  | 13 | 1600 | 513
| 14 | 440 | 300 |  | 14 | 550 | 270 |  | 14 | 1350 | 513
| 15 | 500 | 250 |  | 15 | 450 | 300 |  | 15 | 1300 | 570
| 16 | 750 | 300 |  | 16 | 850 | 770 |  | 16 | 1500 | 1463
| 17 | 1070 | 450 |  | 17 | 1100 | 800 |  | 17 | 1800 | 1520
| 18 | 1090 | 600 |  | 18 | 1200 | 810 |  | 18 | 2020 | 1539
| 19 | 1200 | 770 |  | 19 | 1250 | 850 |  | 19 | 1900 | 1615
| 20 | 1400 | 780 |  | 20 | 1700 | 850 |  | 20 | 1750 | 1615
| 21 | 1450 | 740 |  | 21 | 1650 | 840 |  | 21 | 1800 | 1596
| 22 | 730 | 250 |  | 22 | 1350 | 810 |  | 22 | 1450 | 1400
| 23 | 500 | 240 |  | 23 | 500 | 550 |  | 23 | 1010 | 900
| 24 | 470 | 250 |  | 24 | 570 | 300 |  | 24 | 1020 | 570
Average | kW | 723.75 | 387.2917 | Average | kW | 862.5 | 474.5833 | Average | kW | 1559.1667 | 1027.5833
Max | kW | 1450 | 780 | Max | kW | 1700 | 850 | Max | kW | 2400 | 1700
Min | kW | 350 | 200 | Min | kW | 430 | 200 | Min | kW | 1010 | 513
Daily total | kWh | 17370 | 9295 | Daily total | kWh | 20700 | 11390 | Daily total | kWh | 37420 | 24662
Season | MWh | 3170.025 | 848.1688 | Season | MWh | 3777.75 | 2078.675 | Season | MWh | 3414.575 | 2250.4075
Yearly data
|  | Heat | Power
Average | kW | 1001.9792 | 591.0104
Max | kW | 2400 | 1700
Min | kW | 350 | 200
Total | MWh | 10362.35 | 5177.2513

## CHP, fuel and emissions data
Data for a dual fuel IC engine CHP unit
CHP Fuel Data | [5 empty] | Conventional Fuels Data
|  | Costs £/kWh |  | Emissions kg CO2/kWh |  |  | Costs £/kWh | Emissions kg CO2/kWh
gas £/kwh |  | 0.01 |  | 0.19 |  | grid electricity | 0.08 | 0.43
diesel £/kwh |  | 0.07 |  | 0.25 |  | heating fuel cost | 0.0083 | 0.19
CHP Capital Costs |  |  | CHP Maintenance Costs |  |  | CHP Efficiency | H:P
Size kWe | Capital Cost £/kWe |  | Size kWe | Maintenance Cost £/kWhe | Load %
50 | 914.6101 |  | 50 | 0.018292 | 0.01 | 40.0251 | 1.8318
100 | 796.2143 |  | 100 | 0.015924 | 10 | 46.3096 | 2.0965
200 | 693.1448 |  | 200 | 0.013863 | 20 | 50.9856 | 2.1273
300 | 639.1543 |  | 300 | 0.012783 | 30 | 55.1949 | 2.1457
400 | 603.4176 |  | 400 | 0.012068 | 40 | 59.127 | 2.159
500 | 577.08 |  | 500 | 0.011542 | 50 | 62.8653 | 2.1694
600 | 556.4162 |  | 600 | 0.011128 | 60 | 66.4558 | 2.1779
700 | 539.5235 |  | 700 | 0.01079 | 70 | 69.9281 | 2.1852
800 | 525.3056 |  | 800 | 0.010506 | 80 | 73.3021 | 2.1916
900 | 513.0758 |  | 900 | 0.010262 | 90 | 76.5927 | 2.1972
1000 | 502.3773 |  | 1000 | 0.010048 | 100 | 79.8107 | 2.2023