## Input Data
Ventilation System Design Spreadsheet version 1
Total supply flow rate (m3/s): |  |  |  | 4
System Details
#no | Duct and Geometrical Data | [6 empty] | Fan + Fittings |  | General Data |  |  | Calculated Data | [6 empty] | System Pressures
| name | Shape | Circular | Rectangular |  | Hydraulic | Length | Fitting | Fan | Flowrate | Inlet height | Exit height | Velocity | c/s/ area | Flow fraction | Loss | Pressure Loss | Head Loss | Length | Static Pres | Velocity Pres | Total Pres
|  | (circ or rect) | Diameter | height (m) | width (m) | diameter | (m) | K value | dP (Pa) | m3/s | (m) | (m) | (m/s) | (m2) |  | coefft | (Pa) | (m) | (m) | (Pa) | (Pa) | (Pa)
1 | entry | rect |  | 1.125 | 1.125 | 1.125 | 0 | 1.7 | 0 | 4 | 0 | 0 | 3.1605 | 1.2656 | 1 | 1.02 | 10.1885 | 0.86549 | 0 | -10.1885 | 5.9932 | -4.1953
2 | duct-1 | rect |  | 1.125 | 1.125 | 1.125 | 20 | 0 | 0 | 4 | 0 | 0 | 3.1605 | 1.2656 | 1 | 2.048 | 20.4569 | 1.7378 | 20 | -30.6454 | 5.9932 | -24.6522
3 | filter | rect |  | 1.125 | 1.125 | 1.125 | 0.1 | 2 | 0 | 4 | 0 | 0 | 3.1605 | 1.2656 | 1 | 1.2102 | 12.0887 | 1.0269 | 20.1 | -42.7341 | 5.9932 | -36.7409
4 | fan | rect |  | 1.125 | 1.125 | 1.125 | 0 | 0 | 124.701 | 4 | 0 | 0 | 3.1605 | 1.2656 | 1 | 0 | 0 | 0 | 20.1 | 81.9669 | 5.9932 | 87.9601
5 | heating coil | rect |  | 1.125 | 1.125 | 1.125 | 0.1 | 4 | 0 | 4 | 0 | 0 | 3.1605 | 1.2656 | 1 | 2.4102 | 24.0752 | 2.0451 | 20.2 | 57.8916 | 5.9932 | 63.8849
6 | cooling coil | rect |  | 1.125 | 1.125 | 1.125 | 0.1 | 4 | 0 | 4 | 0 | 0 | 3.1605 | 1.2656 | 1 | 2.4102 | 24.0752 | 2.0451 | 20.3 | 33.8164 | 5.9932 | 39.8097
7 | duct-2 | rect |  | 1.125 | 1.125 | 1.125 | 10 | 0 | 0 | 4 | 0 | 0 | 3.1605 | 1.2656 | 1 | 1.024 | 10.2285 | 0.86888 | 30.3 | 23.588 | 5.9932 | 29.5812
8 | T-junct | rect |  | 1.125 | 1.125 | 1.125 | 0 | 0.9 | 0 | 4 | 0 | 0 | 3.1605 | 1.2656 | 1 | 0.54 | 5.3939 | 0.4582 | 30.3 | 18.1941 | 5.9932 | 24.1873
9 | duct-3 | rect |  | 0.65 | 0.65 | 0.65 | 5 | 0 | 0 | 2 | 0 | 0 | 4.7337 | 0.4225 | 0.5 | 0.22154 | 4.9643 | 0.4217 | 35.3 | 13.2298 | 13.4449 | 26.6747
10 | damper | rect |  | 0.65 | 0.65 | 0.65 | 0.1 | 1.4 | 0 | 2 | 0 | 0 | 4.7337 | 0.4225 | 0.5 | 0.21443 | 4.805 | 0.40817 | 35.4 | 8.4248 | 13.4449 | 21.8697
11 | duct-4 | rect |  | 0.65 | 0.65 | 0.65 | 5 | 0 | 0 | 2 | 0 | 0 | 4.7337 | 0.4225 | 0.5 | 0.22154 | 4.9643 | 0.4217 | 40.4 | 3.4605 | 13.4449 | 16.9054
12 | outlet grill | rect |  | 0.65 | 0.65 | 0.65 | 0.1 | 1 | 0 | 2 | 0 | 0 | 4.7337 | 0.4225 | 0.5 | 0.15443 | 3.4605 | 0.29396 | 40.5 | 0 | 13.4449 | 13.4449
[14 empty] | total: |  | 11.4747 | 124.701 | 10.593
Note: insert rows to add extra system data
Flow | Head loss | Pressure Loss
m3/s | (m) | (Pa)
0 | 0 | 0
0.01 | 9.7474e-05 | 0.0011475
0.1 | 0.0097474 | 0.11475
1 | 0.97474 | 11.4747
2 | 3.899 | 45.8986
3 | 8.7727 | 103.2719
4 | 15.5959 | 183.5945
5 | 24.3685 | 286.8665
6 | 35.0907 | 413.0877
7 | 47.7623 | 562.2583
8 | 62.3835 | 734.3781
9 | 78.9541 | 929.4473
10 | 97.4742 | 1147.4658
20 | 389.8967 | 4589.8634
30 | 877.2675 | 10327.1926
40 | 1559.5866 | 18359.4535
50 | 2436.8541 | 28686.6462