## Contents
Contents
1 | User Guide
2 | Building survey
3 | Energy reduction options
4 | Heating energy calculation; space, hot water and mechanical ventilation supply air
5 | Cooling energy calculation; equipment and mechanical ventilation supply air
6 | Electrical energy calculation; equipment, lighting, chiller, HVAC equipment and absorption chiller
7 | Predicted energy consumption
8 | Simple payback data
9 | Economic, environmental and energy summary
10 | Energy profiles
11 | Annual weather data

## User Guide
User Guide
1 | Aim
The aim of this tool is to allow the user to representatively model the annual energy consumption of an existing building and analyse refurbishment options for energy reduction. It allows the user to compare the building performance to benchmarks figures and identify the highest energy consumers. Energy reduction options are compared relatively and values should not be taken as absolute. It also provides a method of altering electrical and thermal demand profiles post refurbishment.
2 | Building survey
A survey should be carried out on the building to be refurbished. The relevant energy consumption data (as outlined in the 'Building Survey' worksheet) should be gathered. If possible the facilities management team should be interviewed and operating and maintenance manuals collected, to get an overall view of the building services and controls. Alternatively for a new building the proposed design details and anticipated operation can be used.
3 | Energy reduction options
Based on the building survey and the financial position of the user, energy reduction measures can be selected from this table for potential application.
4 | Heating energy calculation
4.1 | Space heating
The annual energy used to provide space heating can be calculated using two methods. 1) Steady state heat loss corrected for plant and distribution efficiency, followed by the degree day method or 2) Dynamic thermal simulation. A representative area of the overall building would be modelled and an average W/m2 figured applied to the full facility. The use of the thermal simulation is essential if thermal profiles are required to size generation plant such as combined heat and power.
Steady state heat loss:
This is a simple way of estimating the heat loss through each element of the building by applying a thermal transmittance value (U-value) to each construction. This U-values should be calculated as per CIBSE Guide A 3.3, 1999. The user is required to provide the areas of exposed building fabric. U-values, infiltration rates, design temperature, plant and distribution efficiency can be altered to represent design changes.
Degree day method:
This is a method for estimating the annual energy required for space heating. Degree days are used to compare the variation in load demand in different climatic locations and time periods. The standard method is used to assess, for monthly periods, the daily difference between a base temperature and the 24hour mean outside temperature. The monthly degree day figures are then added together to represent the overall heating season. The user is required to provide correction factors based on the function of their building and degree day data relevant to the location. For full details of the method refer to CIBSE Guide B 18.9, 1988. Free monthly degree day data for several locations can be found at www.vesma.com.
Dynamic thermal simulation:
This method requires the user to model a representative area of the building over the period of one year. A kWhrs/year/m2 is then applied to the heated area of the facility. This method takes into account accurately internal heat gains, control set points and through he use of hourly weather data, solar heat gains, time varying thermal transmittance and infiltration rates.
4.2 | Hot water heating
The annual energy used to provide hot water is calculated by estimating the number of occupants and applying a average daily consumption figure per occupant. Daily hot water consumption for various types of commercial buildings an be found in CIBSE Guide B, Table B4.8, 1988. The user is required to select a value appropriate to their building, provide the cold feed temperature, storage temperature and distribution efficiency (calculated based on the level of insulation on the flow and return pipework).
4.3 | Mechanical ventilation supply air heating
The annual energy used to temper supply air is calculated by estimating the volume flowrate of air that is being supplied through application of air change rates (alternatively if known air handling unit volumes should be used). This is converted to a heat load based on external temperature data. The user is required to collect external temperature distribution data relating to the hours of operation, this can be found in dynamic simulation programme climate databases. Heat recovery efficiency can be varied to represent heat recovery devices.
5 | Cooling energy calculation
5.1 | Equipment cooling loads
The annual energy used to provide direct space cooling for equipment loads (fan coil units, chilled beams) is calculated by applying a W/m2 figure to the equivalent floor area. The user should calculate this by surveying the installed equipment and the operational times. Alternatively a rule of thumb can be applied from a source such as 'BSRIA Guidelines for assessing building services' although this is at the expense of accuracy.
5.2 | Space Cooling
The annual energy used to cool supply air is calculated by estimating the volume flowrate of air that is being supplied through application of air change rates (alternatively if known air handling unit volumes should be used). This is converted to a cooling load based on external temperature data. The user is required to collect external temperature distribution data relating to the hours of operation, this can be found in dynamic simulation programme climate databases.
6 | Electrical energy calculation
6.1 | Equipment power loads
The annual energy used to power equipment (computers, photocopiers, printers etc) is calculated by applying a W/m2 figure to the equivalent floor area. The user should calculate this by surveying the installed equipment and identifying when the equipment is in use. Alternatively a rule of thumb can be applied from a source such as 'BSRIA Guidelines for assessing building services' although this is at the expense of accuracy.
6.2 | Lighting
The annual energy used for lighting is calculated by applying a W/m2 figure to the equivalent floor area. The user should calculate this by surveying the installed luminaries and lamp types. They should observe typical patterns of use and record daily time periods when lights are on. (Typically for an office this is from the start of the working day to finish regardless of daylight hours). Alternatively a rule of thumb can be applied from a source such as 'BSRIA Guidelines for assessing building services' although this is at the expense of accuracy. The W/m2 figure can be varied to represent high efficiency luminaries or control gear. To analyse lighting controls the user is required to model a representative area of the building over the period of one year. The revised kWhrs/year/m2 is then applied to the equivalent area of the facility. This method takes into account accurately the times when lights can be switched off in perimeter zones due to natural daylight availability.
6.3 | Chiller
The annual energy used to provide chilled water is calculated by adding the equipment and air supply cooling load. A distribution efficiency and co-efficient of performance for the chiller is then applied. The user must define these parameters.
6.4 | HVAC Equipment
The annual energy used to power the pumps and fans is calculated by multiplying each systems resistance with its flow rate. The air flow rate is taken from the heating work sheet. The peak heating and cooling load for the air supply has to calculated from the annual weather data worksheet. The flow rates are then multiplied by the system resistance to give an overall power consumption. The resistance has to be calculated by the user using CIBSE C reference data. The user also has to determine the operating periods based on building occupation and control start times.
6.5 | Absorption Cooling
The absorption chiller is appraised as set out in Good Practice Guide 256, Best Practice Programme. The annual energy used to provide chilled water is calculated by adding the equipment and air supply peak cooling loads. A co-efficient of performance for the chiller is defined by the user. Corrected cost data should be inputted if available from a contractor's quote.
7 | Predicted energy consumption
This table is a summary of the annual energy consumption as predicted by the tool. It allows the user to look at overall energy consumption and its reduction as measures are applied. It also allows the user to compare thermal and electrical consumption against relevant benchmarks.
8 | Simple payback data
This table is used to calculate budget capital costs for the energy reduction measures selected. The data is based on published cost models but is highly variable. Ideally the user should seek quotes based on their actual building parameters.
9 | Economic, environmental and energy summary
This table is a summary of the energy reduction measures. It allows the measures to be compared using relative units of cost and carbon dioxide emissions. A subjective social factor is also included to allow the impact of the measures to be rated by the user. The user is wholly responsible for calculating the figures for entry.
10 | Energy profiles
This worksheet contains the base thermal and electrical supply profiles. These require to be modified for selected energy efficiency measures based on simulation results or hand calculations. Representative periods should be utilised to model a full year. (For the case study a sample day was used to represent summer, winter and autumn periods). Half hourly data should be taken for each period to allow the profile to be broken down and manipulated. The resulting figures are used as input to the GENCalc tool. The user is required to carry out this analysis and manipulate their own supply data in a similar fashion.
11 | Annual weather data
These tables hold annual weather data in the form of external temperature distribution frequency. This data has to be gathered by the user from an appropriate climate database.

## Building Survey
Building Survey
General: University academic office type building based on Graham Hills operation and plant
Building Type: Academic/Office |  | Year of Construction: 1960's
Gross Internal Floor Area: | 30,000m2
Construction Details | External Wall: | 1.2 | U-Value: | W/m2K
| Roof: | 0.75 | U-Value: | W/m2K
| Floor | 0.75 | U-Value: | W/m2K
| Glazing: | 5.2 | U-Value: | W/m2K
Internal Design Temperature (oC): |  | 21
Energy Consumption Details: | [6 empty] | Additional Notes:
University tariffs: 0.045 £/kWh electricity, 0.007 £kWh gas
Metered data available: | Gas: | Yes/No | Electricity: | Yes/No | If yes please obtain:
Utility bills available: | Gas: | Yes/No | Electricity: | Yes/No | If yes Please obtain
Tariffs: | Gas: | £/kWh | Electricity: | £/kWh
Occupancy | [6 empty] | Additional Notes
Day Occupancy | Number of Occupants: |  | 1500 | Duration of Occupancy: |  | 08:00-18:00 | Occupancy based on 1 person per 20m2 GIFA.
Evening Occupancy: | Number of Occupants: |  | 500 | Duration of Occupancy: |  | 18:00-20:00
Weekend: | Number of Occupants: |  | 0 | Duration of Occupancy: |  | Closed
Cleaning: | Number of Occupants: |  | 50 | Duration of Occupancy: |  | 06:00-08:00
Plant Operation | [6 empty] | Operational Times Description:
Central Plant: | Yes/No | Type: Boiler, Chiller |  | Control: | Yes |  | Preheat 5am- 8am. Full operation 8am-8:30pm. Shut down with fabric protection weather compensation at 5oC.
Local plant: | Yes/No | Type: n/a |  | Control: | n/a
Mechanical and Electrical Services: | [6 empty] | Additional Notes/Areas Served:
Mechanical Ventilation: | Yes/No | Openable Windows: | Yes/No | Fan Efficiency: | 65 | % | Mixed mode, internal core areas mechanical ventilation. Perimeter offices natural ventilation.
|  |  |  | Motor Efficiency: | 75 | %
|  |  |  | Inverter Drive: |  | Yes/No
|  | Air Handling Unit Components: |  | preheat, heating coil, cooling coil
|  |  |  | Heat Recovery Type: |  | n/a
|  |  |  | Heat Recovery Efficiency: |  | n/a
Air Conditioning: | Yes/No | Chiller Type: |  | COP: |  | 2.5
|  |  |  | Distribution Efficiency: |  | 94%
|  |  |  | Pump Efficiency: |  | 75%
|  |  |  | Variable Drive: |  | Yes/No
Heating: | Yes/No | Boiler Type: Shell & Tube, LTHW |  | Boiler Efficiency: |  | 75%
|  |  |  | Distribution Efficiency: |  | 95%
|  |  |  | Pump Efficiency: |  | 75%
|  |  |  | Variable Drive: |  | Yes/No
Hot Water Service: | Yes/No | HWS Type: Calorifier |  | Generation Efficiency: |  | 82%
|  |  |  | Distribution Efficiency: |  | 75%
|  |  |  | Pump Efficiency: |  | 75%
|  |  |  | Variable Drive: |  | Yes/No
Lighting: |  | Luminaries/Lamp Type: | T12 | Efficiency: |  | %
Controls: | Yes/No | Building Management System: |  | Yes/No | If yes please describe:
|  | Lighting Control: |  | Yes/No | If yes please describe:
|  | Occupancy Detection: |  | Yes/No | If yes please describe:
| Boiler Operation: |  | On/Off/Modulated |  | Times: | see above
| Chiller Plant Operation: |  | On/Off/Modulated |  | Times: | 24 hrs

## Energy Reduction Options
Energy Reduction Options vs Costs
Efficiency Measures | No Cost Options* | Low Cost Options* | Capital Cost Options*
Building Fabric |  | Improve air tightness by draught stripping to reduce infiltration rates. | Add/upgrade thermal insulation to reduce losses. Particular attention to roof void.
Upgrade glazing to double, triple or solar control.
Utilise solar shading to reduce cooling loads.
Space Heating | Match space temperature set-points to space usage avoiding overheating. | Add/upgrade thermal insulation to plant and distribution circuit to reduce losses. | Upgrade burner for better conversion efficiency.
| Reduce internal design temperature. |  | Replace conventional boiler with condensing type.
Replace boiler with high efficiency heat pump.
Replace existing pump motors with high efficiency types.
Domestic Hot Water |  | Add/upgrade thermal insulation to plant and distribution circuit to reduce losses. | Replace existing pump motors with high efficiency types.
Small Power | Switch off electrical equipment when not in use. | Install power factor correction equipment.
Install energy efficient appliances.
Artificial Lighting | Switch off lights when areas not in use or natural light available. | Install high efficiency luminaries/domestic bulbs.
Replace luminaries with high efficiency reflectors.
Air Conditioning | Matching space temperature set-points to space usage avoiding over cooling. | Add/upgrade thermal insulation to plant and distribution circuit to reduce losses. | Install free cooling chiller to utilise ambient temperature when sufficiently low.
Increase chilled water distribution temperature.
Utilise night purge cooling to reduce day time loads.
Mechanical Ventilation | Increase natural ventilation usage. |  | Install heat recovery devices.
Replace existing fan motors with high efficiency types.
Control Systems | Matching time switch settings to true occupancy. Adjust for BST-GMT switch. | Automatic lighting control using time switches or occupancy sensors. | Install building energy management system to monitor and control plant.
|  | Automatic HVAC plant set backs using time switches or occupancy sensors. Install inverter drives on fans and pumps for this purpose. | Install daylighting sensing controls to increase natural lighting usage.
|  | Improve HVAC control using compensators and thermostatically controlled zone and radiator valves. | Replace lighting system with high frequency control gear.
No Cost Option: Typically good house keeping practices and implemented as part of an energy savings campaign.
Low Cost Options: Typically requiring investment of less than 5% of the annual energy bill and payback within 3-5 years.
Capital Cost Options: Typically when no or low cost schemes have been implemented or when major plant changes are
required at end of life. The economics of these schemes improve when implemented as part of normal refurbishment work
and payback can be reduced to less than 5 years.

## Heating Energy Calc
Heat Loss Calculation: | [16 empty] | Degree Day Method: | [9 empty] | Hot Water Consumption: |  |  |  |  | Mech Vent Supply Air Heating:
U-values: | External Wall: | 1.2 | W/m²K |  |  | User Input | [11 empty] | Correction Factor: |  | Base Temperature (oC): |  | 18 | Ratio | 1.3 |  |  |  | Average occupancy per m2: |  | 0.05 |  |  | Heat Recovery Efficiency (%): |  | 0%
| Floor: | 0.75 | W/m²K | [16 empty] | Building Response: |  | C | Factor | 1 |  |  |  | Consumption (l/person): |  | 8
| Roof: | 0.75 | W/m²K | [16 empty] | Length of Day (Hours): |  | 24 | Factor | 1.04 |  |  |  | Cold feed temperature (oC): |  | 10
| Glazing: | 5.2 | W/m²K | [16 empty] | Length of Week (Days): |  | 7 | Factor | 1 |  |  |  | Storage temperature (oC): |  | 65
[20 empty] | Structure: |  | Heavy
Area Name | Floor Area | Volume | External Wall | Glazing | Infiltration | Internal Temperature | External Temperature | Heat Loss Floor | Heat Loss Roof | Heat Loss Wall | Heat Loss Glazing | Heat Loss Infiltration | Total Heat Loss | Boiler Efficiency | Distribution Efficiency | Corrected Heat Loss | Degree Days | Internal Heat Gain | Corrected Degree Days | Equivalent Full Load | Building Response Correction | Length of Day Correction | Length of Week Correction | Corrected Equivalent Full Load | Space Heating Energy | ESP-r Calculation | Number of Occupants | Average Consumption | Heat Load | Distribution Efficiency | Hot Water Heating Energy | Day AC/Hour | Evening AC/Hour | Day Volume Flowrate | Evening Volume Flowrate | Heat Recovery Efficiency | Design Temperature | Day Heating Energy | Evening Heating Energy
| (m²) | (m³) | (m²) | (m²) | (Air ch/hr) | (ºC) | (ºC) | (W) | (W) | (W) | (W) | (W) | (kW) | (%) | (%) | (kW) |  | (K) |  | (hrs) |  |  |  | (hrs) | (kWhrs/year) | (kWhrs/year) |  | (l/s) | (kW) | (%) | (kWhrs/year) |  |  | (m3/s) | (m3/s) | (%) | (oC) | (kWhrs/year) | (kWhrs/year)
Basement
Car Park | 3750 | [15 empty] | 2314 | 3 | 3008.2 |  | 1 | 1.04 | 1
Level 0
Perimeter Offices | 1504 | 3910.4 | 572 | 114.4 | 2 | 21 | -4 | 28200 | 0 | 13728 | 14872 | 65173.3333 | 121.9733 | 75% | 95% | 170.7627 | 2314 | 3 | 3008.2 | 2887.872 | 1 | 1.04 | 1 | 3003.3869 | 512866.3527 | 173411.2 | 75.2 | 0.006963 | 1.6084 | 75% | 18786.6311
Core Office | 752 | 1955.2 | 0 | 0 | 0.25 | 21 | -4 | 14100 | 0 | 0 | 0 | 4073.3333 | 18.1733 | 75% | 95% | 25.4427 | 2314 | 3 | 3008.2 | 2887.872 | 1 | 1.04 | 1 | 3003.3869 | 76414.1713 | 86705.6 | 37.6 | 0.0034815 | 0.80422 | 75% | 9393.3156 | 6 | 6 | 3.2587 | 3.2587 | 0% | 19 | 81280.7271 | 26634.8749
Core Academic | 940 | 2444 | 0 | 0 | 0.25 | 21 | -4 | 17625 | 0 | 0 | 0 | 5091.6667 | 22.7167 | 75% | 95% | 31.8033 | 2314 | 3 | 3008.2 | 2887.872 | 1 | 1.04 | 1 | 3003.3869 | 95517.7141 | 108382 | 47 | 0.0043519 | 1.0053 | 75% | 11741.6444 | 5 | 5 | 3.3944 | 3.3944 | 0% | 19 | 84667.4241 | 27744.6614
Ancillary | 366 | 951.6 | 104 | 20.8 | 2 | 21 | -4 | 47580 | 0 | 2496 | 2704 | 15860 | 68.64 | 75% | 95% | 96.096 | 2314 | 3 | 3008.2 | 2887.872 | 1 | 1.04 | 1 | 3003.3869 | 288613.4656 | 42199.8 | 18.3 | 0.0016944 | 0.39142 | 75% | 4571.7467 | 4 | 2 | 1.0573 | 0.52867 | 0% | 19 | 26373.0019 | 4321.0834
Corridor/Stair Well | 188
Level 1
Perimeter Offices | 1504 | 3910.4 | 572 | 114.4 | 2 | 21 | -4 | 0 | 0 | 13728 | 11440 | 65173.3333 | 90.3413 | 75% | 95% | 126.4779 | 2314 | 3 | 3008.2 | 2887.872 | 1 | 1.04 | 1 | 3003.3869 | 379861.9654 | 173411.2 | 75.2 | 0.006963 | 1.6084 | 75% | 18786.6311
Core Office | 752 | 1955.2 | 0 | 0 | 0.25 | 21 | -4 | 0 | 0 | 0 | 0 | 4073.3333 | 4.0733 | 75% | 95% | 5.7027 | 2314 | 3 | 3008.2 | 2887.872 | 1 | 1.04 | 1 | 3003.3869 | 17127.3142 | 86705.6 | 37.6 | 0.0034815 | 0.80422 | 75% | 9393.3156 | 6 | 6 | 3.2587 | 3.2587 | 0% | 19 | 81280.7271 | 26634.8749
Core Academic | 940 | 2444 | 0 | 0 | 0.25 | 21 | -4 | 0 | 0 | 0 | 0 | 5091.6667 | 5.0917 | 75% | 95% | 7.1283 | 2314 | 3 | 3008.2 | 2887.872 | 1 | 1.04 | 1 | 3003.3869 | 21409.1428 | 108382 | 47 | 0.0043519 | 1.0053 | 75% | 11741.6444 | 5 | 5 | 3.3944 | 3.3944 | 0% | 19 | 84667.4241 | 27744.6614
Ancillary | 366 | 951.6 | 104 | 20.8 | 2 | 21 | -4 | 0 | 0 | 2496 | 2080 | 15860 | 20.436 | 75% | 95% | 28.6104 | 2314 | 3 | 3008.2 | 2887.872 | 1 | 1.04 | 1 | 3003.3869 | 85928.1 | 42199.8 | 18.3 | 0.0016944 | 0.39142 | 75% | 4571.7467 | 4 | 2 | 1.0573 | 0.52867 | 0% | 19 | 26373.0019 | 4321.0834
Corridor/Stair Well | 188 | [24 empty] | 21676.4
Level 2
Perimeter Offices | 1504 | 3910.4 | 572 | 114.4 | 2 | 21 | -4 | 0 | 0 | 13728 | 11440 | 65173.3333 | 90.3413 | 75% | 95% | 126.4779 | 2314 | 3 | 3008.2 | 2887.872 | 1 | 1.04 | 1 | 3003.3869 | 379861.9654 | 173411.2 | 75.2 | 0.006963 | 1.6084 | 75% | 18786.6311
Core Office | 752 | 1955.2 | 0 | 0 | 0.25 | 21 | -4 | 0 | 0 | 0 | 0 | 4073.3333 | 4.0733 | 75% | 95% | 5.7027 | 2314 | 3 | 3008.2 | 2887.872 | 1 | 1.04 | 1 | 3003.3869 | 17127.3142 | 86705.6 | 37.6 | 0.0034815 | 0.80422 | 75% | 9393.3156 | 6 | 6 | 3.2587 | 3.2587 | 0% | 19 | 81280.7271 | 26634.8749
Core Academic | 940 | 2444 | 0 | 0 | 0.25 | 21 | -4 | 0 | 0 | 0 | 0 | 5091.6667 | 5.0917 | 75% | 95% | 7.1283 | 2314 | 3 | 3008.2 | 2887.872 | 1 | 1.04 | 1 | 3003.3869 | 21409.1428 | 108382 | 47 | 0.0043519 | 1.0053 | 75% | 11741.6444 | 5 | 5 | 3.3944 | 3.3944 | 0% | 19 | 84667.4241 | 27744.6614
Ancillary | 366 | 951.6 | 104 | 20.8 | 2 | 21 | -4 | 0 | 0 | 2496 | 2080 | 15860 | 20.436 | 75% | 95% | 28.6104 | 2314 | 3 | 3008.2 | 2887.872 | 1 | 1.04 | 1 | 3003.3869 | 85928.1 | 42199.8 | 18.3 | 0.0016944 | 0.39142 | 75% | 4571.7467 | 4 | 2 | 1.0573 | 0.52867 | 0% | 19 | 26373.0019 | 4321.0834
Corridor/Stair Well | 188 | [24 empty] | 21676.4
Level 3
Perimeter Offices | 1504 | 3910.4 | 572 | 114.4 | 2 | 21 | -4 | 0 | 0 | 13728 | 11440 | 65173.3333 | 90.3413 | 75% | 95% | 126.4779 | 2314 | 3 | 3008.2 | 2887.872 | 1 | 1.04 | 1 | 3003.3869 | 379861.9654 | 173411.2 | 75.2 | 0.006963 | 1.6084 | 75% | 18786.6311
Core Office | 752 | 1955.2 | 0 | 0 | 0.25 | 21 | -4 | 0 | 0 | 0 | 0 | 4073.3333 | 4.0733 | 75% | 95% | 5.7027 | 2314 | 3 | 3008.2 | 2887.872 | 1 | 1.04 | 1 | 3003.3869 | 17127.3142 | 86705.6 | 37.6 | 0.0034815 | 0.80422 | 75% | 9393.3156 | 6 | 6 | 3.2587 |  | 0% | 19 | 81280.7271
Core Academic | 940 | 2444 | 0 | 0 | 0.25 | 21 | -4 | 0 | 0 | 0 | 0 | 5091.6667 | 5.0917 | 75% | 95% | 7.1283 | 2314 | 3 | 3008.2 | 2887.872 | 1 | 1.04 | 1 | 3003.3869 | 21409.1428 | 108382 | 47 | 0.0043519 | 1.0053 | 75% | 11741.6444 | 5 | 5 | 3.3944 |  | 0% | 19 | 84667.4241
Ancillary | 366 | 951.6 | 104 | 20.8 | 2 | 21 | -4 | 0 | 0 | 2496 | 2080 | 15860 | 20.436 | 75% | 95% | 28.6104 | 2314 | 3 | 3008.2 | 2887.872 | 1 | 1.04 | 1 | 3003.3869 | 85928.1 | 42199.8 | 18.3 | 0.0016944 | 0.39142 | 75% | 4571.7467 | 3 | 2 | 0.793 |  | 0% | 19 | 19779.7514
Corridor/Stair Well | 188
Level 4
Perimeter Offices | 1504 | 3910.4 | 572 | 114.4 | 2 | 21 | -4 | 0 | 0 | 13728 | 11440 | 65173.3333 | 90.3413 | 75% | 95% | 126.4779 | 2314 | 3 | 3008.2 | 2887.872 | 1 | 1.04 | 1 | 3003.3869 | 379861.9654 | 173411.2 | 75.2 | 0.006963 | 1.6084 | 75% | 18786.6311
Core Office | 752 | 1955.2 | 0 | 0 | 0.25 | 21 | -4 | 0 | 0 | 0 | 0 | 4073.3333 | 4.0733 | 75% | 95% | 5.7027 | 2314 | 3 | 3008.2 | 2887.872 | 1 | 1.04 | 1 | 3003.3869 | 17127.3142 | 86705.6 | 37.6 | 0.0034815 | 0.80422 | 75% | 9393.3156 | 6 | 6 | 3.2587 |  | 0% | 19 | 81280.7271
Core Academic | 940 | 2444 | 0 | 0 | 0.25 | 21 | -4 | 0 | 0 | 0 | 0 | 5091.6667 | 5.0917 | 75% | 95% | 7.1283 | 2314 | 3 | 3008.2 | 2887.872 | 1 | 1.04 | 1 | 3003.3869 | 21409.1428 | 108382 | 47 | 0.0043519 | 1.0053 | 75% | 11741.6444 | 5 | 5 | 3.3944 |  | 0% | 19 | 84667.4241
Ancillary | 366 | 951.6 | 104 | 20.8 | 2 | 21 | -4 | 0 | 0 | 2496 | 2080 | 15860 | 20.436 | 75% | 95% | 28.6104 | 2314 | 3 | 3008.2 | 2887.872 | 1 | 1.04 | 1 | 3003.3869 | 85928.1 | 42199.8 | 18.3 | 0.0016944 | 0.39142 | 75% | 4571.7467 | 3 | 2 | 0.793 |  | 0% | 19 | 19779.7514
Corridor/Stair Well | 188 | [24 empty] | 21676.4
Level 5
Perimeter Offices | 1504 | 3910.4 | 572 | 114.4 | 2 | 21 | -4 | 0 | 0 | 13728 | 11440 | 65173.3333 | 90.3413 | 75% | 95% | 126.4779 | 2314 | 3 | 3008.2 | 2887.872 | 1 | 1.04 | 1 | 3003.3869 | 379861.9654 | 173411.2 | 75.2 | 0.006963 | 1.6084 | 75% | 18786.6311
Core Office | 752 | 1955.2 | 0 | 0 | 0.25 | 21 | -4 | 0 | 0 | 0 | 0 | 4073.3333 | 4.0733 | 75% | 95% | 5.7027 | 2314 | 3 | 3008.2 | 2887.872 | 1 | 1.04 | 1 | 3003.3869 | 17127.3142 | 86705.6 | 37.6 | 0.0034815 | 0.80422 | 75% | 9393.3156 | 6 | 6 | 3.2587 |  | 0% | 19 | 81280.7271
Core Academic | 940 | 2444 | 0 | 0 | 0.25 | 21 | -4 | 0 | 0 | 0 | 0 | 5091.6667 | 5.0917 | 75% | 95% | 7.1283 | 2314 | 3 | 3008.2 | 2887.872 | 1 | 1.04 | 1 | 3003.3869 | 21409.1428 | 108382 | 47 | 0.0043519 | 1.0053 | 75% | 11741.6444 | 5 | 5 | 3.3944 |  | 0% | 19 | 84667.4241
Ancillary | 366 | 951.6 | 104 | 20.8 | 2 | 21 | -4 | 0 | 0 | 2496 | 2080 | 15860 | 20.436 | 75% | 95% | 28.6104 | 2314 | 3 | 3008.2 | 2887.872 | 1 | 1.04 | 1 | 3003.3869 | 85928.1 | 42199.8 | 18.3 | 0.0016944 | 0.39142 | 75% | 4571.7467 | 3 | 2 | 0.793 |  | 0% | 19 | 19779.7514
Corridor/Stair Well | 188
Level 6
Perimeter Offices | 1504 | 3910.4 | 572 | 114.4 | 2 | 21 | -4 | 0 | 28200 | 13728 | 11440 | 65173.3333 | 118.5413 | 75% | 95% | 165.9579 | 2314 | 3 | 3008.2 | 2887.872 | 1 | 1.04 | 1 | 3003.3869 | 498435.6794 | 173411.2 | 75.2 | 0.006963 | 1.6084 | 75% | 18786.6311
Core Office | 752 | 1955.2 | 0 | 0 | 0.25 | 21 | -4 | 0 | 14100 | 0 | 0 | 4073.3333 | 18.1733 | 75% | 95% | 25.4427 | 2314 | 3 | 3008.2 | 2887.872 | 1 | 1.04 | 1 | 3003.3869 | 76414.1713 | 86705.6 | 37.6 | 0.0034815 | 0.80422 | 75% | 9393.3156 | 6 | 6 | 3.2587 |  | 0% | 19 | 81280.7271
Core Academic | 940 | 2444 | 0 | 0 | 0.25 | 21 | -4 | 0 | 17625 | 0 | 0 | 5091.6667 | 22.7167 | 75% | 95% | 31.8033 | 2314 | 3 | 3008.2 | 2887.872 | 1 | 1.04 | 1 | 3003.3869 | 95517.7141 | 108382 | 47 | 0.0043519 | 1.0053 | 75% | 11741.6444 | 5 | 5 | 3.3944 |  | 0% | 19 | 84667.4241
Ancillary | 366 | 951.6 | 104 | 20.8 | 2 | 21 | -4 | 0 | 6862.5 | 2496 | 2080 | 15860 | 27.2985 | 75% | 95% | 38.2179 | 2314 | 3 | 3008.2 | 2887.872 | 1 | 1.04 | 1 | 3003.3869 | 114783.1394 | 42199.8 | 18.3 | 0.0016944 | 0.39142 | 75% | 4571.7467 | 3 | 2 | 0.793 |  | 0% | 19 | 19779.7514
Corridor/Stair Well | 188
Level 7
Roof Plantroom | 3750 | [35 empty] | Sub Total: | 1319875.0702 | 113080.1561
Totals | 30000 | 64828.4 |  | 946.4 |  |  |  | 107505 | 66787.5 | 113568 | 98696 | 631388.3333 | 1017.9448 |  |  | 1425.1228 | [6 empty] | Total kWhrs/Yr: |  | 4280195.0198 | 2939919.4 |  |  | Total kWhrs/Yr: |  | 311453.3644 |  |  | 52.1228 | 13.8349 |  | Total kWhrs/Yr: |  | 1432955.2262

## Cooling Energy Calc
Equipment Cooling Loads: |  |  |  | Mech Vent Air Cooling:
| Equipment cooling load (W/m2): |  | 30
| No of hours per day (hrs/day): |  | 10.5
| No of days per year(days/year): |  | 260
Area Name | Floor Area | Cooling Load | Equipment Cooling | Day AC/Hour | Evening AC/Hour | Day Volume Flowrate | Evening Volume Flowrate | Design Temperature | Day Cooling | Night Cooling
| (m²) | (kW) | (kWhrs/year) |  |  | (m3/s) | (m3/s) | (oC) | (kWhrs/year) | (kWhrs/year)
Basement
Car Park | 3750
Level 0
Perimeter Offices | 1504
Core Office | 752 |  |  | 3 | 2 | 1.6293 | 1.0862 | 20 | 465.2724 | 64.4021
Core Academic | 940 | 28.2 | 76986 | 4 | 2 | 2.7156 | 1.3578 | 20 | 775.454 | 80.5026
Ancillary | 366
Corridor/Stair Well | 188
Level 1
Perimeter Offices | 1504
Core Office | 752 |  |  | 3 | 2 | 1.6293 | 1.0862 | 20 | 465.2724 | 64.4021
Core Academic | 940 | 28.2 | 76986 | 4 | 2 | 2.7156 | 1.3578 | 20 | 775.454 | 80.5026
Ancillary | 366
Corridor/Stair Well | 188
Level 2
Perimeter Offices | 1504
Core Office | 752 |  |  | 3 | 2 | 1.6293 |  | 20 | 465.2724
Core Academic | 940 | 28.2 | 76986 | 4 | 2 | 2.7156 |  | 20 | 775.454
Ancillary | 366
Corridor/Stair Well | 188
Level 3
Perimeter Offices | 1504
Core Office | 752 |  |  | 3 | 2 | 1.6293 |  | 20 | 465.2724
Core Academic | 940 | 28.2 | 76986 | 4 | 2 | 2.7156 |  | 20 | 775.454
Ancillary | 366
Corridor/Stair Well | 188
Level 4
Perimeter Offices | 1504
Core Office | 752 |  |  | 3 | 2 | 1.6293 |  | 20 | 465.2724
Core Academic | 940 | 28.2 | 76986 | 4 | 2 | 2.7156 |  | 20 | 775.454
Ancillary | 366
Corridor/Stair Well | 188
0
Level 5 | 0
Perimeter Offices | 1504
Core Office | 752 |  |  | 3 | 2 | 1.6293 |  | 20 | 465.2724
Core Academic | 940 | 28.2 | 76986 | 4 | 2 | 2.7156 |  | 20 | 775.454
Ancillary | 366
Corridor/Stair Well | 188
Level 6
Perimeter Offices | 1504
Core Office | 752 |  |  | 3 | 2 | 1.6293 |  | 20 | 465.2724
Core Academic | 940 | 28.2 | 76986 | 4 | 2 | 2.7156 |  | 20 | 775.454
Ancillary | 366
Corridor/Stair Well | 188
Level 7
Roof Plantroom | 3750 | [6 empty] | Sub Total: | 8685.0853 | 289.8095
| Total kWhrs/Yr: |  | 538902 |  |  |  |  | Total kWhrs/Yr: |  | 8974.8948

## Electrical Energy
Equipment Power Loads: |  |  |  | Lighting Loads: |  |  | Chiller Load: |  |  | HVAC Equipment: | [8 empty] | Absorption Chiller:
| Equip. load office(W/m2): |  | 10 | No of hours per day (hrs/day): |  | 10.5 | Chiller Plant COP: |  | 2.5 |  |  | Pump Efficiency (%): |  | 75% |  |  |  |  | From 'Cooling Energy Calc' work sheet calculate peak load: |  |  |  | 343.7 | kW | 131.6 Equipment
| Equip. load academic(W/m2): |  | 10 | No of days per year(days/year): |  | 260 | [5 empty] | Fan Efficiency (%): |  | 65% |  |  |  |  | From 'Air cooling' and 'Chiller power' work sheet calculate base load: |  |  |  |  | kW | 6.06*35 AHU
| No of hours per day (hrs/day): |  | 10.5 | [8 empty] | Motor Efficiency (%): |  | 75% |  |  |  |  | District Heating flow temperature: |  |  |  | 90 | oC
| No of days per year(days/year): |  | 260 | [8 empty] | LTHW Flow Temperature (oC): |  | 82 | Return (oC): | 71 |  |  | District Heating return temperature: |  |  |  | 80 | oC
| Percentage use factor: |  | 0.75 | [8 empty] | CHW Flow Temperature (oC): |  | 12 | Return (oC): | 6 |  |  | Absorption chiller co-efficient of performance: |  |  |  | 0.68 | COP
Area Name | Floor Area | Volume | Equipment Load | Lighting Load | Percentage Use Factor | Lighting Load | Total Cooling Energy | Distribution Efficiency | Chiller Energy | System | Design Load | Design flow rate | Design flow rate | System Resistance | System Power | Hours Per Day | Hours Per Day | Annual Energy | Required building side flow temperature: |  |  |  | 6 | oC
[19 empty] | Required building side return temperature: |  |  |  | 12 | oC
| (m²) | (m³) | (kWhrs/year) | (W/m2) | (%) | (kWhrs/year) | (kWhrs/year) | (%) | (kWhrs/year) |  | (kW) | (l/s) | (m3/s) | (kPa) | (kW) | (hrs/day) |  | (kWhrs/year)
Basement | [18 empty] | Waste heat required to be provided from district heating system to provide match cooling requirement: |  |  |  | 505.4412 | kW
Car Park | 3750 |  |  | 8 | 1 | 81900 |  |  |  | LTHW (VT) Pump | 1425.1228 | 30.8468 |  | 200 | 10.9678 | 24 | 260 | 68438.7961
[10 empty] | LTHW(CT) Pump | 1050 | 22.7273 |  | 200 | 8.0808 | 14.5 | 260 | 30464.6465
Level 0 | [9 empty] | CHW Pump | 343.7 | 13.6389 |  | 100 | 2.4247 | 10.5 | 260 | 6619.4074 |  | Absorption Chiller
Perimeter Offices | 1504 | 3910.4 | 30794.4 | 12 | 0.8 | 39416.832 | [12 empty] | Capital Cost
Core Office | 752 | 1955.2 | 15397.2 | 12 | 1 | 24635.52 | 529.6745 | 94% | 224.582 | Extract AHU Fan (x7) |  |  | 5.04 | 350 | 3.6185 | 14.5 | 260 | 13641.6 | Chiller | 50544.1176
[10 empty] | Supply AHU Fan (x7) |  |  | 5.04 | 300 | 3.1015 | 14.5 | 260 | 11692.8 | Dry Coolers | 36846.6618
[19 empty] | Chemical Dosing | 7369.3324
Core Academic | 940 | 2444 | 19246.5 | 12 | 1 | 30794.4 | 77841.9567 | 94% | 33004.9896 | [6 empty] | Total kWhrs/Yr: |  | 130857.2499 | Heat Supply P/W | 5776.4706
Ancillary | 366 | 951.6 |  | 12 | 0.3 | 3597.048 | [12 empty] | Condenser Pumps | 12282.2206
Corridor/Stair Well | 188 |  |  | 8 | 0.3 | 1231.776 | [12 empty] | Builders Work | 12636.0294
[19 empty] | Electrical (Main) | 53.0713
Level 1 | [18 empty] | Electrical (Auxiliary) | 644.8166
Perimeter Offices | 1504 | 3910.4 | 30794.4 | 12 | 0.8 | 39416.832 | [12 empty] | Total: | 126152.7203
Core Office | 752 | 1955.2 | 15397.2 | 12 | 1 | 24635.52 | 529.6745 | 94% | 224.582
Core Academic | 940 | 2444 | 19246.5 | 12 | 1 | 30794.4 | 77841.9567 | 94% | 33004.9896 | [9 empty] | Running Cost
Ancillary | 366 | 951.6 |  | 12 | 0.3 | 3597.048 | [12 empty] | Maintenance | 2527.2059
Corridor/Stair Well | 188 |  |  | 8 | 0.3 | 1231.776 | [12 empty] | Heat Source (Pumps) | 1091.7529
[19 empty] | Electrical (Main) | 127.2013
Level 2 | [18 empty] | Electrical (Auxiliary) | 1103.926
Perimeter Offices | 1504 | 3910.4 | 30794.4 | 12 | 0.8 | 39416.832 | [12 empty] | Total: | 4850.0862
Core Office | 752 | 1955.2 | 15397.2 | 12 | 1 | 24635.52 | 465.2724 | 94% | 197.2755
Core Academic | 940 | 2444 | 19246.5 | 12 | 1 | 30794.4 | 77761.454 | 94% | 32970.8565 | [9 empty] | Season Air Cooling: | 3805.3554 | kWh/Yr
Ancillary | 366 | 951.6 |  | 12 | 0.3 | 3597.048 | [12 empty] | Season Equip Cooling: | 70305.984 | kWh/Yr
Corridor/Stair Well | 188 |  |  | 8 | 0.3 | 1231.776 | [12 empty] | Electrical Energy Saving: | 74111.3394 | kWh/Yr | 3335.0103
[19 empty] | Payback (Years) | 37.8268
Level 3
Perimeter Offices | 1504 | 3910.4 | 30794.4 | 12 | 0.8 | 39416.832 | [12 empty] | nb. Waste heat has to be completely free and is assumed to be available during the cooling season June - September inclusive (4 months,16weeks, 5 days a week at 10.5hrs a day = 840hrs)
Core Office | 752 | 1955.2 | 15397.2 | 12 | 1 | 24635.52 | 465.2724 | 94% | 197.2755
Core Academic | 940 | 2444 | 19246.5 | 12 | 1 | 30794.4 | 77761.454 | 94% | 32970.8565
Ancillary | 366 | 951.6 |  | 12 | 0.3 | 3597.048
Corridor/Stair Well | 188 |  |  | 8 | 0.3 | 1231.776
Level 4
Perimeter Offices | 1504 | 3910.4 | 30794.4 | 12 | 0.8 | 39416.832
Core Office | 752 | 1955.2 | 15397.2 | 12 | 1 | 24635.52 | 465.2724 | 94% | 197.2755
Core Academic | 940 | 2444 | 19246.5 | 12 | 1 | 30794.4 | 77761.454 | 94% | 32970.8565
Ancillary | 366 | 951.6 |  | 12 | 0.3 | 3597.048
Corridor/Stair Well | 188 |  |  | 8 | 0.3 | 1231.776
0
Level 5 | 0
Perimeter Offices | 1504 | 3910.4 | 30794.4 | 12 | 0.8 | 39416.832
Core Office | 752 | 1955.2 | 15397.2 | 12 | 1 | 24635.52 | 465.2724 | 94% | 197.2755
Core Academic | 940 | 2444 | 19246.5 | 12 | 1 | 30794.4 | 77761.454 | 94% | 32970.8565
Ancillary | 366 | 951.6 |  | 12 | 0.3 | 3597.048
Corridor/Stair Well | 188 |  |  | 8 | 0.3 | 1231.776
Level 6
Perimeter Offices | 1504 | 3910.4 | 30794.4 | 12 | 0.8 | 39416.832
Core Office | 752 | 1955.2 | 15397.2 | 12 | 1 | 24635.52 | 465.2724 | 94% | 197.2755
Core Academic | 940 | 2444 | 19246.5 | 12 | 1 | 30794.4 | 77761.454 | 94% | 32970.8565
Ancillary | 366 | 951.6 |  | 12 | 0.3 | 3597.048
Corridor/Stair Well | 188 |  |  | 8 | 0.3 | 1231.776
Level 7
Roof Plantroom | 3750 |  |  | 5 | 0.3 | 15356.25
| Total kWhrs/Yr: |  | 458066.7 | Total kWhrs/Yr: |  | 713085.282 | Total kWhrs/Yr: |  | 232299.8034
Note on N14: ahu peak load 30kW for 1m3/s x total m3/s
Note on N15: ahu peak load 6.06kW for 1m3/s x total m3/s + peak equipment 131.6kW
Note on S13: fabric protection constant
Note on S14: ahu coils only

## Simple Payback Data
Simple Payback Data (Office/Academic)
Efficiency Measures | Low Cost Options | Approximate Cost £/m2 GIA | Capital Cost Options | Approximate Cost £/m2 GIA
Building Fabric | Improve air tightness by draught stripping to reduce infiltration rates. | Sealant Windows 4-10 £/m2 of overall glazed area. | Add/upgrade thermal insulation to reduce losses. Particular attention to roof void. | Roof Insulation 8-15 £/m2, Floor Insulation 8-20 £/m2, Cavity Insulation - variable.
|  |  | Upgrade glazing to double, triple or solar control. | Replacement cost - variable.
Utilise solar shading to reduce cooling loads.
Space Heating | Add/upgrade thermal insulation to plant and distribution circuit to reduce losses. | 15mm dia p/w 6.44 £/m ,32 mm dia p/w 7.37 £/m, 100mm dia p/w 14.51 £/m. Typical thickness. ROT: System length = (height + (perimeter*no of floors)) *2. Add 20% to overall cost for fittings. | Upgrade burner for better conversion efficiency. | Replace without refurbishment 2.1 £/per kW - 4.5 £/per kW boiler output. If refurbishing additional cost negligible £/m2.
|  |  | Replace conventional boiler with condensing type. | Replace without refurbishment 4.86 £/m2. If refurbishing additional cost 0.45 £/m2.
|  |  | Replace boiler with high efficiency heat pump. | Replace without refurbishment 7.29 £/m2. If refurbishing additional cost 2.88 £/m2.
|  |  | Replace existing pump motors with high efficiency types. | Replace without refurbishment 219 £/per pump - 345 £/per pump. If refurbishing additional cost negligible £/m2.
Domestic Hot Water | Add/upgrade thermal insulation to plant and distribution circuit to reduce losses. | 15mm dia p/w 6.44 £/m ,32 mm dia p/w 7.37 £/m, 100mm dia p/w 14.51 £/m. Typical thickness. ROT: System length = (height + (perimeter*no of floors)) *2. Add 20% to overall cost for fittings. | Replace existing pump motors with high efficiency types. | Replace without refurbishment 219 £/per pump - 345 £/per pump. If refurbishing additional cost negligible £/m2.
Small Power | Install power factor correction equipment.
| Install energy efficient appliances. | Replacement cost of IT equipment and lab academic equipment.
Artificial Lighting | Install high efficiency luminaries. | 33 £/m2 net internal area. Upgrade to T5. Ballast and lamp replaced.
| Replace luminaries with high efficiency reflectors. | 1.65 £/m2 net internal area. For office type lighting system.
Air Conditioning | Add/upgrade thermal insulation to plant and distribution circuit to reduce losses. | 15mm dia p/w 6.44 £/m ,32 mm dia p/w 7.37 £/m, 100mm dia p/w 14.51 £/m. Typical thickness. ROT: System length = (height + (perimeter*no of floors)) *2. Add 20% to overall cost for fittings. | Install free cooling chiller to utilise ambient temperature when sufficiently low. | Replace without refurbishment 11.22 £/m2. If refurbishing additional cost 1.55 £/m2.
Mechanical Ventilation |  |  | Install heat recovery devices. | RAC 560 £/per m3, PHE 716 £/per m3, TW 720 £/per m3,
|  |  | Replace existing fan motors with high efficiency types. | Replace without refurbishment 219 £/per fan - 345 £/per fan. If refurbishing additional cost negligible £/m2.
Control Systems | Automatic lighting control using time switches or occupancy sensors. | 8.15 £/m2 net internal area. For office type lighting system. | Install building energy management system to monitor and control plant. | 10.50 £/m2 gross internal area, 14.58 £/m2 net internal area.
| Automatic HVAC plant set backs using time switches or occupancy sensors. Install inverter drives on fans and pumps for this purpose. | Central control 1.27 £/m2 gross internal area, 1.76 £/m2 net internal area. Field equipment 0.60 £/m2 gross internal area, 0.83 £/m2 net internal area | Install daylighting sensing controls to increase natural lighting usage. | 10.60 £/m2 net internal area. For office type lighting system.
| Improve HVAC control using compensators and thermostatically controlled zone and radiator valves. | Thermostatic valves 34.17 £/per valve 15mm dia - 39.45 £/per valve 20mm dia. Compensator valves 22.13 £/per valve 15mm dia - 26.16 £/per valve 20mm dia. | Replace lighting system with high frequency control gear.
All costs include: material and installation labour. Costs scaled to 30,000m2. Costs are indicative only.

## Predicted Energy
Predicted Energy Consumption:
Energy User | Thermal |  | Electricity
| kWhr/annum | £/Annum | kWhr/annum | £/Annum
Space Heating | 4280195.0198 | 29961.3651
HWS | 311453.3644 | 2180.1736
AHU Heating | 1432955.2262 | 10030.6866
Equipment Power |  |  | 458066.7 | 20613.0015
Lighting |  |  | 713085.282 | 32088.8377
Chiller |  |  | 232299.8034 | 10453.4912
HVAC Equipment |  |  | 130857.2499 | 5888.5762
Total Base Load & Costs | 6024603.6105 | 42172.2253 | 1534309.0353 | 69043.9066
Annual kWh/m2 | 200.8201 |  | 51.1436
Typical kWh/m2: | 150 |  | 50
Metered Data kWh/m2: | 0 |  | 0
Predicted | 200.8201
Typical | 150
Metered | 0
Predicted | 51.1436
Typical | 50
Metered | 0

## EEE Summary
Economic, environmental and energy summary: | [7 empty] | Table Of Social Impact Factor: | [5 empty] | NPV Calculation (for information):
Recommendations | Estimated Annual Saving |  |  | Simple Payback |  | NPV | Social Factor |  | Energy Savings |  |  |  |  | Draught Stripping |  |  |  | Thermal Insulation |  |  |  | Heat Recovery |  |  |  | High Efficiency Luminaries & Control |  |  |  | HVAC Controls |  |  |  | High Efficiency Motors
| Cost Saving | Energy Saving | CO2 Saving | Budget Capital Cost | Payback | (15 years) |  | Functionality | 1 | 2 | 3 | 4 | 5 | 0 | 9464 |  |  | 0 | 2847.77 |  |  | 0 | 25200 |  |  | 0 | 134940.2 |  |  | 0 | 37400 |  |  | 0 | 3723
| (£) | (kWh) | (kg CO2) | (£) | (years) |  |  | 5 | 5 | 10 | 15 | 20 | 25 | 1 | 4173.88 | 0.943 | 3935.9688 | 1 | 458.98 | 0.943 | 432.8181 | 1 | 5015.34 | 0.943 | 4729.4656 | 1 | 13399.29 | 0.943 | 12635.5305 | 1 | 4085.52 | 0.943 | 3852.6454 | 1 | 981.43 | 0.943 | 925.4885
Draught stripping to external windows | 4173.876 | 596268 | 113290.92 | 9464 | 0.44103 | 31068.55 | 4 | [6 empty] | 2 | 4173.88 | 0.89 | 3714.7532 | 2 | 458.98 | 0.89 | 408.4922 | 2 | 5015.34 | 0.89 | 4463.6526 | 2 | 13399.29 | 0.89 | 11925.3681 | 2 | 4085.52 | 0.89 | 3636.1128 | 2 | 981.43 | 0.89 | 873.4727
Increase thermal insulation on HWS distribution and plant | 458.9844 | 65569.2 | 12458.148 | 2847.77 | 6.2045 | 1609.39 | 4 | 4 | 4 | 8 | 12 | 16 | 20 | 3 | 4173.88 | 0.84 | 3506.0592 | 3 | 458.98 | 0.84 | 385.5432 | 3 | 5015.34 | 0.84 | 4212.8856 | 3 | 13399.29 | 0.84 | 11255.4036 | 3 | 4085.52 | 0.84 | 3431.8368 | 3 | 981.43 | 0.84 | 824.4012
Install thermal wheel heat recovery on AHU's | 5015.3404 | 716477.2 | 136130.668 | 25200 | 5.0246 | 23503.97 | 5 | 3 | 3 | 6 | 9 | 12 | 15 | 4 | 4173.88 | 0.792 | 3305.713 | 4 | 458.98 | 0.792 | 363.5122 | 4 | 5015.34 | 0.792 | 3972.1493 | 4 | 13399.29 | 0.792 | 10612.2377 | 4 | 4085.52 | 0.792 | 3235.7318 | 4 | 981.43 | 0.792 | 777.2926
Install high efficiency luminaries | [7 empty] | 2 | 2 | 4 | 6 | 8 | 10 | 5 | 4173.88 | 0.747 | 3117.8884 | 5 | 458.98 | 0.747 | 342.8581 | 5 | 5015.34 | 0.747 | 3746.459 | 5 | 13399.29 | 0.747 | 10009.2696 | 5 | 4085.52 | 0.747 | 3051.8834 | 5 | 981.43 | 0.747 | 733.1282
Automatic lighting control | 13399.2869 | 297761.93 | 128037.6299 | 134940.2 | 10.0707 | -4819.69 | 6 | 1 | 1 | 2 | 3 | 4 | 5 | 6 | 4173.88 | 0.705 | 2942.5854 | 6 | 458.98 | 0.705 | 323.5809 | 6 | 5015.34 | 0.705 | 3535.8147 | 6 | 13399.29 | 0.705 | 9446.4994 | 6 | 4085.52 | 0.705 | 2880.2916 | 6 | 981.43 | 0.705 | 691.9081
Automatic plant set backs, variable speed drives | 4085.5163 | 90789.25 | 39039.3775 | 37400 | 9.1543 | 2274.485 | 5 | [6 empty] | 7 | 4173.88 | 0.665 | 2775.6302 | 7 | 458.98 | 0.665 | 305.2217 | 7 | 5015.34 | 0.665 | 3335.2011 | 7 | 13399.29 | 0.665 | 8910.5279 | 7 | 4085.52 | 0.665 | 2716.8708 | 7 | 981.43 | 0.665 | 652.6509
Replace HVAC motors with high efficiency type | 981.4275 | 21809.5 | 9378.085 | 3723 | 3.7935 | 5807.667 | 5 | Functionality Scale: | [5 empty] | 8 | 4173.88 | 0.627 | 2617.0228 | 8 | 458.98 | 0.627 | 287.7805 | 8 | 5015.34 | 0.627 | 3144.6182 | 8 | 13399.29 | 0.627 | 8401.3548 | 8 | 4085.52 | 0.627 | 2561.621 | 8 | 981.43 | 0.627 | 615.3566
[8 empty] | 5 | No impact on occupants |  |  |  |  | 9 | 4173.88 | 0.592 | 2470.937 | 9 | 458.98 | 0.592 | 271.7162 | 9 | 5015.34 | 0.592 | 2969.0813 | 9 | 13399.29 | 0.592 | 7932.3797 | 9 | 4085.52 | 0.592 | 2418.6278 | 9 | 981.43 | 0.592 | 581.0066
[8 empty] | 4 | Minimum impact on occupants/Minor interruption to building services |  |  |  |  | 10 | 4173.88 | 0.558 | 2329.025 | 10 | 458.98 | 0.558 | 256.1108 | 10 | 5015.34 | 0.558 | 2798.5597 | 10 | 13399.29 | 0.558 | 7476.8038 | 10 | 4085.52 | 0.558 | 2279.7202 | 10 | 981.43 | 0.558 | 547.6379
[8 empty] | 3 | Minimum impact on occupants/Temporary interruption to building services |  |  |  |  | 11 | 4173.88 | 0.527 | 2199.6348 | 11 | 458.98 | 0.527 | 241.8825 | 11 | 5015.34 | 0.527 | 2643.0842 | 11 | 13399.29 | 0.527 | 7061.4258 | 11 | 4085.52 | 0.527 | 2153.069 | 11 | 981.43 | 0.527 | 517.2136
[8 empty] | 2 | Major impact on occupants/Short term interruption to building services |  |  |  |  | 12 | 4173.88 | 0.497 | 2074.4184 | 12 | 458.98 | 0.497 | 228.1131 | 12 | 5015.34 | 0.497 | 2492.624 | 12 | 13399.29 | 0.497 | 6659.4471 | 12 | 4085.52 | 0.497 | 2030.5034 | 12 | 981.43 | 0.497 | 487.7707
[8 empty] | 1 | Major impact on occupants/Long term interruption to building services |  |  |  |  | 13 | 4173.88 | 0.469 | 1957.5497 | 13 | 458.98 | 0.469 | 215.2616 | 13 | 5015.34 | 0.469 | 2352.1945 | 13 | 13399.29 | 0.469 | 6284.267 | 13 | 4085.52 | 0.469 | 1916.1089 | 13 | 981.43 | 0.469 | 460.2907
[14 empty] | 14 | 4173.88 | 0.442 | 1844.855 | 14 | 458.98 | 0.442 | 202.8692 | 14 | 5015.34 | 0.442 | 2216.7803 | 14 | 13399.29 | 0.442 | 5922.4862 | 14 | 4085.52 | 0.442 | 1805.7998 | 14 | 981.43 | 0.442 | 433.7921
[14 empty] | 15 | 4173.88 | 0.417 | 1740.508 | 15 | 458.98 | 0.417 | 191.3947 | 15 | 5015.34 | 0.417 | 2091.3968 | 15 | 13399.29 | 0.417 | 5587.5039 | 15 | 4085.52 | 0.417 | 1703.6618 | 15 | 981.43 | 0.417 | 409.2563
[8 empty] | Energy Savings Scale: | [8 empty] | 40532.5487 |  |  |  | 4457.1548 |  |  |  | 48703.9667 |  |  |  | 130120.5052 |  |  |  | 39674.4847 |  |  |  | 9530.6667
[8 empty] | 5 | >20 kg of CO2/m2 |  | Compared to typical office 40% saving. | [5 empty] | 31068.5487 |  |  |  | 1609.3848 |  |  |  | 23503.9667 |  |  |  | -4819.6948 |  |  |  | 2274.4847 |  |  |  | 5807.6667
[8 empty] | 4 | 20-15 kg of CO2/m2 |  | Compared to typical office 40-30% saving.
[8 empty] | 3 | 15-10 kg of CO2/m2 |  | Compared to typical office 30-20% saving.
[8 empty] | 2 | 10-5 kg of CO2/m2 |  | Compared to typical office 20-10% saving.
[8 empty] | 1 | 5-2.5 kg of CO2/m2 |  | Compared to typical office 10-5% saving.

## Energy Profile
Base Case: Thermal Profiles
Office Base Case (T): Jan 3rd | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1479.732 | 1768.9597 | 1768.9955 | 1761.0473 | 1733.5295 | 1737.2939 | 1694.2917 | 1703.8172 | 1671.4383 | 1672.3842 | 1670.0209 | 1629.503 | 1526.305 | 1445.4876 | 1358.9281 | 1259.7535 | 1178.0828 | 1135.4325 | 1082.6709 | 787.3356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Office Base Case (T): March 8th | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1036.8985 | 1303.5313 | 1294.6469 | 1258.8268 | 1221.4791 | 1225.5095 | 1229.036 | 1215.7609 | 1185.8762 | 1162.1281 | 1146.2015 | 1103.6899 | 991.3376 | 924.6863 | 822.5288 | 748.8091 | 693.0571 | 671.7307 | 670.1283 | 493.3839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Office Base Case (T): July 4th | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243.825 | 228.6375 | 209.6925 | 190.23 | 166.2825 | 175.5975 | 195.0825 | 206.6175 | 205.29 | 179.865 | 153.96 | 160.0875 | 167.0325 | 145.035 | 134.8275 | 155.7675 | 187.2075 | 242.025 | 267.0825 | 189.8812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Base Case modified for heat recovery: thermal wheel efficiency 50%.
From predicted energy consumption worksheet AHU heating load 24% of overall thermal load.
Office Base Case: Jan 3rd | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1479.732 | 1768.9597 | 1768.9955 | 1761.0473 | 1733.5295 | 1737.2939 | 1694.2917 | 1703.8172 | 1671.4383 | 1672.3842 | 1670.0209 | 1629.503 | 1526.305 | 1445.4876 | 1358.9281 | 1259.7535 | 1178.0828 | 1135.4325 | 1082.6709 | 787.3356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AHU Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355.1357 | 424.5503 | 424.5589 | 422.6514 | 416.0471 | 416.9505 | 406.63 | 408.9161 | 401.1452 | 401.3722 | 400.805 | 391.0807 | 366.3132 | 346.917 | 326.1427 | 302.3408 | 282.7399 | 272.5038 | 259.841 | 188.9605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Saved | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177.5678 | 212.2752 | 212.2795 | 211.3257 | 208.0235 | 208.4753 | 203.315 | 204.4581 | 200.5726 | 200.6861 | 200.4025 | 195.5404 | 183.1566 | 173.4585 | 163.0714 | 151.1704 | 141.3699 | 136.2519 | 129.9205 | 94.4803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Office Revised: Jan 3rd | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1302.1642 | 1556.6845 | 1556.716 | 1549.7217 | 1525.5059 | 1528.8186 | 1490.9767 | 1499.3591 | 1470.8657 | 1471.6981 | 1469.6184 | 1433.9626 | 1343.1484 | 1272.0291 | 1195.8567 | 1108.5831 | 1036.7129 | 999.1806 | 952.7504 | 692.8553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Office Base Case: March 8th | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1036.8985 | 1303.5313 | 1294.6469 | 1258.8268 | 1221.4791 | 1225.5095 | 1229.036 | 1215.7609 | 1185.8762 | 1162.1281 | 1146.2015 | 1103.6899 | 991.3376 | 924.6863 | 822.5288 | 748.8091 | 693.0571 | 671.7307 | 670.1283 | 493.3839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AHU Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 248.8556 | 312.8475 | 310.7152 | 302.1184 | 293.155 | 294.1223 | 294.9686 | 291.7826 | 284.6103 | 278.9107 | 275.0884 | 264.8856 | 237.921 | 221.9247 | 197.4069 | 179.7142 | 166.3337 | 161.2154 | 160.8308 | 118.4121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Saved | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124.4278 | 156.4238 | 155.3576 | 151.0592 | 146.5775 | 147.0611 | 147.4843 | 145.8913 | 142.3051 | 139.4554 | 137.5442 | 132.4428 | 118.9605 | 110.9624 | 98.7035 | 89.8571 | 83.1668 | 80.6077 | 80.4154 | 59.2061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Office Revised: March 8th | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 912.4707 | 1147.1076 | 1139.2892 | 1107.7676 | 1074.9016 | 1078.4484 | 1081.5517 | 1069.8696 | 1043.571 | 1022.6727 | 1008.6573 | 971.2471 | 872.3771 | 813.7239 | 723.8253 | 658.952 | 609.8902 | 591.123 | 589.7129 | 434.1779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Office Base Case: July 4th | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243.825 | 228.6375 | 209.6925 | 190.23 | 166.2825 | 175.5975 | 195.0825 | 206.6175 | 205.29 | 179.865 | 153.96 | 160.0875 | 167.0325 | 145.035 | 134.8275 | 155.7675 | 187.2075 | 242.025 | 267.0825 | 189.8812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AHU Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.518 | 54.873 | 50.3262 | 45.6552 | 39.9078 | 42.1434 | 46.8198 | 49.5882 | 49.2696 | 43.1676 | 36.9504 | 38.421 | 40.0878 | 34.8084 | 32.3586 | 37.3842 | 44.9298 | 58.086 | 64.0998 | 45.5715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Saved | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.259 | 27.4365 | 25.1631 | 22.8276 | 19.9539 | 21.0717 | 23.4099 | 24.7941 | 24.6348 | 21.5838 | 18.4752 | 19.2105 | 20.0439 | 17.4042 | 16.1793 | 18.6921 | 22.4649 | 29.043 | 32.0499 | 22.7858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Office Revised: July 4th | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214.566 | 201.201 | 184.5294 | 167.4024 | 146.3286 | 154.5258 | 171.6726 | 181.8234 | 180.6552 | 158.2812 | 135.4848 | 140.877 | 146.9886 | 127.6308 | 118.6482 | 137.0754 | 164.7426 | 212.982 | 235.0326 | 167.0955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Office Base Case: Jan 3rd | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1479.732 | 1768.9597 | 1768.9955 | 1761.0473 | 1733.5295 | 1737.2939 | 1694.2917 | 1703.8172 | 1671.4383 | 1672.3842 | 1670.0209 | 1629.503 | 1526.305 | 1445.4876 | 1358.9281 | 1259.7535 | 1178.0828 | 1135.4325 | 1082.6709 | 787.3356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Office Revised: Jan 3rd | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1302.1642 | 1556.6845 | 1556.716 | 1549.7217 | 1525.5059 | 1528.8186 | 1490.9767 | 1499.3591 | 1470.8657 | 1471.6981 | 1469.6184 | 1433.9626 | 1343.1484 | 1272.0291 | 1195.8567 | 1108.5831 | 1036.7129 | 999.1806 | 952.7504 | 692.8553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Office Base Case: March 8th | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1036.8985 | 1303.5313 | 1294.6469 | 1258.8268 | 1221.4791 | 1225.5095 | 1229.036 | 1215.7609 | 1185.8762 | 1162.1281 | 1146.2015 | 1103.6899 | 991.3376 | 924.6863 | 822.5288 | 748.8091 | 693.0571 | 671.7307 | 670.1283 | 493.3839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Office Revised: March 8th | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 912.4707 | 1147.1076 | 1139.2892 | 1107.7676 | 1074.9016 | 1078.4484 | 1081.5517 | 1069.8696 | 1043.571 | 1022.6727 | 1008.6573 | 971.2471 | 872.3771 | 813.7239 | 723.8253 | 658.952 | 609.8902 | 591.123 | 589.7129 | 434.1779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Office Base Case: July 4th | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243.825 | 228.6375 | 209.6925 | 190.23 | 166.2825 | 175.5975 | 195.0825 | 206.6175 | 205.29 | 179.865 | 153.96 | 160.0875 | 167.0325 | 145.035 | 134.8275 | 155.7675 | 187.2075 | 242.025 | 267.0825 | 189.8812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Office Revised: July 4th | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214.566 | 201.201 | 184.5294 | 167.4024 | 146.3286 | 154.5258 | 171.6726 | 181.8234 | 180.6552 | 158.2812 | 135.4848 | 140.877 | 146.9886 | 127.6308 | 118.6482 | 137.0754 | 164.7426 | 212.982 | 235.0326 | 167.0955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Base Case: Electrical Profiles
Office Base Case (E): Jan 3rd | 262.8339 | 252.5184 | 240.4335 | 235.615 | 255.4714 | 243.4268 | 231.2985 | 236.9784 | 227.9984 | 241.7008 | 278.3676 | 211.8481 | 322.8431 | 291.5278 | 363.5723 | 418.7413 | 461.7016 | 611.4519 | 456.818 | 626.1738 | 612.4156 | 584.5676 | 582.6743 | 512.3403 | 568.8449 | 612.1274 | 612.3319 | 613.7697 | 559.5519 | 567.0662 | 567.3823 | 451.4945 | 481.152 | 546.3701 | 504.1009 | 475.6859 | 453.9052 | 420.0211 | 414.1584 | 396.9947 | 400.174 | 346.5977 | 343.0744 | 291.2427 | 288.5871 | 277.5558 | 256.1283 | 256.308
Office Base Case (E): March 8th | 225.3417 | 216.861 | 251.4589 | 183.2636 | 174.6776 | 185.8716 | 222.2598 | 227.8351 | 209.3777 | 216.1858 | 205.8064 | 231.1772 | 267.3826 | 261.3024 | 376.4202 | 379.0654 | 444.0859 | 567.1392 | 578.5841 | 570.7787 | 560.7771 | 602.5517 | 519.2844 | 513.6968 | 505.1015 | 499.6501 | 541.5671 | 572.795 | 538.1321 | 509.9396 | 501.2948 | 583.4996 | 456.398 | 578.0637 | 470.1815 | 456.8843 | 415.8965 | 388.3297 | 411.6748 | 387.8744 | 428.5463 | 328.2836 | 275.4358 | 208.2781 | 270.6008 | 234.8383 | 244.7593 | 234.4604
Office Base Case (E): July 4th | 188.9913 | 197.9873 | 173.6809 | 173.5416 | 171.5349 | 150.9601 | 170.9837 | 161.5974 | 205.9459 | 167.2521 | 165.0968 | 154.6545 | 204.7877 | 253.7566 | 271.1231 | 262.6473 | 353.5306 | 438.6106 | 516.664 | 526.5984 | 468.6335 | 459.0367 | 459.3681 | 479.9088 | 440.2023 | 557.2995 | 370.123 | 388.9729 | 461.7959 | 503.6887 | 451.7191 | 420.9498 | 587.8396 | 396.2874 | 372.9813 | 384.5414 | 371.0984 | 320.51 | 322.8264 | 307.29 | 247.6003 | 285.4734 | 327.3569 | 330.1811 | 246.2284 | 215.9484 | 198.3465 | 203.2394
Base Case modified for high efficiency luminaries: energy consumption 8W/m2.
From predicted energy consumption worksheet lighting load 46% of overall electrical load.
Office Base Case: Jan 3rd | 262.8339 | 252.5184 | 240.4335 | 235.615 | 255.4714 | 243.4268 | 231.2985 | 236.9784 | 227.9984 | 241.7008 | 278.3676 | 211.8481 | 322.8431 | 291.5278 | 363.5723 | 418.7413 | 461.7016 | 611.4519 | 456.818 | 626.1738 | 612.4156 | 584.5676 | 582.6743 | 512.3403 | 568.8449 | 612.1274 | 612.3319 | 613.7697 | 559.5519 | 567.0662 | 567.3823 | 451.4945 | 481.152 | 546.3701 | 504.1009 | 475.6859 | 453.9052 | 420.0211 | 414.1584 | 396.9947 | 400.174 | 346.5977 | 343.0744 | 291.2427 | 288.5871 | 277.5558 | 256.1283 | 256.308
Lighting Energy | 120.9036 | 116.1585 | 110.5994 | 108.3829 | 117.5168 | 111.9763 | 106.3973 | 109.0101 | 104.8793 | 111.1824 | 128.0491 | 97.4501 | 148.5078 | 134.1028 | 167.2432 | 192.621 | 212.3827 | 281.2679 | 210.1363 | 288.0399 | 281.7112 | 268.9011 | 268.0302 | 235.6765 | 261.6686 | 281.5786 | 281.6727 | 282.3341 | 257.3939 | 260.8505 | 260.9959 | 207.6875 | 221.3299 | 251.3303 | 231.8864 | 218.8155 | 208.7964 | 193.2097 | 190.5128 | 182.6176 | 184.08 | 159.4349 | 157.8142 | 133.9716 | 132.7501 | 127.6757 | 117.819 | 117.9017
Energy Saved | 40.3012 | 38.7195 | 36.8665 | 36.1276 | 39.1723 | 37.3254 | 35.4658 | 36.3367 | 34.9598 | 37.0608 | 42.683 | 32.4834 | 49.5026 | 44.7009 | 55.7477 | 64.207 | 70.7942 | 93.756 | 70.0454 | 96.0133 | 93.9037 | 89.6337 | 89.3434 | 78.5588 | 87.2229 | 93.8595 | 93.8909 | 94.1114 | 85.798 | 86.9502 | 86.9986 | 69.2292 | 73.7766 | 83.7768 | 77.2955 | 72.9385 | 69.5988 | 64.4032 | 63.5043 | 60.8725 | 61.36 | 53.145 | 52.6047 | 44.6572 | 44.25 | 42.5586 | 39.273 | 39.3006
Office Revised: Jan 3rd | 222.5327 | 213.7989 | 203.567 | 199.4874 | 216.2991 | 206.1014 | 195.8328 | 200.6417 | 193.0387 | 204.64 | 235.6846 | 179.3647 | 273.3405 | 246.8268 | 307.8245 | 354.5343 | 390.9073 | 517.6959 | 386.7726 | 530.1605 | 518.5119 | 494.9339 | 493.3309 | 433.7815 | 481.622 | 518.2679 | 518.441 | 519.6583 | 473.754 | 480.1161 | 480.3837 | 382.2653 | 407.3754 | 462.5934 | 426.8054 | 402.7474 | 384.3064 | 355.6179 | 350.6541 | 336.1222 | 338.814 | 293.4527 | 290.4697 | 246.5855 | 244.3371 | 234.9972 | 216.8553 | 217.0075
Office Base Case: March 8th | 225.3417 | 216.861 | 251.4589 | 183.2636 | 174.6776 | 185.8716 | 222.2598 | 227.8351 | 209.3777 | 216.1858 | 205.8064 | 231.1772 | 267.3826 | 261.3024 | 376.4202 | 379.0654 | 444.0859 | 567.1392 | 578.5841 | 570.7787 | 560.7771 | 602.5517 | 519.2844 | 513.6968 | 505.1015 | 499.6501 | 541.5671 | 572.795 | 538.1321 | 509.9396 | 501.2948 | 583.4996 | 456.398 | 578.0637 | 470.1815 | 456.8843 | 415.8965 | 388.3297 | 411.6748 | 387.8744 | 428.5463 | 328.2836 | 275.4358 | 208.2781 | 270.6008 | 234.8383 | 244.7593 | 234.4604
Lighting Energy | 103.6572 | 99.7561 | 115.6711 | 84.3012 | 80.3517 | 85.5009 | 102.2395 | 104.8041 | 96.3137 | 99.4455 | 94.6709 | 106.3415 | 122.996 | 120.1991 | 173.1533 | 174.3701 | 204.2795 | 260.884 | 266.1487 | 262.5582 | 257.9575 | 277.1738 | 238.8708 | 236.3005 | 232.3467 | 229.839 | 249.1209 | 263.4857 | 247.5408 | 234.5722 | 230.5956 | 268.4098 | 209.9431 | 265.9093 | 216.2835 | 210.1668 | 191.3124 | 178.6317 | 189.3704 | 178.4222 | 197.1313 | 151.0104 | 126.7005 | 95.8079 | 124.4764 | 108.0256 | 112.5893 | 107.8518
Energy Saved | 34.5524 | 33.252 | 38.557 | 28.1004 | 26.7839 | 28.5003 | 34.0798 | 34.9347 | 32.1046 | 33.1485 | 31.557 | 35.4472 | 40.9987 | 40.0664 | 57.7178 | 58.1234 | 68.0932 | 86.9613 | 88.7162 | 87.5194 | 85.9858 | 92.3913 | 79.6236 | 78.7668 | 77.4489 | 76.613 | 83.0403 | 87.8286 | 82.5136 | 78.1907 | 76.8652 | 89.4699 | 69.981 | 88.6364 | 72.0945 | 70.0556 | 63.7708 | 59.5439 | 63.1235 | 59.4741 | 65.7104 | 50.3368 | 42.2335 | 31.936 | 41.4921 | 36.0085 | 37.5298 | 35.9506
Office Revised: March 8th | 190.7893 | 183.609 | 212.9019 | 155.1631 | 147.8937 | 157.3713 | 188.1799 | 192.9004 | 177.2731 | 183.0373 | 174.2494 | 195.73 | 226.3839 | 221.2361 | 318.7024 | 320.942 | 375.9927 | 480.1779 | 489.8679 | 483.2593 | 474.7913 | 510.1605 | 439.6608 | 434.9299 | 427.6526 | 423.0371 | 458.5268 | 484.9665 | 455.6185 | 431.7488 | 424.4296 | 494.0297 | 386.417 | 489.4273 | 398.087 | 386.8287 | 352.1257 | 328.7858 | 348.5513 | 328.4003 | 362.8358 | 277.9468 | 233.2023 | 176.3421 | 229.1087 | 198.8297 | 207.2295 | 198.5098
Office Base Case: July 4th | 188.9913 | 197.9873 | 173.6809 | 173.5416 | 171.5349 | 150.9601 | 170.9837 | 161.5974 | 205.9459 | 167.2521 | 165.0968 | 154.6545 | 204.7877 | 253.7566 | 271.1231 | 262.6473 | 353.5306 | 438.6106 | 516.664 | 526.5984 | 468.6335 | 459.0367 | 459.3681 | 479.9088 | 440.2023 | 557.2995 | 370.123 | 388.9729 | 461.7959 | 503.6887 | 451.7191 | 420.9498 | 587.8396 | 396.2874 | 372.9813 | 384.5414 | 371.0984 | 320.51 | 322.8264 | 307.29 | 247.6003 | 285.4734 | 327.3569 | 330.1811 | 246.2284 | 215.9484 | 198.3465 | 203.2394
Lighting Energy | 45.3579 | 47.517 | 41.6834 | 41.65 | 41.1684 | 36.2304 | 41.0361 | 38.7834 | 49.427 | 40.1405 | 39.6232 | 37.1171 | 49.1491 | 60.9016 | 65.0695 | 63.0354 | 84.8473 | 105.2665 | 123.9994 | 126.3836 | 112.472 | 110.1688 | 110.2483 | 115.1781 | 105.6486 | 133.7519 | 88.8295 | 93.3535 | 110.831 | 120.8853 | 108.4126 | 101.028 | 141.0815 | 95.109 | 89.5155 | 92.2899 | 89.0636 | 76.9224 | 77.4783 | 73.7496 | 59.4241 | 68.5136 | 78.5657 | 79.2435 | 59.0948 | 51.8276 | 47.6032 | 48.7774
Energy Saved | 15.1193 | 15.839 | 13.8945 | 13.8833 | 13.7228 | 12.0768 | 13.6787 | 12.9278 | 16.4757 | 13.3802 | 13.2077 | 12.3724 | 16.383 | 20.3005 | 21.6898 | 21.0118 | 28.2824 | 35.0888 | 41.3331 | 42.1279 | 37.4907 | 36.7229 | 36.7494 | 38.3927 | 35.2162 | 44.584 | 29.6098 | 31.1178 | 36.9437 | 40.2951 | 36.1375 | 33.676 | 47.0272 | 31.703 | 29.8385 | 30.7633 | 29.6879 | 25.6408 | 25.8261 | 24.5832 | 19.808 | 22.8379 | 26.1886 | 26.4145 | 19.6983 | 17.2759 | 15.8677 | 16.2591
Office Revised: July 4th | 173.872 | 182.1483 | 159.7865 | 159.6583 | 157.8121 | 138.8833 | 157.305 | 148.6696 | 189.4703 | 153.8719 | 151.889 | 142.2822 | 188.4047 | 233.456 | 249.4333 | 241.6355 | 325.2481 | 403.5217 | 475.3309 | 484.4705 | 431.1428 | 422.3138 | 422.6186 | 441.5161 | 404.9861 | 512.7156 | 340.5131 | 357.855 | 424.8522 | 463.3936 | 415.5816 | 387.2738 | 540.8125 | 364.5844 | 343.1428 | 353.7781 | 341.4105 | 294.8692 | 297.0002 | 282.7068 | 227.7922 | 262.6356 | 301.1684 | 303.7666 | 226.5301 | 198.6726 | 182.4788 | 186.9802
Office Base Case: Jan 3rd | 262.8339 | 252.5184 | 240.4335 | 235.615 | 255.4714 | 243.4268 | 231.2985 | 236.9784 | 227.9984 | 241.7008 | 278.3676 | 211.8481 | 322.8431 | 291.5278 | 363.5723 | 418.7413 | 461.7016 | 611.4519 | 456.818 | 626.1738 | 612.4156 | 584.5676 | 582.6743 | 512.3403 | 568.8449 | 612.1274 | 612.3319 | 613.7697 | 559.5519 | 567.0662 | 567.3823 | 451.4945 | 481.152 | 546.3701 | 504.1009 | 475.6859 | 453.9052 | 420.0211 | 414.1584 | 396.9947 | 400.174 | 346.5977 | 343.0744 | 291.2427 | 288.5871 | 277.5558 | 256.1283 | 256.308
Office Revised: Jan 3rd | 222.5327 | 213.7989 | 203.567 | 199.4874 | 216.2991 | 206.1014 | 195.8328 | 200.6417 | 193.0387 | 204.64 | 235.6846 | 179.3647 | 273.3405 | 246.8268 | 307.8245 | 354.5343 | 390.9073 | 517.6959 | 386.7726 | 530.1605 | 518.5119 | 494.9339 | 493.3309 | 433.7815 | 481.622 | 518.2679 | 518.441 | 519.6583 | 473.754 | 480.1161 | 480.3837 | 382.2653 | 407.3754 | 462.5934 | 426.8054 | 402.7474 | 384.3064 | 355.6179 | 350.6541 | 336.1222 | 338.814 | 293.4527 | 290.4697 | 246.5855 | 244.3371 | 234.9972 | 216.8553 | 217.0075
Office Base Case: March 8th | 225.3417 | 216.861 | 251.4589 | 183.2636 | 174.6776 | 185.8716 | 222.2598 | 227.8351 | 209.3777 | 216.1858 | 205.8064 | 231.1772 | 267.3826 | 261.3024 | 376.4202 | 379.0654 | 444.0859 | 567.1392 | 578.5841 | 570.7787 | 560.7771 | 602.5517 | 519.2844 | 513.6968 | 505.1015 | 499.6501 | 541.5671 | 572.795 | 538.1321 | 509.9396 | 501.2948 | 583.4996 | 456.398 | 578.0637 | 470.1815 | 456.8843 | 415.8965 | 388.3297 | 411.6748 | 387.8744 | 428.5463 | 328.2836 | 275.4358 | 208.2781 | 270.6008 | 234.8383 | 244.7593 | 234.4604
Office Revised: March 8th | 190.7893 | 183.609 | 212.9019 | 155.1631 | 147.8937 | 157.3713 | 188.1799 | 192.9004 | 177.2731 | 183.0373 | 174.2494 | 195.73 | 226.3839 | 221.2361 | 318.7024 | 320.942 | 375.9927 | 480.1779 | 489.8679 | 483.2593 | 474.7913 | 510.1605 | 439.6608 | 434.9299 | 427.6526 | 423.0371 | 458.5268 | 484.9665 | 455.6185 | 431.7488 | 424.4296 | 494.0297 | 386.417 | 489.4273 | 398.087 | 386.8287 | 352.1257 | 328.7858 | 348.5513 | 328.4003 | 362.8358 | 277.9468 | 233.2023 | 176.3421 | 229.1087 | 198.8297 | 207.2295 | 198.5098
Office Base Case: July 4th | 188.9913 | 197.9873 | 173.6809 | 173.5416 | 171.5349 | 150.9601 | 170.9837 | 161.5974 | 205.9459 | 167.2521 | 165.0968 | 154.6545 | 204.7877 | 253.7566 | 271.1231 | 262.6473 | 353.5306 | 438.6106 | 516.664 | 526.5984 | 468.6335 | 459.0367 | 459.3681 | 479.9088 | 440.2023 | 557.2995 | 370.123 | 388.9729 | 461.7959 | 503.6887 | 451.7191 | 420.9498 | 587.8396 | 396.2874 | 372.9813 | 384.5414 | 371.0984 | 320.51 | 322.8264 | 307.29 | 247.6003 | 285.4734 | 327.3569 | 330.1811 | 246.2284 | 215.9484 | 198.3465 | 203.2394
Office Revised: July 4th | 173.872 | 182.1483 | 159.7865 | 159.6583 | 157.8121 | 138.8833 | 157.305 | 148.6696 | 189.4703 | 153.8719 | 151.889 | 142.2822 | 188.4047 | 233.456 | 249.4333 | 241.6355 | 325.2481 | 403.5217 | 475.3309 | 484.4705 | 431.1428 | 422.3138 | 422.6186 | 441.5161 | 404.9861 | 512.7156 | 340.5131 | 357.855 | 424.8522 | 463.3936 | 415.5816 | 387.2738 | 540.8125 | 364.5844 | 343.1428 | 353.7781 | 341.4105 | 294.8692 | 297.0002 | 282.7068 | 227.7922 | 262.6356 | 301.1684 | 303.7666 | 226.5301 | 198.6726 | 182.4788 | 186.9802
Base Case modified for high efficiency luminaries and lighting control. Including subsequent increase in thermal energy:
Sample area modelled in ESP-r. Please see results Table 1 below.
North Office Zone:
Office Revised (E): Jan 3rd | 222.5327 | 213.7989 | 203.567 | 199.4874 | 216.2991 | 206.1014 | 195.8328 | 200.6417 | 193.0387 | 204.64 | 235.6846 | 179.3647 | 273.3405 | 246.8268 | 307.8245 | 354.5343 | 390.9073 | 517.6959 | 386.7726 | 530.1605 | 518.5119 | 494.9339 | 493.3309 | 433.7815 | 481.622 | 518.2679 | 518.441 | 519.6583 | 473.754 | 480.1161 | 480.3837 | 382.2653 | 407.3754 | 462.5934 | 426.8054 | 402.7474 | 384.3064 | 355.6179 | 350.6541 | 336.1222 | 338.814 | 293.4527 | 290.4697 | 246.5855 | 244.3371 | 234.9972 | 216.8553 | 217.0075
Office Revised 2 (E): Jan 3rd | 222.5327 | 213.7989 | 203.567 | 199.4874 | 216.2991 | 206.1014 | 195.8328 | 200.6417 | 193.0387 | 204.64 | 235.6846 | 179.3647 | 273.3405 | 246.8268 | 307.8245 | 354.5343 | 390.9073 | 517.6959 | 386.7726 | 530.1605 | 518.5119 | 494.9339 | 450.1645 | 395.8256 | 397.3382 | 427.571 | 427.7138 | 428.7181 | 390.847 | 396.0958 | 396.3166 | 315.3689 | 371.73 | 422.1165 | 426.8054 | 402.7474 | 384.3064 | 355.6179 | 350.6541 | 336.1222 | 338.814 | 293.4527 | 290.4697 | 246.5855 | 244.3371 | 234.9972 | 216.8553 | 217.0075
North Perimeter Offices (% floor area): | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55%
Lights On (%): | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Office Base Case (T): Jan 3rd | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1479.732 | 1768.9597 | 1768.9955 | 1761.0473 | 1733.5295 | 1737.2939 | 1694.2917 | 1703.8172 | 1671.4383 | 1672.3842 | 1670.0209 | 1629.503 | 1526.305 | 1445.4876 | 1358.9281 | 1259.7535 | 1178.0828 | 1135.4325 | 1082.6709 | 787.3356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Office Revised (T): Jan 3rd | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1484.9111 | 1775.151 | 1775.187 | 1767.211 | 1742.6305 | 1746.4147 | 1735.8018 | 1745.5607 | 1759.1888 | 1760.1843 | 1775.2322 | 1732.1616 | 1635.8174 | 1549.2014 | 1456.4312 | 1350.1408 | 1233.7472 | 1189.0816 | 1094.0389 | 795.6026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Increase(%): | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 2 | 3 | 3 | 14 | 14 | 30 | 30 | 36 | 36 | 41 | 41 | 41 | 41 | 27 | 27 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(Revised figures require to now be corrected again for heat recovery)
South Office Zone:
Office Revised (E): Jan 3rd | 222.5327 | 213.7989 | 203.567 | 199.4874 | 216.2991 | 206.1014 | 195.8328 | 200.6417 | 193.0387 | 204.64 | 235.6846 | 179.3647 | 273.3405 | 246.8268 | 307.8245 | 354.5343 | 390.9073 | 517.6959 | 386.7726 | 530.1605 | 518.5119 | 494.9339 | 493.3309 | 433.7815 | 481.622 | 518.2679 | 518.441 | 519.6583 | 473.754 | 480.1161 | 480.3837 | 382.2653 | 407.3754 | 462.5934 | 426.8054 | 402.7474 | 384.3064 | 355.6179 | 350.6541 | 336.1222 | 338.814 | 293.4527 | 290.4697 | 246.5855 | 244.3371 | 234.9972 | 216.8553 | 217.0075
Office Revised 2 (E): Jan 3rd | 222.5327 | 213.7989 | 203.567 | 199.4874 | 216.2991 | 206.1014 | 195.8328 | 200.6417 | 193.0387 | 204.64 | 235.6846 | 179.3647 | 273.3405 | 246.8268 | 307.8245 | 354.5343 | 390.9073 | 517.6959 | 386.7726 | 530.1605 | 518.5119 | 494.9339 | 450.1645 | 395.8256 | 397.3382 | 427.571 | 427.7138 | 428.7181 | 390.847 | 396.0958 | 459.3669 | 365.5412 | 353.9074 | 401.878 | 426.8054 | 402.7474 | 384.3064 | 355.6179 | 350.6541 | 336.1222 | 338.814 | 293.4527 | 290.4697 | 246.5855 | 244.3371 | 234.9972 | 216.8553 | 217.0075
South Perimeter Offices (% floor area): | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55% | 17.55%
Lights On (%): | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 75 | 75 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Office Base Case (T): Jan 3rd | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1479.732 | 1768.9597 | 1768.9955 | 1761.0473 | 1733.5295 | 1737.2939 | 1694.2917 | 1703.8172 | 1671.4383 | 1672.3842 | 1670.0209 | 1629.503 | 1526.305 | 1445.4876 | 1358.9281 | 1259.7535 | 1178.0828 | 1135.4325 | 1082.6709 | 787.3356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Office Revised (T): Jan 3rd | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1482.3215 | 1772.0554 | 1772.0912 | 1764.1292 | 1739.5968 | 1743.3744 | 1738.7669 | 1748.5424 | 1767.9638 | 1768.9644 | 1772.3096 | 1729.31 | 1662.5278 | 1574.4974 | 1430.2718 | 1325.8905 | 1209.0075 | 1165.2376 | 1111.091 | 808.0031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Increase(%): | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 2 | 2 | 15 | 15 | 33 | 33 | 35 | 35 | 51 | 51 | 30 | 30 | 15 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Table 1: Results from ESP-r model. Lighting 12W/m2 at 400 lux. Lighting control at 600 lux set point in 6m by 10m room. 1 AC/H, 21oC heating set point and 10W/m2 equipment load.
Time (Half Hours) | Jan North | Jan North | Jan North | Jan North | Revised | Jan South | Jan South | Jan South | Jan South | Revised | Mar North | Mar North | Mar North | Mar North | Revised | Mar South | Mar South | Mar South | Mar South | Revised | July North | July North | July North | July North | Revised | July South | July South | July South | July South | Revised
| % Lights | Heat (kW) | % Lights | Heat (kW) | Heat (%) | % Lights | Heat (kW) | % Lights | Heat (kW) | Heat (%) | % Lights | Heat (kW) | % Lights | Heat (kW) | Heat (%) | % Lights | Heat (kW) | % Lights | Heat (kW) | Heat (%) | % Lights | Heat (kW) | % Lights | Heat (kW) | Heat (%) | % Lights | Heat (kW) | % Lights | Heat (kW) | Heat (%)
00h30 | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0
01h30 | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0
02h30 | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0
03h30 | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0
04h30 | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0
05h30 | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0
06h30 | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0
07h30 | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0
08h30 | 100 | 1.32 | 100 | 1.34 | 1.515% | 100 | 1.29 | 100 | 1.3 | 0.7752% | 100 | 0.94 | 75 | 1.07 | 13.83% | 100 | 0.85 | 75 | 0.99 | 16.47% | 100 | 0 | 50 | 0.1 | + | 100 | 0 | 50 | 0.04 | +
09h30 | 100 | 1.74 | 100 | 1.77 | 1.724% | 100 | 1.68 | 100 | 1.7 | 1.19% | 100 | 1.11 | 25 | 1.5 | 35.14% | 100 | 0.88 | 25 | 1.29 | 46.59% | 100 | 0 | 0 | 0.1 | + | 100 | 0 | 0 | 0.04 | +
10h30 | 100 | 1.83 | 100 | 1.88 | 2.732% | 100 | 1.78 | 100 | 1.81 | 1.685% | 100 | 1.16 | 0 | 1.7 | 46.55% | 100 | 0.81 | 0 | 1.37 | 69.14% | 100 | 0 | 0 | 0 |  | 100 | 0 | 0 | 0
11h30 | 100 | 1.63 | 50 | 1.86 | 14.11% | 100 | 1.56 | 50 | 1.79 | 14.74% | 100 | 0.99 | 0 | 1.43 | 44.44% | 100 | 0.77 | 0 | 1.07 | 38.96% | 100 | 0 | 0 | 0 |  | 100 | 0 | 0 | 0
12h30 | 100 | 1.48 | 0 | 1.93 | 30.41% | 100 | 1.38 | 0 | 1.83 | 32.61% | 100 | 0.75 | 0 | 1.23 | 64% | 100 | 0.38 | 0 | 0.79 | 107.9% | 100 | 0 | 0 | 0 |  | 100 | 0 | 0 | 0
13h30 | 100 | 1.33 | 0 | 1.81 | 36.09% | 100 | 1.21 | 0 | 1.63 | 34.71% | 100 | 0.75 | 0 | 1.08 | 44% | 100 | 0.38 | 0 | 0.79 | 107.9% | 100 | 0 | 0 | 0 |  | 100 | 0 | 0 | 0
14h30 | 100 | 1.2 | 0 | 1.69 | 40.83% | 100 | 0.91 | 0 | 1.37 | 50.55% | 100 | 0.51 | 0 | 0.95 | 86.27% | 100 | 0 | 0 | 0.24 | + | 100 | 0 | 0 | 0 |  | 100 | 0 | 0 | 0
15h30 | 100 | 1.15 | 0 | 1.62 | 40.87% | 100 | 0.91 | 25 | 1.18 | 29.67% | 100 | 0.51 | 0 | 0.95 | 86.27% | 100 | 0 | 0 | 0.24 | + | 100 | 0 | 0 | 0 |  | 100 | 0 | 0 | 0
16h30 | 100 | 1.09 | 50 | 1.38 | 26.61% | 100 | 0.8 | 75 | 0.92 | 15% | 100 | 0.36 | 0 | 0.88 | 144.4% | 100 | 0 | 0 | 0.15 | + | 100 | 0 | 0 | 0 |  | 100 | 0 | 0 | 0
17h30 | 100 | 1.09 | 100 | 1.16 | 6.422% | 100 | 0.8 | 100 | 0.92 | 15% | 100 | 0.36 | 50 | 0.88 | 144.4% | 100 | 0 | 50 | 0.15 | + | 100 | 0 | 0 | 0 |  | 100 | 0 | 0 | 0
18h30 | 100 | 1.01 | 100 | 1.08 | 6.931% | 100 | 0.78 | 100 | 0.9 | 15.38% | 100 | 0.33 | 100 | 0.6 | 81.82% | 100 | 0 | 100 | 0 |  | 100 | 0 | 50 | 0 |  | 100 | 0 | 50 | 0
19h30 | 100 | 1.01 | 100 | 1.08 | 6.931% | 100 | 0.78 | 100 | 0.9 | 15.38% | 100 | 0.33 | 100 | 0.6 | 81.82% | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0
20h30 | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0
21h30 | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0
22h30 | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0
23h30 | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0 |  | 100 | 0 | 100 | 0
Note on V163: Systems Manager:

## Annual Weather Data
Air Heating Data: | [6 empty] | Air Cooling Data:
Number of hours temperature occurs in the specified band in a yearly period. | [6 empty] | Number of hours temperature occurs in the specified band in a yearly period.
Temperature Band | Day Operation (06.00-18.00) | Evening Operation (18.00-20.00) | Design Temperature | Temperature Rise | Day Heating for I m3/s | Evening Heating for I m3/s | Temperature Band | Day Operation (06.00-18.30) | Evening Operation (18.30-20.30) | Design Temperature | Temperature Rise | Day Heating for I m3/s | Evening Heating for I m3/s
(°C) | (hrs) | (hrs) | (oC) | (oC) | (kWhrs/Yr) | (kWhrs/Yr) | (°C) | (hrs) | (hrs) | (oC) | (oC) | (kWhrs/Yr) | (kWhrs/Yr)
< - 4 °C | 9 | 2 | 19 | 23 | 250.47 | 55.66 | < - 4 °C | 9 | 2 | 20 | 24
- 4 to - 3 °C | 6 | 2 | 19 | 22 | 159.72 | 53.24 | - 4 to - 3 °C | 6 | 2 | 20 | 23
- 3 to - 2 °C | 6 | 1 | 19 | 21 | 152.46 | 25.41 | - 3 to - 2 °C | 6 | 1 | 20 | 22
- 2 to - 1 °C | 15 | 4 | 19 | 20 | 363 | 96.8 | - 2 to - 1 °C | 15 | 4 | 0 | 1
- 1 to 0 °C | 26 | 10 | 19 | 19 | 597.74 | 229.9 | - 1 to 0 °C | 26 | 10 | 20 | 20
0 to 1 °C | 32 | 19 | 19 | 18 | 696.96 | 413.82 | 0 to 1 °C | 32 | 19 | 20 | 19
1 to 2 °C | 38 | 14 | 19 | 17 | 781.66 | 287.98 | 1 to 2 °C | 38 | 14 | 20 | 18
2 to 3 °C | 36 | 12 | 19 | 16 | 696.96 | 232.32 | 2 to 3 °C | 36 | 12 | 20 | 17
3 to 4 °C | 83 | 41 | 19 | 15 | 1506.45 | 744.15 | 3 to 4 °C | 83 | 41 | 20 | 16
4 to 5 °C | 111 | 29 | 19 | 14 | 1880.34 | 491.26 | 4 to 5 °C | 111 | 29 | 20 | 15
5 to 6 °C | 157 | 46 | 19 | 13 | 2469.61 | 723.58 | 5 to 6 °C | 157 | 46 | 20 | 14
6 to 7 °C | 135 | 43 | 19 | 12 | 1960.2 | 624.36 | 6 to 7 °C | 135 | 43 | 20 | 13
7 to 8 °C | 168 | 65 | 19 | 11 | 2236.08 | 865.15 | 7 to 8 °C | 168 | 65 | 20 | 12
8 to 9 °C | 211 | 71 | 19 | 10 | 2553.1 | 859.1 | 8 to 9 °C | 211 | 71 | 20 | 11
9 to 10 °C | 183 | 60 | 19 | 9 | 1992.87 | 653.4 | 9 to 10 °C | 183 | 60 | 20 | 10
10 to 11 °C | 158 | 36 | 19 | 8 | 1529.44 | 348.48 | 10 to 11 °C | 158 | 36 | 20 | 9
11 to 12 °C | 146 | 33 | 19 | 7 | 1236.62 | 279.51 | 11 to 12 °C | 146 | 33 | 20 | 8
12 to 13 °C | 163 | 51 | 19 | 6 | 1183.38 | 370.26 | 12 to 13 °C | 163 | 51 | 20 | 7
13 to 14 °C | 149 | 54 | 19 | 5 | 901.45 | 326.7 | 13 to 14 °C | 149 | 54 | 20 | 6
14 to 15 °C | 163 | 53 | 19 | 4 | 788.92 | 256.52 | 14 to 15 °C | 163 | 53 | 20 | 5
15 to 16 °C | 150 | 37 | 19 | 3 | 544.5 | 134.31 | 15 to 16 °C | 150 | 37 | 20 | 4
16 to 17 °C | 133 | 31 | 19 | 2 | 321.86 | 75.02 | 16 to 17 °C | 133 | 31 | 20 | 3
17 to 18 °C | 115 | 22 | 19 | 1 | 139.15 | 26.62 | 17 to 18 °C | 115 | 22 | 20 | 2
18 to 19 °C | 75 | 14 | 19 | 0 |  |  | 18 to 19 °C | 75 | 14 | 20 | 1
19 to 20 °C | 48 | 12 | 19 | -1 |  |  | 19 to 20 °C | 48 | 12 | 20 | 0 | 0 | 0
20 to 21 °C | 28 | 7 | 19 | -2 |  |  | 20 to 21 °C | 28 | 7 | 20 | 1 | 33.88 | 8.47
21 to 22 °C | 30 | 7 | 19 | -3 |  |  | 21 to 22 °C | 30 | 7 | 20 | 2 | 72.6 | 16.94
22 to 23 °C | 14 | 3 | 19 | -4 |  |  | 22 to 23 °C | 14 | 3 | 20 | 3 | 50.82 | 10.89
23 to 24 °C | 4 | 1 | 19 | -5 |  |  | 23 to 24 °C | 4 | 1 | 20 | 4 | 19.36 | 4.84
25 °C + | 18 | 3 | 19 | -6 |  |  | 25 °C + | 18 | 3 | 20 | 5 | 108.9 | 18.15
| 2610 | 783 | Total kWhrs/Yr: |  | 24942.94 | 8173.55 |  | 2610 | 783 | Total kWhrs/Yr: |  | 285.56 | 59.29