## Instructions
NB. | worksheets with red and green tabs are the tool's active sheets - the remaining white tabs contain results and information specific to our case study
GENcalc : Description
GENcalc is a tool that can be used to analyse and quantify the possible supply options for a given estate. Supply options considered include CHP, PV, Wind and Solar
Thermal. These options can be combined with energy efficiency measures and absorbtion cooling.
The key parameters available fron the tool are:
- Demand and Supply matching per 30min interval
- Payback and NPV
- Positive or negative cashflow per 30min interval of operation
- Nett CO2 saving / loss per 30min interval of operation
- Annual Primary Fuel and CO2 reduction with CHP
- Annual utility cost reduction with CHP
- Proposed and current utility supply breakout
The tool can be used to find the plant and operating regime for optimum energy or environmental performance.
Instructions for using GENcalc
This sheet covers the logical steps required to use the GENcalc tool. For more background refer to the EEE Framework on project website.
In the sheet only fields with format |  | like this | should be freely modified, others are calculated or based on sourced data so modify only with caution!
Note: This spreadsheet was set up to utilise demand and supply profiles for 4 typical days (summer, intermediate, intermediate weekend and
winter). This data was then scaled up to represent annual profiles. If desired the spreadsheet could be modified to accept annual data. This would
improve accuracy but was not felt to be necessary for this example.
Note: The example data and analysis in the downloaded tool is for the EEE Project Case Study, for more info see the EEE Project website at ESRU.
Note: Data provided within the spreadsheet is for one example and should be validated before being used in another situation e.g system costs,
interest rates, utility costs, charges, grants etc.Some sources for information are given within the sheets.
When to consider CHP, Renewables or energy efficiency?
If looking to follow Energy Supply Management best practice?
If looking to reduce utility bills?
If looking to reduce environmental impact?
If considering replacement or upgrade of thermal / cooling plant?
If looking to attract Government funding for energy plant?
Define estate parameters for CHP:
1 | Number of buildings to be supplied |  |  | Enter in 'CHP Financials' sheet | Column F
2 | Length of mains required (sum of heat + cool ) |  |  | Enter in 'CHP Financials' sheet | Column F
3 | No.of buildings that will require new wet heating systems |  |  | Enter in 'CHP Financials' sheet | Column F
4 | Local customers available for excess electricity? |  |  | Could model different scenario's before decision
5 | - Private wire an option (buy DNO, install own)? |  |  | Enter capital cost of Pwire in 'CHP Financials' sheet | Column F
6 | - Consider Dist Network |  |  | See Utility Export below
7 | Local customers available for excess heat? |  |  | Add to estate thermal demand profile as appropriate (see below)
| - Leisure centres / market gardens / abs cooling load etc? |  |  | modify sheets to capture revenues
8 | Make sure all costs are captured (plant,design,legal,admin etc) |  |  | Include in total capital costs in 'CHP Financials' sheet | Column F
Input utility demands and current unit costs:
9 | Electricity demand profile (half hourly - 4 typical days) |  |  | Enter in 'Calculation' sheet (from MERIT or other source) | Column AK
10 | Electricity supply from renewables (half hourly - 4 typical days) |  |  | Reduce electric demand profile as appropriate
11 | Electricity demand reductions (half hourly - 4 typical days) |  |  | Reduce electric demand profile as appropriate
12 | Heat demand profile (half hourly - 4 typical days) |  |  | Enter in 'Calculation' sheet (from MERIT or other source) | Column AO
13 | Cooling demand profile (half hourly - 4 typical days) |  |  | Include (abs cool) into heat demand profile
14 | Heat demand reductions (half hourly - 4 typical days) |  |  | Include in heat demand profile
15 | Current (or projected) utility tariffs for supply
15a | - Grid Electricity Costs per kWh (half hourly - 4 typical days) |  |  | Enter in 'Elec_Gas parameters' sheet | Column B
15b | - Mains Gas Costs (half hourly - 4 typical days) |  |  | Enter in 'Elec_Gas parameters' sheet | Column B
Utility export options
note: export of excess electricity or heat may generate enhanced revenues and also achieve improved nett CO2 savings, export can be achieved in 3
main ways; (i) Private Wire - this allows excess electricity to be transported to other owned sites - this will displace elec that would have been
imported from the grid and avoids any dist charges, however the cost of the private wire has to be captured in the capital for the project. (ii) Distribution
Network distribution to private customers - this is allowed under 2001 elec regs (exempt supplier), export is limited to 2.5MWe or 5MWe in some
cases. The DNO operator will charge a dist'n fee. Metering methods and costs need to be confirmed with DNO. (iii) Export to Grid - this is often
the least economic of the options due to low price paid by Distn and Supply Co's - need to confirm metering and prices.
16 | Revenues for export of electricity (half hourly - 4 typical days) |  |  | Enter in 'Elec_Gas parameters' sheet (Pwire,DN,Grid) | Column B
17 | Revenues for export of heat (half hourly - 4 typical days) |  |  | Modify spreadsheet to capture revenues if required.
CHP engine size and operation - optimisation
note: engine size and operation has a big impact on financial and environmental performance. The spreadsheet allows operation and engine size
to be investigated and a optimum can be established for either / both financial or environmental criteria.
Common operating regimes are: (i) Base Electric, (ii) Base Heat, (iii) Electric demand following, (iv) Heat demand following, (v) Electricity export.
Within these regimes there may be different approaches taken to running the engine i.e. run when financialy beneficial or run when environmentally
beneficial.The financial optimum will depend strongly on the tariffs for the displaced grid imported electricity and also the tariff received for any
electricity exported. Where different electricity export options are being considered these usualy need separately financial models.
18 | Input Maint costs (£/op hr or £/kWhe) |  |  | Enter in 'CHP Financials' sheet | Column F
For each operating regime to be considered (eg (i) to (v) above with on or off at low tariff) actions 14 to 17 should be repeated…
19 | Input CHP Electricity supply profile (half hourly - 4 typical days) |  |  | Enter in 'Calculation' sheet (from MERIT or other source) | Column AK
20 | Input CHP Heat supply profile (half hourly - 4 typical days) |  |  | Enter in 'Calculation' sheet (from MERIT or other source) | Column AO
note: the supply profiles can be manipulated within the spreadsheet by scaling the size or output from the CHP engine (separate scaling factors
can be applied to different times of day), the supply profiles can also be modified by clipping (limiting) the engine size to a maximum in kWe.
The spreadsheet is set up to allow a different scaling to be applied to the times when the electricity import tariff is low (00:00 to 07:00) and when
the tariff is high (07:00 to 24:00), this can be modified to a different case as appropriate.
note: there is an option which allows the CHP capital cost to be based on a single engine or multiple engines. The multiple engine option may give
some operational advantages (flexibility, maint costs, min load capability) but has a higher capital cost.
21 | Create table and graph of key parameters vs engine size |  |  | Record table and graph in 'Engine scaling results' sheet
note: supply profile is varied to reflect different engine sizes using scaling and clipping on 'Calculations' sheet.
22 | Identify engine sizes for optimum payback and CO2 emissions |  |  | Enter both optima in 'Chooser' sheet
23 | Repeat 19 to 22 for each operation option.
24 | Make selection of best option |  |  | Sort 'Chooser' by desired criteria
note: 'Chooser' can be sorted or filtered to allow different criteria to be used for selection of "best" option. As well as CHP options 'Chooser' can be
populated with other supply or demand reduction options eg. Renewables (PV, Wind Solar thermal etc) or energy savings (lighting etc) and these can
be compared together with the CHP options. "Best" option selection may be made based on financial, environmental or other criteria. In the example
spreadsheet the 'Chooser' is shown sorted in several different ways.
note: Tools are available for analysis of PV and Wind Generation options (GencalcPV, GencalcWind), these can be used to look at different options
and provide data that can be input into Gencalc's 'Calculations' and 'Chooser' sheets.There is also a tool available for detailed analysis of energy reduction
options (DemCalc) which can be used to fed the Gencalc 'Calculations' and 'Chooser' sheets if desired. These can be downloaded from the EEE
project website.
Check chosen combination of technologies
25 | Confirm CHP engine size and operation still optimum |  |  | Repeat analysis with energy reductions and renewables applied (see steps 7,8,10,11)

## Elec_Gas parameters
Electricity | £ / kWh
Import Tariff - cost, 00:00 - 07:00 | 0.015
Import Tariff - cost, 07:00 - 24:00 | 0.045
Grid sale of export - revenue, 00:00 - 07:00 | 0.005 |  | The current export
Grid sale of export - revenue, 07:00 - 24:00 | 0.015 |  | tariffs in 'calculation'
DNO local access charges - cost | 0.015
DNO export to local customer - revenue, 00:00 - 07:00 | 0
DNO export to local customer - revenue, 07:00 - 24:00 | 0.03
PW export to local customer - revenue, 00:00 - 07:00 | 0.015 | Elec | 0.015 | 00:00-07:00
PW export to local customer - revenue, 07:00 - 24:00 | 0.045 | Elec | 0.045 | 07:00-24:00
Gas
Gas unit price | 0.007

## CHP Financials
CHP System and Maintenance Contract description
1. Max CHP kWe required |  |  |  |  | 2250 |  | from calculations spreadsheet
2. Number of engines required |  |  |  |  | 1 |  | define after modelling requirements v. engine specs.
2. Length of district heating mains (hot+cool) |  |  |  |  | 500 |  | from survey
3. Number of buildings connected to mains (Heat Stations) |  |  |  |  | 6 |  | from survey
4. Buildings that will require new wet heating system |  |  |  |  | 0 |  | from survey
5. Private Wire Electrical Network length |  |  |  |  | 500 |  | from survey and elec load sizing
6. Maintenance cost £/kWhe |  |  |  |  | 0.008 |  | from manufacturers / maintenance contract - note: may be £ / Op hr.
Capital Costs |  |  |  |  | k£
1. CHP system (engines plus integration / controls) |  |  |  |  | 953.175 |  | Cost per engine = -2E-05*(kWe)^2 + 0.4133(kWe) + 124.51 [best fit from multiple sources - below]
2. District Heating Network |  |  |  |  | 600 |  | £12k per 10m mains plus 10k per building heat station. (Ind std - Hulley)
3. Heat Stations |  |  |  |  | 60 |  | £10k per building (Ind std - Hulley) - depends on site
4. New building wet heating system cost |  |  |  |  | 0 |  | £50k per building - depends on site
5. Private Wire Network Cost |  |  |  |  | 0 |  | £40k used for 500m example if Private Wire selected on calculator - will depend on survey or DNO negociation
TOTAL |  |  |  |  | 1613.175
Annual Maintenance Costs |  |  |  |  | k£pa
TOTAL |  |  |  |  | 111.69 |  | cost / kWhe * Annual kWhe
CHP Capital Cost Data and sources (k£)
Power curve created from multiple datapoints:
[10 empty] | same as Jung |  | jungbacher engine ($/kWe) |  |  | jungbacher system ($/kWe) |  |  | jungbacher engine (k£) |  |  | jungbacher system (k£)
| LEB Curve | Time Capsule | BRE CHPsizer | Jenb max | Jung ave | EEEStrend |  |  | EEES | Educogen | CHPclub | min | max | ave | min | max | ave | min | max | ave | min | max | ave
50 | 45.7305 |  | 42.5 |  |  | 145.115 |  | 50 | 60 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
100 | 79.6214 |  | 76.9 |  |  | 165.63 |  | 100 | 110 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
150 | 110.1293 |  | 110.2 |  |  | 186.045 |  | 150 | 160 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
200 | 138.629 |  | 142.7 |  |  | 206.36 |  | 200 | 200 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
250 | 165.7227 |  |  |  |  | 226.575 |  | 250 | 245 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
300 | 191.7463 |  | 203.8 | 337.5 | 281.25 | 246.69 |  | 300 | 281.25 |  |  | 400 | 700 | 550 | 1100 | 1800 | 1500 | 75 | 131.25 | 103.125 | 206.25 | 337.5 | 281.25
325 | 204.4263 | 250 |  |  |  | 256.71 |  | 325 | 300 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
350 | 216.9124 |  |  |  |  | 266.705 |  | 350 | 315 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
400 | 241.3671 |  | 262.3 | 375 | 325 | 286.62 |  | 400 | 325 |  |  | 375 | 600 | 500 | 1000 | 1500 | 1300 | 93.75 | 150 | 125 | 250 | 375 | 325
450 | 265.2162 |  |  |  |  | 306.435 |  | 450 | 340 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
500 | 288.54 |  |  |  |  | 326.15 |  | 500 | 352 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
550 | 311.4011 |  |  |  |  | 345.765 |  | 550 | 363 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
600 | 333.8497 |  | 376.1 | 450 | 375 | 365.28 |  | 600 | 375 |  |  | 360 | 525 | 450 | 850 | 1200 | 1000 | 135 | 196.875 | 168.75 | 318.75 | 450 | 375
650 | 355.9268 |  |  |  |  | 384.695 |  | 650 | 395 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
700 | 377.6665 |  |  |  |  | 404.01 |  | 700 | 408 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
750 | 399.0975 |  |  |  |  | 423.225 |  | 750 | 425 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
800 | 420.2444 |  | 479 | 500 | 425 | 442.34 |  | 800 | 440 |  |  | 340 | 500 | 425 | 700 | 1000 | 850 | 170 | 250 | 212.5 | 350 | 500 | 425
850 | 441.1285 |  |  |  |  | 461.355 |  | 850 | 450 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
900 | 461.7682 |  |  |  |  | 480.27 |  | 900 | 461.7682 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
1000 | 502.3773 |  | 577 | 562.5 | 456.25 | 517.8 |  | 1000 | 502.3773 |  | 950 | 340 | 480 | 400 | 625 | 900 | 730 | 212.5 | 300 | 250 | 390.625 | 562.5 | 456.25
1100 | 542.1808 |  |  |  |  | 554.93 |  | 1100 | 542.1808 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
1200 | 581.2661 |  |  |  |  | 591.66 |  | 1200 | 581.2661 |  |  | 340 | 480 | 400 | 580 | 760 | 640 | 255 | 360 | 300 | 435 | 570 | 480
1300 | 619.7045 |  |  |  |  | 627.99 |  | 1300 | 619.7045 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
1400 | 657.5555 |  |  |  |  | 663.92 |  | 1400 | 657.5555 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
1500 | 694.8691 |  | 865.5 |  |  | 699.45 |  | 1500 | 694.8691 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
1750 | 786.0686 |  |  | 787.5 | 656.25 | 786.525 |  | 1750 | 786.0686 |  |  | 340 | 480 | 400 | 550 | 720 | 600 | 371.875 | 525 | 437.5 | 601.5625 | 787.5 | 656.25
2000 | 874.6897 |  |  |  |  | 871.1 |  | 2000 | 874.6897 |  | 1750 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
2250 | 961.1164 |  |  |  |  | 953.175 |  | 2250 | 961.1164 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
2500 | 1045.6396 |  |  |  |  | 1032.75 |  | 2500 | 1045.6396 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
2750 | 1128.4859 |  |  |  |  | 1109.825 |  | 2750 | 1128.4859 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
3000 | 1209.8374 |  |  |  |  | 1184.4 |  | 3000 | 1209.8374 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
CHP System Maintenance Costs
= 0.6 - 1 p / kWhe (BRE, Educogen)

## Plant Parameters
Grid Power |  | Fuel Efficiency | 40%
|  | CO2 Tonnes/(kWh Pr Fuel) | 0.000208 |  | from BRE CHPsizer
Engine | MERIT 442kWe engine | 442kWe engine:
|  | Peak power | 485kWe
|  | Min Load | 20%
|  | Cum Efficiency (H+P) | 85%
|  | Capital cost | see finance sheet | £
|  | Maint cost | see finance sheet | £
|  | CO2 Tonnes/(kWh Pr Fuel) | 0.000208 |  | from BRE CHPsizer
Boiler |  | Fuel Efficiency | 85%
|  | Capital cost |  | £
|  | Maint cost |  | £
|  | CO2 Tonnes/(kWh Pr Fuel) | 0.000208 |  | from BRE CHPsizer
PV
|  | CO2 Tonnes/(kWh Pr Fuel) | 0

## Calculation & perfomance view
| DEMAND: |  |  | 60,000m2 Base Case | [7 empty] | SUPPLY: |  |  |  | E follow CHP | [11 empty] | CHART SOURCE TABLES - DATA FROM MAIN HEADER
[6 empty] | KEY METRICS |  | chp engine (kWe) | payback (years) | npv 15 (k£) | CO2 saved (tonnes pa) | Utility saved (k£pa) | Capital (k£) |  |  | Capital / CO2 | CO2 / payback
[5 empty] | E follow CHP |  |  | 2250 | 3.1167 | 2048.2385 | 1138.2383 | 422.2405 | 967.905 |  |  | 0.85035 | 365.2016
Supply Modification |  | Scaling: | HI tariff | 8 | LO tariff | 0 |  | Clipping: | Max Elec | 2250 | Max Th | 2706.875 |  |  |  | Min Load % | 20% | Min Elec | 450 | Min Th | 541.375
[8 empty] | Runtime: | On |  | Off
Grants available |  | 40% | Cost redn | 0% | [32 empty] | Original | Proposed
Cashflow: | [5 empty] | Annual Demands (kWh) |  | Annual |  | Original |  |  | Proposed |  |  |  |  | Annual Utility Costs | [7 empty] | Original | Proposed | Delta | [7 empty] | grid elec | 5582346.2432 | -8378903.7568
Annual saved electric cost (£) |  |  |  | 209547.6973 |  | Electric | 5582346.2432 | Supply | kWh | Pr Fuel kWh | CO2 Tonnes | kWh | Pr Fuel kWh |  |  | CO2 Tonnes |  | k£ | Original | Proposed | Delta |  |  | CO2 (Tonnes/a) |  | 4478.6922 | 3340.4539 | 1138.2383 | [7 empty] | boiler heat | 6439862.2156 | 698654.4387
Annual revenue from elec sales (£) |  |  |  | 418708.5527 |  | Thermal | 6439862.2156 | Elec grid | 5582346.2432 | 13955865.6081 | 2902.82 | -8378903.7568 | -20947259.3919 |  |  | -4357.03 |  | Electricity | 223.4337 | -404.8226 | -628.2563 | [14 empty] | chp elec | 0 | 13961250
Annual extra gas cost (£) |  |  |  | -206015.7779 |  | Total | 12022208.4589 | Elec CHP | 0 | 0 | 0 | 13961250 | 36185187.5 |  |  | 7526.519 |  | Gas | 53.0342 | 259.0499 | 206.0158 |  |  |  |  | Original | Proposed | Delta |  |  | Original | Proposed | Delta |  |  | chp heat | 0 | 16796159.375
Annual maint cost (£) |  |  |  | -111690 |  |  |  | Elec other | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  | Total | 276.4678 | -145.7727 | -422.2405 |  |  |  | Primary Fuel (MWh/a) | 21532.1741 | 16059.8745 | 5472.2996 |  | Primary Fuel (%) | 100% | 74.59% | 25.41%
Annual cash flow (£) |  |  |  | 310550.4721 | Engines: | 1 |  | Th boiler | 6439862.2156 | 7576308.489 | 1575.8722 | 698654.4387 | 821946.3985 |  |  | 170.9649 | Fuel Tariffs (£/kWh) |  | Private wire? Y=1: |  | 0
Capital Cost (£) |  |  |  | 967905 | Max kWe | 2250 |  | Th CHP | 0 | 0 | 0 | 16796159.375 | 0 |  |  | 0 | Elec costs | Import | Grid Export | P-Wire | Dist Nwk |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
Simple Payback (years) |  |  |  | 3.1167 |  |  |  | Th other | 0 | 0 | 0 | 0 | 0 |  |  | 0 | Elec high | 0.045 | 0.015 | 0.045 | 0.03 |  |  | NPV (k£) |  | -967.905 | -674.9329 | -398.544 | -137.7999 | 108.1852 | 340.2466 | 559.1724 | 765.7062 | 960.5494 | 1144.3637 | 1317.7735 | 1481.3676 | 1635.7017 | 1781.2999 | 1918.6566 | 2048.2385
Discount rate |  |  |  | 0.06 |  | Excess Th | 11054951.5981 | Total | 12022208.4589 | 21532174.0971 | 4478.6922 | 23077160.057 | 16059874.5066 |  |  | 3340.4539 | Elec low | 0.015 | 0.005 | 0.015 | 0 |  |  | discount factor |  | 1 | 0.9434 | 0.89 | 0.83962 | 0.79209 | 0.74726 | 0.70496 | 0.66506 | 0.62741 | 0.5919 | 0.55839 | 0.52679 | 0.49697 | 0.46884 | 0.4423 | 0.41727
NPV 15yr (k£) |  |  |  | 2048.2385 |  | Excess E | 9304634.5041 | Delta |  |  |  | -11054951.5981 | 5472299.5904 |  |  | 1138.2383 | Gas cost | 0.007 | Selected | Elec high | 0.045
[19 empty] | ElecExport | Elec low | 0.015 | [29 empty] | Below is data for the
INPUT DEMAND AND SUPPLY DATA IN COLS AK, AO, AS, AW >>> | [41 empty] | Demand and supply entry and Modifications Section | [8 empty] | engine on / off time fn.
day | time | elec tariff | E demand | elec res | elec supply | saved elec cost £ | cashflow elec-gas-maint | excess elec | elec sale tariff | elec revenue | Th demand | therm res | therm supply | res boiler | unutilised | elec eff | therm eff | chp gas used | boiler gas displaced | extra gas cost | grid fuel displaced | e+th fuel displaced | fuel saved | old prim fuel | new prim fuel | estate fuel saved | old elec cost | old gas cost | chp gas cost | new boiler gas cost | new nett gas cost | new grid elec cost | new nett elec cost | CO2 saving | elec demand | E Esave reduction | renewable supply deduction | reduced demand | th demand | Th Esave reduction | renewable supply deduction | reduced demand | e supply Profile | scaled e supply | min e load applied | max e output clipped | th supply Profile | scaled th supply | min th load applied | max th output clipped
winter | 0 | 0.015 | 486.0646 | 486.0646 | 0 | 0 | 0 | 0 | 0.015 | 0 | 177.124 | 177.124 | 0 | 177.124 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1423.5426 | 1423.5426 | 0 | 3.6455 | 0.72933 | 0 | 0.72933 | 0.72933 | 3.6455 | 3.6455 | 0 | 486.0646 | 0 | 0 | 486.0646 | 177.124 | 0 | 0 | 177.124 | 486.0646 | 0 | 0 | 0 | 580.0981 | 0 | 0 | 0 | 0:00 | 0
winter | 0.5 | 0.015 | 425.3649 | 425.3649 | 0 | 0 | 0 | 0 | 0.015 | 0 | 147.803 | 147.803 | 0 | 147.803 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1237.2982 | 1237.2982 | 0 | 3.1902 | 0.6086 | 0 | 0.6086 | 0.6086 | 3.1902 | 3.1902 | 0 | 425.3649 | 0 | 0 | 425.3649 | 147.803 | 0 | 0 | 147.803 | 425.3649 | 0 | 0 | 0 | 506.9125 | 0 | 0 | 0 | 0:30 | 0.5
winter | 1 | 0.015 | 391.1014 | 391.1014 | 0 | 0 | 0 | 0 | 0.015 | 0 | 128.236 | 128.236 | 0 | 128.236 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1128.6195 | 1128.6195 | 0 | 2.9333 | 0.52803 | 0 | 0.52803 | 0.52803 | 2.9333 | 2.9333 | 0 | 391.1014 | 0 | 0 | 391.1014 | 128.236 | 0 | 0 | 128.236 | 391.1014 | 0 | 0 | 0 | 465.601 | 0 | 0 | 0 | 1:00 | 1
winter | 1.5 | 0.015 | 363.0195 | 363.0195 | 0 | 0 | 0 | 0 | 0.015 | 0 | 121.871 | 121.871 | 0 | 121.871 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1050.9264 | 1050.9264 | 0 | 2.7226 | 0.50182 | 0 | 0.50182 | 0.50182 | 2.7226 | 2.7226 | 0 | 363.0195 | 0 | 0 | 363.0195 | 121.871 | 0 | 0 | 121.871 | 363.0195 | 0 | 0 | 0 | 431.7426 | 0 | 0 | 0 | 1:30 | 1.5
winter | 2 | 0.015 | 378.4158 | 378.4158 | 0 | 0 | 0 | 0 | 0.015 | 0 | 115.649 | 115.649 | 0 | 115.649 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1082.0972 | 1082.0972 | 0 | 2.8381 | 0.4762 | 0 | 0.4762 | 0.4762 | 2.8381 | 2.8381 | 0 | 378.4158 | 0 | 0 | 378.4158 | 115.649 | 0 | 0 | 115.649 | 378.4158 | 0 | 0 | 0 | 450.306 | 0 | 0 | 0 | 2:00 | 2
winter | 2.5 | 0.015 | 360.7062 | 360.7062 | 0 | 0 | 0 | 0 | 0.015 | 0 | 112.44 | 112.44 | 0 | 112.44 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1034.0478 | 1034.0478 | 0 | 2.7053 | 0.46299 | 0 | 0.46299 | 0.46299 | 2.7053 | 2.7053 | 0 | 360.7062 | 0 | 0 | 360.7062 | 112.44 | 0 | 0 | 112.44 | 360.7062 | 0 | 0 | 0 | 428.9534 | 0 | 0 | 0 | 2:30 | 2.5
winter | 3 | 0.015 | 349.1807 | 349.1807 | 0 | 0 | 0 | 0 | 0.015 | 0 | 111.383 | 111.383 | 0 | 111.383 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1003.9906 | 1003.9906 | 0 | 2.6189 | 0.45864 | 0 | 0.45864 | 0.45864 | 2.6189 | 2.6189 | 0 | 349.1807 | 0 | 0 | 349.1807 | 111.383 | 0 | 0 | 111.383 | 349.1807 | 0 | 0 | 0 | 415.0572 | 0 | 0 | 0 | 3:00 | 3
winter | 3.5 | 0.015 | 351.8471 | 351.8471 | 0 | 0 | 0 | 0 | 0.015 | 0 | 342.418 | 342.418 | 0 | 342.418 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1282.4625 | 1282.4625 | 0 | 2.6389 | 1.41 | 0 | 1.41 | 1.41 | 2.6389 | 2.6389 | 0 | 351.8471 | 0 | 0 | 351.8471 | 342.418 | 0 | 0 | 342.418 | 351.8471 | 0 | 0 | 0 | 418.2721 | 0 | 0 | 0 | 3:30 | 3.5
winter | 4 | 0.015 | 345.3985 | 345.3985 | 0 | 0 | 0 | 0 | 0.015 | 0 | 575.575 | 575.575 | 0 | 575.575 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1540.6433 | 1540.6433 | 0 | 2.5905 | 2.37 | 0 | 2.37 | 2.37 | 2.5905 | 2.5905 | 0 | 345.3985 | 0 | 0 | 345.3985 | 575.575 | 0 | 0 | 575.575 | 345.3985 | 0 | 0 | 0 | 410.497 | 0 | 0 | 0 | 4:00 | 4
winter | 4.5 | 0.015 | 360.6677 | 360.6677 | 0 | 0 | 0 | 0 | 0.015 | 0 | 574.855 | 574.855 | 0 | 574.855 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1577.9692 | 1577.9692 | 0 | 2.705 | 2.367 | 0 | 2.367 | 2.367 | 2.705 | 2.705 | 0 | 360.6677 | 0 | 0 | 360.6677 | 574.855 | 0 | 0 | 574.855 | 360.6677 | 0 | 0 | 0 | 428.907 | 0 | 0 | 0 | 4:30 | 4.5
winter | 5 | 0.015 | 402.7582 | 402.7582 | 0 | 0 | 0 | 0 | 0.015 | 0 | 589.242 | 589.242 | 0 | 589.242 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1700.1215 | 1700.1215 | 0 | 3.0207 | 2.4263 | 0 | 2.4263 | 2.4263 | 3.0207 | 3.0207 | 0 | 402.7582 | 0 | 0 | 402.7582 | 589.242 | 0 | 0 | 589.242 | 402.7582 | 0 | 0 | 0 | 479.6556 | 0 | 0 | 0 | 5:00 | 5
winter | 5.5 | 0.015 | 351.6681 | 351.6681 | 0 | 0 | 0 | 0 | 0.015 | 0 | 623.226 | 623.226 | 0 | 623.226 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1612.3773 | 1612.3773 | 0 | 2.6375 | 2.5662 | 0 | 2.5662 | 2.5662 | 2.6375 | 2.6375 | 0 | 351.6681 | 0 | 0 | 351.6681 | 623.226 | 0 | 0 | 623.226 | 351.6681 | 0 | 0 | 0 | 418.0562 | 0 | 0 | 0 | 5:30 | 5.5
winter | 6 | 0.015 | 491.9523 | 491.9523 | 0 | 0 | 0 | 0 | 0.015 | 0 | 676.028 | 676.028 | 0 | 676.028 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 2025.2077 | 2025.2077 | 0 | 3.6896 | 2.7836 | 0 | 2.7836 | 2.7836 | 3.6896 | 3.6896 | 0 | 491.9523 | 0 | 0 | 491.9523 | 676.028 | 0 | 0 | 676.028 | 491.9523 | 0 | 0 | 0 | 587.1969 | 0 | 0 | 0 | 6:00 | 6
winter | 6.5 | 0.015 | 538.8654 | 538.8654 | 0 | 0 | 0 | 0 | 0.015 | 0 | 741.484 | 741.484 | 0 | 741.484 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 2219.4977 | 2219.4977 | 0 | 4.0415 | 3.0532 | 0 | 3.0532 | 3.0532 | 4.0415 | 4.0415 | 0 | 538.8654 | 0 | 0 | 538.8654 | 741.484 | 0 | 0 | 741.484 | 538.8654 | 0 | 0 | 0 | 643.76 | 0 | 0 | 0 | 6:30 | 6.5
winter | 7 | 0.045 | 715.2938 | -1534.7062 | 2250 | 16.0941 | 24.5842 | 1534.7062 | 0.045 | 34.5309 | 818.403 | -1888.472 | 2706.875 | 0 | -1888.472 | 38.58% | 46.42% | 5831.6176 | 962.8271 | 17.0408 | 5625 | 6587.8271 | 756.2094 | 6587.8271 | 5831.6176 | 756.2094 | 16.0941 | 3.3699 | 20.4107 | 0 | 20.4107 | 0 | -34.5309 | 0.078646 | 715.2938 | 0 | 0 | 715.2938 | 818.403 | 0 | 0 | 818.403 | 715.2938 | 5722.3501 | 5722.3501 | 2250 | 856.4797 | 6851.8375 | 6851.8375 | 2706.875 | 7:00 | 7
winter | 7.5 | 0.045 | 824.7036 | -1425.2964 | 2250 | 18.5558 | 27.535 | 1425.2964 | 0.045 | 32.0692 | 1535.012 | -1171.863 | 2706.875 | 0 | -1171.863 | 38.58% | 46.42% | 5831.6176 | 1805.8965 | 14.09 | 5625 | 7430.8965 | 1599.2788 | 7430.8965 | 5831.6176 | 1599.2788 | 18.5558 | 6.3206 | 20.4107 | 0 | 20.4107 | 0 | -32.0692 | 0.16632 | 824.7036 | 0 | 0 | 824.7036 | 1535.012 | 0 | 0 | 1535.012 | 824.7036 | 6597.6289 | 6597.6289 | 2250 | 988.3951 | 7907.1612 | 7907.1612 | 2706.875 | 7:30 | 7.5
winter | 8 | 0.045 | 847.7749 | -1402.2251 | 2250 | 19.0749 | 31.0824 | 1402.2251 | 0.045 | 31.5501 | 2396.531 | -310.344 | 2706.875 | 0 | -310.344 | 38.58% | 46.42% | 5831.6176 | 2819.4482 | 10.5426 | 5625 | 8444.4482 | 2612.8306 | 8444.4482 | 5831.6176 | 2612.8306 | 19.0749 | 9.8681 | 20.4107 | 0 | 20.4107 | 0 | -31.5501 | 0.27173 | 847.7749 | 0 | 0 | 847.7749 | 2396.531 | 0 | 0 | 2396.531 | 847.7749 | 6782.1992 | 6782.1992 | 2250 | 1016.2122 | 8129.6976 | 8129.6976 | 2706.875 | 8:00 | 8
winter | 8.5 | 0.045 | 981.1306 | -1268.8694 | 2250 | 22.0754 | 31.8127 | 1268.8694 | 0.045 | 28.5496 | 2573.895 | -132.98 | 2706.875 | 0 | -132.98 | 38.58% | 46.42% | 5831.6176 | 3028.1118 | 9.8123 | 5625 | 8653.1118 | 2821.4941 | 8653.1118 | 5831.6176 | 2821.4941 | 22.0754 | 10.5984 | 20.4107 | 0 | 20.4107 | 0 | -28.5496 | 0.29344 | 981.1306 | 0 | 0 | 981.1306 | 2573.895 | 0 | 0 | 2573.895 | 981.1306 | 7849.0449 | 7849.0449 | 2250 | 1176.9992 | 9415.9935 | 9415.9935 | 2706.875 | 8:30 | 8.5
winter | 9 | 0.045 | 783.4669 | -1466.5331 | 2250 | 17.628 | 31.7241 | 1466.5331 | 0.045 | 32.997 | 2552.371 | -154.504 | 2706.875 | 0 | -154.504 | 38.58% | 46.42% | 5831.6176 | 3002.7894 | 9.9009 | 5625 | 8627.7894 | 2796.1718 | 8627.7894 | 5831.6176 | 2796.1718 | 17.628 | 10.5098 | 20.4107 | 0 | 20.4107 | 0 | -32.997 | 0.2908 | 783.4669 | 0 | 0 | 783.4669 | 2552.371 | 0 | 0 | 2552.371 | 783.4669 | 6267.7354 | 6267.7354 | 2250 | 938.6761 | 7509.4085 | 7509.4085 | 2706.875 | 9:00 | 9
winter | 9.5 | 0.045 | 934.4994 | -1315.5006 | 2250 | 21.0262 | 31.5896 | 1315.5006 | 0.045 | 29.5988 | 2519.706 | -187.169 | 2706.875 | 0 | -187.169 | 38.58% | 46.42% | 5831.6176 | 2964.36 | 10.0354 | 5625 | 8589.36 | 2757.7424 | 8589.36 | 5831.6176 | 2757.7424 | 21.0262 | 10.3753 | 20.4107 | 0 | 20.4107 | 0 | -29.5988 | 0.28681 | 934.4994 | 0 | 0 | 934.4994 | 2519.706 | 0 | 0 | 2519.706 | 934.4994 | 7475.9951 | 7475.9951 | 2250 | 1120.7759 | 8966.2073 | 8966.2073 | 2706.875 | 9:30 | 9.5
winter | 10 | 0.045 | 916.7635 | -1333.2365 | 2250 | 20.6272 | 31.4332 | 1333.2365 | 0.045 | 29.9978 | 2481.727 | -225.148 | 2706.875 | 0 | -225.148 | 38.58% | 46.42% | 5831.6176 | 2919.6788 | 10.1918 | 5625 | 8544.6788 | 2713.0612 | 8544.6788 | 5831.6176 | 2713.0612 | 20.6272 | 10.2189 | 20.4107 | 0 | 20.4107 | 0 | -29.9978 | 0.28216 | 916.7635 | 0 | 0 | 916.7635 | 2481.727 | 0 | 0 | 2481.727 | 916.7635 | 7334.1084 | 7334.1084 | 2250 | 1099.3918 | 8795.1345 | 8795.1345 | 2706.875 | 10:00 | 10
winter | 10.5 | 0.045 | 880.5989 | -1369.4011 | 2250 | 19.8135 | 31.3241 | 1369.4011 | 0.045 | 30.8115 | 2455.24 | -251.635 | 2706.875 | 0 | -251.635 | 38.58% | 46.42% | 5831.6176 | 2888.5176 | 10.3009 | 5625 | 8513.5176 | 2681.9 | 8513.5176 | 5831.6176 | 2681.9 | 19.8135 | 10.1098 | 20.4107 | 0 | 20.4107 | 0 | -30.8115 | 0.27892 | 880.5989 | 0 | 0 | 880.5989 | 2455.24 | 0 | 0 | 2455.24 | 880.5989 | 7044.791 | 7044.791 | 2250 | 1055.7881 | 8446.3045 | 8446.3045 | 2706.875 | 10:30 | 10.5
winter | 11 | 0.045 | 888.5896 | -1361.4104 | 2250 | 19.9933 | 31.2079 | 1361.4104 | 0.045 | 30.6317 | 2427.006 | -279.869 | 2706.875 | 0 | -279.869 | 38.58% | 46.42% | 5831.6176 | 2855.3012 | 10.4171 | 5625 | 8480.3012 | 2648.6835 | 8480.3012 | 5831.6176 | 2648.6835 | 19.9933 | 9.9936 | 20.4107 | 0 | 20.4107 | 0 | -30.6317 | 0.27546 | 888.5896 | 0 | 0 | 888.5896 | 2427.006 | 0 | 0 | 2427.006 | 888.5896 | 7108.7168 | 7108.7168 | 2250 | 1065.4225 | 8523.3798 | 8523.3798 | 2706.875 | 11:00 | 11
winter | 11.5 | 0.045 | 817.8948 | -1432.1052 | 2250 | 18.4026 | 31.1181 | 1432.1052 | 0.045 | 32.2224 | 2405.205 | -301.67 | 2706.875 | 0 | -301.67 | 38.58% | 46.42% | 5831.6176 | 2829.6529 | 10.5069 | 5625 | 8454.6529 | 2623.0353 | 8454.6529 | 5831.6176 | 2623.0353 | 18.4026 | 9.9038 | 20.4107 | 0 | 20.4107 | 0 | -32.2224 | 0.2728 | 817.8948 | 0 | 0 | 817.8948 | 2405.205 | 0 | 0 | 2405.205 | 817.8948 | 6543.1582 | 6543.1582 | 2250 | 980.1857 | 7841.4858 | 7841.4858 | 2706.875 | 11:30 | 11.5
winter | 12 | 0.045 | 900.6757 | -1349.3243 | 2250 | 20.2652 | 31.0804 | 1349.3243 | 0.045 | 30.3598 | 2396.043 | -310.832 | 2706.875 | 0 | -310.832 | 38.58% | 46.42% | 5831.6176 | 2818.8741 | 10.5446 | 5625 | 8443.8741 | 2612.2565 | 8443.8741 | 5831.6176 | 2612.2565 | 20.2652 | 9.8661 | 20.4107 | 0 | 20.4107 | 0 | -30.3598 | 0.27167 | 900.6757 | 0 | 0 | 900.6757 | 2396.043 | 0 | 0 | 2396.043 | 900.6757 | 7205.4053 | 7205.4053 | 2250 | 1079.9946 | 8639.9571 | 8639.9571 | 2706.875 | 12:00 | 12
winter | 12.5 | 0.045 | 928.6496 | -1321.3504 | 2250 | 20.8946 | 31.0439 | 1321.3504 | 0.045 | 29.7304 | 2387.189 | -319.686 | 2706.875 | 0 | -319.686 | 38.58% | 46.42% | 5831.6176 | 2808.4576 | 10.5811 | 5625 | 8433.4576 | 2601.84 | 8433.4576 | 5831.6176 | 2601.84 | 20.8946 | 9.8296 | 20.4107 | 0 | 20.4107 | 0 | -29.7304 | 0.27059 | 928.6496 | 0 | 0 | 928.6496 | 2387.189 | 0 | 0 | 2387.189 | 928.6496 | 7429.1968 | 7429.1968 | 2250 | 1113.7228 | 8909.7826 | 8909.7826 | 2706.875 | 12:30 | 12.5
winter | 13 | 0.045 | 923.3094 | -1326.6906 | 2250 | 20.7745 | 30.9993 | 1326.6906 | 0.045 | 29.8505 | 2376.356 | -330.519 | 2706.875 | 0 | -330.519 | 38.58% | 46.42% | 5831.6176 | 2795.7129 | 10.6257 | 5625 | 8420.7129 | 2589.0953 | 8420.7129 | 5831.6176 | 2589.0953 | 20.7745 | 9.785 | 20.4107 | 0 | 20.4107 | 0 | -29.8505 | 0.26927 | 923.3094 | 0 | 0 | 923.3094 | 2376.356 | 0 | 0 | 2376.356 | 923.3094 | 7386.4751 | 7386.4751 | 2250 | 1107.2841 | 8858.273 | 8858.273 | 2706.875 | 13:00 | 13
winter | 13.5 | 0.045 | 902.2069 | -1347.7931 | 2250 | 20.2997 | 30.7051 | 1347.7931 | 0.045 | 30.3253 | 2304.902 | -401.973 | 2706.875 | 0 | -401.973 | 38.58% | 46.42% | 5831.6176 | 2711.6494 | 10.9199 | 5625 | 8336.6494 | 2505.0318 | 8336.6494 | 5831.6176 | 2505.0318 | 20.2997 | 9.4908 | 20.4107 | 0 | 20.4107 | 0 | -30.3253 | 0.26052 | 902.2069 | 0 | 0 | 902.2069 | 2304.902 | 0 | 0 | 2304.902 | 902.2069 | 7217.6553 | 7217.6553 | 2250 | 1081.8409 | 8654.727 | 8654.727 | 2706.875 | 13:30 | 13.5
winter | 14 | 0.045 | 840.637 | -1409.363 | 2250 | 18.9143 | 30.2924 | 1409.363 | 0.045 | 31.7107 | 2204.675 | -502.2 | 2706.875 | 0 | -502.2 | 38.58% | 46.42% | 5831.6176 | 2593.7353 | 11.3326 | 5625 | 8218.7353 | 2387.1176 | 8218.7353 | 5831.6176 | 2387.1176 | 18.9143 | 9.0781 | 20.4107 | 0 | 20.4107 | 0 | -31.7107 | 0.24826 | 840.637 | 0 | 0 | 840.637 | 2204.675 | 0 | 0 | 2204.675 | 840.637 | 6725.0957 | 6725.0957 | 2250 | 1007.606 | 8060.8479 | 8060.8479 | 2706.875 | 14:00 | 14
winter | 14.5 | 0.045 | 854.5396 | -1395.4604 | 2250 | 19.2271 | 30.0044 | 1395.4604 | 0.045 | 31.3979 | 2134.735 | -572.14 | 2706.875 | 0 | -572.14 | 38.58% | 46.42% | 5831.6176 | 2511.4529 | 11.6206 | 5625 | 8136.4529 | 2304.8353 | 8136.4529 | 5831.6176 | 2304.8353 | 19.2271 | 8.7901 | 20.4107 | 0 | 20.4107 | 0 | -31.3979 | 0.2397 | 854.5396 | 0 | 0 | 854.5396 | 2134.735 | 0 | 0 | 2134.735 | 854.5396 | 6836.3169 | 6836.3169 | 2250 | 1024.3684 | 8194.9473 | 8194.9473 | 2706.875 | 14:30 | 14.5
winter | 15 | 0.045 | 864.9808 | -1385.0192 | 2250 | 19.4621 | 29.6953 | 1385.0192 | 0.045 | 31.1629 | 2059.653 | -647.222 | 2706.875 | 0 | -647.222 | 38.58% | 46.42% | 5831.6176 | 2423.1212 | 11.9297 | 5625 | 8048.1212 | 2216.5035 | 8048.1212 | 5831.6176 | 2216.5035 | 19.4621 | 8.4809 | 20.4107 | 0 | 20.4107 | 0 | -31.1629 | 0.23052 | 864.9808 | 0 | 0 | 864.9808 | 2059.653 | 0 | 0 | 2059.653 | 864.9808 | 6919.8462 | 6919.8462 | 2250 | 1036.9573 | 8295.6586 | 8295.6586 | 2706.875 | 15:00 | 15
winter | 15.5 | 0.045 | 790.3176 | -1459.6824 | 2250 | 17.7821 | 29.5108 | 1459.6824 | 0.045 | 32.8429 | 2014.843 | -692.032 | 2706.875 | 0 | -692.032 | 38.58% | 46.42% | 5831.6176 | 2370.4035 | 12.1142 | 5625 | 7995.4035 | 2163.7859 | 7995.4035 | 5831.6176 | 2163.7859 | 17.7821 | 8.2964 | 20.4107 | 0 | 20.4107 | 0 | -32.8429 | 0.22503 | 790.3176 | 0 | 0 | 790.3176 | 2014.843 | 0 | 0 | 2014.843 | 790.3176 | 6322.541 | 6322.541 | 2250 | 946.936 | 7575.4877 | 7575.4877 | 2706.875 | 15:30 | 15.5
winter | 16 | 0.045 | 924.4799 | -1325.5201 | 2250 | 20.8008 | 29.5527 | 1325.5201 | 0.045 | 29.8242 | 2025.039 | -681.836 | 2706.875 | 0 | -681.836 | 38.58% | 46.42% | 5831.6176 | 2382.3988 | 12.0723 | 5625 | 8007.3988 | 2175.7812 | 8007.3988 | 5831.6176 | 2175.7812 | 20.8008 | 8.3384 | 20.4107 | 0 | 20.4107 | 0 | -29.8242 | 0.22628 | 924.4799 | 0 | 0 | 924.4799 | 2025.039 | 0 | 0 | 2025.039 | 924.4799 | 7395.8394 | 7395.8394 | 2250 | 1108.6954 | 8869.5635 | 8869.5635 | 2706.875 | 16:00 | 16
winter | 16.5 | 0.045 | 1080.3407 | -1169.6593 | 2250 | 24.3077 | 29.6607 | 1169.6593 | 0.045 | 26.3173 | 2051.271 | -655.604 | 2706.875 | 0 | -655.604 | 38.58% | 46.42% | 5831.6176 | 2413.26 | 11.9643 | 5625 | 8038.26 | 2206.6424 | 8038.26 | 5831.6176 | 2206.6424 | 24.3077 | 8.4464 | 20.4107 | 0 | 20.4107 | 0 | -26.3173 | 0.22949 | 1080.3407 | 0 | 0 | 1080.3407 | 2051.271 | 0 | 0 | 2051.271 | 1080.3407 | 8642.7256 | 8642.7256 | 2250 | 1296.6168 | 10372.9342 | 10372.9342 | 2706.875 | 16:30 | 16.5
winter | 17 | 0.045 | 1072.907 | -1177.093 | 2250 | 24.1404 | 29.6743 | 1177.093 | 0.045 | 26.4846 | 2054.57 | -652.305 | 2706.875 | 0 | -652.305 | 38.58% | 46.42% | 5831.6176 | 2417.1412 | 11.9507 | 5625 | 8042.1412 | 2210.5235 | 8042.1412 | 5831.6176 | 2210.5235 | 24.1404 | 8.46 | 20.4107 | 0 | 20.4107 | 0 | -26.4846 | 0.22989 | 1072.907 | 0 | 0 | 1072.907 | 2054.57 | 0 | 0 | 2054.57 | 1072.907 | 8583.2559 | 8583.2559 | 2250 | 1287.6539 | 10301.2316 | 10301.2316 | 2706.875 | 17:00 | 17
winter | 17.5 | 0.045 | 1075.1086 | -1174.8914 | 2250 | 24.1899 | 27.5541 | 1174.8914 | 0.045 | 26.4351 | 1539.645 | -1167.23 | 2706.875 | 0 | -1167.23 | 38.58% | 46.42% | 5831.6176 | 1811.3471 | 14.0709 | 5625 | 7436.3471 | 1604.7294 | 7436.3471 | 5831.6176 | 1604.7294 | 24.1899 | 6.3397 | 20.4107 | 0 | 20.4107 | 0 | -26.4351 | 0.16689 | 1075.1086 | 0 | 0 | 1075.1086 | 1539.645 | 0 | 0 | 1539.645 | 1075.1086 | 8600.8691 | 8600.8691 | 2250 | 1290.3085 | 10322.4679 | 10322.4679 | 2706.875 | 17:30 | 17.5
winter | 18 | 0.045 | 1081.2926 | -1168.7074 | 2250 | 24.3291 | 25.4662 | 1168.7074 | 0.045 | 26.2959 | 1032.6 | -1674.275 | 2706.875 | 0 | -1674.275 | 38.58% | 46.42% | 5831.6176 | 1214.8235 | 16.1588 | 5625 | 6839.8235 | 1008.2059 | 6839.8235 | 5831.6176 | 1008.2059 | 24.3291 | 4.2519 | 20.4107 | 0 | 20.4107 | 0 | -26.2959 | 0.10485 | 1081.2926 | 0 | 0 | 1081.2926 | 1032.6 | 0 | 0 | 1032.6 | 1081.2926 | 8650.3408 | 8650.3408 | 2250 | 1297.7645 | 10382.1159 | 10382.1159 | 2706.875 | 18:00 | 18
winter | 18.5 | 0.045 | 1028.364 | -1221.636 | 2250 | 23.1382 | 25.5036 | 1221.636 | 0.045 | 27.4868 | 1041.672 | -1665.203 | 2706.875 | 0 | -1665.203 | 38.58% | 46.42% | 5831.6176 | 1225.4965 | 16.1214 | 5625 | 6850.4965 | 1018.8788 | 6850.4965 | 5831.6176 | 1018.8788 | 23.1382 | 4.2892 | 20.4107 | 0 | 20.4107 | 0 | -27.4868 | 0.10596 | 1028.364 | 0 | 0 | 1028.364 | 1041.672 | 0 | 0 | 1041.672 | 1028.364 | 8226.9121 | 8226.9121 | 2250 | 1233.9485 | 9871.5879 | 9871.5879 | 2706.875 | 18:30 | 18.5
winter | 19 | 0.045 | 1013.7022 | -1236.2978 | 2250 | 22.8083 | 25.3902 | 1236.2978 | 0.045 | 27.8167 | 1014.143 | -1692.732 | 2706.875 | 0 | -1692.732 | 38.58% | 46.42% | 5831.6176 | 1193.1094 | 16.2348 | 5625 | 6818.1094 | 986.4918 | 6818.1094 | 5831.6176 | 986.4918 | 22.8083 | 4.1759 | 20.4107 | 0 | 20.4107 | 0 | -27.8167 | 0.1026 | 1013.7022 | 0 | 0 | 1013.7022 | 1014.143 | 0 | 0 | 1014.143 | 1013.7022 | 8109.6177 | 8109.6177 | 2250 | 1216.2708 | 9730.166 | 9730.166 | 2706.875 | 19:00 | 19
winter | 19.5 | 0.045 | 956.6412 | -1293.3588 | 2250 | 21.5244 | 25.2457 | 1293.3588 | 0.045 | 29.1006 | 979.034 | -1727.841 | 2706.875 | 0 | -1727.841 | 38.58% | 46.42% | 5831.6176 | 1151.8047 | 16.3793 | 5625 | 6776.8047 | 945.1871 | 6776.8047 | 5831.6176 | 945.1871 | 21.5244 | 4.0313 | 20.4107 | 0 | 20.4107 | 0 | -29.1006 | 0.098299 | 956.6412 | 0 | 0 | 956.6412 | 979.034 | 0 | 0 | 979.034 | 956.6412 | 7653.1299 | 7653.1299 | 2250 | 1147.4723 | 9179.7787 | 9179.7787 | 2706.875 | 19:30 | 19.5
winter | 20 | 0.045 | 934.2667 | -1315.7333 | 2250 | 21.021 | 25.2326 | 1315.7333 | 0.045 | 29.604 | 975.855 | -1731.02 | 2706.875 | 0 | -1731.02 | 38.58% | 46.42% | 5831.6176 | 1148.0647 | 16.3924 | 5625 | 6773.0647 | 941.4471 | 6773.0647 | 5831.6176 | 941.4471 | 21.021 | 4.0182 | 20.4107 | 0 | 20.4107 | 0 | -29.604 | 0.09791 | 934.2667 | 0 | 0 | 934.2667 | 975.855 | 0 | 0 | 975.855 | 934.2667 | 7474.1338 | 7474.1338 | 2250 | 1120.4954 | 8963.9631 | 8963.9631 | 2706.875 | 20:00 | 20
winter | 20.5 | 0.045 | 891.0571 | -1358.9429 | 2250 | 20.0488 | 25.2101 | 1358.9429 | 0.045 | 30.5762 | 970.405 | -1736.47 | 2706.875 | 0 | -1736.47 | 38.58% | 46.42% | 5831.6176 | 1141.6529 | 16.4149 | 5625 | 6766.6529 | 935.0353 | 6766.6529 | 5831.6176 | 935.0353 | 20.0488 | 3.9958 | 20.4107 | 0 | 20.4107 | 0 | -30.5762 | 0.097244 | 891.0571 | 0 | 0 | 891.0571 | 970.405 | 0 | 0 | 970.405 | 891.0571 | 7128.4565 | 7128.4565 | 2250 | 1068.3975 | 8547.1801 | 8547.1801 | 2706.875 | 20:30 | 20.5
winter | 21 | 0.045 | 880.3018 | -1369.6982 | 2250 | 19.8068 | 25.1196 | 1369.6982 | 0.045 | 30.8182 | 948.416 | -1758.459 | 2706.875 | 0 | -1758.459 | 38.58% | 46.42% | 5831.6176 | 1115.7835 | 16.5054 | 5625 | 6740.7835 | 909.1659 | 6740.7835 | 5831.6176 | 909.1659 | 19.8068 | 3.9052 | 20.4107 | 0 | 20.4107 | 0 | -30.8182 | 0.094553 | 880.3018 | 0 | 0 | 880.3018 | 948.416 | 0 | 0 | 948.416 | 880.3018 | 7042.4141 | 7042.4141 | 2250 | 1055.4298 | 8443.4386 | 8443.4386 | 2706.875 | 21:00 | 21
winter | 21.5 | 0.045 | 751.3272 | -1498.6728 | 2250 | 16.9049 | 24.9931 | 1498.6728 | 0.045 | 33.7201 | 917.701 | -1789.174 | 2706.875 | 0 | -1789.174 | 38.58% | 46.42% | 5831.6176 | 1079.6482 | 16.6319 | 5625 | 6704.6482 | 873.0306 | 6704.6482 | 5831.6176 | 873.0306 | 16.9049 | 3.7788 | 20.4107 | 0 | 20.4107 | 0 | -33.7201 | 0.090795 | 751.3272 | 0 | 0 | 751.3272 | 917.701 | 0 | 0 | 917.701 | 751.3272 | 6010.6177 | 6010.6177 | 2250 | 899.9252 | 7199.4017 | 7199.4017 | 2706.875 | 21:30 | 21.5
winter | 22 | 0.045 | 723.9617 | -1526.0383 | 2250 | 16.2891 | 23.8586 | 1526.0383 | 0.045 | 34.3359 | 642.179 | -2064.696 | 2706.875 | 0 | -2064.696 | 38.58% | 46.42% | 5831.6176 | 755.5047 | 17.7664 | 5625 | 6380.5047 | 548.8871 | 6380.5047 | 5831.6176 | 548.8871 | 16.2891 | 2.6443 | 20.4107 | 0 | 20.4107 | 0 | -34.3359 | 0.057084 | 723.9617 | 0 | 0 | 723.9617 | 642.179 | 0 | 0 | 642.179 | 723.9617 | 5791.6934 | 5791.6934 | 2250 | 866.9306 | 6935.4447 | 6935.4447 | 2706.875 | 22:00 | 22
winter | 22.5 | 0.045 | 679.5419 | -1570.4581 | 2250 | 15.2897 | 22.6287 | 1570.4581 | 0.045 | 35.3353 | 343.49 | -2363.385 | 2706.875 | 0 | -2363.385 | 38.58% | 46.42% | 5831.6176 | 404.1059 | 18.9963 | 5625 | 6029.1059 | 197.4882 | 6029.1059 | 5831.6176 | 197.4882 | 15.2897 | 1.4144 | 20.4107 | 0 | 20.4107 | 0 | -35.3353 | 0.020539 | 679.5419 | 0 | 0 | 679.5419 | 343.49 | 0 | 0 | 343.49 | 679.5419 | 5436.335 | 5436.335 | 2250 | 813.3736 | 6506.9891 | 6506.9891 | 2706.875 | 22:30 | 22.5
winter | 23 | 0.045 | 588.5651 | -1661.4349 | 2250 | 13.2427 | 22.37 | 1661.4349 | 0.045 | 37.3823 | 280.665 | -2426.21 | 2706.875 | 0 | -2426.21 | 38.58% | 46.42% | 5831.6176 | 330.1941 | 19.255 | 5625 | 5955.1941 | 123.5765 | 5955.1941 | 5831.6176 | 123.5765 | 13.2427 | 1.1557 | 20.4107 | 0 | 20.4107 | 0 | -37.3823 | 0.012852 | 588.5651 | 0 | 0 | 588.5651 | 280.665 | 0 | 0 | 280.665 | 588.5651 | 4708.521 | 4708.521 | 2250 | 703.683 | 5629.4638 | 5629.4638 | 2706.875 | 23:00 | 23
winter | 23.5 | 0.045 | 517.5078 | -1732.4922 | 2250 | 11.6439 | 22.1522 | 1732.4922 | 0.045 | 38.9811 | 227.759 | -2479.116 | 2706.875 | 0 | -2479.116 | 38.58% | 46.42% | 5831.6176 | 267.9518 | 19.4728 | 5625 | 5892.9518 | 61.3341 | 5892.9518 | 5831.6176 | 61.3341 | 11.6439 | 0.93783 | 20.4107 | 0 | 20.4107 | 0 | -38.9811 | 0.0063787 | 517.5078 | 0 | 0 | 517.5078 | 227.759 | 0 | 0 | 227.759 | 517.5078 | 4140.0625 | 4140.0625 | 2250 | 618.0092 | 4944.0734 | 4944.0734 | 2706.875 | 23:30 | 23.5
transition 1 | 0 | 0.015 | 430.31 | 430.31 | 0 | 0 | 0 | 0 | 0.015 | 0 | 178.639 | 178.639 | 0 | 178.639 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1285.9386 | 1285.9386 | 0 | 3.2273 | 0.73557 | 0 | 0.73557 | 0.73557 | 3.2273 | 3.2273 | 0 | 430.31 | 0 | 0 | 430.31 | 178.639 | 0 | 0 | 178.639 | 430.31 | 0 | 0 | 0 | 512.8748 | 0 | 0 | 0 | 1 | 0
transition 1 | 0.5 | 0.015 | 387.6275 | 387.6275 | 0 | 0 | 0 | 0 | 0.015 | 0 | 143.755 | 143.755 | 0 | 143.755 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1138.1924 | 1138.1924 | 0 | 2.9072 | 0.59193 | 0 | 0.59193 | 0.59193 | 2.9072 | 2.9072 | 0 | 387.6275 | 0 | 0 | 387.6275 | 143.755 | 0 | 0 | 143.755 | 387.6275 | 0 | 0 | 0 | 461.4125 | 0 | 0 | 0 | 48 | 23.5
transition 1 | 1 | 0.015 | 397.537 | 397.537 | 0 | 0 | 0 | 0 | 0.015 | 0 | 129.871 | 129.871 | 0 | 129.871 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1146.6319 | 1146.6319 | 0 | 2.9815 | 0.53476 | 0 | 0.53476 | 0.53476 | 2.9815 | 2.9815 | 0 | 397.537 | 0 | 0 | 397.537 | 129.871 | 0 | 0 | 129.871 | 397.537 | 0 | 0 | 0 | 473.3603 | 0 | 0 | 0
transition 1 | 1.5 | 0.015 | 307.3038 | 307.3038 | 0 | 0 | 0 | 0 | 0.015 | 0 | 119.795 | 119.795 | 0 | 119.795 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 909.1949 | 909.1949 | 0 | 2.3048 | 0.49327 | 0 | 0.49327 | 0.49327 | 2.3048 | 2.3048 | 0 | 307.3038 | 0 | 0 | 307.3038 | 119.795 | 0 | 0 | 119.795 | 307.3038 | 0 | 0 | 0 | 364.5662 | 0 | 0 | 0
transition 1 | 2 | 0.015 | 300.7653 | 300.7653 | 0 | 0 | 0 | 0 | 0.015 | 0 | 110.281 | 110.281 | 0 | 110.281 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 881.6556 | 881.6556 | 0 | 2.2557 | 0.4541 | 0 | 0.4541 | 0.4541 | 2.2557 | 2.2557 | 0 | 300.7653 | 0 | 0 | 300.7653 | 110.281 | 0 | 0 | 110.281 | 300.7653 | 0 | 0 | 0 | 356.6827 | 0 | 0 | 0
transition 1 | 2.5 | 0.015 | 304.1312 | 304.1312 | 0 | 0 | 0 | 0 | 0.015 | 0 | 107.605 | 107.605 | 0 | 107.605 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 886.9221 | 886.9221 | 0 | 2.281 | 0.44308 | 0 | 0.44308 | 0.44308 | 2.281 | 2.281 | 0 | 304.1312 | 0 | 0 | 304.1312 | 107.605 | 0 | 0 | 107.605 | 304.1312 | 0 | 0 | 0 | 360.741 | 0 | 0 | 0
transition 1 | 3 | 0.015 | 336.6653 | 336.6653 | 0 | 0 | 0 | 0 | 0.015 | 0 | 108.482 | 108.482 | 0 | 108.482 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 969.2891 | 969.2891 | 0 | 2.525 | 0.44669 | 0 | 0.44669 | 0.44669 | 2.525 | 2.525 | 0 | 336.6653 | 0 | 0 | 336.6653 | 108.482 | 0 | 0 | 108.482 | 336.6653 | 0 | 0 | 0 | 399.9673 | 0 | 0 | 0
transition 1 | 3.5 | 0.015 | 351.7545 | 351.7545 | 0 | 0 | 0 | 0 | 0.015 | 0 | 234.161 | 234.161 | 0 | 234.161 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1154.8697 | 1154.8697 | 0 | 2.6382 | 0.96419 | 0 | 0.96419 | 0.96419 | 2.6382 | 2.6382 | 0 | 351.7545 | 0 | 0 | 351.7545 | 234.161 | 0 | 0 | 234.161 | 351.7545 | 0 | 0 | 0 | 418.1603 | 0 | 0 | 0
transition 1 | 4 | 0.015 | 323.9038 | 323.9038 | 0 | 0 | 0 | 0 | 0.015 | 0 | 360.044 | 360.044 | 0 | 360.044 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1233.3406 | 1233.3406 | 0 | 2.4293 | 1.4825 | 0 | 1.4825 | 1.4825 | 2.4293 | 2.4293 | 0 | 323.9038 | 0 | 0 | 323.9038 | 360.044 | 0 | 0 | 360.044 | 323.9038 | 0 | 0 | 0 | 384.5808 | 0 | 0 | 0
transition 1 | 4.5 | 0.015 | 330.5913 | 330.5913 | 0 | 0 | 0 | 0 | 0.015 | 0 | 371.447 | 371.447 | 0 | 371.447 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1263.4748 | 1263.4748 | 0 | 2.4794 | 1.5295 | 0 | 1.5295 | 1.5295 | 2.4794 | 2.4794 | 0 | 330.5913 | 0 | 0 | 330.5913 | 371.447 | 0 | 0 | 371.447 | 330.5913 | 0 | 0 | 0 | 392.644 | 0 | 0 | 0
transition 1 | 5 | 0.015 | 327.5583 | 327.5583 | 0 | 0 | 0 | 0 | 0.015 | 0 | 392.243 | 392.243 | 0 | 392.243 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1280.358 | 1280.358 | 0 | 2.4567 | 1.6151 | 0 | 1.6151 | 1.6151 | 2.4567 | 2.4567 | 0 | 327.5583 | 0 | 0 | 327.5583 | 392.243 | 0 | 0 | 392.243 | 327.5583 | 0 | 0 | 0 | 388.987 | 0 | 0 | 0
transition 1 | 5.5 | 0.015 | 369.6685 | 369.6685 | 0 | 0 | 0 | 0 | 0.015 | 0 | 409.397 | 409.397 | 0 | 409.397 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1405.8147 | 1405.8147 | 0 | 2.7725 | 1.6858 | 0 | 1.6858 | 1.6858 | 2.7725 | 2.7725 | 0 | 369.6685 | 0 | 0 | 369.6685 | 409.397 | 0 | 0 | 409.397 | 369.6685 | 0 | 0 | 0 | 439.7593 | 0 | 0 | 0
transition 1 | 6 | 0.015 | 439.112 | 439.112 | 0 | 0 | 0 | 0 | 0.015 | 0 | 465.782 | 465.782 | 0 | 465.782 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1645.7588 | 1645.7588 | 0 | 3.2933 | 1.9179 | 0 | 1.9179 | 1.9179 | 3.2933 | 3.2933 | 0 | 439.112 | 0 | 0 | 439.112 | 465.782 | 0 | 0 | 465.782 | 439.112 | 0 | 0 | 0 | 523.4873 | 0 | 0 | 0
transition 1 | 6.5 | 0.015 | 489.3928 | 489.3928 | 0 | 0 | 0 | 0 | 0.015 | 0 | 543.48 | 543.48 | 0 | 543.48 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1862.8703 | 1862.8703 | 0 | 3.6704 | 2.2379 | 0 | 2.2379 | 2.2379 | 3.6704 | 3.6704 | 0 | 489.3928 | 0 | 0 | 489.3928 | 543.48 | 0 | 0 | 543.48 | 489.3928 | 0 | 0 | 0 | 584.1109 | 0 | 0 | 0
transition 1 | 7 | 0.045 | 686.8831 | -1563.1169 | 2250 | 15.4549 | 23.6966 | 1563.1169 | 0.045 | 35.1701 | 602.842 | -2104.033 | 2706.875 | 0 | -2104.033 | 38.58% | 46.42% | 5831.6176 | 709.2259 | 17.9284 | 5625 | 6334.2259 | 502.6082 | 6334.2259 | 5831.6176 | 502.6082 | 15.4549 | 2.4823 | 20.4107 | 0 | 20.4107 | 0 | -35.1701 | 0.052271 | 686.8831 | 0 | 0 | 686.8831 | 602.842 | 0 | 0 | 602.842 | 686.8831 | 5495.0645 | 5495.0645 | 2250 | 822.2249 | 6577.7992 | 6577.7992 | 2706.875
transition 1 | 7.5 | 0.045 | 755.7643 | -1494.2357 | 2250 | 17.0047 | 25.5752 | 1494.2357 | 0.045 | 33.6203 | 1059.057 | -1647.818 | 2706.875 | 0 | -1647.818 | 38.58% | 46.42% | 5831.6176 | 1245.9494 | 16.0498 | 5625 | 6870.9494 | 1039.3318 | 6870.9494 | 5831.6176 | 1039.3318 | 17.0047 | 4.3608 | 20.4107 | 0 | 20.4107 | 0 | -33.6203 | 0.10809 | 755.7643 | 0 | 0 | 755.7643 | 1059.057 | 0 | 0 | 1059.057 | 755.7643 | 6046.1147 | 6046.1147 | 2250 | 905.2751 | 7242.2005 | 7242.2005 | 2706.875
transition 1 | 8 | 0.045 | 817.5326 | -1432.4674 | 2250 | 18.3945 | 28.1666 | 1432.4674 | 0.045 | 32.2305 | 1688.416 | -1018.459 | 2706.875 | 0 | -1018.459 | 38.58% | 46.42% | 5831.6176 | 1986.3718 | 13.4584 | 5625 | 7611.3718 | 1779.7541 | 7611.3718 | 5831.6176 | 1779.7541 | 18.3945 | 6.9523 | 20.4107 | 0 | 20.4107 | 0 | -32.2305 | 0.18509 | 817.5326 | 0 | 0 | 817.5326 | 1688.416 | 0 | 0 | 1688.416 | 817.5326 | 6540.2607 | 6540.2607 | 2250 | 979.749 | 7837.9924 | 7837.9924 | 2706.875
transition 1 | 8.5 | 0.045 | 884.2237 | -1365.7763 | 2250 | 19.895 | 28.8471 | 1365.7763 | 0.045 | 30.73 | 1853.672 | -853.203 | 2706.875 | 0 | -853.203 | 38.58% | 46.42% | 5831.6176 | 2180.7906 | 12.7779 | 5625 | 7805.7906 | 1974.1729 | 7805.7906 | 5831.6176 | 1974.1729 | 19.895 | 7.6328 | 20.4107 | 0 | 20.4107 | 0 | -30.73 | 0.20531 | 884.2237 | 0 | 0 | 884.2237 | 1853.672 | 0 | 0 | 1853.672 | 884.2237 | 7073.7896 | 7073.7896 | 2250 | 1060.1585 | 8481.2681 | 8481.2681 | 2706.875
transition 1 | 9 | 0.045 | 896.9931 | -1353.0069 | 2250 | 20.1823 | 28.6851 | 1353.0069 | 0.045 | 30.4427 | 1814.32 | -892.555 | 2706.875 | 0 | -892.555 | 38.58% | 46.42% | 5831.6176 | 2134.4941 | 12.9399 | 5625 | 7759.4941 | 1927.8765 | 7759.4941 | 5831.6176 | 1927.8765 | 20.1823 | 7.4707 | 20.4107 | 0 | 20.4107 | 0 | -30.4427 | 0.2005 | 896.9931 | 0 | 0 | 896.9931 | 1814.32 | 0 | 0 | 1814.32 | 896.9931 | 7175.9448 | 7175.9448 | 2250 | 1075.5546 | 8604.4367 | 8604.4367 | 2706.875
transition 1 | 9.5 | 0.045 | 871.846 | -1378.154 | 2250 | 19.6165 | 28.4521 | 1378.154 | 0.045 | 31.0085 | 1757.748 | -949.127 | 2706.875 | 0 | -949.127 | 38.58% | 46.42% | 5831.6176 | 2067.9388 | 13.1729 | 5625 | 7692.9388 | 1861.3212 | 7692.9388 | 5831.6176 | 1861.3212 | 19.6165 | 7.2378 | 20.4107 | 0 | 20.4107 | 0 | -31.0085 | 0.19358 | 871.846 | 0 | 0 | 871.846 | 1757.748 | 0 | 0 | 1757.748 | 871.846 | 6974.7681 | 6974.7681 | 2250 | 1045.2347 | 8361.8779 | 8361.8779 | 2706.875
transition 1 | 10 | 0.045 | 854.4984 | -1395.5016 | 2250 | 19.2262 | 28.2022 | 1395.5016 | 0.045 | 31.3988 | 1697.06 | -1009.815 | 2706.875 | 0 | -1009.815 | 38.58% | 46.42% | 5831.6176 | 1996.5412 | 13.4228 | 5625 | 7621.5412 | 1789.9235 | 7621.5412 | 5831.6176 | 1789.9235 | 19.2262 | 6.9879 | 20.4107 | 0 | 20.4107 | 0 | -31.3988 | 0.18615 | 854.4984 | 0 | 0 | 854.4984 | 1697.06 | 0 | 0 | 1697.06 | 854.4984 | 6835.9868 | 6835.9868 | 2250 | 1024.3187 | 8194.5493 | 8194.5493 | 2706.875
transition 1 | 10.5 | 0.045 | 889.0468 | -1360.9532 | 2250 | 20.0036 | 28.1644 | 1360.9532 | 0.045 | 30.6214 | 1687.876 | -1018.999 | 2706.875 | 0 | -1018.999 | 38.58% | 46.42% | 5831.6176 | 1985.7365 | 13.4606 | 5625 | 7610.7365 | 1779.1188 | 7610.7365 | 5831.6176 | 1779.1188 | 20.0036 | 6.9501 | 20.4107 | 0 | 20.4107 | 0 | -30.6214 | 0.18503 | 889.0468 | 0 | 0 | 889.0468 | 1687.876 | 0 | 0 | 1687.876 | 889.0468 | 7112.374 | 7112.374 | 2250 | 1065.9737 | 8527.7894 | 8527.7894 | 2706.875
transition 1 | 11 | 0.045 | 801.0835 | -1448.9165 | 2250 | 18.0244 | 28.1697 | 1448.9165 | 0.045 | 32.6006 | 1689.158 | -1017.717 | 2706.875 | 0 | -1017.717 | 38.58% | 46.42% | 5831.6176 | 1987.2447 | 13.4553 | 5625 | 7612.2447 | 1780.6271 | 7612.2447 | 5831.6176 | 1780.6271 | 18.0244 | 6.9554 | 20.4107 | 0 | 20.4107 | 0 | -32.6006 | 0.18519 | 801.0835 | 0 | 0 | 801.0835 | 1689.158 | 0 | 0 | 1689.158 | 801.0835 | 6408.668 | 6408.668 | 2250 | 959.9164 | 7679.331 | 7679.331 | 2706.875
transition 1 | 11.5 | 0.045 | 810.9109 | -1439.0891 | 2250 | 18.2455 | 28.1196 | 1439.0891 | 0.045 | 32.3795 | 1676.99 | -1029.885 | 2706.875 | 0 | -1029.885 | 38.58% | 46.42% | 5831.6176 | 1972.9294 | 13.5054 | 5625 | 7597.9294 | 1766.3118 | 7597.9294 | 5831.6176 | 1766.3118 | 18.2455 | 6.9053 | 20.4107 | 0 | 20.4107 | 0 | -32.3795 | 0.1837 | 810.9109 | 0 | 0 | 810.9109 | 1676.99 | 0 | 0 | 1676.99 | 810.9109 | 6487.2876 | 6487.2876 | 2250 | 971.7653 | 7774.1227 | 7774.1227 | 2706.875
transition 1 | 12 | 0.045 | 818.5737 | -1431.4263 | 2250 | 18.4179 | 28.0416 | 1431.4263 | 0.045 | 32.2071 | 1658.053 | -1048.822 | 2706.875 | 0 | -1048.822 | 38.58% | 46.42% | 5831.6176 | 1950.6506 | 13.5834 | 5625 | 7575.6506 | 1744.0329 | 7575.6506 | 5831.6176 | 1744.0329 | 18.4179 | 6.8273 | 20.4107 | 0 | 20.4107 | 0 | -32.2071 | 0.18138 | 818.5737 | 0 | 0 | 818.5737 | 1658.053 | 0 | 0 | 1658.053 | 818.5737 | 6548.5898 | 6548.5898 | 2250 | 981.0043 | 7848.0348 | 7848.0348 | 2706.875
transition 1 | 12.5 | 0.045 | 801.9224 | -1448.0776 | 2250 | 18.0433 | 27.8751 | 1448.0776 | 0.045 | 32.5817 | 1617.607 | -1089.268 | 2706.875 | 0 | -1089.268 | 38.58% | 46.42% | 5831.6176 | 1903.0671 | 13.7499 | 5625 | 7528.0671 | 1696.4494 | 7528.0671 | 5831.6176 | 1696.4494 | 18.0433 | 6.6607 | 20.4107 | 0 | 20.4107 | 0 | -32.5817 | 0.17643 | 801.9224 | 0 | 0 | 801.9224 | 1617.607 | 0 | 0 | 1617.607 | 801.9224 | 6415.3794 | 6415.3794 | 2250 | 960.9279 | 7687.4229 | 7687.4229 | 2706.875
transition 1 | 13 | 0.045 | 831.9165 | -1418.0835 | 2250 | 18.7181 | 27.7008 | 1418.0835 | 0.045 | 31.9069 | 1575.286 | -1131.589 | 2706.875 | 0 | -1131.589 | 38.58% | 46.42% | 5831.6176 | 1853.2776 | 13.9242 | 5625 | 7478.2776 | 1646.66 | 7478.2776 | 5831.6176 | 1646.66 | 18.7181 | 6.4865 | 20.4107 | 0 | 20.4107 | 0 | -31.9069 | 0.17125 | 831.9165 | 0 | 0 | 831.9165 | 1575.286 | 0 | 0 | 1575.286 | 831.9165 | 6655.332 | 6655.332 | 2250 | 997.0917 | 7976.7338 | 7976.7338 | 2706.875
transition 1 | 13.5 | 0.045 | 855.3162 | -1394.6838 | 2250 | 19.2446 | 27.4162 | 1394.6838 | 0.045 | 31.3804 | 1506.156 | -1200.719 | 2706.875 | 0 | -1200.719 | 38.58% | 46.42% | 5831.6176 | 1771.9482 | 14.2088 | 5625 | 7396.9482 | 1565.3306 | 7396.9482 | 5831.6176 | 1565.3306 | 19.2446 | 6.2018 | 20.4107 | 0 | 20.4107 | 0 | -31.3804 | 0.16279 | 855.3162 | 0 | 0 | 855.3162 | 1506.156 | 0 | 0 | 1506.156 | 855.3162 | 6842.5298 | 6842.5298 | 2250 | 1025.3048 | 8202.4382 | 8202.4382 | 2706.875
transition 1 | 14 | 0.045 | 798.9763 | -1451.0237 | 2250 | 17.977 | 26.9562 | 1451.0237 | 0.045 | 32.648 | 1394.458 | -1312.417 | 2706.875 | 0 | -1312.417 | 38.58% | 46.42% | 5831.6176 | 1640.5388 | 14.6688 | 5625 | 7265.5388 | 1433.9212 | 7265.5388 | 5831.6176 | 1433.9212 | 17.977 | 5.7419 | 20.4107 | 0 | 20.4107 | 0 | -32.648 | 0.14913 | 798.9763 | 0 | 0 | 798.9763 | 1394.458 | 0 | 0 | 1394.458 | 798.9763 | 6391.8105 | 6391.8105 | 2250 | 957.3757 | 7659.006 | 7659.006 | 2706.875
transition 1 | 14.5 | 0.045 | 774.8787 | -1475.1213 | 2250 | 17.4348 | 26.6536 | 1475.1213 | 0.045 | 33.1902 | 1320.958 | -1385.917 | 2706.875 | 0 | -1385.917 | 38.58% | 46.42% | 5831.6176 | 1554.0682 | 14.9714 | 5625 | 7179.0682 | 1347.4506 | 7179.0682 | 5831.6176 | 1347.4506 | 17.4348 | 5.4392 | 20.4107 | 0 | 20.4107 | 0 | -33.1902 | 0.14013 | 774.8787 | 0 | 0 | 774.8787 | 1320.958 | 0 | 0 | 1320.958 | 774.8787 | 6199.0298 | 6199.0298 | 2250 | 928.3213 | 7426.5702 | 7426.5702 | 2706.875
transition 1 | 15 | 0.045 | 783.9371 | -1466.0629 | 2250 | 17.6386 | 26.3208 | 1466.0629 | 0.045 | 32.9864 | 1240.132 | -1466.743 | 2706.875 | 0 | -1466.743 | 38.58% | 46.42% | 5831.6176 | 1458.9788 | 15.3042 | 5625 | 7083.9788 | 1252.3612 | 7083.9788 | 5831.6176 | 1252.3612 | 17.6386 | 5.1064 | 20.4107 | 0 | 20.4107 | 0 | -32.9864 | 0.13025 | 783.9371 | 0 | 0 | 783.9371 | 1240.132 | 0 | 0 | 1240.132 | 783.9371 | 6271.4971 | 6271.4971 | 2250 | 939.243 | 7513.944 | 7513.944 | 2706.875
transition 1 | 15.5 | 0.045 | 887.6979 | -1362.3021 | 2250 | 19.9732 | 26.1865 | 1362.3021 | 0.045 | 30.6518 | 1207.535 | -1499.34 | 2706.875 | 0 | -1499.34 | 38.58% | 46.42% | 5831.6176 | 1420.6294 | 15.4385 | 5625 | 7045.6294 | 1214.0118 | 7045.6294 | 5831.6176 | 1214.0118 | 19.9732 | 4.9722 | 20.4107 | 0 | 20.4107 | 0 | -30.6518 | 0.12626 | 887.6979 | 0 | 0 | 887.6979 | 1207.535 | 0 | 0 | 1207.535 | 887.6979 | 7101.5835 | 7101.5835 | 2250 | 1064.3474 | 8514.7792 | 8514.7792 | 2706.875
transition 1 | 16 | 0.045 | 822.8597 | -1427.1403 | 2250 | 18.5143 | 26.3292 | 1427.1403 | 0.045 | 32.1107 | 1242.179 | -1464.696 | 2706.875 | 0 | -1464.696 | 38.58% | 46.42% | 5831.6176 | 1461.3871 | 15.2958 | 5625 | 7086.3871 | 1254.7694 | 7086.3871 | 5831.6176 | 1254.7694 | 18.5143 | 5.1149 | 20.4107 | 0 | 20.4107 | 0 | -32.1107 | 0.1305 | 822.8597 | 0 | 0 | 822.8597 | 1242.179 | 0 | 0 | 1242.179 | 822.8597 | 6582.8779 | 6582.8779 | 2250 | 986.172 | 7889.3759 | 7889.3759 | 2706.875
transition 1 | 16.5 | 0.045 | 1018.7086 | -1231.2914 | 2250 | 22.9209 | 26.5923 | 1231.2914 | 0.045 | 27.7041 | 1306.068 | -1400.807 | 2706.875 | 0 | -1400.807 | 38.58% | 46.42% | 5831.6176 | 1536.5506 | 15.0327 | 5625 | 7161.5506 | 1329.9329 | 7161.5506 | 5831.6176 | 1329.9329 | 22.9209 | 5.3779 | 20.4107 | 0 | 20.4107 | 0 | -27.7041 | 0.13831 | 1018.7086 | 0 | 0 | 1018.7086 | 1306.068 | 0 | 0 | 1306.068 | 1018.7086 | 8149.6689 | 8149.6689 | 2250 | 1222.307 | 9778.4558 | 9778.4558 | 2706.875
transition 1 | 17 | 0.045 | 987.541 | -1262.459 | 2250 | 22.2197 | 26.7785 | 1262.459 | 0.045 | 28.4053 | 1351.298 | -1355.577 | 2706.875 | 0 | -1355.577 | 38.58% | 46.42% | 5831.6176 | 1589.7624 | 14.8465 | 5625 | 7214.7624 | 1383.1447 | 7214.7624 | 5831.6176 | 1383.1447 | 22.2197 | 5.5642 | 20.4107 | 0 | 20.4107 | 0 | -28.4053 | 0.14385 | 987.541 | 0 | 0 | 987.541 | 1351.298 | 0 | 0 | 1351.298 | 987.541 | 7900.3276 | 7900.3276 | 2250 | 1184.7281 | 9477.825 | 9477.825 | 2706.875
transition 1 | 17.5 | 0.045 | 985.9257 | -1264.0743 | 2250 | 22.1833 | 25.5361 | 1264.0743 | 0.045 | 28.4417 | 1049.573 | -1657.302 | 2706.875 | 0 | -1657.302 | 38.58% | 46.42% | 5831.6176 | 1234.7918 | 16.0889 | 5625 | 6859.7918 | 1028.1741 | 6859.7918 | 5831.6176 | 1028.1741 | 22.1833 | 4.3218 | 20.4107 | 0 | 20.4107 | 0 | -28.4417 | 0.10693 | 985.9257 | 0 | 0 | 985.9257 | 1049.573 | 0 | 0 | 1049.573 | 985.9257 | 7887.4053 | 7887.4053 | 2250 | 1182.7806 | 9462.2445 | 9462.2445 | 2706.875
transition 1 | 18 | 0.045 | 903.5106 | -1346.4894 | 2250 | 20.329 | 24.2177 | 1346.4894 | 0.045 | 30.296 | 729.399 | -1977.476 | 2706.875 | 0 | -1977.476 | 38.58% | 46.42% | 5831.6176 | 858.1165 | 17.4073 | 5625 | 6483.1165 | 651.4988 | 6483.1165 | 5831.6176 | 651.4988 | 20.329 | 3.0034 | 20.4107 | 0 | 20.4107 | 0 | -30.296 | 0.067756 | 903.5106 | 0 | 0 | 903.5106 | 729.399 | 0 | 0 | 729.399 | 903.5106 | 7228.0845 | 7228.0845 | 2250 | 1083.4127 | 8667.3014 | 8667.3014 | 2706.875
transition 1 | 18.5 | 0.045 | 940.3738 | -1309.6262 | 2250 | 21.1584 | 24.044 | 1309.6262 | 0.045 | 29.4666 | 687.213 | -2019.662 | 2706.875 | 0 | -2019.662 | 38.58% | 46.42% | 5831.6176 | 808.4859 | 17.581 | 5625 | 6433.4859 | 601.8682 | 6433.4859 | 5831.6176 | 601.8682 | 21.1584 | 2.8297 | 20.4107 | 0 | 20.4107 | 0 | -29.4666 | 0.062594 | 940.3738 | 0 | 0 | 940.3738 | 687.213 | 0 | 0 | 687.213 | 940.3738 | 7522.9902 | 7522.9902 | 2250 | 1127.8587 | 9022.8693 | 9022.8693 | 2706.875
transition 1 | 19 | 0.045 | 881.8265 | -1368.1735 | 2250 | 19.8411 | 24.0382 | 1368.1735 | 0.045 | 30.7839 | 685.804 | -2021.071 | 2706.875 | 0 | -2021.071 | 38.58% | 46.42% | 5831.6176 | 806.8282 | 17.5868 | 5625 | 6431.8282 | 600.2106 | 6431.8282 | 5831.6176 | 600.2106 | 19.8411 | 2.8239 | 20.4107 | 0 | 20.4107 | 0 | -30.7839 | 0.062422 | 881.8265 | 0 | 0 | 881.8265 | 685.804 | 0 | 0 | 685.804 | 881.8265 | 7054.6123 | 7054.6123 | 2250 | 1057.2683 | 8458.1461 | 8458.1461 | 2706.875
transition 1 | 19.5 | 0.045 | 864.4092 | -1385.5908 | 2250 | 19.4492 | 24.2218 | 1385.5908 | 0.045 | 31.1758 | 730.373 | -1976.502 | 2706.875 | 0 | -1976.502 | 38.58% | 46.42% | 5831.6176 | 859.2624 | 17.4032 | 5625 | 6484.2624 | 652.6447 | 6484.2624 | 5831.6176 | 652.6447 | 19.4492 | 3.0074 | 20.4107 | 0 | 20.4107 | 0 | -31.1758 | 0.067875 | 864.4092 | 0 | 0 | 864.4092 | 730.373 | 0 | 0 | 730.373 | 864.4092 | 6915.2739 | 6915.2739 | 2250 | 1036.2682 | 8290.1458 | 8290.1458 | 2706.875
transition 1 | 20 | 0.045 | 890.6292 | -1359.3708 | 2250 | 20.0392 | 24.2827 | 1359.3708 | 0.045 | 30.5858 | 745.172 | -1961.703 | 2706.875 | 0 | -1961.703 | 38.58% | 46.42% | 5831.6176 | 876.6729 | 17.3423 | 5625 | 6501.6729 | 670.0553 | 6501.6729 | 5831.6176 | 670.0553 | 20.0392 | 3.0684 | 20.4107 | 0 | 20.4107 | 0 | -30.5858 | 0.069686 | 890.6292 | 0 | 0 | 890.6292 | 745.172 | 0 | 0 | 745.172 | 890.6292 | 7125.0332 | 7125.0332 | 2250 | 1067.8816 | 8543.0525 | 8543.0525 | 2706.875
transition 1 | 20.5 | 0.045 | 876.595 | -1373.405 | 2250 | 19.7234 | 24.1993 | 1373.405 | 0.045 | 30.9016 | 724.908 | -1981.967 | 2706.875 | 0 | -1981.967 | 38.58% | 46.42% | 5831.6176 | 852.8329 | 17.4257 | 5625 | 6477.8329 | 646.2153 | 6477.8329 | 5831.6176 | 646.2153 | 19.7234 | 2.9849 | 20.4107 | 0 | 20.4107 | 0 | -30.9016 | 0.067206 | 876.595 | 0 | 0 | 876.595 | 724.908 | 0 | 0 | 724.908 | 876.595 | 7012.7598 | 7012.7598 | 2250 | 1050.9606 | 8407.6844 | 8407.6844 | 2706.875
transition 1 | 21 | 0.045 | 763.4127 | -1486.5873 | 2250 | 17.1768 | 24.1589 | 1486.5873 | 0.045 | 33.4482 | 715.117 | -1991.758 | 2706.875 | 0 | -1991.758 | 38.58% | 46.42% | 5831.6176 | 841.3141 | 17.4661 | 5625 | 6466.3141 | 634.6965 | 6466.3141 | 5831.6176 | 634.6965 | 17.1768 | 2.9446 | 20.4107 | 0 | 20.4107 | 0 | -33.4482 | 0.066008 | 763.4127 | 0 | 0 | 763.4127 | 715.117 | 0 | 0 | 715.117 | 763.4127 | 6107.3013 | 6107.3013 | 2250 | 914.4966 | 7315.9731 | 7315.9731 | 2706.875
transition 1 | 21.5 | 0.045 | 669.3999 | -1580.6001 | 2250 | 15.0615 | 24.1371 | 1580.6001 | 0.045 | 35.5635 | 709.824 | -1997.051 | 2706.875 | 0 | -1997.051 | 38.58% | 46.42% | 5831.6176 | 835.0871 | 17.4879 | 5625 | 6460.0871 | 628.4694 | 6460.0871 | 5831.6176 | 628.4694 | 15.0615 | 2.9228 | 20.4107 | 0 | 20.4107 | 0 | -35.5635 | 0.065361 | 669.3999 | 0 | 0 | 669.3999 | 709.824 | 0 | 0 | 709.824 | 669.3999 | 5355.1992 | 5355.1992 | 2250 | 801.1455 | 6409.1637 | 6409.1637 | 2706.875
transition 1 | 22 | 0.045 | 710.4059 | -1539.5941 | 2250 | 15.9841 | 23.4265 | 1539.5941 | 0.045 | 34.6409 | 537.228 | -2169.647 | 2706.875 | 0 | -2169.647 | 38.58% | 46.42% | 5831.6176 | 632.0329 | 18.1985 | 5625 | 6257.0329 | 425.4153 | 6257.0329 | 5831.6176 | 425.4153 | 15.9841 | 2.2121 | 20.4107 | 0 | 20.4107 | 0 | -34.6409 | 0.044243 | 710.4059 | 0 | 0 | 710.4059 | 537.228 | 0 | 0 | 537.228 | 710.4059 | 5683.2476 | 5683.2476 | 2250 | 850.5864 | 6804.6916 | 6804.6916 | 2706.875
transition 1 | 22.5 | 0.045 | 623.2204 | -1626.7796 | 2250 | 14.0225 | 22.5838 | 1626.7796 | 0.045 | 36.6025 | 332.59 | -2374.285 | 2706.875 | 0 | -2374.285 | 38.58% | 46.42% | 5831.6176 | 391.2824 | 19.0412 | 5625 | 6016.2824 | 184.6647 | 6016.2824 | 5831.6176 | 184.6647 | 14.0225 | 1.3695 | 20.4107 | 0 | 20.4107 | 0 | -36.6025 | 0.019205 | 623.2204 | 0 | 0 | 623.2204 | 332.59 | 0 | 0 | 332.59 | 623.2204 | 4985.7632 | 4985.7632 | 2250 | 745.4668 | 5963.7347 | 5963.7347 | 2706.875
transition 1 | 23 | 0.045 | 563.774 | -1686.226 | 2250 | 12.6849 | 22.3378 | 1686.226 | 0.045 | 37.9401 | 272.831 | -2434.044 | 2706.875 | 0 | -2434.044 | 38.58% | 46.42% | 5831.6176 | 320.9776 | 19.2872 | 5625 | 5945.9776 | 114.36 | 5945.9776 | 5831.6176 | 114.36 | 12.6849 | 1.1234 | 20.4107 | 0 | 20.4107 | 0 | -37.9401 | 0.011893 | 563.774 | 0 | 0 | 563.774 | 272.831 | 0 | 0 | 272.831 | 563.774 | 4510.1924 | 4510.1924 | 2250 | 673.7924 | 5390.339 | 5390.339 | 2706.875
transition 1 | 23.5 | 0.045 | 500.6068 | -1749.3932 | 2250 | 11.2637 | 22.077 | 1749.3932 | 0.045 | 39.3613 | 209.496 | -2497.379 | 2706.875 | 0 | -2497.379 | 38.58% | 46.42% | 5831.6176 | 246.4659 | 19.548 | 5625 | 5871.4659 | 39.8482 | 5871.4659 | 5831.6176 | 39.8482 | 11.2637 | 0.86263 | 20.4107 | 0 | 20.4107 | 0 | -39.3613 | 0.0041442 | 500.6068 | 0 | 0 | 500.6068 | 209.496 | 0 | 0 | 209.496 | 500.6068 | 4004.8542 | 4004.8542 | 2250 | 597.6316 | 4781.0528 | 4781.0528 | 2706.875
transition 2 | 0 | 0.015 | 379.3809 | 379.3809 | 0 | 0 | 0 | 0 | 0.015 | 0 | 162.438 | 162.438 | 0 | 162.438 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1139.5558 | 1139.5558 | 0 | 2.8454 | 0.66886 | 0 | 0.66886 | 0.66886 | 2.8454 | 2.8454 | 0 | 379.3809 | 0 | 0 | 379.3809 | 162.438 | 0 | 0 | 162.438 | 379.3809 | 0 | 0 | 0 | 451.4695 | 0 | 0 | 0
transition 2 | 0.5 | 0.015 | 353.9354 | 353.9354 | 0 | 0 | 0 | 0 | 0.015 | 0 | 140.381 | 140.381 | 0 | 140.381 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1049.9925 | 1049.9925 | 0 | 2.6545 | 0.57804 | 0 | 0.57804 | 0.57804 | 2.6545 | 2.6545 | 0 | 353.9354 | 0 | 0 | 353.9354 | 140.381 | 0 | 0 | 140.381 | 353.9354 | 0 | 0 | 0 | 420.7899 | 0 | 0 | 0
transition 2 | 1 | 0.015 | 310.2408 | 310.2408 | 0 | 0 | 0 | 0 | 0.015 | 0 | 130.178 | 130.178 | 0 | 130.178 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 928.7526 | 928.7526 | 0 | 2.3268 | 0.53603 | 0 | 0.53603 | 0.53603 | 2.3268 | 2.3268 | 0 | 310.2408 | 0 | 0 | 310.2408 | 130.178 | 0 | 0 | 130.178 | 310.2408 | 0 | 0 | 0 | 368.1073 | 0 | 0 | 0
transition 2 | 1.5 | 0.015 | 306.007 | 306.007 | 0 | 0 | 0 | 0 | 0.015 | 0 | 119.69 | 119.69 | 0 | 119.69 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 905.8294 | 905.8294 | 0 | 2.2951 | 0.49284 | 0 | 0.49284 | 0.49284 | 2.2951 | 2.2951 | 0 | 306.007 | 0 | 0 | 306.007 | 119.69 | 0 | 0 | 119.69 | 306.007 | 0 | 0 | 0 | 363.0027 | 0 | 0 | 0
transition 2 | 2 | 0.015 | 291.5966 | 291.5966 | 0 | 0 | 0 | 0 | 0.015 | 0 | 110.176 | 110.176 | 0 | 110.176 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 858.6103 | 858.6103 | 0 | 2.187 | 0.45367 | 0 | 0.45367 | 0.45367 | 2.187 | 2.187 | 0 | 291.5966 | 0 | 0 | 291.5966 | 110.176 | 0 | 0 | 110.176 | 291.5966 | 0 | 0 | 0 | 345.628 | 0 | 0 | 0
transition 2 | 2.5 | 0.015 | 266.4459 | 266.4459 | 0 | 0 | 0 | 0 | 0.015 | 0 | 112.807 | 112.807 | 0 | 112.807 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 798.8289 | 798.8289 | 0 | 1.9983 | 0.4645 | 0 | 0.4645 | 0.4645 | 1.9983 | 1.9983 | 0 | 266.4459 | 0 | 0 | 266.4459 | 112.807 | 0 | 0 | 112.807 | 266.4459 | 0 | 0 | 0 | 315.3038 | 0 | 0 | 0
transition 2 | 3 | 0.015 | 284.3016 | 284.3016 | 0 | 0 | 0 | 0 | 0.015 | 0 | 109.539 | 109.539 | 0 | 109.539 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 839.6234 | 839.6234 | 0 | 2.1323 | 0.45104 | 0 | 0.45104 | 0.45104 | 2.1323 | 2.1323 | 0 | 284.3016 | 0 | 0 | 284.3016 | 109.539 | 0 | 0 | 109.539 | 284.3016 | 0 | 0 | 0 | 336.8324 | 0 | 0 | 0
transition 2 | 3.5 | 0.015 | 274.0725 | 274.0725 | 0 | 0 | 0 | 0 | 0.015 | 0 | 187.65 | 187.65 | 0 | 187.65 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 905.946 | 905.946 | 0 | 2.0555 | 0.77268 | 0 | 0.77268 | 0.77268 | 2.0555 | 2.0555 | 0 | 274.0725 | 0 | 0 | 274.0725 | 187.65 | 0 | 0 | 187.65 | 274.0725 | 0 | 0 | 0 | 324.4992 | 0 | 0 | 0
transition 2 | 4 | 0.015 | 319.0226 | 319.0226 | 0 | 0 | 0 | 0 | 0.015 | 0 | 266.616 | 266.616 | 0 | 266.616 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1111.2225 | 1111.2225 | 0 | 2.3927 | 1.0978 | 0 | 1.0978 | 1.0978 | 2.3927 | 2.3927 | 0 | 319.0226 | 0 | 0 | 319.0226 | 266.616 | 0 | 0 | 266.616 | 319.0226 | 0 | 0 | 0 | 378.6956 | 0 | 0 | 0
transition 2 | 4.5 | 0.015 | 280.0884 | 280.0884 | 0 | 0 | 0 | 0 | 0.015 | 0 | 249.83 | 249.83 | 0 | 249.83 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 994.1386 | 994.1386 | 0 | 2.1007 | 1.0287 | 0 | 1.0287 | 1.0287 | 2.1007 | 2.1007 | 0 | 280.0884 | 0 | 0 | 280.0884 | 249.83 | 0 | 0 | 249.83 | 280.0884 | 0 | 0 | 0 | 331.7526 | 0 | 0 | 0
transition 2 | 5 | 0.015 | 283.8339 | 283.8339 | 0 | 0 | 0 | 0 | 0.015 | 0 | 237.783 | 237.783 | 0 | 237.783 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 989.3294 | 989.3294 | 0 | 2.1288 | 0.97911 | 0 | 0.97911 | 0.97911 | 2.1288 | 2.1288 | 0 | 283.8339 | 0 | 0 | 283.8339 | 237.783 | 0 | 0 | 237.783 | 283.8339 | 0 | 0 | 0 | 336.2685 | 0 | 0 | 0
transition 2 | 5.5 | 0.015 | 286.6385 | 286.6385 | 0 | 0 | 0 | 0 | 0.015 | 0 | 230.788 | 230.788 | 0 | 230.788 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 988.1116 | 988.1116 | 0 | 2.1498 | 0.9503 | 0 | 0.9503 | 0.9503 | 2.1498 | 2.1498 | 0 | 286.6385 | 0 | 0 | 286.6385 | 230.788 | 0 | 0 | 230.788 | 286.6385 | 0 | 0 | 0 | 339.6501 | 0 | 0 | 0
transition 2 | 6 | 0.015 | 348.2115 | 348.2115 | 0 | 0 | 0 | 0 | 0.015 | 0 | 245.654 | 245.654 | 0 | 245.654 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1159.5335 | 1159.5335 | 0 | 2.6116 | 1.0115 | 0 | 1.0115 | 1.0115 | 2.6116 | 2.6116 | 0 | 348.2115 | 0 | 0 | 348.2115 | 245.654 | 0 | 0 | 245.654 | 348.2115 | 0 | 0 | 0 | 413.8886 | 0 | 0 | 0
transition 2 | 6.5 | 0.015 | 444.2659 | 444.2659 | 0 | 0 | 0 | 0 | 0.015 | 0 | 280.463 | 280.463 | 0 | 280.463 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1440.6213 | 1440.6213 | 0 | 3.332 | 1.1548 | 0 | 1.1548 | 1.1548 | 3.332 | 3.332 | 0 | 444.2659 | 0 | 0 | 444.2659 | 280.463 | 0 | 0 | 280.463 | 444.2659 | 0 | 0 | 0 | 529.7014 | 0 | 0 | 0
transition 2 | 7 | 0.045 | 526.4209 | -1723.5791 | 2250 | 11.8445 | 22.4661 | 1723.5791 | 0.045 | 38.7805 | 304.004 | -2402.871 | 2706.875 | 0 | -2402.871 | 38.58% | 46.42% | 5831.6176 | 357.6518 | 19.1589 | 5625 | 5982.6518 | 151.0341 | 5982.6518 | 5831.6176 | 151.0341 | 11.8445 | 1.2518 | 20.4107 | 0 | 20.4107 | 0 | -38.7805 | 0.015708 | 526.4209 | 0 | 0 | 526.4209 | 304.004 | 0 | 0 | 304.004 | 526.4209 | 4211.3672 | 4211.3672 | 2250 | 628.7557 | 5030.0454 | 5030.0454 | 2706.875
transition 2 | 7.5 | 0.045 | 545.7633 | -1704.2367 | 2250 | 12.2797 | 22.8404 | 1704.2367 | 0.045 | 38.3453 | 394.89 | -2311.985 | 2706.875 | 0 | -2311.985 | 38.58% | 46.42% | 5831.6176 | 464.5765 | 18.7846 | 5625 | 6089.5765 | 257.9588 | 6089.5765 | 5831.6176 | 257.9588 | 12.2797 | 1.626 | 20.4107 | 0 | 20.4107 | 0 | -38.3453 | 0.026828 | 545.7633 | 0 | 0 | 545.7633 | 394.89 | 0 | 0 | 394.89 | 545.7633 | 4366.1064 | 4366.1064 | 2250 | 652.0768 | 5216.6145 | 5216.6145 | 2706.875
transition 2 | 8 | 0.045 | 628.4567 | -1621.5433 | 2250 | 14.1403 | 23.2215 | 1621.5433 | 0.045 | 36.4847 | 487.455 | -2219.42 | 2706.875 | 0 | -2219.42 | 38.58% | 46.42% | 5831.6176 | 573.4765 | 18.4035 | 5625 | 6198.4765 | 366.8588 | 6198.4765 | 5831.6176 | 366.8588 | 14.1403 | 2.0072 | 20.4107 | 0 | 20.4107 | 0 | -36.4847 | 0.038153 | 628.4567 | 0 | 0 | 628.4567 | 487.455 | 0 | 0 | 487.455 | 628.4567 | 5027.6538 | 5027.6538 | 2250 | 751.7803 | 6014.2422 | 6014.2422 | 2706.875
transition 2 | 8.5 | 0.045 | 708.2371 | -1541.7629 | 2250 | 15.9353 | 23.0965 | 1541.7629 | 0.045 | 34.6897 | 457.092 | -2249.783 | 2706.875 | 0 | -2249.783 | 38.58% | 46.42% | 5831.6176 | 537.7553 | 18.5285 | 5625 | 6162.7553 | 331.1376 | 6162.7553 | 5831.6176 | 331.1376 | 15.9353 | 1.8821 | 20.4107 | 0 | 20.4107 | 0 | -34.6897 | 0.034438 | 708.2371 | 0 | 0 | 708.2371 | 457.092 | 0 | 0 | 457.092 | 708.2371 | 5665.897 | 5665.897 | 2250 | 847.9715 | 6783.772 | 6783.772 | 2706.875
transition 2 | 9 | 0.045 | 777.8599 | -1472.1401 | 2250 | 17.5018 | 22.9405 | 1472.1401 | 0.045 | 33.1232 | 419.218 | -2287.657 | 2706.875 | 0 | -2287.657 | 38.58% | 46.42% | 5831.6176 | 493.1976 | 18.6845 | 5625 | 6118.1976 | 286.58 | 6118.1976 | 5831.6176 | 286.58 | 17.5018 | 1.7262 | 20.4107 | 0 | 20.4107 | 0 | -33.1232 | 0.029804 | 777.8599 | 0 | 0 | 777.8599 | 419.218 | 0 | 0 | 419.218 | 777.8599 | 6222.8794 | 6222.8794 | 2250 | 931.9157 | 7455.3257 | 7455.3257 | 2706.875
transition 2 | 9.5 | 0.045 | 779.8462 | -1470.1538 | 2250 | 17.5465 | 22.7803 | 1470.1538 | 0.045 | 33.0785 | 380.308 | -2326.567 | 2706.875 | 0 | -2326.567 | 38.58% | 46.42% | 5831.6176 | 447.4212 | 18.8447 | 5625 | 6072.4212 | 240.8035 | 6072.4212 | 5831.6176 | 240.8035 | 17.5465 | 1.566 | 20.4107 | 0 | 20.4107 | 0 | -33.0785 | 0.025044 | 779.8462 | 0 | 0 | 779.8462 | 380.308 | 0 | 0 | 380.308 | 779.8462 | 6238.7695 | 6238.7695 | 2250 | 934.3106 | 7474.4844 | 7474.4844 | 2706.875
transition 2 | 10 | 0.045 | 716.5833 | -1533.4167 | 2250 | 16.1231 | 22.5832 | 1533.4167 | 0.045 | 34.5019 | 332.432 | -2374.443 | 2706.875 | 0 | -2374.443 | 38.58% | 46.42% | 5831.6176 | 391.0965 | 19.0418 | 5625 | 6016.0965 | 184.4788 | 6016.0965 | 5831.6176 | 184.4788 | 16.1231 | 1.3688 | 20.4107 | 0 | 20.4107 | 0 | -34.5019 | 0.019186 | 716.5833 | 0 | 0 | 716.5833 | 332.432 | 0 | 0 | 332.432 | 716.5833 | 5732.666 | 5732.666 | 2250 | 858.0344 | 6864.2754 | 6864.2754 | 2706.875
transition 2 | 10.5 | 0.045 | 697.473 | -1552.527 | 2250 | 15.6931 | 22.6599 | 1552.527 | 0.045 | 34.9319 | 351.055 | -2355.82 | 2706.875 | 0 | -2355.82 | 38.58% | 46.42% | 5831.6176 | 413.0059 | 18.9651 | 5625 | 6038.0059 | 206.3882 | 6038.0059 | 5831.6176 | 206.3882 | 15.6931 | 1.4455 | 20.4107 | 0 | 20.4107 | 0 | -34.9319 | 0.021464 | 697.473 | 0 | 0 | 697.473 | 351.055 | 0 | 0 | 351.055 | 697.473 | 5579.7837 | 5579.7837 | 2250 | 834.9931 | 6679.9452 | 6679.9452 | 2706.875
transition 2 | 11 | 0.045 | 694.4325 | -1555.5675 | 2250 | 15.6247 | 22.8203 | 1555.5675 | 0.045 | 35.0003 | 390.009 | -2316.866 | 2706.875 | 0 | -2316.866 | 38.58% | 46.42% | 5831.6176 | 458.8341 | 18.8047 | 5625 | 6083.8341 | 252.2165 | 6083.8341 | 5831.6176 | 252.2165 | 15.6247 | 1.6059 | 20.4107 | 0 | 20.4107 | 0 | -35.0003 | 0.026231 | 694.4325 | 0 | 0 | 694.4325 | 390.009 | 0 | 0 | 390.009 | 694.4325 | 5555.46 | 5555.46 | 2250 | 831.3273 | 6650.6181 | 6650.6181 | 2706.875
transition 2 | 11.5 | 0.045 | 763.1429 | -1486.8571 | 2250 | 17.1707 | 22.9152 | 1486.8571 | 0.045 | 33.4543 | 413.07 | -2293.805 | 2706.875 | 0 | -2293.805 | 38.58% | 46.42% | 5831.6176 | 485.9647 | 18.7098 | 5625 | 6110.9647 | 279.3471 | 6110.9647 | 5831.6176 | 279.3471 | 17.1707 | 1.7009 | 20.4107 | 0 | 20.4107 | 0 | -33.4543 | 0.029052 | 763.1429 | 0 | 0 | 763.1429 | 413.07 | 0 | 0 | 413.07 | 763.1429 | 6105.1431 | 6105.1431 | 2250 | 914.1714 | 7313.371 | 7313.371 | 2706.875
transition 2 | 12 | 0.045 | 705.7344 | -1544.2656 | 2250 | 15.879 | 22.9043 | 1544.2656 | 0.045 | 34.746 | 410.416 | -2296.459 | 2706.875 | 0 | -2296.459 | 38.58% | 46.42% | 5831.6176 | 482.8424 | 18.7207 | 5625 | 6107.8424 | 276.2247 | 6107.8424 | 5831.6176 | 276.2247 | 15.879 | 1.6899 | 20.4107 | 0 | 20.4107 | 0 | -34.746 | 0.028727 | 705.7344 | 0 | 0 | 705.7344 | 410.416 | 0 | 0 | 410.416 | 705.7344 | 5645.875 | 5645.875 | 2250 | 844.9539 | 6759.6315 | 6759.6315 | 2706.875
transition 2 | 12.5 | 0.045 | 820.9035 | -1429.0965 | 2250 | 18.4703 | 22.695 | 1429.0965 | 0.045 | 32.1547 | 359.586 | -2347.289 | 2706.875 | 0 | -2347.289 | 38.58% | 46.42% | 5831.6176 | 423.0424 | 18.93 | 5625 | 6048.0424 | 216.4247 | 6048.0424 | 5831.6176 | 216.4247 | 18.4703 | 1.4806 | 20.4107 | 0 | 20.4107 | 0 | -32.1547 | 0.022508 | 820.9035 | 0 | 0 | 820.9035 | 359.586 | 0 | 0 | 359.586 | 820.9035 | 6567.228 | 6567.228 | 2250 | 983.8134 | 7870.5068 | 7870.5068 | 2706.875
transition 2 | 13 | 0.045 | 615.5449 | -1634.4551 | 2250 | 13.8498 | 22.4817 | 1634.4551 | 0.045 | 36.7752 | 307.797 | -2399.078 | 2706.875 | 0 | -2399.078 | 38.58% | 46.42% | 5831.6176 | 362.1141 | 19.1433 | 5625 | 5987.1141 | 155.4965 | 5987.1141 | 5831.6176 | 155.4965 | 13.8498 | 1.2674 | 20.4107 | 0 | 20.4107 | 0 | -36.7752 | 0.016172 | 615.5449 | 0 | 0 | 615.5449 | 307.797 | 0 | 0 | 307.797 | 615.5449 | 4924.3589 | 4924.3589 | 2250 | 736.2124 | 5889.6995 | 5889.6995 | 2706.875
transition 2 | 13.5 | 0.045 | 620.064 | -1629.936 | 2250 | 13.9514 | 22.5322 | 1629.936 | 0.045 | 36.6736 | 320.047 | -2386.828 | 2706.875 | 0 | -2386.828 | 38.58% | 46.42% | 5831.6176 | 376.5259 | 19.0928 | 5625 | 6001.5259 | 169.9082 | 6001.5259 | 5831.6176 | 169.9082 | 13.9514 | 1.3178 | 20.4107 | 0 | 20.4107 | 0 | -36.6736 | 0.01767 | 620.064 | 0 | 0 | 620.064 | 320.047 | 0 | 0 | 320.047 | 620.064 | 4960.5117 | 4960.5117 | 2250 | 741.6611 | 5933.289 | 5933.289 | 2706.875
transition 2 | 14 | 0.045 | 673.1365 | -1576.8635 | 2250 | 15.1456 | 22.5894 | 1576.8635 | 0.045 | 35.4794 | 333.932 | -2372.943 | 2706.875 | 0 | -2372.943 | 38.58% | 46.42% | 5831.6176 | 392.8612 | 19.0356 | 5625 | 6017.8612 | 186.2435 | 6017.8612 | 5831.6176 | 186.2435 | 15.1456 | 1.375 | 20.4107 | 0 | 20.4107 | 0 | -35.4794 | 0.019369 | 673.1365 | 0 | 0 | 673.1365 | 333.932 | 0 | 0 | 333.932 | 673.1365 | 5385.0923 | 5385.0923 | 2250 | 805.6507 | 6445.2058 | 6445.2058 | 2706.875
transition 2 | 14.5 | 0.045 | 726.3488 | -1523.6512 | 2250 | 16.3428 | 22.4083 | 1523.6512 | 0.045 | 34.2822 | 289.954 | -2416.921 | 2706.875 | 0 | -2416.921 | 38.58% | 46.42% | 5831.6176 | 341.1224 | 19.2167 | 5625 | 5966.1224 | 134.5047 | 5966.1224 | 5831.6176 | 134.5047 | 16.3428 | 1.1939 | 20.4107 | 0 | 20.4107 | 0 | -34.2822 | 0.013988 | 726.3488 | 0 | 0 | 726.3488 | 289.954 | 0 | 0 | 289.954 | 726.3488 | 5810.7905 | 5810.7905 | 2250 | 869.8088 | 6958.4701 | 6958.4701 | 2706.875
transition 2 | 15 | 0.045 | 673.8981 | -1576.1019 | 2250 | 15.1627 | 22.3242 | 1576.1019 | 0.045 | 35.4623 | 269.547 | -2437.328 | 2706.875 | 0 | -2437.328 | 38.58% | 46.42% | 5831.6176 | 317.1141 | 19.3008 | 5625 | 5942.1141 | 110.4965 | 5942.1141 | 5831.6176 | 110.4965 | 15.1627 | 1.1099 | 20.4107 | 0 | 20.4107 | 0 | -35.4623 | 0.011492 | 673.8981 | 0 | 0 | 673.8981 | 269.547 | 0 | 0 | 269.547 | 673.8981 | 5391.1846 | 5391.1846 | 2250 | 806.5689 | 6452.5512 | 6452.5512 | 2706.875
transition 2 | 15.5 | 0.045 | 673.9579 | -1576.0421 | 2250 | 15.1641 | 22.4966 | 1576.0421 | 0.045 | 35.4609 | 311.411 | -2395.464 | 2706.875 | 0 | -2395.464 | 38.58% | 46.42% | 5831.6176 | 366.3659 | 19.1284 | 5625 | 5991.3659 | 159.7482 | 5991.3659 | 5831.6176 | 159.7482 | 15.1641 | 1.2823 | 20.4107 | 0 | 20.4107 | 0 | -35.4609 | 0.016614 | 673.9579 | 0 | 0 | 673.9579 | 311.411 | 0 | 0 | 311.411 | 673.9579 | 5391.6631 | 5391.6631 | 2250 | 806.641 | 6453.1282 | 6453.1282 | 2706.875
transition 2 | 16 | 0.045 | 862.5224 | -1387.4776 | 2250 | 19.4068 | 22.7554 | 1387.4776 | 0.045 | 31.2182 | 374.266 | -2332.609 | 2706.875 | 0 | -2332.609 | 38.58% | 46.42% | 5831.6176 | 440.3129 | 18.8696 | 5625 | 6065.3129 | 233.6953 | 6065.3129 | 5831.6176 | 233.6953 | 19.4068 | 1.5411 | 20.4107 | 0 | 20.4107 | 0 | -31.2182 | 0.024304 | 862.5224 | 0 | 0 | 862.5224 | 374.266 | 0 | 0 | 374.266 | 862.5224 | 6900.1792 | 6900.1792 | 2250 | 1033.9933 | 8271.9461 | 8271.9461 | 2706.875
transition 2 | 16.5 | 0.045 | 715.4089 | -1534.5911 | 2250 | 16.0967 | 23.2067 | 1534.5911 | 0.045 | 34.5283 | 483.857 | -2223.018 | 2706.875 | 0 | -2223.018 | 38.58% | 46.42% | 5831.6176 | 569.2435 | 18.4183 | 5625 | 6194.2435 | 362.6259 | 6194.2435 | 5831.6176 | 362.6259 | 16.0967 | 1.9924 | 20.4107 | 0 | 20.4107 | 0 | -34.5283 | 0.037713 | 715.4089 | 0 | 0 | 715.4089 | 483.857 | 0 | 0 | 483.857 | 715.4089 | 5723.2715 | 5723.2715 | 2250 | 856.6186 | 6852.9484 | 6852.9484 | 2706.875
transition 2 | 17 | 0.045 | 740.0322 | -1509.9678 | 2250 | 16.6507 | 23.413 | 1509.9678 | 0.045 | 33.9743 | 533.952 | -2172.923 | 2706.875 | 0 | -2172.923 | 38.58% | 46.42% | 5831.6176 | 628.1788 | 18.212 | 5625 | 6253.1788 | 421.5612 | 6253.1788 | 5831.6176 | 421.5612 | 16.6507 | 2.1986 | 20.4107 | 0 | 20.4107 | 0 | -33.9743 | 0.043842 | 740.0322 | 0 | 0 | 740.0322 | 533.952 | 0 | 0 | 533.952 | 740.0322 | 5920.2573 | 5920.2573 | 2250 | 886.3068 | 7090.4543 | 7090.4543 | 2706.875
transition 2 | 17.5 | 0.045 | 739.3088 | -1510.6912 | 2250 | 16.6344 | 22.7774 | 1510.6912 | 0.045 | 33.9906 | 379.611 | -2327.264 | 2706.875 | 0 | -2327.264 | 38.58% | 46.42% | 5831.6176 | 446.6012 | 18.8476 | 5625 | 6071.6012 | 239.9835 | 6071.6012 | 5831.6176 | 239.9835 | 16.6344 | 1.5631 | 20.4107 | 0 | 20.4107 | 0 | -33.9906 | 0.024958 | 739.3088 | 0 | 0 | 739.3088 | 379.611 | 0 | 0 | 379.611 | 739.3088 | 5914.4707 | 5914.4707 | 2250 | 885.4347 | 7083.4773 | 7083.4773 | 2706.875
transition 2 | 18 | 0.045 | 721.2899 | -1528.7101 | 2250 | 16.229 | 22.1974 | 1528.7101 | 0.045 | 34.396 | 238.742 | -2468.133 | 2706.875 | 0 | -2468.133 | 38.58% | 46.42% | 5831.6176 | 280.8729 | 19.4276 | 5625 | 5905.8729 | 74.2553 | 5905.8729 | 5831.6176 | 74.2553 | 16.229 | 0.98306 | 20.4107 | 0 | 20.4107 | 0 | -34.396 | 0.0077226 | 721.2899 | 0 | 0 | 721.2899 | 238.742 | 0 | 0 | 238.742 | 721.2899 | 5770.3193 | 5770.3193 | 2250 | 863.7093 | 6909.674 | 6909.674 | 2706.875
transition 2 | 18.5 | 0.045 | 663.8378 | -1586.1622 | 2250 | 14.9364 | 22.2683 | 1586.1622 | 0.045 | 35.6886 | 255.97 | -2450.905 | 2706.875 | 0 | -2450.905 | 38.58% | 46.42% | 5831.6176 | 301.1412 | 19.3567 | 5625 | 5926.1412 | 94.5235 | 5926.1412 | 5831.6176 | 94.5235 | 14.9364 | 1.054 | 20.4107 | 0 | 20.4107 | 0 | -35.6886 | 0.0098304 | 663.8378 | 0 | 0 | 663.8378 | 255.97 | 0 | 0 | 255.97 | 663.8378 | 5310.7026 | 5310.7026 | 2250 | 794.4393 | 6355.5142 | 6355.5142 | 2706.875
transition 2 | 19 | 0.045 | 642.6712 | -1607.3288 | 2250 | 14.4601 | 22.3672 | 1607.3288 | 0.045 | 36.1649 | 279.983 | -2426.892 | 2706.875 | 0 | -2426.892 | 38.58% | 46.42% | 5831.6176 | 329.3918 | 19.2578 | 5625 | 5954.3918 | 122.7741 | 5954.3918 | 5831.6176 | 122.7741 | 14.4601 | 1.1529 | 20.4107 | 0 | 20.4107 | 0 | -36.1649 | 0.012769 | 642.6712 | 0 | 0 | 642.6712 | 279.983 | 0 | 0 | 279.983 | 642.6712 | 5141.3696 | 5141.3696 | 2250 | 768.9187 | 6151.3494 | 6151.3494 | 2706.875
transition 2 | 19.5 | 0.045 | 618.585 | -1631.415 | 2250 | 13.9182 | 22.3671 | 1631.415 | 0.045 | 36.7068 | 279.946 | -2426.929 | 2706.875 | 0 | -2426.929 | 38.58% | 46.42% | 5831.6176 | 329.3482 | 19.2579 | 5625 | 5954.3482 | 122.7306 | 5954.3482 | 5831.6176 | 122.7306 | 13.9182 | 1.1527 | 20.4107 | 0 | 20.4107 | 0 | -36.7068 | 0.012764 | 618.585 | 0 | 0 | 618.585 | 279.946 | 0 | 0 | 279.946 | 618.585 | 4948.6797 | 4948.6797 | 2250 | 739.8779 | 5919.0231 | 5919.0231 | 2706.875
transition 2 | 20 | 0.045 | 574.6714 | -1675.3286 | 2250 | 12.9301 | 22.3543 | 1675.3286 | 0.045 | 37.6949 | 276.842 | -2430.033 | 2706.875 | 0 | -2430.033 | 38.58% | 46.42% | 5831.6176 | 325.6965 | 19.2707 | 5625 | 5950.6965 | 119.0788 | 5950.6965 | 5831.6176 | 119.0788 | 12.9301 | 1.1399 | 20.4107 | 0 | 20.4107 | 0 | -37.6949 | 0.012384 | 574.6714 | 0 | 0 | 574.6714 | 276.842 | 0 | 0 | 276.842 | 574.6714 | 4597.3716 | 4597.3716 | 2250 | 686.9314 | 5495.4509 | 5495.4509 | 2706.875
transition 2 | 20.5 | 0.045 | 594.8419 | -1655.1581 | 2250 | 13.3839 | 22.4283 | 1655.1581 | 0.045 | 37.2411 | 294.827 | -2412.048 | 2706.875 | 0 | -2412.048 | 38.58% | 46.42% | 5831.6176 | 346.8553 | 19.1967 | 5625 | 5971.8553 | 140.2376 | 5971.8553 | 5831.6176 | 140.2376 | 13.3839 | 1.214 | 20.4107 | 0 | 20.4107 | 0 | -37.2411 | 0.014585 | 594.8419 | 0 | 0 | 594.8419 | 294.827 | 0 | 0 | 294.827 | 594.8419 | 4758.7349 | 4758.7349 | 2250 | 711.2508 | 5690.0066 | 5690.0066 | 2706.875
transition 2 | 21 | 0.045 | 666.2289 | -1583.7711 | 2250 | 14.9902 | 22.5115 | 1583.7711 | 0.045 | 35.6348 | 315.017 | -2391.858 | 2706.875 | 0 | -2391.858 | 38.58% | 46.42% | 5831.6176 | 370.6082 | 19.1135 | 5625 | 5995.6082 | 163.9906 | 5995.6082 | 5831.6176 | 163.9906 | 14.9902 | 1.2971 | 20.4107 | 0 | 20.4107 | 0 | -35.6348 | 0.017055 | 666.2289 | 0 | 0 | 666.2289 | 315.017 | 0 | 0 | 315.017 | 666.2289 | 5329.8315 | 5329.8315 | 2250 | 797.3222 | 6378.5779 | 6378.5779 | 2706.875
transition 2 | 21.5 | 0.045 | 679.53 | -1570.47 | 2250 | 15.2894 | 22.6689 | 1570.47 | 0.045 | 35.3356 | 353.244 | -2353.631 | 2706.875 | 0 | -2353.631 | 38.58% | 46.42% | 5831.6176 | 415.5812 | 18.9561 | 5625 | 6040.5812 | 208.9635 | 6040.5812 | 5831.6176 | 208.9635 | 15.2894 | 1.4545 | 20.4107 | 0 | 20.4107 | 0 | -35.3356 | 0.021732 | 679.53 | 0 | 0 | 679.53 | 353.244 | 0 | 0 | 353.244 | 679.53 | 5436.2402 | 5436.2402 | 2250 | 813.3594 | 6506.8749 | 6506.8749 | 2706.875
transition 2 | 22 | 0.045 | 608.1024 | -1641.8976 | 2250 | 13.6823 | 22.6569 | 1641.8976 | 0.045 | 36.9427 | 350.335 | -2356.54 | 2706.875 | 0 | -2356.54 | 38.58% | 46.42% | 5831.6176 | 412.1588 | 18.9681 | 5625 | 6037.1588 | 205.5412 | 6037.1588 | 5831.6176 | 205.5412 | 13.6823 | 1.4426 | 20.4107 | 0 | 20.4107 | 0 | -36.9427 | 0.021376 | 608.1024 | 0 | 0 | 608.1024 | 350.335 | 0 | 0 | 350.335 | 608.1024 | 4864.8193 | 4864.8193 | 2250 | 727.2391 | 5817.9127 | 5817.9127 | 2706.875
transition 2 | 22.5 | 0.045 | 548.0778 | -1701.9222 | 2250 | 12.3317 | 22.3803 | 1701.9222 | 0.045 | 38.2933 | 283.154 | -2423.721 | 2706.875 | 0 | -2423.721 | 38.58% | 46.42% | 5831.6176 | 333.1224 | 19.2447 | 5625 | 5958.1224 | 126.5047 | 5958.1224 | 5831.6176 | 126.5047 | 12.3317 | 1.1659 | 20.4107 | 0 | 20.4107 | 0 | -38.2933 | 0.013156 | 548.0778 | 0 | 0 | 548.0778 | 283.154 | 0 | 0 | 283.154 | 548.0778 | 4384.6221 | 4384.6221 | 2250 | 654.8674 | 5238.9388 | 5238.9388 | 2706.875
transition 2 | 23 | 0.045 | 482.4266 | -1767.5734 | 2250 | 10.8546 | 22.1778 | 1767.5734 | 0.045 | 39.7704 | 233.982 | -2472.893 | 2706.875 | 0 | -2472.893 | 38.58% | 46.42% | 5831.6176 | 275.2729 | 19.4472 | 5625 | 5900.2729 | 68.6553 | 5900.2729 | 5831.6176 | 68.6553 | 10.8546 | 0.96346 | 20.4107 | 0 | 20.4107 | 0 | -39.7704 | 0.0071402 | 482.4266 | 0 | 0 | 482.4266 | 233.982 | 0 | 0 | 233.982 | 482.4266 | 3859.4128 | 3859.4128 | 2250 | 575.7118 | 4605.6941 | 4605.6941 | 2706.875
transition 2 | 23.5 | 0.045 | 442.7622 | -1807.2378 | 2250 | 9.9621 | 22.0574 | 1807.2378 | 0.045 | 40.6629 | 204.736 | -2502.139 | 2706.875 | 0 | -2502.139 | 38.58% | 46.42% | 5831.6176 | 240.8659 | 19.5676 | 5625 | 5865.8659 | 34.2482 | 5865.8659 | 5831.6176 | 34.2482 | 9.9621 | 0.84303 | 20.4107 | 0 | 20.4107 | 0 | -40.6629 | 0.0035618 | 442.7622 | 0 | 0 | 442.7622 | 204.736 | 0 | 0 | 204.736 | 442.7622 | 3542.0977 | 3542.0977 | 2250 | 527.8884 | 4223.1071 | 4223.1071 | 2706.875
summer | 0 | 0.015 | 494.568 | 494.568 | 0 | 0 | 0 | 0 | 0.015 | 0 | 179.291 | 179.291 | 0 | 179.291 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1447.3506 | 1447.3506 | 0 | 3.7093 | 0.73826 | 0 | 0.73826 | 0.73826 | 3.7093 | 3.7093 | 0 | 494.568 | 0 | 0 | 494.568 | 179.291 | 0 | 0 | 179.291 | 494.568 | 0 | 0 | 0 | 590.3507 | 0 | 0 | 0
summer | 0.5 | 0.015 | 426.4431 | 426.4431 | 0 | 0 | 0 | 0 | 0.015 | 0 | 144.992 | 144.992 | 0 | 144.992 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1236.6866 | 1236.6866 | 0 | 3.1983 | 0.59703 | 0 | 0.59703 | 0.59703 | 3.1983 | 3.1983 | 0 | 426.4431 | 0 | 0 | 426.4431 | 144.992 | 0 | 0 | 144.992 | 426.4431 | 0 | 0 | 0 | 508.2125 | 0 | 0 | 0
summer | 1 | 0.015 | 427.6698 | 427.6698 | 0 | 0 | 0 | 0 | 0.015 | 0 | 128.934 | 128.934 | 0 | 128.934 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1220.8615 | 1220.8615 | 0 | 3.2075 | 0.5309 | 0 | 0.5309 | 0.5309 | 3.2075 | 3.2075 | 0 | 427.6698 | 0 | 0 | 427.6698 | 128.934 | 0 | 0 | 128.934 | 427.6698 | 0 | 0 | 0 | 509.6914 | 0 | 0 | 0
summer | 1.5 | 0.015 | 358.176 | 358.176 | 0 | 0 | 0 | 0 | 0.015 | 0 | 121.242 | 121.242 | 0 | 121.242 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1038.0776 | 1038.0776 | 0 | 2.6863 | 0.49923 | 0 | 0.49923 | 0.49923 | 2.6863 | 2.6863 | 0 | 358.176 | 0 | 0 | 358.176 | 121.242 | 0 | 0 | 121.242 | 358.176 | 0 | 0 | 0 | 425.9028 | 0 | 0 | 0
summer | 2 | 0.015 | 353.2493 | 353.2493 | 0 | 0 | 0 | 0 | 0.015 | 0 | 112.493 | 112.493 | 0 | 112.493 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1015.468 | 1015.468 | 0 | 2.6494 | 0.46321 | 0 | 0.46321 | 0.46321 | 2.6494 | 2.6494 | 0 | 353.2493 | 0 | 0 | 353.2493 | 112.493 | 0 | 0 | 112.493 | 353.2493 | 0 | 0 | 0 | 419.9627 | 0 | 0 | 0
summer | 2.5 | 0.015 | 324.8823 | 324.8823 | 0 | 0 | 0 | 0 | 0.015 | 0 | 108.384 | 108.384 | 0 | 108.384 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 939.7162 | 939.7162 | 0 | 2.4366 | 0.44629 | 0 | 0.44629 | 0.44629 | 2.4366 | 2.4366 | 0 | 324.8823 | 0 | 0 | 324.8823 | 108.384 | 0 | 0 | 108.384 | 324.8823 | 0 | 0 | 0 | 385.7605 | 0 | 0 | 0
summer | 3 | 0.015 | 305.5898 | 305.5898 | 0 | 0 | 0 | 0 | 0.015 | 0 | 107.065 | 107.065 | 0 | 107.065 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 889.9333 | 889.9333 | 0 | 2.2919 | 0.44086 | 0 | 0.44086 | 0.44086 | 2.2919 | 2.2919 | 0 | 305.5898 | 0 | 0 | 305.5898 | 107.065 | 0 | 0 | 107.065 | 305.5898 | 0 | 0 | 0 | 362.4996 | 0 | 0 | 0
summer | 3.5 | 0.015 | 365.4618 | 365.4618 | 0 | 0 | 0 | 0 | 0.015 | 0 | 269.15 | 269.15 | 0 | 269.15 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1230.3015 | 1230.3015 | 0 | 2.741 | 1.1083 | 0 | 1.1083 | 1.1083 | 2.741 | 2.741 | 0 | 365.4618 | 0 | 0 | 365.4618 | 269.15 | 0 | 0 | 269.15 | 365.4618 | 0 | 0 | 0 | 434.6872 | 0 | 0 | 0
summer | 4 | 0.015 | 331.1358 | 331.1358 | 0 | 0 | 0 | 0 | 0.015 | 0 | 431.325 | 431.325 | 0 | 431.325 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1335.2808 | 1335.2808 | 0 | 2.4835 | 1.776 | 0 | 1.776 | 1.776 | 2.4835 | 2.4835 | 0 | 331.1358 | 0 | 0 | 331.1358 | 431.325 | 0 | 0 | 431.325 | 331.1358 | 0 | 0 | 0 | 393.3005 | 0 | 0 | 0
summer | 4.5 | 0.015 | 337.4177 | 337.4177 | 0 | 0 | 0 | 0 | 0.015 | 0 | 432.54 | 432.54 | 0 | 432.54 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1352.4149 | 1352.4149 | 0 | 2.5306 | 1.781 | 0 | 1.781 | 1.781 | 2.5306 | 2.5306 | 0 | 337.4177 | 0 | 0 | 337.4177 | 432.54 | 0 | 0 | 432.54 | 337.4177 | 0 | 0 | 0 | 400.8746 | 0 | 0 | 0
summer | 5 | 0.015 | 333.3169 | 333.3169 | 0 | 0 | 0 | 0 | 0.015 | 0 | 443.26 | 443.26 | 0 | 443.26 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1354.7745 | 1354.7745 | 0 | 2.4999 | 1.8252 | 0 | 1.8252 | 1.8252 | 2.4999 | 2.4999 | 0 | 333.3169 | 0 | 0 | 333.3169 | 443.26 | 0 | 0 | 443.26 | 333.3169 | 0 | 0 | 0 | 395.9301 | 0 | 0 | 0
summer | 5.5 | 0.015 | 340.8905 | 340.8905 | 0 | 0 | 0 | 0 | 0.015 | 0 | 464.417 | 464.417 | 0 | 464.417 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1398.5992 | 1398.5992 | 0 | 2.5567 | 1.9123 | 0 | 1.9123 | 1.9123 | 2.5567 | 2.5567 | 0 | 340.8905 | 0 | 0 | 340.8905 | 464.417 | 0 | 0 | 464.417 | 340.8905 | 0 | 0 | 0 | 405.0617 | 0 | 0 | 0
summer | 6 | 0.015 | 385.5162 | 385.5162 | 0 | 0 | 0 | 0 | 0.015 | 0 | 503.904 | 503.904 | 0 | 503.904 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1556.6187 | 1556.6187 | 0 | 2.8914 | 2.0749 | 0 | 2.0749 | 2.0749 | 2.8914 | 2.8914 | 0 | 385.5162 | 0 | 0 | 385.5162 | 503.904 | 0 | 0 | 503.904 | 385.5162 | 0 | 0 | 0 | 458.8669 | 0 | 0 | 0
summer | 6.5 | 0.015 | 384.2984 | 384.2984 | 0 | 0 | 0 | 0 | 0.015 | 0 | 569.668 | 569.668 | 0 | 569.668 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1630.9436 | 1630.9436 | 0 | 2.8822 | 2.3457 | 0 | 2.3457 | 2.3457 | 2.8822 | 2.8822 | 0 | 384.2984 | 0 | 0 | 384.2984 | 569.668 | 0 | 0 | 569.668 | 384.2984 | 0 | 0 | 0 | 457.3986 | 0 | 0 | 0
summer | 7 | 0.045 | 432.2341 | -1817.7659 | 2250 | 9.7253 | 23.8024 | 1817.7659 | 0.045 | 40.8997 | 628.526 | -2078.349 | 2706.875 | 0 | -2078.349 | 38.58% | 46.42% | 5831.6176 | 739.4424 | 17.8226 | 5625 | 6364.4424 | 532.8247 | 6364.4424 | 5831.6176 | 532.8247 | 9.7253 | 2.588 | 20.4107 | 0 | 20.4107 | 0 | -40.8997 | 0.055414 | 432.2341 | 0 | 0 | 432.2341 | 628.526 | 0 | 0 | 628.526 | 432.2341 | 3457.8728 | 3457.8728 | 2250 | 515.1947 | 4121.5572 | 4121.5572 | 2706.875
summer | 7.5 | 0.045 | 512.7245 | -1737.2755 | 2250 | 11.5363 | 23.8244 | 1737.2755 | 0.045 | 39.0887 | 633.879 | -2072.996 | 2706.875 | 0 | -2072.996 | 38.58% | 46.42% | 5831.6176 | 745.74 | 17.8006 | 5625 | 6370.74 | 539.1224 | 6370.74 | 5831.6176 | 539.1224 | 11.5363 | 2.6101 | 20.4107 | 0 | 20.4107 | 0 | -39.0887 | 0.056069 | 512.7245 | 0 | 0 | 512.7245 | 633.879 | 0 | 0 | 633.879 | 512.7245 | 4101.7964 | 4101.7964 | 2250 | 612.242 | 4897.9359 | 4897.9359 | 2706.875
summer | 8 | 0.045 | 493.4192 | -1756.5808 | 2250 | 11.1019 | 23.7158 | 1756.5808 | 0.045 | 39.5231 | 607.505 | -2099.37 | 2706.875 | 0 | -2099.37 | 38.58% | 46.42% | 5831.6176 | 714.7118 | 17.9092 | 5625 | 6339.7118 | 508.0941 | 6339.7118 | 5831.6176 | 508.0941 | 11.1019 | 2.5015 | 20.4107 | 0 | 20.4107 | 0 | -39.5231 | 0.052842 | 493.4192 | 0 | 0 | 493.4192 | 607.505 | 0 | 0 | 607.505 | 493.4192 | 3947.3533 | 3947.3533 | 2250 | 588.9655 | 4711.7238 | 4711.7238 | 2706.875
summer | 8.5 | 0.045 | 532.6486 | -1717.3514 | 2250 | 11.9846 | 23.51 | 1717.3514 | 0.045 | 38.6404 | 557.515 | -2149.36 | 2706.875 | 0 | -2149.36 | 38.58% | 46.42% | 5831.6176 | 655.9 | 18.115 | 5625 | 6280.9 | 449.2824 | 6280.9 | 5831.6176 | 449.2824 | 11.9846 | 2.2957 | 20.4107 | 0 | 20.4107 | 0 | -38.6404 | 0.046725 | 532.6486 | 0 | 0 | 532.6486 | 557.515 | 0 | 0 | 557.515 | 532.6486 | 4261.1885 | 4261.1885 | 2250 | 636.2644 | 5090.1149 | 5090.1149 | 2706.875
summer | 9 | 0.045 | 526.9628 | -1723.0372 | 2250 | 11.8567 | 23.3871 | 1723.0372 | 0.045 | 38.7683 | 527.662 | -2179.213 | 2706.875 | 0 | -2179.213 | 38.58% | 46.42% | 5831.6176 | 620.7788 | 18.2379 | 5625 | 6245.7788 | 414.1612 | 6245.7788 | 5831.6176 | 414.1612 | 11.8567 | 2.1727 | 20.4107 | 0 | 20.4107 | 0 | -38.7683 | 0.043073 | 526.9628 | 0 | 0 | 526.9628 | 527.662 | 0 | 0 | 527.662 | 526.9628 | 4215.7026 | 4215.7026 | 2250 | 629.4091 | 5035.2727 | 5035.2727 | 2706.875
summer | 9.5 | 0.045 | 578.7302 | -1671.2698 | 2250 | 13.0214 | 23.3313 | 1671.2698 | 0.045 | 37.6036 | 514.13 | -2192.745 | 2706.875 | 0 | -2192.745 | 38.58% | 46.42% | 5831.6176 | 604.8588 | 18.2937 | 5625 | 6229.8588 | 398.2412 | 6229.8588 | 5831.6176 | 398.2412 | 13.0214 | 2.117 | 20.4107 | 0 | 20.4107 | 0 | -37.6036 | 0.041417 | 578.7302 | 0 | 0 | 578.7302 | 514.13 | 0 | 0 | 514.13 | 578.7302 | 4629.8418 | 4629.8418 | 2250 | 691.825 | 5534.6003 | 5534.6003 | 2706.875
summer | 10 | 0.045 | 654.0448 | -1595.9552 | 2250 | 14.716 | 23.2339 | 1595.9552 | 0.045 | 35.909 | 490.454 | -2216.421 | 2706.875 | 0 | -2216.421 | 38.58% | 46.42% | 5831.6176 | 577.0047 | 18.3911 | 5625 | 6202.0047 | 370.3871 | 6202.0047 | 5831.6176 | 370.3871 | 14.716 | 2.0195 | 20.4107 | 0 | 20.4107 | 0 | -35.909 | 0.03852 | 654.0448 | 0 | 0 | 654.0448 | 490.454 | 0 | 0 | 490.454 | 654.0448 | 5232.3584 | 5232.3584 | 2250 | 782.6318 | 6261.0545 | 6261.0545 | 2706.875
summer | 10.5 | 0.045 | 653.1376 | -1596.8624 | 2250 | 14.6956 | 23.1746 | 1596.8624 | 0.045 | 35.9294 | 476.067 | -2230.808 | 2706.875 | 0 | -2230.808 | 38.58% | 46.42% | 5831.6176 | 560.0788 | 18.4504 | 5625 | 6185.0788 | 353.4612 | 6185.0788 | 5831.6176 | 353.4612 | 14.6956 | 1.9603 | 20.4107 | 0 | 20.4107 | 0 | -35.9294 | 0.03676 | 653.1376 | 0 | 0 | 653.1376 | 476.067 | 0 | 0 | 476.067 | 653.1376 | 5225.1006 | 5225.1006 | 2250 | 781.538 | 6252.3038 | 6252.3038 | 2706.875
summer | 11 | 0.045 | 681.4976 | -1568.5024 | 2250 | 15.3337 | 23.1696 | 1568.5024 | 0.045 | 35.2913 | 474.845 | -2232.03 | 2706.875 | 0 | -2232.03 | 38.58% | 46.42% | 5831.6176 | 558.6412 | 18.4554 | 5625 | 6183.6412 | 352.0235 | 6183.6412 | 5831.6176 | 352.0235 | 15.3337 | 1.9552 | 20.4107 | 0 | 20.4107 | 0 | -35.2913 | 0.03661 | 681.4976 | 0 | 0 | 681.4976 | 474.845 | 0 | 0 | 474.845 | 681.4976 | 5451.9805 | 5451.9805 | 2250 | 815.7316 | 6525.8529 | 6525.8529 | 2706.875
summer | 11.5 | 0.045 | 727.585 | -1522.415 | 2250 | 16.3707 | 23.1384 | 1522.415 | 0.045 | 34.2543 | 467.273 | -2239.602 | 2706.875 | 0 | -2239.602 | 38.58% | 46.42% | 5831.6176 | 549.7329 | 18.4866 | 5625 | 6174.7329 | 343.1153 | 6174.7329 | 5831.6176 | 343.1153 | 16.3707 | 1.9241 | 20.4107 | 0 | 20.4107 | 0 | -34.2543 | 0.035684 | 727.585 | 0 | 0 | 727.585 | 467.273 | 0 | 0 | 467.273 | 727.585 | 5820.6802 | 5820.6802 | 2250 | 871.2993 | 6970.3941 | 6970.3941 | 2706.875
summer | 12 | 0.045 | 739.14 | -1510.86 | 2250 | 16.6307 | 23.0445 | 1510.86 | 0.045 | 33.9943 | 444.475 | -2262.4 | 2706.875 | 0 | -2262.4 | 38.58% | 46.42% | 5831.6176 | 522.9118 | 18.5805 | 5625 | 6147.9118 | 316.2941 | 6147.9118 | 5831.6176 | 316.2941 | 16.6307 | 1.8302 | 20.4107 | 0 | 20.4107 | 0 | -33.9943 | 0.032895 | 739.14 | 0 | 0 | 739.14 | 444.475 | 0 | 0 | 444.475 | 739.14 | 5913.1201 | 5913.1201 | 2250 | 885.2311 | 7081.8489 | 7081.8489 | 2706.875
summer | 12.5 | 0.045 | 751.5535 | -1498.4465 | 2250 | 16.91 | 22.9358 | 1498.4465 | 0.045 | 33.715 | 418.071 | -2288.804 | 2706.875 | 0 | -2288.804 | 38.58% | 46.42% | 5831.6176 | 491.8482 | 18.6892 | 5625 | 6116.8482 | 285.2306 | 6116.8482 | 5831.6176 | 285.2306 | 16.91 | 1.7215 | 20.4107 | 0 | 20.4107 | 0 | -33.715 | 0.029664 | 751.5535 | 0 | 0 | 751.5535 | 418.071 | 0 | 0 | 418.071 | 751.5535 | 6012.4277 | 6012.4277 | 2250 | 900.198 | 7201.5841 | 7201.5841 | 2706.875
summer | 13 | 0.045 | 686.9969 | -1563.0031 | 2250 | 15.4574 | 22.8034 | 1563.0031 | 0.045 | 35.1676 | 385.908 | -2320.967 | 2706.875 | 0 | -2320.967 | 38.58% | 46.42% | 5831.6176 | 454.0094 | 18.8216 | 5625 | 6079.0094 | 247.3918 | 6079.0094 | 5831.6176 | 247.3918 | 15.4574 | 1.589 | 20.4107 | 0 | 20.4107 | 0 | -35.1676 | 0.025729 | 686.9969 | 0 | 0 | 686.9969 | 385.908 | 0 | 0 | 385.908 | 686.9969 | 5495.9756 | 5495.9756 | 2250 | 822.3622 | 6578.8978 | 6578.8978 | 2706.875
summer | 13.5 | 0.045 | 607.8934 | -1642.1066 | 2250 | 13.6776 | 22.7796 | 1642.1066 | 0.045 | 36.9474 | 380.128 | -2326.747 | 2706.875 | 0 | -2326.747 | 38.58% | 46.42% | 5831.6176 | 447.2094 | 18.8454 | 5625 | 6072.2094 | 240.5918 | 6072.2094 | 5831.6176 | 240.5918 | 13.6776 | 1.5652 | 20.4107 | 0 | 20.4107 | 0 | -36.9474 | 0.025022 | 607.8934 | 0 | 0 | 607.8934 | 380.128 | 0 | 0 | 380.128 | 607.8934 | 4863.147 | 4863.147 | 2250 | 726.987 | 5815.8963 | 5815.8963 | 2706.875
summer | 14 | 0.045 | 620.34 | -1629.66 | 2250 | 13.9576 | 22.7891 | 1629.66 | 0.045 | 36.6674 | 382.452 | -2324.423 | 2706.875 | 0 | -2324.423 | 38.58% | 46.42% | 5831.6176 | 449.9435 | 18.8359 | 5625 | 6074.9435 | 243.3259 | 6074.9435 | 5831.6176 | 243.3259 | 13.9576 | 1.5748 | 20.4107 | 0 | 20.4107 | 0 | -36.6674 | 0.025306 | 620.34 | 0 | 0 | 620.34 | 382.452 | 0 | 0 | 382.452 | 620.34 | 4962.7197 | 4962.7197 | 2250 | 741.9939 | 5935.9512 | 5935.9512 | 2706.875
summer | 14.5 | 0.045 | 596.0881 | -1653.9119 | 2250 | 13.412 | 22.8156 | 1653.9119 | 0.045 | 37.213 | 388.885 | -2317.99 | 2706.875 | 0 | -2317.99 | 38.58% | 46.42% | 5831.6176 | 457.5118 | 18.8094 | 5625 | 6082.5118 | 250.8941 | 6082.5118 | 5831.6176 | 250.8941 | 13.412 | 1.6013 | 20.4107 | 0 | 20.4107 | 0 | -37.213 | 0.026093 | 596.0881 | 0 | 0 | 596.0881 | 388.885 | 0 | 0 | 388.885 | 596.0881 | 4768.7051 | 4768.7051 | 2250 | 712.7535 | 5702.0277 | 5702.0277 | 2706.875
summer | 15 | 0.045 | 613.2395 | -1636.7605 | 2250 | 13.7979 | 22.8935 | 1636.7605 | 0.045 | 36.8271 | 407.785 | -2299.09 | 2706.875 | 0 | -2299.09 | 38.58% | 46.42% | 5831.6176 | 479.7471 | 18.7315 | 5625 | 6104.7471 | 273.1294 | 6104.7471 | 5831.6176 | 273.1294 | 13.7979 | 1.6791 | 20.4107 | 0 | 20.4107 | 0 | -36.8271 | 0.028405 | 613.2395 | 0 | 0 | 613.2395 | 407.785 | 0 | 0 | 407.785 | 613.2395 | 4905.916 | 4905.916 | 2250 | 733.4329 | 5867.4629 | 5867.4629 | 2706.875
summer | 15.5 | 0.045 | 583.3041 | -1666.6959 | 2250 | 13.1243 | 23.0871 | 1666.6959 | 0.045 | 37.5007 | 454.813 | -2252.062 | 2706.875 | 0 | -2252.062 | 38.58% | 46.42% | 5831.6176 | 535.0741 | 18.5379 | 5625 | 6160.0741 | 328.4565 | 6160.0741 | 5831.6176 | 328.4565 | 13.1243 | 1.8728 | 20.4107 | 0 | 20.4107 | 0 | -37.5007 | 0.034159 | 583.3041 | 0 | 0 | 583.3041 | 454.813 | 0 | 0 | 454.813 | 583.3041 | 4666.4326 | 4666.4326 | 2250 | 697.3397 | 5578.7178 | 5578.7178 | 2706.875
summer | 16 | 0.045 | 609.3741 | -1640.6259 | 2250 | 13.7109 | 23.3363 | 1640.6259 | 0.045 | 36.9141 | 515.329 | -2191.546 | 2706.875 | 0 | -2191.546 | 38.58% | 46.42% | 5831.6176 | 606.2694 | 18.2887 | 5625 | 6231.2694 | 399.6518 | 6231.2694 | 5831.6176 | 399.6518 | 13.7109 | 2.1219 | 20.4107 | 0 | 20.4107 | 0 | -36.9141 | 0.041564 | 609.3741 | 0 | 0 | 609.3741 | 515.329 | 0 | 0 | 515.329 | 609.3741 | 4874.9932 | 4874.9932 | 2250 | 728.7724 | 5830.1793 | 5830.1793 | 2706.875
summer | 16.5 | 0.045 | 683.4822 | -1566.5178 | 2250 | 15.3784 | 23.6601 | 1566.5178 | 0.045 | 35.2466 | 593.98 | -2112.895 | 2706.875 | 0 | -2112.895 | 38.58% | 46.42% | 5831.6176 | 698.8 | 17.9649 | 5625 | 6323.8 | 492.1824 | 6323.8 | 5831.6176 | 492.1824 | 15.3784 | 2.4458 | 20.4107 | 0 | 20.4107 | 0 | -35.2466 | 0.051187 | 683.4822 | 0 | 0 | 683.4822 | 593.98 | 0 | 0 | 593.98 | 683.4822 | 5467.8579 | 5467.8579 | 2250 | 818.1245 | 6544.9963 | 6544.9963 | 2706.875
summer | 17 | 0.045 | 689.0898 | -1560.9102 | 2250 | 15.5045 | 23.9327 | 1560.9102 | 0.045 | 35.1205 | 660.179 | -2046.696 | 2706.875 | 0 | -2046.696 | 38.58% | 46.42% | 5831.6176 | 776.6812 | 17.6923 | 5625 | 6401.6812 | 570.0635 | 6401.6812 | 5831.6176 | 570.0635 | 15.5045 | 2.7184 | 20.4107 | 0 | 20.4107 | 0 | -35.1205 | 0.059287 | 689.0898 | 0 | 0 | 689.0898 | 660.179 | 0 | 0 | 660.179 | 689.0898 | 5512.7188 | 5512.7188 | 2250 | 824.8856 | 6599.085 | 6599.085 | 2706.875
summer | 17.5 | 0.045 | 733.8575 | -1516.1425 | 2250 | 16.5118 | 24.0135 | 1516.1425 | 0.045 | 34.1132 | 679.791 | -2027.084 | 2706.875 | 0 | -2027.084 | 38.58% | 46.42% | 5831.6176 | 799.7541 | 17.6115 | 5625 | 6424.7541 | 593.1365 | 6424.7541 | 5831.6176 | 593.1365 | 16.5118 | 2.7991 | 20.4107 | 0 | 20.4107 | 0 | -34.1132 | 0.061686 | 733.8575 | 0 | 0 | 733.8575 | 679.791 | 0 | 0 | 679.791 | 733.8575 | 5870.8604 | 5870.8604 | 2250 | 878.862 | 7030.8963 | 7030.8963 | 2706.875
summer | 18 | 0.045 | 723.7244 | -1526.2756 | 2250 | 16.2838 | 24.0199 | 1526.2756 | 0.045 | 34.3412 | 681.35 | -2025.525 | 2706.875 | 0 | -2025.525 | 38.58% | 46.42% | 5831.6176 | 801.5882 | 17.6051 | 5625 | 6426.5882 | 594.9706 | 6426.5882 | 5831.6176 | 594.9706 | 16.2838 | 2.8056 | 20.4107 | 0 | 20.4107 | 0 | -34.3412 | 0.061877 | 723.7244 | 0 | 0 | 723.7244 | 681.35 | 0 | 0 | 681.35 | 723.7244 | 5789.7954 | 5789.7954 | 2250 | 866.6445 | 6933.1563 | 6933.1563 | 2706.875
summer | 18.5 | 0.045 | 722.0084 | -1527.9916 | 2250 | 16.2452 | 24.1503 | 1527.9916 | 0.045 | 34.3798 | 713.01 | -1993.865 | 2706.875 | 0 | -1993.865 | 38.58% | 46.42% | 5831.6176 | 838.8353 | 17.4747 | 5625 | 6463.8353 | 632.2176 | 6463.8353 | 5831.6176 | 632.2176 | 16.2452 | 2.9359 | 20.4107 | 0 | 20.4107 | 0 | -34.3798 | 0.065751 | 722.0084 | 0 | 0 | 722.0084 | 713.01 | 0 | 0 | 713.01 | 722.0084 | 5776.0669 | 5776.0669 | 2250 | 864.5755 | 6916.6039 | 6916.6039 | 2706.875
summer | 19 | 0.045 | 761.3257 | -1488.6743 | 2250 | 17.1298 | 24.1998 | 1488.6743 | 0.045 | 33.4952 | 725.035 | -1981.84 | 2706.875 | 0 | -1981.84 | 38.58% | 46.42% | 5831.6176 | 852.9824 | 17.4252 | 5625 | 6477.9824 | 646.3647 | 6477.9824 | 5831.6176 | 646.3647 | 17.1298 | 2.9854 | 20.4107 | 0 | 20.4107 | 0 | -33.4952 | 0.067222 | 761.3257 | 0 | 0 | 761.3257 | 725.035 | 0 | 0 | 725.035 | 761.3257 | 6090.6055 | 6090.6055 | 2250 | 911.9804 | 7295.843 | 7295.843 | 2706.875
summer | 19.5 | 0.045 | 739.4775 | -1510.5225 | 2250 | 16.6382 | 24.0861 | 1510.5225 | 0.045 | 33.9868 | 697.424 | -2009.451 | 2706.875 | 0 | -2009.451 | 38.58% | 46.42% | 5831.6176 | 820.4988 | 17.5389 | 5625 | 6445.4988 | 613.8812 | 6445.4988 | 5831.6176 | 613.8812 | 16.6382 | 2.8717 | 20.4107 | 0 | 20.4107 | 0 | -33.9868 | 0.063844 | 739.4775 | 0 | 0 | 739.4775 | 697.424 | 0 | 0 | 697.424 | 739.4775 | 5915.8203 | 5915.8203 | 2250 | 885.6381 | 7085.1046 | 7085.1046 | 2706.875
summer | 20 | 0.045 | 715.3882 | -1534.6118 | 2250 | 16.0962 | 24.0697 | 1534.6118 | 0.045 | 34.5288 | 693.451 | -2013.424 | 2706.875 | 0 | -2013.424 | 38.58% | 46.42% | 5831.6176 | 815.8247 | 17.5553 | 5625 | 6440.8247 | 609.2071 | 6440.8247 | 5831.6176 | 609.2071 | 16.0962 | 2.8554 | 20.4107 | 0 | 20.4107 | 0 | -34.5288 | 0.063358 | 715.3882 | 0 | 0 | 715.3882 | 693.451 | 0 | 0 | 693.451 | 715.3882 | 5723.1055 | 5723.1055 | 2250 | 856.5935 | 6852.7483 | 6852.7483 | 2706.875
summer | 20.5 | 0.045 | 741.1058 | -1508.8942 | 2250 | 16.6749 | 24.1559 | 1508.8942 | 0.045 | 33.9501 | 714.382 | -1992.493 | 2706.875 | 0 | -1992.493 | 38.58% | 46.42% | 5831.6176 | 840.4494 | 17.4691 | 5625 | 6465.4494 | 633.8318 | 6465.4494 | 5831.6176 | 633.8318 | 16.6749 | 2.9416 | 20.4107 | 0 | 20.4107 | 0 | -33.9501 | 0.065919 | 741.1058 | 0 | 0 | 741.1058 | 714.382 | 0 | 0 | 714.382 | 741.1058 | 5928.8462 | 5928.8462 | 2250 | 887.6012 | 7100.8099 | 7100.8099 | 2706.875
summer | 21 | 0.045 | 736.881 | -1513.119 | 2250 | 16.5798 | 24.2067 | 1513.119 | 0.045 | 34.0452 | 726.707 | -1980.168 | 2706.875 | 0 | -1980.168 | 38.58% | 46.42% | 5831.6176 | 854.9494 | 17.4183 | 5625 | 6479.9494 | 648.3318 | 6479.9494 | 5831.6176 | 648.3318 | 16.5798 | 2.9923 | 20.4107 | 0 | 20.4107 | 0 | -34.0452 | 0.067427 | 736.881 | 0 | 0 | 736.881 | 726.707 | 0 | 0 | 726.707 | 736.881 | 5895.0479 | 5895.0479 | 2250 | 882.5074 | 7060.0592 | 7060.0592 | 2706.875
summer | 21.5 | 0.045 | 674.5272 | -1575.4728 | 2250 | 15.1769 | 24.1445 | 1575.4728 | 0.045 | 35.4481 | 711.608 | -1995.267 | 2706.875 | 0 | -1995.267 | 38.58% | 46.42% | 5831.6176 | 837.1859 | 17.4805 | 5625 | 6462.1859 | 630.5682 | 6462.1859 | 5831.6176 | 630.5682 | 15.1769 | 2.9302 | 20.4107 | 0 | 20.4107 | 0 | -35.4481 | 0.065579 | 674.5272 | 0 | 0 | 674.5272 | 711.608 | 0 | 0 | 711.608 | 674.5272 | 5396.2178 | 5396.2178 | 2250 | 807.3275 | 6458.6198 | 6458.6198 | 2706.875
summer | 22 | 0.045 | 629.3905 | -1620.6095 | 2250 | 14.1613 | 23.3581 | 1620.6095 | 0.045 | 36.4637 | 520.63 | -2186.245 | 2706.875 | 0 | -2186.245 | 38.58% | 46.42% | 5831.6176 | 612.5059 | 18.2669 | 5625 | 6237.5059 | 405.8882 | 6237.5059 | 5831.6176 | 405.8882 | 14.1613 | 2.1438 | 20.4107 | 0 | 20.4107 | 0 | -36.4637 | 0.042212 | 629.3905 | 0 | 0 | 629.3905 | 520.63 | 0 | 0 | 520.63 | 629.3905 | 5035.124 | 5035.124 | 2250 | 752.9061 | 6023.249 | 6023.249 | 2706.875
summer | 22.5 | 0.045 | 603.7038 | -1646.2962 | 2250 | 13.5833 | 22.5521 | 1646.2962 | 0.045 | 37.0417 | 324.89 | -2381.985 | 2706.875 | 0 | -2381.985 | 38.58% | 46.42% | 5831.6176 | 382.2235 | 19.0729 | 5625 | 6007.2235 | 175.6059 | 6007.2235 | 5831.6176 | 175.6059 | 13.5833 | 1.3378 | 20.4107 | 0 | 20.4107 | 0 | -37.0417 | 0.018263 | 603.7038 | 0 | 0 | 603.7038 | 324.89 | 0 | 0 | 324.89 | 603.7038 | 4829.6304 | 4829.6304 | 2250 | 721.9357 | 5775.4853 | 5775.4853 | 2706.875
summer | 23 | 0.045 | 554.7539 | -1695.2461 | 2250 | 12.482 | 22.3662 | 1695.2461 | 0.045 | 38.143 | 279.743 | -2427.132 | 2706.875 | 0 | -2427.132 | 38.58% | 46.42% | 5831.6176 | 329.1094 | 19.2588 | 5625 | 5954.1094 | 122.4918 | 5954.1094 | 5831.6176 | 122.4918 | 12.482 | 1.1519 | 20.4107 | 0 | 20.4107 | 0 | -38.143 | 0.012739 | 554.7539 | 0 | 0 | 554.7539 | 279.743 | 0 | 0 | 279.743 | 554.7539 | 4438.0312 | 4438.0312 | 2250 | 662.9168 | 5303.3343 | 5303.3343 | 2706.875
summer | 23.5 | 0.045 | 484.4757 | -1765.5243 | 2250 | 10.9007 | 21.7158 | 1765.5243 | 0.045 | 39.7243 | 121.789 | -2585.086 | 2706.875 | 0 | -2585.086 | 38.58% | 46.42% | 5831.6176 | 143.2812 | 19.9092 | 5625 | 5768.2812 | -63.3365 | 5768.2812 | 5831.6176 | -63.3365 | 10.9007 | 0.50148 | 20.4107 | 0 | 20.4107 | 0 | -39.7243 | -0.006587 | 484.4757 | 0 | 0 | 484.4757 | 121.789 | 0 | 0 | 121.789 | 484.4757 | 3875.8059 | 3875.8059 | 2250 | 578.1824 | 4625.4592 | 4625.4592 | 2706.875
Note on B24: MERIT, select 4 representative days
Note on C24: 0.5hr intervals for 4 representative days. Note: 4x91.25=365 used to scale to annual no.
Note on D9: Adds a multiplier to the supply profile, separate values can be set for Hi and Lo tariff periods
Note on D24: From elec_gas parameters sheet (£/kWh)
Note on E24: Final demand after Esave and RES reductions
Note on F18: See CHP financial pages
Note on F24: demand - supply
Note on G24: Final supply after spreadsheet modifications (kW)
Note on H23: Demand and supply profiles are entered from MERIT or other source and then can be modified in spreadsheet
Note on H24: [lesser of load or supply]*tariff*0.5 (£)
Note on I24: the offset electricity saving - the cost of the extra gas
Note on J9: Limits the engine size to a maximum value & controls on/off times.
Note on J24: if supp>load then supp-load else 0 (kW)
Note on K10: determines when the chp plant will switch on (scaling at HI & LO tariffs should be non-zero)
Note on K24: From elec_gas parameters sheet (£/kWh), depends on Private, Distribution or Grid Customer and time of day
Note on L24: Excess elec*elec sale tariff*0.5 (£)
Note on M10: determines when the chp plant will switch on (scaling at HI & LO tariffs should be non-zero)
Note on M24: Final demand after Esave and RES reductions (kW)
Note on N24: MERIT saved graph data (kW)
Note on O24: Thermal supply after modifications (kW)
Note on P24: only positive residual is supplied by boilers, negative residual is excess from CHP to be dumped.
Note on R9: Sets value below which the cHP engine will not operate and will switch off
Note on R24: Eff(e,chp)= [Elec supply/(elec supply+heat supply)]*Eff(fuel,chp), Eff(fuel,chp) from plant parameters sheet.
Note on S24: Eff(th,chp)= [heat supply/(elec supply+heat supply)]*Eff(fuel,chp), Eff(fuel,chp) from plant parameters sheet.
Note on T24: CHP gas used = Elec supply / Eff(e,chp), (kW)
Note on U24: The thermal load supplied by CHP replaces the supply from boilers. Boiler Fuel saved = (IF therm supply > therm load THEN therm load, ELSE th supply) / Eff(th,boiler), (kW)
Note on V17: This entry determines whether private wire cost is included in capital
Note on V24: Extra gas cost to run CHP rather than boilers = (chp gas used - boiler gas saved) * gas tariff *0.5, (£). Gas tariff from 'elec_gas parameters' sheet.
Note on W24: Primary fuel required by grid to produce the chp supply amount = elec supply / Eff(e, grid), (kW). Eff(e,grid) from Plant Parameters sheet
Note on X24: Total gas use by grid elec generation and boiler therm generation (kW)
Note on Y24: % fuel saved by chp replacement of boilers and grid electricity = (1-chp gas used / (boiler gas saved + grid gas saved) * 100.
Note on Z24: Old primary fuel use = [Elec demand / Eff(e,grid)] + [Heat demand / Eff(th,boiler)], (kW)
Note on AA24: New primary fuel use = Fuel used in CHP to satisfy demands plus top up required from boilers or grid. (kW). Note energy used for export electricity not included.
Note on AK24: MERIT save graph data or from other source (kW)
Note on AO24: From MERIT or other source (kW)
Note on AS24: From MERIT or other source (kW)
Note on AW24: From MERIT or other source

## Financiator
Financial Summary - based on RETScreen
Annual Energy/CO2 Balance | [7 empty] | Yearly Anlysis
| electricity |  |  | gas |  |  | CO2 emissions | Year | net Profit | Debt payment | Discounted cashflow | Cum cashflow
| grid (kWh) | chp (kWh) | surplus | boiler (kWh) | chp (kWh) | surplus
base case | 5582346.2432 | 0 | 0 | 6439862.2156 | 0 | 0 |  | 0 |  |  | -967905 | -967905
alternative | -8378903.7568 | 13961250 | 0 | 698654.4387 | 16796159.375 | 11054951.5981 |  | 1 | 314259.0317 | 87111.45 | 206497.8015 | -761407.1985
balance | 13961250 | -13961250 | 0 | 5741207.7769 | -16796159.375 | -11054951.5981 |  | 2 | 322115.5075 | 85175.64 | 195818.0723 | -565589.1262
[8 empty] | 3 | 330168.3952 | 83239.83 | 185521.0858 | -380068.0404
Capital Costs | [7 empty] | 4 | 338422.605 | 81304.02 | 175615.4532 | -204452.5872
[8 empty] | 5 | 346883.1702 | 79368.21 | 166105.743 | -38346.8442
Initial Costs |  |  |  | Periodic Costs |  |  |  | 6 | 355555.2494 | 77432.4 | 156993.0978 | 118646.2536
Feasibility study |  |  | 0 | 5 yr |  |  | - | 7 | 364444.1306 | 75496.59 | 148275.7762 | 266922.0299
Development |  |  | 0 | 10 yr |  |  | - | 8 | 373555.2339 | 73560.78 | 139949.6268 | 406871.6566
Engineering |  |  | 0 | 15 yr |  | engine replacem | 800000 | 9 | 382894.1148 | 71624.97 | 132008.503 | 538880.1596
RE equipment |  |  | 0 | 20 yr |  |  | - | 10 | 392466.4676 | 69689.16 | 124444.6249 | 663324.7845
Balance of equipment |  |  | 0 | 25 yr |  |  | - | 11 | 402278.1293 | 67753.35 | 117248.8944 | 780573.6789
Miscellaneous |  |  | 0 | end of project life |  |  | - | 12 | 412335.0826 | 65817.54 | 110411.1679 | 890984.8468
CHP plant capital |  |  | 1613175 |  |  |  |  | 13 | 422643.4596 | 63881.73 | 103920.4939 | 994905.3407
Total |  |  | 1613175 |  |  |  |  | 14 | 433209.5461 | 61945.92 | 97765.3163 | 1092670.6571
Incentives/Grants |  | 40% | 645270 |  |  |  |  | 15 | -355960.2152 | 60010.11 | -99579.9886 | 193090.6684
Own capital |  |  | 0 |  |  |  |  | 16 | 455140.7794 | 58074.3 | 86413.2348 | 279503.9032
Bank debt |  |  | 967905 |  |  |  |  | 17 | 466519.2989 | 56138.49 | 81191.6553 | 360695.5585
[8 empty] | 18 | 478182.2813 | 54202.68 | 76256.458 | 436952.0165
Financial Parameters | [7 empty] | 19 | 490136.8384 | 52266.87 | 71595.2388 | 508547.2553
[8 empty] | 20 | 502390.2593 | 50331.06 | 67195.7195 | 575742.9747
Inflation | 2.5% |  |  | Debt ratio |  | 60% |  | 21 | 514950.0158 | 48395.25 | 63045.8119 | 638788.7866
Discount rate | 10% |  |  | Debt interest rate |  | 5% |  | 22 | 527823.7662 | 46459.44 | 59133.6693 | 697922.4559
Project life | 25 |  |  | Debt term |  | 25 |  | 23 | 541019.3604 | 44523.63 | 55447.7285 | 753370.1844
|  |  |  | Avg debt payment |  | 87111.45 |  | 24 | 554544.8444 | 42587.82 | 51976.743 | 805346.9275
[8 empty] | 25 | 568408.4655 | 40652.01 | 48709.8089 | 854056.7363
income tax | n.a. |  |  | Depreciation rate |  | n.a.
VAT | 6% |  |  | Depreciation period |  | n.a.
|  |  |  | Annual depreciation |  | n.a.
Project Costs and Savings
Income |  |  |  | Costs
| CHP therm |  | 0 | Operation |  | 0
| CHP elect |  | 209547.6973 | Maintenance |  | 111690
| Pwire elec |  | 418708.5527 | Gas (extra) (minus VAT) |  | 193654.8312
| Dist. Heating |  | 0 | Electricity |  | 0
| other1 |  | 0 | Insurance |  | 1000
| other2 |  | 0 | contingencies | 5% | 15317.2416
Total |  |  | 628256.25 | Total |  | 321662.0728
Financial Feasibility
Simple Payback |  |  | 3.157
Year-to-positive cash flow |  |  | 14
Annual Life Cycle Savings |  |  | 7664854.4311
Net Present Value @15y |  |  | 193090.6684
Note on A27: migueltrms: high risk; higher interest rate

## Chooser
Selection of best supply and energy reduction options:
The criteria for selection may be based on financial, environmental or other (eg marketing) criteria.
This sheet allows the options to be sorted by different criteria to facilitate the decision making eg.
- Minimise payback
- Maximise CO2
- Minimise capital | [5 empty] | scroll down for options sorted
etc… | [5 empty] | by various criteria!
This sheet contains the list of options for the case study sorted in each different way….. See below…..
Tech | The options | chp engine (kWe) | payback (years) | npv 15 (k£) | CO2 saved (tonnes) | Utility saved (k£pa) | Capital (k£) | Capital per CO2 (k£ / tonne) | CO2 / payback
WIND | 48 2.5kWe Proven Wts - 50% Grant | n/a | 17.9 | -44 | 69 | 5.4 | 96 | 1.3913 | 3.8547
WIND | 8 2.5kWe Proven Wts - 50% Grant | n/a | 21.3 | -10 | 11 | 0.9 | 19 | 1.7273 | 0.51643
SOL TH | 500 m2 - 30% Grant | n/a | 170 | -165 | 60 | 2 | 175 | 2.9167 | 0.35294
PV | 10,000 130Wp (1m2) panel PV - 50% Grant | n/a | 20.1 | -619 | 697 | 60 | 1200 | 1.7217 | 34.6766
PV | 1,000 130Wp (1m2) panel PV - 50% Grant | n/a | 25.1 | -92 | 70 | 6 | 150 | 2.1429 | 2.7888
PV | 100 130Wp (1m2) panel PV - 50% Grant | n/a | 28.4 | -11 | 7 | 0.6 | 17 | 2.4286 | 0.24648
ESAVE | Hi eff HVAC motors | n/a | 3.79 | 6 | 9 | 0.9 | 3.7 | 0.41111 | 2.3747
ESAVE | Draught stripping to ext windows | n/a | 0.44 | 31 | 11 | 4 | 9.5 | 0.86364 | 25
ESAVE | Th wheel heat recover on AHU's | n/a | 5 | 24 | 136 | 5 | 25 | 0.18382 | 27.2
ESAVE | Insulation HWS distribution/plant | n/a | 6.2 | 1.6 | 12 | 0.5 | 3 | 0.25 | 1.9355
ESAVE | Lighting eff / pir control | n/a | 10.7 | -5 | 128 | 13 | 135 | 1.0547 | 11.9626
ESAVE | Auto plant setbacks / var speed | n/a | 9.15 | 2 | 39 | 4 | 37 | 0.94872 | 4.2623
CHP | electrical exporting (private wire), low tariff on, 40% grant, optimum payback | 2250 | 3.1 | 2048 | 1238 | 424 | 967 | 0.7811 | 399.3548
CHP | electrical exporting (private wire), low tariff on, 40% grant, optimum CO2 | 1688 | 3.5 | 1503 | 1299 | 328 | 855 | 0.6582 | 371.1429
CHP | electrical following, 40% grant - optimum payback | 844 | 5.9 | 433 | 1058 | 157 | 671 | 0.63422 | 179.322
CHP | electrical following, 40% grant - optimum CO2 | 1125 | 6.2 | 417 | 1083 | 162 | 725 | 0.66944 | 174.6774
CHP | electrical exporting (private wire), low tariff off - optimum payback | 2250 | 5.3 | 1363 | 1139 | 422 | 1653 | 1.4513 | 214.9057
CHP | electrical exporting (private wire), low tariff on - optimum payback | 2250 | 5.4 | 1318 | 1238 | 424 | 1653 | 1.3352 | 229.2593
CHP | electrical exporting (private wire), low tariff off - optimum CO2 | 1688 | 6 | 893 | 1148 | 327 | 1465 | 1.2761 | 191.3333
CHP | electrical exporting (private wire), low tariff on - optimum CO2 | 1688 | 6.2 | 820 | 1299 | 328 | 1465 | 1.1278 | 209.5161
CHP | electrical exporting (dist network), low tariff off - optimum payback | 1125 | 9 | 94 | 1024 | 192 | 1224 | 1.1953 | 113.7778
CHP | electrical exporting (dist network), low tariff off - optimum CO2 | 1688 | 9.2 | 86 | 1148 | 239 | 1425 | 1.2413 | 124.7826
CHP | electrical following, low tariff off - optimum payback | 844 | 9.4 | 33 | 914 | 155 | 1119 | 1.2243 | 97.234
CHP | electrical following - optimum payback | 844 | 9.8 | -15 | 1058 | 157 | 1119 | 1.0577 | 107.9592
CHP | electrical following, low tariff off - optimum CO2 | 1125 | 9.9 | -19 | 940 | 159 | 1224 | 1.3021 | 94.9495
CHP | electrical exporting (grid), low tariff off - optimum payback | 731 | 10 | -29 | 851 | 144 | 1076 | 1.2644 | 85.1
CHP | electrical following - optimum CO2 | 1125 | 10.3 | -66 | 1083 | 162 | 1224 | 1.1302 | 105.1456
CHP | high tariff base electrical, low tariff off (no £ for excess e) - optimum payback | 675 | 10.4 | -69 | 820 | 135 | 1054 | 1.2854 | 78.8462
CHP | elec exporting (grid), low tariff on - optimum payback | 731 | 11 | -129 | 1001 | 143 | 1075 | 1.0739 | 91
CHP | base electrical, low tariff off | 338 | 15.6 | -349 | 536 | 76 | 922 | 1.7201 | 34.359
CHP | base electrical | 338 | 16.8 | -390 | 672 | 78 | 922 | 1.372 | 40
CHP | high tariff base electrical, low tariff off (no £ for excess e) - optimum CO2 | 1125 | 18.5 | -583 | 1024 | 122 | 1224 | 1.1953 | 55.3514
CHP | electrical exporting (grid), low tariff off - optimum CO2 | 1688 | 20.8 | -761 | 1148 | 152 | 1425 | 1.2413 | 55.1923
CHP | elec exporting (grid), low tariff on - optimum CO2 | 1688 | 24.6 | -861 | 1299 | 151 | 1425 | 1.097 | 52.8049
Tech | The options sorted by npv / pb | chp engine (kWe) | payback (years) | npv 15 (k£) | CO2 saved (tonnes) | Utility saved (k£pa) | Capital (k£) | Capital per CO2 (k£ / tonne) | CO2 / payback
CHP | electrical exporting (private wire), low tariff on, 40% grant, optimum payback | 2250 | 3.1 | 2048 | 1238 | 424 | 967 | 0.7811 | 399.3548
CHP | electrical exporting (private wire), low tariff on, 40% grant, optimum CO2 | 1688 | 3.5 | 1503 | 1299 | 328 | 855 | 0.6582 | 371.1429
CHP | electrical exporting (private wire), low tariff off - optimum payback | 2250 | 5.3 | 1363 | 1139 | 422 | 1653 | 1.4513 | 214.9057
CHP | electrical exporting (private wire), low tariff on - optimum payback | 2250 | 5.4 | 1318 | 1238 | 424 | 1653 | 1.3352 | 229.2593
CHP | electrical exporting (private wire), low tariff off - optimum CO2 | 1688 | 6 | 893 | 1148 | 327 | 1465 | 1.2761 | 191.3333
CHP | electrical exporting (private wire), low tariff on - optimum CO2 | 1688 | 6.2 | 820 | 1299 | 328 | 1465 | 1.1278 | 209.5161
CHP | electrical following, 40% grant - optimum payback | 844 | 5.9 | 433 | 1058 | 157 | 671 | 0.63422 | 179.322
CHP | electrical following, 40% grant - optimum CO2 | 1125 | 6.2 | 417 | 1083 | 162 | 725 | 0.66944 | 174.6774
CHP | electrical exporting (dist network), low tariff off - optimum payback | 1125 | 9 | 94 | 1024 | 192 | 1224 | 1.1953 | 113.7778
CHP | electrical exporting (dist network), low tariff off - optimum CO2 | 1688 | 9.2 | 86 | 1148 | 239 | 1425 | 1.2413 | 124.7826
CHP | electrical following, low tariff off - optimum payback | 844 | 9.4 | 33 | 914 | 155 | 1119 | 1.2243 | 97.234
ESAVE | Draught stripping to ext windows | n/a | 0.44 | 31 | 11 | 4 | 9.5 | 0.86364 | 25
ESAVE | Th wheel heat recover on AHU's | n/a | 5 | 24 | 136 | 5 | 25 | 0.18382 | 27.2
ESAVE | Hi eff HVAC motors | n/a | 3.79 | 6 | 9 | 0.9 | 3.7 | 0.41111 | 2.3747
ESAVE | Auto plant setbacks / var speed | n/a | 9.15 | 2 | 39 | 4 | 37 | 0.94872 | 4.2623
ESAVE | Insulation HWS distribution/plant | n/a | 6.2 | 1.6 | 12 | 0.5 | 3 | 0.25 | 1.9355
ESAVE | Lighting eff / pir control | n/a | 10.7 | -5 | 128 | 13 | 135 | 1.0547 | 11.9626
WIND | 8 2.5kWe Proven Wts - 50% Grant | n/a | 21.3 | -10 | 11 | 0.9 | 19 | 1.7273 | 0.51643
PV | 100 130Wp (1m2) panel PV - 50% Grant | n/a | 28.4 | -11 | 7 | 0.6 | 17 | 2.4286 | 0.24648
CHP | electrical following - optimum payback | 844 | 9.8 | -15 | 1058 | 157 | 1119 | 1.0577 | 107.9592
CHP | electrical following, low tariff off - optimum CO2 | 1125 | 9.9 | -19 | 940 | 159 | 1224 | 1.3021 | 94.9495
CHP | electrical exporting (grid), low tariff off - optimum payback | 731 | 10 | -29 | 851 | 144 | 1076 | 1.2644 | 85.1
WIND | 48 2.5kWe Proven Wts - 50% Grant | n/a | 17.9 | -44 | 69 | 5.4 | 96 | 1.3913 | 3.8547
CHP | electrical following - optimum CO2 | 1125 | 10.3 | -66 | 1083 | 162 | 1224 | 1.1302 | 105.1456
CHP | high tariff base electrical, low tariff off (no £ for excess e) - optimum payback | 675 | 10.4 | -69 | 820 | 135 | 1054 | 1.2854 | 78.8462
PV | 1,000 130Wp (1m2) panel PV - 50% Grant | n/a | 25.1 | -92 | 70 | 6 | 150 | 2.1429 | 2.7888
CHP | elec exporting (grid), low tariff on - optimum payback | 731 | 11 | -129 | 1001 | 143 | 1075 | 1.0739 | 91
SOL TH | 500 m2 - 30% Grant | n/a | 170 | -165 | 60 | 2 | 175 | 2.9167 | 0.35294
CHP | base electrical, low tariff off | 338 | 15.6 | -349 | 536 | 76 | 922 | 1.7201 | 34.359
CHP | base electrical | 338 | 16.8 | -390 | 672 | 78 | 922 | 1.372 | 40
CHP | high tariff base electrical, low tariff off (no £ for excess e) - optimum CO2 | 1125 | 18.5 | -583 | 1024 | 122 | 1224 | 1.1953 | 55.3514
PV | 10,000 130Wp (1m2) panel PV - 50% Grant | n/a | 20.1 | -619 | 697 | 60 | 1200 | 1.7217 | 34.6766
CHP | electrical exporting (grid), low tariff off - optimum CO2 | 1688 | 20.8 | -761 | 1148 | 152 | 1425 | 1.2413 | 55.1923
CHP | elec exporting (grid), low tariff on - optimum CO2 | 1688 | 24.6 | -861 | 1299 | 151 | 1425 | 1.097 | 52.8049
Tech | The options sorted by CO2 saved | chp engine (kWe) | payback (years) | npv 15 (k£) | CO2 saved (tonnes) | Utility saved (k£pa) | Capital (k£) | Capital per CO2 (k£ / tonne) | CO2 / payback
CHP | electrical exporting (private wire), low tariff on, 40% grant, optimum CO2 | 1688 | 3.5 | 1503 | 1299 | 328 | 855 | 0.6582 | 371.1429
CHP | electrical exporting (private wire), low tariff on - optimum CO2 | 1688 | 6.2 | 820 | 1299 | 328 | 1465 | 1.1278 | 209.5161
CHP | elec exporting (grid), low tariff on - optimum CO2 | 1688 | 24.6 | -861 | 1299 | 151 | 1425 | 1.097 | 52.8049
CHP | electrical exporting (private wire), low tariff on, 40% grant, optimum payback | 2250 | 3.1 | 2048 | 1238 | 424 | 967 | 0.7811 | 399.3548
CHP | electrical exporting (private wire), low tariff on - optimum payback | 2250 | 5.4 | 1318 | 1238 | 424 | 1653 | 1.3352 | 229.2593
CHP | electrical exporting (private wire), low tariff off - optimum CO2 | 1688 | 6 | 893 | 1148 | 327 | 1465 | 1.2761 | 191.3333
CHP | electrical exporting (dist network), low tariff off - optimum CO2 | 1688 | 9.2 | 86 | 1148 | 239 | 1425 | 1.2413 | 124.7826
CHP | electrical exporting (grid), low tariff off - optimum CO2 | 1688 | 20.8 | -761 | 1148 | 152 | 1425 | 1.2413 | 55.1923
CHP | electrical exporting (private wire), low tariff off - optimum payback | 2250 | 5.3 | 1363 | 1139 | 422 | 1653 | 1.4513 | 214.9057
CHP | electrical following, 40% grant - optimum CO2 | 1125 | 6.2 | 417 | 1083 | 162 | 725 | 0.66944 | 174.6774
CHP | electrical following - optimum CO2 | 1125 | 10.3 | -66 | 1083 | 162 | 1224 | 1.1302 | 105.1456
CHP | electrical following, 40% grant - optimum payback | 844 | 5.9 | 433 | 1058 | 157 | 671 | 0.63422 | 179.322
CHP | electrical following - optimum payback | 844 | 9.8 | -15 | 1058 | 157 | 1119 | 1.0577 | 107.9592
CHP | electrical exporting (dist network), low tariff off - optimum payback | 1125 | 9 | 94 | 1024 | 192 | 1224 | 1.1953 | 113.7778
CHP | high tariff base electrical, low tariff off (no £ for excess e) - optimum CO2 | 1125 | 18.5 | -583 | 1024 | 122 | 1224 | 1.1953 | 55.3514
CHP | elec exporting (grid), low tariff on - optimum payback | 731 | 11 | -129 | 1001 | 143 | 1075 | 1.0739 | 91
CHP | electrical following, low tariff off - optimum CO2 | 1125 | 9.9 | -19 | 940 | 159 | 1224 | 1.3021 | 94.9495
CHP | electrical following, low tariff off - optimum payback | 844 | 9.4 | 33 | 914 | 155 | 1119 | 1.2243 | 97.234
CHP | electrical exporting (grid), low tariff off - optimum payback | 731 | 10 | -29 | 851 | 144 | 1076 | 1.2644 | 85.1
CHP | high tariff base electrical, low tariff off (no £ for excess e) - optimum payback | 675 | 10.4 | -69 | 820 | 135 | 1054 | 1.2854 | 78.8462
PV | 10,000 130Wp (1m2) panel PV - 50% Grant | n/a | 20.1 | -619 | 697 | 60 | 1200 | 1.7217 | 34.6766
CHP | base electrical | 338 | 16.8 | -390 | 672 | 78 | 922 | 1.372 | 40
CHP | base electrical, low tariff off | 338 | 15.6 | -349 | 536 | 76 | 922 | 1.7201 | 34.359
ESAVE | Th wheel heat recover on AHU's | n/a | 5 | 24 | 136 | 5 | 25 | 0.18382 | 27.2
ESAVE | Lighting eff / pir control | n/a | 10.7 | -5 | 128 | 13 | 135 | 1.0547 | 11.9626
PV | 1,000 130Wp (1m2) panel PV - 50% Grant | n/a | 25.1 | -92 | 70 | 6 | 150 | 2.1429 | 2.7888
WIND | 48 2.5kWe Proven Wts - 50% Grant | n/a | 17.9 | -44 | 69 | 5.4 | 96 | 1.3913 | 3.8547
SOL TH | 500 m2 - 30% Grant | n/a | 170 | -165 | 60 | 2 | 175 | 2.9167 | 0.35294
ESAVE | Auto plant setbacks / var speed | n/a | 9.15 | 2 | 39 | 4 | 37 | 0.94872 | 4.2623
ESAVE | Insulation HWS distribution/plant | n/a | 6.2 | 1.6 | 12 | 0.5 | 3 | 0.25 | 1.9355
WIND | 8 2.5kWe Proven Wts - 50% Grant | n/a | 21.3 | -10 | 11 | 0.9 | 19 | 1.7273 | 0.51643
ESAVE | Draught stripping to ext windows | n/a | 0.44 | 31 | 11 | 4 | 9.5 | 0.86364 | 25
ESAVE | Hi eff HVAC motors | n/a | 3.79 | 6 | 9 | 0.9 | 3.7 | 0.41111 | 2.3747
PV | 100 130Wp (1m2) panel PV - 50% Grant | n/a | 28.4 | -11 | 7 | 0.6 | 17 | 2.4286 | 0.24648
Tech | The options sorted by capital | chp engine (kWe) | payback (years) | npv 15 (k£) | CO2 saved (tonnes) | Utility saved (k£pa) | Capital (k£) | Capital per CO2 (k£ / tonne) | CO2 / payback
ESAVE | Insulation HWS distribution/plant | n/a | 6.2 | 1.6 | 12 | 0.5 | 3 | 0.25 | 1.9355
ESAVE | Hi eff HVAC motors | n/a | 3.79 | 6 | 9 | 0.9 | 3.7 | 0.41111 | 2.3747
ESAVE | Draught stripping to ext windows | n/a | 0.44 | 31 | 11 | 4 | 9.5 | 0.86364 | 25
PV | 100 130Wp (1m2) panel PV - 50% Grant | n/a | 28.4 | -11 | 7 | 0.6 | 17 | 2.4286 | 0.24648
WIND | 8 2.5kWe Proven Wts - 50% Grant | n/a | 21.3 | -10 | 11 | 0.9 | 19 | 1.7273 | 0.51643
ESAVE | Th wheel heat recover on AHU's | n/a | 5 | 24 | 136 | 5 | 25 | 0.18382 | 27.2
ESAVE | Auto plant setbacks / var speed | n/a | 9.15 | 2 | 39 | 4 | 37 | 0.94872 | 4.2623
WIND | 48 2.5kWe Proven Wts - 50% Grant | n/a | 17.9 | -44 | 69 | 5.4 | 96 | 1.3913 | 3.8547
ESAVE | Lighting eff / pir control | n/a | 10.7 | -5 | 128 | 13 | 135 | 1.0547 | 11.9626
PV | 1,000 130Wp (1m2) panel PV - 50% Grant | n/a | 25.1 | -92 | 70 | 6 | 150 | 2.1429 | 2.7888
SOL TH | 500 m2 - 30% Grant | n/a | 170 | -165 | 60 | 2 | 175 | 2.9167 | 0.35294
CHP | electrical following, 40% grant - optimum payback | 844 | 5.9 | 433 | 1058 | 157 | 671 | 0.63422 | 179.322
CHP | electrical following, 40% grant - optimum CO2 | 1125 | 6.2 | 417 | 1083 | 162 | 725 | 0.66944 | 174.6774
CHP | electrical exporting (private wire), low tariff on, 40% grant, optimum CO2 | 1688 | 3.5 | 1503 | 1299 | 328 | 855 | 0.6582 | 371.1429
CHP | base electrical, low tariff off | 338 | 15.6 | -349 | 536 | 76 | 922 | 1.7201 | 34.359
CHP | base electrical | 338 | 16.8 | -390 | 672 | 78 | 922 | 1.372 | 40
CHP | electrical exporting (private wire), low tariff on, 40% grant, optimum payback | 2250 | 3.1 | 2048 | 1238 | 424 | 967 | 0.7811 | 399.3548
CHP | high tariff base electrical, low tariff off (no £ for excess e) - optimum payback | 675 | 10.4 | -69 | 820 | 135 | 1054 | 1.2854 | 78.8462
CHP | elec exporting (grid), low tariff on - optimum payback | 731 | 11 | -129 | 1001 | 143 | 1075 | 1.0739 | 91
CHP | electrical exporting (grid), low tariff off - optimum payback | 731 | 10 | -29 | 851 | 144 | 1076 | 1.2644 | 85.1
CHP | electrical following, low tariff off - optimum payback | 844 | 9.4 | 33 | 914 | 155 | 1119 | 1.2243 | 97.234
CHP | electrical following - optimum payback | 844 | 9.8 | -15 | 1058 | 157 | 1119 | 1.0577 | 107.9592
PV | 10,000 130Wp (1m2) panel PV - 50% Grant | n/a | 20.1 | -619 | 697 | 60 | 1200 | 1.7217 | 34.6766
CHP | electrical exporting (dist network), low tariff off - optimum payback | 1125 | 9 | 94 | 1024 | 192 | 1224 | 1.1953 | 113.7778
CHP | electrical following, low tariff off - optimum CO2 | 1125 | 9.9 | -19 | 940 | 159 | 1224 | 1.3021 | 94.9495
CHP | electrical following - optimum CO2 | 1125 | 10.3 | -66 | 1083 | 162 | 1224 | 1.1302 | 105.1456
CHP | high tariff base electrical, low tariff off (no £ for excess e) - optimum CO2 | 1125 | 18.5 | -583 | 1024 | 122 | 1224 | 1.1953 | 55.3514
CHP | electrical exporting (dist network), low tariff off - optimum CO2 | 1688 | 9.2 | 86 | 1148 | 239 | 1425 | 1.2413 | 124.7826
CHP | electrical exporting (grid), low tariff off - optimum CO2 | 1688 | 20.8 | -761 | 1148 | 152 | 1425 | 1.2413 | 55.1923
CHP | elec exporting (grid), low tariff on - optimum CO2 | 1688 | 24.6 | -861 | 1299 | 151 | 1425 | 1.097 | 52.8049
CHP | electrical exporting (private wire), low tariff off - optimum CO2 | 1688 | 6 | 893 | 1148 | 327 | 1465 | 1.2761 | 191.3333
CHP | electrical exporting (private wire), low tariff on - optimum CO2 | 1688 | 6.2 | 820 | 1299 | 328 | 1465 | 1.1278 | 209.5161
CHP | electrical exporting (private wire), low tariff off - optimum payback | 2250 | 5.3 | 1363 | 1139 | 422 | 1653 | 1.4513 | 214.9057
CHP | electrical exporting (private wire), low tariff on - optimum payback | 2250 | 5.4 | 1318 | 1238 | 424 | 1653 | 1.3352 | 229.2593
Tech | The options sorted by capital / CO2 | chp engine (kWe) | payback (years) | npv 15 (k£) | CO2 saved (tonnes) | Utility saved (k£pa) | Capital (k£) | Capital per CO2 (k£ / tonne) | CO2 / payback
ESAVE | Th wheel heat recover on AHU's | n/a | 5 | 24 | 136 | 5 | 25 | 0.18382 | 27.2
ESAVE | Insulation HWS distribution/plant | n/a | 6.2 | 1.6 | 12 | 0.5 | 3 | 0.25 | 1.9355
ESAVE | Hi eff HVAC motors | n/a | 3.79 | 6 | 9 | 0.9 | 3.7 | 0.41111 | 2.3747
CHP | electrical following, 40% grant - optimum payback | 844 | 5.9 | 433 | 1058 | 157 | 671 | 0.63422 | 179.322
CHP | electrical exporting (private wire), low tariff on, 40% grant, optimum CO2 | 1688 | 3.5 | 1503 | 1299 | 328 | 855 | 0.6582 | 371.1429
CHP | electrical following, 40% grant - optimum CO2 | 1125 | 6.2 | 417 | 1083 | 162 | 725 | 0.66944 | 174.6774
CHP | electrical exporting (private wire), low tariff on, 40% grant, optimum payback | 2250 | 3.1 | 2048 | 1238 | 424 | 967 | 0.7811 | 399.3548
ESAVE | Draught stripping to ext windows | n/a | 0.44 | 31 | 11 | 4 | 9.5 | 0.86364 | 25
ESAVE | Auto plant setbacks / var speed | n/a | 9.15 | 2 | 39 | 4 | 37 | 0.94872 | 4.2623
ESAVE | Lighting eff / pir control | n/a | 10.7 | -5 | 128 | 13 | 135 | 1.0547 | 11.9626
CHP | electrical following - optimum payback | 844 | 9.8 | -15 | 1058 | 157 | 1119 | 1.0577 | 107.9592
CHP | elec exporting (grid), low tariff on - optimum payback | 731 | 11 | -129 | 1001 | 143 | 1075 | 1.0739 | 91
CHP | elec exporting (grid), low tariff on - optimum CO2 | 1688 | 24.6 | -861 | 1299 | 151 | 1425 | 1.097 | 52.8049
CHP | electrical exporting (private wire), low tariff on - optimum CO2 | 1688 | 6.2 | 820 | 1299 | 328 | 1465 | 1.1278 | 209.5161
CHP | electrical following - optimum CO2 | 1125 | 10.3 | -66 | 1083 | 162 | 1224 | 1.1302 | 105.1456
CHP | electrical exporting (dist network), low tariff off - optimum payback | 1125 | 9 | 94 | 1024 | 192 | 1224 | 1.1953 | 113.7778
CHP | high tariff base electrical, low tariff off (no £ for excess e) - optimum CO2 | 1125 | 18.5 | -583 | 1024 | 122 | 1224 | 1.1953 | 55.3514
CHP | electrical following, low tariff off - optimum payback | 844 | 9.4 | 33 | 914 | 155 | 1119 | 1.2243 | 97.234
CHP | electrical exporting (dist network), low tariff off - optimum CO2 | 1688 | 9.2 | 86 | 1148 | 239 | 1425 | 1.2413 | 124.7826
CHP | electrical exporting (grid), low tariff off - optimum CO2 | 1688 | 20.8 | -761 | 1148 | 152 | 1425 | 1.2413 | 55.1923
CHP | electrical exporting (grid), low tariff off - optimum payback | 731 | 10 | -29 | 851 | 144 | 1076 | 1.2644 | 85.1
CHP | electrical exporting (private wire), low tariff off - optimum CO2 | 1688 | 6 | 893 | 1148 | 327 | 1465 | 1.2761 | 191.3333
CHP | high tariff base electrical, low tariff off (no £ for excess e) - optimum payback | 675 | 10.4 | -69 | 820 | 135 | 1054 | 1.2854 | 78.8462
CHP | electrical following, low tariff off - optimum CO2 | 1125 | 9.9 | -19 | 940 | 159 | 1224 | 1.3021 | 94.9495
CHP | electrical exporting (private wire), low tariff on - optimum payback | 2250 | 5.4 | 1318 | 1238 | 424 | 1653 | 1.3352 | 229.2593
CHP | base electrical | 338 | 16.8 | -390 | 672 | 78 | 922 | 1.372 | 40
WIND | 48 2.5kWe Proven Wts - 50% Grant | n/a | 17.9 | -44 | 69 | 5.4 | 96 | 1.3913 | 3.8547
CHP | electrical exporting (private wire), low tariff off - optimum payback | 2250 | 5.3 | 1363 | 1139 | 422 | 1653 | 1.4513 | 214.9057
CHP | base electrical, low tariff off | 338 | 15.6 | -349 | 536 | 76 | 922 | 1.7201 | 34.359
PV | 10,000 130Wp (1m2) panel PV - 50% Grant | n/a | 20.1 | -619 | 697 | 60 | 1200 | 1.7217 | 34.6766
WIND | 8 2.5kWe Proven Wts - 50% Grant | n/a | 21.3 | -10 | 11 | 0.9 | 19 | 1.7273 | 0.51643
PV | 1,000 130Wp (1m2) panel PV - 50% Grant | n/a | 25.1 | -92 | 70 | 6 | 150 | 2.1429 | 2.7888
PV | 100 130Wp (1m2) panel PV - 50% Grant | n/a | 28.4 | -11 | 7 | 0.6 | 17 | 2.4286 | 0.24648
SOL TH | 500 m2 - 30% Grant | n/a | 170 | -165 | 60 | 2 | 175 | 2.9167 | 0.35294
Tech | The options sorted by CO2 / pb | chp engine (kWe) | payback (years) | npv 15 (k£) | CO2 saved (tonnes) | Utility saved (k£pa) | Capital (k£) | Capital per CO2 (k£ / tonne) | CO2 / payback
SOL TH | 500 m2 - 30% Grant | n/a | 170 | -165 | 60 | 2 | 175 | 2.9167 | 0.35294
PV | 100 130Wp (1m2) panel PV - 50% Grant | n/a | 28.4 | -11 | 7 | 0.6 | 17 | 2.4286 | 0.24648
PV | 1,000 130Wp (1m2) panel PV - 50% Grant | n/a | 25.1 | -92 | 70 | 6 | 150 | 2.1429 | 2.7888
WIND | 8 2.5kWe Proven Wts - 50% Grant | n/a | 21.3 | -10 | 11 | 0.9 | 19 | 1.7273 | 0.51643
PV | 10,000 130Wp (1m2) panel PV - 50% Grant | n/a | 20.1 | -619 | 697 | 60 | 1200 | 1.7217 | 34.6766
CHP | base electrical, low tariff off | 338 | 15.6 | -349 | 536 | 76 | 922 | 1.7201 | 34.359
CHP | electrical exporting (private wire), low tariff off - optimum payback | 2250 | 5.3 | 1363 | 1139 | 422 | 1653 | 1.4513 | 214.9057
WIND | 48 2.5kWe Proven Wts - 50% Grant | n/a | 17.9 | -44 | 69 | 5.4 | 96 | 1.3913 | 3.8547
CHP | base electrical | 338 | 16.8 | -390 | 672 | 78 | 922 | 1.372 | 40
CHP | electrical exporting (private wire), low tariff on - optimum payback | 2250 | 5.4 | 1318 | 1238 | 424 | 1653 | 1.3352 | 229.2593
CHP | electrical following, low tariff off - optimum CO2 | 1125 | 9.9 | -19 | 940 | 159 | 1224 | 1.3021 | 94.9495
CHP | high tariff base electrical, low tariff off (no £ for excess e) - optimum payback | 675 | 10.4 | -69 | 820 | 135 | 1054 | 1.2854 | 78.8462
CHP | electrical exporting (private wire), low tariff off - optimum CO2 | 1688 | 6 | 893 | 1148 | 327 | 1465 | 1.2761 | 191.3333
CHP | electrical exporting (grid), low tariff off - optimum payback | 731 | 10 | -29 | 851 | 144 | 1076 | 1.2644 | 85.1
CHP | electrical exporting (dist network), low tariff off - optimum CO2 | 1688 | 9.2 | 86 | 1148 | 239 | 1425 | 1.2413 | 124.7826
CHP | electrical exporting (grid), low tariff off - optimum CO2 | 1688 | 20.8 | -761 | 1148 | 152 | 1425 | 1.2413 | 55.1923
CHP | electrical following, low tariff off - optimum payback | 844 | 9.4 | 33 | 914 | 155 | 1119 | 1.2243 | 97.234
CHP | electrical exporting (dist network), low tariff off - optimum payback | 1125 | 9 | 94 | 1024 | 192 | 1224 | 1.1953 | 113.7778
CHP | high tariff base electrical, low tariff off (no £ for excess e) - optimum CO2 | 1125 | 18.5 | -583 | 1024 | 122 | 1224 | 1.1953 | 55.3514
CHP | electrical following - optimum CO2 | 1125 | 10.3 | -66 | 1083 | 162 | 1224 | 1.1302 | 105.1456
CHP | electrical exporting (private wire), low tariff on - optimum CO2 | 1688 | 6.2 | 820 | 1299 | 328 | 1465 | 1.1278 | 209.5161
CHP | elec exporting (grid), low tariff on - optimum CO2 | 1688 | 24.6 | -861 | 1299 | 151 | 1425 | 1.097 | 52.8049
CHP | elec exporting (grid), low tariff on - optimum payback | 731 | 11 | -129 | 1001 | 143 | 1075 | 1.0739 | 91
CHP | electrical following - optimum payback | 844 | 9.8 | -15 | 1058 | 157 | 1119 | 1.0577 | 107.9592
ESAVE | Lighting eff / pir control | n/a | 10.7 | -5 | 128 | 13 | 135 | 1.0547 | 11.9626
ESAVE | Auto plant setbacks / var speed | n/a | 9.15 | 2 | 39 | 4 | 37 | 0.94872 | 4.2623
ESAVE | Draught stripping to ext windows | n/a | 0.44 | 31 | 11 | 4 | 9.5 | 0.86364 | 25
CHP | electrical exporting (private wire), low tariff on, 40% grant, optimum payback | 2250 | 3.1 | 2048 | 1238 | 424 | 967 | 0.7811 | 399.3548
CHP | electrical following, 40% grant - optimum CO2 | 1125 | 6.2 | 417 | 1083 | 162 | 725 | 0.66944 | 174.6774
CHP | electrical exporting (private wire), low tariff on, 40% grant, optimum CO2 | 1688 | 3.5 | 1503 | 1299 | 328 | 855 | 0.6582 | 371.1429
CHP | electrical following, 40% grant - optimum payback | 844 | 5.9 | 433 | 1058 | 157 | 671 | 0.63422 | 179.322
ESAVE | Hi eff HVAC motors | n/a | 3.79 | 6 | 9 | 0.9 | 3.7 | 0.41111 | 2.3747
ESAVE | Insulation HWS distribution/plant | n/a | 6.2 | 1.6 | 12 | 0.5 | 3 | 0.25 | 1.9355
ESAVE | Th wheel heat recover on AHU's | n/a | 5 | 24 | 136 | 5 | 25 | 0.18382 | 27.2

## CHP optima
CHP engine size and operation optimisation for case study 1 (60,000m2 Office and Residential)
This estate description is captured on CHP Financials sheet.
Approach taken was to investigate the following size and operational options:
a) | base electrical
b) | base electrical, low tariff off
c) | base heat
d) | high tariff base electrical, low tariff throttle
e) | high tariff base electrical, low tariff off
f) | electrical following
g) | electrical following, 40% grant
h) | electrical following, low tariff off
i) | heat following
j) | electrical exporting (grid), low tariff off
k) | electrical exporting (dist network), low tariff off
l) | electrical exporting (private wire), low tariff off
m) | electrical exporting (private wire), low tariff on
n) | electrical exporting (private wire), low tariff on, 40% grant
For each option the optimum financial (payback) and energy (CO2) options were highlighted | [7 empty] | by | and | respectively
These optimums were then inserted in the chooser sheet for comparison and selection
a) | base electrical
| engine (kWe) | payback (years) | npv 15 (k£) | CO2 saved (Tonnes) | Utility saved (k£pa) | Capital (k£) | Capital per CO2 (k£/tonne)
| 338 | 16.8 | -390 | 672 | 78 | 922 | 1.372
b) | base electrical, low tariff off
| engine (kWe) | payback (years) | npv 15 (k£) | CO2 saved (Tonnes) | Utility saved (k£pa) | Capital (k£) | Capital per CO2 (k£/tonne) | Low tariff engine off mode improves financial performance but degrades
| 338 | 15.6 | -349 | 536 | 76 | 922 | 1.7201 | environmental benefit.
c) | base heat - not analysed as very low heat base load
d) | high tariff base electrical, low tariff throttle (grid revenue for excess electricity) - also called elec exporting (grid), low tariff on, (see option h) ).
| engine (kWe) | payback (years) | npv 15 (k£) | CO2 saved (Tonnes) | Utility saved (k£pa) | Capital (k£) | Capital per CO2 (k£/tonne)
338
| 450 | 14.2 | -306 | 800 | 99 | 966 | 1.2075
| 563 | 12.3 | -211 | 900 | 120 | 1010 | 1.1222
| 619 | 11.6 | -171 | 939 | 130 | 1032 | 1.099
| 675 | 11.2 | -144 | 971 | 137 | 1054 | 1.0855
| 731 | 11 | -129 | 1001 | 143 | 1075 | 1.0739
| 788 | 11 | -131 | 1033 | 148 | 1098 | 1.0629
| 844 | 11.1 | -143 | 1061 | 152 | 1119 | 1.0547
| 1125 | 13.5 | -345 | 1174 | 156 | 1224 | 1.0426
| 1688 | 24.6 | -861 | 1299 | 151 | 1425 | 1.097
| 2250 | 60.4 | -1355 | 1244 | 143 | 1613 | 1.2966
e) | high tariff base electrical, low tariff off (no revenue for excess electricity)
| engine (kWe) | payback (years) | npv 15 (k£) | CO2 saved (Tonnes) | Utility saved (k£pa) | Capital (k£) | Capital per CO2 (k£/tonne)
| 338 | 15.6 | -349 | 536 | 76 | 922 | 1.7201
| 450 | 12.7 | -224 | 653 | 99 | 966 | 1.4793
| 563 | 11 | -119 | 750 | 120 | 1010 | 1.3467
| 619 | 10.6 | -85 | 788 | 128 | 1032 | 1.3096
| 675 | 10.4 | -69 | 820 | 135 | 1054 | 1.2854
| 731 | 10.4 | -74 | 851 | 139 | 1075 | 1.2632
| 788 | 10.7 | -104 | 882 | 141 | 1098 | 1.2449
| 844 | 11.2 | -150 | 910 | 142 | 1119 | 1.2297
| 1125 | 18.5 | -583 | 1024 | 122 | 1224 | 1.1953
| 1688 |  | -1608 | 1148 | 65 | 1425 | 1.2413
2250
f) | electrical following
|  | payback (years) | npv 15 (k£) | CO2 saved (Tonnes) | Utility saved (k£pa) | Capital (k£) | Capital per CO2 (k£/tonne)
| 338 | 16.8 | -390 | 672 | 78 | 922 | 1.372
| 450 | 13.5 | -271 | 795 | 101 | 966 | 1.2151
| 563 | 11.5 | -159 | 892 | 123 | 1010 | 1.1323
| 619 | 10.9 | -111 | 932 | 132 | 1032 | 1.1073
| 675 | 10.4 | -73 | 965 | 141 | 1054 | 1.0922
| 731 | 10.1 | -43 | 999 | 147 | 1075 | 1.0761
| 788 | 9.9 | -24 | 1033 | 153 | 1098 | 1.0629
| 844 | 9.8 | -15 | 1058 | 157 | 1119 | 1.0577
| 1125 | 10.3 | -66 | 1083 | 162 | 1224 | 1.1302
1688
2250
g) | electrical following, 40% grant
| engine (kWe) | payback (years) | npv 15 (k£) | CO2 saved (Tonnes) | Utility saved (k£pa) | Capital (k£) | Capital per CO2 (k£/tonne)
| 338 | 10.1 | -21 | 672 | 78 | 553 | 0.82292 | Greatly improved financials with 40% grant (NPV, Payback)
| 450 | 8.1 | 115 | 795 | 101 | 579 | 0.7283
| 563 | 6.9 | 246 | 892 | 123 | 606 | 0.67937
| 619 | 6.5 | 302 | 932 | 132 | 619 | 0.66416
| 675 | 6.3 | 349 | 965 | 141 | 633 | 0.65596
| 731 | 6.1 | 387 | 999 | 147 | 645 | 0.64565
| 788 | 6 | 415 | 1033 | 153 | 658 | 0.63698
| 844 | 5.9 | 433 | 1058 | 157 | 671 | 0.63422
| 1125 | 6.2 | 417 | 1083 | 162 | 725 | 0.66944
1688
2250
h) | electrical following, low tariff off
| engine (kWe) | payback (years) | npv 15 (k£) | CO2 saved (Tonnes) | Utility saved (k£pa) | Capital (k£) | Capital per CO2 (k£/tonne)
| 338 | 15.6 | -349 | 536 | 76 | 922 | 1.7201
| 450 | 12.6 | -224 | 653 | 99 | 966 | 1.4793
| 563 | 10.9 | -111 | 749 | 120 | 1010 | 1.3485
| 619 | 10.4 | -64 | 788 | 129 | 1032 | 1.3096
| 675 | 10 | -25 | 822 | 138 | 1054 | 1.2822
| 731 | 9.7 | 4 | 855 | 145 | 1075 | 1.2573
| 788 | 9.5 | 23 | 889 | 150 | 1098 | 1.2351
| 844 | 9.4 | 33 | 914 | 155 | 1119 | 1.2243
| 1125 | 9.9 | -19 | 940 | 159 | 1224 | 1.3021
1688
2250
i) | heat following - not analysed as very high variation in heat load and low base
j) | electrical exporting (grid), low tariff off
|  | payback (years) | npv 15 (k£) | CO2 saved (Tonnes) | Utility saved (k£pa) | Capital (k£) | Capital per CO2 (k£/tonne)
| 338 | 15.8 | -349 | 536 | 76 | 922 | 1.7201
| 450 | 12.7 | -224 | 653 | 99 | 966 | 1.4793
| 563 | 10.9 | -111 | 749 | 120 | 1010 | 1.3485
| 619 | 10.4 | -72 | 788 | 129 | 1032 | 1.3096
| 675 | 10.1 | -44 | 820 | 137 | 1054 | 1.2854
| 731 | 10 | -29 | 851 | 144 | 1076 | 1.2644
| 788 | 10 | -30 | 882 | 149 | 1098 | 1.2449
| 844 | 10.1 | -43 | 910 | 152 | 1119 | 1.2297
| 1125 | 12.1 | -244 | 1024 | 157 | 1224 | 1.1953
| 1688 | 20.8 | -761 | 1148 | 152 | 1425 | 1.2413
| 2250 | 51.2 | -1307 | 1139 | 143 | 1613 | 1.4162
k) | electrical exporting (dist network), low tariff off
|  | payback (years) | npv 15 (k£) | CO2 saved (Tonnes) | Utility saved (k£pa) | Capital (k£) | Capital per CO2 (k£/tonne)
| 338 | 15.6 | -349 | 536 | 76 | 922 | 1.7201
| 450 | 12.6 | -224 | 653 | 99 | 966 | 1.4793
| 563 | 10.9 | -109 | 749 | 121 | 1010 | 1.3485
| 619 | 10.3 | -60 | 788 | 131 | 1032 | 1.3096
| 675 | 9.9 | -18 | 820 | 140 | 1054 | 1.2854
| 731 | 9.6 | 16 | 851 | 149 | 1076 | 1.2644
| 788 | 9.3 | 43 | 882 | 157 | 1098 | 1.2449
| 844 | 9.2 | 63 | 910 | 164 | 1119 | 1.2297
| 1125 | 9 | 94 | 1024 | 192 | 1224 | 1.1953
| 1688 | 9.2 | 86 | 1148 | 239 | 1425 | 1.2413
| 2250 | 9.4 | 47 | 1139 | 283 | 1613 | 1.4162
l) | electrical exporting (private wire), low tariff off
| engine (kWe) | payback (years) | npv 15 (k£) | CO2 saved (Tonnes) | Utility saved (k£pa) | Capital (k£) | Capital per CO2 (k£/tonne)
| 338 | 16.3 | -389 | 536 | 76 | 962 | 1.7948
| 450 | 13.2 | -264 | 653 | 99 | 1006 | 1.5406
| 563 | 11.3 | -144 | 749 | 121 | 1050 | 1.4019
| 619 | 10.6 | -87 | 788 | 132 | 1072 | 1.3604
| 675 | 10 | -33 | 820 | 143 | 1094 | 1.3341
| 731 | 9.5 | 21 | 851 | 153 | 1115 | 1.3102
| 788 | 9.1 | 77 | 882 | 164 | 1137 | 1.2891
| 844 | 8.7 | 130 | 910 | 175 | 1159 | 1.2736
| 1125 | 7.4 | 392 | 1024 | 226 | 1264 | 1.2344
| 1688 | 6 | 893 | 1148 | 327 | 1465 | 1.2761
| 2250 | 5.3 | 1363 | 1139 | 422 | 1653 | 1.4513
m) | electrical exporting (private wire), low tariff on
|  | payback (years) | npv 15 (k£) | CO2 saved (Tonnes) | Utility saved (k£pa) | Capital (k£) | Capital per CO2 (k£/tonne)
| 338 | 17.7 | -433 | 672 | 78 | 962 | 1.4315
| 450 | 14.4 | -328 | 800 | 101 | 1006 | 1.2575
| 563 | 12.2 | -216 | 900 | 123 | 1050 | 1.1667
| 619 | 11.4 | -160 | 939 | 134 | 1072 | 1.1416
| 675 | 10.8 | -106 | 971 | 145 | 1094 | 1.1267
| 731 | 10.2 | -52 | 1001 | 155 | 1115 | 1.1139
| 788 | 9.7 | 3 | 1033 | 166 | 1137 | 1.1007
| 844 | 9.3 | 56 | 1061 | 177 | 1159 | 1.0924
| 1125 | 7.8 | 319 | 1174 | 228 | 1264 | 1.0767
| 1688 | 6.2 | 820 | 1299 | 328 | 1465 | 1.1278
| 2250 | 5.4 | 1318 | 1238 | 424 | 1653 | 1.3352
n) | electrical exporting (private wire), low tariff on, 40% grant
| engine (kWe) | payback (years) | npv 15 (k£) | CO2 saved (Tonnes) | Utility saved (k£pa) | Capital (k£) | Capital per CO2 (k£/tonne)
| 338 | 9.4 | 19 | 672 | 78 | 553 | 0.82292
| 450 | 7.6 | 162 | 800 | 101 | 579 | 0.72375
| 563 | 6.5 | 300 | 900 | 123 | 606 | 0.67333 | Greatly improved financials with 40% grant
| 619 | 6.1 | 365 | 939 | 134 | 619 | 0.65921
| 675 | 5.8 | 429 | 971 | 145 | 632 | 0.65088
| 731 | 5.5 | 492 | 1001 | 155 | 645 | 0.64436
| 788 | 5.3 | 556 | 1033 | 166 | 659 | 0.63795
| 844 | 5.1 | 618 | 1061 | 177 | 671 | 0.63242
| 1125 | 4.3 | 922 | 1174 | 228 | 734 | 0.62521
| 1688 | 3.5 | 1503 | 1299 | 328 | 855 | 0.6582
| 2250 | 3.1 | 2048 | 1238 | 424 | 967 | 0.7811

## CO2per£sort
The options sorted by CO2 / capital £ |  | chp engine (kWe) | payback (years) | npv 15 (k£) | CO2 saved (tonnes) | Utility saved (k£pa) | Capital (k£) | CO2 per k£ capital
ESAVE | Th wheel heat recover on AHU's | n/a | 5 | 24 | 136 | 5 | 25 | 5.44
ESAVE | Insulation HWS distribution/plant | n/a | 6.2 | 1.6 | 12 | 0.5 | 3 | 4
ESAVE | Hi eff HVAC motors | n/a | 3.79 | 6 | 9 | 0.9 | 3.7 | 2.4324
CHP | electrical following, 40% grant - optimum £ | 844 | 5.9 | 433 | 1058 | 157 | 671 | 1.5768
ESAVE | Draught stripping to ext windows | n/a | 0.44 | 31 | 11 | 4 | 9.5 | 1.1579
ESAVE | Auto plant setbacks / var speed | n/a | 9.15 | 2 | 39 | 4 | 37 | 1.0541
ESAVE | Lighting eff / pir control | n/a | 10.7 | -5 | 128 | 13 | 135 | 0.94815
CHP | electrical following - optimum £ | 844 | 9.8 | -15 | 1058 | 157 | 1119 | 0.94549

## £capitalsort
The options sorted by capital |  | chp engine (kWe) | payback (years) | npv 15 (k£) | CO2 saved (tonnes) | Utility saved (k£pa) | Capital (k£)
ESAVE | Insulation HWS distribution/plant | n/a | 6.2 | 1.6 | 12 | 0.5 | 3
ESAVE | Hi eff HVAC motors | n/a | 3.79 | 6 | 9 | 0.9 | 3.7
ESAVE | Draught stripping to ext windows | n/a | 0.44 | 31 | 11 | 4 | 9.5
PV | 100 130Wp (1m2) panel PV - 50% Grant | n/a | 28.4 | -11 | 7 | 0.6 | 17
WIND | 8 2.5kWe Proven Wts - 50% Grant | n/a | 21.3 | -10 | 11 | 0.9 | 19
ESAVE | Th wheel heat recover on AHU's | n/a | 5 | 24 | 136 | 5 | 25
ESAVE | Auto plant setbacks / var speed | n/a | 9.15 | 2 | 39 | 4 | 37
ESAVE | Lighting eff / pir control | n/a | 10.7 | -5 | 128 | 13 | 135
SOL TH | 500 m2 - 30% Grant | n/a | 170 | -165 | 60 | 2 | 175
CHP | base electrical | 338 | 16.8 | -390 | 672 | 78 | 922

## CO2sort
The options sorted by CO2 saved |  | chp engine (kWe) | payback (years) | npv 15 (k£) | CO2 saved (tonnes) | Utility saved (k£pa) | Capital (k£)
CHP | Electrical exporting (private wire), 40% grant, optimum CO2 | 1688 | 3.5 | 1503 | 1299 | 328 | 855
PV | 10,000 130Wp (1m2) panel PV - 50% Grant | n/a | 20.1 | -619 | 697 | 60 | 1200
ESAVE | Th wheel heat recover on AHU's | n/a | 5 | 24 | 136 | 5 | 25
ESAVE | Lighting eff / pir control | n/a | 10.7 | -5 | 128 | 13 | 135
WIND | 48 2.5kWe Proven Wts - 50% Grant | n/a | 17.9 | -44 | 69 | 5.4 | 96
SOL TH | 500 m2 - 30% Grant | n/a | 170 | -165 | 60 | 2 | 175
ESAVE | Auto plant setbacks / var speed | n/a | 9.15 | 2 | 39 | 4 | 37
ESAVE | Insulation HWS distribution/plant | n/a | 6.2 | 1.6 | 12 | 0.5 | 3
ESAVE | Draught stripping to ext windows | n/a | 0.44 | 31 | 11 | 4 | 9.5
ESAVE | Hi eff HVAC motors | n/a | 3.79 | 6 | 9 | 0.9 | 3.7

## NPVsort
The options sorted by npv / pb |  | chp engine (kWe) | payback (years) | npv 15 (k£) | CO2 saved (tonnes) | Utility saved (k£pa) | Capital (k£)
CHP | Electrical exporting (private wire), 40% grant, optimum £ | 2250 | 3.1 | 2048 | 1238 | 424 | 967
CHP | Electrical exporting (private wire), optimum £ | 2250 | 5.4 | 1318 | 1238 | 424 | 1653
ESAVE | Draught stripping to ext windows | n/a | 0.44 | 31 | 11 | 4 | 9.5
ESAVE | Th wheel heat recover on AHU's | n/a | 5 | 24 | 136 | 5 | 25
ESAVE | Hi eff HVAC motors | n/a | 3.79 | 6 | 9 | 0.9 | 3.7
ESAVE | Auto plant setbacks / var speed | n/a | 9.15 | 2 | 39 | 4 | 37
ESAVE | Insulation HWS distribution/plant | n/a | 6.2 | 1.6 | 12 | 0.5 | 3
ESAVE | Lighting eff / pir control | n/a | 10.7 | -5 | 128 | 13 | 135

## case study selection
The options selected |  | chp engine (kWe) | payback (years) | npv 15 (k£) | CO2 saved (tonnes) | Utility saved (k£pa) | Capital (k£)
CHP | Electrical exporting (private wire), 40% grant, optimum £ | 2250 | 3.1 | 2048 | 1238 | 424 | 967
PV | 100 130Wp (1m2) panel PV - 50% Grant | n/a | 28.4 | -11 | 7 | 0.6 | 17
WIND | 8 2.5kWe Proven Wts - 50% Grant | n/a | 21.3 | -10 | 11 | 0.9 | 19
ESAVE | Draught stripping to ext windows | n/a | 0.44 | 31 | 11 | 4 | 9.5
ESAVE | Th wheel heat recover on AHU's | n/a | 5 | 24 | 136 | 5 | 25
ESAVE | Hi eff HVAC motors | n/a | 3.79 | 6 | 9 | 0.9 | 3.7
ESAVE | Auto plant setbacks / var speed | n/a | 9.15 | 2 | 39 | 4 | 37
ESAVE | Insulation HWS distribution/plant | n/a | 6.2 | 1.6 | 12 | 0.5 | 3
ESAVE | Lighting eff / pir control | n/a | 10.7 | -5 | 128 | 13 | 135

## Wind
WIND
NUMBER 2.5kW machines = |  |  | 240
Nordex 600kW | Scaled | cost per 2.5kWe unit |  | 5000 | notes: | based on MERIT 600kW Nordex
0 | 0 | Cost for 240 units |  | 1200000 |  | equiv to 240 Proven 2.5kW turbines
0 | 0 |  |  |  |  | assumed costs for roof mounted machines
0 | 0 | unit cost with grants |  | 2500 |  | Proven cut-in at 5mph = 2.2m/s
0 | 0 | cost for 240 units |  | 600000 |  | Nordex cut-in at 3m/s
0 | 0 |  |  |  |  | Proven data suggests 2000 - 4000kWh p.a.
0 | 0 | grants plus 30% cost reduce |  | 1750 |  | => for 240 systems: 480,000 - 960,000kWh
0 | 0 | cost for 240 units |  | 420000 |  | (GENcalc model predicts 661,000kWh)
0 | 0
0 | 0
0 | 0
11.7054 | 11.7054
11.7054 | 11.7054
79.1393 | 79.1393
79.1393 | 79.1393
35.9272 | 35.9272
35.9272 | 35.9272
35.9531 | 35.9531
35.9531 | 35.9531
23.0476 | 23.0476
23.0476 | 23.0476
23.0809 | 23.0809
23.0809 | 23.0809
23.0976 | 23.0976
23.0976 | 23.0976
11.7223 | 11.7223
11.7223 | 11.7223
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
22.8908 | 22.8908
22.8908 | 22.8908
22.8581 | 22.8581
22.8581 | 22.8581
168.1749 | 168.1749
168.1749 | 168.1749
168.1749 | 168.1749
168.1749 | 168.1749
220.6911 | 220.6911
220.6911 | 220.6911
237.6402 | 237.6402
237.6402 | 237.6402
220.2994 | 220.2994
220.2994 | 220.2994
366.821 | 366.821
366.821 | 366.821
421.9074 | 421.9074
421.9074 | 421.9074
108.2381 | 108.2381
108.2381 | 108.2381
108.3152 | 108.3152
108.3152 | 108.3152
239.4244 | 239.4244
239.4244 | 239.4244
370.5023 | 370.5023
370.5023 | 370.5023
146.1077 | 146.1077
146.1077 | 146.1077
168.7156 | 168.7156
168.7156 | 168.7156
239.8532 | 239.8532
239.8532 | 239.8532
79.3394 | 79.3394
79.3394 | 79.3394
36.1093 | 36.1093
36.1093 | 36.1093
36.1879 | 36.1879
36.1879 | 36.1879
55.0368 | 55.0368
55.0368 | 55.0368
54.977 | 54.977
54.977 | 54.977
79.5117 | 79.5117
79.5117 | 79.5117
0 | 0
0 | 0
11.2508 | 11.2508
11.2508 | 11.2508
0 | 0
0 | 0
0 | 0
0 | 0
22.2302 | 22.2302
22.2302 | 22.2302
11.286 | 11.286
11.286 | 11.286
22.2689 | 22.2689
22.2689 | 22.2689
22.3156 | 22.3156
22.3156 | 22.3156
34.8598 | 34.8598
34.8598 | 34.8598
76.6541 | 76.6541
76.6541 | 76.6541
22.3 | 22.3
22.3 | 22.3
76.3876 | 76.3876
76.3876 | 76.3876
141.782 | 141.782
141.782 | 141.782
141.634 | 141.634
141.634 | 141.634
163.7431 | 163.7431
163.7431 | 163.7431
163.3466 | 163.3466
163.3466 | 163.3466
140.8498 | 140.8498
140.8498 | 140.8498
163.5729 | 163.5729
163.5729 | 163.5729
141.3389 | 141.3389
141.3389 | 141.3389
141.5355 | 141.5355
141.5355 | 141.5355
106.1995 | 106.1995
106.1995 | 106.1995
142.2775 | 142.2775
142.2775 | 142.2775
106.6458 | 106.6458
106.6458 | 106.6458
106.7955 | 106.7955
106.7955 | 106.7955
77.6567 | 77.6567
77.6567 | 77.6567
107.8165 | 107.8165
107.8165 | 107.8165
53.7704 | 53.7704
53.7704 | 53.7704
22.6155 | 22.6155
22.6155 | 22.6155
22.6636 | 22.6636
22.6636 | 22.6636
22.6556 | 22.6556
22.6556 | 22.6556
22.5199 | 22.5199
22.5199 | 22.5199
53.4676 | 53.4676
53.4676 | 53.4676
107.0583 | 107.0583
107.0583 | 107.0583
106.7206 | 106.7206
106.7206 | 106.7206
106.2365 | 106.2365
106.2365 | 106.2365
106.0885 | 106.0885
106.0885 | 106.0885
76.4673 | 76.4673
76.4673 | 76.4673
105.7568 | 105.7568
105.7568 | 105.7568
141.2408 | 141.2408
141.2408 | 141.2408
105.6101 | 105.6101
105.6101 | 105.6101
76.361 | 76.361
76.361 | 76.361
52.9274 | 52.9274
52.9274 | 52.9274
34.9208 | 34.9208
34.9208 | 34.9208
35.0435 | 35.0435
35.0435 | 35.0435
0 | 0
0 | 0
11.4695 | 11.4695
11.4695 | 11.4695
11.4898 | 11.4898
11.4898 | 11.4898
11.498 | 11.498
11.498 | 11.498

## SolarPV
SOLAR PV
NUMBER OF 1M2 PV PANELS = |  | 10000
130W Mono: BP Solar BP130L | No.x130W Mono: BP Solar BP130L |  | Cost per unit(£) = | 400
0 | 0 |  | 10000units = | 4000000
0 | 0
0 | 0 |  | Costwith 50% grant= | 200
0 | 0 |  | 10000units = | 2000000
0 | 0
0 | 0 |  | 50% grant +30% red'n= | 140 | note assume 40% reduction for 10,000,
0 | 0 |  | 10,000units= | 1400000 | 25% reduction for 1,000 and 15% for 100.
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0.00029152 | 2.9152
0.0002915 | 2.915
0.0022626 | 22.6262
0.002267 | 22.6696
0.0036307 | 36.3069
0.0036319 | 36.3194
0.010198 | 101.9826
0.010198 | 101.9789
0.018975 | 189.7473
0.018945 | 189.452
0.027316 | 273.1583
0.027192 | 271.9161
0.015552 | 155.5172
0.015423 | 154.2283
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0.0030191 | 30.191
0.0030252 | 30.2523
0.0093395 | 93.3953
0.0093497 | 93.4974
0.020487 | 204.8713
0.020516 | 205.1594
0.034519 | 345.1856
0.034549 | 345.4941
0.017352 | 173.5209
0.017355 | 173.5485
0.076269 | 762.6893
0.076106 | 761.064
0.066367 | 663.6684
0.066138 | 661.3778
0.055595 | 555.9535
0.05524 | 552.4036
0.03164 | 316.4005
0.031311 | 313.1059
0.017198 | 171.979
0.016755 | 167.5489
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0.00078228 | 7.8228
0.00078228 | 7.8228
0.0048163 | 48.1629
0.004816 | 48.1605
0.011845 | 118.4518
0.011905 | 119.0527
0.032263 | 322.6308
0.032564 | 325.6442
0.062838 | 628.3834
0.063248 | 632.4841
0.054736 | 547.3591
0.054936 | 549.3559
0.057244 | 572.4426
0.057347 | 573.4718
0.079673 | 796.7293
0.079719 | 797.1861
0.074724 | 747.2377
0.074729 | 747.2907
0.073949 | 739.4881
0.073874 | 738.736
0.07186 | 718.599
0.071707 | 717.0665
0.078245 | 782.4527
0.07792 | 779.2023
0.049214 | 492.1386
0.048957 | 489.5686
0.04048 | 404.8026
0.040035 | 400.3531
0.022347 | 223.4709
0.021846 | 218.4556
0.0091728 | 91.7282
0.009174 | 91.7404
0.0046863 | 46.8634
0.0046866 | 46.8655
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0.0030191 | 30.191
0.0030252 | 30.2523
0.0093395 | 93.3953
0.0093497 | 93.4974
0.020487 | 204.8713
0.020516 | 205.1594
0.034519 | 345.1856
0.034549 | 345.4941
0.017352 | 173.5209
0.017355 | 173.5485
0.076269 | 762.6893
0.076106 | 761.064
0.066367 | 663.6684
0.066138 | 661.3778
0.055595 | 555.9535
0.05524 | 552.4036
0.03164 | 316.4005
0.031311 | 313.1059
0.017198 | 171.979
0.016755 | 167.5489
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0

## SolarHW
SOLAR THERMAL HOT WATER
Area of collector (m2) |  | 2500 | Kwhpa | 1231187.1271 | notes: | for UK typical output for flat plate collector = 370 kWhpa/m2
Scaling Factor |  | 1 | kWhpa/m2 | 492.4749 |  | evacuated tube type typical = 490 kWhpa/m2
Base HW | Scaled HW |  |  |  |  | Merit was used to find typical days and then the profile
0 | 0 |  |  |  |  | scaled to give the required kWhpa/m2 for the given collector
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
27.5593 | 27.5593
27.3523 | 27.3523
52.054 | 52.054
53.1597 | 53.1597
136.4817 | 136.4817
138.767 | 138.767
229.007 | 229.007
230.504 | 230.504
173.2217 | 173.2217
171.1087 | 171.1087
175.0243 | 175.0243
174.916 | 174.916
238.7127 | 238.7127
239.9637 | 239.9637
220.031 | 220.031
219.3553 | 219.3553
231.4237 | 231.4237
231.355 | 231.355
233.5157 | 233.5157
233.2773 | 233.2773
273.6497 | 273.6497
273.9643 | 273.9643
195.3147 | 195.3147
192.7213 | 192.7213
202.4953 | 202.4953
202.0157 | 202.0157
173.868 | 173.868
172.0847 | 172.0847
107.2387 | 107.2387
103.5407 | 103.5407
33.441 | 33.441
29.8607 | 29.8607
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
27.5593 | 27.5593
27.3523 | 27.3523
52.054 | 52.054
53.1597 | 53.1597
136.4817 | 136.4817
138.767 | 138.767
229.007 | 229.007
230.504 | 230.504
173.2217 | 173.2217
171.1087 | 171.1087
175.0243 | 175.0243
174.916 | 174.916
238.7127 | 238.7127
239.9637 | 239.9637
220.031 | 220.031
219.3553 | 219.3553
231.4237 | 231.4237
231.355 | 231.355
233.5157 | 233.5157
233.2773 | 233.2773
273.6497 | 273.6497
273.9643 | 273.9643
195.3147 | 195.3147
192.7213 | 192.7213
202.4953 | 202.4953
202.0157 | 202.0157
173.868 | 173.868
172.0847 | 172.0847
107.2387 | 107.2387
103.5407 | 103.5407
33.441 | 33.441
29.8607 | 29.8607
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
82.678 | 82.678
82.057 | 82.057
156.162 | 156.162
159.479 | 159.479
409.445 | 409.445
416.301 | 416.301
687.021 | 687.021
691.512 | 691.512
519.665 | 519.665
513.326 | 513.326
525.073 | 525.073
524.748 | 524.748
716.138 | 716.138
719.891 | 719.891
660.093 | 660.093
658.066 | 658.066
694.271 | 694.271
694.065 | 694.065
700.547 | 700.547
699.832 | 699.832
820.949 | 820.949
821.893 | 821.893
585.944 | 585.944
578.164 | 578.164
607.486 | 607.486
606.047 | 606.047
521.604 | 521.604
516.254 | 516.254
321.716 | 321.716
310.622 | 310.622
100.323 | 100.323
89.582 | 89.582
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0