## Energy bills
Month | Night (kWh) or total | Day | Hot water and heating | Non-heating appliances
September 05 | 68008 | - | 14218 | 53790
October 05 | 81691 | - | 27901 | 53790
November 05 | 106814 | - | 53024 | 53790
December 05 | 124068 | - | 70278 | 53790
January 06 | 140300 | - | 86510 | 53790
February 06 | 131860 | - | 78070 | 53790
March 06 | 136006 | - | 82216 | 53790
April 06 | 26077 | 65681 | 37968 | 53790
May 06 | 21199 | 52465 | 19874 | 53790 | Lower occupancy (figures not accurate)
June 06 | 17114 | 42167 | 5491 | 53790 | Lower occupancy (figures not accurate)
July 06 | 12773 | 32604 | -8413 | 53790 | Lower occupancy (figures not accurate)
August 06 | 13294 | 38103 | -2393 | 53790 | Lower occupancy (figures not accurate)
September 06 | 18535 | 53790 | 18535 | 53790
October 06 | 20662 | 59359 | 26231 | 53790
November 06 | 27671 | 86228 | 60109 | 53790
December 06 | 30482 | 86611 | 63303 | 53790
Kirkmichael 2005-2006 | Energy (l) | Energy/30 days
22/09-02/11 | 5000 | 3750
02/11-18/11 | 2700 | 5062.5
18/11-07/12 | 4900 | 7736.8421
07/12-30/12 | 4600 | 6000
30/12-23/01 | 4000 | 5217.3913
23/01-07/02 | 5000 | 10714.2857
07/02-27/02 | 5000 | 7500
27/02-17/03 | 2300 | 3450
17/03-28/03 | 4800 | 13090.9091
28/03-27/04 | 4200 | 4344.8276
27/04-23/06 | 2000 | 2307.6923
0
Kirchmichael 2006-2007 | Energy (l) | Energy/30 days
23/06-22/08 | 5095 | 2590.678
22/08-26/10 | 4516 | 2116.875
26/10-22/11 | 4000 | 4615.3846
22/11-15/12 | 5500 | 7173.913
15/12-09/01 | 4100 | 5125
Nith-Cree 2005-2006 | Energy (l) | Energy/30 days
23/09/05-19/11/05 | 2232 | 1195.7143
19/11/05-22/12/05 | 1885 | 1713.6364
22/12/05-04/02/06 | 2200 | 1571.4286
04/02/06-15/03/06 | 2358 | 1725.3659
15/03/06-27/04/06 | 2000 | 1428.5714
538.7383
Nith-Cree 2006-2007 | Energy (l) | Energy/30 days
27/04/06-16/11/06 | 2300 | 346.7337
16/11/06-05/01/07 | 2300 | 1408.1633
Boilerhouse 2 2005-2006 | Energy (l) | Energy/30 days
13/10/05-21/11/2005 | 1890 | 1492.1053
21/11/2005-07/12/05 | 1164 | 2182.5
07/12/05-06/01/06 | 1212 | 1253.7931
06/01/06-02/02/06 | 1619 | 1868.0769
02/02/06-20/02/06 | 1260 | 2100
20/02/06-08/03/06 | 1151 | 1918.3333
08/03/06-27/03/06 | 1062 | 1676.8421
27/03/06-20/04/06 | 871 | 1136.087
20/04/06-18/05/06 | 460 | 492.8571
18/05/06-07/07/06 | 728 | 445.7143
Boilerhouse 2 2006-2007 | Energy (l) | Energy/30 days
07/07/06-19/09/06 | 641 | 267.0833
19/09/06-30/10/06 | 809 | 591.9512
30/10/06-17/11/06 | 809 | 1427.6471
17/11/06-27/12/06 | 1831 | 1373.25
Boilerhouse 3 2005-2006 | Energy (l) = Heating | Energy/30 days
13/10/05-21/11/2005 | 1203 | 949.7368
21/11/2005-07/12/05 | 976 | 1830
07/12/05-06/01/06 | 1311 | 1356.2069
06/01/06-02/02/06 | 1342 | 1548.4615
02/02/06-20/02/06 | 695 | 1158.3333
20/02/06-08/03/06 | 919 | 1531.6667
08/03/06-27/03/06 | 621 | 980.5263
27/03/06-20/04/06 | 904 | 1179.1304
20/04/06-18/05/06 | 246 | 263.5714
Boilerhouse 3 2006-2007 | Energy (l) = Heating | Energy/30 days
18/05/06-19/09/06 | 211 | 52.314
19/09/06-30/10/06 | 294 | 215.122
30/10/06-17/11/06 | 672 | 1185.8824
17/11/06-27/12/06 | 1367 | 1025.25

## power calculations
| Winter heating and hot water 05/06(dec-jan-fev-march) kJ | hot water (kJ) | heating alone | Electric non-heating appliances
Electricity | 1141466400
Kirchmichael | 972432432.4324
Nith-Cree | 229281931.0345
Boilerhouse 2 | 173990400
Boilerhouse 3 | 134908800
Total | 2652079963.4669 | 123549096 | 2528530867.4669
Average power (kW) | 255.7947 | 11.9164 | 243.8784 | 74.7083
Estimated peak hot water demand (kW) | 100.7554
UA (W/K) | 22563.9195
Estimated coldest day heating demand | 631.7897
Maximum instantaneous demand (kW) | 732.5452

## CO2 calculations
| Energy origin | Energy (kJ) | CO2 released (kg)
Electricity | Grid mix | 1683003600 | 269280.576
Kirchmichael | Oil | 1720741400 | 206488.968
Nith-Cree | Oil | 376104089.7098 | 45132.4908
Boilerhouse 2 | LPG | 292408491.5493 | 29240.8492
Boilerhouse 3 | LPG | 189138167.6056 | 18913.8168
Total |  | 4261395748.8647 | 569056.7007
ODT of wood required | 218.5331
Road distance (km) | 130
CO2 released (kg) if 100% woodchip heating | 14882.1052
| Energy type | Energy (GJ) | CO2 old system (tons) | CO2 new system (tons)
| Grid electricity | 1683.0036 | 269.2806 | 0
| Oil | 2096.8455 | 251.6215 | 22.9
| LPG | 481.5467 | 48.1547 | 0
| woodchips |  | 0 | 14.2