## Overview
High Rise with 80 flats | Description of Current Building
The building is simulated to be electrically heated, insulated to under 50mm, have single glazing and have an average natural ventilation rate of 0.75ach-1.
Description of Upgrade
Heating Demand Reduction Measures -
1. Insulation up to 300mm
2. Double Glazing
3. Decreased ventilation rate of 0.45ach-1
4. Smart temperature control system
Electricity Demand Reduction Measures -
1. 25% reduction in daytime electrity baseload to simulate energy efficiency appliances and lightbulbs
2. Peaks are clipped to around 1250W per household
CHP system
Hybrid CHP system which takes electricity from grid during peak conditions
System not designed to require exporting electricity to the grid
Uses 3 Baxi Dachs 5.34kWe CHP system
This spreadsheet covers the analysis for installing CHP to cover the hot water demand of a typical high rise building in Glasgow. It assumes that the high-rise has 80 flats, each around 65m2 and 1.5 person occupancy.
CHP unit - 5.34kWe, "off-the-shelf" technology, widely available in the UK

## Elec Profile
Electricity Profiles - simulating total for high rise (with peak sharing)
To simulate the electricity consumption patterns of each household, a daily profile has been assumed and repeated throughout the analysis year. It is taken as a standard European "low" profile (75%) and medium (25%) to represent an average household occupancy of 1.5.
Ref:
Electricity Profiles - Individual Household Examples

## Heating Profile
Space Heating Profile - simulating a typical high-rise flat of 65m2
Annual Household Energy consumption kWh
|  | Heating Req per flat - kWh | Boiler 65%
| Current | 6940.6956 | 10677.9933
| Insulated | 5755.6894 | 8854.9067
| Airtight | 3607.1521 | 5549.4648
| Extra Glazing | 2683.1811 | 4127.971
| Smart Heating | 2087.5461 | 3211.6094
| Condensing Boiler (85%) |  | 2455.9366
Daily Energy Consumption (kWh)
|  | Current | With Reduction
| Winter | 47.4814 | 19.5586
| Transition | 29.7119 | 8.2836
| Summer | 0 | 0

## HW Profile
Hot Water Profiles - normalised from US data
US values |  |  | UK household
|  |  | Households |  | 1 | 80
(gal/hr) | m3/hr | kW | hour | l/hour | kW | kW
1.7 | 0.00629 | 0.40169 | 0 | 1.2089 | 0.077201 | 6.1761
1.6 | 0.00592 | 0.37806 | 1 | 1.1378 | 0.07266 | 5.8128
1.6 | 0.00592 | 0.37806 | 2 | 1.1378 | 0.07266 | 5.8128
1.5 | 0.00555 | 0.35443 | 3 | 1.0667 | 0.068119 | 5.4495
1.5 | 0.00555 | 0.35443 | 4 | 1.0667 | 0.068119 | 5.4495
2.1 | 0.00777 | 0.4962 | 5 | 1.4933 | 0.095366 | 7.6293
3.3 | 0.01221 | 0.77974 | 6 | 2.3467 | 0.14986 | 11.9889
4.7 | 0.01739 | 1.1105 | 7 | 3.3422 | 0.21344 | 17.075
5.3 | 0.01961 | 1.2523 | 8 | 3.7689 | 0.24069 | 19.2548
5.2 | 0.01924 | 1.2287 | 9 | 3.6978 | 0.23614 | 18.8915
5.4 | 0.01998 | 1.2759 | 10 | 3.84 | 0.24523 | 19.6181
5.2 | 0.01924 | 1.2287 | 11 | 3.6978 | 0.23614 | 18.8915
5 | 0.0185 | 1.1814 | 12 | 3.5556 | 0.22706 | 18.1649
4.4 | 0.01628 | 1.0397 | 13 | 3.1289 | 0.19981 | 15.9851
4 | 0.0148 | 0.94514 | 14 | 2.8444 | 0.18165 | 14.532
4 | 0.0148 | 0.94514 | 15 | 2.8444 | 0.18165 | 14.532
4 | 0.0148 | 0.94514 | 16 | 2.8444 | 0.18165 | 14.532
4.5 | 0.01665 | 1.0633 | 17 | 3.2 | 0.20436 | 16.3484
5 | 0.0185 | 1.1814 | 18 | 3.5556 | 0.22706 | 18.1649
5 | 0.0185 | 1.1814 | 19 | 3.5556 | 0.22706 | 18.1649
5.3 | 0.01961 | 1.2523 | 20 | 3.7689 | 0.24069 | 19.2548
4.2 | 0.01554 | 0.9924 | 21 | 2.9867 | 0.19073 | 15.2585
3 | 0.0111 | 0.70886 | 22 | 2.1333 | 0.13624 | 10.899
2.5 | 0.00925 | 0.59072 | 23 | 1.7778 | 0.11353 | 9.0825
0.0037 | gal-m3 conversion
kWh
US daily total | 21.2658
US yearly total | 7761.9987
UK
Daily HW usage | 40 | l/person/day
household | 1.6 | persons
Daily household HW | 64 | l/day
Daily household P | 4.0871 | kWh
UK yearly total | 1491.7956 | kWh
Normalisation factor | 5.2031

## CHP spec
CHP Specification
| Size of CHP | 5.34 | kWe
| Efficiency Range | 79 - 92% |  |  | Max Electricity |  | 5.34 | kW
| Heat Output | 10.4 - 12.5 | kWth |  | Heat at full load |  | 12.5589 | kW
| Number of engines | 1
| Total elec capacity | 5.34 | kWe
Efficiency Curves
| Load | Thermal Efficiency | Electrical efficiency | Overall
| 0% | 80% | 0% | 80%
| 10% | 77.36% | 4.59% | 81.95%
| 20% | 74.94% | 8.76% | 83.7%
| 30% | 72.74% | 12.51% | 85.25%
| 40% | 70.76% | 15.84% | 86.6%
| 50% | 69% | 18.75% | 87.75%
| 60% | 67.46% | 21.24% | 88.7%
| 70% | 66.14% | 23.31% | 89.45%
| 80% | 65.04% | 24.96% | 90%
| 90% | 64.16% | 26.19% | 90.35%
| 100% | 63.5% | 27% | 90.5%
Curve Calculations
Electricity Curve
| Slope of Electricity |  | 0.48
| Degree of bend of electricity |  | 0.21
Overall Curve
| Heat Recovery |  | 0.8
| Slope of Overall |  | 0.205
| Degree of bend of Overall |  | 0.1
| Electrical Profile | CHP efficiencies |  |  | CHP output |  |  | Grid Electricity
Time step | Power Requirement | Thermal eff | Electrical Eff | Overall Eff | CHP Heat Supply | CHP Power Supply
0:00 | 12.72 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 7.38
0:05 | 12.696 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 7.356
0:10 | 13.032 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 7.692
0:15 | 13.416 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 8.076
0:20 | 13.344 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 8.004
0:25 | 12.504 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 7.164
0:30 | 12.432 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 7.092
0:35 | 12.816 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 7.476
0:40 | 10.368 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 5.028
0:45 | 9.072 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 3.732
0:50 | 8.496 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 3.156
0:55 | 8.256 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 2.916
1:00 | 7.248 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 1.908
1:05 | 7.224 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 1.884
1:10 | 7.416 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 2.076
1:15 | 7.008 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 1.668
1:20 | 6.768 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 1.428
1:25 | 6.96 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 1.62
1:30 | 6.912 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 1.572
1:35 | 6.696 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 1.356
1:40 | 6.912 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 1.572
1:45 | 6.936 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 1.596
1:50 | 6.816 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 1.476
1:55 | 6.816 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 1.476
2:00 | 6.816 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 1.476
2:05 | 6.48 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 1.14
2:10 | 6.48 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 1.14
2:15 | 5.904 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.564
2:20 | 5.52 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.18
2:25 | 5.808 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.468
2:30 | 5.832 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.492
2:35 | 6.216 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.876
2:40 | 6.192 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.852
2:45 | 6.144 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.804
2:50 | 5.88 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.54
2:55 | 5.52 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.18
3:00 | 6 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.66
3:05 | 5.544 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.204
3:10 | 5.544 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.204
3:15 | 5.904 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.564
3:20 | 5.832 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.492
3:25 | 4.848 | 0.6416 | 0.2619 | 0.9035 | 12.6894 | 5.1798 |  | 0
3:30 | 5.568 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.228
3:35 | 5.256 | 0.6416 | 0.2619 | 0.9035 | 12.6894 | 5.1798 |  | 0.0762
3:40 | 5.568 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.228
3:45 | 5.688 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.348
3:50 | 6.096 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.756
3:55 | 5.448 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.108
4:00 | 4.656 | 0.6504 | 0.2496 | 0.9 | 12.8635 | 4.9365 |  | 0
4:05 | 5.496 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.156
4:10 | 5.184 | 0.6416 | 0.2619 | 0.9035 | 12.6894 | 5.1798 |  | 0.0042
4:15 | 5.496 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.156
4:20 | 5.184 | 0.6416 | 0.2619 | 0.9035 | 12.6894 | 5.1798 |  | 0.0042
4:25 | 5.52 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.18
4:30 | 5.16 | 0.6416 | 0.2619 | 0.9035 | 12.6894 | 5.1798 |  | 0
4:35 | 5.76 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.42
4:40 | 5.52 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.18
4:45 | 5.448 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.108
4:50 | 5.832 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.492
4:55 | 5.28 | 0.6416 | 0.2619 | 0.9035 | 12.6894 | 5.1798 |  | 0.1002
5:00 | 5.256 | 0.6416 | 0.2619 | 0.9035 | 12.6894 | 5.1798 |  | 0.0762
5:05 | 5.208 | 0.6416 | 0.2619 | 0.9035 | 12.6894 | 5.1798 |  | 0.0282
5:10 | 5.256 | 0.6416 | 0.2619 | 0.9035 | 12.6894 | 5.1798 |  | 0.0762
5:15 | 5.208 | 0.6416 | 0.2619 | 0.9035 | 12.6894 | 5.1798 |  | 0.0282
5:20 | 5.736 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.396
5:25 | 5.64 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.3
5:30 | 5.976 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.636
5:35 | 5.664 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.324
5:40 | 5.904 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.564
5:45 | 5.256 | 0.6416 | 0.2619 | 0.9035 | 12.6894 | 5.1798 |  | 0.0762
5:50 | 4.992 | 0.6416 | 0.2619 | 0.9035 | 12.6894 | 5.1798 |  | 0
5:55 | 4.92 | 0.6416 | 0.2619 | 0.9035 | 12.6894 | 5.1798 |  | 0
6:00 | 5.232 | 0.6416 | 0.2619 | 0.9035 | 12.6894 | 5.1798 |  | 0.0522
6:05 | 4.872 | 0.6416 | 0.2619 | 0.9035 | 12.6894 | 5.1798 |  | 0
6:10 | 5.808 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.468
6:15 | 4.704 | 0.6504 | 0.2496 | 0.9 | 12.8635 | 4.9365 |  | 0
6:20 | 5.088 | 0.6416 | 0.2619 | 0.9035 | 12.6894 | 5.1798 |  | 0
6:25 | 5.952 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.612
6:30 | 7.156 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 1.816
6:35 | 5.376 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.036
6:40 | 5.64 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.3
6:45 | 6.576 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 1.236
6:50 | 6.336 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.996
6:55 | 4.662 | 0.6504 | 0.2496 | 0.9 | 12.8635 | 4.9365 |  | 0
7:00 | 5.328 | 0.6416 | 0.2619 | 0.9035 | 12.6894 | 5.1798 |  | 0.1482
7:05 | 5.328 | 0.6416 | 0.2619 | 0.9035 | 12.6894 | 5.1798 |  | 0.1482
7:10 | 5.652 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 0.312
7:15 | 9.831 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 4.491
7:20 | 12.675 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 7.335
7:25 | 10.224 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 4.884
7:30 | 10.692 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 5.352
7:35 | 11.682 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 6.342
7:40 | 9.936 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 4.596
7:45 | 9.324 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 3.984
7:50 | 8.622 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 3.282
7:55 | 10.482 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 5.142
8:00 | 7.668 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 2.328
8:05 | 8.244 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 2.904
8:10 | 10.623 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 5.283
8:15 | 9.363 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 4.023
8:20 | 9.666 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 4.326
8:25 | 9.018 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 3.678
8:30 | 8.766 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 3.426
8:35 | 8.514 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 3.174
8:40 | 9.414 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 4.074
8:45 | 8.604 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 3.264
8:50 | 8.874 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 3.534
8:55 | 9.342 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 4.002
9:00 | 11.196 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 5.856
9:05 | 9.81 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 4.47
9:10 | 10.206 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 4.866
9:15 | 11.196 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 5.856
9:20 | 12.441 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 7.101
9:25 | 13.107 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 7.767
9:30 | 10.638 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 5.298
9:35 | 10.926 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 5.586
9:40 | 10.314 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 4.974
9:45 | 11.145 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 5.805
9:50 | 10.944 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 5.604
9:55 | 10.371 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 5.031
10:00 | 13.38 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 8.04
10:05 | 13.665 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 8.325
10:10 | 14.298 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 8.958
10:15 | 12.603 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 7.263
10:20 | 11.451 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 6.111
10:25 | 13.509 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 8.169
10:30 | 12.282 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 6.942
10:35 | 13.992 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 8.652
10:40 | 14.283 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 8.943
10:45 | 11.829 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 6.489
10:50 | 11.325 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 5.985
10:55 | 12.981 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 7.641
11:00 | 12.423 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 7.083
11:05 | 11.955 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 6.615
11:10 | 13.545 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 8.205
11:15 | 16.134 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 10.794
11:20 | 11.466 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 6.126
11:25 | 9.162 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 3.822
11:30 | 12.672 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 7.332
11:35 | 11.883 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 6.543
11:40 | 12.081 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 6.741
11:45 | 9.792 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 4.452
11:50 | 12.459 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 7.119
11:55 | 12.549 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 7.209
12:00 | 13.593 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 8.253
12:05 | 12.153 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 6.813
12:10 | 11.886 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 6.546
12:15 | 12.426 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 7.086
12:20 | 11.49 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 6.15
12:25 | 10.101 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 4.761
12:30 | 9.723 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 4.383
12:35 | 10.662 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 5.322
12:40 | 8.715 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 3.375
12:45 | 11.001 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 5.661
12:50 | 8.838 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 3.498
12:55 | 11.772 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 6.432
13:00 | 10.209 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 4.869
13:05 | 12.027 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 6.687
13:10 | 13.809 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 8.469
13:15 | 11.343 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 6.003
13:20 | 12.279 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 6.939
13:25 | 10.245 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 4.905
13:30 | 11.073 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 5.733
13:35 | 11.127 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 5.787
13:40 | 11.574 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 6.234
13:45 | 9.486 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 4.146
13:50 | 9.738 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 4.398
13:55 | 9.9 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 4.56
14:00 | 10.296 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 4.956
14:05 | 9.18 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 3.84
14:10 | 9.849 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 4.509
14:15 | 10.044 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 4.704
14:20 | 11.937 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 6.597
14:25 | 11.451 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 6.111
14:30 | 11.649 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 6.309
14:35 | 13.254 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 7.914
14:40 | 12.948 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 7.608
14:45 | 13.47 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 8.13
14:50 | 13.47 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 8.13
14:55 | 12.246 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 6.906
15:00 | 12.318 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 6.978
15:05 | 11.148 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 5.808
15:10 | 9.561 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 4.221
15:15 | 11.544 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 6.204
15:20 | 10.641 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 5.301
15:25 | 8.553 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 3.213
15:30 | 10.119 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 4.779
15:35 | 9.918 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 4.578
15:40 | 14.964 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 9.624
15:45 | 14.583 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 9.243
15:50 | 13.917 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 8.577
15:55 | 15.594 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 10.254
16:00 | 17.412 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 12.072
16:05 | 12.729 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 7.389
16:10 | 11.739 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 6.399
16:15 | 11.055 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 5.715
16:20 | 11.739 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 6.399
16:25 | 10.803 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 5.463
16:30 | 10.497 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 5.157
16:35 | 9.741 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 4.401
16:40 | 9.111 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 3.771
16:45 | 10.101 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 4.761
16:50 | 12.081 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 6.741
16:55 | 10.407 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 5.067
17:00 | 10.062 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 4.722
17:05 | 9.936 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 4.596
17:10 | 10.788 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 5.448
17:15 | 10.731 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 5.391
17:20 | 11.49 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 6.15
17:25 | 12.174 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 6.834
17:30 | 12.03 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 6.69
17:35 | 13.365 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 8.025
17:40 | 11.544 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 6.204
17:45 | 14.046 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 8.706
17:50 | 12.066 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 6.726
17:55 | 12.12 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 6.78
18:00 | 12.858 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 7.518
18:05 | 16.101 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 10.761
18:10 | 14.871 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 9.531
18:15 | 13.017 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 7.677
18:20 | 14.313 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 8.973
18:25 | 16.08 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 10.74
18:30 | 15.177 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 9.837
18:35 | 13.86 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 8.52
18:40 | 13.683 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 8.343
18:45 | 15.501 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 10.161
18:50 | 13.503 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 8.163
18:55 | 12.891 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 7.551
19:00 | 13.866 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 8.526
19:05 | 12.6 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 7.26
19:10 | 13.053 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 7.713
19:15 | 13.503 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 8.163
19:20 | 13.2 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 7.86
19:25 | 11.811 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 6.471
19:30 | 13.557 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 8.217
19:35 | 14.565 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 9.225
19:40 | 12.456 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 7.116
19:45 | 14.742 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 9.402
19:50 | 17.373 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 12.033
19:55 | 15.681 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 10.341
20:00 | 14.868 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 9.528
20:05 | 16.326 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 10.986
20:10 | 14.976 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 9.636
20:15 | 17.013 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 11.673
20:20 | 17.661 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 12.321
20:25 | 15.498 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 10.158
20:30 | 16.326 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 10.986
20:35 | 14.778 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 9.438
20:40 | 15.21 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 9.87
20:45 | 15.246 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 9.906
20:50 | 17.496 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 12.156
20:55 | 19.317 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 13.977
21:00 | 17.424 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 12.084
21:05 | 16.452 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 11.112
21:10 | 15.3 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 9.96
21:15 | 16.848 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 11.508
21:20 | 14.724 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 9.384
21:25 | 14.076 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 8.736
21:30 | 14.94 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 9.6
21:35 | 14.706 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 9.366
21:40 | 14.85 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 9.51
21:45 | 13.896 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 8.556
21:50 | 13.644 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 8.304
21:55 | 14.94 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 9.6
22:00 | 15.915 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 10.575
22:05 | 14.184 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 8.844
22:10 | 15.642 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 10.302
22:15 | 14.274 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 8.934
22:20 | 13.014 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 7.674
22:25 | 13.572 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 8.232
22:30 | 14.472 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 9.132
22:35 | 16.236 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 10.896
22:40 | 17.661 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 12.321
22:45 | 15.462 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 10.122
22:50 | 15.462 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 10.122
22:55 | 16.545 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 11.205
23:00 | 14.67 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 9.33
23:05 | 15.102 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 9.762
23:10 | 16.542 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 11.202
23:15 | 15.231 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 9.891
23:20 | 13.572 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 8.232
23:25 | 12.636 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 7.296
23:30 | 12.564 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 7.224
23:35 | 12.204 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 6.864
23:40 | 11.736 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 6.396
23:45 | 11.124 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 5.784
23:50 | 10.44 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 5.1
23:55 | 10.638 | 0.635 | 0.27 | 0.905 | 12.5589 | 5.34 |  | 5.298

## CHP&HW results
CHP Sizing and Results
|  | Daily Heat Balance |  |  |  | KWh per Day | Tank Sizer
| Total | -25.0334 | kWh | Deficit | CHP Supply | 301.9355 | Energy Storage required | 40 | kWh
| Percentage | -8.291% | Heat | Deficit | Hot Water Requirements | 326.9689 | Time taken | 7 | h
| Total Tank Size | 0.78295 | m3 |  | Heat Wasted | -25.0334 | Power Addition Rate | 5.7143 | kW
[7 empty] | Mass addition rate | 0.024856 | kg/s
[7 empty] | Capacity req | 626.3593 | kg
[7 empty] | volume | 0.78295 | m3
DATA
Daily Heat Usage |  | CHP supply |  |  | Hot Water Requirements |  | Total Heat Usage
Time step | Power Requirement | Thermal eff | Heat Supply kW | Cumulative kWh | Heat req kW | Cumulative kWh | kWh
0 | 11.596 | 0.635 | 12.5589 | 12.5589 | -6.1761 | -6.1761 | 6.3828
1 | 6.976 | 0.635 | 12.5589 | 25.1178 | -5.8128 | -11.9889 | 13.1289
2 | 6.066 | 0.635 | 12.5589 | 37.6767 | -5.8128 | -17.8016 | 19.875
3 | 5.608 | 0.635 | 12.5589 | 50.2356 | -5.4495 | -23.2511 | 26.9844
4 | 5.378 | 0.635 | 12.5589 | 62.7944 | -5.4495 | -28.7006 | 34.0938
5 | 5.418 | 0.635 | 12.5589 | 75.3533 | -7.6293 | -36.3299 | 39.0235
6 | 5.6168 | 0.635 | 12.5589 | 87.9122 | -11.9889 | -48.3187 | 39.5935
7 | 4.0865 | 0.6614 | 13.081 | 100.9932 | -17.075 | -65.3938 | 35.5995
8 | 9.008 | 0.635 | 12.5589 | 113.5521 | -19.2548 | -84.6486 | 28.9035
9 | 11.0245 | 0.635 | 12.5589 | 126.111 | -18.8915 | -103.5401 | 22.5709
10 | 12.9665 | 0.635 | 12.5589 | 138.6699 | -19.6181 | -123.1583 | 15.5116
11 | 12.1768 | 0.635 | 12.5589 | 151.2288 | -18.8915 | -142.0498 | 9.179
12 | 11.03 | 0.635 | 12.5589 | 163.7877 | -18.1649 | -160.2148 | 3.5729
13 | 11.0675 | 0.635 | 12.5589 | 176.3466 | -15.9851 | -176.1999 | 0.14668
14 | 11.6495 | 0.635 | 12.5589 | 188.9055 | -14.532 | -190.7319 | -1.8264
15 | 11.905 | 0.635 | 12.5589 | 201.4644 | -14.532 | -205.2638 | -3.7994
16 | 11.4512 | 0.635 | 12.5589 | 214.0232 | -14.532 | -219.7958 | -5.7725
17 | 11.696 | 0.635 | 12.5589 | 226.5821 | -16.3484 | -236.1442 | -9.5621
18 | 14.3212 | 0.635 | 12.5589 | 239.141 | -18.1649 | -254.3091 | -15.1681
19 | 13.8673 | 0.635 | 12.5589 | 251.6999 | -18.1649 | -272.4741 | -20.7742
20 | 16.2263 | 0.635 | 12.5589 | 264.2588 | -19.2548 | -291.7289 | -27.4701
21 | 15.15 | 0.635 | 12.5589 | 276.8177 | -15.2585 | -306.9875 | -30.1698
22 | 15.2033 | 0.635 | 12.5589 | 289.3766 | -10.899 | -317.8864 | -28.5098
23 | 14.67 | 0.635 | 12.5589 | 301.9355 | -9.0825 | -326.9689 | -25.0334
25.0334

## Summary
Energy Use Summary
Energy Savings
[6 empty] | New Heating Load | 167003.69 | kWh
Reducing Heating Costs |  |  | Energy Use |  |  | Heating Savings | 388251.96 | kWh
Original Heating Load | 555255.65 | kWh | Original Heating Load | 555255.65 | kWh | Hot Water Demand | 119343.6444 | kWh
New Heating Load | 167003.69 | kWh | Hot Water | 119343.6444 | kWh | Electrical Savings | 37357.7196 | kWh
|  |  | Original Electrical Load | 130990.47 | kWh | CHP Electricity | 46653.8742 | kWh
Savings | 388251.96 | kWh |  |  |  | Grid Electricity | 48187.6292 | kWh
Savings % | 69.92% |  |  |  |  | % savings | 67.5%
Reducing Electrical Load
Original Electrical Load | 130990.47 | kWh
New Electrical Load | 93632.7504 | kWh
Savings | 37357.7196 | kWh
Savings % | 28.52%
CHP
Hot Water Demand | 119343.6444 | kWh
Hot Water Supply | 110206.4453
Waste Heat | -8.291%
CHP Electricity | 46653.8742 | kWh
Grid Electricity | 48187.6292 | kWh
Unused Electricity | 1208.7529 | kWh
% CHP electricity | 48.57%
Average CHP % | 90.49%
Average elec CHP % | 26.93%
Carbon Savings
Embodied CO2
Natural Gas | 0.206 | kg/kWh
Electricity | 0.562 | kg/kWh
Carbon Savings | Tonnes saved/year
Reducing Heating Demand | 218.1976
Reducing Electrical Demand | 20.995
CHP for Hot Water and Electricity | 81.99
CHP embodied CO2 | 37.7027
Grid Embodied CO2 | 52.6216
Tonnes saved/year | Original Building | New Building
Heating | 312.0537 | 93.8561
Electricity | 73.6166 | 27.0814
CHP | 67.0711 | 35.6902
| 452.7414 | 156.6277
Reduction |  | 65.4%

## Cost
Fuel Poverty Study
| Fuel Costs |  |  |  | NHER | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
| Natural Gas | 0.04 | p/kWh |  | Weekly Fuel Costs* 60m2 flat | 28.85 | 21.15 | 16.34 | 13.46 | 11.54 | 10.58 | 9.62 | 8.65 | 7.69 | 6.73 | 5.77
| Electricity | 0.14 | p/kWh
[5 empty] | Scenario | 0: Cost/week; 1: NHER
| Running Costs |  |  | 1 | Original | 0: 27.1112; 1: 0.22582
| Original Heating | 77735.791 | £/annum | 2 | Just Insulation | 0: 14.045; 1: 2.7969
| Heat demand reduction | 23380.5166 | £/annum | 3 | Just CHP for central heating | 0: 21.015; 1: 1.0281
|  |  |  | 4 | Just CHP for Hot Water | 0: 22.0863; 1: 0.87841
| Original Electricity | 18338.6658 | £/annum | 5 | Insulation and CHP for Hot Water | 0: 9.0201; 1: 6.6184
| New Grid Electricity | 6746.2681 | £/annum
Cost Assumptions
| Hot Water | 16708.1102 | £/annum |  | High-rise Insulation | 0: Cost Saving; 1: Capital Cost
| New Hot Water | 0 | £/annum |  | Cavity wall + loft insulation | 0: 13224.6697; 1: 64000
[5 empty] | Double glazing + Draught Proofing | 0: 34289.1921; 1: 200000
| CHP maintenance coeff | 0.006 | £/kWh |  | Heating Controls Upgrade | 0: 8400; 1: 8000
| CHP fuel | 7109.6858 | £/annum |  | Total | 0: 55913.8618; 1: 272000
| CHP maintenance | 287.1758 | £/annum
| CHP Total Cost | 7396.8616 | £/annum |  | CHP for Central Heating | 0: per flat; 1: total
[5 empty] | Upgraded gas supply | 0: 150; 1: 12000
| Per Flat Savings |  |  |  | Upgraded electricity controls | 0: 250; 1: 20000
| Heating Savings | 679.4409 | £/annum |  | Installation Cost in building | 0: 400; 1: 32000
| Hot Water & Elec Savings | 261.2956 | £/annum |  | 10 Baxi CHP | 0: 1625; 1: 130000
[5 empty] | Central Heating Installation | 0: 2000; 1: 160000
| CHP for Hot Water | per flat | total |  | Total | 0: 4425; 1: 354000
| Upgraded gas supply | 150 | 12000
| Upgraded electricity controls | 250 | 20000 |  | CHP for Central Heating
| Installation Cost in building | 400 | 32000 |  | Energy Saved (per highrise_ | 0: 166; 1: tonnes
| 1 Baxi CHP | 162.5 | 13000 |  | Cost Saving | 0: 317; 1: per highrise
| Total | 962.5 | 77000 |  | Payback | 0: 13.959; 1: years
Capital Investment Analysis
| Scenario | Capital Cost | Payback Period
1 | Original
2 | Just Insulation | 3400 | 4.8646
3 | Just CHP for central heating | 4425 | 13.959
4 | Just CHP for Hot Water | 962.5 | 3.6836
5 | Insulation and CHP for Hot Water | 4362.5 | 4.6373
Sustainability for Glasgow Analysis | bar: 3 to 10
| Number of Highrise households in Glasgow | 12000 | bar: 3 to 10
| Scenario | Investment | Payback Period |  | Annual Savings | 0: Carbon Saved (tonnes); 1: Carbon Investment
1 | Original
2 | Just Insulation | 40800000 | 4.8646 |  | 8153291.16 | 0: 32729.6402; 1: 1246.5765
3 | Just CHP for central heating | 53100000 | 13.959 |  | 3804000 | 0: 24900; 1: 2132.5301
4 | Just CHP for Hot Water | 11550000 | 3.6836 |  | 3135546.9538 | 0: 15447.7586; 1: 747.6813
5 | Insulation and CHP for Hot Water | 52350000 | 4.6373 |  | 11288838.1138 | 0: 48177.3988; 1: 1086.6091

## Elec Data
Wh Energy consumption for 4 typical January Weeks (every 5mins reading) | [20 empty] | Wh Energy consumption for 4 typical December Weeks (every 5mins reading) | [19 empty] | Original W Power consumption for 4 typical January Weeks (Each a 5min time period) | [20 empty] | Original W Power consumption for 4 typical December Weeks (Each a 5min time period) | [19 empty] | 1250 | New W Power consumption for 4 typical January Weeks (1000W max) | [47 empty] | Sum of 36 houses |  | 80 Houses
| mon | tue | wed | thu | fri | mon | tue | wed | thu | fri | mon | tue | wed | thu | fri | mon | tue | wed | thu | fri | mon | tue | wed | thu | fri | mon | tue | wed | thu | fri | mon | tue | wed | thu | fri | mon | tue | wed | thu | fri |  | mon | tue | wed | thu | fri | mon | tue | wed | thu | fri | mon | tue | wed | thu | fri | mon | tue | wed | thu | fri | mon | tue | wed | thu | fri | mon | tue | wed | thu | fri | mon | tue | wed | thu | fri | mon | tue | wed | thu | fri |  |  | mon | tue | wed | thu | fri |  | mon | tue | wed | thu | fri |  | mon | tue | wed | thu | fri |  | mon | tue | wed | thu | fri |  | mon | tue | wed | thu | fri |  | mon | tue | wed | thu | fri |  | mon | tue | wed | thu | fri |  | mon | tue | wed | thu | fri | Original | New | Original | New |  |  |  | Original-Total | New-Total
0:00 | 15 | 15 | 23 | 28 | 6 | 8 | 24 | 0 | 0 | 11 | 0 | 20 | 27 | 22 | 23 | 1 | 22 | 0 | 0 | 7 | 32 | 15 | 15 | 2 | 24 | 17 | 7 | 20 | 20 | 3 | 5 | 16 | 5 | 25 | 18 | 20 | 4 | 4 | 9 | 17 | 0:00 | 180 | 180 | 276 | 336 | 72 | 96 | 288 | 0 | 0 | 132 | 0 | 240 | 324 | 264 | 276 | 12 | 264 | 0 | 0 | 84 | 384 | 180 | 180 | 24 | 288 | 204 | 84 | 240 | 240 | 36 | 60 | 192 | 60 | 300 | 216 | 240 | 48 | 48 | 108 | 204 |  | 0:00 | 180 | 180 | 276 | 336 | 72 |  | 96 | 288 | 0 | 0 | 132 |  | 0 | 240 | 324 | 264 | 276 |  | 12 | 264 | 0 | 0 | 84 |  | 384 | 180 | 180 | 24 | 288 |  | 204 | 84 | 240 | 240 | 36 |  | 60 | 192 | 60 | 300 | 216 |  | 240 | 48 | 48 | 108 | 204 | 6360 | 6360 | 12720 | 12720 | 12.72 | 12.72 | 0 | 11596 | 11596 | 11.596 | 11.596
0:05 | 15 | 15 | 22 | 28 | 7 | 4 | 24 | 0 | 0 | 10 | 10 | 20 | 24 | 22 | 24 | 2 | 30 | 0 | 0 | 7 | 31 | 15 | 14 | 3 | 24 | 15 | 9 | 29 | 20 | 2 | 5 | 7 | 5 | 17 | 17 | 20 | 3 | 4 | 9 | 16 | 0:05 | 180 | 180 | 264 | 336 | 84 | 48 | 288 | 0 | 0 | 120 | 120 | 240 | 288 | 264 | 288 | 24 | 360 | 0 | 0 | 84 | 372 | 180 | 168 | 36 | 288 | 180 | 108 | 348 | 240 | 24 | 60 | 84 | 60 | 204 | 204 | 240 | 36 | 48 | 108 | 192 |  | 0:05 | 180 | 180 | 264 | 336 | 84 |  | 48 | 288 | 0 | 0 | 120 |  | 120 | 240 | 288 | 264 | 288 |  | 24 | 360 | 0 | 0 | 84 |  | 372 | 180 | 168 | 36 | 288 |  | 180 | 108 | 348 | 240 | 24 |  | 60 | 84 | 60 | 204 | 204 |  | 240 | 36 | 48 | 108 | 192 | 6348 | 6348 | 12696 | 12696 | 12.696 | 12.696 | 1 | 6976 | 6976 | 6.976 | 6.976
0:10 | 20 | 18 | 22 | 27 | 6 | 2 | 24 | 0 | 0 | 15 | 16 | 23 | 23 | 22 | 23 | 2 | 29 | 0 | 0 | 7 | 29 | 15 | 15 | 2 | 23 | 14 | 5 | 29 | 20 | 3 | 5 | 4 | 17 | 14 | 16 | 20 | 4 | 5 | 9 | 15 | 0:10 | 240 | 216 | 264 | 324 | 72 | 24 | 288 | 0 | 0 | 180 | 192 | 276 | 276 | 264 | 276 | 24 | 348 | 0 | 0 | 84 | 348 | 180 | 180 | 24 | 276 | 168 | 60 | 348 | 240 | 36 | 60 | 48 | 204 | 168 | 192 | 240 | 48 | 60 | 108 | 180 |  | 0:10 | 240 | 216 | 264 | 324 | 72 |  | 24 | 288 | 0 | 0 | 180 |  | 192 | 276 | 276 | 264 | 276 |  | 24 | 348 | 0 | 0 | 84 |  | 348 | 180 | 180 | 24 | 276 |  | 168 | 60 | 348 | 240 | 36 |  | 60 | 48 | 204 | 168 | 192 |  | 240 | 48 | 60 | 108 | 180 | 6516 | 6516 | 13032 | 13032 | 13.032 | 13.032 | 2 | 6066 | 6066 | 6.066 | 6.066
0:15 | 23 | 15 | 22 | 28 | 7 | 1 | 25 | 0 | 0 | 20 | 10 | 29 | 24 | 15 | 24 | 2 | 28 | 0 | 0 | 7 | 23 | 15 | 15 | 2 | 24 | 15 | 2 | 28 | 20 | 2 | 13 | 4 | 17 | 15 | 17 | 18 | 3 | 11 | 19 | 16 | 0:15 | 276 | 180 | 264 | 336 | 84 | 12 | 300 | 0 | 0 | 240 | 120 | 348 | 288 | 180 | 288 | 24 | 336 | 0 | 0 | 84 | 276 | 180 | 180 | 24 | 288 | 180 | 24 | 336 | 240 | 24 | 156 | 48 | 204 | 180 | 204 | 216 | 36 | 132 | 228 | 192 |  | 0:15 | 276 | 180 | 264 | 336 | 84 |  | 12 | 300 | 0 | 0 | 240 |  | 120 | 348 | 288 | 180 | 288 |  | 24 | 336 | 0 | 0 | 84 |  | 276 | 180 | 180 | 24 | 288 |  | 180 | 24 | 336 | 240 | 24 |  | 156 | 48 | 204 | 180 | 204 |  | 216 | 36 | 132 | 228 | 192 | 6708 | 6708 | 13416 | 13416 | 13.416 | 13.416 | 3 | 5608 | 5608 | 5.608 | 5.608
0:20 | 23 | 22 | 22 | 23 | 6 | 2 | 35 | 0 | 0 | 19 | 2 | 28 | 23 | 15 | 23 | 1 | 27 | 0 | 0 | 7 | 23 | 15 | 14 | 3 | 23 | 14 | 1 | 28 | 20 | 3 | 17 | 4 | 16 | 15 | 16 | 10 | 4 | 17 | 21 | 14 | 0:20 | 276 | 264 | 264 | 276 | 72 | 24 | 420 | 0 | 0 | 228 | 24 | 336 | 276 | 180 | 276 | 12 | 324 | 0 | 0 | 84 | 276 | 180 | 168 | 36 | 276 | 168 | 12 | 336 | 240 | 36 | 204 | 48 | 192 | 180 | 192 | 120 | 48 | 204 | 252 | 168 |  | 0:20 | 276 | 264 | 264 | 276 | 72 |  | 24 | 420 | 0 | 0 | 228 |  | 24 | 336 | 276 | 180 | 276 |  | 12 | 324 | 0 | 0 | 84 |  | 276 | 180 | 168 | 36 | 276 |  | 168 | 12 | 336 | 240 | 36 |  | 204 | 48 | 192 | 180 | 192 |  | 120 | 48 | 204 | 252 | 168 | 6672 | 6672 | 13344 | 13344 | 13.344 | 13.344 | 4 | 5378 | 5378 | 5.378 | 5.378
0:25 | 23 | 14 | 23 | 20 | 7 | 3 | 31 | 0 | 0 | 18 | 2 | 28 | 23 | 14 | 23 | 2 | 20 | 0 | 0 | 7 | 23 | 15 | 14 | 2 | 23 | 11 | 2 | 27 | 22 | 2 | 16 | 3 | 16 | 16 | 16 | 8 | 7 | 16 | 20 | 4 | 0:25 | 276 | 168 | 276 | 240 | 84 | 36 | 372 | 0 | 0 | 216 | 24 | 336 | 276 | 168 | 276 | 24 | 240 | 0 | 0 | 84 | 276 | 180 | 168 | 24 | 276 | 132 | 24 | 324 | 264 | 24 | 192 | 36 | 192 | 192 | 192 | 96 | 84 | 192 | 240 | 48 |  | 0:25 | 276 | 168 | 276 | 240 | 84 |  | 36 | 372 | 0 | 0 | 216 |  | 24 | 336 | 276 | 168 | 276 |  | 24 | 240 | 0 | 0 | 84 |  | 276 | 180 | 168 | 24 | 276 |  | 132 | 24 | 324 | 264 | 24 |  | 192 | 36 | 192 | 192 | 192 |  | 96 | 84 | 192 | 240 | 48 | 6252 | 6252 | 12504 | 12504 | 12.504 | 12.504 | 5 | 5418 | 5418 | 5.418 | 5.418
0:30 | 27 | 14 | 22 | 20 | 6 | 11 | 30 | 0 | 0 | 19 | 1 | 28 | 24 | 6 | 23 | 2 | 25 | 0 | 5 | 7 | 11 | 15 | 7 | 3 | 24 | 0 | 1 | 28 | 29 | 3 | 16 | 4 | 15 | 16 | 16 | 8 | 15 | 16 | 16 | 5 | 0:30 | 324 | 168 | 264 | 240 | 72 | 132 | 360 | 0 | 0 | 228 | 12 | 336 | 288 | 72 | 276 | 24 | 300 | 0 | 60 | 84 | 132 | 180 | 84 | 36 | 288 | 0 | 12 | 336 | 348 | 36 | 192 | 48 | 180 | 192 | 192 | 96 | 180 | 192 | 192 | 60 |  | 0:30 | 324 | 168 | 264 | 240 | 72 |  | 132 | 360 | 0 | 0 | 228 |  | 12 | 336 | 288 | 72 | 276 |  | 24 | 300 | 0 | 60 | 84 |  | 132 | 180 | 84 | 36 | 288 |  | 0 | 12 | 336 | 348 | 36 |  | 192 | 48 | 180 | 192 | 192 |  | 96 | 180 | 192 | 192 | 60 | 6216 | 6216 | 12432 | 12432 | 12.432 | 12.432 | 6 | 5750 | 5616.8333 | 12 | 12.02
0:35 | 22 | 9 | 22 | 21 | 7 | 9 | 24 | 0 | 0 | 18 | 3 | 28 | 23 | 1 | 18 | 2 | 14 | 0 | 10 | 8 | 2 | 20 | 3 | 2 | 24 | 0 | 2 | 27 | 28 | 2 | 16 | 4 | 13 | 79 | 16 | 8 | 15 | 15 | 14 | 5 | 0:35 | 264 | 108 | 264 | 252 | 84 | 108 | 288 | 0 | 0 | 216 | 36 | 336 | 276 | 12 | 216 | 24 | 168 | 0 | 120 | 96 | 24 | 240 | 36 | 24 | 288 | 0 | 24 | 324 | 336 | 24 | 192 | 48 | 156 | 948 | 192 | 96 | 180 | 180 | 168 | 60 |  | 0:35 | 264 | 108 | 264 | 252 | 84 |  | 108 | 288 | 0 | 0 | 216 |  | 36 | 336 | 276 | 12 | 216 |  | 24 | 168 | 0 | 120 | 96 |  | 24 | 240 | 36 | 24 | 288 |  | 0 | 24 | 324 | 336 | 24 |  | 192 | 48 | 156 | 948 | 192 |  | 96 | 180 | 180 | 168 | 60 | 6408 | 6408 | 12816 | 12816 | 12.816 | 12.816 | 7 | 5542 | 4086.5 | 12.2 | 12.03
0:40 | 20 | 9 | 16 | 16 | 7 | 9 | 24 | 0 | 3 | 18 | 11 | 27 | 25 | 2 | 16 | 1 | 9 | 0 | 9 | 6 | 3 | 24 | 2 | 3 | 24 | 0 | 1 | 22 | 27 | 3 | 16 | 8 | 4 | 24 | 7 | 8 | 15 | 5 | 4 | 4 | 0:40 | 240 | 108 | 192 | 192 | 84 | 108 | 288 | 0 | 36 | 216 | 132 | 324 | 300 | 24 | 192 | 12 | 108 | 0 | 108 | 72 | 36 | 288 | 24 | 36 | 288 | 0 | 12 | 264 | 324 | 36 | 192 | 96 | 48 | 288 | 84 | 96 | 180 | 60 | 48 | 48 |  | 0:40 | 240 | 108 | 192 | 192 | 84 |  | 108 | 288 | 0 | 36 | 216 |  | 132 | 324 | 300 | 24 | 192 |  | 12 | 108 | 0 | 108 | 72 |  | 36 | 288 | 24 | 36 | 288 |  | 0 | 12 | 264 | 324 | 36 |  | 192 | 96 | 48 | 288 | 84 |  | 96 | 180 | 60 | 48 | 48 | 5184 | 5184 | 10368 | 10368 | 10.368 | 10.368 | 8 | 12064 | 9008 | 12.064 | 9.008
0:45 | 14 | 9 | 15 | 4 | 16 | 9 | 15 | 0 | 11 | 18 | 11 | 28 | 3 | 2 | 16 | 2 | 8 | 0 | 9 | 1 | 3 | 22 | 3 | 2 | 24 | 0 | 2 | 19 | 14 | 2 | 7 | 16 | 5 | 26 | 6 | 8 | 15 | 5 | 3 | 5 | 0:45 | 168 | 108 | 180 | 48 | 192 | 108 | 180 | 0 | 132 | 216 | 132 | 336 | 36 | 24 | 192 | 24 | 96 | 0 | 108 | 12 | 36 | 264 | 36 | 24 | 288 | 0 | 24 | 228 | 168 | 24 | 84 | 192 | 60 | 312 | 72 | 96 | 180 | 60 | 36 | 60 |  | 0:45 | 168 | 108 | 180 | 48 | 192 |  | 108 | 180 | 0 | 132 | 216 |  | 132 | 336 | 36 | 24 | 192 |  | 24 | 96 | 0 | 108 | 12 |  | 36 | 264 | 36 | 24 | 288 |  | 0 | 24 | 228 | 168 | 24 |  | 84 | 192 | 60 | 312 | 72 |  | 96 | 180 | 60 | 36 | 60 | 4536 | 4536 | 9072 | 9072 | 9.072 | 9.072 | 9 | 14932 | 11024.5 | 14.932 | 11.0245
0:50 | 13 | 10 | 15 | 0 | 14 | 9 | 15 | 0 | 10 | 17 | 10 | 27 | 0 | 1 | 16 | 2 | 1 | 0 | 9 | 0 | 3 | 22 | 3 | 3 | 24 | 0 | 1 | 20 | 11 | 3 | 5 | 15 | 5 | 26 | 5 | 16 | 10 | 5 | 3 | 5 | 0:50 | 156 | 120 | 180 | 0 | 168 | 108 | 180 | 0 | 120 | 204 | 120 | 324 | 0 | 12 | 192 | 24 | 12 | 0 | 108 | 0 | 36 | 264 | 36 | 36 | 288 | 0 | 12 | 240 | 132 | 36 | 60 | 180 | 60 | 312 | 60 | 192 | 120 | 60 | 36 | 60 |  | 0:50 | 156 | 120 | 180 | 0 | 168 |  | 108 | 180 | 0 | 120 | 204 |  | 120 | 324 | 0 | 12 | 192 |  | 24 | 12 | 0 | 108 | 0 |  | 36 | 264 | 36 | 36 | 288 |  | 0 | 12 | 240 | 132 | 36 |  | 60 | 180 | 60 | 312 | 60 |  | 192 | 120 | 60 | 36 | 60 | 4248 | 4248 | 8496 | 8496 | 8.496 | 8.496 | 10 | 21910 | 12966.5 | 21.91 | 12.9665
0:55 | 8 | 9 | 15 | 0 | 15 | 9 | 15 | 4 | 9 | 15 | 10 | 19 | 0 | 2 | 16 | 2 | 0 | 0 | 8 | 0 | 3 | 22 | 2 | 2 | 24 | 0 | 2 | 15 | 10 | 2 | 5 | 15 | 5 | 25 | 5 | 21 | 4 | 5 | 4 | 17 | 0:55 | 96 | 108 | 180 | 0 | 180 | 108 | 180 | 48 | 108 | 180 | 120 | 228 | 0 | 24 | 192 | 24 | 0 | 0 | 96 | 0 | 36 | 264 | 24 | 24 | 288 | 0 | 24 | 180 | 120 | 24 | 60 | 180 | 60 | 300 | 60 | 252 | 48 | 60 | 48 | 204 |  | 0:55 | 96 | 108 | 180 | 0 | 180 |  | 108 | 180 | 48 | 108 | 180 |  | 120 | 228 | 0 | 24 | 192 |  | 24 | 0 | 0 | 96 | 0 |  | 36 | 264 | 24 | 24 | 288 |  | 0 | 24 | 180 | 120 | 24 |  | 60 | 180 | 60 | 300 | 60 |  | 252 | 48 | 60 | 48 | 204 | 4128 | 4128 | 8256 | 8256 | 8.256 | 8.256 | 11 | 17988 | 12176.75 | 17.988 | 12.1768
1:00 | 0 | 2 | 5 | 0 | 14 | 8 | 14 | 10 | 10 | 10 | 9 | 19 | 0 | 2 | 16 | 1 | 0 | 1 | 9 | 0 | 3 | 21 | 3 | 2 | 24 | 0 | 1 | 5 | 8 | 3 | 6 | 14 | 5 | 26 | 5 | 19 | 3 | 5 | 3 | 16 | 1:00 | 0 | 24 | 60 | 0 | 168 | 96 | 168 | 120 | 120 | 120 | 108 | 228 | 0 | 24 | 192 | 12 | 0 | 12 | 108 | 0 | 36 | 252 | 36 | 24 | 288 | 0 | 12 | 60 | 96 | 36 | 72 | 168 | 60 | 312 | 60 | 228 | 36 | 60 | 36 | 192 |  | 1:00 | 0 | 24 | 60 | 0 | 168 |  | 96 | 168 | 120 | 120 | 120 |  | 108 | 228 | 0 | 24 | 192 |  | 12 | 0 | 12 | 108 | 0 |  | 36 | 252 | 36 | 24 | 288 |  | 0 | 12 | 60 | 96 | 36 |  | 72 | 168 | 60 | 312 | 60 |  | 228 | 36 | 60 | 36 | 192 | 3624 | 3624 | 7248 | 7248 | 7.248 | 7.248 | 12 | 17742 | 11030 | 17.742 | 11.03
1:05 | 0 | 1 | 2 | 0 | 14 | 8 | 9 | 10 | 9 | 10 | 10 | 20 | 0 | 2 | 15 | 2 | 0 | 11 | 8 | 0 | 3 | 21 | 3 | 3 | 29 | 0 | 0 | 2 | 3 | 2 | 5 | 15 | 4 | 23 | 9 | 19 | 4 | 5 | 4 | 16 | 1:05 | 0 | 12 | 24 | 0 | 168 | 96 | 108 | 120 | 108 | 120 | 120 | 240 | 0 | 24 | 180 | 24 | 0 | 132 | 96 | 0 | 36 | 252 | 36 | 36 | 348 | 0 | 0 | 24 | 36 | 24 | 60 | 180 | 48 | 276 | 108 | 228 | 48 | 60 | 48 | 192 |  | 1:05 | 0 | 12 | 24 | 0 | 168 |  | 96 | 108 | 120 | 108 | 120 |  | 120 | 240 | 0 | 24 | 180 |  | 24 | 0 | 132 | 96 | 0 |  | 36 | 252 | 36 | 36 | 348 |  | 0 | 0 | 24 | 36 | 24 |  | 60 | 180 | 48 | 276 | 108 |  | 228 | 48 | 60 | 48 | 192 | 3612 | 3612 | 7224 | 7224 | 7.224 | 7.224 | 13 | 18610 | 11067.5 | 18.61 | 11.0675
1:10 | 0 | 0 | 0 | 0 | 13 | 8 | 7 | 10 | 9 | 11 | 9 | 18 | 0 | 1 | 16 | 1 | 0 | 10 | 4 | 1 | 3 | 22 | 3 | 2 | 33 | 0 | 0 | 3 | 2 | 3 | 5 | 8 | 5 | 20 | 17 | 15 | 3 | 16 | 15 | 16 | 1:10 | 0 | 0 | 0 | 0 | 156 | 96 | 84 | 120 | 108 | 132 | 108 | 216 | 0 | 12 | 192 | 12 | 0 | 120 | 48 | 12 | 36 | 264 | 36 | 24 | 396 | 0 | 0 | 36 | 24 | 36 | 60 | 96 | 60 | 240 | 204 | 180 | 36 | 192 | 180 | 192 |  | 1:10 | 0 | 0 | 0 | 0 | 156 |  | 96 | 84 | 120 | 108 | 132 |  | 108 | 216 | 0 | 12 | 192 |  | 12 | 0 | 120 | 48 | 12 |  | 36 | 264 | 36 | 24 | 396 |  | 0 | 0 | 36 | 24 | 36 |  | 60 | 96 | 60 | 240 | 204 |  | 180 | 36 | 192 | 180 | 192 | 3708 | 3708 | 7416 | 7416 | 7.416 | 7.416 | 14 | 19450 | 11649.5 | 19.45 | 11.6495
1:15 | 0 | 0 | 0 | 0 | 14 | 2 | 7 | 9 | 6 | 10 | 9 | 16 | 5 | 2 | 16 | 5 | 0 | 9 | 0 | 11 | 3 | 22 | 2 | 3 | 33 | 0 | 0 | 2 | 3 | 2 | 6 | 4 | 8 | 8 | 17 | 8 | 4 | 17 | 15 | 14 | 1:15 | 0 | 0 | 0 | 0 | 168 | 24 | 84 | 108 | 72 | 120 | 108 | 192 | 60 | 24 | 192 | 60 | 0 | 108 | 0 | 132 | 36 | 264 | 24 | 36 | 396 | 0 | 0 | 24 | 36 | 24 | 72 | 48 | 96 | 96 | 204 | 96 | 48 | 204 | 180 | 168 |  | 1:15 | 0 | 0 | 0 | 0 | 168 |  | 24 | 84 | 108 | 72 | 120 |  | 108 | 192 | 60 | 24 | 192 |  | 60 | 0 | 108 | 0 | 132 |  | 36 | 264 | 24 | 36 | 396 |  | 0 | 0 | 24 | 36 | 24 |  | 72 | 48 | 96 | 96 | 204 |  | 96 | 48 | 204 | 180 | 168 | 3504 | 3504 | 7008 | 7008 | 7.008 | 7.008 | 15 | 18228 | 11905 | 18.228 | 11.905
1:20 | 0 | 0 | 1 | 0 | 14 | 1 | 7 | 10 | 1 | 10 | 2 | 1 | 10 | 6 | 16 | 11 | 0 | 10 | 0 | 10 | 3 | 19 | 3 | 2 | 32 | 0 | 0 | 3 | 2 | 3 | 14 | 3 | 17 | 6 | 17 | 8 | 4 | 17 | 14 | 5 | 1:20 | 0 | 0 | 12 | 0 | 168 | 12 | 84 | 120 | 12 | 120 | 24 | 12 | 120 | 72 | 192 | 132 | 0 | 120 | 0 | 120 | 36 | 228 | 36 | 24 | 384 | 0 | 0 | 36 | 24 | 36 | 168 | 36 | 204 | 72 | 204 | 96 | 48 | 204 | 168 | 60 |  | 1:20 | 0 | 0 | 12 | 0 | 168 |  | 12 | 84 | 120 | 12 | 120 |  | 24 | 12 | 120 | 72 | 192 |  | 132 | 0 | 120 | 0 | 120 |  | 36 | 228 | 36 | 24 | 384 |  | 0 | 0 | 36 | 24 | 36 |  | 168 | 36 | 204 | 72 | 204 |  | 96 | 48 | 204 | 168 | 60 | 3384 | 3384 | 6768 | 6768 | 6.768 | 6.768 | 16 | 17992 | 11451.25 | 17.992 | 11.4512
1:25 | 0 | 0 | 2 | 0 | 13 | 2 | 8 | 9 | 0 | 11 | 2 | 2 | 10 | 10 | 16 | 10 | 0 | 9 | 0 | 9 | 2 | 15 | 3 | 3 | 32 | 0 | 0 | 2 | 3 | 2 | 17 | 4 | 17 | 5 | 16 | 8 | 14 | 16 | 14 | 4 | 1:25 | 0 | 0 | 24 | 0 | 156 | 24 | 96 | 108 | 0 | 132 | 24 | 24 | 120 | 120 | 192 | 120 | 0 | 108 | 0 | 108 | 24 | 180 | 36 | 36 | 384 | 0 | 0 | 24 | 36 | 24 | 204 | 48 | 204 | 60 | 192 | 96 | 168 | 192 | 168 | 48 |  | 1:25 | 0 | 0 | 24 | 0 | 156 |  | 24 | 96 | 108 | 0 | 132 |  | 24 | 24 | 120 | 120 | 192 |  | 120 | 0 | 108 | 0 | 108 |  | 24 | 180 | 36 | 36 | 384 |  | 0 | 0 | 24 | 36 | 24 |  | 204 | 48 | 204 | 60 | 192 |  | 96 | 168 | 192 | 168 | 48 | 3480 | 3480 | 6960 | 6960 | 6.96 | 6.96 | 17 | 20250 | 11696 | 20.25 | 11.696
1:30 | 0 | 0 | 1 | 0 | 14 | 1 | 4 | 9 | 0 | 10 | 2 | 2 | 10 | 10 | 21 | 10 | 0 | 9 | 0 | 9 | 3 | 14 | 3 | 2 | 31 | 0 | 0 | 3 | 3 | 3 | 17 | 3 | 20 | 5 | 16 | 8 | 16 | 10 | 14 | 5 | 1:30 | 0 | 0 | 12 | 0 | 168 | 12 | 48 | 108 | 0 | 120 | 24 | 24 | 120 | 120 | 252 | 120 | 0 | 108 | 0 | 108 | 36 | 168 | 36 | 24 | 372 | 0 | 0 | 36 | 36 | 36 | 204 | 36 | 240 | 60 | 192 | 96 | 192 | 120 | 168 | 60 |  | 1:30 | 0 | 0 | 12 | 0 | 168 |  | 12 | 48 | 108 | 0 | 120 |  | 24 | 24 | 120 | 120 | 252 |  | 120 | 0 | 108 | 0 | 108 |  | 36 | 168 | 36 | 24 | 372 |  | 0 | 0 | 36 | 36 | 36 |  | 204 | 36 | 240 | 60 | 192 |  | 96 | 192 | 120 | 168 | 60 | 3456 | 3456 | 6912 | 6912 | 6.912 | 6.912 | 18 | 21196 | 14321.25 | 21.196 | 14.3212
1:35 | 0 | 2 | 2 | 10 | 8 | 2 | 0 | 8 | 0 | 10 | 2 | 1 | 9 | 10 | 24 | 9 | 0 | 8 | 0 | 9 | 3 | 15 | 2 | 3 | 31 | 0 | 2 | 2 | 2 | 8 | 16 | 4 | 19 | 5 | 16 | 8 | 15 | 5 | 4 | 5 | 1:35 | 0 | 24 | 24 | 120 | 96 | 24 | 0 | 96 | 0 | 120 | 24 | 12 | 108 | 120 | 288 | 108 | 0 | 96 | 0 | 108 | 36 | 180 | 24 | 36 | 372 | 0 | 24 | 24 | 24 | 96 | 192 | 48 | 228 | 60 | 192 | 96 | 180 | 60 | 48 | 60 |  | 1:35 | 0 | 24 | 24 | 120 | 96 |  | 24 | 0 | 96 | 0 | 120 |  | 24 | 12 | 108 | 120 | 288 |  | 108 | 0 | 96 | 0 | 108 |  | 36 | 180 | 24 | 36 | 372 |  | 0 | 24 | 24 | 24 | 96 |  | 192 | 48 | 228 | 60 | 192 |  | 96 | 180 | 60 | 48 | 60 | 3348 | 3348 | 6696 | 6696 | 6.696 | 6.696 | 19 | 19484 | 13867.25 | 19.484 | 13.8673
1:40 | 0 | 0 | 1 | 10 | 6 | 1 | 0 | 9 | 0 | 11 | 1 | 2 | 9 | 9 | 24 | 9 | 0 | 8 | 0 | 9 | 3 | 14 | 3 | 9 | 32 | 0 | 11 | 3 | 3 | 12 | 16 | 3 | 18 | 5 | 12 | 7 | 15 | 5 | 4 | 4 | 1:40 | 0 | 0 | 12 | 120 | 72 | 12 | 0 | 108 | 0 | 132 | 12 | 24 | 108 | 108 | 288 | 108 | 0 | 96 | 0 | 108 | 36 | 168 | 36 | 108 | 384 | 0 | 132 | 36 | 36 | 144 | 192 | 36 | 216 | 60 | 144 | 84 | 180 | 60 | 48 | 48 |  | 1:40 | 0 | 0 | 12 | 120 | 72 |  | 12 | 0 | 108 | 0 | 132 |  | 12 | 24 | 108 | 108 | 288 |  | 108 | 0 | 96 | 0 | 108 |  | 36 | 168 | 36 | 108 | 384 |  | 0 | 132 | 36 | 36 | 144 |  | 192 | 36 | 216 | 60 | 144 |  | 84 | 180 | 60 | 48 | 48 | 3456 | 3456 | 6912 | 6912 | 6.912 | 6.912 | 20 | 21832 | 16226.25 | 21.832 | 16.2263
1:45 | 0 | 0 | 2 | 10 | 7 | 2 | 0 | 4 | 0 | 9 | 2 | 1 | 9 | 9 | 23 | 9 | 0 | 9 | 0 | 9 | 7 | 14 | 3 | 11 | 28 | 7 | 10 | 2 | 2 | 11 | 14 | 4 | 12 | 5 | 5 | 20 | 14 | 5 | 3 | 7 | 1:45 | 0 | 0 | 24 | 120 | 84 | 24 | 0 | 48 | 0 | 108 | 24 | 12 | 108 | 108 | 276 | 108 | 0 | 108 | 0 | 108 | 84 | 168 | 36 | 132 | 336 | 84 | 120 | 24 | 24 | 132 | 168 | 48 | 144 | 60 | 60 | 240 | 168 | 60 | 36 | 84 |  | 1:45 | 0 | 0 | 24 | 120 | 84 |  | 24 | 0 | 48 | 0 | 108 |  | 24 | 12 | 108 | 108 | 276 |  | 108 | 0 | 108 | 0 | 108 |  | 84 | 168 | 36 | 132 | 336 |  | 84 | 120 | 24 | 24 | 132 |  | 168 | 48 | 144 | 60 | 60 |  | 240 | 168 | 60 | 36 | 84 | 3468 | 3468 | 6936 | 6936 | 6.936 | 6.936 | 21 | 20200 | 15150 | 20.2 | 15.15
1:50 | 0 | 0 | 1 | 9 | 6 | 1 | 0 | 0 | 0 | 3 | 1 | 2 | 9 | 9 | 24 | 9 | 0 | 7 | 0 | 9 | 12 | 15 | 2 | 12 | 22 | 11 | 10 | 3 | 3 | 10 | 5 | 11 | 8 | 13 | 6 | 20 | 6 | 5 | 3 | 17 | 1:50 | 0 | 0 | 12 | 108 | 72 | 12 | 0 | 0 | 0 | 36 | 12 | 24 | 108 | 108 | 288 | 108 | 0 | 84 | 0 | 108 | 144 | 180 | 24 | 144 | 264 | 132 | 120 | 36 | 36 | 120 | 60 | 132 | 96 | 156 | 72 | 240 | 72 | 60 | 36 | 204 |  | 1:50 | 0 | 0 | 12 | 108 | 72 |  | 12 | 0 | 0 | 0 | 36 |  | 12 | 24 | 108 | 108 | 288 |  | 108 | 0 | 84 | 0 | 108 |  | 144 | 180 | 24 | 144 | 264 |  | 132 | 120 | 36 | 36 | 120 |  | 60 | 132 | 96 | 156 | 72 |  | 240 | 72 | 60 | 36 | 204 | 3408 | 3408 | 6816 | 6816 | 6.816 | 6.816 | 22 | 20432 | 15203.25 | 20.432 | 15.2033
1:55 | 3 | 0 | 8 | 10 | 6 | 2 | 0 | 0 | 0 | 0 | 2 | 2 | 9 | 9 | 23 | 9 | 0 | 1 | 0 | 2 | 11 | 14 | 13 | 10 | 18 | 9 | 9 | 2 | 2 | 11 | 6 | 15 | 7 | 17 | 5 | 20 | 3 | 5 | 4 | 17 | 1:55 | 36 | 0 | 96 | 120 | 72 | 24 | 0 | 0 | 0 | 0 | 24 | 24 | 108 | 108 | 276 | 108 | 0 | 12 | 0 | 24 | 132 | 168 | 156 | 120 | 216 | 108 | 108 | 24 | 24 | 132 | 72 | 180 | 84 | 204 | 60 | 240 | 36 | 60 | 48 | 204 |  | 1:55 | 36 | 0 | 96 | 120 | 72 |  | 24 | 0 | 0 | 0 | 0 |  | 24 | 24 | 108 | 108 | 276 |  | 108 | 0 | 12 | 0 | 24 |  | 132 | 168 | 156 | 120 | 216 |  | 108 | 108 | 24 | 24 | 132 |  | 72 | 180 | 84 | 204 | 60 |  | 240 | 36 | 60 | 48 | 204 | 3408 | 3408 | 6816 | 6816 | 6.816 | 6.816 | 23 | 19560 | 14670 | 19.56 | 14.67
2:00 | 11 | 7 | 11 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 4 | 4 | 23 | 6 | 0 | 0 | 0 | 0 | 11 | 15 | 12 | 11 | 19 | 9 | 10 | 3 | 3 | 10 | 5 | 15 | 7 | 16 | 5 | 19 | 4 | 7 | 3 | 16 | 2:00 | 132 | 84 | 132 | 108 | 72 | 0 | 0 | 0 | 0 | 0 | 24 | 12 | 48 | 48 | 276 | 72 | 0 | 0 | 0 | 0 | 132 | 180 | 144 | 132 | 228 | 108 | 120 | 36 | 36 | 120 | 60 | 180 | 84 | 192 | 60 | 228 | 48 | 84 | 36 | 192 |  | 2:00 | 132 | 84 | 132 | 108 | 72 |  | 0 | 0 | 0 | 0 | 0 |  | 24 | 12 | 48 | 48 | 276 |  | 72 | 0 | 0 | 0 | 0 |  | 132 | 180 | 144 | 132 | 228 |  | 108 | 120 | 36 | 36 | 120 |  | 60 | 180 | 84 | 192 | 60 |  | 228 | 48 | 84 | 36 | 192 | 3408 | 3408 | 6816 | 6816 | 6.816 | 6.816
2:05 | 10 | 11 | 10 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 1 | 2 | 23 | 1 | 0 | 0 | 0 | 0 | 10 | 15 | 11 | 10 | 1 | 9 | 9 | 2 | 2 | 10 | 5 | 15 | 8 | 16 | 6 | 11 | 4 | 18 | 15 | 16 | 2:05 | 120 | 132 | 120 | 108 | 72 | 0 | 0 | 0 | 0 | 0 | 12 | 36 | 12 | 24 | 276 | 12 | 0 | 0 | 0 | 0 | 120 | 180 | 132 | 120 | 12 | 108 | 108 | 24 | 24 | 120 | 60 | 180 | 96 | 192 | 72 | 132 | 48 | 216 | 180 | 192 |  | 2:05 | 120 | 132 | 120 | 108 | 72 |  | 0 | 0 | 0 | 0 | 0 |  | 12 | 36 | 12 | 24 | 276 |  | 12 | 0 | 0 | 0 | 0 |  | 120 | 180 | 132 | 120 | 12 |  | 108 | 108 | 24 | 24 | 120 |  | 60 | 180 | 96 | 192 | 72 |  | 132 | 48 | 216 | 180 | 192 | 3240 | 3240 | 6480 | 6480 | 6.48 | 6.48
2:10 | 9 | 9 | 9 | 9 | 6 | 0 | 1 | 0 | 0 | 0 | 2 | 11 | 0 | 1 | 23 | 0 | 0 | 0 | 0 | 0 | 11 | 15 | 10 | 10 | 0 | 9 | 7 | 3 | 2 | 10 | 6 | 14 | 5 | 16 | 17 | 8 | 3 | 17 | 15 | 12 | 2:10 | 108 | 108 | 108 | 108 | 72 | 0 | 12 | 0 | 0 | 0 | 24 | 132 | 0 | 12 | 276 | 0 | 0 | 0 | 0 | 0 | 132 | 180 | 120 | 120 | 0 | 108 | 84 | 36 | 24 | 120 | 72 | 168 | 60 | 192 | 204 | 96 | 36 | 204 | 180 | 144 |  | 2:10 | 108 | 108 | 108 | 108 | 72 |  | 0 | 12 | 0 | 0 | 0 |  | 24 | 132 | 0 | 12 | 276 |  | 0 | 0 | 0 | 0 | 0 |  | 132 | 180 | 120 | 120 | 0 |  | 108 | 84 | 36 | 24 | 120 |  | 72 | 168 | 60 | 192 | 204 |  | 96 | 36 | 204 | 180 | 144 | 3240 | 3240 | 6480 | 6480 | 6.48 | 6.48
2:15 | 9 | 10 | 9 | 6 | 6 | 0 | 2 | 0 | 0 | 0 | 1 | 10 | 0 | 1 | 22 | 0 | 5 | 0 | 0 | 0 | 3 | 21 | 11 | 10 | 0 | 8 | 1 | 2 | 2 | 3 | 5 | 14 | 5 | 16 | 17 | 8 | 4 | 16 | 15 | 4 | 2:15 | 108 | 120 | 108 | 72 | 72 | 0 | 24 | 0 | 0 | 0 | 12 | 120 | 0 | 12 | 264 | 0 | 60 | 0 | 0 | 0 | 36 | 252 | 132 | 120 | 0 | 96 | 12 | 24 | 24 | 36 | 60 | 168 | 60 | 192 | 204 | 96 | 48 | 192 | 180 | 48 |  | 2:15 | 108 | 120 | 108 | 72 | 72 |  | 0 | 24 | 0 | 0 | 0 |  | 12 | 120 | 0 | 12 | 264 |  | 0 | 60 | 0 | 0 | 0 |  | 36 | 252 | 132 | 120 | 0 |  | 96 | 12 | 24 | 24 | 36 |  | 60 | 168 | 60 | 192 | 204 |  | 96 | 48 | 192 | 180 | 48 | 2952 | 2952 | 5904 | 5904 | 5.904 | 5.904
2:20 | 9 | 9 | 9 | 1 | 6 | 2 | 0 | 0 | 0 | 1 | 2 | 10 | 0 | 1 | 16 | 0 | 11 | 0 | 0 | 0 | 3 | 27 | 10 | 9 | 0 | 1 | 0 | 3 | 2 | 2 | 6 | 3 | 4 | 15 | 17 | 8 | 8 | 16 | 14 | 5 | 2:20 | 108 | 108 | 108 | 12 | 72 | 24 | 0 | 0 | 0 | 12 | 24 | 120 | 0 | 12 | 192 | 0 | 132 | 0 | 0 | 0 | 36 | 324 | 120 | 108 | 0 | 12 | 0 | 36 | 24 | 24 | 72 | 36 | 48 | 180 | 204 | 96 | 96 | 192 | 168 | 60 |  | 2:20 | 108 | 108 | 108 | 12 | 72 |  | 24 | 0 | 0 | 0 | 12 |  | 24 | 120 | 0 | 12 | 192 |  | 0 | 132 | 0 | 0 | 0 |  | 36 | 324 | 120 | 108 | 0 |  | 12 | 0 | 36 | 24 | 24 |  | 72 | 36 | 48 | 180 | 204 |  | 96 | 96 | 192 | 168 | 60 | 2760 | 2760 | 5520 | 5520 | 5.52 | 5.52
2:25 | 9 | 10 | 9 | 0 | 7 | 11 | 1 | 0 | 0 | 11 | 1 | 9 | 0 | 2 | 15 | 0 | 10 | 0 | 0 | 0 | 3 | 25 | 10 | 3 | 0 | 0 | 0 | 2 | 2 | 3 | 16 | 4 | 10 | 5 | 16 | 8 | 16 | 6 | 13 | 5 | 2:25 | 108 | 120 | 108 | 0 | 84 | 132 | 12 | 0 | 0 | 132 | 12 | 108 | 0 | 24 | 180 | 0 | 120 | 0 | 0 | 0 | 36 | 300 | 120 | 36 | 0 | 0 | 0 | 24 | 24 | 36 | 192 | 48 | 120 | 60 | 192 | 96 | 192 | 72 | 156 | 60 |  | 2:25 | 108 | 120 | 108 | 0 | 84 |  | 132 | 12 | 0 | 0 | 132 |  | 12 | 108 | 0 | 24 | 180 |  | 0 | 120 | 0 | 0 | 0 |  | 36 | 300 | 120 | 36 | 0 |  | 0 | 0 | 24 | 24 | 36 |  | 192 | 48 | 120 | 60 | 192 |  | 96 | 192 | 72 | 156 | 60 | 2904 | 2904 | 5808 | 5808 | 5.808 | 5.808
2:30 | 9 | 9 | 9 | 0 | 6 | 10 | 5 | 0 | 0 | 10 | 2 | 10 | 0 | 1 | 15 | 0 | 10 | 0 | 0 | 0 | 2 | 25 | 10 | 3 | 0 | 0 | 0 | 8 | 2 | 2 | 17 | 3 | 17 | 5 | 16 | 8 | 15 | 5 | 4 | 5 | 2:30 | 108 | 108 | 108 | 0 | 72 | 120 | 60 | 0 | 0 | 120 | 24 | 120 | 0 | 12 | 180 | 0 | 120 | 0 | 0 | 0 | 24 | 300 | 120 | 36 | 0 | 0 | 0 | 96 | 24 | 24 | 204 | 36 | 204 | 60 | 192 | 96 | 180 | 60 | 48 | 60 |  | 2:30 | 108 | 108 | 108 | 0 | 72 |  | 120 | 60 | 0 | 0 | 120 |  | 24 | 120 | 0 | 12 | 180 |  | 0 | 120 | 0 | 0 | 0 |  | 24 | 300 | 120 | 36 | 0 |  | 0 | 0 | 96 | 24 | 24 |  | 204 | 36 | 204 | 60 | 192 |  | 96 | 180 | 60 | 48 | 60 | 2916 | 2916 | 5832 | 5832 | 5.832 | 5.832
2:35 | 9 | 9 | 8 | 0 | 6 | 9 | 11 | 0 | 0 | 9 | 1 | 9 | 0 | 2 | 18 | 0 | 9 | 0 | 7 | 0 | 3 | 25 | 4 | 2 | 0 | 0 | 0 | 12 | 2 | 3 | 17 | 3 | 16 | 6 | 17 | 15 | 15 | 5 | 3 | 4 | 2:35 | 108 | 108 | 96 | 0 | 72 | 108 | 132 | 0 | 0 | 108 | 12 | 108 | 0 | 24 | 216 | 0 | 108 | 0 | 84 | 0 | 36 | 300 | 48 | 24 | 0 | 0 | 0 | 144 | 24 | 36 | 204 | 36 | 192 | 72 | 204 | 180 | 180 | 60 | 36 | 48 |  | 2:35 | 108 | 108 | 96 | 0 | 72 |  | 108 | 132 | 0 | 0 | 108 |  | 12 | 108 | 0 | 24 | 216 |  | 0 | 108 | 0 | 84 | 0 |  | 36 | 300 | 48 | 24 | 0 |  | 0 | 0 | 144 | 24 | 36 |  | 204 | 36 | 192 | 72 | 204 |  | 180 | 180 | 60 | 36 | 48 | 3108 | 3108 | 6216 | 6216 | 6.216 | 6.216
2:40 | 5 | 6 | 8 | 0 | 6 | 9 | 10 | 0 | 0 | 10 | 5 | 9 | 0 | 1 | 19 | 0 | 10 | 0 | 9 | 0 | 3 | 24 | 3 | 3 | 0 | 0 | 0 | 11 | 3 | 2 | 17 | 4 | 16 | 5 | 7 | 20 | 15 | 5 | 3 | 10 | 2:40 | 60 | 72 | 96 | 0 | 72 | 108 | 120 | 0 | 0 | 120 | 60 | 108 | 0 | 12 | 228 | 0 | 120 | 0 | 108 | 0 | 36 | 288 | 36 | 36 | 0 | 0 | 0 | 132 | 36 | 24 | 204 | 48 | 192 | 60 | 84 | 240 | 180 | 60 | 36 | 120 |  | 2:40 | 60 | 72 | 96 | 0 | 72 |  | 108 | 120 | 0 | 0 | 120 |  | 60 | 108 | 0 | 12 | 228 |  | 0 | 120 | 0 | 108 | 0 |  | 36 | 288 | 36 | 36 | 0 |  | 0 | 0 | 132 | 36 | 24 |  | 204 | 48 | 192 | 60 | 84 |  | 240 | 180 | 60 | 36 | 120 | 3096 | 3096 | 6192 | 6192 | 6.192 | 6.192
2:45 | 0 | 1 | 9 | 0 | 14 | 9 | 10 | 0 | 9 | 9 | 11 | 9 | 0 | 2 | 10 | 0 | 9 | 0 | 9 | 0 | 2 | 24 | 2 | 2 | 0 | 0 | 0 | 11 | 2 | 3 | 16 | 3 | 16 | 5 | 6 | 20 | 7 | 5 | 4 | 17 | 2:45 | 0 | 12 | 108 | 0 | 168 | 108 | 120 | 0 | 108 | 108 | 132 | 108 | 0 | 24 | 120 | 0 | 108 | 0 | 108 | 0 | 24 | 288 | 24 | 24 | 0 | 0 | 0 | 132 | 24 | 36 | 192 | 36 | 192 | 60 | 72 | 240 | 84 | 60 | 48 | 204 |  | 2:45 | 0 | 12 | 108 | 0 | 168 |  | 108 | 120 | 0 | 108 | 108 |  | 132 | 108 | 0 | 24 | 120 |  | 0 | 108 | 0 | 108 | 0 |  | 24 | 288 | 24 | 24 | 0 |  | 0 | 0 | 132 | 24 | 36 |  | 192 | 36 | 192 | 60 | 72 |  | 240 | 84 | 60 | 48 | 204 | 3072 | 3072 | 6144 | 6144 | 6.144 | 6.144
2:50 | 0 | 2 | 9 | 0 | 15 | 9 | 10 | 0 | 11 | 9 | 10 | 2 | 0 | 1 | 10 | 0 | 9 | 0 | 9 | 0 | 3 | 24 | 3 | 3 | 0 | 0 | 0 | 10 | 3 | 2 | 13 | 4 | 16 | 5 | 5 | 20 | 4 | 5 | 3 | 16 | 2:50 | 0 | 24 | 108 | 0 | 180 | 108 | 120 | 0 | 132 | 108 | 120 | 24 | 0 | 12 | 120 | 0 | 108 | 0 | 108 | 0 | 36 | 288 | 36 | 36 | 0 | 0 | 0 | 120 | 36 | 24 | 156 | 48 | 192 | 60 | 60 | 240 | 48 | 60 | 36 | 192 |  | 2:50 | 0 | 24 | 108 | 0 | 180 |  | 108 | 120 | 0 | 132 | 108 |  | 120 | 24 | 0 | 12 | 120 |  | 0 | 108 | 0 | 108 | 0 |  | 36 | 288 | 36 | 36 | 0 |  | 0 | 0 | 120 | 36 | 24 |  | 156 | 48 | 192 | 60 | 60 |  | 240 | 48 | 60 | 36 | 192 | 2940 | 2940 | 5880 | 5880 | 5.88 | 5.88
2:55 | 0 | 1 | 9 | 0 | 14 | 9 | 9 | 0 | 10 | 9 | 10 | 2 | 0 | 2 | 10 | 0 | 9 | 0 | 8 | 0 | 3 | 24 | 2 | 2 | 0 | 0 | 0 | 11 | 2 | 3 | 5 | 4 | 10 | 5 | 5 | 18 | 3 | 11 | 4 | 16 | 2:55 | 0 | 12 | 108 | 0 | 168 | 108 | 108 | 0 | 120 | 108 | 120 | 24 | 0 | 24 | 120 | 0 | 108 | 0 | 96 | 0 | 36 | 288 | 24 | 24 | 0 | 0 | 0 | 132 | 24 | 36 | 60 | 48 | 120 | 60 | 60 | 216 | 36 | 132 | 48 | 192 |  | 2:55 | 0 | 12 | 108 | 0 | 168 |  | 108 | 108 | 0 | 120 | 108 |  | 120 | 24 | 0 | 24 | 120 |  | 0 | 108 | 0 | 96 | 0 |  | 36 | 288 | 24 | 24 | 0 |  | 0 | 0 | 132 | 24 | 36 |  | 60 | 48 | 120 | 60 | 60 |  | 216 | 36 | 132 | 48 | 192 | 2760 | 2760 | 5520 | 5520 | 5.52 | 5.52
3:00 | 0 | 2 | 5 | 0 | 14 | 9 | 9 | 0 | 9 | 9 | 10 | 1 | 0 | 1 | 9 | 0 | 6 | 0 | 9 | 0 | 2 | 18 | 3 | 3 | 0 | 0 | 0 | 10 | 11 | 2 | 6 | 16 | 5 | 16 | 5 | 8 | 4 | 17 | 15 | 16 | 3:00 | 0 | 24 | 60 | 0 | 168 | 108 | 108 | 0 | 108 | 108 | 120 | 12 | 0 | 12 | 108 | 0 | 72 | 0 | 108 | 0 | 24 | 216 | 36 | 36 | 0 | 0 | 0 | 120 | 132 | 24 | 72 | 192 | 60 | 192 | 60 | 96 | 48 | 204 | 180 | 192 |  | 3:00 | 0 | 24 | 60 | 0 | 168 |  | 108 | 108 | 0 | 108 | 108 |  | 120 | 12 | 0 | 12 | 108 |  | 0 | 72 | 0 | 108 | 0 |  | 24 | 216 | 36 | 36 | 0 |  | 0 | 0 | 120 | 132 | 24 |  | 72 | 192 | 60 | 192 | 60 |  | 96 | 48 | 204 | 180 | 192 | 3000 | 3000 | 6000 | 6000 | 6 | 6
3:05 | 0 | 1 | 0 | 0 | 14 | 2 | 9 | 0 | 10 | 8 | 9 | 2 | 0 | 2 | 10 | 0 | 1 | 0 | 8 | 0 | 3 | 17 | 2 | 2 | 0 | 0 | 0 | 10 | 12 | 3 | 5 | 15 | 5 | 17 | 10 | 8 | 4 | 17 | 15 | 10 | 3:05 | 0 | 12 | 0 | 0 | 168 | 24 | 108 | 0 | 120 | 96 | 108 | 24 | 0 | 24 | 120 | 0 | 12 | 0 | 96 | 0 | 36 | 204 | 24 | 24 | 0 | 0 | 0 | 120 | 144 | 36 | 60 | 180 | 60 | 204 | 120 | 96 | 48 | 204 | 180 | 120 |  | 3:05 | 0 | 12 | 0 | 0 | 168 |  | 24 | 108 | 0 | 120 | 96 |  | 108 | 24 | 0 | 24 | 120 |  | 0 | 12 | 0 | 96 | 0 |  | 36 | 204 | 24 | 24 | 0 |  | 0 | 0 | 120 | 144 | 36 |  | 60 | 180 | 60 | 204 | 120 |  | 96 | 48 | 204 | 180 | 120 | 2772 | 2772 | 5544 | 5544 | 5.544 | 5.544
3:10 | 0 | 2 | 0 | 0 | 14 | 0 | 8 | 8 | 9 | 1 | 9 | 1 | 0 | 1 | 17 | 0 | 2 | 2 | 8 | 0 | 3 | 17 | 3 | 3 | 0 | 0 | 0 | 4 | 11 | 2 | 6 | 15 | 5 | 16 | 17 | 8 | 3 | 16 | 15 | 5 | 3:10 | 0 | 24 | 0 | 0 | 168 | 0 | 96 | 96 | 108 | 12 | 108 | 12 | 0 | 12 | 204 | 0 | 24 | 24 | 96 | 0 | 36 | 204 | 36 | 36 | 0 | 0 | 0 | 48 | 132 | 24 | 72 | 180 | 60 | 192 | 204 | 96 | 36 | 192 | 180 | 60 |  | 3:10 | 0 | 24 | 0 | 0 | 168 |  | 0 | 96 | 96 | 108 | 12 |  | 108 | 12 | 0 | 12 | 204 |  | 0 | 24 | 24 | 96 | 0 |  | 36 | 204 | 36 | 36 | 0 |  | 0 | 0 | 48 | 132 | 24 |  | 72 | 180 | 60 | 192 | 204 |  | 96 | 36 | 192 | 180 | 60 | 2772 | 2772 | 5544 | 5544 | 5.544 | 5.544
3:15 | 0 | 1 | 0 | 0 | 13 | 1 | 1 | 11 | 9 | 0 | 9 | 2 | 4 | 4 | 23 | 0 | 1 | 11 | 3 | 11 | 2 | 17 | 2 | 2 | 0 | 0 | 0 | 2 | 11 | 3 | 5 | 15 | 5 | 17 | 17 | 8 | 6 | 11 | 15 | 4 | 3:15 | 0 | 12 | 0 | 0 | 156 | 12 | 12 | 132 | 108 | 0 | 108 | 24 | 48 | 48 | 276 | 0 | 12 | 132 | 36 | 132 | 24 | 204 | 24 | 24 | 0 | 0 | 0 | 24 | 132 | 36 | 60 | 180 | 60 | 204 | 204 | 96 | 72 | 132 | 180 | 48 |  | 3:15 | 0 | 12 | 0 | 0 | 156 |  | 12 | 12 | 132 | 108 | 0 |  | 108 | 24 | 48 | 48 | 276 |  | 0 | 12 | 132 | 36 | 132 |  | 24 | 204 | 24 | 24 | 0 |  | 0 | 0 | 24 | 132 | 36 |  | 60 | 180 | 60 | 204 | 204 |  | 96 | 72 | 132 | 180 | 48 | 2952 | 2952 | 5904 | 5904 | 5.904 | 5.904
3:20 | 0 | 2 | 0 | 1 | 14 | 1 | 2 | 10 | 0 | 0 | 9 | 2 | 10 | 11 | 14 | 0 | 2 | 10 | 0 | 10 | 3 | 17 | 3 | 3 | 0 | 0 | 0 | 3 | 10 | 2 | 5 | 14 | 5 | 16 | 17 | 8 | 16 | 5 | 13 | 5 | 3:20 | 0 | 24 | 0 | 12 | 168 | 12 | 24 | 120 | 0 | 0 | 108 | 24 | 120 | 132 | 168 | 0 | 24 | 120 | 0 | 120 | 36 | 204 | 36 | 36 | 0 | 0 | 0 | 36 | 120 | 24 | 60 | 168 | 60 | 192 | 204 | 96 | 192 | 60 | 156 | 60 |  | 3:20 | 0 | 24 | 0 | 12 | 168 |  | 12 | 24 | 120 | 0 | 0 |  | 108 | 24 | 120 | 132 | 168 |  | 0 | 24 | 120 | 0 | 120 |  | 36 | 204 | 36 | 36 | 0 |  | 0 | 0 | 36 | 120 | 24 |  | 60 | 168 | 60 | 192 | 204 |  | 96 | 192 | 60 | 156 | 60 | 2916 | 2916 | 5832 | 5832 | 5.832 | 5.832
3:25 | 0 | 1 | 0 | 0 | 13 | 1 | 1 | 9 | 0 | 0 | 2 | 1 | 10 | 10 | 10 | 0 | 1 | 10 | 0 | 9 | 3 | 17 | 2 | 2 | 0 | 0 | 0 | 2 | 11 | 3 | 6 | 4 | 5 | 16 | 16 | 8 | 16 | 5 | 3 | 5 | 3:25 | 0 | 12 | 0 | 0 | 156 | 12 | 12 | 108 | 0 | 0 | 24 | 12 | 120 | 120 | 120 | 0 | 12 | 120 | 0 | 108 | 36 | 204 | 24 | 24 | 0 | 0 | 0 | 24 | 132 | 36 | 72 | 48 | 60 | 192 | 192 | 96 | 192 | 60 | 36 | 60 |  | 3:25 | 0 | 12 | 0 | 0 | 156 |  | 12 | 12 | 108 | 0 | 0 |  | 24 | 12 | 120 | 120 | 120 |  | 0 | 12 | 120 | 0 | 108 |  | 36 | 204 | 24 | 24 | 0 |  | 0 | 0 | 24 | 132 | 36 |  | 72 | 48 | 60 | 192 | 192 |  | 96 | 192 | 60 | 36 | 60 | 2424 | 2424 | 4848 | 4848 | 4.848 | 4.848
3:30 | 0 | 2 | 0 | 6 | 13 | 2 | 2 | 10 | 0 | 0 | 1 | 2 | 10 | 10 | 10 | 0 | 2 | 9 | 0 | 10 | 3 | 17 | 3 | 3 | 0 | 0 | 0 | 5 | 10 | 2 | 17 | 3 | 5 | 15 | 17 | 15 | 15 | 5 | 3 | 5 | 3:30 | 0 | 24 | 0 | 72 | 156 | 24 | 24 | 120 | 0 | 0 | 12 | 24 | 120 | 120 | 120 | 0 | 24 | 108 | 0 | 120 | 36 | 204 | 36 | 36 | 0 | 0 | 0 | 60 | 120 | 24 | 204 | 36 | 60 | 180 | 204 | 180 | 180 | 60 | 36 | 60 |  | 3:30 | 0 | 24 | 0 | 72 | 156 |  | 24 | 24 | 120 | 0 | 0 |  | 12 | 24 | 120 | 120 | 120 |  | 0 | 24 | 108 | 0 | 120 |  | 36 | 204 | 36 | 36 | 0 |  | 0 | 0 | 60 | 120 | 24 |  | 204 | 36 | 60 | 180 | 204 |  | 180 | 180 | 60 | 36 | 60 | 2784 | 2784 | 5568 | 5568 | 5.568 | 5.568
3:35 | 0 | 1 | 1 | 11 | 7 | 0 | 1 | 9 | 0 | 1 | 2 | 2 | 9 | 9 | 9 | 3 | 1 | 9 | 0 | 9 | 2 | 17 | 2 | 2 | 0 | 0 | 0 | 10 | 5 | 3 | 17 | 3 | 7 | 5 | 9 | 20 | 14 | 5 | 4 | 10 | 3:35 | 0 | 12 | 12 | 132 | 84 | 0 | 12 | 108 | 0 | 12 | 24 | 24 | 108 | 108 | 108 | 36 | 12 | 108 | 0 | 108 | 24 | 204 | 24 | 24 | 0 | 0 | 0 | 120 | 60 | 36 | 204 | 36 | 84 | 60 | 108 | 240 | 168 | 60 | 48 | 120 |  | 3:35 | 0 | 12 | 12 | 132 | 84 |  | 0 | 12 | 108 | 0 | 12 |  | 24 | 24 | 108 | 108 | 108 |  | 36 | 12 | 108 | 0 | 108 |  | 24 | 204 | 24 | 24 | 0 |  | 0 | 0 | 120 | 60 | 36 |  | 204 | 36 | 84 | 60 | 108 |  | 240 | 168 | 60 | 48 | 120 | 2628 | 2628 | 5256 | 5256 | 5.256 | 5.256
3:40 | 4 | 2 | 0 | 10 | 6 | 1 | 0 | 9 | 0 | 0 | 1 | 1 | 9 | 9 | 9 | 11 | 2 | 9 | 0 | 9 | 3 | 17 | 2 | 3 | 0 | 0 | 0 | 3 | 3 | 2 | 16 | 4 | 18 | 5 | 5 | 20 | 14 | 5 | 3 | 17 | 3:40 | 48 | 24 | 0 | 120 | 72 | 12 | 0 | 108 | 0 | 0 | 12 | 12 | 108 | 108 | 108 | 132 | 24 | 108 | 0 | 108 | 36 | 204 | 24 | 36 | 0 | 0 | 0 | 36 | 36 | 24 | 192 | 48 | 216 | 60 | 60 | 240 | 168 | 60 | 36 | 204 |  | 3:40 | 48 | 24 | 0 | 120 | 72 |  | 12 | 0 | 108 | 0 | 0 |  | 12 | 12 | 108 | 108 | 108 |  | 132 | 24 | 108 | 0 | 108 |  | 36 | 204 | 24 | 36 | 0 |  | 0 | 0 | 36 | 36 | 24 |  | 192 | 48 | 216 | 60 | 60 |  | 240 | 168 | 60 | 36 | 204 | 2784 | 2784 | 5568 | 5568 | 5.568 | 5.568
3:45 | 11 | 11 | 0 | 9 | 6 | 1 | 0 | 9 | 0 | 0 | 2 | 2 | 9 | 10 | 9 | 10 | 1 | 8 | 0 | 9 | 3 | 17 | 3 | 2 | 0 | 0 | 0 | 2 | 2 | 3 | 17 | 3 | 17 | 5 | 5 | 19 | 4 | 8 | 4 | 16 | 3:45 | 132 | 132 | 0 | 108 | 72 | 12 | 0 | 108 | 0 | 0 | 24 | 24 | 108 | 120 | 108 | 120 | 12 | 96 | 0 | 108 | 36 | 204 | 36 | 24 | 0 | 0 | 0 | 24 | 24 | 36 | 204 | 36 | 204 | 60 | 60 | 228 | 48 | 96 | 48 | 192 |  | 3:45 | 132 | 132 | 0 | 108 | 72 |  | 12 | 0 | 108 | 0 | 0 |  | 24 | 24 | 108 | 120 | 108 |  | 120 | 12 | 96 | 0 | 108 |  | 36 | 204 | 36 | 24 | 0 |  | 0 | 0 | 24 | 24 | 36 |  | 204 | 36 | 204 | 60 | 60 |  | 228 | 48 | 96 | 48 | 192 | 2844 | 2844 | 5688 | 5688 | 5.688 | 5.688
3:50 | 9 | 11 | 0 | 10 | 7 | 1 | 0 | 9 | 0 | 0 | 1 | 2 | 9 | 9 | 9 | 10 | 2 | 9 | 0 | 8 | 12 | 16 | 2 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 17 | 4 | 16 | 5 | 6 | 18 | 4 | 17 | 3 | 16 | 3:50 | 108 | 132 | 0 | 120 | 84 | 12 | 0 | 108 | 0 | 0 | 12 | 24 | 108 | 108 | 108 | 120 | 24 | 108 | 0 | 96 | 144 | 192 | 24 | 36 | 0 | 0 | 0 | 36 | 36 | 36 | 204 | 48 | 192 | 60 | 72 | 216 | 48 | 204 | 36 | 192 |  | 3:50 | 108 | 132 | 0 | 120 | 84 |  | 12 | 0 | 108 | 0 | 0 |  | 12 | 24 | 108 | 108 | 108 |  | 120 | 24 | 108 | 0 | 96 |  | 144 | 192 | 24 | 36 | 0 |  | 0 | 0 | 36 | 36 | 36 |  | 204 | 48 | 192 | 60 | 72 |  | 216 | 48 | 204 | 36 | 192 | 3048 | 3048 | 6096 | 6096 | 6.096 | 6.096
3:55 | 10 | 9 | 0 | 9 | 6 | 2 | 0 | 6 | 0 | 0 | 2 | 1 | 9 | 8 | 7 | 9 | 1 | 8 | 0 | 1 | 11 | 18 | 3 | 2 | 0 | 0 | 0 | 2 | 2 | 2 | 11 | 3 | 15 | 5 | 5 | 8 | 3 | 17 | 16 | 16 | 3:55 | 120 | 108 | 0 | 108 | 72 | 24 | 0 | 72 | 0 | 0 | 24 | 12 | 108 | 96 | 84 | 108 | 12 | 96 | 0 | 12 | 132 | 216 | 36 | 24 | 0 | 0 | 0 | 24 | 24 | 24 | 132 | 36 | 180 | 60 | 60 | 96 | 36 | 204 | 192 | 192 |  | 3:55 | 120 | 108 | 0 | 108 | 72 |  | 24 | 0 | 72 | 0 | 0 |  | 24 | 12 | 108 | 96 | 84 |  | 108 | 12 | 96 | 0 | 12 |  | 132 | 216 | 36 | 24 | 0 |  | 0 | 0 | 24 | 24 | 24 |  | 132 | 36 | 180 | 60 | 60 |  | 96 | 36 | 204 | 192 | 192 | 2724 | 2724 | 5448 | 5448 | 5.448 | 5.448
4:00 | 9 | 10 | 0 | 9 | 6 | 1 | 0 | 1 | 0 | 0 | 1 | 2 | 4 | 1 | 1 | 10 | 2 | 0 | 0 | 0 | 12 | 21 | 2 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 6 | 5 | 16 | 5 | 7 | 8 | 4 | 16 | 15 | 8 | 4:00 | 108 | 120 | 0 | 108 | 72 | 12 | 0 | 12 | 0 | 0 | 12 | 24 | 48 | 12 | 12 | 120 | 24 | 0 | 0 | 0 | 144 | 252 | 24 | 36 | 0 | 0 | 0 | 36 | 36 | 36 | 72 | 60 | 192 | 60 | 84 | 96 | 48 | 192 | 180 | 96 |  | 4:00 | 108 | 120 | 0 | 108 | 72 |  | 12 | 0 | 12 | 0 | 0 |  | 12 | 24 | 48 | 12 | 12 |  | 120 | 24 | 0 | 0 | 0 |  | 144 | 252 | 24 | 36 | 0 |  | 0 | 0 | 36 | 36 | 36 |  | 72 | 60 | 192 | 60 | 84 |  | 96 | 48 | 192 | 180 | 96 | 2328 | 2328 | 4656 | 4656 | 4.656 | 4.656
4:05 | 9 | 9 | 1 | 9 | 6 | 2 | 0 | 1 | 0 | 0 | 2 | 5 | 1 | 2 | 2 | 9 | 1 | 0 | 0 | 0 | 11 | 29 | 3 | 2 | 10 | 0 | 0 | 2 | 3 | 5 | 5 | 16 | 13 | 6 | 17 | 8 | 4 | 16 | 15 | 5 | 4:05 | 108 | 108 | 12 | 108 | 72 | 24 | 0 | 12 | 0 | 0 | 24 | 60 | 12 | 24 | 24 | 108 | 12 | 0 | 0 | 0 | 132 | 348 | 36 | 24 | 120 | 0 | 0 | 24 | 36 | 60 | 60 | 192 | 156 | 72 | 204 | 96 | 48 | 192 | 180 | 60 |  | 4:05 | 108 | 108 | 12 | 108 | 72 |  | 24 | 0 | 12 | 0 | 0 |  | 24 | 60 | 12 | 24 | 24 |  | 108 | 12 | 0 | 0 | 0 |  | 132 | 348 | 36 | 24 | 120 |  | 0 | 0 | 24 | 36 | 60 |  | 60 | 192 | 156 | 72 | 204 |  | 96 | 48 | 192 | 180 | 60 | 2748 | 2748 | 5496 | 5496 | 5.496 | 5.496
4:10 | 9 | 9 | 0 | 8 | 7 | 1 | 0 | 1 | 0 | 0 | 1 | 11 | 0 | 1 | 1 | 9 | 2 | 0 | 0 | 0 | 10 | 12 | 2 | 3 | 11 | 7 | 0 | 3 | 2 | 12 | 6 | 16 | 4 | 15 | 17 | 8 | 3 | 5 | 15 | 5 | 4:10 | 108 | 108 | 0 | 96 | 84 | 12 | 0 | 12 | 0 | 0 | 12 | 132 | 0 | 12 | 12 | 108 | 24 | 0 | 0 | 0 | 120 | 144 | 24 | 36 | 132 | 84 | 0 | 36 | 24 | 144 | 72 | 192 | 48 | 180 | 204 | 96 | 36 | 60 | 180 | 60 |  | 4:10 | 108 | 108 | 0 | 96 | 84 |  | 12 | 0 | 12 | 0 | 0 |  | 12 | 132 | 0 | 12 | 12 |  | 108 | 24 | 0 | 0 | 0 |  | 120 | 144 | 24 | 36 | 132 |  | 84 | 0 | 36 | 24 | 144 |  | 72 | 192 | 48 | 180 | 204 |  | 96 | 36 | 60 | 180 | 60 | 2592 | 2592 | 5184 | 5184 | 5.184 | 5.184
4:15 | 9 | 10 | 6 | 2 | 6 | 2 | 0 | 0 | 0 | 0 | 2 | 10 | 0 | 2 | 2 | 9 | 1 | 0 | 0 | 0 | 8 | 11 | 3 | 2 | 10 | 11 | 9 | 2 | 3 | 12 | 5 | 15 | 5 | 17 | 17 | 8 | 9 | 5 | 11 | 5 | 4:15 | 108 | 120 | 72 | 24 | 72 | 24 | 0 | 0 | 0 | 0 | 24 | 120 | 0 | 24 | 24 | 108 | 12 | 0 | 0 | 0 | 96 | 132 | 36 | 24 | 120 | 132 | 108 | 24 | 36 | 144 | 60 | 180 | 60 | 204 | 204 | 96 | 108 | 60 | 132 | 60 |  | 4:15 | 108 | 120 | 72 | 24 | 72 |  | 24 | 0 | 0 | 0 | 0 |  | 24 | 120 | 0 | 24 | 24 |  | 108 | 12 | 0 | 0 | 0 |  | 96 | 132 | 36 | 24 | 120 |  | 132 | 108 | 24 | 36 | 144 |  | 60 | 180 | 60 | 204 | 204 |  | 96 | 108 | 60 | 132 | 60 | 2748 | 2748 | 5496 | 5496 | 5.496 | 5.496
4:20 | 9 | 8 | 10 | 0 | 6 | 4 | 0 | 0 | 0 | 0 | 1 | 10 | 0 | 1 | 1 | 4 | 2 | 0 | 0 | 0 | 3 | 10 | 2 | 4 | 10 | 10 | 11 | 3 | 2 | 11 | 6 | 14 | 5 | 16 | 17 | 8 | 16 | 5 | 3 | 4 | 4:20 | 108 | 96 | 120 | 0 | 72 | 48 | 0 | 0 | 0 | 0 | 12 | 120 | 0 | 12 | 12 | 48 | 24 | 0 | 0 | 0 | 36 | 120 | 24 | 48 | 120 | 120 | 132 | 36 | 24 | 132 | 72 | 168 | 60 | 192 | 204 | 96 | 192 | 60 | 36 | 48 |  | 4:20 | 108 | 96 | 120 | 0 | 72 |  | 48 | 0 | 0 | 0 | 0 |  | 12 | 120 | 0 | 12 | 12 |  | 48 | 24 | 0 | 0 | 0 |  | 36 | 120 | 24 | 48 | 120 |  | 120 | 132 | 36 | 24 | 132 |  | 72 | 168 | 60 | 192 | 204 |  | 96 | 192 | 60 | 36 | 48 | 2592 | 2592 | 5184 | 5184 | 5.184 | 5.184
4:25 | 8 | 2 | 10 | 1 | 6 | 11 | 0 | 0 | 0 | 0 | 2 | 10 | 0 | 2 | 2 | 1 | 1 | 0 | 0 | 0 | 3 | 10 | 3 | 13 | 9 | 10 | 10 | 2 | 3 | 10 | 5 | 15 | 5 | 16 | 16 | 15 | 16 | 5 | 3 | 5 | 4:25 | 96 | 24 | 120 | 12 | 72 | 132 | 0 | 0 | 0 | 0 | 24 | 120 | 0 | 24 | 24 | 12 | 12 | 0 | 0 | 0 | 36 | 120 | 36 | 156 | 108 | 120 | 120 | 24 | 36 | 120 | 60 | 180 | 60 | 192 | 192 | 180 | 192 | 60 | 36 | 60 |  | 4:25 | 96 | 24 | 120 | 12 | 72 |  | 132 | 0 | 0 | 0 | 0 |  | 24 | 120 | 0 | 24 | 24 |  | 12 | 12 | 0 | 0 | 0 |  | 36 | 120 | 36 | 156 | 108 |  | 120 | 120 | 24 | 36 | 120 |  | 60 | 180 | 60 | 192 | 192 |  | 180 | 192 | 60 | 36 | 60 | 2760 | 2760 | 5520 | 5520 | 5.52 | 5.52
4:30 | 1 | 1 | 10 | 0 | 7 | 10 | 0 | 0 | 0 | 0 | 1 | 9 | 0 | 1 | 1 | 0 | 6 | 0 | 0 | 0 | 2 | 10 | 2 | 11 | 9 | 9 | 10 | 3 | 2 | 11 | 6 | 4 | 5 | 15 | 11 | 20 | 15 | 5 | 4 | 14 | 4:30 | 12 | 12 | 120 | 0 | 84 | 120 | 0 | 0 | 0 | 0 | 12 | 108 | 0 | 12 | 12 | 0 | 72 | 0 | 0 | 0 | 24 | 120 | 24 | 132 | 108 | 108 | 120 | 36 | 24 | 132 | 72 | 48 | 60 | 180 | 132 | 240 | 180 | 60 | 48 | 168 |  | 4:30 | 12 | 12 | 120 | 0 | 84 |  | 120 | 0 | 0 | 0 | 0 |  | 12 | 108 | 0 | 12 | 12 |  | 0 | 72 | 0 | 0 | 0 |  | 24 | 120 | 24 | 132 | 108 |  | 108 | 120 | 36 | 24 | 132 |  | 72 | 48 | 60 | 180 | 132 |  | 240 | 180 | 60 | 48 | 168 | 2580 | 2580 | 5160 | 5160 | 5.16 | 5.16
4:35 | 0 | 2 | 9 | 2 | 6 | 9 | 0 | 1 | 0 | 10 | 2 | 9 | 0 | 2 | 2 | 0 | 11 | 0 | 0 | 0 | 3 | 10 | 3 | 11 | 9 | 9 | 9 | 2 | 3 | 10 | 18 | 3 | 5 | 16 | 5 | 19 | 15 | 5 | 3 | 17 | 4:35 | 0 | 24 | 108 | 24 | 72 | 108 | 0 | 12 | 0 | 120 | 24 | 108 | 0 | 24 | 24 | 0 | 132 | 0 | 0 | 0 | 36 | 120 | 36 | 132 | 108 | 108 | 108 | 24 | 36 | 120 | 216 | 36 | 60 | 192 | 60 | 228 | 180 | 60 | 36 | 204 |  | 4:35 | 0 | 24 | 108 | 24 | 72 |  | 108 | 0 | 12 | 0 | 120 |  | 24 | 108 | 0 | 24 | 24 |  | 0 | 132 | 0 | 0 | 0 |  | 36 | 120 | 36 | 132 | 108 |  | 108 | 108 | 24 | 36 | 120 |  | 216 | 36 | 60 | 192 | 60 |  | 228 | 180 | 60 | 36 | 204 | 2880 | 2880 | 5760 | 5760 | 5.76 | 5.76
4:40 | 0 | 1 | 9 | 1 | 6 | 9 | 1 | 1 | 0 | 10 | 1 | 9 | 0 | 1 | 1 | 0 | 10 | 0 | 0 | 0 | 3 | 2 | 11 | 11 | 9 | 9 | 10 | 3 | 2 | 10 | 18 | 4 | 5 | 11 | 5 | 17 | 7 | 14 | 3 | 16 | 4:40 | 0 | 12 | 108 | 12 | 72 | 108 | 12 | 12 | 0 | 120 | 12 | 108 | 0 | 12 | 12 | 0 | 120 | 0 | 0 | 0 | 36 | 24 | 132 | 132 | 108 | 108 | 120 | 36 | 24 | 120 | 216 | 48 | 60 | 132 | 60 | 204 | 84 | 168 | 36 | 192 |  | 4:40 | 0 | 12 | 108 | 12 | 72 |  | 108 | 12 | 12 | 0 | 120 |  | 12 | 108 | 0 | 12 | 12 |  | 0 | 120 | 0 | 0 | 0 |  | 36 | 24 | 132 | 132 | 108 |  | 108 | 120 | 36 | 24 | 120 |  | 216 | 48 | 60 | 132 | 60 |  | 204 | 84 | 168 | 36 | 192 | 2760 | 2760 | 5520 | 5520 | 5.52 | 5.52
4:45 | 0 | 1 | 9 | 1 | 12 | 10 | 12 | 1 | 0 | 10 | 2 | 6 | 0 | 2 | 2 | 0 | 10 | 0 | 9 | 0 | 3 | 3 | 12 | 10 | 2 | 2 | 9 | 2 | 3 | 5 | 17 | 3 | 4 | 5 | 5 | 14 | 4 | 17 | 3 | 17 | 4:45 | 0 | 12 | 108 | 12 | 144 | 120 | 144 | 12 | 0 | 120 | 24 | 72 | 0 | 24 | 24 | 0 | 120 | 0 | 108 | 0 | 36 | 36 | 144 | 120 | 24 | 24 | 108 | 24 | 36 | 60 | 204 | 36 | 48 | 60 | 60 | 168 | 48 | 204 | 36 | 204 |  | 4:45 | 0 | 12 | 108 | 12 | 144 |  | 120 | 144 | 12 | 0 | 120 |  | 24 | 72 | 0 | 24 | 24 |  | 0 | 120 | 0 | 108 | 0 |  | 36 | 36 | 144 | 120 | 24 |  | 24 | 108 | 24 | 36 | 60 |  | 204 | 36 | 48 | 60 | 60 |  | 168 | 48 | 204 | 36 | 204 | 2724 | 2724 | 5448 | 5448 | 5.448 | 5.448
4:50 | 0 | 2 | 9 | 0 | 15 | 8 | 10 | 2 | 8 | 10 | 12 | 2 | 0 | 1 | 1 | 0 | 10 | 0 | 10 | 0 | 2 | 2 | 11 | 10 | 0 | 0 | 3 | 3 | 3 | 3 | 16 | 4 | 18 | 5 | 6 | 6 | 3 | 17 | 17 | 14 | 4:50 | 0 | 24 | 108 | 0 | 180 | 96 | 120 | 24 | 96 | 120 | 144 | 24 | 0 | 12 | 12 | 0 | 120 | 0 | 120 | 0 | 24 | 24 | 132 | 120 | 0 | 0 | 36 | 36 | 36 | 36 | 192 | 48 | 216 | 60 | 72 | 72 | 36 | 204 | 204 | 168 |  | 4:50 | 0 | 24 | 108 | 0 | 180 |  | 96 | 120 | 24 | 96 | 120 |  | 144 | 24 | 0 | 12 | 12 |  | 0 | 120 | 0 | 120 | 0 |  | 24 | 24 | 132 | 120 | 0 |  | 0 | 36 | 36 | 36 | 36 |  | 192 | 48 | 216 | 60 | 72 |  | 72 | 36 | 204 | 204 | 168 | 2916 | 2916 | 5832 | 5832 | 5.832 | 5.832
4:55 | 0 | 1 | 8 | 0 | 14 | 9 | 10 | 0 | 10 | 9 | 10 | 2 | 0 | 2 | 2 | 0 | 9 | 0 | 9 | 0 | 3 | 3 | 11 | 10 | 0 | 0 | 0 | 2 | 2 | 2 | 17 | 3 | 17 | 5 | 5 | 5 | 4 | 16 | 15 | 5 | 4:55 | 0 | 12 | 96 | 0 | 168 | 108 | 120 | 0 | 120 | 108 | 120 | 24 | 0 | 24 | 24 | 0 | 108 | 0 | 108 | 0 | 36 | 36 | 132 | 120 | 0 | 0 | 0 | 24 | 24 | 24 | 204 | 36 | 204 | 60 | 60 | 60 | 48 | 192 | 180 | 60 |  | 4:55 | 0 | 12 | 96 | 0 | 168 |  | 108 | 120 | 0 | 120 | 108 |  | 120 | 24 | 0 | 24 | 24 |  | 0 | 108 | 0 | 108 | 0 |  | 36 | 36 | 132 | 120 | 0 |  | 0 | 0 | 24 | 24 | 24 |  | 204 | 36 | 204 | 60 | 60 |  | 60 | 48 | 192 | 180 | 60 | 2640 | 2640 | 5280 | 5280 | 5.28 | 5.28
5:00 | 0 | 2 | 8 | 0 | 14 | 9 | 9 | 0 | 10 | 9 | 10 | 1 | 0 | 1 | 1 | 0 | 9 | 0 | 9 | 0 | 3 | 2 | 11 | 9 | 0 | 0 | 0 | 4 | 3 | 3 | 13 | 4 | 16 | 5 | 17 | 5 | 4 | 9 | 15 | 4 | 5:00 | 0 | 24 | 96 | 0 | 168 | 108 | 108 | 0 | 120 | 108 | 120 | 12 | 0 | 12 | 12 | 0 | 108 | 0 | 108 | 0 | 36 | 24 | 132 | 108 | 0 | 0 | 0 | 48 | 36 | 36 | 156 | 48 | 192 | 60 | 204 | 60 | 48 | 108 | 180 | 48 |  | 5:00 | 0 | 24 | 96 | 0 | 168 |  | 108 | 108 | 0 | 120 | 108 |  | 120 | 12 | 0 | 12 | 12 |  | 0 | 108 | 0 | 108 | 0 |  | 36 | 24 | 132 | 108 | 0 |  | 0 | 0 | 48 | 36 | 36 |  | 156 | 48 | 192 | 60 | 204 |  | 60 | 48 | 108 | 180 | 48 | 2628 | 2628 | 5256 | 5256 | 5.256 | 5.256
5:05 | 0 | 1 | 9 | 0 | 14 | 5 | 9 | 0 | 10 | 9 | 9 | 2 | 0 | 2 | 11 | 0 | 10 | 0 | 9 | 0 | 2 | 3 | 10 | 5 | 0 | 0 | 0 | 12 | 2 | 2 | 5 | 3 | 16 | 5 | 17 | 6 | 4 | 5 | 15 | 5 | 5:05 | 0 | 12 | 108 | 0 | 168 | 60 | 108 | 0 | 120 | 108 | 108 | 24 | 0 | 24 | 132 | 0 | 120 | 0 | 108 | 0 | 24 | 36 | 120 | 60 | 0 | 0 | 0 | 144 | 24 | 24 | 60 | 36 | 192 | 60 | 204 | 72 | 48 | 60 | 180 | 60 |  | 5:05 | 0 | 12 | 108 | 0 | 168 |  | 60 | 108 | 0 | 120 | 108 |  | 108 | 24 | 0 | 24 | 132 |  | 0 | 120 | 0 | 108 | 0 |  | 24 | 36 | 120 | 60 | 0 |  | 0 | 0 | 144 | 24 | 24 |  | 60 | 36 | 192 | 60 | 204 |  | 72 | 48 | 60 | 180 | 60 | 2604 | 2604 | 5208 | 5208 | 5.208 | 5.208
5:10 | 0 | 2 | 9 | 0 | 14 | 1 | 9 | 0 | 9 | 9 | 10 | 2 | 0 | 1 | 10 | 0 | 9 | 0 | 8 | 0 | 3 | 2 | 10 | 3 | 0 | 0 | 0 | 12 | 3 | 3 | 6 | 17 | 15 | 5 | 16 | 5 | 6 | 5 | 10 | 5 | 5:10 | 0 | 24 | 108 | 0 | 168 | 12 | 108 | 0 | 108 | 108 | 120 | 24 | 0 | 12 | 120 | 0 | 108 | 0 | 96 | 0 | 36 | 24 | 120 | 36 | 0 | 0 | 0 | 144 | 36 | 36 | 72 | 204 | 180 | 60 | 192 | 60 | 72 | 60 | 120 | 60 |  | 5:10 | 0 | 24 | 108 | 0 | 168 |  | 12 | 108 | 0 | 108 | 108 |  | 120 | 24 | 0 | 12 | 120 |  | 0 | 108 | 0 | 96 | 0 |  | 36 | 24 | 120 | 36 | 0 |  | 0 | 0 | 144 | 36 | 36 |  | 72 | 204 | 180 | 60 | 192 |  | 60 | 72 | 60 | 120 | 60 | 2628 | 2628 | 5256 | 5256 | 5.256 | 5.256
5:15 | 0 | 1 | 3 | 0 | 13 | 1 | 9 | 0 | 9 | 9 | 9 | 1 | 1 | 2 | 9 | 0 | 6 | 0 | 9 | 9 | 3 | 2 | 10 | 2 | 0 | 0 | 0 | 11 | 3 | 3 | 5 | 16 | 15 | 5 | 16 | 5 | 16 | 5 | 4 | 5 | 5:15 | 0 | 12 | 36 | 0 | 156 | 12 | 108 | 0 | 108 | 108 | 108 | 12 | 12 | 24 | 108 | 0 | 72 | 0 | 108 | 108 | 36 | 24 | 120 | 24 | 0 | 0 | 0 | 132 | 36 | 36 | 60 | 192 | 180 | 60 | 192 | 60 | 192 | 60 | 48 | 60 |  | 5:15 | 0 | 12 | 36 | 0 | 156 |  | 12 | 108 | 0 | 108 | 108 |  | 108 | 12 | 12 | 24 | 108 |  | 0 | 72 | 0 | 108 | 108 |  | 36 | 24 | 120 | 24 | 0 |  | 0 | 0 | 132 | 36 | 36 |  | 60 | 192 | 180 | 60 | 192 |  | 60 | 192 | 60 | 48 | 60 | 2604 | 2604 | 5208 | 5208 | 5.208 | 5.208
5:20 | 0 | 2 | 0 | 0 | 14 | 0 | 8 | 5 | 9 | 7 | 9 | 2 | 11 | 7 | 9 | 0 | 1 | 7 | 7 | 10 | 3 | 3 | 6 | 3 | 0 | 0 | 0 | 11 | 2 | 2 | 6 | 15 | 5 | 17 | 16 | 13 | 16 | 5 | 3 | 5 | 5:20 | 0 | 24 | 0 | 0 | 168 | 0 | 96 | 60 | 108 | 84 | 108 | 24 | 132 | 84 | 108 | 0 | 12 | 84 | 84 | 120 | 36 | 36 | 72 | 36 | 0 | 0 | 0 | 132 | 24 | 24 | 72 | 180 | 60 | 204 | 192 | 156 | 192 | 60 | 36 | 60 |  | 5:20 | 0 | 24 | 0 | 0 | 168 |  | 0 | 96 | 60 | 108 | 84 |  | 108 | 24 | 132 | 84 | 108 |  | 0 | 12 | 84 | 84 | 120 |  | 36 | 36 | 72 | 36 | 0 |  | 0 | 0 | 132 | 24 | 24 |  | 72 | 180 | 60 | 204 | 192 |  | 156 | 192 | 60 | 36 | 60 | 2868 | 2868 | 5736 | 5736 | 5.736 | 5.736
5:25 | 0 | 8 | 0 | 2 | 13 | 1 | 1 | 11 | 2 | 1 | 9 | 2 | 10 | 11 | 9 | 0 | 2 | 11 | 0 | 10 | 2 | 2 | 3 | 2 | 0 | 0 | 0 | 10 | 3 | 3 | 5 | 14 | 4 | 16 | 9 | 18 | 15 | 5 | 3 | 18 | 5:25 | 0 | 96 | 0 | 24 | 156 | 12 | 12 | 132 | 24 | 12 | 108 | 24 | 120 | 132 | 108 | 0 | 24 | 132 | 0 | 120 | 24 | 24 | 36 | 24 | 0 | 0 | 0 | 120 | 36 | 36 | 60 | 168 | 48 | 192 | 108 | 216 | 180 | 60 | 36 | 216 |  | 5:25 | 0 | 96 | 0 | 24 | 156 |  | 12 | 12 | 132 | 24 | 12 |  | 108 | 24 | 120 | 132 | 108 |  | 0 | 24 | 132 | 0 | 120 |  | 24 | 24 | 36 | 24 | 0 |  | 0 | 0 | 120 | 36 | 36 |  | 60 | 168 | 48 | 192 | 108 |  | 216 | 180 | 60 | 36 | 216 | 2820 | 2820 | 5640 | 5640 | 5.64 | 5.64
5:30 | 11 | 10 | 0 | 11 | 14 | 2 | 0 | 10 | 0 | 0 | 5 | 1 | 10 | 10 | 9 | 0 | 1 | 10 | 0 | 9 | 3 | 3 | 3 | 3 | 0 | 0 | 0 | 10 | 2 | 2 | 6 | 15 | 5 | 17 | 5 | 17 | 15 | 10 | 4 | 16 | 5:30 | 132 | 120 | 0 | 132 | 168 | 24 | 0 | 120 | 0 | 0 | 60 | 12 | 120 | 120 | 108 | 0 | 12 | 120 | 0 | 108 | 36 | 36 | 36 | 36 | 0 | 0 | 0 | 120 | 24 | 24 | 72 | 180 | 60 | 204 | 60 | 204 | 180 | 120 | 48 | 192 |  | 5:30 | 132 | 120 | 0 | 132 | 168 |  | 24 | 0 | 120 | 0 | 0 |  | 60 | 12 | 120 | 120 | 108 |  | 0 | 12 | 120 | 0 | 108 |  | 36 | 36 | 36 | 36 | 0 |  | 0 | 0 | 120 | 24 | 24 |  | 72 | 180 | 60 | 204 | 60 |  | 204 | 180 | 120 | 48 | 192 | 2988 | 2988 | 5976 | 5976 | 5.976 | 5.976
5:35 | 10 | 10 | 0 | 10 | 6 | 2 | 1 | 10 | 2 | 1 | 2 | 3 | 10 | 10 | 9 | 2 | 2 | 10 | 0 | 9 | 3 | 2 | 2 | 2 | 0 | 0 | 0 | 10 | 6 | 3 | 5 | 5 | 5 | 16 | 5 | 16 | 10 | 17 | 3 | 17 | 5:35 | 120 | 120 | 0 | 120 | 72 | 24 | 12 | 120 | 24 | 12 | 24 | 36 | 120 | 120 | 108 | 24 | 24 | 120 | 0 | 108 | 36 | 24 | 24 | 24 | 0 | 0 | 0 | 120 | 72 | 36 | 60 | 60 | 60 | 192 | 60 | 192 | 120 | 204 | 36 | 204 |  | 5:35 | 120 | 120 | 0 | 120 | 72 |  | 24 | 12 | 120 | 24 | 12 |  | 24 | 36 | 120 | 120 | 108 |  | 24 | 24 | 120 | 0 | 108 |  | 36 | 24 | 24 | 24 | 0 |  | 0 | 0 | 120 | 72 | 36 |  | 60 | 60 | 60 | 192 | 60 |  | 192 | 120 | 204 | 36 | 204 | 2832 | 2832 | 5664 | 5664 | 5.664 | 5.664
5:40 | 10 | 10 | 0 | 10 | 6 | 2 | 2 | 10 | 2 | 2 | 2 | 2 | 9 | 9 | 9 | 2 | 2 | 9 | 0 | 9 | 3 | 3 | 3 | 2 | 0 | 0 | 0 | 8 | 13 | 2 | 16 | 3 | 5 | 16 | 5 | 17 | 4 | 17 | 6 | 16 | 5:40 | 120 | 120 | 0 | 120 | 72 | 24 | 24 | 120 | 24 | 24 | 24 | 24 | 108 | 108 | 108 | 24 | 24 | 108 | 0 | 108 | 36 | 36 | 36 | 24 | 0 | 0 | 0 | 96 | 156 | 24 | 192 | 36 | 60 | 192 | 60 | 204 | 48 | 204 | 72 | 192 |  | 5:40 | 120 | 120 | 0 | 120 | 72 |  | 24 | 24 | 120 | 24 | 24 |  | 24 | 24 | 108 | 108 | 108 |  | 24 | 24 | 108 | 0 | 108 |  | 36 | 36 | 36 | 24 | 0 |  | 0 | 0 | 96 | 156 | 24 |  | 192 | 36 | 60 | 192 | 60 |  | 204 | 48 | 204 | 72 | 192 | 2952 | 2952 | 5904 | 5904 | 5.904 | 5.904
5:45 | 9 | 9 | 0 | 9 | 6 | 2 | 2 | 9 | 1 | 2 | 2 | 2 | 9 | 9 | 2 | 2 | 2 | 10 | 0 | 9 | 2 | 2 | 2 | 3 | 0 | 0 | 0 | 2 | 11 | 3 | 18 | 3 | 5 | 15 | 5 | 6 | 3 | 17 | 16 | 10 | 5:45 | 108 | 108 | 0 | 108 | 72 | 24 | 24 | 108 | 12 | 24 | 24 | 24 | 108 | 108 | 24 | 24 | 24 | 120 | 0 | 108 | 24 | 24 | 24 | 36 | 0 | 0 | 0 | 24 | 132 | 36 | 216 | 36 | 60 | 180 | 60 | 72 | 36 | 204 | 192 | 120 |  | 5:45 | 108 | 108 | 0 | 108 | 72 |  | 24 | 24 | 108 | 12 | 24 |  | 24 | 24 | 108 | 108 | 24 |  | 24 | 24 | 120 | 0 | 108 |  | 24 | 24 | 24 | 36 | 0 |  | 0 | 0 | 24 | 132 | 36 |  | 216 | 36 | 60 | 180 | 60 |  | 72 | 36 | 204 | 192 | 120 | 2628 | 2628 | 5256 | 5256 | 5.256 | 5.256
5:50 | 9 | 9 | 0 | 9 | 7 | 2 | 2 | 10 | 2 | 2 | 2 | 2 | 10 | 10 | 2 | 2 | 2 | 9 | 0 | 9 | 4 | 3 | 3 | 2 | 0 | 0 | 0 | 3 | 12 | 2 | 17 | 3 | 5 | 7 | 5 | 6 | 4 | 12 | 15 | 5 | 5:50 | 108 | 108 | 0 | 108 | 84 | 24 | 24 | 120 | 24 | 24 | 24 | 24 | 120 | 120 | 24 | 24 | 24 | 108 | 0 | 108 | 48 | 36 | 36 | 24 | 0 | 0 | 0 | 36 | 144 | 24 | 204 | 36 | 60 | 84 | 60 | 72 | 48 | 144 | 180 | 60 |  | 5:50 | 108 | 108 | 0 | 108 | 84 |  | 24 | 24 | 120 | 24 | 24 |  | 24 | 24 | 120 | 120 | 24 |  | 24 | 24 | 108 | 0 | 108 |  | 48 | 36 | 36 | 24 | 0 |  | 0 | 0 | 36 | 144 | 24 |  | 204 | 36 | 60 | 84 | 60 |  | 72 | 48 | 144 | 180 | 60 | 2496 | 2496 | 4992 | 4992 | 4.992 | 4.992
5:55 | 9 | 9 | 0 | 10 | 6 | 1 | 2 | 9 | 2 | 2 | 2 | 2 | 9 | 10 | 2 | 3 | 2 | 9 | 0 | 2 | 13 | 2 | 2 | 3 | 0 | 0 | 0 | 2 | 10 | 3 | 17 | 3 | 5 | 5 | 17 | 5 | 4 | 5 | 14 | 4 | 5:55 | 108 | 108 | 0 | 120 | 72 | 12 | 24 | 108 | 24 | 24 | 24 | 24 | 108 | 120 | 24 | 36 | 24 | 108 | 0 | 24 | 156 | 24 | 24 | 36 | 0 | 0 | 0 | 24 | 120 | 36 | 204 | 36 | 60 | 60 | 204 | 60 | 48 | 60 | 168 | 48 |  | 5:55 | 108 | 108 | 0 | 120 | 72 |  | 12 | 24 | 108 | 24 | 24 |  | 24 | 24 | 108 | 120 | 24 |  | 36 | 24 | 108 | 0 | 24 |  | 156 | 24 | 24 | 36 | 0 |  | 0 | 0 | 24 | 120 | 36 |  | 204 | 36 | 60 | 60 | 204 |  | 60 | 48 | 60 | 168 | 48 | 2460 | 2460 | 4920 | 4920 | 4.92 | 4.92
6:00 | 9 | 9 | 0 | 9 | 6 | 2 | 1 | 9 | 2 | 1 | 2 | 2 | 9 | 6 | 2 | 11 | 2 | 9 | 0 | 0 | 11 | 5 | 3 | 2 | 0 | 0 | 0 | 2 | 11 | 2 | 16 | 4 | 15 | 5 | 18 | 5 | 4 | 5 | 15 | 4 | 6:00 | 108 | 108 | 0 | 108 | 72 | 24 | 12 | 108 | 24 | 12 | 24 | 24 | 108 | 72 | 24 | 132 | 24 | 108 | 0 | 0 | 132 | 60 | 36 | 24 | 0 | 0 | 0 | 24 | 132 | 24 | 192 | 48 | 180 | 60 | 216 | 60 | 48 | 60 | 180 | 48 |  | 6:00 | 108 | 108 | 0 | 108 | 72 |  | 24 | 12 | 108 | 24 | 12 |  | 24 | 24 | 108 | 72 | 24 |  | 132 | 24 | 108 | 0 | 0 |  | 132 | 60 | 36 | 24 | 0 |  | 0 | 0 | 24 | 132 | 24 |  | 192 | 48 | 180 | 60 | 216 |  | 60 | 48 | 60 | 180 | 48 | 2616 | 2616 | 5232 | 5232 | 5.232 | 5.232
6:05 | 9 | 7 | 0 | 9 | 6 | 2 | 2 | 5 | 1 | 2 | 1 | 7 | 2 | 2 | 2 | 11 | 2 | 5 | 0 | 1 | 12 | 12 | 2 | 3 | 0 | 0 | 0 | 3 | 10 | 3 | 10 | 3 | 16 | 5 | 17 | 6 | 3 | 5 | 12 | 5 | 6:05 | 108 | 84 | 0 | 108 | 72 | 24 | 24 | 60 | 12 | 24 | 12 | 84 | 24 | 24 | 24 | 132 | 24 | 60 | 0 | 12 | 144 | 144 | 24 | 36 | 0 | 0 | 0 | 36 | 120 | 36 | 120 | 36 | 192 | 60 | 204 | 72 | 36 | 60 | 144 | 60 |  | 6:05 | 108 | 84 | 0 | 108 | 72 |  | 24 | 24 | 60 | 12 | 24 |  | 12 | 84 | 24 | 24 | 24 |  | 132 | 24 | 60 | 0 | 12 |  | 144 | 144 | 24 | 36 | 0 |  | 0 | 0 | 36 | 120 | 36 |  | 120 | 36 | 192 | 60 | 204 |  | 72 | 36 | 60 | 144 | 60 | 2436 | 2436 | 4872 | 4872 | 4.872 | 4.872
6:10 | 6 | 0 | 0 | 6 | 7 | 2 | 2 | 2 | 2 | 2 | 2 | 11 | 1 | 1 | 2 | 10 | 2 | 1 | 0 | 1 | 10 | 11 | 3 | 2 | 0 | 0 | 0 | 2 | 10 | 2 | 6 | 4 | 17 | 66 | 16 | 5 | 15 | 5 | 3 | 5 | 6:10 | 72 | 0 | 0 | 72 | 84 | 24 | 24 | 24 | 24 | 24 | 24 | 132 | 12 | 12 | 24 | 120 | 24 | 12 | 0 | 12 | 120 | 132 | 36 | 24 | 0 | 0 | 0 | 24 | 120 | 24 | 72 | 48 | 204 | 792 | 192 | 60 | 180 | 60 | 36 | 60 |  | 6:10 | 72 | 0 | 0 | 72 | 84 |  | 24 | 24 | 24 | 24 | 24 |  | 24 | 132 | 12 | 12 | 24 |  | 120 | 24 | 12 | 0 | 12 |  | 120 | 132 | 36 | 24 | 0 |  | 0 | 0 | 24 | 120 | 24 |  | 72 | 48 | 204 | 792 | 192 |  | 60 | 180 | 60 | 36 | 60 | 2904 | 2904 | 5808 | 5808 | 5.808 | 5.808
6:15 | 1 | 0 | 0 | 2 | 6 | 2 | 2 | 1 | 2 | 2 | 2 | 11 | 2 | 2 | 2 | 10 | 2 | 2 | 0 | 0 | 10 | 10 | 2 | 3 | 0 | 0 | 0 | 3 | 4 | 3 | 5 | 15 | 15 | 20 | 16 | 5 | 16 | 6 | 3 | 9 | 6:15 | 12 | 0 | 0 | 24 | 72 | 24 | 24 | 12 | 24 | 24 | 24 | 132 | 24 | 24 | 24 | 120 | 24 | 24 | 0 | 0 | 120 | 120 | 24 | 36 | 0 | 0 | 0 | 36 | 48 | 36 | 60 | 180 | 180 | 240 | 192 | 60 | 192 | 72 | 36 | 108 |  | 6:15 | 12 | 0 | 0 | 24 | 72 |  | 24 | 24 | 12 | 24 | 24 |  | 24 | 132 | 24 | 24 | 24 |  | 120 | 24 | 24 | 0 | 0 |  | 120 | 120 | 24 | 36 | 0 |  | 0 | 0 | 36 | 48 | 36 |  | 60 | 180 | 180 | 240 | 192 |  | 60 | 192 | 72 | 36 | 108 | 2352 | 2352 | 4704 | 4704 | 4.704 | 4.704
6:20 | 0 | 0 | 0 | 1 | 7 | 1 | 2 | 2 | 2 | 2 | 2 | 10 | 2 | 2 | 2 | 9 | 2 | 2 | 9 | 1 | 6 | 10 | 3 | 3 | 0 | 0 | 0 | 2 | 2 | 2 | 6 | 16 | 16 | 22 | 7 | 18 | 15 | 5 | 4 | 17 | 6:20 | 0 | 0 | 0 | 12 | 84 | 12 | 24 | 24 | 24 | 24 | 24 | 120 | 24 | 24 | 24 | 108 | 24 | 24 | 108 | 12 | 72 | 120 | 36 | 36 | 0 | 0 | 0 | 24 | 24 | 24 | 72 | 192 | 192 | 264 | 84 | 216 | 180 | 60 | 48 | 204 |  | 6:20 | 0 | 0 | 0 | 12 | 84 |  | 12 | 24 | 24 | 24 | 24 |  | 24 | 120 | 24 | 24 | 24 |  | 108 | 24 | 24 | 108 | 12 |  | 72 | 120 | 36 | 36 | 0 |  | 0 | 0 | 24 | 24 | 24 |  | 72 | 192 | 192 | 264 | 84 |  | 216 | 180 | 60 | 48 | 204 | 2544 | 2544 | 5088 | 5088 | 5.088 | 5.088
6:25 | 0 | 0 | 1 | 2 | 6 | 2 | 1 | 2 | 2 | 1 | 2 | 10 | 2 | 2 | 2 | 10 | 2 | 2 | 3 | 1 | 3 | 10 | 2 | 13 | 0 | 0 | 0 | 3 | 3 | 3 | 5 | 14 | 16 | 49 | 5 | 17 | 15 | 17 | 3 | 17 | 6:25 | 0 | 0 | 12 | 24 | 72 | 24 | 12 | 24 | 24 | 12 | 24 | 120 | 24 | 24 | 24 | 120 | 24 | 24 | 36 | 12 | 36 | 120 | 24 | 156 | 0 | 0 | 0 | 36 | 36 | 36 | 60 | 168 | 192 | 588 | 60 | 204 | 180 | 204 | 36 | 204 |  | 6:25 | 0 | 0 | 12 | 24 | 72 |  | 24 | 12 | 24 | 24 | 12 |  | 24 | 120 | 24 | 24 | 24 |  | 120 | 24 | 24 | 36 | 12 |  | 36 | 120 | 24 | 156 | 0 |  | 0 | 0 | 36 | 36 | 36 |  | 60 | 168 | 192 | 588 | 60 |  | 204 | 180 | 204 | 36 | 204 | 2976 | 2976 | 5952 | 5952 | 5.952 | 5.952
6:30 | 0 | 0 | 8 | 1 | 6 | 11 | 2 | 2 | 2 | 2 | 2 | 9 | 2 | 2 | 2 | 9 | 1 | 2 | 0 | 1 | 3 | 9 | 3 | 16 | 0 | 0 | 0 | 2 | 2 | 2 | 5 | 15 | 5 | 106 | 5 | 16 | 10 | 17 | 4 | 16 | 6:30 | 0 | 0 | 96 | 12 | 72 | 132 | 24 | 24 | 24 | 24 | 24 | 108 | 24 | 24 | 24 | 108 | 12 | 24 | 0 | 12 | 36 | 108 | 36 | 192 | 0 | 0 | 0 | 24 | 24 | 24 | 60 | 180 | 60 | 1272 | 60 | 192 | 120 | 204 | 48 | 192 |  | 6:30 | 0 | 0 | 96 | 12 | 72 |  | 132 | 24 | 24 | 24 | 24 |  | 24 | 108 | 24 | 24 | 24 |  | 108 | 12 | 24 | 0 | 12 |  | 36 | 108 | 36 | 192 | 0 |  | 0 | 0 | 24 | 24 | 24 |  | 60 | 180 | 60 | 1250 | 60 |  | 192 | 120 | 204 | 48 | 192 | 3600 | 3578 | 7200 | 7156 | 7.2 | 7.156
6:35 | 0 | 0 | 13 | 2 | 7 | 11 | 2 | 2 | 2 | 2 | 2 | 10 | 1 | 2 | 1 | 10 | 2 | 1 | 0 | 2 | 2 | 8 | 2 | 12 | 0 | 0 | 0 | 3 | 3 | 3 | 5 | 14 | 5 | 33 | 6 | 17 | 4 | 16 | 3 | 16 | 6:35 | 0 | 0 | 156 | 24 | 84 | 132 | 24 | 24 | 24 | 24 | 24 | 120 | 12 | 24 | 12 | 120 | 24 | 12 | 0 | 24 | 24 | 96 | 24 | 144 | 0 | 0 | 0 | 36 | 36 | 36 | 60 | 168 | 60 | 396 | 72 | 204 | 48 | 192 | 36 | 192 |  | 6:35 | 0 | 0 | 156 | 24 | 84 |  | 132 | 24 | 24 | 24 | 24 |  | 24 | 120 | 12 | 24 | 12 |  | 120 | 24 | 12 | 0 | 24 |  | 24 | 96 | 24 | 144 | 0 |  | 0 | 0 | 36 | 36 | 36 |  | 60 | 168 | 60 | 396 | 72 |  | 204 | 48 | 192 | 36 | 192 | 2688 | 2688 | 5376 | 5376 | 5.376 | 5.376
6:40 | 0 | 1 | 18 | 2 | 6 | 10 | 2 | 1 | 1 | 2 | 2 | 9 | 2 | 2 | 3 | 4 | 2 | 2 | 0 | 2 | 3 | 2 | 3 | 16 | 0 | 8 | 0 | 2 | 2 | 6 | 6 | 5 | 5 | 52 | 5 | 10 | 4 | 16 | 14 | 5 | 6:40 | 0 | 12 | 216 | 24 | 72 | 120 | 24 | 12 | 12 | 24 | 24 | 108 | 24 | 24 | 36 | 48 | 24 | 24 | 0 | 24 | 36 | 24 | 36 | 192 | 0 | 96 | 0 | 24 | 24 | 72 | 72 | 60 | 60 | 624 | 60 | 120 | 48 | 192 | 168 | 60 |  | 6:40 | 0 | 12 | 216 | 24 | 72 |  | 120 | 24 | 12 | 12 | 24 |  | 24 | 108 | 24 | 24 | 36 |  | 48 | 24 | 24 | 0 | 24 |  | 36 | 24 | 36 | 192 | 0 |  | 96 | 0 | 24 | 24 | 72 |  | 72 | 60 | 60 | 624 | 60 |  | 120 | 48 | 192 | 168 | 60 | 2820 | 2820 | 5640 | 5640 | 5.64 | 5.64
6:45 | 0 | 1 | 18 | 1 | 12 | 10 | 1 | 2 | 2 | 2 | 2 | 4 | 2 | 2 | 1 | 2 | 6 | 2 | 0 | 1 | 3 | 3 | 2 | 13 | 0 | 11 | 0 | 2 | 3 | 11 | 18 | 3 | 5 | 84 | 9 | 6 | 4 | 6 | 15 | 5 | 6:45 | 0 | 12 | 216 | 12 | 144 | 120 | 12 | 24 | 24 | 24 | 24 | 48 | 24 | 24 | 12 | 24 | 72 | 24 | 0 | 12 | 36 | 36 | 24 | 156 | 0 | 132 | 0 | 24 | 36 | 132 | 216 | 36 | 60 | 1008 | 108 | 72 | 48 | 72 | 180 | 60 |  | 6:45 | 0 | 12 | 216 | 12 | 144 |  | 120 | 12 | 24 | 24 | 24 |  | 24 | 48 | 24 | 24 | 12 |  | 24 | 72 | 24 | 0 | 12 |  | 36 | 36 | 24 | 156 | 0 |  | 132 | 0 | 24 | 36 | 132 |  | 216 | 36 | 60 | 1008 | 108 |  | 72 | 48 | 72 | 180 | 60 | 3288 | 3288 | 6576 | 6576 | 6.576 | 6.576
6:50 | 0 | 2 | 10 | 2 | 17 | 9 | 2 | 2 | 2 | 10 | 2 | 2 | 2 | 2 | 2 | 2 | 11 | 2 | 0 | 2 | 2 | 2 | 3 | 4 | 0 | 10 | 11 | 3 | 2 | 11 | 17 | 3 | 4 | 59 | 18 | 5 | 3 | 5 | 14 | 5 | 6:50 | 0 | 24 | 120 | 24 | 204 | 108 | 24 | 24 | 24 | 120 | 24 | 24 | 24 | 24 | 24 | 24 | 132 | 24 | 0 | 24 | 24 | 24 | 36 | 48 | 0 | 120 | 132 | 36 | 24 | 132 | 204 | 36 | 48 | 708 | 216 | 60 | 36 | 60 | 168 | 60 |  | 6:50 | 0 | 24 | 120 | 24 | 204 |  | 108 | 24 | 24 | 24 | 120 |  | 24 | 24 | 24 | 24 | 24 |  | 24 | 132 | 24 | 0 | 24 |  | 24 | 24 | 36 | 48 | 0 |  | 120 | 132 | 36 | 24 | 132 |  | 204 | 36 | 48 | 708 | 216 |  | 60 | 36 | 60 | 168 | 60 | 3168 | 3168 | 6336 | 6336 | 6.336 | 6.336
6:55 | 0 | 3 | 10 | 1 | 15 | 9 | 11 | 2 | 2 | 11 | 9 | 2 | 2 | 1 | 5 | 1 | 11 | 2 | 7 | 2 | 3 | 3 | 2 | 2 | 0 | 10 | 11 | 2 | 3 | 11 | 17 | 4 | 5 | 31 | 16 | 5 | 4 | 5 | 15 | 4 | 6:55 | 0 | 36 | 120 | 12 | 180 | 108 | 132 | 24 | 24 | 132 | 108 | 24 | 24 | 12 | 60 | 12 | 132 | 24 | 84 | 24 | 36 | 36 | 24 | 24 | 0 | 120 | 132 | 24 | 36 | 132 | 204 | 48 | 60 | 372 | 192 | 60 | 48 | 60 | 180 | 48 |  | 6:55 | 0 | 27 | 90 | 9 | 135 | 0 | 81 | 99 | 18 | 18 | 99 | 0 | 81 | 18 | 18 | 9 | 45 | 0 | 9 | 99 | 18 | 63 | 18 | 0 | 27 | 27 | 18 | 18 | 0 | 0 | 90 | 99 | 18 | 27 | 99 | 0 | 153 | 36 | 45 | 279 | 144 | 0 | 45 | 36 | 45 | 135 | 36 | 3108 | 2331 | 6216 | 4662 | 6.216 | 4.662
7:00 | 0 | 2 | 11 | 2 | 16 | 10 | 10 | 3 | 12 | 10 | 11 | 2 | 9 | 2 | 11 | 2 | 10 | 2 | 10 | 2 | 3 | 2 | 3 | 3 | 0 | 23 | 9 | 3 | 2 | 10 | 16 | 3 | 5 | 30 | 16 | 5 | 4 | 5 | 12 | 5 | 7:00 | 0 | 24 | 132 | 24 | 192 | 120 | 120 | 36 | 144 | 120 | 132 | 24 | 108 | 24 | 132 | 24 | 120 | 24 | 120 | 24 | 36 | 24 | 36 | 36 | 0 | 276 | 108 | 36 | 24 | 120 | 192 | 36 | 60 | 360 | 192 | 60 | 48 | 60 | 144 | 60 |  | 7:00 | 0 | 18 | 99 | 18 | 144 | 0 | 90 | 90 | 27 | 108 | 90 | 0 | 99 | 18 | 81 | 18 | 99 | 0 | 18 | 90 | 18 | 90 | 18 | 0 | 27 | 18 | 27 | 27 | 0 | 0 | 207 | 81 | 27 | 18 | 90 | 0 | 144 | 27 | 45 | 270 | 144 | 0 | 45 | 36 | 45 | 108 | 45 | 3552 | 2664 | 7104 | 5328 | 7.104 | 5.328
7:05 | 0 | 1 | 10 | 2 | 16 | 11 | 10 | 3 | 11 | 10 | 11 | 2 | 8 | 2 | 11 | 2 | 9 | 2 | 10 | 3 | 2 | 2 | 2 | 2 | 0 | 23 | 10 | 2 | 3 | 10 | 16 | 4 | 5 | 31 | 18 | 5 | 13 | 5 | 4 | 5 | 7:05 | 0 | 12 | 120 | 24 | 192 | 132 | 120 | 36 | 132 | 120 | 132 | 24 | 96 | 24 | 132 | 24 | 108 | 24 | 120 | 36 | 24 | 24 | 24 | 24 | 0 | 276 | 120 | 24 | 36 | 120 | 192 | 48 | 60 | 372 | 216 | 60 | 156 | 60 | 48 | 60 |  | 7:05 | 0 | 9 | 90 | 18 | 144 | 0 | 99 | 90 | 27 | 99 | 90 | 0 | 99 | 18 | 72 | 18 | 99 | 0 | 18 | 81 | 18 | 90 | 27 | 0 | 18 | 18 | 18 | 18 | 0 | 0 | 207 | 90 | 18 | 27 | 90 | 0 | 144 | 36 | 45 | 279 | 162 | 0 | 45 | 117 | 45 | 36 | 45 | 3552 | 2664 | 7104 | 5328 | 7.104 | 5.328
7:10 | 1 | 9 | 10 | 3 | 15 | 9 | 10 | 2 | 11 | 11 | 10 | 2 | 2 | 2 | 10 | 2 | 10 | 1 | 10 | 12 | 3 | 3 | 3 | 4 | 0 | 9 | 9 | 3 | 2 | 10 | 10 | 3 | 10 | 23 | 28 | 6 | 15 | 5 | 3 | 23 | 7:10 | 12 | 108 | 120 | 36 | 180 | 108 | 120 | 24 | 132 | 132 | 120 | 24 | 24 | 24 | 120 | 24 | 120 | 12 | 120 | 144 | 36 | 36 | 36 | 48 | 0 | 108 | 108 | 36 | 24 | 120 | 120 | 36 | 120 | 276 | 336 | 72 | 180 | 60 | 36 | 276 |  | 7:10 | 9 | 81 | 90 | 27 | 135 | 0 | 81 | 90 | 18 | 99 | 99 | 0 | 90 | 18 | 18 | 18 | 90 | 0 | 18 | 90 | 9 | 90 | 108 | 0 | 27 | 27 | 27 | 36 | 0 | 0 | 81 | 81 | 27 | 18 | 90 | 0 | 90 | 27 | 90 | 207 | 252 | 0 | 54 | 135 | 45 | 27 | 207 | 3768 | 2826 | 7536 | 5652 | 7.536 | 5.652
7:15 | 11 | 12 | 11 | 1 | 15 | 10 | 10 | 4 | 11 | 10 | 11 | 3 | 2 | 2 | 9 | 3 | 9 | 1 | 9 | 16 | 3 | 2 | 2 | 13 | 0 | 147 | 9 | 2 | 3 | 10 | 24 | 3 | 24 | 20 | 53 | 16 | 15 | 27 | 3 | 53 | 7:15 | 132 | 144 | 132 | 12 | 180 | 120 | 120 | 48 | 132 | 120 | 132 | 36 | 24 | 24 | 108 | 36 | 108 | 12 | 108 | 192 | 36 | 24 | 24 | 156 | 0 | 1764 | 108 | 24 | 36 | 120 | 288 | 36 | 288 | 240 | 636 | 192 | 180 | 324 | 36 | 636 |  | 7:15 | 99 | 108 | 99 | 9 | 135 | 0 | 90 | 90 | 36 | 99 | 90 | 0 | 99 | 27 | 18 | 18 | 81 | 0 | 27 | 81 | 9 | 81 | 144 | 0 | 27 | 18 | 18 | 117 | 0 | 0 | 937.5 | 81 | 18 | 27 | 90 | 0 | 216 | 27 | 216 | 180 | 477 | 0 | 144 | 135 | 243 | 27 | 477 | 7068 | 4915.5 | 14136 | 9831 | 14.136 | 9.831
7:20 | 10 | 10 | 9 | 2 | 15 | 2 | 10 | 4 | 10 | 10 | 10 | 4 | 7 | 2 | 10 | 3 | 10 | 2 | 9 | 16 | 2 | 3 | 3 | 11 | 5 | 43 | 9 | 2 | 3 | 6 | 81 | 16 | 24 | 16 | 92 | 17 | 14 | 94 | 4 | 108 | 7:20 | 120 | 120 | 108 | 24 | 180 | 24 | 120 | 48 | 120 | 120 | 120 | 48 | 84 | 24 | 120 | 36 | 120 | 24 | 108 | 192 | 24 | 36 | 36 | 132 | 60 | 516 | 108 | 24 | 36 | 72 | 972 | 192 | 288 | 192 | 1104 | 204 | 168 | 1128 | 48 | 1296 |  | 7:20 | 90 | 90 | 81 | 18 | 135 | 0 | 18 | 90 | 36 | 90 | 90 | 0 | 90 | 36 | 63 | 18 | 90 | 0 | 27 | 90 | 18 | 81 | 144 | 0 | 18 | 27 | 27 | 99 | 45 | 0 | 387 | 81 | 18 | 27 | 54 | 0 | 729 | 144 | 216 | 144 | 828 | 0 | 153 | 126 | 846 | 36 | 937.5 | 8496 | 6337.5 | 16992 | 12675 | 16.992 | 12.675
7:25 | 10 | 12 | 5 | 2 | 14 | 4 | 10 | 6 | 11 | 11 | 11 | 3 | 11 | 4 | 9 | 4 | 9 | 2 | 8 | 17 | 3 | 2 | 2 | 11 | 11 | 7 | 2 | 3 | 2 | 3 | 82 | 15 | 23 | 16 | 25 | 17 | 12 | 85 | 3 | 81 | 7:25 | 120 | 144 | 60 | 24 | 168 | 48 | 120 | 72 | 132 | 132 | 132 | 36 | 132 | 48 | 108 | 48 | 108 | 24 | 96 | 204 | 36 | 24 | 24 | 132 | 132 | 84 | 24 | 36 | 24 | 36 | 984 | 180 | 276 | 192 | 300 | 204 | 144 | 1020 | 36 | 972 |  | 7:25 | 90 | 108 | 45 | 18 | 126 | 0 | 36 | 90 | 54 | 99 | 99 | 0 | 99 | 27 | 99 | 36 | 81 | 0 | 36 | 81 | 18 | 72 | 153 | 0 | 27 | 18 | 18 | 99 | 99 | 0 | 63 | 18 | 27 | 18 | 27 | 0 | 738 | 135 | 207 | 144 | 225 | 0 | 153 | 108 | 765 | 27 | 729 | 6816 | 5112 | 13632 | 10224 | 13.632 | 10.224
7:30 | 11 | 10 | 6 | 10 | 13 | 7 | 10 | 17 | 7 | 10 | 11 | 5 | 11 | 11 | 9 | 4 | 8 | 11 | 9 | 18 | 3 | 3 | 11 | 11 | 10 | 0 | 0 | 2 | 3 | 2 | 66 | 14 | 22 | 16 | 52 | 16 | 4 | 77 | 3 | 81 | 7:30 | 132 | 120 | 72 | 120 | 156 | 84 | 120 | 204 | 84 | 120 | 132 | 60 | 132 | 132 | 108 | 48 | 96 | 132 | 108 | 216 | 36 | 36 | 132 | 132 | 120 | 0 | 0 | 24 | 36 | 24 | 792 | 168 | 264 | 192 | 624 | 192 | 48 | 924 | 36 | 972 |  | 7:30 | 99 | 90 | 54 | 90 | 117 | 0 | 63 | 90 | 153 | 63 | 90 | 0 | 99 | 45 | 99 | 99 | 81 | 0 | 36 | 72 | 99 | 81 | 162 | 0 | 27 | 27 | 99 | 99 | 90 | 0 | 0 | 0 | 18 | 27 | 18 | 0 | 594 | 126 | 198 | 144 | 468 | 0 | 144 | 36 | 693 | 27 | 729 | 7128 | 5346 | 14256 | 10692 | 14.256 | 10.692
7:35 | 10 | 10 | 4 | 12 | 9 | 6 | 9 | 18 | 3 | 4 | 9 | 6 | 10 | 11 | 7 | 6 | 2 | 12 | 2 | 18 | 2 | 2 | 11 | 10 | 10 | 0 | 0 | 12 | 2 | 3 | 69 | 14 | 23 | 56 | 88 | 13 | 3 | 69 | 16 | 78 | 7:35 | 120 | 120 | 48 | 144 | 108 | 72 | 108 | 216 | 36 | 48 | 108 | 72 | 120 | 132 | 84 | 72 | 24 | 144 | 24 | 216 | 24 | 24 | 132 | 120 | 120 | 0 | 0 | 144 | 24 | 36 | 828 | 168 | 276 | 672 | 1056 | 156 | 36 | 828 | 192 | 936 |  | 7:35 | 90 | 90 | 36 | 108 | 81 | 0 | 54 | 81 | 162 | 27 | 36 | 0 | 81 | 54 | 90 | 99 | 63 | 0 | 54 | 18 | 108 | 18 | 162 | 0 | 18 | 18 | 99 | 90 | 90 | 0 | 0 | 0 | 108 | 18 | 27 | 0 | 621 | 126 | 207 | 504 | 792 | 0 | 117 | 27 | 621 | 144 | 702 | 7788 | 5841 | 15576 | 11682 | 15.576 | 11.682
7:40 | 10 | 11 | 6 | 11 | 9 | 6 | 2 | 17 | 3 | 3 | 3 | 8 | 10 | 11 | 3 | 7 | 2 | 11 | 0 | 20 | 3 | 3 | 12 | 10 | 9 | 0 | 0 | 11 | 2 | 2 | 70 | 14 | 14 | 32 | 44 | 5 | 4 | 76 | 15 | 73 | 7:40 | 120 | 132 | 72 | 132 | 108 | 72 | 24 | 204 | 36 | 36 | 36 | 96 | 120 | 132 | 36 | 84 | 24 | 132 | 0 | 240 | 36 | 36 | 144 | 120 | 108 | 0 | 0 | 132 | 24 | 24 | 840 | 168 | 168 | 384 | 528 | 60 | 48 | 912 | 180 | 876 |  | 7:40 | 90 | 99 | 54 | 99 | 81 | 0 | 54 | 18 | 153 | 27 | 27 | 0 | 27 | 72 | 90 | 99 | 27 | 0 | 63 | 18 | 99 | 0 | 180 | 0 | 27 | 27 | 108 | 90 | 81 | 0 | 0 | 0 | 99 | 18 | 18 | 0 | 630 | 126 | 126 | 288 | 396 | 0 | 45 | 36 | 684 | 135 | 657 | 6624 | 4968 | 13248 | 9936 | 13.248 | 9.936
7:45 | 10 | 10 | 6 | 11 | 8 | 5 | 2 | 18 | 3 | 4 | 2 | 10 | 9 | 11 | 4 | 9 | 2 | 10 | 0 | 14 | 5 | 2 | 10 | 10 | 9 | 0 | 0 | 11 | 3 | 3 | 51 | 5 | 12 | 45 | 46 | 5 | 4 | 62 | 14 | 73 | 7:45 | 120 | 120 | 72 | 132 | 96 | 60 | 24 | 216 | 36 | 48 | 24 | 120 | 108 | 132 | 48 | 108 | 24 | 120 | 0 | 168 | 60 | 24 | 120 | 120 | 108 | 0 | 0 | 132 | 36 | 36 | 612 | 60 | 144 | 540 | 552 | 60 | 48 | 744 | 168 | 876 |  | 7:45 | 90 | 90 | 54 | 99 | 72 | 0 | 45 | 18 | 162 | 27 | 36 | 0 | 18 | 90 | 81 | 99 | 36 | 0 | 81 | 18 | 90 | 0 | 126 | 0 | 45 | 18 | 90 | 90 | 81 | 0 | 0 | 0 | 99 | 27 | 27 | 0 | 459 | 45 | 108 | 405 | 414 | 0 | 45 | 36 | 558 | 126 | 657 | 6216 | 4662 | 12432 | 9324 | 12.432 | 9.324
7:50 | 10 | 4 | 9 | 10 | 10 | 3 | 2 | 19 | 2 | 5 | 3 | 10 | 9 | 10 | 6 | 6 | 3 | 11 | 0 | 12 | 18 | 2 | 10 | 10 | 9 | 0 | 0 | 11 | 2 | 2 | 53 | 3 | 12 | 55 | 45 | 5 | 3 | 37 | 15 | 43 | 7:50 | 120 | 48 | 108 | 120 | 120 | 36 | 24 | 228 | 24 | 60 | 36 | 120 | 108 | 120 | 72 | 72 | 36 | 132 | 0 | 144 | 216 | 24 | 120 | 120 | 108 | 0 | 0 | 132 | 24 | 24 | 636 | 36 | 144 | 660 | 540 | 60 | 36 | 444 | 180 | 516 |  | 7:50 | 90 | 36 | 81 | 90 | 90 | 0 | 27 | 18 | 171 | 18 | 45 | 0 | 27 | 90 | 81 | 90 | 54 | 0 | 54 | 27 | 99 | 0 | 108 | 0 | 162 | 18 | 90 | 90 | 81 | 0 | 0 | 0 | 99 | 18 | 18 | 0 | 477 | 27 | 108 | 495 | 405 | 0 | 45 | 27 | 333 | 135 | 387 | 5748 | 4311 | 11496 | 8622 | 11.496 | 8.622
7:55 | 6 | 3 | 13 | 11 | 10 | 3 | 3 | 18 | 2 | 5 | 3 | 10 | 10 | 10 | 8 | 9 | 3 | 10 | 0 | 13 | 25 | 3 | 10 | 3 | 9 | 0 | 0 | 10 | 3 | 2 | 110 | 3 | 11 | 51 | 45 | 6 | 4 | 25 | 14 | 109 | 7:55 | 72 | 36 | 156 | 132 | 120 | 36 | 36 | 216 | 24 | 60 | 36 | 120 | 120 | 120 | 96 | 108 | 36 | 120 | 0 | 156 | 300 | 36 | 120 | 36 | 108 | 0 | 0 | 120 | 36 | 24 | 1320 | 36 | 132 | 612 | 540 | 72 | 48 | 300 | 168 | 1308 |  | 7:55 | 54 | 27 | 117 | 99 | 90 | 0 | 27 | 27 | 162 | 18 | 45 | 0 | 27 | 90 | 90 | 90 | 72 | 0 | 81 | 27 | 90 | 0 | 117 | 0 | 225 | 27 | 90 | 27 | 81 | 0 | 0 | 0 | 90 | 27 | 18 | 0 | 937.5 | 27 | 99 | 459 | 405 | 0 | 54 | 36 | 225 | 126 | 937.5 | 7116 | 5241 | 14232 | 10482 | 14.232 | 10.482
8:00 | 1 | 3 | 13 | 10 | 10 | 3 | 3 | 21 | 3 | 4 | 5 | 5 | 11 | 11 | 10 | 7 | 2 | 11 | 0 | 14 | 19 | 2 | 16 | 3 | 4 | 0 | 0 | 10 | 2 | 3 | 36 | 4 | 12 | 46 | 44 | 5 | 11 | 25 | 3 | 34 | 8:00 | 12 | 36 | 156 | 120 | 120 | 36 | 36 | 252 | 36 | 48 | 60 | 60 | 132 | 132 | 120 | 84 | 24 | 132 | 0 | 168 | 228 | 24 | 192 | 36 | 48 | 0 | 0 | 120 | 24 | 36 | 432 | 48 | 144 | 552 | 528 | 60 | 132 | 300 | 36 | 408 |  | 8:00 | 9 | 27 | 117 | 90 | 90 | 0 | 27 | 27 | 189 | 27 | 36 | 0 | 45 | 45 | 99 | 99 | 90 | 0 | 63 | 18 | 99 | 0 | 126 | 0 | 171 | 18 | 144 | 27 | 36 | 0 | 0 | 0 | 90 | 18 | 27 | 0 | 324 | 36 | 108 | 414 | 396 | 0 | 45 | 99 | 225 | 27 | 306 | 5112 | 3834 | 10224 | 7668 | 10.224 | 7.668
8:05 | 1 | 4 | 14 | 11 | 11 | 3 | 4 | 20 | 4 | 4 | 5 | 19 | 7 | 10 | 12 | 12 | 3 | 11 | 0 | 14 | 11 | 3 | 17 | 2 | 0 | 0 | 0 | 10 | 3 | 2 | 36 | 3 | 12 | 48 | 35 | 5 | 16 | 29 | 3 | 54 | 8:05 | 12 | 48 | 168 | 132 | 132 | 36 | 48 | 240 | 48 | 48 | 60 | 228 | 84 | 120 | 144 | 144 | 36 | 132 | 0 | 168 | 132 | 36 | 204 | 24 | 0 | 0 | 0 | 120 | 36 | 24 | 432 | 36 | 144 | 576 | 420 | 60 | 192 | 348 | 36 | 648 |  | 8:05 | 9 | 36 | 126 | 99 | 99 | 0 | 27 | 36 | 180 | 36 | 36 | 0 | 45 | 171 | 63 | 90 | 108 | 0 | 108 | 27 | 99 | 0 | 126 | 0 | 99 | 27 | 153 | 18 | 0 | 0 | 0 | 0 | 90 | 27 | 18 | 0 | 324 | 27 | 108 | 432 | 315 | 0 | 45 | 144 | 261 | 27 | 486 | 5496 | 4122 | 10992 | 8244 | 10.992 | 8.244
8:10 | 3 | 4 | 13 | 4 | 10 | 3 | 5 | 15 | 5 | 5 | 6 | 22 | 3 | 5 | 11 | 7 | 4 | 11 | 1 | 15 | 11 | 2 | 7 | 2 | 0 | 0 | 0 | 7 | 2 | 3 | 35 | 3 | 11 | 124 | 77 | 12 | 15 | 101 | 4 | 42 | 8:10 | 36 | 48 | 156 | 48 | 120 | 36 | 60 | 180 | 60 | 60 | 72 | 264 | 36 | 60 | 132 | 84 | 48 | 132 | 12 | 180 | 132 | 24 | 84 | 24 | 0 | 0 | 0 | 84 | 24 | 36 | 420 | 36 | 132 | 1488 | 924 | 144 | 180 | 1212 | 48 | 504 |  | 8:10 | 27 | 36 | 117 | 36 | 90 | 0 | 27 | 45 | 135 | 45 | 45 | 0 | 54 | 198 | 27 | 45 | 99 | 0 | 63 | 36 | 99 | 9 | 135 | 0 | 99 | 18 | 63 | 18 | 0 | 0 | 0 | 0 | 63 | 18 | 27 | 0 | 315 | 27 | 99 | 937.5 | 693 | 0 | 108 | 135 | 909 | 36 | 378 | 7320 | 5311.5 | 14640 | 10623 | 14.64 | 10.623
8:15 | 1 | 5 | 14 | 2 | 11 | 4 | 4 | 14 | 5 | 4 | 8 | 22 | 3 | 4 | 11 | 9 | 2 | 7 | 1 | 14 | 10 | 5 | 9 | 3 | 0 | 0 | 0 | 3 | 3 | 2 | 23 | 4 | 12 | 80 | 111 | 17 | 15 | 41 | 3 | 41 | 8:15 | 12 | 60 | 168 | 24 | 132 | 48 | 48 | 168 | 60 | 48 | 96 | 264 | 36 | 48 | 132 | 108 | 24 | 84 | 12 | 168 | 120 | 60 | 108 | 36 | 0 | 0 | 0 | 36 | 36 | 24 | 276 | 48 | 144 | 960 | 1332 | 204 | 180 | 492 | 36 | 492 |  | 8:15 | 9 | 45 | 126 | 18 | 99 | 0 | 36 | 36 | 126 | 45 | 36 | 0 | 72 | 198 | 27 | 36 | 99 | 0 | 81 | 18 | 63 | 9 | 126 | 0 | 90 | 45 | 81 | 27 | 0 | 0 | 0 | 0 | 27 | 27 | 18 | 0 | 207 | 36 | 108 | 720 | 937.5 | 0 | 153 | 135 | 369 | 27 | 369 | 6324 | 4681.5 | 12648 | 9363 | 12.648 | 9.363
8:20 | 1 | 4 | 7 | 4 | 12 | 11 | 5 | 15 | 6 | 4 | 9 | 21 | 2 | 5 | 12 | 15 | 2 | 5 | 1 | 15 | 11 | 12 | 21 | 2 | 0 | 0 | 0 | 2 | 11 | 3 | 17 | 3 | 17 | 96 | 77 | 16 | 13 | 36 | 3 | 41 | 8:20 | 12 | 48 | 84 | 48 | 144 | 132 | 60 | 180 | 72 | 48 | 108 | 252 | 24 | 60 | 144 | 180 | 24 | 60 | 12 | 180 | 132 | 144 | 252 | 24 | 0 | 0 | 0 | 24 | 132 | 36 | 204 | 36 | 204 | 1152 | 924 | 192 | 156 | 432 | 36 | 492 |  | 8:20 | 9 | 36 | 63 | 36 | 108 | 0 | 99 | 45 | 135 | 54 | 36 | 0 | 81 | 189 | 18 | 45 | 108 | 0 | 135 | 18 | 45 | 9 | 135 | 0 | 99 | 108 | 189 | 18 | 0 | 0 | 0 | 0 | 18 | 99 | 27 | 0 | 153 | 27 | 153 | 864 | 693 | 0 | 144 | 117 | 324 | 27 | 369 | 6444 | 4833 | 12888 | 9666 | 12.888 | 9.666
8:25 | 1 | 4 | 15 | 3 | 10 | 14 | 3 | 15 | 14 | 5 | 16 | 21 | 2 | 5 | 12 | 14 | 2 | 4 | 2 | 15 | 10 | 11 | 21 | 3 | 0 | 0 | 0 | 3 | 12 | 2 | 24 | 12 | 24 | 49 | 58 | 16 | 4 | 36 | 4 | 35 | 8:25 | 12 | 48 | 180 | 36 | 120 | 168 | 36 | 180 | 168 | 60 | 192 | 252 | 24 | 60 | 144 | 168 | 24 | 48 | 24 | 180 | 120 | 132 | 252 | 36 | 0 | 0 | 0 | 36 | 144 | 24 | 288 | 144 | 288 | 588 | 696 | 192 | 48 | 432 | 48 | 420 |  | 8:25 | 9 | 36 | 135 | 27 | 90 | 0 | 126 | 27 | 135 | 126 | 45 | 0 | 144 | 189 | 18 | 45 | 108 | 0 | 126 | 18 | 36 | 18 | 135 | 0 | 90 | 99 | 189 | 27 | 0 | 0 | 0 | 0 | 27 | 108 | 18 | 0 | 216 | 108 | 216 | 441 | 522 | 0 | 144 | 36 | 324 | 36 | 315 | 6012 | 4509 | 12024 | 9018 | 12.024 | 9.018
8:30 | 2 | 4 | 14 | 3 | 12 | 17 | 4 | 14 | 8 | 4 | 16 | 21 | 3 | 14 | 13 | 15 | 3 | 5 | 1 | 14 | 4 | 11 | 3 | 2 | 0 | 0 | 0 | 2 | 11 | 3 | 17 | 16 | 23 | 48 | 46 | 16 | 4 | 31 | 10 | 53 | 8:30 | 24 | 48 | 168 | 36 | 144 | 204 | 48 | 168 | 96 | 48 | 192 | 252 | 36 | 168 | 156 | 180 | 36 | 60 | 12 | 168 | 48 | 132 | 36 | 24 | 0 | 0 | 0 | 24 | 132 | 36 | 204 | 192 | 276 | 576 | 552 | 192 | 48 | 372 | 120 | 636 |  | 8:30 | 18 | 36 | 126 | 27 | 108 | 0 | 153 | 36 | 126 | 72 | 36 | 0 | 144 | 189 | 27 | 126 | 117 | 0 | 135 | 27 | 45 | 9 | 126 | 0 | 36 | 99 | 27 | 18 | 0 | 0 | 0 | 0 | 18 | 99 | 27 | 0 | 153 | 144 | 207 | 432 | 414 | 0 | 144 | 36 | 279 | 90 | 477 | 5844 | 4383 | 11688 | 8766 | 11.688 | 8.766
8:35 | 1 | 4 | 16 | 3 | 12 | 15 | 4 | 15 | 9 | 4 | 8 | 22 | 3 | 6 | 14 | 18 | 3 | 4 | 1 | 14 | 3 | 10 | 3 | 2 | 0 | 0 | 0 | 2 | 10 | 2 | 14 | 15 | 23 | 44 | 54 | 6 | 3 | 25 | 15 | 66 | 8:35 | 12 | 48 | 192 | 36 | 144 | 180 | 48 | 180 | 108 | 48 | 96 | 264 | 36 | 72 | 168 | 216 | 36 | 48 | 12 | 168 | 36 | 120 | 36 | 24 | 0 | 0 | 0 | 24 | 120 | 24 | 168 | 180 | 276 | 528 | 648 | 72 | 36 | 300 | 180 | 792 |  | 8:35 | 9 | 36 | 144 | 27 | 108 | 0 | 135 | 36 | 135 | 81 | 36 | 0 | 72 | 198 | 27 | 54 | 126 | 0 | 162 | 27 | 36 | 9 | 126 | 0 | 27 | 90 | 27 | 18 | 0 | 0 | 0 | 0 | 18 | 90 | 18 | 0 | 126 | 135 | 207 | 396 | 486 | 0 | 54 | 27 | 225 | 135 | 594 | 5676 | 4257 | 11352 | 8514 | 11.352 | 8.514
8:40 | 2 | 5 | 18 | 4 | 13 | 18 | 3 | 15 | 8 | 4 | 14 | 22 | 4 | 11 | 14 | 18 | 4 | 5 | 1 | 15 | 3 | 10 | 3 | 4 | 1 | 8 | 0 | 3 | 10 | 3 | 14 | 16 | 23 | 46 | 44 | 5 | 4 | 81 | 15 | 32 | 8:40 | 24 | 60 | 216 | 48 | 156 | 216 | 36 | 180 | 96 | 48 | 168 | 264 | 48 | 132 | 168 | 216 | 48 | 60 | 12 | 180 | 36 | 120 | 36 | 48 | 12 | 96 | 0 | 36 | 120 | 36 | 168 | 192 | 276 | 552 | 528 | 60 | 48 | 972 | 180 | 384 |  | 8:40 | 18 | 45 | 162 | 36 | 117 | 0 | 162 | 27 | 135 | 72 | 36 | 0 | 126 | 198 | 36 | 99 | 126 | 0 | 162 | 36 | 45 | 9 | 135 | 0 | 27 | 90 | 27 | 36 | 9 | 0 | 72 | 0 | 27 | 90 | 27 | 0 | 126 | 144 | 207 | 414 | 396 | 0 | 45 | 36 | 729 | 135 | 288 | 6276 | 4707 | 12552 | 9414 | 12.552 | 9.414
8:45 | 2 | 5 | 17 | 3 | 20 | 23 | 4 | 14 | 6 | 4 | 15 | 17 | 5 | 16 | 15 | 24 | 4 | 4 | 2 | 14 | 2 | 11 | 5 | 3 | 3 | 10 | 0 | 2 | 10 | 4 | 6 | 15 | 23 | 46 | 42 | 6 | 3 | 30 | 15 | 28 | 8:45 | 24 | 60 | 204 | 36 | 240 | 276 | 48 | 168 | 72 | 48 | 180 | 204 | 60 | 192 | 180 | 288 | 48 | 48 | 24 | 168 | 24 | 132 | 60 | 36 | 36 | 120 | 0 | 24 | 120 | 48 | 72 | 180 | 276 | 552 | 504 | 72 | 36 | 360 | 180 | 336 |  | 8:45 | 18 | 45 | 153 | 27 | 180 | 0 | 207 | 36 | 126 | 54 | 36 | 0 | 135 | 153 | 45 | 144 | 135 | 0 | 216 | 36 | 36 | 18 | 126 | 0 | 18 | 99 | 45 | 27 | 27 | 0 | 90 | 0 | 18 | 90 | 36 | 0 | 54 | 135 | 207 | 414 | 378 | 0 | 54 | 27 | 270 | 135 | 252 | 5736 | 4302 | 11472 | 8604 | 11.472 | 8.604
8:50 | 3 | 8 | 14 | 4 | 22 | 23 | 6 | 15 | 16 | 6 | 14 | 14 | 4 | 17 | 15 | 22 | 4 | 3 | 2 | 14 | 3 | 11 | 7 | 3 | 5 | 10 | 0 | 3 | 10 | 6 | 11 | 11 | 16 | 46 | 67 | 6 | 5 | 14 | 15 | 18 | 8:50 | 36 | 96 | 168 | 48 | 264 | 276 | 72 | 180 | 192 | 72 | 168 | 168 | 48 | 204 | 180 | 264 | 48 | 36 | 24 | 168 | 36 | 132 | 84 | 36 | 60 | 120 | 0 | 36 | 120 | 72 | 132 | 132 | 192 | 552 | 804 | 72 | 60 | 168 | 180 | 216 |  | 8:50 | 27 | 72 | 126 | 36 | 198 | 0 | 207 | 54 | 135 | 144 | 54 | 0 | 126 | 126 | 36 | 153 | 135 | 0 | 198 | 36 | 27 | 18 | 126 | 0 | 27 | 99 | 63 | 27 | 45 | 0 | 90 | 0 | 27 | 90 | 54 | 0 | 99 | 99 | 144 | 414 | 603 | 0 | 54 | 45 | 126 | 135 | 162 | 5916 | 4437 | 11832 | 8874 | 11.832 | 8.874
8:55 | 4 | 14 | 18 | 4 | 23 | 23 | 5 | 14 | 16 | 4 | 10 | 14 | 4 | 14 | 23 | 39 | 3 | 4 | 3 | 14 | 2 | 4 | 3 | 4 | 5 | 9 | 0 | 2 | 8 | 9 | 19 | 7 | 12 | 84 | 37 | 6 | 10 | 13 | 5 | 27 | 8:55 | 48 | 168 | 216 | 48 | 276 | 276 | 60 | 168 | 192 | 48 | 120 | 168 | 48 | 168 | 276 | 468 | 36 | 48 | 36 | 168 | 24 | 48 | 36 | 48 | 60 | 108 | 0 | 24 | 96 | 108 | 228 | 84 | 144 | 1008 | 444 | 72 | 120 | 156 | 60 | 324 |  | 8:55 | 36 | 126 | 162 | 36 | 207 | 0 | 207 | 45 | 126 | 144 | 36 | 0 | 90 | 126 | 36 | 126 | 207 | 0 | 351 | 27 | 36 | 27 | 126 | 0 | 18 | 36 | 27 | 36 | 45 | 0 | 81 | 0 | 18 | 72 | 81 | 0 | 171 | 63 | 108 | 756 | 333 | 0 | 54 | 90 | 117 | 45 | 243 | 6228 | 4671 | 12456 | 9342 | 12.456 | 9.342
9:00 | 12 | 15 | 18 | 4 | 20 | 21 | 5 | 15 | 17 | 10 | 21 | 15 | 4 | 17 | 24 | 27 | 6 | 4 | 3 | 14 | 4 | 4 | 6 | 4 | 7 | 9 | 0 | 3 | 3 | 4 | 20 | 9 | 12 | 72 | 33 | 7 | 18 | 46 | 6 | 83 | 9:00 | 144 | 180 | 216 | 48 | 240 | 252 | 60 | 180 | 204 | 120 | 252 | 180 | 48 | 204 | 288 | 324 | 72 | 48 | 36 | 168 | 48 | 48 | 72 | 48 | 84 | 108 | 0 | 36 | 36 | 48 | 240 | 108 | 144 | 864 | 396 | 84 | 216 | 552 | 72 | 996 |  | 9:00 | 108 | 135 | 162 | 36 | 180 | 0 | 189 | 45 | 135 | 153 | 90 | 0 | 189 | 135 | 36 | 153 | 216 | 0 | 243 | 54 | 36 | 27 | 126 | 0 | 36 | 36 | 54 | 36 | 63 | 0 | 81 | 0 | 27 | 27 | 36 | 0 | 180 | 81 | 108 | 648 | 297 | 0 | 63 | 162 | 414 | 54 | 747 | 7464 | 5598 | 14928 | 11196 | 14.928 | 11.196
9:05 | 12 | 14 | 16 | 4 | 22 | 21 | 5 | 14 | 16 | 13 | 18 | 14 | 4 | 16 | 23 | 14 | 12 | 4 | 5 | 13 | 4 | 3 | 10 | 3 | 9 | 9 | 0 | 2 | 2 | 2 | 19 | 11 | 12 | 57 | 23 | 9 | 19 | 25 | 12 | 54 | 9:05 | 144 | 168 | 192 | 48 | 264 | 252 | 60 | 168 | 192 | 156 | 216 | 168 | 48 | 192 | 276 | 168 | 144 | 48 | 60 | 156 | 48 | 36 | 120 | 36 | 108 | 108 | 0 | 24 | 24 | 24 | 228 | 132 | 144 | 684 | 276 | 108 | 228 | 300 | 144 | 648 |  | 9:05 | 108 | 126 | 144 | 36 | 198 | 0 | 189 | 45 | 126 | 144 | 117 | 0 | 162 | 126 | 36 | 144 | 207 | 0 | 126 | 108 | 36 | 45 | 117 | 0 | 36 | 27 | 90 | 27 | 81 | 0 | 81 | 0 | 18 | 18 | 18 | 0 | 171 | 99 | 108 | 513 | 207 | 0 | 81 | 171 | 225 | 108 | 486 | 6540 | 4905 | 13080 | 9810 | 13.08 | 9.81
9:10 | 10 | 13 | 12 | 3 | 23 | 21 | 16 | 15 | 16 | 12 | 23 | 14 | 4 | 15 | 22 | 14 | 11 | 5 | 12 | 23 | 4 | 3 | 9 | 3 | 9 | 9 | 0 | 4 | 4 | 4 | 19 | 10 | 12 | 33 | 23 | 19 | 18 | 54 | 18 | 28 | 9:10 | 120 | 156 | 144 | 36 | 276 | 252 | 192 | 180 | 192 | 144 | 276 | 168 | 48 | 180 | 264 | 168 | 132 | 60 | 144 | 276 | 48 | 36 | 108 | 36 | 108 | 108 | 0 | 48 | 48 | 48 | 228 | 120 | 144 | 396 | 276 | 228 | 216 | 648 | 216 | 336 |  | 9:10 | 90 | 117 | 108 | 27 | 207 | 0 | 189 | 144 | 135 | 144 | 108 | 0 | 207 | 126 | 36 | 135 | 198 | 0 | 126 | 99 | 45 | 108 | 207 | 0 | 36 | 27 | 81 | 27 | 81 | 0 | 81 | 0 | 36 | 36 | 36 | 0 | 171 | 90 | 108 | 297 | 207 | 0 | 171 | 162 | 486 | 162 | 252 | 6804 | 5103 | 13608 | 10206 | 13.608 | 10.206
9:15 | 11 | 14 | 15 | 14 | 23 | 21 | 15 | 15 | 16 | 12 | 23 | 14 | 4 | 15 | 22 | 8 | 11 | 3 | 11 | 21 | 4 | 4 | 10 | 3 | 9 | 5 | 0 | 4 | 4 | 3 | 18 | 11 | 12 | 34 | 26 | 22 | 17 | 97 | 25 | 26 | 9:15 | 132 | 168 | 180 | 168 | 276 | 252 | 180 | 180 | 192 | 144 | 276 | 168 | 48 | 180 | 264 | 96 | 132 | 36 | 132 | 252 | 48 | 48 | 120 | 36 | 108 | 60 | 0 | 48 | 48 | 36 | 216 | 132 | 144 | 408 | 312 | 264 | 204 | 1164 | 300 | 312 |  | 9:15 | 99 | 126 | 135 | 126 | 207 | 0 | 189 | 135 | 135 | 144 | 108 | 0 | 207 | 126 | 36 | 135 | 198 | 0 | 72 | 99 | 27 | 99 | 189 | 0 | 36 | 36 | 90 | 27 | 81 | 0 | 45 | 0 | 36 | 36 | 27 | 0 | 162 | 99 | 108 | 306 | 234 | 0 | 198 | 153 | 873 | 225 | 234 | 7464 | 5598 | 14928 | 11196 | 14.928 | 11.196
9:20 | 14 | 13 | 16 | 12 | 23 | 17 | 14 | 13 | 17 | 11 | 21 | 14 | 4 | 15 | 23 | 7 | 11 | 4 | 11 | 20 | 4 | 5 | 5 | 4 | 10 | 2 | 0 | 3 | 4 | 13 | 16 | 11 | 122 | 33 | 86 | 22 | 13 | 38 | 24 | 14 | 9:20 | 168 | 156 | 192 | 144 | 276 | 204 | 168 | 156 | 204 | 132 | 252 | 168 | 48 | 180 | 276 | 84 | 132 | 48 | 132 | 240 | 48 | 60 | 60 | 48 | 120 | 24 | 0 | 36 | 48 | 156 | 192 | 132 | 1464 | 396 | 1032 | 264 | 156 | 456 | 288 | 168 |  | 9:20 | 126 | 117 | 144 | 108 | 207 | 0 | 153 | 126 | 117 | 153 | 99 | 0 | 189 | 126 | 36 | 135 | 207 | 0 | 63 | 99 | 36 | 99 | 180 | 0 | 36 | 45 | 45 | 36 | 90 | 0 | 18 | 0 | 27 | 36 | 117 | 0 | 144 | 99 | 937.5 | 297 | 774 | 0 | 198 | 117 | 342 | 216 | 126 | 8508 | 6220.5 | 17016 | 12441 | 17.016 | 12.441
9:25 | 10 | 19 | 16 | 12 | 23 | 22 | 16 | 13 | 19 | 12 | 20 | 14 | 11 | 24 | 20 | 11 | 10 | 5 | 10 | 21 | 4 | 5 | 7 | 5 | 9 | 0 | 8 | 8 | 3 | 13 | 8 | 10 | 23 | 82 | 25 | 21 | 12 | 34 | 157 | 39 | 9:25 | 120 | 228 | 192 | 144 | 276 | 264 | 192 | 156 | 228 | 144 | 240 | 168 | 132 | 288 | 240 | 132 | 120 | 60 | 120 | 252 | 48 | 60 | 84 | 60 | 108 | 0 | 96 | 96 | 36 | 156 | 96 | 120 | 276 | 984 | 300 | 252 | 144 | 408 | 1884 | 468 |  | 9:25 | 90 | 171 | 144 | 108 | 207 | 0 | 198 | 144 | 117 | 171 | 108 | 0 | 180 | 126 | 99 | 216 | 180 | 0 | 99 | 90 | 45 | 90 | 189 | 0 | 36 | 45 | 63 | 45 | 81 | 0 | 0 | 72 | 72 | 27 | 117 | 0 | 72 | 90 | 207 | 738 | 225 | 0 | 189 | 108 | 306 | 937.5 | 351 | 9372 | 6553.5 | 18744 | 13107 | 18.744 | 13.107
9:30 | 10 | 12 | 5 | 12 | 22 | 12 | 13 | 16 | 19 | 12 | 19 | 13 | 13 | 23 | 23 | 5 | 10 | 5 | 11 | 19 | 3 | 6 | 13 | 8 | 9 | 1 | 11 | 3 | 3 | 13 | 8 | 14 | 29 | 50 | 28 | 16 | 13 | 14 | 66 | 9 | 9:30 | 120 | 144 | 60 | 144 | 264 | 144 | 156 | 192 | 228 | 144 | 228 | 156 | 156 | 276 | 276 | 60 | 120 | 60 | 132 | 228 | 36 | 72 | 156 | 96 | 108 | 12 | 132 | 36 | 36 | 156 | 96 | 168 | 348 | 600 | 336 | 192 | 156 | 168 | 792 | 108 |  | 9:30 | 90 | 108 | 45 | 108 | 198 | 0 | 108 | 117 | 144 | 171 | 108 | 0 | 171 | 117 | 117 | 207 | 207 | 0 | 45 | 90 | 45 | 99 | 171 | 0 | 27 | 54 | 117 | 72 | 81 | 0 | 9 | 99 | 27 | 27 | 117 | 0 | 72 | 126 | 261 | 450 | 252 | 0 | 144 | 117 | 126 | 594 | 81 | 7092 | 5319 | 14184 | 10638 | 14.184 | 10.638
9:35 | 9 | 5 | 8 | 13 | 23 | 11 | 16 | 22 | 20 | 12 | 19 | 13 | 13 | 21 | 15 | 4 | 11 | 5 | 10 | 18 | 3 | 4 | 13 | 8 | 8 | 1 | 9 | 4 | 3 | 13 | 9 | 22 | 46 | 30 | 27 | 14 | 16 | 12 | 83 | 14 | 9:35 | 108 | 60 | 96 | 156 | 276 | 132 | 192 | 264 | 240 | 144 | 228 | 156 | 156 | 252 | 180 | 48 | 132 | 60 | 120 | 216 | 36 | 48 | 156 | 96 | 96 | 12 | 108 | 48 | 36 | 156 | 108 | 264 | 552 | 360 | 324 | 168 | 192 | 144 | 996 | 168 |  | 9:35 | 81 | 45 | 72 | 117 | 207 | 0 | 99 | 144 | 198 | 180 | 108 | 0 | 171 | 117 | 117 | 189 | 135 | 0 | 36 | 99 | 45 | 90 | 162 | 0 | 27 | 36 | 117 | 72 | 72 | 0 | 9 | 81 | 36 | 27 | 117 | 0 | 81 | 198 | 414 | 270 | 243 | 0 | 126 | 144 | 108 | 747 | 126 | 7284 | 5463 | 14568 | 10926 | 14.568 | 10.926
9:40 | 3 | 3 | 6 | 12 | 19 | 7 | 14 | 21 | 19 | 12 | 23 | 13 | 14 | 21 | 15 | 6 | 10 | 9 | 9 | 18 | 4 | 5 | 10 | 8 | 7 | 1 | 11 | 7 | 3 | 13 | 8 | 25 | 71 | 24 | 31 | 11 | 19 | 9 | 36 | 16 | 9:40 | 36 | 36 | 72 | 144 | 228 | 84 | 168 | 252 | 228 | 144 | 276 | 156 | 168 | 252 | 180 | 72 | 120 | 108 | 108 | 216 | 48 | 60 | 120 | 96 | 84 | 12 | 132 | 84 | 36 | 156 | 96 | 300 | 852 | 288 | 372 | 132 | 228 | 108 | 432 | 192 |  | 9:40 | 27 | 27 | 54 | 108 | 171 | 0 | 63 | 126 | 189 | 171 | 108 | 0 | 207 | 117 | 126 | 189 | 135 | 0 | 54 | 90 | 81 | 81 | 162 | 0 | 36 | 45 | 90 | 72 | 63 | 0 | 9 | 99 | 63 | 27 | 117 | 0 | 72 | 225 | 639 | 216 | 279 | 0 | 99 | 171 | 81 | 324 | 144 | 6876 | 5157 | 13752 | 10314 | 13.752 | 10.314
9:45 | 3 | 11 | 135 | 13 | 14 | 7 | 20 | 20 | 9 | 7 | 3 | 13 | 10 | 20 | 10 | 8 | 9 | 15 | 6 | 19 | 13 | 5 | 9 | 9 | 8 | 1 | 10 | 11 | 3 | 12 | 8 | 21 | 38 | 23 | 32 | 13 | 21 | 7 | 36 | 18 | 9:45 | 36 | 132 | 1620 | 156 | 168 | 84 | 240 | 240 | 108 | 84 | 36 | 156 | 120 | 240 | 120 | 96 | 108 | 180 | 72 | 228 | 156 | 60 | 108 | 108 | 96 | 12 | 120 | 132 | 36 | 144 | 96 | 252 | 456 | 276 | 384 | 156 | 252 | 84 | 432 | 216 |  | 9:45 | 27 | 99 | 937.5 | 117 | 126 | 0 | 63 | 180 | 180 | 81 | 63 | 0 | 27 | 117 | 90 | 180 | 90 | 0 | 72 | 81 | 135 | 54 | 171 | 0 | 117 | 45 | 81 | 81 | 72 | 0 | 9 | 90 | 99 | 27 | 108 | 0 | 72 | 189 | 342 | 207 | 288 | 0 | 117 | 189 | 63 | 324 | 162 | 7800 | 5572.5 | 15600 | 11145 | 15.6 | 11.145
9:50 | 3 | 10 | 57 | 11 | 14 | 6 | 14 | 19 | 5 | 6 | 15 | 12 | 12 | 20 | 14 | 5 | 4 | 13 | 2 | 21 | 14 | 6 | 10 | 9 | 7 | 1 | 10 | 9 | 5 | 11 | 8 | 22 | 54 | 13 | 67 | 12 | 23 | 9 | 26 | 29 | 9:50 | 36 | 120 | 684 | 132 | 168 | 72 | 168 | 228 | 60 | 72 | 180 | 144 | 144 | 240 | 168 | 60 | 48 | 156 | 24 | 252 | 168 | 72 | 120 | 108 | 84 | 12 | 120 | 108 | 60 | 132 | 96 | 264 | 648 | 156 | 804 | 144 | 276 | 108 | 312 | 348 |  | 9:50 | 27 | 90 | 513 | 99 | 126 | 0 | 54 | 126 | 171 | 45 | 54 | 0 | 135 | 108 | 108 | 180 | 126 | 0 | 45 | 36 | 117 | 18 | 189 | 0 | 126 | 54 | 90 | 81 | 63 | 0 | 9 | 90 | 81 | 45 | 99 | 0 | 72 | 198 | 486 | 117 | 603 | 0 | 108 | 207 | 81 | 234 | 261 | 7296 | 5472 | 14592 | 10944 | 14.592 | 10.944
9:55 | 3 | 6 | 9 | 10 | 13 | 7 | 6 | 19 | 6 | 6 | 7 | 11 | 10 | 20 | 13 | 5 | 4 | 13 | 2 | 24 | 15 | 9 | 9 | 9 | 8 | 2 | 11 | 10 | 6 | 10 | 9 | 21 | 30 | 13 | 30 | 13 | 119 | 18 | 27 | 28 | 9:55 | 36 | 72 | 108 | 120 | 156 | 84 | 72 | 228 | 72 | 72 | 84 | 132 | 120 | 240 | 156 | 60 | 48 | 156 | 24 | 288 | 180 | 108 | 108 | 108 | 96 | 24 | 132 | 120 | 72 | 120 | 108 | 252 | 360 | 156 | 360 | 156 | 1428 | 216 | 324 | 336 |  | 9:55 | 27 | 54 | 81 | 90 | 117 | 0 | 63 | 54 | 171 | 54 | 54 | 0 | 63 | 99 | 90 | 180 | 117 | 0 | 45 | 36 | 117 | 18 | 216 | 0 | 135 | 81 | 81 | 81 | 72 | 0 | 18 | 99 | 90 | 54 | 90 | 0 | 81 | 189 | 270 | 117 | 270 | 0 | 117 | 937.5 | 162 | 243 | 252 | 7092 | 5185.5 | 14184 | 10371 | 14.184 | 10.371
10:00 | 3 | 12 | 19 | 5 | 13 | 4 | 6 | 18 | 6 | 5 | 16 | 11 | 11 | 19 | 18 | 11 | 4 | 14 | 2 | 23 | 15 | 11 | 12 | 9 | 8 | 2 | 5 | 10 | 5 | 4 | 18 | 105 | 74 | 12 | 25 | 18 | 34 | 26 | 27 | 187 | 10:00 | 36 | 144 | 228 | 60 | 156 | 48 | 72 | 216 | 72 | 60 | 192 | 132 | 132 | 228 | 216 | 132 | 48 | 168 | 24 | 276 | 180 | 132 | 144 | 108 | 96 | 24 | 60 | 120 | 60 | 48 | 216 | 1260 | 888 | 144 | 300 | 216 | 408 | 312 | 324 | 2244 |  | 10:00 | 27 | 108 | 171 | 45 | 117 | 0 | 36 | 54 | 162 | 54 | 45 | 0 | 144 | 99 | 99 | 171 | 162 | 0 | 99 | 36 | 126 | 18 | 207 | 0 | 135 | 99 | 108 | 81 | 72 | 0 | 18 | 45 | 90 | 45 | 36 | 0 | 162 | 937.5 | 666 | 108 | 225 | 0 | 162 | 306 | 234 | 243 | 937.5 | 9924 | 6690 | 19848 | 13380 | 19.848 | 13.38
10:05 | 4 | 9 | 42 | 4 | 14 | 9 | 5 | 41 | 7 | 5 | 11 | 19 | 10 | 13 | 6 | 8 | 4 | 14 | 2 | 21 | 15 | 9 | 5 | 9 | 8 | 1 | 3 | 20 | 4 | 4 | 20 | 54 | 19 | 13 | 45 | 92 | 35 | 25 | 26 | 239 | 10:05 | 48 | 108 | 504 | 48 | 168 | 108 | 60 | 492 | 84 | 60 | 132 | 228 | 120 | 156 | 72 | 96 | 48 | 168 | 24 | 252 | 180 | 108 | 60 | 108 | 96 | 12 | 36 | 240 | 48 | 48 | 240 | 648 | 228 | 156 | 540 | 1104 | 420 | 300 | 312 | 2868 |  | 10:05 | 36 | 81 | 378 | 36 | 126 | 0 | 81 | 45 | 369 | 63 | 45 | 0 | 99 | 171 | 90 | 117 | 54 | 0 | 72 | 36 | 126 | 18 | 189 | 0 | 135 | 81 | 45 | 81 | 72 | 0 | 9 | 27 | 180 | 36 | 36 | 0 | 180 | 486 | 171 | 117 | 405 | 0 | 828 | 315 | 225 | 234 | 937.5 | 10728 | 6832.5 | 21456 | 13665 | 21.456 | 13.665
10:10 | 4 | 4 | 27 | 5 | 14 | 11 | 5 | 145 | 6 | 5 | 2 | 18 | 9 | 11 | 5 | 7 | 4 | 12 | 2 | 22 | 20 | 9 | 5 | 19 | 8 | 1 | 1 | 19 | 5 | 4 | 19 | 57 | 20 | 12 | 24 | 30 | 95 | 39 | 26 | 293 | 10:10 | 48 | 48 | 324 | 60 | 168 | 132 | 60 | 1740 | 72 | 60 | 24 | 216 | 108 | 132 | 60 | 84 | 48 | 144 | 24 | 264 | 240 | 108 | 60 | 228 | 96 | 12 | 12 | 228 | 60 | 48 | 228 | 684 | 240 | 144 | 288 | 360 | 1140 | 468 | 312 | 3516 |  | 10:10 | 36 | 36 | 243 | 45 | 126 | 0 | 99 | 45 | 937.5 | 54 | 45 | 0 | 18 | 162 | 81 | 99 | 45 | 0 | 63 | 36 | 108 | 18 | 198 | 0 | 180 | 81 | 45 | 171 | 72 | 0 | 9 | 9 | 171 | 45 | 36 | 0 | 171 | 513 | 180 | 108 | 216 | 0 | 270 | 855 | 351 | 234 | 937.5 | 12288 | 7149 | 24576 | 14298 | 24.576 | 14.298
10:15 | 3 | 7 | 7 | 5 | 12 | 9 | 6 | 76 | 4 | 5 | 9 | 18 | 6 | 10 | 14 | 6 | 4 | 13 | 2 | 21 | 13 | 9 | 6 | 19 | 8 | 2 | 2 | 18 | 6 | 5 | 18 | 22 | 19 | 14 | 51 | 31 | 24 | 73 | 19 | 422 | 10:15 | 36 | 84 | 84 | 60 | 144 | 108 | 72 | 912 | 48 | 60 | 108 | 216 | 72 | 120 | 168 | 72 | 48 | 156 | 24 | 252 | 156 | 108 | 72 | 228 | 96 | 24 | 24 | 216 | 72 | 60 | 216 | 264 | 228 | 168 | 612 | 372 | 288 | 876 | 228 | 5064 |  | 10:15 | 27 | 63 | 63 | 45 | 108 | 0 | 81 | 54 | 684 | 36 | 45 | 0 | 81 | 162 | 54 | 90 | 126 | 0 | 54 | 36 | 117 | 18 | 189 | 0 | 117 | 81 | 54 | 171 | 72 | 0 | 18 | 18 | 162 | 54 | 45 | 0 | 162 | 198 | 171 | 126 | 459 | 0 | 279 | 216 | 657 | 171 | 937.5 | 12216 | 6301.5 | 24432 | 12603 | 24.432 | 12.603
10:20 | 3 | 4 | 32 | 6 | 12 | 8 | 5 | 52 | 4 | 4 | 7 | 17 | 6 | 11 | 2 | 7 | 4 | 13 | 3 | 20 | 19 | 9 | 12 | 17 | 8 | 2 | 8 | 17 | 6 | 5 | 19 | 16 | 19 | 19 | 37 | 31 | 23 | 14 | 31 | 399 | 10:20 | 36 | 48 | 384 | 72 | 144 | 96 | 60 | 624 | 48 | 48 | 84 | 204 | 72 | 132 | 24 | 84 | 48 | 156 | 36 | 240 | 228 | 108 | 144 | 204 | 96 | 24 | 96 | 204 | 72 | 60 | 228 | 192 | 228 | 228 | 444 | 372 | 276 | 168 | 372 | 4788 |  | 10:20 | 27 | 36 | 288 | 54 | 108 | 0 | 72 | 45 | 468 | 36 | 36 | 0 | 63 | 153 | 54 | 99 | 18 | 0 | 63 | 36 | 117 | 27 | 180 | 0 | 171 | 81 | 108 | 153 | 72 | 0 | 18 | 72 | 153 | 54 | 45 | 0 | 171 | 144 | 171 | 171 | 333 | 0 | 279 | 207 | 126 | 279 | 937.5 | 11172 | 5725.5 | 22344 | 11451 | 22.344 | 11.451
10:25 | 4 | 6 | 25 | 5 | 11 | 7 | 4 | 16 | 4 | 5 | 9 | 18 | 5 | 9 | 10 | 6 | 5 | 11 | 3 | 20 | 13 | 9 | 15 | 16 | 8 | 2 | 1 | 17 | 14 | 6 | 15 | 15 | 14 | 26 | 169 | 27 | 24 | 33 | 113 | 159 | 10:25 | 48 | 72 | 300 | 60 | 132 | 84 | 48 | 192 | 48 | 60 | 108 | 216 | 60 | 108 | 120 | 72 | 60 | 132 | 36 | 240 | 156 | 108 | 180 | 192 | 96 | 24 | 12 | 204 | 168 | 72 | 180 | 180 | 168 | 312 | 2028 | 324 | 288 | 396 | 1356 | 1908 |  | 10:25 | 36 | 54 | 225 | 45 | 99 | 0 | 63 | 36 | 144 | 36 | 45 | 0 | 81 | 162 | 45 | 81 | 90 | 0 | 54 | 45 | 99 | 27 | 180 | 0 | 117 | 81 | 135 | 144 | 72 | 0 | 18 | 9 | 153 | 126 | 54 | 0 | 135 | 135 | 126 | 234 | 937.5 | 0 | 243 | 216 | 297 | 937.5 | 937.5 | 10548 | 6754.5 | 21096 | 13509 | 21.096 | 13.509
10:30 | 5 | 7 | 20 | 5 | 10 | 6 | 6 | 12 | 5 | 5 | 8 | 18 | 4 | 13 | 12 | 6 | 4 | 5 | 4 | 19 | 16 | 9 | 16 | 16 | 7 | 1 | 2 | 17 | 7 | 7 | 7 | 17 | 22 | 26 | 287 | 19 | 57 | 15 | 39 | 150 | 10:30 | 60 | 84 | 240 | 60 | 120 | 72 | 72 | 144 | 60 | 60 | 96 | 216 | 48 | 156 | 144 | 72 | 48 | 60 | 48 | 228 | 192 | 108 | 192 | 192 | 84 | 12 | 24 | 204 | 84 | 84 | 84 | 204 | 264 | 312 | 3444 | 228 | 684 | 180 | 468 | 1800 |  | 10:30 | 45 | 63 | 180 | 45 | 90 | 0 | 54 | 54 | 108 | 45 | 45 | 0 | 72 | 162 | 36 | 117 | 108 | 0 | 54 | 36 | 45 | 36 | 171 | 0 | 144 | 81 | 144 | 144 | 63 | 0 | 9 | 18 | 153 | 63 | 63 | 0 | 63 | 153 | 198 | 234 | 937.5 | 0 | 171 | 513 | 135 | 351 | 937.5 | 10932 | 6141 | 21864 | 12282 | 21.864 | 12.282
10:35 | 4 | 20 | 17 | 5 | 12 | 8 | 6 | 18 | 5 | 5 | 9 | 3 | 4 | 49 | 6 | 11 | 3 | 4 | 2 | 19 | 13 | 9 | 15 | 16 | 7 | 2 | 2 | 16 | 10 | 6 | 9 | 24 | 87 | 25 | 252 | 19 | 56 | 14 | 29 | 163 | 10:35 | 48 | 240 | 204 | 60 | 144 | 96 | 72 | 216 | 60 | 60 | 108 | 36 | 48 | 588 | 72 | 132 | 36 | 48 | 24 | 228 | 156 | 108 | 180 | 192 | 84 | 24 | 24 | 192 | 120 | 72 | 108 | 288 | 1044 | 300 | 3024 | 228 | 672 | 168 | 348 | 1956 |  | 10:35 | 36 | 180 | 153 | 45 | 108 | 0 | 72 | 54 | 162 | 45 | 45 | 0 | 81 | 27 | 36 | 441 | 54 | 0 | 99 | 27 | 36 | 18 | 171 | 0 | 117 | 81 | 135 | 144 | 63 | 0 | 18 | 18 | 144 | 90 | 54 | 0 | 81 | 216 | 783 | 225 | 937.5 | 0 | 171 | 504 | 126 | 261 | 937.5 | 11808 | 6996 | 23616 | 13992 | 23.616 | 13.992
10:40 | 12 | 18 | 13 | 7 | 11 | 8 | 6 | 7 | 5 | 5 | 7 | 1 | 4 | 24 | 8 | 15 | 5 | 5 | 4 | 19 | 9 | 9 | 20 | 16 | 9 | 1 | 1 | 15 | 8 | 5 | 7 | 59 | 42 | 26 | 264 | 17 | 113 | 25 | 28 | 151 | 10:40 | 144 | 216 | 156 | 84 | 132 | 96 | 72 | 84 | 60 | 60 | 84 | 12 | 48 | 288 | 96 | 180 | 60 | 60 | 48 | 228 | 108 | 108 | 240 | 192 | 108 | 12 | 12 | 180 | 96 | 60 | 84 | 708 | 504 | 312 | 3168 | 204 | 1356 | 300 | 336 | 1812 |  | 10:40 | 108 | 162 | 117 | 63 | 99 | 0 | 72 | 54 | 63 | 45 | 45 | 0 | 63 | 9 | 36 | 216 | 72 | 0 | 135 | 45 | 45 | 36 | 171 | 0 | 81 | 81 | 180 | 144 | 81 | 0 | 9 | 9 | 135 | 72 | 45 | 0 | 63 | 531 | 378 | 234 | 937.5 | 0 | 153 | 937.5 | 225 | 252 | 937.5 | 12108 | 7141.5 | 24216 | 14283 | 24.216 | 14.283
10:45 | 12 | 15 | 14 | 5 | 12 | 2 | 6 | 5 | 5 | 5 | 5 | 8 | 7 | 9 | 7 | 15 | 8 | 6 | 3 | 17 | 7 | 18 | 17 | 15 | 17 | 2 | 1 | 10 | 9 | 7 | 10 | 32 | 39 | 25 | 266 | 63 | 23 | 25 | 10 | 57 | 10:45 | 144 | 180 | 168 | 60 | 144 | 24 | 72 | 60 | 60 | 60 | 60 | 96 | 84 | 108 | 84 | 180 | 96 | 72 | 36 | 204 | 84 | 216 | 204 | 180 | 204 | 24 | 12 | 120 | 108 | 84 | 120 | 384 | 468 | 300 | 3192 | 756 | 276 | 300 | 120 | 684 |  | 10:45 | 108 | 135 | 126 | 45 | 108 | 0 | 18 | 54 | 45 | 45 | 45 | 0 | 45 | 72 | 63 | 81 | 63 | 0 | 135 | 72 | 54 | 27 | 153 | 0 | 63 | 162 | 153 | 135 | 153 | 0 | 18 | 9 | 90 | 81 | 63 | 0 | 90 | 288 | 351 | 225 | 937.5 | 0 | 567 | 207 | 225 | 90 | 513 | 9828 | 5914.5 | 19656 | 11829 | 19.656 | 11.829
10:50 | 13 | 12 | 12 | 7 | 14 | 7 | 0 | 7 | 7 | 5 | 5 | 6 | 5 | 7 | 6 | 13 | 5 | 7 | 3 | 11 | 6 | 16 | 12 | 12 | 16 | 2 | 1 | 8 | 9 | 6 | 10 | 31 | 26 | 25 | 269 | 63 | 41 | 26 | 8 | 55 | 10:50 | 156 | 144 | 144 | 84 | 168 | 84 | 0 | 84 | 84 | 60 | 60 | 72 | 60 | 84 | 72 | 156 | 60 | 84 | 36 | 132 | 72 | 192 | 144 | 144 | 192 | 24 | 12 | 96 | 108 | 72 | 120 | 372 | 312 | 300 | 3228 | 756 | 492 | 312 | 96 | 660 |  | 10:50 | 117 | 108 | 108 | 63 | 126 | 0 | 63 | 0 | 63 | 63 | 45 | 0 | 45 | 54 | 45 | 63 | 54 | 0 | 117 | 45 | 63 | 27 | 99 | 0 | 54 | 144 | 108 | 108 | 144 | 0 | 18 | 9 | 72 | 81 | 54 | 0 | 90 | 279 | 234 | 225 | 937.5 | 0 | 567 | 369 | 234 | 72 | 495 | 9528 | 5662.5 | 19056 | 11325 | 19.056 | 11.325
10:55 | 12 | 8 | 11 | 5 | 63 | 13 | 6 | 6 | 7 | 4 | 5 | 11 | 5 | 15 | 23 | 15 | 5 | 7 | 3 | 17 | 6 | 16 | 13 | 8 | 14 | 7 | 1 | 9 | 101 | 4 | 9 | 30 | 23 | 24 | 248 | 17 | 30 | 25 | 8 | 31 | 10:55 | 144 | 96 | 132 | 60 | 756 | 156 | 72 | 72 | 84 | 48 | 60 | 132 | 60 | 180 | 276 | 180 | 60 | 84 | 36 | 204 | 72 | 192 | 156 | 96 | 168 | 84 | 12 | 108 | 1212 | 48 | 108 | 360 | 276 | 288 | 2976 | 204 | 360 | 300 | 96 | 372 |  | 10:55 | 108 | 72 | 99 | 45 | 567 | 0 | 117 | 54 | 54 | 63 | 36 | 0 | 45 | 99 | 45 | 135 | 207 | 0 | 135 | 45 | 63 | 27 | 153 | 0 | 54 | 144 | 117 | 72 | 126 | 0 | 63 | 9 | 81 | 909 | 36 | 0 | 81 | 270 | 207 | 216 | 937.5 | 0 | 153 | 270 | 225 | 72 | 279 | 10380 | 6490.5 | 20760 | 12981 | 20.76 | 12.981
11:00 | 12 | 54 | 11 | 5 | 29 | 10 | 5 | 5 | 7 | 6 | 4 | 6 | 5 | 14 | 14 | 11 | 5 | 6 | 3 | 27 | 6 | 16 | 13 | 7 | 15 | 12 | 2 | 8 | 56 | 7 | 9 | 25 | 35 | 16 | 249 | 28 | 28 | 28 | 8 | 28 | 11:00 | 144 | 648 | 132 | 60 | 348 | 120 | 60 | 60 | 84 | 72 | 48 | 72 | 60 | 168 | 168 | 132 | 60 | 72 | 36 | 324 | 72 | 192 | 156 | 84 | 180 | 144 | 24 | 96 | 672 | 84 | 108 | 300 | 420 | 192 | 2988 | 336 | 336 | 336 | 96 | 336 |  | 11:00 | 108 | 486 | 99 | 45 | 261 | 0 | 90 | 45 | 45 | 63 | 54 | 0 | 36 | 54 | 45 | 126 | 126 | 0 | 99 | 45 | 54 | 27 | 243 | 0 | 54 | 144 | 117 | 63 | 135 | 0 | 108 | 18 | 72 | 504 | 63 | 0 | 81 | 225 | 315 | 144 | 937.5 | 0 | 252 | 252 | 252 | 72 | 252 | 10020 | 6211.5 | 20040 | 12423 | 20.04 | 12.423
11:05 | 12 | 34 | 11 | 6 | 17 | 19 | 5 | 17 | 13 | 7 | 9 | 8 | 6 | 7 | 14 | 14 | 4 | 4 | 3 | 26 | 6 | 15 | 7 | 7 | 13 | 12 | 1 | 6 | 20 | 6 | 20 | 13 | 23 | 13 | 232 | 57 | 28 | 41 | 9 | 27 | 11:05 | 144 | 408 | 132 | 72 | 204 | 228 | 60 | 204 | 156 | 84 | 108 | 96 | 72 | 84 | 168 | 168 | 48 | 48 | 36 | 312 | 72 | 180 | 84 | 84 | 156 | 144 | 12 | 72 | 240 | 72 | 240 | 156 | 276 | 156 | 2784 | 684 | 336 | 492 | 108 | 324 |  | 11:05 | 108 | 306 | 99 | 54 | 153 | 0 | 171 | 45 | 153 | 117 | 63 | 0 | 81 | 72 | 54 | 63 | 126 | 0 | 126 | 36 | 36 | 27 | 234 | 0 | 54 | 135 | 63 | 63 | 117 | 0 | 108 | 9 | 54 | 180 | 54 | 0 | 180 | 117 | 207 | 117 | 937.5 | 0 | 513 | 252 | 369 | 81 | 243 | 9504 | 5977.5 | 19008 | 11955 | 19.008 | 11.955
11:10 | 12 | 14 | 10 | 10 | 17 | 13 | 5 | 13 | 14 | 13 | 12 | 4 | 5 | 6 | 13 | 14 | 4 | 4 | 2 | 23 | 5 | 15 | 6 | 7 | 15 | 10 | 2 | 7 | 12 | 5 | 22 | 29 | 23 | 13 | 230 | 117 | 22 | 187 | 9 | 30 | 11:10 | 144 | 168 | 120 | 120 | 204 | 156 | 60 | 156 | 168 | 156 | 144 | 48 | 60 | 72 | 156 | 168 | 48 | 48 | 24 | 276 | 60 | 180 | 72 | 84 | 180 | 120 | 24 | 84 | 144 | 60 | 264 | 348 | 276 | 156 | 2760 | 1404 | 264 | 2244 | 108 | 360 |  | 11:10 | 108 | 126 | 90 | 90 | 153 | 0 | 117 | 45 | 117 | 126 | 117 | 0 | 108 | 36 | 45 | 54 | 117 | 0 | 126 | 36 | 36 | 18 | 207 | 0 | 45 | 135 | 54 | 63 | 135 | 0 | 90 | 18 | 63 | 108 | 45 | 0 | 198 | 261 | 207 | 117 | 937.5 | 0 | 937.5 | 198 | 937.5 | 81 | 270 | 11688 | 6772.5 | 23376 | 13545 | 23.376 | 13.545
11:15 | 10 | 22 | 9 | 13 | 15 | 47 | 5 | 17 | 13 | 14 | 11 | 10 | 4 | 10 | 14 | 14 | 5 | 5 | 2 | 31 | 5 | 15 | 6 | 6 | 14 | 11 | 1 | 6 | 16 | 5 | 21 | 87 | 25 | 70 | 155 | 21 | 63 | 105 | 22 | 23 | 11:15 | 120 | 264 | 108 | 156 | 180 | 564 | 60 | 204 | 156 | 168 | 132 | 120 | 48 | 120 | 168 | 168 | 60 | 60 | 24 | 372 | 60 | 180 | 72 | 72 | 168 | 132 | 12 | 72 | 192 | 60 | 252 | 1044 | 300 | 840 | 1860 | 252 | 756 | 1260 | 264 | 276 |  | 11:15 | 90 | 198 | 81 | 117 | 135 | 0 | 423 | 45 | 153 | 117 | 126 | 0 | 99 | 90 | 36 | 90 | 126 | 0 | 126 | 45 | 45 | 18 | 279 | 0 | 45 | 135 | 54 | 54 | 126 | 0 | 99 | 9 | 54 | 144 | 45 | 0 | 189 | 783 | 225 | 630 | 937.5 | 0 | 189 | 567 | 937.5 | 198 | 207 | 11376 | 8067 | 22752 | 16134 | 22.752 | 16.134
11:20 | 8 | 2 | 9 | 14 | 16 | 47 | 13 | 16 | 12 | 15 | 11 | 5 | 4 | 0 | 12 | 12 | 13 | 0 | 9 | 27 | 4 | 14 | 6 | 7 | 12 | 10 | 1 | 7 | 15 | 6 | 19 | 90 | 13 | 31 | 59 | 19 | 16 | 19 | 21 | 23 | 11:20 | 96 | 24 | 108 | 168 | 192 | 564 | 156 | 192 | 144 | 180 | 132 | 60 | 48 | 0 | 144 | 144 | 156 | 0 | 108 | 324 | 48 | 168 | 72 | 84 | 144 | 120 | 12 | 84 | 180 | 72 | 228 | 1080 | 156 | 372 | 708 | 228 | 192 | 228 | 252 | 276 |  | 11:20 | 72 | 18 | 81 | 126 | 144 | 0 | 423 | 117 | 144 | 108 | 135 | 0 | 99 | 45 | 36 | 0 | 108 | 0 | 108 | 117 | 0 | 81 | 243 | 0 | 36 | 126 | 54 | 63 | 108 | 0 | 90 | 9 | 63 | 135 | 54 | 0 | 171 | 810 | 117 | 279 | 531 | 0 | 171 | 144 | 171 | 189 | 207 | 7644 | 5733 | 15288 | 11466 | 15.288 | 11.466
11:25 | 3 | 12 | 9 | 11 | 18 | 10 | 15 | 14 | 13 | 16 | 11 | 3 | 4 | 7 | 14 | 7 | 12 | 5 | 11 | 32 | 3 | 14 | 6 | 7 | 12 | 10 | 1 | 6 | 15 | 6 | 20 | 17 | 14 | 12 | 46 | 10 | 15 | 24 | 20 | 24 | 11:25 | 36 | 144 | 108 | 132 | 216 | 120 | 180 | 168 | 156 | 192 | 132 | 36 | 48 | 84 | 168 | 84 | 144 | 60 | 132 | 384 | 36 | 168 | 72 | 84 | 144 | 120 | 12 | 72 | 180 | 72 | 240 | 204 | 168 | 144 | 552 | 120 | 180 | 288 | 240 | 288 |  | 11:25 | 27 | 108 | 81 | 99 | 162 | 0 | 90 | 135 | 126 | 117 | 144 | 0 | 99 | 27 | 36 | 63 | 126 | 0 | 63 | 108 | 45 | 99 | 288 | 0 | 27 | 126 | 54 | 63 | 108 | 0 | 90 | 9 | 54 | 135 | 54 | 0 | 180 | 153 | 126 | 108 | 414 | 0 | 90 | 135 | 216 | 180 | 216 | 6108 | 4581 | 12216 | 9162 | 12.216 | 9.162
11:30 | 5 | 0 | 8 | 17 | 15 | 23 | 13 | 18 | 12 | 15 | 9 | 26 | 10 | 9 | 12 | 5 | 12 | 13 | 11 | 35 | 3 | 14 | 5 | 6 | 8 | 10 | 2 | 7 | 21 | 9 | 16 | 92 | 13 | 13 | 31 | 46 | 55 | 31 | 21 | 33 | 11:30 | 60 | 0 | 96 | 204 | 180 | 276 | 156 | 216 | 144 | 180 | 108 | 312 | 120 | 108 | 144 | 60 | 144 | 156 | 132 | 420 | 36 | 168 | 60 | 72 | 96 | 120 | 24 | 84 | 252 | 108 | 192 | 1104 | 156 | 156 | 372 | 552 | 660 | 372 | 252 | 396 |  | 11:30 | 45 | 0 | 72 | 153 | 135 | 0 | 207 | 117 | 162 | 108 | 135 | 0 | 81 | 234 | 90 | 81 | 108 | 0 | 45 | 108 | 117 | 99 | 315 | 0 | 27 | 126 | 45 | 54 | 72 | 0 | 90 | 18 | 63 | 189 | 81 | 0 | 144 | 828 | 117 | 117 | 279 | 0 | 414 | 495 | 279 | 189 | 297 | 8448 | 6336 | 16896 | 12672 | 16.896 | 12.672
11:35 | 5 | 0 | 8 | 12 | 13 | 13 | 12 | 16 | 12 | 16 | 9 | 45 | 15 | 24 | 15 | 6 | 12 | 13 | 10 | 33 | 14 | 7 | 5 | 6 | 5 | 3 | 1 | 6 | 16 | 11 | 10 | 12 | 16 | 25 | 31 | 12 | 134 | 36 | 18 | 33 | 11:35 | 60 | 0 | 96 | 144 | 156 | 156 | 144 | 192 | 144 | 192 | 108 | 540 | 180 | 288 | 180 | 72 | 144 | 156 | 120 | 396 | 168 | 84 | 60 | 72 | 60 | 36 | 12 | 72 | 192 | 132 | 120 | 144 | 192 | 300 | 372 | 144 | 1608 | 432 | 216 | 396 |  | 11:35 | 45 | 0 | 72 | 108 | 117 | 0 | 117 | 108 | 144 | 108 | 144 | 0 | 81 | 405 | 135 | 216 | 135 | 0 | 54 | 108 | 117 | 90 | 297 | 0 | 126 | 63 | 45 | 54 | 45 | 0 | 27 | 9 | 54 | 144 | 99 | 0 | 90 | 108 | 144 | 225 | 279 | 0 | 108 | 937.5 | 324 | 162 | 297 | 8280 | 5941.5 | 16560 | 11883 | 16.56 | 11.883
11:40 | 5 | 0 | 7 | 8 | 14 | 13 | 13 | 9 | 13 | 12 | 8 | 52 | 14 | 19 | 6 | 6 | 14 | 0 | 10 | 19 | 14 | 7 | 5 | 6 | 4 | 3 | 1 | 7 | 15 | 6 | 9 | 18 | 18 | 24 | 31 | 11 | 189 | 38 | 10 | 98 | 11:40 | 60 | 0 | 84 | 96 | 168 | 156 | 156 | 108 | 156 | 144 | 96 | 624 | 168 | 228 | 72 | 72 | 168 | 0 | 120 | 228 | 168 | 84 | 60 | 72 | 48 | 36 | 12 | 84 | 180 | 72 | 108 | 216 | 216 | 288 | 372 | 132 | 2268 | 456 | 120 | 1176 |  | 11:40 | 45 | 0 | 63 | 72 | 126 | 0 | 117 | 117 | 81 | 117 | 108 | 0 | 72 | 468 | 126 | 171 | 54 | 0 | 54 | 126 | 0 | 90 | 171 | 0 | 126 | 63 | 45 | 54 | 36 | 0 | 27 | 9 | 63 | 135 | 54 | 0 | 81 | 162 | 162 | 216 | 279 | 0 | 99 | 937.5 | 342 | 90 | 882 | 9072 | 6040.5 | 18144 | 12081 | 18.144 | 12.081
11:45 | 4 | 0 | 7 | 7 | 14 | 7 | 9 | 3 | 11 | 16 | 8 | 36 | 13 | 20 | 8 | 6 | 14 | 0 | 12 | 20 | 13 | 6 | 5 | 6 | 6 | 3 | 2 | 6 | 13 | 6 | 9 | 23 | 16 | 24 | 30 | 14 | 68 | 35 | 10 | 34 | 11:45 | 48 | 0 | 84 | 84 | 168 | 84 | 108 | 36 | 132 | 192 | 96 | 432 | 156 | 240 | 96 | 72 | 168 | 0 | 144 | 240 | 156 | 72 | 60 | 72 | 72 | 36 | 24 | 72 | 156 | 72 | 108 | 276 | 192 | 288 | 360 | 168 | 816 | 420 | 120 | 408 |  | 11:45 | 36 | 0 | 63 | 63 | 126 | 0 | 63 | 81 | 27 | 99 | 144 | 0 | 72 | 324 | 117 | 180 | 72 | 0 | 54 | 126 | 0 | 108 | 180 | 0 | 117 | 54 | 45 | 54 | 54 | 0 | 27 | 18 | 54 | 117 | 54 | 0 | 81 | 207 | 144 | 216 | 270 | 0 | 126 | 612 | 315 | 90 | 306 | 6528 | 4896 | 13056 | 9792 | 13.056 | 9.792
11:50 | 5 | 0 | 7 | 7 | 13 | 13 | 11 | 6 | 6 | 15 | 77 | 62 | 13 | 18 | 2 | 5 | 13 | 7 | 11 | 26 | 14 | 6 | 10 | 6 | 4 | 2 | 10 | 6 | 8 | 17 | 8 | 22 | 22 | 24 | 28 | 17 | 28 | 30 | 9 | 182 | 11:50 | 60 | 0 | 84 | 84 | 156 | 156 | 132 | 72 | 72 | 180 | 924 | 744 | 156 | 216 | 24 | 60 | 156 | 84 | 132 | 312 | 168 | 72 | 120 | 72 | 48 | 24 | 120 | 72 | 96 | 204 | 96 | 264 | 264 | 288 | 336 | 204 | 336 | 360 | 108 | 2184 |  | 11:50 | 45 | 0 | 63 | 63 | 117 | 0 | 117 | 99 | 54 | 54 | 135 | 0 | 693 | 558 | 117 | 162 | 18 | 0 | 45 | 117 | 63 | 99 | 234 | 0 | 126 | 54 | 90 | 54 | 36 | 0 | 18 | 90 | 54 | 72 | 153 | 0 | 72 | 198 | 198 | 216 | 252 | 0 | 153 | 252 | 270 | 81 | 937.5 | 9240 | 6229.5 | 18480 | 12459 | 18.48 | 12.459
11:55 | 5 | 13 | 7 | 7 | 12 | 4 | 11 | 6 | 5 | 13 | 12 | 63 | 12 | 14 | 8 | 5 | 16 | 16 | 10 | 19 | 13 | 6 | 4 | 6 | 6 | 2 | 11 | 6 | 6 | 16 | 8 | 40 | 45 | 58 | 20 | 27 | 27 | 25 | 9 | 242 | 11:55 | 60 | 156 | 84 | 84 | 144 | 48 | 132 | 72 | 60 | 156 | 144 | 756 | 144 | 168 | 96 | 60 | 192 | 192 | 120 | 228 | 156 | 72 | 48 | 72 | 72 | 24 | 132 | 72 | 72 | 192 | 96 | 480 | 540 | 696 | 240 | 324 | 324 | 300 | 108 | 2904 |  | 11:55 | 45 | 117 | 63 | 63 | 108 | 0 | 36 | 99 | 54 | 45 | 117 | 0 | 108 | 567 | 108 | 126 | 72 | 0 | 45 | 144 | 144 | 90 | 171 | 0 | 117 | 54 | 36 | 54 | 54 | 0 | 18 | 99 | 54 | 54 | 144 | 0 | 72 | 360 | 405 | 522 | 180 | 0 | 243 | 243 | 225 | 81 | 937.5 | 10020 | 6274.5 | 20040 | 12549 | 20.04 | 12.549
12:00 | 5 | 11 | 6 | 6 | 5 | 8 | 12 | 15 | 5 | 8 | 4 | 59 | 12 | 13 | 5 | 6 | 13 | 17 | 7 | 18 | 12 | 5 | 5 | 7 | 6 | 2 | 11 | 5 | 6 | 14 | 8 | 48 | 209 | 38 | 20 | 57 | 26 | 84 | 9 | 53 | 12:00 | 60 | 132 | 72 | 72 | 60 | 96 | 144 | 180 | 60 | 96 | 48 | 708 | 144 | 156 | 60 | 72 | 156 | 204 | 84 | 216 | 144 | 60 | 60 | 84 | 72 | 24 | 132 | 60 | 72 | 168 | 96 | 576 | 2508 | 456 | 240 | 684 | 312 | 1008 | 108 | 636 |  | 12:00 | 45 | 99 | 54 | 54 | 45 | 0 | 72 | 108 | 135 | 45 | 72 | 0 | 36 | 531 | 108 | 117 | 45 | 0 | 54 | 117 | 153 | 63 | 162 | 0 | 108 | 45 | 45 | 63 | 54 | 0 | 18 | 99 | 45 | 54 | 126 | 0 | 72 | 432 | 937.5 | 342 | 180 | 0 | 513 | 234 | 756 | 81 | 477 | 10320 | 6796.5 | 20640 | 13593 | 20.64 | 13.593
12:05 | 5 | 8 | 6 | 1 | 7 | 1 | 4 | 4 | 5 | 7 | 12 | 71 | 13 | 20 | 5 | 6 | 8 | 8 | 3 | 32 | 6 | 6 | 5 | 6 | 5 | 3 | 10 | 5 | 8 | 14 | 8 | 53 | 70 | 31 | 21 | 33 | 24 | 27 | 10 | 128 | 12:05 | 60 | 96 | 72 | 12 | 84 | 12 | 48 | 48 | 60 | 84 | 144 | 852 | 156 | 240 | 60 | 72 | 96 | 96 | 36 | 384 | 72 | 72 | 60 | 72 | 60 | 36 | 120 | 60 | 96 | 168 | 96 | 636 | 840 | 372 | 252 | 396 | 288 | 324 | 120 | 1536 |  | 12:05 | 45 | 72 | 54 | 9 | 63 | 0 | 9 | 36 | 36 | 45 | 63 | 0 | 108 | 639 | 117 | 180 | 45 | 0 | 54 | 72 | 72 | 27 | 288 | 0 | 54 | 54 | 45 | 54 | 45 | 0 | 27 | 90 | 45 | 72 | 126 | 0 | 72 | 477 | 630 | 279 | 189 | 0 | 297 | 216 | 243 | 90 | 937.5 | 8388 | 6076.5 | 16776 | 12153 | 16.776 | 12.153
12:10 | 5 | 5 | 2 | 0 | 6 | 4 | 3 | 6 | 1 | 6 | 6 | 68 | 13 | 17 | 3 | 5 | 3 | 12 | 4 | 19 | 5 | 6 | 7 | 5 | 0 | 3 | 10 | 5 | 12 | 13 | 17 | 23 | 181 | 22 | 21 | 39 | 13 | 127 | 22 | 41 | 12:10 | 60 | 60 | 24 | 0 | 72 | 48 | 36 | 72 | 12 | 72 | 72 | 816 | 156 | 204 | 36 | 60 | 36 | 144 | 48 | 228 | 60 | 72 | 84 | 60 | 0 | 36 | 120 | 60 | 144 | 156 | 204 | 276 | 2172 | 264 | 252 | 468 | 156 | 1524 | 264 | 492 |  | 12:10 | 45 | 45 | 18 | 0 | 54 | 0 | 36 | 27 | 54 | 9 | 54 | 0 | 54 | 612 | 117 | 153 | 27 | 0 | 45 | 27 | 108 | 36 | 171 | 0 | 45 | 54 | 63 | 45 | 0 | 0 | 27 | 90 | 45 | 108 | 117 | 0 | 153 | 207 | 937.5 | 198 | 189 | 0 | 351 | 117 | 937.5 | 198 | 369 | 9120 | 5943 | 18240 | 11886 | 18.24 | 11.886
12:15 | 4 | 9 | 0 | 0 | 5 | 0 | 9 | 6 | 0 | 7 | 5 | 78 | 8 | 12 | 9 | 4 | 4 | 13 | 3 | 19 | 5 | 5 | 8 | 5 | 3 | 5 | 10 | 6 | 7 | 13 | 21 | 11 | 210 | 23 | 66 | 39 | 12 | 368 | 21 | 27 | 12:15 | 48 | 108 | 0 | 0 | 60 | 0 | 108 | 72 | 0 | 84 | 60 | 936 | 96 | 144 | 108 | 48 | 48 | 156 | 36 | 228 | 60 | 60 | 96 | 60 | 36 | 60 | 120 | 72 | 84 | 156 | 252 | 132 | 2520 | 276 | 792 | 468 | 144 | 4416 | 252 | 324 |  | 12:15 | 36 | 81 | 0 | 0 | 45 | 0 | 0 | 81 | 54 | 0 | 63 | 0 | 45 | 702 | 72 | 108 | 81 | 0 | 36 | 36 | 117 | 27 | 171 | 0 | 45 | 45 | 72 | 45 | 27 | 0 | 45 | 90 | 54 | 63 | 117 | 0 | 189 | 99 | 937.5 | 207 | 594 | 0 | 351 | 108 | 937.5 | 189 | 243 | 12720 | 6213 | 25440 | 12426 | 25.44 | 12.426
12:20 | 5 | 18 | 0 | 0 | 3 | 0 | 5 | 4 | 0 | 0 | 6 | 26 | 4 | 3 | 7 | 5 | 73 | 11 | 4 | 18 | 5 | 5 | 7 | 5 | 5 | 4 | 10 | 12 | 3 | 13 | 21 | 12 | 157 | 23 | 30 | 15 | 13 | 404 | 21 | 34 | 12:20 | 60 | 216 | 0 | 0 | 36 | 0 | 60 | 48 | 0 | 0 | 72 | 312 | 48 | 36 | 84 | 60 | 876 | 132 | 48 | 216 | 60 | 60 | 84 | 60 | 60 | 48 | 120 | 144 | 36 | 156 | 252 | 144 | 1884 | 276 | 360 | 180 | 156 | 4848 | 252 | 408 |  | 12:20 | 45 | 162 | 0 | 0 | 27 | 0 | 0 | 45 | 36 | 0 | 0 | 0 | 54 | 234 | 36 | 27 | 63 | 0 | 45 | 657 | 99 | 36 | 162 | 0 | 45 | 45 | 63 | 45 | 45 | 0 | 36 | 90 | 108 | 27 | 117 | 0 | 189 | 108 | 937.5 | 207 | 270 | 0 | 135 | 117 | 937.5 | 189 | 306 | 11892 | 5745 | 23784 | 11490 | 23.784 | 11.49
12:25 | 14 | 13 | 0 | 0 | 2 | 3 | 4 | 7 | 5 | 0 | 0 | 12 | 4 | 0 | 5 | 6 | 6 | 8 | 3 | 19 | 6 | 5 | 5 | 5 | 7 | 4 | 9 | 14 | 12 | 13 | 20 | 25 | 55 | 23 | 27 | 15 | 12 | 198 | 20 | 69 | 12:25 | 168 | 156 | 0 | 0 | 24 | 36 | 48 | 84 | 60 | 0 | 0 | 144 | 48 | 0 | 60 | 72 | 72 | 96 | 36 | 228 | 72 | 60 | 60 | 60 | 84 | 48 | 108 | 168 | 144 | 156 | 240 | 300 | 660 | 276 | 324 | 180 | 144 | 2376 | 240 | 828 |  | 12:25 | 126 | 117 | 0 | 0 | 18 | 0 | 27 | 36 | 63 | 45 | 0 | 0 | 0 | 108 | 36 | 0 | 45 | 0 | 54 | 54 | 72 | 27 | 171 | 0 | 54 | 45 | 45 | 45 | 63 | 0 | 36 | 81 | 126 | 108 | 117 | 0 | 180 | 225 | 495 | 207 | 243 | 0 | 135 | 108 | 937.5 | 180 | 621 | 7860 | 5050.5 | 15720 | 10101 | 15.72 | 10.101
12:30 | 12 | 14 | 0 | 0 | 1 | 2 | 0 | 6 | 11 | 0 | 0 | 15 | 4 | 5 | 13 | 6 | 4 | 6 | 3 | 18 | 6 | 6 | 6 | 5 | 3 | 4 | 2 | 14 | 6 | 12 | 20 | 32 | 74 | 23 | 27 | 14 | 11 | 269 | 17 | 34 | 12:30 | 144 | 168 | 0 | 0 | 12 | 24 | 0 | 72 | 132 | 0 | 0 | 180 | 48 | 60 | 156 | 72 | 48 | 72 | 36 | 216 | 72 | 72 | 72 | 60 | 36 | 48 | 24 | 168 | 72 | 144 | 240 | 384 | 888 | 276 | 324 | 168 | 132 | 3228 | 204 | 408 |  | 12:30 | 108 | 126 | 0 | 0 | 9 | 0 | 18 | 0 | 54 | 99 | 0 | 0 | 0 | 135 | 36 | 45 | 117 | 0 | 54 | 36 | 54 | 27 | 162 | 0 | 54 | 54 | 54 | 45 | 27 | 0 | 36 | 18 | 126 | 54 | 108 | 0 | 180 | 288 | 666 | 207 | 243 | 0 | 126 | 99 | 937.5 | 153 | 306 | 8460 | 4861.5 | 16920 | 9723 | 16.92 | 9.723
12:35 | 13 | 17 | 0 | 0 | 3 | 0 | 8 | 9 | 5 | 130 | 2 | 15 | 5 | 9 | 6 | 6 | 4 | 7 | 4 | 18 | 5 | 6 | 5 | 11 | 14 | 4 | 1 | 12 | 6 | 12 | 19 | 9 | 25 | 21 | 33 | 15 | 12 | 310 | 9 | 34 | 12:35 | 156 | 204 | 0 | 0 | 36 | 0 | 96 | 108 | 60 | 1560 | 24 | 180 | 60 | 108 | 72 | 72 | 48 | 84 | 48 | 216 | 60 | 72 | 60 | 132 | 168 | 48 | 12 | 144 | 72 | 144 | 228 | 108 | 300 | 252 | 396 | 180 | 144 | 3720 | 108 | 408 |  | 12:35 | 117 | 153 | 0 | 0 | 27 | 0 | 0 | 72 | 81 | 45 | 937.5 | 0 | 18 | 135 | 45 | 81 | 54 | 0 | 54 | 36 | 63 | 36 | 162 | 0 | 45 | 54 | 45 | 99 | 126 | 0 | 36 | 9 | 108 | 54 | 108 | 0 | 171 | 81 | 225 | 189 | 297 | 0 | 135 | 108 | 937.5 | 81 | 306 | 9888 | 5331 | 19776 | 10662 | 19.776 | 10.662
12:40 | 12 | 11 | 0 | 0 | 4 | 0 | 4 | 0 | 5 | 15 | 0 | 30 | 5 | 18 | 6 | 6 | 4 | 7 | 6 | 10 | 5 | 6 | 6 | 14 | 6 | 4 | 2 | 13 | 5 | 9 | 11 | 9 | 25 | 23 | 27 | 14 | 16 | 170 | 8 | 34 | 12:40 | 144 | 132 | 0 | 0 | 48 | 0 | 48 | 0 | 60 | 180 | 0 | 360 | 60 | 216 | 72 | 72 | 48 | 84 | 72 | 120 | 60 | 72 | 72 | 168 | 72 | 48 | 24 | 156 | 60 | 108 | 132 | 108 | 300 | 276 | 324 | 168 | 192 | 2040 | 96 | 408 |  | 12:40 | 108 | 99 | 0 | 0 | 36 | 0 | 0 | 36 | 0 | 45 | 135 | 0 | 0 | 270 | 45 | 162 | 54 | 0 | 54 | 36 | 63 | 54 | 90 | 0 | 45 | 54 | 54 | 126 | 54 | 0 | 36 | 18 | 117 | 45 | 81 | 0 | 99 | 81 | 225 | 207 | 243 | 0 | 126 | 144 | 937.5 | 72 | 306 | 6600 | 4357.5 | 13200 | 8715 | 13.2 | 8.715
12:45 | 12 | 12 | 0 | 0 | 5 | 0 | 3 | 21 | 5 | 38 | 0 | 61 | 4 | 0 | 7 | 5 | 7 | 6 | 5 | 115 | 6 | 5 | 3 | 13 | 3 | 4 | 2 | 12 | 5 | 4 | 9 | 14 | 22 | 21 | 25 | 15 | 22 | 86 | 10 | 35 | 12:45 | 144 | 144 | 0 | 0 | 60 | 0 | 36 | 252 | 60 | 456 | 0 | 732 | 48 | 0 | 84 | 60 | 84 | 72 | 60 | 1380 | 72 | 60 | 36 | 156 | 36 | 48 | 24 | 144 | 60 | 48 | 108 | 168 | 264 | 252 | 300 | 180 | 264 | 1032 | 120 | 420 |  | 12:45 | 108 | 108 | 0 | 0 | 45 | 0 | 0 | 27 | 189 | 45 | 342 | 0 | 0 | 549 | 36 | 0 | 63 | 0 | 45 | 63 | 54 | 45 | 937.5 | 0 | 54 | 45 | 27 | 117 | 27 | 0 | 36 | 18 | 108 | 45 | 36 | 0 | 81 | 126 | 198 | 189 | 225 | 0 | 135 | 198 | 774 | 90 | 315 | 7464 | 5500.5 | 14928 | 11001 | 14.928 | 11.001
12:50 | 12 | 10 | 0 | 0 | 4 | 0 | 4 | 10 | 0 | 14 | 0 | 6 | 5 | 0 | 5 | 7 | 2 | 4 | 5 | 99 | 7 | 13 | 6 | 13 | 4 | 3 | 2 | 12 | 5 | 4 | 9 | 20 | 46 | 23 | 15 | 23 | 22 | 39 | 9 | 29 | 12:50 | 144 | 120 | 0 | 0 | 48 | 0 | 48 | 120 | 0 | 168 | 0 | 72 | 60 | 0 | 60 | 84 | 24 | 48 | 60 | 1188 | 84 | 156 | 72 | 156 | 48 | 36 | 24 | 144 | 60 | 48 | 108 | 240 | 552 | 276 | 180 | 276 | 264 | 468 | 108 | 348 |  | 12:50 | 108 | 90 | 0 | 0 | 36 | 0 | 0 | 36 | 90 | 0 | 126 | 0 | 0 | 54 | 45 | 0 | 45 | 0 | 63 | 18 | 36 | 45 | 891 | 0 | 63 | 117 | 54 | 117 | 36 | 0 | 27 | 18 | 108 | 45 | 36 | 0 | 81 | 180 | 414 | 207 | 135 | 0 | 207 | 198 | 351 | 81 | 261 | 5892 | 4419 | 11784 | 8838 | 11.784 | 8.838
12:55 | 12 | 20 | 0 | 0 | 3 | 0 | 5 | 49 | 1 | 14 | 11 | 15 | 4 | 12 | 4 | 12 | 2 | 6 | 5 | 24 | 6 | 13 | 7 | 13 | 2 | 3 | 2 | 12 | 5 | 4 | 9 | 19 | 76 | 21 | 15 | 69 | 20 | 64 | 9 | 86 | 12:55 | 144 | 240 | 0 | 0 | 36 | 0 | 60 | 588 | 12 | 168 | 132 | 180 | 48 | 144 | 48 | 144 | 24 | 72 | 60 | 288 | 72 | 156 | 84 | 156 | 24 | 36 | 24 | 144 | 60 | 48 | 108 | 228 | 912 | 252 | 180 | 828 | 240 | 768 | 108 | 1032 |  | 12:55 | 108 | 180 | 0 | 0 | 27 | 0 | 0 | 45 | 441 | 9 | 126 | 0 | 99 | 135 | 36 | 108 | 36 | 0 | 108 | 18 | 54 | 45 | 216 | 0 | 54 | 117 | 63 | 117 | 18 | 0 | 27 | 18 | 108 | 45 | 36 | 0 | 81 | 171 | 684 | 189 | 135 | 0 | 621 | 180 | 576 | 81 | 774 | 7848 | 5886 | 15696 | 11772 | 15.696 | 11.772
13:00 | 12 | 21 | 0 | 0 | 5 | 0 | 5 | 20 | 2 | 20 | 7 | 6 | 4 | 5 | 9 | 15 | 3 | 0 | 5 | 12 | 5 | 13 | 16 | 12 | 5 | 3 | 2 | 12 | 5 | 4 | 8 | 21 | 23 | 22 | 16 | 51 | 23 | 57 | 14 | 398 | 13:00 | 144 | 252 | 0 | 0 | 60 | 0 | 60 | 240 | 24 | 240 | 84 | 72 | 48 | 60 | 108 | 180 | 36 | 0 | 60 | 144 | 60 | 156 | 192 | 144 | 60 | 36 | 24 | 144 | 60 | 48 | 96 | 252 | 276 | 264 | 192 | 612 | 276 | 684 | 168 | 4776 |  | 13:00 | 108 | 189 | 0 | 0 | 45 | 0 | 0 | 45 | 180 | 18 | 180 | 0 | 63 | 54 | 36 | 45 | 81 | 0 | 135 | 27 | 0 | 45 | 108 | 0 | 45 | 117 | 144 | 108 | 45 | 0 | 27 | 18 | 108 | 45 | 36 | 0 | 72 | 189 | 207 | 198 | 144 | 0 | 459 | 207 | 513 | 126 | 937.5 | 10332 | 5104.5 | 20664 | 10209 | 20.664 | 10.209
13:05 | 6 | 7 | 0 | 0 | 8 | 0 | 4 | 11 | 9 | 17 | 17 | 3 | 3 | 16 | 14 | 14 | 5 | 13 | 4 | 94 | 5 | 13 | 17 | 12 | 5 | 4 | 2 | 11 | 5 | 4 | 7 | 24 | 25 | 21 | 16 | 25 | 11 | 53 | 59 | 366 | 13:05 | 72 | 84 | 0 | 0 | 96 | 0 | 48 | 132 | 108 | 204 | 204 | 36 | 36 | 192 | 168 | 168 | 60 | 156 | 48 | 1128 | 60 | 156 | 204 | 144 | 60 | 48 | 24 | 132 | 60 | 48 | 84 | 288 | 300 | 252 | 192 | 300 | 132 | 636 | 708 | 4392 |  | 13:05 | 54 | 63 | 0 | 0 | 72 | 0 | 0 | 36 | 99 | 81 | 153 | 0 | 153 | 27 | 27 | 144 | 126 | 0 | 126 | 45 | 117 | 36 | 846 | 0 | 45 | 117 | 153 | 108 | 45 | 0 | 36 | 18 | 99 | 45 | 36 | 0 | 63 | 216 | 225 | 189 | 144 | 0 | 225 | 99 | 477 | 531 | 937.5 | 11160 | 6013.5 | 22320 | 12027 | 22.32 | 12.027
13:10 | 66 | 3 | 0 | 0 | 18 | 10 | 5 | 16 | 12 | 48 | 5 | 12 | 4 | 5 | 13 | 12 | 7 | 2 | 5 | 91 | 3 | 12 | 11 | 12 | 3 | 3 | 2 | 12 | 5 | 4 | 9 | 22 | 39 | 21 | 15 | 66 | 15 | 31 | 44 | 262 | 13:10 | 792 | 36 | 0 | 0 | 216 | 120 | 60 | 192 | 144 | 576 | 60 | 144 | 48 | 60 | 156 | 144 | 84 | 24 | 60 | 1092 | 36 | 144 | 132 | 144 | 36 | 36 | 24 | 144 | 60 | 48 | 108 | 264 | 468 | 252 | 180 | 792 | 180 | 372 | 528 | 3144 |  | 13:10 | 594 | 27 | 0 | 0 | 162 | 0 | 90 | 45 | 144 | 108 | 432 | 0 | 45 | 108 | 36 | 45 | 117 | 0 | 108 | 63 | 18 | 45 | 819 | 0 | 27 | 108 | 99 | 108 | 27 | 0 | 27 | 18 | 108 | 45 | 36 | 0 | 81 | 198 | 351 | 189 | 135 | 0 | 594 | 135 | 279 | 396 | 937.5 | 11100 | 6904.5 | 22200 | 13809 | 22.2 | 13.809
13:15 | 5 | 4 | 7 | 0 | 19 | 24 | 4 | 9 | 17 | 46 | 4 | 29 | 4 | 11 | 13 | 13 | 4 | 2 | 4 | 20 | 4 | 12 | 14 | 12 | 3 | 6 | 2 | 12 | 6 | 5 | 8 | 21 | 40 | 22 | 22 | 27 | 10 | 34 | 27 | 429 | 13:15 | 60 | 48 | 84 | 0 | 228 | 288 | 48 | 108 | 204 | 552 | 48 | 348 | 48 | 132 | 156 | 156 | 48 | 24 | 48 | 240 | 48 | 144 | 168 | 144 | 36 | 72 | 24 | 144 | 72 | 60 | 96 | 252 | 480 | 264 | 264 | 324 | 120 | 408 | 324 | 5148 |  | 13:15 | 45 | 36 | 63 | 0 | 171 | 0 | 216 | 36 | 81 | 153 | 414 | 0 | 36 | 261 | 36 | 99 | 117 | 0 | 117 | 36 | 18 | 36 | 180 | 0 | 36 | 108 | 126 | 108 | 27 | 0 | 54 | 18 | 108 | 54 | 45 | 0 | 72 | 189 | 360 | 198 | 198 | 0 | 243 | 90 | 306 | 243 | 937.5 | 11460 | 5671.5 | 22920 | 11343 | 22.92 | 11.343
13:20 | 6 | 2 | 4 | 5 | 18 | 8 | 11 | 19 | 13 | 15 | 14 | 0 | 3 | 22 | 13 | 11 | 4 | 5 | 4 | 94 | 2 | 13 | 16 | 12 | 3 | 12 | 2 | 10 | 13 | 4 | 19 | 20 | 41 | 21 | 26 | 14 | 10 | 42 | 27 | 432 | 13:20 | 72 | 24 | 48 | 60 | 216 | 96 | 132 | 228 | 156 | 180 | 168 | 0 | 36 | 264 | 156 | 132 | 48 | 60 | 48 | 1128 | 24 | 156 | 192 | 144 | 36 | 144 | 24 | 120 | 156 | 48 | 228 | 240 | 492 | 252 | 312 | 168 | 120 | 504 | 324 | 5184 |  | 13:20 | 54 | 18 | 36 | 45 | 162 | 0 | 72 | 99 | 171 | 117 | 135 | 0 | 126 | 0 | 27 | 198 | 117 | 0 | 99 | 36 | 45 | 36 | 846 | 0 | 18 | 117 | 144 | 108 | 27 | 0 | 108 | 18 | 90 | 117 | 36 | 0 | 171 | 180 | 369 | 189 | 234 | 0 | 126 | 90 | 378 | 243 | 937.5 | 12120 | 6139.5 | 24240 | 12279 | 24.24 | 12.279
13:25 | 5 | 7 | 4 | 5 | 19 | 4 | 8 | 9 | 12 | 14 | 8 | 0 | 4 | 6 | 11 | 12 | 4 | 6 | 4 | 10 | 11 | 13 | 14 | 12 | 10 | 12 | 2 | 4 | 14 | 5 | 20 | 21 | 38 | 20 | 29 | 13 | 11 | 42 | 22 | 422 | 13:25 | 60 | 84 | 48 | 60 | 228 | 48 | 96 | 108 | 144 | 168 | 96 | 0 | 48 | 72 | 132 | 144 | 48 | 72 | 48 | 120 | 132 | 156 | 168 | 144 | 120 | 144 | 24 | 48 | 168 | 60 | 240 | 252 | 456 | 240 | 348 | 156 | 132 | 504 | 264 | 5064 |  | 13:25 | 45 | 63 | 36 | 45 | 171 | 0 | 36 | 72 | 81 | 108 | 126 | 0 | 72 | 0 | 36 | 54 | 99 | 0 | 108 | 36 | 54 | 36 | 90 | 0 | 99 | 117 | 126 | 108 | 90 | 0 | 108 | 18 | 36 | 126 | 45 | 0 | 180 | 189 | 342 | 180 | 261 | 0 | 117 | 99 | 378 | 198 | 937.5 | 10644 | 5122.5 | 21288 | 10245 | 21.288 | 10.245
13:30 | 5 | 12 | 4 | 4 | 18 | 3 | 9 | 10 | 11 | 10 | 10 | 0 | 6 | 10 | 24 | 13 | 9 | 5 | 4 | 26 | 13 | 12 | 12 | 11 | 14 | 11 | 2 | 4 | 15 | 4 | 19 | 21 | 26 | 21 | 29 | 38 | 9 | 42 | 15 | 333 | 13:30 | 60 | 144 | 48 | 48 | 216 | 36 | 108 | 120 | 132 | 120 | 120 | 0 | 72 | 120 | 288 | 156 | 108 | 60 | 48 | 312 | 156 | 144 | 144 | 132 | 168 | 132 | 24 | 48 | 180 | 48 | 228 | 252 | 312 | 252 | 348 | 456 | 108 | 504 | 180 | 3996 |  | 13:30 | 45 | 108 | 36 | 36 | 162 | 0 | 27 | 81 | 90 | 99 | 90 | 0 | 90 | 0 | 54 | 90 | 216 | 0 | 117 | 81 | 45 | 36 | 234 | 0 | 117 | 108 | 108 | 99 | 126 | 0 | 99 | 18 | 36 | 135 | 36 | 0 | 171 | 189 | 234 | 189 | 261 | 0 | 342 | 81 | 378 | 135 | 937.5 | 10128 | 5536.5 | 20256 | 11073 | 20.256 | 11.073
13:35 | 4 | 17 | 4 | 4 | 18 | 3 | 15 | 14 | 12 | 5 | 10 | 1 | 14 | 4 | 11 | 13 | 19 | 6 | 11 | 26 | 13 | 12 | 12 | 11 | 11 | 11 | 2 | 4 | 13 | 4 | 19 | 20 | 42 | 20 | 30 | 27 | 14 | 23 | 15 | 118 | 13:35 | 48 | 204 | 48 | 48 | 216 | 36 | 180 | 168 | 144 | 60 | 120 | 12 | 168 | 48 | 132 | 156 | 228 | 72 | 132 | 312 | 156 | 144 | 144 | 132 | 132 | 132 | 24 | 48 | 156 | 48 | 228 | 240 | 504 | 240 | 360 | 324 | 168 | 276 | 180 | 1416 |  | 13:35 | 36 | 153 | 36 | 36 | 162 | 0 | 27 | 135 | 126 | 108 | 45 | 0 | 90 | 9 | 126 | 36 | 99 | 0 | 117 | 171 | 54 | 99 | 234 | 0 | 117 | 108 | 108 | 99 | 99 | 0 | 99 | 18 | 36 | 117 | 36 | 0 | 171 | 180 | 378 | 180 | 270 | 0 | 243 | 126 | 207 | 135 | 937.5 | 7584 | 5563.5 | 15168 | 11127 | 15.168 | 11.127
13:40 | 5 | 7 | 3 | 5 | 18 | 7 | 13 | 16 | 11 | 3 | 10 | 0 | 12 | 5 | 14 | 10 | 43 | 4 | 13 | 27 | 13 | 12 | 13 | 4 | 11 | 11 | 2 | 3 | 13 | 5 | 19 | 20 | 82 | 20 | 26 | 51 | 28 | 13 | 15 | 56 | 13:40 | 60 | 84 | 36 | 60 | 216 | 84 | 156 | 192 | 132 | 36 | 120 | 0 | 144 | 60 | 168 | 120 | 516 | 48 | 156 | 324 | 156 | 144 | 156 | 48 | 132 | 132 | 24 | 36 | 156 | 60 | 228 | 240 | 984 | 240 | 312 | 612 | 336 | 156 | 180 | 672 |  | 13:40 | 45 | 63 | 27 | 45 | 162 | 0 | 63 | 117 | 144 | 99 | 27 | 0 | 90 | 0 | 108 | 45 | 126 | 0 | 90 | 387 | 36 | 117 | 243 | 0 | 117 | 108 | 117 | 36 | 99 | 0 | 99 | 18 | 27 | 117 | 45 | 0 | 171 | 180 | 738 | 180 | 234 | 0 | 459 | 252 | 117 | 135 | 504 | 7716 | 5787 | 15432 | 11574 | 15.432 | 11.574
13:45 | 5 | 3 | 3 | 4 | 18 | 4 | 13 | 2 | 11 | 4 | 18 | 5 | 11 | 6 | 11 | 4 | 84 | 2 | 11 | 26 | 12 | 11 | 12 | 4 | 13 | 10 | 2 | 4 | 14 | 4 | 19 | 20 | 20 | 20 | 19 | 16 | 25 | 10 | 15 | 32 | 13:45 | 60 | 36 | 36 | 48 | 216 | 48 | 156 | 24 | 132 | 48 | 216 | 60 | 132 | 72 | 132 | 48 | 1008 | 24 | 132 | 312 | 144 | 132 | 144 | 48 | 156 | 120 | 24 | 48 | 168 | 48 | 228 | 240 | 240 | 240 | 228 | 192 | 300 | 120 | 180 | 384 |  | 13:45 | 45 | 27 | 27 | 36 | 162 | 0 | 36 | 117 | 18 | 99 | 36 | 0 | 162 | 45 | 99 | 54 | 99 | 0 | 36 | 756 | 18 | 99 | 234 | 0 | 108 | 99 | 108 | 36 | 117 | 0 | 90 | 18 | 36 | 126 | 36 | 0 | 171 | 180 | 180 | 180 | 171 | 0 | 144 | 225 | 90 | 135 | 288 | 6324 | 4743 | 12648 | 9486 | 12.648 | 9.486
13:50 | 91 | 1 | 4 | 4 | 17 | 3 | 9 | 5 | 11 | 6 | 6 | 0 | 11 | 13 | 5 | 3 | 40 | 6 | 11 | 29 | 12 | 12 | 6 | 4 | 10 | 10 | 2 | 4 | 13 | 4 | 10 | 19 | 22 | 24 | 19 | 23 | 19 | 10 | 14 | 29 | 13:50 | 1092 | 12 | 48 | 48 | 204 | 36 | 108 | 60 | 132 | 72 | 72 | 0 | 132 | 156 | 60 | 36 | 480 | 72 | 132 | 348 | 144 | 144 | 72 | 48 | 120 | 120 | 24 | 48 | 156 | 48 | 120 | 228 | 264 | 288 | 228 | 276 | 228 | 120 | 168 | 348 |  | 13:50 | 819 | 9 | 36 | 36 | 153 | 0 | 27 | 81 | 45 | 99 | 54 | 0 | 54 | 0 | 99 | 117 | 45 | 0 | 27 | 360 | 54 | 99 | 261 | 0 | 108 | 108 | 54 | 36 | 90 | 0 | 90 | 18 | 36 | 117 | 36 | 0 | 90 | 171 | 198 | 216 | 171 | 0 | 207 | 171 | 90 | 126 | 261 | 6492 | 4869 | 12984 | 9738 | 12.984 | 9.738
13:55 | 23 | 2 | 16 | 5 | 17 | 2 | 12 | 22 | 10 | 11 | 61 | 1 | 12 | 17 | 2 | 4 | 5 | 5 | 11 | 20 | 12 | 11 | 6 | 4 | 11 | 3 | 1 | 4 | 14 | 4 | 9 | 20 | 25 | 23 | 18 | 43 | 25 | 8 | 19 | 32 | 13:55 | 276 | 24 | 192 | 60 | 204 | 24 | 144 | 264 | 120 | 132 | 732 | 12 | 144 | 204 | 24 | 48 | 60 | 60 | 132 | 240 | 144 | 132 | 72 | 48 | 132 | 36 | 12 | 48 | 168 | 48 | 108 | 240 | 300 | 276 | 216 | 516 | 300 | 96 | 228 | 384 |  | 13:55 | 207 | 18 | 144 | 45 | 153 | 0 | 18 | 108 | 198 | 90 | 99 | 0 | 549 | 9 | 108 | 153 | 18 | 0 | 36 | 45 | 45 | 99 | 180 | 0 | 108 | 99 | 54 | 36 | 99 | 0 | 27 | 9 | 36 | 126 | 36 | 0 | 81 | 180 | 225 | 207 | 162 | 0 | 387 | 225 | 72 | 171 | 288 | 6600 | 4950 | 13200 | 9900 | 13.2 | 9.9
14:00 | 22 | 6 | 63 | 5 | 17 | 4 | 12 | 1 | 4 | 13 | 20 | 11 | 11 | 17 | 5 | 4 | 4 | 5 | 12 | 14 | 4 | 11 | 6 | 5 | 10 | 4 | 1 | 4 | 14 | 4 | 9 | 20 | 34 | 22 | 18 | 74 | 9 | 19 | 26 | 28 | 14:00 | 264 | 72 | 756 | 60 | 204 | 48 | 144 | 12 | 48 | 156 | 240 | 132 | 132 | 204 | 60 | 48 | 48 | 60 | 144 | 168 | 48 | 132 | 72 | 60 | 120 | 48 | 12 | 48 | 168 | 48 | 108 | 240 | 408 | 264 | 216 | 888 | 108 | 228 | 312 | 336 |  | 14:00 | 198 | 54 | 567 | 45 | 153 | 0 | 36 | 108 | 9 | 36 | 117 | 0 | 180 | 99 | 99 | 153 | 45 | 0 | 36 | 36 | 45 | 108 | 126 | 0 | 36 | 99 | 54 | 45 | 90 | 0 | 36 | 9 | 36 | 126 | 36 | 0 | 81 | 180 | 306 | 198 | 162 | 0 | 666 | 81 | 171 | 234 | 252 | 6864 | 5148 | 13728 | 10296 | 13.728 | 10.296
14:05 | 23 | 14 | 5 | 4 | 17 | 4 | 13 | 15 | 4 | 13 | 3 | 3 | 11 | 16 | 5 | 4 | 6 | 6 | 11 | 19 | 5 | 12 | 6 | 3 | 11 | 3 | 1 | 4 | 12 | 3 | 8 | 20 | 60 | 21 | 27 | 21 | 7 | 32 | 34 | 24 | 14:05 | 276 | 168 | 60 | 48 | 204 | 48 | 156 | 180 | 48 | 156 | 36 | 36 | 132 | 192 | 60 | 48 | 72 | 72 | 132 | 228 | 60 | 144 | 72 | 36 | 132 | 36 | 12 | 48 | 144 | 36 | 96 | 240 | 720 | 252 | 324 | 252 | 84 | 384 | 408 | 288 |  | 14:05 | 207 | 126 | 45 | 36 | 153 | 0 | 36 | 117 | 135 | 36 | 117 | 0 | 27 | 27 | 99 | 144 | 45 | 0 | 36 | 54 | 54 | 99 | 171 | 0 | 45 | 108 | 54 | 27 | 99 | 0 | 27 | 9 | 36 | 108 | 27 | 0 | 72 | 180 | 540 | 189 | 243 | 0 | 189 | 63 | 288 | 306 | 216 | 6120 | 4590 | 12240 | 9180 | 12.24 | 9.18
14:10 | 22 | 20 | 4 | 4 | 17 | 4 | 13 | 14 | 0 | 3 | 6 | 0 | 11 | 13 | 5 | 5 | 15 | 4 | 12 | 18 | 5 | 12 | 4 | 4 | 10 | 3 | 1 | 3 | 4 | 9 | 8 | 18 | 29 | 22 | 105 | 20 | 9 | 42 | 30 | 20 | 14:10 | 264 | 240 | 48 | 48 | 204 | 48 | 156 | 168 | 0 | 36 | 72 | 0 | 132 | 156 | 60 | 60 | 180 | 48 | 144 | 216 | 60 | 144 | 48 | 48 | 120 | 36 | 12 | 36 | 48 | 108 | 96 | 216 | 348 | 264 | 1260 | 240 | 108 | 504 | 360 | 240 |  | 14:10 | 198 | 180 | 36 | 36 | 153 | 0 | 36 | 117 | 126 | 0 | 27 | 0 | 54 | 0 | 99 | 117 | 45 | 0 | 45 | 135 | 36 | 108 | 162 | 0 | 45 | 108 | 36 | 36 | 90 | 0 | 27 | 9 | 27 | 36 | 81 | 0 | 72 | 162 | 261 | 198 | 937.5 | 0 | 180 | 81 | 378 | 270 | 180 | 6576 | 4924.5 | 13152 | 9849 | 13.152 | 9.849
14:15 | 22 | 21 | 4 | 4 | 16 | 2 | 14 | 12 | 3 | 7 | 7 | 7 | 10 | 10 | 52 | 5 | 14 | 14 | 8 | 20 | 6 | 12 | 4 | 4 | 5 | 3 | 1 | 4 | 5 | 14 | 8 | 18 | 10 | 20 | 41 | 10 | 10 | 29 | 29 | 73 | 14:15 | 264 | 252 | 48 | 48 | 192 | 24 | 168 | 144 | 36 | 84 | 84 | 84 | 120 | 120 | 624 | 60 | 168 | 168 | 96 | 240 | 72 | 144 | 48 | 48 | 60 | 36 | 12 | 48 | 60 | 168 | 96 | 216 | 120 | 240 | 492 | 120 | 120 | 348 | 348 | 876 |  | 14:15 | 198 | 189 | 36 | 36 | 144 | 0 | 18 | 126 | 108 | 27 | 63 | 0 | 63 | 63 | 90 | 90 | 468 | 0 | 45 | 126 | 126 | 72 | 180 | 0 | 54 | 108 | 36 | 36 | 45 | 0 | 27 | 9 | 36 | 45 | 126 | 0 | 72 | 162 | 90 | 180 | 369 | 0 | 90 | 90 | 261 | 261 | 657 | 6696 | 5022 | 13392 | 10044 | 13.392 | 10.044
14:20 | 22 | 13 | 4 | 4 | 15 | 3 | 12 | 5 | 5 | 37 | 65 | 7 | 4 | 14 | 53 | 4 | 22 | 14 | 3 | 22 | 6 | 5 | 4 | 4 | 3 | 3 | 12 | 3 | 3 | 12 | 9 | 19 | 253 | 23 | 41 | 9 | 8 | 27 | 22 | 18 | 14:20 | 264 | 156 | 48 | 48 | 180 | 36 | 144 | 60 | 60 | 444 | 780 | 84 | 48 | 168 | 636 | 48 | 264 | 168 | 36 | 264 | 72 | 60 | 48 | 48 | 36 | 36 | 144 | 36 | 36 | 144 | 108 | 228 | 3036 | 276 | 492 | 108 | 96 | 324 | 264 | 216 |  | 14:20 | 198 | 117 | 36 | 36 | 135 | 0 | 27 | 108 | 45 | 45 | 333 | 0 | 585 | 63 | 36 | 126 | 477 | 0 | 36 | 198 | 126 | 27 | 198 | 0 | 54 | 45 | 36 | 36 | 27 | 0 | 27 | 108 | 27 | 27 | 108 | 0 | 81 | 171 | 937.5 | 207 | 369 | 0 | 81 | 72 | 243 | 198 | 162 | 9744 | 5968.5 | 19488 | 11937 | 19.488 | 11.937
14:25 | 21 | 12 | 0 | 6 | 16 | 0 | 15 | 3 | 4 | 22 | 39 | 7 | 6 | 17 | 46 | 5 | 15 | 13 | 2 | 22 | 6 | 5 | 5 | 5 | 4 | 4 | 11 | 4 | 2 | 12 | 9 | 19 | 377 | 21 | 40 | 9 | 8 | 27 | 18 | 52 | 14:25 | 252 | 144 | 0 | 72 | 192 | 0 | 180 | 36 | 48 | 264 | 468 | 84 | 72 | 204 | 552 | 60 | 180 | 156 | 24 | 264 | 72 | 60 | 60 | 60 | 48 | 48 | 132 | 48 | 24 | 144 | 108 | 228 | 4524 | 252 | 480 | 108 | 96 | 324 | 216 | 624 |  | 14:25 | 189 | 108 | 0 | 54 | 144 | 0 | 0 | 135 | 27 | 36 | 198 | 0 | 351 | 63 | 54 | 153 | 414 | 0 | 45 | 135 | 117 | 18 | 198 | 0 | 54 | 45 | 45 | 45 | 36 | 0 | 36 | 99 | 36 | 18 | 108 | 0 | 81 | 171 | 937.5 | 189 | 360 | 0 | 81 | 72 | 243 | 162 | 468 | 10908 | 5725.5 | 21816 | 11451 | 21.816 | 11.451
14:30 | 20 | 13 | 0 | 5 | 16 | 0 | 0 | 2 | 5 | 4 | 51 | 7 | 4 | 12 | 4 | 5 | 13 | 13 | 2 | 23 | 5 | 4 | 4 | 3 | 3 | 4 | 11 | 3 | 4 | 11 | 18 | 18 | 233 | 19 | 40 | 10 | 14 | 94 | 18 | 61 | 14:30 | 240 | 156 | 0 | 60 | 192 | 0 | 0 | 24 | 60 | 48 | 612 | 84 | 48 | 144 | 48 | 60 | 156 | 156 | 24 | 276 | 60 | 48 | 48 | 36 | 36 | 48 | 132 | 36 | 48 | 132 | 216 | 216 | 2796 | 228 | 480 | 120 | 168 | 1128 | 216 | 732 |  | 14:30 | 180 | 117 | 0 | 45 | 144 | 0 | 0 | 0 | 18 | 45 | 36 | 0 | 459 | 63 | 36 | 108 | 36 | 0 | 45 | 117 | 117 | 18 | 207 | 0 | 45 | 36 | 36 | 27 | 27 | 0 | 36 | 99 | 27 | 36 | 99 | 0 | 162 | 162 | 937.5 | 171 | 360 | 0 | 90 | 126 | 846 | 162 | 549 | 9312 | 5824.5 | 18624 | 11649 | 18.624 | 11.649
14:35 | 20 | 16 | 0 | 0 | 9 | 0 | 13 | 5 | 3 | 6 | 58 | 13 | 5 | 14 | 6 | 4 | 2 | 13 | 4 | 19 | 5 | 4 | 4 | 4 | 3 | 3 | 10 | 4 | 5 | 12 | 21 | 12 | 381 | 20 | 37 | 34 | 147 | 84 | 18 | 38 | 14:35 | 240 | 192 | 0 | 0 | 108 | 0 | 156 | 60 | 36 | 72 | 696 | 156 | 60 | 168 | 72 | 48 | 24 | 156 | 48 | 228 | 60 | 48 | 48 | 48 | 36 | 36 | 120 | 48 | 60 | 144 | 252 | 144 | 4572 | 240 | 444 | 408 | 1764 | 1008 | 216 | 456 |  | 14:35 | 180 | 144 | 0 | 0 | 81 | 0 | 0 | 117 | 45 | 27 | 54 | 0 | 522 | 117 | 45 | 126 | 54 | 0 | 36 | 18 | 117 | 36 | 171 | 0 | 45 | 36 | 36 | 36 | 27 | 0 | 27 | 90 | 36 | 45 | 108 | 0 | 189 | 108 | 937.5 | 180 | 333 | 0 | 306 | 937.5 | 756 | 162 | 342 | 12672 | 6627 | 25344 | 13254 | 25.344 | 13.254
14:40 | 13 | 15 | 0 | 0 | 10 | 0 | 6 | 8 | 7 | 26 | 76 | 57 | 4 | 7 | 4 | 4 | 0 | 12 | 4 | 17 | 3 | 4 | 4 | 4 | 3 | 3 | 10 | 4 | 3 | 11 | 20 | 9 | 389 | 20 | 28 | 20 | 20 | 53 | 134 | 22 | 14:40 | 156 | 180 | 0 | 0 | 120 | 0 | 72 | 96 | 84 | 312 | 912 | 684 | 48 | 84 | 48 | 48 | 0 | 144 | 48 | 204 | 36 | 48 | 48 | 48 | 36 | 36 | 120 | 48 | 36 | 132 | 240 | 108 | 4668 | 240 | 336 | 240 | 240 | 636 | 1608 | 264 |  | 14:40 | 117 | 135 | 0 | 0 | 90 | 0 | 0 | 54 | 72 | 63 | 234 | 0 | 684 | 513 | 36 | 63 | 36 | 0 | 36 | 0 | 108 | 36 | 153 | 0 | 27 | 36 | 36 | 36 | 27 | 0 | 27 | 90 | 36 | 27 | 99 | 0 | 180 | 81 | 937.5 | 180 | 252 | 0 | 180 | 180 | 477 | 937.5 | 198 | 12408 | 6474 | 24816 | 12948 | 24.816 | 12.948
14:45 | 14 | 11 | 0 | 0 | 9 | 0 | 3 | 7 | 3 | 49 | 70 | 55 | 4 | 6 | 16 | 5 | 0 | 14 | 4 | 14 | 3 | 4 | 4 | 3 | 3 | 3 | 9 | 3 | 4 | 12 | 20 | 8 | 278 | 20 | 29 | 37 | 19 | 17 | 58 | 142 | 14:45 | 168 | 132 | 0 | 0 | 108 | 0 | 36 | 84 | 36 | 588 | 840 | 660 | 48 | 72 | 192 | 60 | 0 | 168 | 48 | 168 | 36 | 48 | 48 | 36 | 36 | 36 | 108 | 36 | 48 | 144 | 240 | 96 | 3336 | 240 | 348 | 444 | 228 | 204 | 696 | 1704 |  | 14:45 | 126 | 99 | 0 | 0 | 81 | 0 | 0 | 27 | 63 | 27 | 441 | 0 | 630 | 495 | 36 | 54 | 144 | 0 | 45 | 0 | 126 | 36 | 126 | 0 | 27 | 36 | 36 | 27 | 27 | 0 | 27 | 81 | 27 | 36 | 108 | 0 | 180 | 72 | 937.5 | 180 | 261 | 0 | 333 | 171 | 153 | 522 | 937.5 | 11520 | 6735 | 23040 | 13470 | 23.04 | 13.47
14:50 | 13 | 12 | 0 | 0 | 9 | 0 | 2 | 5 | 5 | 35 | 67 | 59 | 4 | 5 | 12 | 5 | 0 | 13 | 4 | 22 | 3 | 4 | 4 | 4 | 2 | 2 | 9 | 12 | 1 | 13 | 18 | 10 | 193 | 20 | 29 | 30 | 18 | 16 | 73 | 240 | 14:50 | 156 | 144 | 0 | 0 | 108 | 0 | 24 | 60 | 60 | 420 | 804 | 708 | 48 | 60 | 144 | 60 | 0 | 156 | 48 | 264 | 36 | 48 | 48 | 48 | 24 | 24 | 108 | 144 | 12 | 156 | 216 | 120 | 2316 | 240 | 348 | 360 | 216 | 192 | 876 | 2880 |  | 14:50 | 117 | 108 | 0 | 0 | 81 | 0 | 0 | 18 | 45 | 45 | 315 | 0 | 603 | 531 | 36 | 45 | 108 | 0 | 45 | 0 | 117 | 36 | 198 | 0 | 27 | 36 | 36 | 36 | 18 | 0 | 18 | 81 | 108 | 9 | 117 | 0 | 162 | 90 | 937.5 | 180 | 261 | 0 | 270 | 162 | 144 | 657 | 937.5 | 11676 | 6735 | 23352 | 13470 | 23.352 | 13.47
14:55 | 13 | 12 | 0 | 0 | 9 | 0 | 6 | 4 | 0 | 65 | 40 | 27 | 4 | 2 | 5 | 3 | 5 | 11 | 4 | 20 | 3 | 3 | 5 | 4 | 2 | 2 | 5 | 13 | 4 | 12 | 18 | 8 | 311 | 20 | 28 | 30 | 18 | 16 | 51 | 234 | 14:55 | 156 | 144 | 0 | 0 | 108 | 0 | 72 | 48 | 0 | 780 | 480 | 324 | 48 | 24 | 60 | 36 | 60 | 132 | 48 | 240 | 36 | 36 | 60 | 48 | 24 | 24 | 60 | 156 | 48 | 144 | 216 | 96 | 3732 | 240 | 336 | 360 | 216 | 192 | 612 | 2808 |  | 14:55 | 117 | 108 | 0 | 0 | 81 | 0 | 0 | 54 | 36 | 0 | 585 | 0 | 360 | 243 | 36 | 18 | 45 | 0 | 27 | 45 | 99 | 36 | 180 | 0 | 27 | 27 | 45 | 36 | 18 | 0 | 18 | 45 | 117 | 36 | 108 | 0 | 162 | 72 | 937.5 | 180 | 252 | 0 | 270 | 162 | 144 | 459 | 937.5 | 12204 | 6123 | 24408 | 12246 | 24.408 | 12.246
15:00 | 13 | 13 | 0 | 0 | 9 | 0 | 4 | 2 | 5 | 76 | 63 | 36 | 4 | 2 | 10 | 5 | 1 | 13 | 5 | 23 | 2 | 2 | 5 | 4 | 2 | 2 | 2 | 13 | 4 | 7 | 10 | 7 | 262 | 13 | 27 | 30 | 8 | 16 | 38 | 235 | 15:00 | 156 | 156 | 0 | 0 | 108 | 0 | 48 | 24 | 60 | 912 | 756 | 432 | 48 | 24 | 120 | 60 | 12 | 156 | 60 | 276 | 24 | 24 | 60 | 48 | 24 | 24 | 24 | 156 | 48 | 84 | 120 | 84 | 3144 | 156 | 324 | 360 | 96 | 192 | 456 | 2820 |  | 15:00 | 117 | 117 | 0 | 0 | 81 | 0 | 0 | 36 | 18 | 45 | 684 | 0 | 567 | 324 | 36 | 18 | 90 | 0 | 45 | 9 | 117 | 45 | 207 | 0 | 18 | 18 | 45 | 36 | 18 | 0 | 18 | 18 | 117 | 36 | 63 | 0 | 90 | 63 | 937.5 | 117 | 243 | 0 | 270 | 72 | 144 | 342 | 937.5 | 11676 | 6159 | 23352 | 12318 | 23.352 | 12.318
15:05 | 0 | 11 | 0 | 0 | 9 | 0 | 4 | 3 | 2 | 60 | 29 | 12 | 4 | 0 | 4 | 5 | 7 | 7 | 3 | 30 | 3 | 4 | 4 | 4 | 2 | 2 | 0 | 11 | 3 | 4 | 9 | 8 | 160 | 56 | 33 | 27 | 9 | 21 | 21 | 155 | 15:05 | 0 | 132 | 0 | 0 | 108 | 0 | 48 | 36 | 24 | 720 | 348 | 144 | 48 | 0 | 48 | 60 | 84 | 84 | 36 | 360 | 36 | 48 | 48 | 48 | 24 | 24 | 0 | 132 | 36 | 48 | 108 | 96 | 1920 | 672 | 396 | 324 | 108 | 252 | 252 | 1860 |  | 15:05 | 0 | 99 | 0 | 0 | 81 | 0 | 0 | 36 | 27 | 18 | 540 | 0 | 261 | 108 | 36 | 0 | 36 | 0 | 45 | 63 | 63 | 27 | 270 | 0 | 27 | 36 | 36 | 36 | 18 | 0 | 18 | 0 | 99 | 27 | 36 | 0 | 81 | 72 | 937.5 | 504 | 297 | 0 | 243 | 81 | 189 | 189 | 937.5 | 8712 | 5574 | 17424 | 11148 | 17.424 | 11.148
15:10 | 0 | 5 | 0 | 0 | 9 | 0 | 3 | 6 | 5 | 41 | 7 | 14 | 4 | 8 | 32 | 4 | 4 | 5 | 4 | 30 | 4 | 3 | 4 | 3 | 11 | 1 | 0 | 12 | 3 | 4 | 8 | 16 | 175 | 19 | 44 | 16 | 8 | 41 | 20 | 29 | 15:10 | 0 | 60 | 0 | 0 | 108 | 0 | 36 | 72 | 60 | 492 | 84 | 168 | 48 | 96 | 384 | 48 | 48 | 60 | 48 | 360 | 48 | 36 | 48 | 36 | 132 | 12 | 0 | 144 | 36 | 48 | 96 | 192 | 2100 | 228 | 528 | 192 | 96 | 492 | 240 | 348 |  | 15:10 | 0 | 45 | 0 | 0 | 81 | 0 | 0 | 27 | 54 | 45 | 369 | 0 | 63 | 126 | 36 | 72 | 288 | 0 | 36 | 36 | 45 | 36 | 270 | 0 | 36 | 27 | 36 | 27 | 99 | 0 | 9 | 0 | 108 | 27 | 36 | 0 | 72 | 144 | 937.5 | 171 | 396 | 0 | 144 | 72 | 369 | 180 | 261 | 7224 | 4780.5 | 14448 | 9561 | 14.448 | 9.561
15:15 | 0 | 6 | 0 | 0 | 9 | 0 | 3 | 7 | 9 | 0 | 0 | 19 | 4 | 15 | 37 | 8 | 6 | 4 | 4 | 28 | 4 | 4 | 3 | 3 | 12 | 1 | 0 | 12 | 5 | 3 | 8 | 18 | 153 | 8 | 101 | 15 | 8 | 53 | 16 | 177 | 15:15 | 0 | 72 | 0 | 0 | 108 | 0 | 36 | 84 | 108 | 0 | 0 | 228 | 48 | 180 | 444 | 96 | 72 | 48 | 48 | 336 | 48 | 48 | 36 | 36 | 144 | 12 | 0 | 144 | 60 | 36 | 96 | 216 | 1836 | 96 | 1212 | 180 | 96 | 636 | 192 | 2124 |  | 15:15 | 0 | 54 | 0 | 0 | 81 | 0 | 0 | 27 | 63 | 81 | 0 | 0 | 0 | 171 | 36 | 135 | 333 | 0 | 72 | 54 | 36 | 36 | 252 | 0 | 36 | 36 | 27 | 27 | 108 | 0 | 9 | 0 | 108 | 45 | 27 | 0 | 72 | 162 | 937.5 | 72 | 909 | 0 | 135 | 72 | 477 | 144 | 937.5 | 9156 | 5772 | 18312 | 11544 | 18.312 | 11.544
15:20 | 0 | 8 | 0 | 0 | 9 | 0 | 8 | 6 | 15 | 2 | 0 | 16 | 4 | 0 | 34 | 14 | 6 | 3 | 3 | 29 | 11 | 3 | 2 | 3 | 11 | 1 | 0 | 11 | 3 | 4 | 8 | 17 | 96 | 9 | 78 | 15 | 8 | 41 | 9 | 259 | 15:20 | 0 | 96 | 0 | 0 | 108 | 0 | 96 | 72 | 180 | 24 | 0 | 192 | 48 | 0 | 408 | 168 | 72 | 36 | 36 | 348 | 132 | 36 | 24 | 36 | 132 | 12 | 0 | 132 | 36 | 48 | 96 | 204 | 1152 | 108 | 936 | 180 | 96 | 492 | 108 | 3108 |  | 15:20 | 0 | 72 | 0 | 0 | 81 | 0 | 0 | 72 | 54 | 135 | 18 | 0 | 0 | 144 | 36 | 0 | 306 | 0 | 126 | 54 | 27 | 27 | 261 | 0 | 99 | 27 | 18 | 27 | 99 | 0 | 9 | 0 | 99 | 27 | 36 | 0 | 72 | 153 | 864 | 81 | 702 | 0 | 135 | 72 | 369 | 81 | 937.5 | 8952 | 5320.5 | 17904 | 10641 | 17.904 | 10.641
15:25 | 0 | 7 | 0 | 0 | 9 | 4 | 5 | 4 | 13 | 3 | 1 | 16 | 3 | 0 | 13 | 13 | 5 | 4 | 4 | 28 | 12 | 3 | 3 | 3 | 11 | 0 | 0 | 11 | 4 | 4 | 7 | 17 | 31 | 7 | 51 | 15 | 8 | 43 | 9 | 270 | 15:25 | 0 | 84 | 0 | 0 | 108 | 48 | 60 | 48 | 156 | 36 | 12 | 192 | 36 | 0 | 156 | 156 | 60 | 48 | 48 | 336 | 144 | 36 | 36 | 36 | 132 | 0 | 0 | 132 | 48 | 48 | 84 | 204 | 372 | 84 | 612 | 180 | 96 | 516 | 108 | 3240 |  | 15:25 | 0 | 63 | 0 | 0 | 81 | 0 | 36 | 45 | 36 | 117 | 27 | 0 | 9 | 144 | 27 | 0 | 117 | 0 | 117 | 45 | 36 | 36 | 252 | 0 | 108 | 27 | 27 | 27 | 99 | 0 | 0 | 0 | 99 | 36 | 36 | 0 | 63 | 153 | 279 | 63 | 459 | 0 | 135 | 72 | 387 | 81 | 937.5 | 7692 | 4276.5 | 15384 | 8553 | 15.384 | 8.553
15:30 | 12 | 7 | 7 | 0 | 9 | 7 | 4 | 4 | 13 | 1 | 3 | 32 | 3 | 0 | 14 | 13 | 4 | 3 | 4 | 28 | 13 | 3 | 3 | 6 | 11 | 1 | 0 | 9 | 3 | 3 | 8 | 17 | 34 | 22 | 84 | 13 | 15 | 37 | 8 | 195 | 15:30 | 144 | 84 | 84 | 0 | 108 | 84 | 48 | 48 | 156 | 12 | 36 | 384 | 36 | 0 | 168 | 156 | 48 | 36 | 48 | 336 | 156 | 36 | 36 | 72 | 132 | 12 | 0 | 108 | 36 | 36 | 96 | 204 | 408 | 264 | 1008 | 156 | 180 | 444 | 96 | 2340 |  | 15:30 | 108 | 63 | 63 | 0 | 81 | 0 | 63 | 36 | 36 | 117 | 9 | 0 | 27 | 288 | 27 | 0 | 126 | 0 | 117 | 36 | 27 | 36 | 252 | 0 | 117 | 27 | 27 | 54 | 99 | 0 | 9 | 0 | 81 | 27 | 27 | 0 | 72 | 153 | 306 | 198 | 756 | 0 | 117 | 135 | 333 | 72 | 937.5 | 7836 | 5059.5 | 15672 | 10119 | 15.672 | 10.119
15:35 | 16 | 6 | 7 | 0 | 8 | 14 | 0 | 5 | 13 | 10 | 12 | 3 | 8 | 9 | 13 | 13 | 4 | 4 | 4 | 29 | 11 | 3 | 4 | 13 | 20 | 0 | 0 | 8 | 4 | 3 | 8 | 17 | 36 | 40 | 61 | 14 | 26 | 27 | 9 | 69 | 15:35 | 192 | 72 | 84 | 0 | 96 | 168 | 0 | 60 | 156 | 120 | 144 | 36 | 96 | 108 | 156 | 156 | 48 | 48 | 48 | 348 | 132 | 36 | 48 | 156 | 240 | 0 | 0 | 96 | 48 | 36 | 96 | 204 | 432 | 480 | 732 | 168 | 312 | 324 | 108 | 828 |  | 15:35 | 144 | 54 | 63 | 0 | 72 | 0 | 126 | 0 | 45 | 117 | 90 | 0 | 108 | 27 | 72 | 81 | 117 | 0 | 117 | 36 | 36 | 36 | 261 | 0 | 99 | 27 | 36 | 117 | 180 | 0 | 0 | 0 | 72 | 36 | 27 | 0 | 72 | 153 | 324 | 360 | 549 | 0 | 126 | 234 | 243 | 81 | 621 | 6612 | 4959 | 13224 | 9918 | 13.224 | 9.918
15:40 | 22 | 6 | 7 | 0 | 9 | 13 | 3 | 8 | 12 | 55 | 40 | 2 | 12 | 13 | 22 | 12 | 4 | 5 | 3 | 27 | 10 | 3 | 12 | 11 | 108 | 5 | 0 | 4 | 3 | 3 | 18 | 17 | 25 | 79 | 34 | 38 | 27 | 26 | 33 | 147 | 15:40 | 264 | 72 | 84 | 0 | 108 | 156 | 36 | 96 | 144 | 660 | 480 | 24 | 144 | 156 | 264 | 144 | 48 | 60 | 36 | 324 | 120 | 36 | 144 | 132 | 1296 | 60 | 0 | 48 | 36 | 36 | 216 | 204 | 300 | 948 | 408 | 456 | 324 | 312 | 396 | 1764 |  | 15:40 | 198 | 54 | 63 | 0 | 81 | 0 | 117 | 27 | 72 | 108 | 495 | 0 | 360 | 18 | 108 | 117 | 198 | 0 | 108 | 36 | 45 | 27 | 243 | 0 | 90 | 27 | 108 | 99 | 937.5 | 0 | 45 | 0 | 36 | 27 | 27 | 0 | 162 | 153 | 225 | 711 | 306 | 0 | 342 | 243 | 234 | 297 | 937.5 | 10536 | 7482 | 21072 | 14964 | 21.072 | 14.964
15:45 | 22 | 6 | 6 | 1 | 13 | 11 | 4 | 6 | 13 | 11 | 38 | 15 | 11 | 10 | 11 | 13 | 4 | 4 | 4 | 27 | 10 | 2 | 12 | 11 | 104 | 10 | 0 | 3 | 3 | 2 | 19 | 16 | 29 | 42 | 34 | 41 | 26 | 27 | 85 | 138 | 15:45 | 264 | 72 | 72 | 12 | 156 | 132 | 48 | 72 | 156 | 132 | 456 | 180 | 132 | 120 | 132 | 156 | 48 | 48 | 48 | 324 | 120 | 24 | 144 | 132 | 1248 | 120 | 0 | 36 | 36 | 24 | 228 | 192 | 348 | 504 | 408 | 492 | 312 | 324 | 1020 | 1656 |  | 15:45 | 198 | 54 | 54 | 9 | 117 | 0 | 99 | 36 | 54 | 117 | 99 | 0 | 342 | 135 | 99 | 90 | 99 | 0 | 117 | 36 | 36 | 36 | 243 | 0 | 90 | 18 | 108 | 99 | 936 | 0 | 90 | 0 | 27 | 27 | 18 | 0 | 171 | 144 | 261 | 378 | 306 | 0 | 369 | 234 | 243 | 765 | 937.5 | 10128 | 7291.5 | 20256 | 14583 | 20.256 | 14.583
15:50 | 21 | 1 | 7 | 9 | 17 | 10 | 4 | 7 | 13 | 14 | 9 | 45 | 11 | 3 | 11 | 12 | 5 | 5 | 12 | 26 | 3 | 8 | 11 | 11 | 66 | 10 | 0 | 2 | 13 | 3 | 19 | 16 | 26 | 69 | 34 | 33 | 26 | 25 | 52 | 137 | 15:50 | 252 | 12 | 84 | 108 | 204 | 120 | 48 | 84 | 156 | 168 | 108 | 540 | 132 | 36 | 132 | 144 | 60 | 60 | 144 | 312 | 36 | 96 | 132 | 132 | 792 | 120 | 0 | 24 | 156 | 36 | 228 | 192 | 312 | 828 | 408 | 396 | 312 | 300 | 624 | 1644 |  | 15:50 | 189 | 9 | 63 | 81 | 153 | 0 | 90 | 36 | 63 | 117 | 126 | 0 | 81 | 405 | 99 | 27 | 99 | 0 | 108 | 45 | 45 | 108 | 234 | 0 | 27 | 72 | 99 | 99 | 594 | 0 | 90 | 0 | 18 | 117 | 27 | 0 | 171 | 144 | 234 | 621 | 306 | 0 | 297 | 234 | 225 | 468 | 937.5 | 9672 | 6958.5 | 19344 | 13917 | 19.344 | 13.917
15:55 | 23 | 0 | 7 | 9 | 16 | 11 | 16 | 12 | 11 | 13 | 8 | 27 | 11 | 0 | 43 | 13 | 9 | 4 | 12 | 15 | 2 | 11 | 10 | 10 | 40 | 10 | 0 | 2 | 11 | 2 | 18 | 17 | 133 | 67 | 34 | 30 | 30 | 26 | 78 | 140 | 15:55 | 276 | 0 | 84 | 108 | 192 | 132 | 192 | 144 | 132 | 156 | 96 | 324 | 132 | 0 | 516 | 156 | 108 | 48 | 144 | 180 | 24 | 132 | 120 | 120 | 480 | 120 | 0 | 24 | 132 | 24 | 216 | 204 | 1596 | 804 | 408 | 360 | 360 | 312 | 936 | 1680 |  | 15:55 | 207 | 0 | 63 | 81 | 144 | 0 | 99 | 144 | 108 | 99 | 117 | 0 | 72 | 243 | 99 | 0 | 387 | 0 | 117 | 81 | 36 | 108 | 135 | 0 | 18 | 99 | 90 | 90 | 360 | 0 | 90 | 0 | 18 | 99 | 18 | 0 | 162 | 153 | 937.5 | 603 | 306 | 0 | 270 | 270 | 234 | 702 | 937.5 | 11172 | 7797 | 22344 | 15594 | 22.344 | 15.594
16:00 | 21 | 60 | 6 | 9 | 16 | 10 | 15 | 11 | 13 | 13 | 7 | 53 | 11 | 1 | 45 | 11 | 15 | 5 | 12 | 141 | 3 | 11 | 10 | 10 | 31 | 9 | 0 | 3 | 11 | 2 | 18 | 15 | 13 | 68 | 46 | 29 | 83 | 30 | 33 | 146 | 16:00 | 252 | 720 | 72 | 108 | 192 | 120 | 180 | 132 | 156 | 156 | 84 | 636 | 132 | 12 | 540 | 132 | 180 | 60 | 144 | 1692 | 36 | 132 | 120 | 120 | 372 | 108 | 0 | 36 | 132 | 24 | 216 | 180 | 156 | 816 | 552 | 348 | 996 | 360 | 396 | 1752 |  | 16:00 | 189 | 540 | 54 | 81 | 144 | 0 | 90 | 135 | 99 | 117 | 117 | 0 | 63 | 477 | 99 | 9 | 405 | 0 | 99 | 135 | 45 | 108 | 937.5 | 0 | 27 | 99 | 90 | 90 | 279 | 0 | 81 | 0 | 27 | 99 | 18 | 0 | 162 | 135 | 117 | 612 | 414 | 0 | 261 | 747 | 270 | 297 | 937.5 | 12552 | 8706 | 25104 | 17412 | 25.104 | 17.412
16:05 | 21 | 3 | 7 | 9 | 16 | 11 | 14 | 13 | 8 | 11 | 9 | 41 | 11 | 10 | 47 | 6 | 12 | 4 | 11 | 16 | 2 | 10 | 10 | 9 | 31 | 8 | 0 | 2 | 10 | 3 | 14 | 15 | 8 | 57 | 32 | 18 | 24 | 38 | 32 | 152 | 16:05 | 252 | 36 | 84 | 108 | 192 | 132 | 168 | 156 | 96 | 132 | 108 | 492 | 132 | 120 | 564 | 72 | 144 | 48 | 132 | 192 | 24 | 120 | 120 | 108 | 372 | 96 | 0 | 24 | 120 | 36 | 168 | 180 | 96 | 684 | 384 | 216 | 288 | 456 | 384 | 1824 |  | 16:05 | 189 | 27 | 63 | 81 | 144 | 0 | 99 | 126 | 117 | 72 | 99 | 0 | 81 | 369 | 99 | 90 | 423 | 0 | 54 | 108 | 36 | 99 | 144 | 0 | 18 | 90 | 90 | 81 | 279 | 0 | 72 | 0 | 18 | 90 | 27 | 0 | 126 | 135 | 72 | 513 | 288 | 0 | 162 | 216 | 342 | 288 | 937.5 | 9060 | 6364.5 | 18120 | 12729 | 18.12 | 12.729
16:10 | 20 | 9 | 7 | 8 | 16 | 9 | 11 | 0 | 4 | 11 | 7 | 3 | 10 | 9 | 50 | 4 | 11 | 4 | 9 | 4 | 3 | 10 | 9 | 9 | 30 | 9 | 0 | 3 | 10 | 2 | 7 | 16 | 7 | 98 | 26 | 19 | 20 | 37 | 27 | 160 | 16:10 | 240 | 108 | 84 | 96 | 192 | 108 | 132 | 0 | 48 | 132 | 84 | 36 | 120 | 108 | 600 | 48 | 132 | 48 | 108 | 48 | 36 | 120 | 108 | 108 | 360 | 108 | 0 | 36 | 120 | 24 | 84 | 192 | 84 | 1176 | 312 | 228 | 240 | 444 | 324 | 1920 |  | 16:10 | 180 | 81 | 63 | 72 | 144 | 0 | 81 | 99 | 0 | 36 | 99 | 0 | 63 | 27 | 90 | 81 | 450 | 0 | 36 | 99 | 36 | 81 | 36 | 0 | 27 | 90 | 81 | 81 | 270 | 0 | 81 | 0 | 27 | 90 | 18 | 0 | 63 | 144 | 63 | 882 | 234 | 0 | 171 | 180 | 333 | 243 | 937.5 | 8496 | 5869.5 | 16992 | 11739 | 16.992 | 11.739
16:15 | 20 | 9 | 7 | 8 | 16 | 10 | 11 | 10 | 4 | 13 | 12 | 4 | 10 | 9 | 64 | 4 | 12 | 4 | 11 | 0 | 3 | 10 | 10 | 3 | 31 | 7 | 0 | 2 | 10 | 2 | 8 | 8 | 18 | 35 | 26 | 19 | 21 | 37 | 22 | 162 | 16:15 | 240 | 108 | 84 | 96 | 192 | 120 | 132 | 120 | 48 | 156 | 144 | 48 | 120 | 108 | 768 | 48 | 144 | 48 | 132 | 0 | 36 | 120 | 120 | 36 | 372 | 84 | 0 | 24 | 120 | 24 | 96 | 96 | 216 | 420 | 312 | 228 | 252 | 444 | 264 | 1944 |  | 16:15 | 180 | 81 | 63 | 72 | 144 | 0 | 90 | 99 | 90 | 36 | 117 | 0 | 108 | 36 | 90 | 81 | 576 | 0 | 36 | 108 | 36 | 99 | 0 | 0 | 27 | 90 | 90 | 27 | 279 | 0 | 63 | 0 | 18 | 90 | 18 | 0 | 72 | 72 | 162 | 315 | 234 | 0 | 171 | 189 | 333 | 198 | 937.5 | 8064 | 5527.5 | 16128 | 11055 | 16.128 | 11.055
16:20 | 18 | 8 | 7 | 8 | 16 | 11 | 17 | 8 | 5 | 12 | 12 | 0 | 10 | 9 | 45 | 3 | 12 | 3 | 10 | 7 | 2 | 10 | 9 | 2 | 30 | 1 | 0 | 2 | 10 | 3 | 7 | 7 | 19 | 102 | 26 | 18 | 21 | 36 | 22 | 218 | 16:20 | 216 | 96 | 84 | 96 | 192 | 132 | 204 | 96 | 60 | 144 | 144 | 0 | 120 | 108 | 540 | 36 | 144 | 36 | 120 | 84 | 24 | 120 | 108 | 24 | 360 | 12 | 0 | 24 | 120 | 36 | 84 | 84 | 228 | 1224 | 312 | 216 | 252 | 432 | 264 | 2616 |  | 16:20 | 162 | 72 | 63 | 72 | 144 | 0 | 99 | 153 | 72 | 45 | 108 | 0 | 108 | 0 | 90 | 81 | 405 | 0 | 27 | 108 | 27 | 90 | 63 | 0 | 18 | 90 | 81 | 18 | 270 | 0 | 9 | 0 | 18 | 90 | 27 | 0 | 63 | 63 | 171 | 918 | 234 | 0 | 162 | 189 | 324 | 198 | 937.5 | 9192 | 5869.5 | 18384 | 11739 | 18.384 | 11.739
16:25 | 7 | 8 | 8 | 8 | 16 | 13 | 7 | 7 | 4 | 12 | 14 | 1 | 6 | 9 | 39 | 4 | 10 | 4 | 10 | 5 | 3 | 10 | 3 | 3 | 28 | 0 | 0 | 3 | 9 | 2 | 7 | 6 | 24 | 249 | 20 | 21 | 20 | 36 | 22 | 87 | 16:25 | 84 | 96 | 96 | 96 | 192 | 156 | 84 | 84 | 48 | 144 | 168 | 12 | 72 | 108 | 468 | 48 | 120 | 48 | 120 | 60 | 36 | 120 | 36 | 36 | 336 | 0 | 0 | 36 | 108 | 24 | 84 | 72 | 288 | 2988 | 240 | 252 | 240 | 432 | 264 | 1044 |  | 16:25 | 63 | 72 | 72 | 72 | 144 | 0 | 117 | 63 | 63 | 36 | 108 | 0 | 126 | 9 | 54 | 81 | 351 | 0 | 36 | 90 | 36 | 90 | 45 | 0 | 27 | 90 | 27 | 27 | 252 | 0 | 0 | 0 | 27 | 81 | 18 | 0 | 63 | 54 | 216 | 937.5 | 180 | 0 | 189 | 180 | 324 | 198 | 783 | 8940 | 5401.5 | 17880 | 10803 | 17.88 | 10.803
16:30 | 5 | 8 | 6 | 8 | 15 | 4 | 15 | 7 | 4 | 13 | 7 | 8 | 4 | 12 | 55 | 4 | 10 | 4 | 10 | 5 | 2 | 10 | 2 | 2 | 25 | 0 | 0 | 2 | 2 | 2 | 7 | 6 | 45 | 243 | 16 | 14 | 16 | 28 | 22 | 74 | 16:30 | 60 | 96 | 72 | 96 | 180 | 48 | 180 | 84 | 48 | 156 | 84 | 96 | 48 | 144 | 660 | 48 | 120 | 48 | 120 | 60 | 24 | 120 | 24 | 24 | 300 | 0 | 0 | 24 | 24 | 24 | 84 | 72 | 540 | 2916 | 192 | 168 | 192 | 336 | 264 | 888 |  | 16:30 | 45 | 72 | 54 | 72 | 135 | 0 | 36 | 135 | 63 | 36 | 117 | 0 | 63 | 72 | 36 | 108 | 495 | 0 | 36 | 90 | 36 | 90 | 45 | 0 | 18 | 90 | 18 | 18 | 225 | 0 | 0 | 0 | 18 | 18 | 18 | 0 | 63 | 54 | 405 | 937.5 | 144 | 0 | 126 | 144 | 252 | 198 | 666 | 8664 | 5248.5 | 17328 | 10497 | 17.328 | 10.497
16:35 | 4 | 8 | 4 | 8 | 16 | 3 | 10 | 7 | 4 | 13 | 0 | 10 | 3 | 13 | 51 | 3 | 9 | 14 | 4 | 4 | 3 | 9 | 2 | 3 | 27 | 0 | 0 | 3 | 3 | 3 | 7 | 6 | 27 | 254 | 15 | 29 | 23 | 25 | 22 | 42 | 16:35 | 48 | 96 | 48 | 96 | 192 | 36 | 120 | 84 | 48 | 156 | 0 | 120 | 36 | 156 | 612 | 36 | 108 | 168 | 48 | 48 | 36 | 108 | 24 | 36 | 324 | 0 | 0 | 36 | 36 | 36 | 84 | 72 | 324 | 3048 | 180 | 348 | 276 | 300 | 264 | 504 |  | 16:35 | 36 | 72 | 36 | 72 | 144 | 0 | 27 | 90 | 63 | 36 | 117 | 0 | 0 | 90 | 27 | 117 | 459 | 0 | 27 | 81 | 126 | 36 | 36 | 0 | 27 | 81 | 18 | 27 | 243 | 0 | 0 | 0 | 27 | 27 | 27 | 0 | 63 | 54 | 243 | 937.5 | 135 | 0 | 261 | 207 | 225 | 198 | 378 | 8292 | 4870.5 | 16584 | 9741 | 16.584 | 9.741
16:40 | 4 | 9 | 0 | 8 | 16 | 3 | 10 | 3 | 4 | 12 | 1 | 14 | 4 | 9 | 19 | 3 | 10 | 13 | 2 | 5 | 3 | 2 | 3 | 2 | 34 | 0 | 0 | 2 | 2 | 2 | 7 | 6 | 26 | 263 | 15 | 36 | 26 | 24 | 29 | 34 | 16:40 | 48 | 108 | 0 | 96 | 192 | 36 | 120 | 36 | 48 | 144 | 12 | 168 | 48 | 108 | 228 | 36 | 120 | 156 | 24 | 60 | 36 | 24 | 36 | 24 | 408 | 0 | 0 | 24 | 24 | 24 | 84 | 72 | 312 | 3156 | 180 | 432 | 312 | 288 | 348 | 408 |  | 16:40 | 36 | 81 | 0 | 72 | 144 | 0 | 27 | 90 | 27 | 36 | 108 | 0 | 9 | 126 | 36 | 81 | 171 | 0 | 27 | 90 | 117 | 18 | 45 | 0 | 27 | 18 | 27 | 18 | 306 | 0 | 0 | 0 | 18 | 18 | 18 | 0 | 63 | 54 | 234 | 937.5 | 135 | 0 | 324 | 234 | 216 | 261 | 306 | 7980 | 4555.5 | 15960 | 9111 | 15.96 | 9.111
16:45 | 5 | 8 | 1 | 9 | 16 | 4 | 8 | 2 | 4 | 6 | 0 | 11 | 3 | 12 | 48 | 4 | 22 | 12 | 3 | 5 | 2 | 2 | 2 | 2 | 33 | 0 | 0 | 2 | 3 | 11 | 11 | 6 | 25 | 245 | 15 | 36 | 30 | 26 | 34 | 34 | 16:45 | 60 | 96 | 12 | 108 | 192 | 48 | 96 | 24 | 48 | 72 | 0 | 132 | 36 | 144 | 576 | 48 | 264 | 144 | 36 | 60 | 24 | 24 | 24 | 24 | 396 | 0 | 0 | 24 | 36 | 132 | 132 | 72 | 300 | 2940 | 180 | 432 | 360 | 312 | 408 | 408 |  | 16:45 | 45 | 72 | 9 | 81 | 144 | 0 | 36 | 72 | 18 | 36 | 54 | 0 | 0 | 99 | 27 | 108 | 432 | 0 | 36 | 198 | 108 | 27 | 45 | 0 | 18 | 18 | 18 | 18 | 297 | 0 | 0 | 0 | 18 | 27 | 99 | 0 | 99 | 54 | 225 | 937.5 | 135 | 0 | 324 | 270 | 234 | 306 | 306 | 8424 | 5050.5 | 16848 | 10101 | 16.848 | 10.101
16:50 | 4 | 8 | 0 | 8 | 15 | 2 | 4 | 0 | 2 | 5 | 5 | 11 | 3 | 11 | 45 | 4 | 41 | 11 | 3 | 5 | 3 | 3 | 2 | 2 | 32 | 0 | 28 | 3 | 2 | 11 | 19 | 14 | 25 | 244 | 15 | 35 | 88 | 33 | 33 | 32 | 16:50 | 48 | 96 | 0 | 96 | 180 | 24 | 48 | 0 | 24 | 60 | 60 | 132 | 36 | 132 | 540 | 48 | 492 | 132 | 36 | 60 | 36 | 36 | 24 | 24 | 384 | 0 | 336 | 36 | 24 | 132 | 228 | 168 | 300 | 2928 | 180 | 420 | 1056 | 396 | 396 | 384 |  | 16:50 | 36 | 72 | 0 | 72 | 135 | 0 | 18 | 36 | 0 | 18 | 45 | 0 | 45 | 99 | 27 | 99 | 405 | 0 | 36 | 369 | 99 | 27 | 45 | 0 | 27 | 27 | 18 | 18 | 288 | 0 | 0 | 252 | 27 | 18 | 99 | 0 | 171 | 126 | 225 | 937.5 | 135 | 0 | 315 | 792 | 297 | 297 | 288 | 9732 | 6040.5 | 19464 | 12081 | 19.464 | 12.081
16:55 | 5 | 8 | 1 | 8 | 7 | 0 | 0 | 0 | 1 | 4 | 2 | 27 | 3 | 12 | 1 | 7 | 18 | 12 | 3 | 4 | 2 | 2 | 3 | 26 | 26 | 0 | 32 | 2 | 2 | 11 | 18 | 17 | 15 | 239 | 24 | 35 | 34 | 33 | 32 | 37 | 16:55 | 60 | 96 | 12 | 96 | 84 | 0 | 0 | 0 | 12 | 48 | 24 | 324 | 36 | 144 | 12 | 84 | 216 | 144 | 36 | 48 | 24 | 24 | 36 | 312 | 312 | 0 | 384 | 24 | 24 | 132 | 216 | 204 | 180 | 2868 | 288 | 420 | 408 | 396 | 384 | 444 |  | 16:55 | 45 | 72 | 9 | 72 | 63 | 0 | 0 | 0 | 0 | 9 | 36 | 0 | 18 | 243 | 27 | 108 | 9 | 0 | 63 | 162 | 108 | 27 | 36 | 0 | 18 | 18 | 27 | 234 | 234 | 0 | 0 | 288 | 18 | 18 | 99 | 0 | 162 | 153 | 135 | 937.5 | 216 | 0 | 315 | 306 | 297 | 288 | 333 | 8556 | 5203.5 | 17112 | 10407 | 17.112 | 10.407
17:00 | 4 | 2 | 1 | 7 | 8 | 2 | 1 | 1 | 1 | 4 | 0 | 31 | 3 | 5 | 0 | 4 | 31 | 11 | 3 | 5 | 3 | 2 | 2 | 43 | 27 | 0 | 19 | 2 | 3 | 10 | 18 | 16 | 15 | 80 | 26 | 33 | 22 | 42 | 31 | 41 | 17:00 | 48 | 24 | 12 | 84 | 96 | 24 | 12 | 12 | 12 | 48 | 0 | 372 | 36 | 60 | 0 | 48 | 372 | 132 | 36 | 60 | 36 | 24 | 24 | 516 | 324 | 0 | 228 | 24 | 36 | 120 | 216 | 192 | 180 | 960 | 312 | 396 | 264 | 504 | 372 | 492 |  | 17:00 | 36 | 18 | 9 | 63 | 72 | 0 | 18 | 9 | 9 | 9 | 36 | 0 | 0 | 279 | 27 | 45 | 0 | 0 | 36 | 279 | 99 | 27 | 45 | 0 | 27 | 18 | 18 | 387 | 243 | 0 | 0 | 171 | 18 | 27 | 90 | 0 | 162 | 144 | 135 | 720 | 234 | 0 | 297 | 198 | 378 | 279 | 369 | 6708 | 5031 | 13416 | 10062 | 13.416 | 10.062
17:05 | 5 | 1 | 0 | 1 | 8 | 4 | 1 | 1 | 1 | 4 | 0 | 41 | 4 | 4 | 1 | 4 | 10 | 11 | 2 | 4 | 2 | 3 | 2 | 41 | 18 | 0 | 18 | 3 | 2 | 10 | 17 | 16 | 15 | 46 | 63 | 24 | 16 | 77 | 26 | 46 | 17:05 | 60 | 12 | 0 | 12 | 96 | 48 | 12 | 12 | 12 | 48 | 0 | 492 | 48 | 48 | 12 | 48 | 120 | 132 | 24 | 48 | 24 | 36 | 24 | 492 | 216 | 0 | 216 | 36 | 24 | 120 | 204 | 192 | 180 | 552 | 756 | 288 | 192 | 924 | 312 | 552 |  | 17:05 | 45 | 9 | 0 | 9 | 72 | 0 | 36 | 9 | 9 | 9 | 36 | 0 | 0 | 369 | 36 | 36 | 9 | 0 | 36 | 90 | 99 | 18 | 36 | 0 | 18 | 27 | 18 | 369 | 162 | 0 | 0 | 162 | 27 | 18 | 90 | 0 | 153 | 144 | 135 | 414 | 567 | 0 | 216 | 144 | 693 | 234 | 414 | 6624 | 4968 | 13248 | 9936 | 13.248 | 9.936
17:10 | 3 | 2 | 1 | 2 | 7 | 1 | 1 | 1 | 3 | 4 | 1 | 31 | 4 | 3 | 2 | 4 | 3 | 10 | 3 | 13 | 3 | 2 | 3 | 42 | 18 | 0 | 18 | 2 | 3 | 9 | 18 | 16 | 15 | 34 | 28 | 24 | 139 | 108 | 18 | 39 | 17:10 | 36 | 24 | 12 | 24 | 84 | 12 | 12 | 12 | 36 | 48 | 12 | 372 | 48 | 36 | 24 | 48 | 36 | 120 | 36 | 156 | 36 | 24 | 36 | 504 | 216 | 0 | 216 | 24 | 36 | 108 | 216 | 192 | 180 | 408 | 336 | 288 | 1668 | 1296 | 216 | 468 |  | 17:10 | 27 | 18 | 9 | 18 | 63 | 0 | 9 | 9 | 9 | 27 | 36 | 0 | 9 | 279 | 36 | 27 | 18 | 0 | 36 | 27 | 90 | 27 | 117 | 0 | 27 | 18 | 27 | 378 | 162 | 0 | 0 | 162 | 18 | 27 | 81 | 0 | 162 | 144 | 135 | 306 | 252 | 0 | 216 | 937.5 | 937.5 | 162 | 351 | 7656 | 5394 | 15312 | 10788 | 15.312 | 10.788
17:15 | 4 | 2 | 1 | 1 | 8 | 1 | 0 | 1 | 11 | 4 | 0 | 48 | 4 | 4 | 1 | 5 | 3 | 10 | 4 | 13 | 7 | 2 | 2 | 42 | 18 | 0 | 17 | 11 | 2 | 10 | 10 | 16 | 15 | 30 | 61 | 24 | 231 | 58 | 14 | 28 | 17:15 | 48 | 24 | 12 | 12 | 96 | 12 | 0 | 12 | 132 | 48 | 0 | 576 | 48 | 48 | 12 | 60 | 36 | 120 | 48 | 156 | 84 | 24 | 24 | 504 | 216 | 0 | 204 | 132 | 24 | 120 | 120 | 192 | 180 | 360 | 732 | 288 | 2772 | 696 | 168 | 336 |  | 17:15 | 36 | 18 | 9 | 9 | 72 | 0 | 9 | 0 | 9 | 99 | 36 | 0 | 0 | 432 | 36 | 36 | 9 | 0 | 45 | 27 | 90 | 36 | 117 | 0 | 63 | 18 | 18 | 378 | 162 | 0 | 0 | 153 | 99 | 18 | 90 | 0 | 90 | 144 | 135 | 270 | 549 | 0 | 216 | 937.5 | 522 | 126 | 252 | 8676 | 5365.5 | 17352 | 10731 | 17.352 | 10.731
17:20 | 4 | 1 | 0 | 1 | 9 | 0 | 6 | 1 | 12 | 3 | 10 | 45 | 3 | 4 | 1 | 3 | 1 | 4 | 2 | 12 | 12 | 3 | 3 | 43 | 18 | 0 | 18 | 18 | 2 | 10 | 7 | 16 | 15 | 125 | 37 | 25 | 230 | 45 | 10 | 26 | 17:20 | 48 | 12 | 0 | 12 | 108 | 0 | 72 | 12 | 144 | 36 | 120 | 540 | 36 | 48 | 12 | 36 | 12 | 48 | 24 | 144 | 144 | 36 | 36 | 516 | 216 | 0 | 216 | 216 | 24 | 120 | 84 | 192 | 180 | 1500 | 444 | 300 | 2760 | 540 | 120 | 312 |  | 17:20 | 36 | 9 | 0 | 9 | 81 | 0 | 0 | 54 | 9 | 108 | 27 | 0 | 90 | 405 | 27 | 36 | 9 | 0 | 27 | 9 | 36 | 18 | 108 | 0 | 108 | 27 | 27 | 387 | 162 | 0 | 0 | 162 | 162 | 18 | 90 | 0 | 63 | 144 | 135 | 937.5 | 333 | 0 | 225 | 937.5 | 405 | 90 | 234 | 9420 | 5745 | 18840 | 11490 | 18.84 | 11.49
17:25 | 11 | 1 | 2 | 1 | 10 | 1 | 4 | 0 | 13 | 4 | 18 | 36 | 4 | 5 | 1 | 4 | 2 | 4 | 3 | 12 | 11 | 2 | 2 | 42 | 23 | 0 | 12 | 33 | 3 | 2 | 7 | 16 | 15 | 325 | 21 | 24 | 228 | 38 | 57 | 24 | 17:25 | 132 | 12 | 24 | 12 | 120 | 12 | 48 | 0 | 156 | 48 | 216 | 432 | 48 | 60 | 12 | 48 | 24 | 48 | 36 | 144 | 132 | 24 | 24 | 504 | 276 | 0 | 144 | 396 | 36 | 24 | 84 | 192 | 180 | 3900 | 252 | 288 | 2736 | 456 | 684 | 288 |  | 17:25 | 99 | 9 | 18 | 9 | 90 | 0 | 9 | 36 | 0 | 117 | 36 | 0 | 162 | 324 | 36 | 45 | 9 | 0 | 36 | 18 | 36 | 27 | 108 | 0 | 99 | 18 | 18 | 378 | 207 | 0 | 0 | 108 | 297 | 27 | 18 | 0 | 63 | 144 | 135 | 937.5 | 189 | 0 | 216 | 937.5 | 342 | 513 | 216 | 12252 | 6087 | 24504 | 12174 | 24.504 | 12.174
17:30 | 13 | 1 | 2 | 2 | 9 | 2 | 5 | 2 | 21 | 4 | 18 | 36 | 4 | 4 | 8 | 4 | 4 | 4 | 2 | 11 | 11 | 3 | 2 | 40 | 28 | 0 | 9 | 32 | 2 | 3 | 7 | 18 | 30 | 358 | 15 | 24 | 232 | 34 | 25 | 21 | 17:30 | 156 | 12 | 24 | 24 | 108 | 24 | 60 | 24 | 252 | 48 | 216 | 432 | 48 | 48 | 96 | 48 | 48 | 48 | 24 | 132 | 132 | 36 | 24 | 480 | 336 | 0 | 108 | 384 | 24 | 36 | 84 | 216 | 360 | 4296 | 180 | 288 | 2784 | 408 | 300 | 252 |  | 17:30 | 117 | 9 | 18 | 18 | 81 | 0 | 18 | 45 | 18 | 189 | 36 | 0 | 162 | 324 | 36 | 36 | 72 | 0 | 36 | 36 | 36 | 18 | 99 | 0 | 99 | 27 | 18 | 360 | 252 | 0 | 0 | 81 | 288 | 18 | 27 | 0 | 63 | 162 | 270 | 937.5 | 135 | 0 | 216 | 937.5 | 306 | 225 | 189 | 12600 | 6015 | 25200 | 12030 | 25.2 | 12.03
17:35 | 12 | 24 | 1 | 1 | 10 | 2 | 2 | 1 | 19 | 4 | 25 | 9 | 3 | 3 | 10 | 4 | 3 | 4 | 2 | 11 | 10 | 2 | 3 | 30 | 27 | 0 | 10 | 29 | 3 | 2 | 6 | 158 | 36 | 397 | 15 | 33 | 239 | 27 | 33 | 14 | 17:35 | 144 | 288 | 12 | 12 | 120 | 24 | 24 | 12 | 228 | 48 | 300 | 108 | 36 | 36 | 120 | 48 | 36 | 48 | 24 | 132 | 120 | 24 | 36 | 360 | 324 | 0 | 120 | 348 | 36 | 24 | 72 | 1896 | 432 | 4764 | 180 | 396 | 2868 | 324 | 396 | 168 |  | 17:35 | 108 | 216 | 9 | 9 | 90 | 0 | 18 | 18 | 9 | 171 | 36 | 0 | 225 | 81 | 27 | 27 | 90 | 0 | 36 | 27 | 36 | 18 | 99 | 0 | 90 | 18 | 27 | 270 | 243 | 0 | 0 | 90 | 261 | 27 | 18 | 0 | 54 | 937.5 | 324 | 937.5 | 135 | 0 | 297 | 937.5 | 243 | 297 | 126 | 14688 | 6682.5 | 29376 | 13365 | 29.376 | 13.365
17:40 | 12 | 5 | 2 | 1 | 7 | 2 | 3 | 14 | 19 | 4 | 6 | 1 | 4 | 4 | 9 | 12 | 3 | 3 | 2 | 13 | 10 | 2 | 2 | 27 | 28 | 0 | 10 | 20 | 2 | 2 | 7 | 30 | 35 | 240 | 15 | 36 | 238 | 33 | 26 | 22 | 17:40 | 144 | 60 | 24 | 12 | 84 | 24 | 36 | 168 | 228 | 48 | 72 | 12 | 48 | 48 | 108 | 144 | 36 | 36 | 24 | 156 | 120 | 24 | 24 | 324 | 336 | 0 | 120 | 240 | 24 | 24 | 84 | 360 | 420 | 2880 | 180 | 432 | 2856 | 396 | 312 | 264 |  | 17:40 | 108 | 45 | 18 | 9 | 63 | 0 | 18 | 27 | 126 | 171 | 36 | 0 | 54 | 9 | 36 | 36 | 81 | 0 | 108 | 27 | 27 | 18 | 117 | 0 | 90 | 18 | 18 | 243 | 252 | 0 | 0 | 90 | 180 | 18 | 18 | 0 | 63 | 270 | 315 | 937.5 | 135 | 0 | 324 | 937.5 | 297 | 234 | 198 | 10932 | 5772 | 21864 | 11544 | 21.864 | 11.544
17:45 | 11 | 1 | 10 | 1 | 7 | 0 | 4 | 10 | 19 | 3 | 1 | 0 | 10 | 3 | 8 | 12 | 5 | 2 | 3 | 11 | 4 | 3 | 2 | 32 | 27 | 0 | 10 | 20 | 2 | 3 | 7 | 50 | 86 | 149 | 15 | 36 | 238 | 45 | 25 | 84 | 17:45 | 132 | 12 | 120 | 12 | 84 | 0 | 48 | 120 | 228 | 36 | 12 | 0 | 120 | 36 | 96 | 144 | 60 | 24 | 36 | 132 | 48 | 36 | 24 | 384 | 324 | 0 | 120 | 240 | 24 | 36 | 84 | 600 | 1032 | 1788 | 180 | 432 | 2856 | 540 | 300 | 1008 |  | 17:45 | 99 | 9 | 90 | 9 | 63 | 0 | 0 | 36 | 90 | 171 | 27 | 0 | 9 | 0 | 90 | 27 | 72 | 0 | 108 | 45 | 18 | 27 | 99 | 0 | 36 | 27 | 18 | 288 | 243 | 0 | 0 | 90 | 180 | 18 | 27 | 0 | 63 | 450 | 774 | 937.5 | 135 | 0 | 324 | 937.5 | 405 | 225 | 756 | 11508 | 7023 | 23016 | 14046 | 23.016 | 14.046
17:50 | 11 | 1 | 9 | 1 | 8 | 5 | 2 | 2 | 19 | 4 | 3 | 1 | 12 | 4 | 9 | 11 | 2 | 2 | 3 | 11 | 3 | 2 | 3 | 31 | 27 | 0 | 10 | 20 | 3 | 2 | 7 | 57 | 35 | 147 | 25 | 35 | 241 | 16 | 25 | 41 | 17:50 | 132 | 12 | 108 | 12 | 96 | 60 | 24 | 24 | 228 | 48 | 36 | 12 | 144 | 48 | 108 | 132 | 24 | 24 | 36 | 132 | 36 | 24 | 36 | 372 | 324 | 0 | 120 | 240 | 36 | 24 | 84 | 684 | 420 | 1764 | 300 | 420 | 2892 | 192 | 300 | 492 |  | 17:50 | 99 | 9 | 81 | 9 | 72 | 0 | 45 | 18 | 18 | 171 | 36 | 0 | 27 | 9 | 108 | 36 | 81 | 0 | 99 | 18 | 18 | 27 | 99 | 0 | 27 | 18 | 27 | 279 | 243 | 0 | 0 | 90 | 180 | 27 | 18 | 0 | 63 | 513 | 315 | 937.5 | 225 | 0 | 315 | 937.5 | 144 | 225 | 369 | 10200 | 6033 | 20400 | 12066 | 20.4 | 12.066
17:55 | 11 | 1 | 9 | 2 | 10 | 11 | 2 | 10 | 10 | 5 | 10 | 1 | 15 | 3 | 9 | 11 | 3 | 2 | 3 | 9 | 2 | 3 | 2 | 31 | 30 | 0 | 9 | 13 | 2 | 3 | 13 | 25 | 29 | 144 | 36 | 34 | 244 | 26 | 28 | 42 | 17:55 | 132 | 12 | 108 | 24 | 120 | 132 | 24 | 120 | 120 | 60 | 120 | 12 | 180 | 36 | 108 | 132 | 36 | 24 | 36 | 108 | 24 | 36 | 24 | 372 | 360 | 0 | 108 | 156 | 24 | 36 | 156 | 300 | 348 | 1728 | 432 | 408 | 2928 | 312 | 336 | 504 |  | 17:55 | 99 | 9 | 81 | 18 | 90 | 0 | 99 | 18 | 90 | 90 | 45 | 0 | 90 | 9 | 135 | 27 | 81 | 0 | 99 | 27 | 18 | 27 | 81 | 0 | 18 | 27 | 18 | 279 | 270 | 0 | 0 | 81 | 117 | 18 | 27 | 0 | 117 | 225 | 261 | 937.5 | 324 | 0 | 306 | 937.5 | 234 | 252 | 378 | 10236 | 6060 | 20472 | 12120 | 20.472 | 12.12
18:00 | 11 | 4 | 8 | 1 | 8 | 13 | 4 | 10 | 9 | 3 | 9 | 14 | 21 | 4 | 9 | 9 | 3 | 2 | 2 | 4 | 2 | 2 | 3 | 30 | 35 | 0 | 10 | 12 | 3 | 10 | 19 | 32 | 25 | 184 | 41 | 25 | 226 | 26 | 31 | 52 | 18:00 | 132 | 48 | 96 | 12 | 96 | 156 | 48 | 120 | 108 | 36 | 108 | 168 | 252 | 48 | 108 | 108 | 36 | 24 | 24 | 48 | 24 | 24 | 36 | 360 | 420 | 0 | 120 | 144 | 36 | 120 | 228 | 384 | 300 | 2208 | 492 | 300 | 2712 | 312 | 372 | 624 |  | 18:00 | 99 | 36 | 72 | 9 | 72 | 0 | 117 | 36 | 90 | 81 | 27 | 0 | 81 | 126 | 189 | 36 | 81 | 0 | 81 | 27 | 18 | 18 | 36 | 0 | 18 | 18 | 27 | 270 | 315 | 0 | 0 | 90 | 108 | 27 | 90 | 0 | 171 | 288 | 225 | 937.5 | 369 | 0 | 225 | 937.5 | 234 | 279 | 468 | 10992 | 6429 | 21984 | 12858 | 21.984 | 12.858
18:05 | 9 | 10 | 9 | 1 | 12 | 12 | 3 | 10 | 10 | 70 | 8 | 2 | 12 | 4 | 9 | 10 | 3 | 2 | 10 | 4 | 3 | 3 | 2 | 30 | 34 | 0 | 10 | 12 | 2 | 22 | 18 | 44 | 73 | 141 | 209 | 25 | 148 | 25 | 20 | 49 | 18:05 | 108 | 120 | 108 | 12 | 144 | 144 | 36 | 120 | 120 | 840 | 96 | 24 | 144 | 48 | 108 | 120 | 36 | 24 | 120 | 48 | 36 | 36 | 24 | 360 | 408 | 0 | 120 | 144 | 24 | 264 | 216 | 528 | 876 | 1692 | 2508 | 300 | 1776 | 300 | 240 | 588 |  | 18:05 | 81 | 90 | 81 | 9 | 108 | 0 | 108 | 27 | 90 | 90 | 630 | 0 | 72 | 18 | 108 | 36 | 81 | 0 | 90 | 27 | 18 | 90 | 36 | 0 | 27 | 27 | 18 | 270 | 306 | 0 | 0 | 90 | 108 | 18 | 198 | 0 | 162 | 396 | 657 | 937.5 | 937.5 | 0 | 225 | 937.5 | 225 | 180 | 441 | 12960 | 8050.5 | 25920 | 16101 | 25.92 | 16.101
18:10 | 4 | 9 | 7 | 1 | 17 | 13 | 4 | 9 | 9 | 37 | 6 | 0 | 10 | 1 | 9 | 10 | 5 | 2 | 10 | 4 | 2 | 2 | 3 | 30 | 34 | 6 | 10 | 12 | 2 | 25 | 18 | 80 | 30 | 29 | 276 | 21 | 101 | 31 | 20 | 99 | 18:10 | 48 | 108 | 84 | 12 | 204 | 156 | 48 | 108 | 108 | 444 | 72 | 0 | 120 | 12 | 108 | 120 | 60 | 24 | 120 | 48 | 24 | 24 | 36 | 360 | 408 | 72 | 120 | 144 | 24 | 300 | 216 | 960 | 360 | 348 | 3312 | 252 | 1212 | 372 | 240 | 1188 |  | 18:10 | 36 | 81 | 63 | 9 | 153 | 0 | 117 | 36 | 81 | 81 | 333 | 0 | 54 | 0 | 90 | 9 | 81 | 0 | 90 | 45 | 18 | 90 | 36 | 0 | 18 | 18 | 27 | 270 | 306 | 0 | 54 | 90 | 108 | 18 | 225 | 0 | 162 | 720 | 270 | 261 | 937.5 | 0 | 189 | 909 | 279 | 180 | 891 | 11976 | 7435.5 | 23952 | 14871 | 23.952 | 14.871
18:15 | 4 | 9 | 8 | 5 | 15 | 12 | 13 | 11 | 4 | 11 | 4 | 0 | 10 | 1 | 6 | 10 | 11 | 7 | 10 | 4 | 3 | 3 | 3 | 30 | 34 | 11 | 10 | 13 | 11 | 26 | 17 | 45 | 30 | 25 | 154 | 16 | 44 | 26 | 20 | 97 | 18:15 | 48 | 108 | 96 | 60 | 180 | 144 | 156 | 132 | 48 | 132 | 48 | 0 | 120 | 12 | 72 | 120 | 132 | 84 | 120 | 48 | 36 | 36 | 36 | 360 | 408 | 132 | 120 | 156 | 132 | 312 | 204 | 540 | 360 | 300 | 1848 | 192 | 528 | 312 | 240 | 1164 |  | 18:15 | 36 | 81 | 72 | 45 | 135 | 0 | 108 | 117 | 99 | 36 | 99 | 0 | 36 | 0 | 90 | 9 | 54 | 0 | 90 | 99 | 63 | 90 | 36 | 0 | 27 | 27 | 27 | 270 | 306 | 0 | 99 | 90 | 117 | 99 | 234 | 0 | 153 | 405 | 270 | 225 | 937.5 | 0 | 144 | 396 | 234 | 180 | 873 | 9276 | 6508.5 | 18552 | 13017 | 18.552 | 13.017
18:20 | 3 | 7 | 8 | 11 | 16 | 11 | 11 | 24 | 4 | 11 | 3 | 3 | 10 | 2 | 1 | 10 | 11 | 11 | 9 | 5 | 3 | 10 | 2 | 26 | 34 | 10 | 10 | 12 | 12 | 25 | 18 | 103 | 29 | 26 | 145 | 16 | 65 | 17 | 20 | 82 | 18:20 | 36 | 84 | 96 | 132 | 192 | 132 | 132 | 288 | 48 | 132 | 36 | 36 | 120 | 24 | 12 | 120 | 132 | 132 | 108 | 60 | 36 | 120 | 24 | 312 | 408 | 120 | 120 | 144 | 144 | 300 | 216 | 1236 | 348 | 312 | 1740 | 192 | 780 | 204 | 240 | 984 |  | 18:20 | 27 | 63 | 72 | 99 | 144 | 0 | 99 | 99 | 216 | 36 | 99 | 0 | 27 | 27 | 90 | 18 | 9 | 0 | 90 | 99 | 99 | 81 | 45 | 0 | 27 | 90 | 18 | 234 | 306 | 0 | 90 | 90 | 108 | 108 | 225 | 0 | 162 | 927 | 261 | 234 | 937.5 | 0 | 144 | 585 | 153 | 180 | 738 | 10032 | 7156.5 | 20064 | 14313 | 20.064 | 14.313
18:25 | 3 | 8 | 8 | 9 | 14 | 8 | 11 | 24 | 3 | 11 | 61 | 1 | 9 | 8 | 0 | 9 | 10 | 13 | 9 | 5 | 3 | 12 | 12 | 20 | 34 | 10 | 11 | 13 | 11 | 25 | 6 | 116 | 30 | 39 | 142 | 17 | 102 | 14 | 20 | 82 | 18:25 | 36 | 96 | 96 | 108 | 168 | 96 | 132 | 288 | 36 | 132 | 732 | 12 | 108 | 96 | 0 | 108 | 120 | 156 | 108 | 60 | 36 | 144 | 144 | 240 | 408 | 120 | 132 | 156 | 132 | 300 | 72 | 1392 | 360 | 468 | 1704 | 204 | 1224 | 168 | 240 | 984 |  | 18:25 | 27 | 72 | 72 | 81 | 126 | 0 | 72 | 99 | 216 | 27 | 99 | 0 | 549 | 9 | 81 | 72 | 0 | 0 | 81 | 90 | 117 | 81 | 45 | 0 | 27 | 108 | 108 | 180 | 306 | 0 | 90 | 99 | 117 | 99 | 225 | 0 | 54 | 937.5 | 270 | 351 | 937.5 | 0 | 153 | 918 | 126 | 180 | 738 | 11316 | 8040 | 22632 | 16080 | 22.632 | 16.08
18:30 | 3 | 9 | 8 | 9 | 16 | 8 | 11 | 24 | 2 | 10 | 24 | 3 | 3 | 11 | 2 | 1 | 11 | 11 | 9 | 4 | 3 | 11 | 12 | 15 | 34 | 9 | 10 | 13 | 10 | 21 | 7 | 97 | 68 | 65 | 142 | 21 | 41 | 14 | 20 | 89 | 18:30 | 36 | 108 | 96 | 108 | 192 | 96 | 132 | 288 | 24 | 120 | 288 | 36 | 36 | 132 | 24 | 12 | 132 | 132 | 108 | 48 | 36 | 132 | 144 | 180 | 408 | 108 | 120 | 156 | 120 | 252 | 84 | 1164 | 816 | 780 | 1704 | 252 | 492 | 168 | 240 | 1068 |  | 18:30 | 27 | 81 | 72 | 81 | 144 | 0 | 72 | 99 | 216 | 18 | 90 | 0 | 216 | 27 | 27 | 99 | 18 | 0 | 9 | 99 | 99 | 81 | 36 | 0 | 27 | 99 | 108 | 135 | 306 | 0 | 81 | 90 | 117 | 90 | 189 | 0 | 63 | 873 | 612 | 585 | 937.5 | 0 | 189 | 369 | 126 | 180 | 801 | 10572 | 7588.5 | 21144 | 15177 | 21.144 | 15.177
18:35 | 3 | 5 | 6 | 6 | 15 | 11 | 11 | 25 | 2 | 15 | 8 | 6 | 1 | 11 | 2 | 2 | 9 | 11 | 9 | 4 | 3 | 11 | 11 | 14 | 33 | 10 | 10 | 24 | 11 | 21 | 7 | 30 | 92 | 70 | 70 | 29 | 30 | 13 | 32 | 87 | 18:35 | 36 | 60 | 72 | 72 | 180 | 132 | 132 | 300 | 24 | 180 | 96 | 72 | 12 | 132 | 24 | 24 | 108 | 132 | 108 | 48 | 36 | 132 | 132 | 168 | 396 | 120 | 120 | 288 | 132 | 252 | 84 | 360 | 1104 | 840 | 840 | 348 | 360 | 156 | 384 | 1044 |  | 18:35 | 27 | 45 | 54 | 54 | 135 | 0 | 99 | 99 | 225 | 18 | 135 | 0 | 72 | 54 | 9 | 99 | 18 | 0 | 18 | 81 | 99 | 81 | 36 | 0 | 27 | 99 | 99 | 126 | 297 | 0 | 90 | 90 | 216 | 99 | 189 | 0 | 63 | 270 | 828 | 630 | 630 | 0 | 261 | 270 | 117 | 288 | 783 | 9240 | 6930 | 18480 | 13860 | 18.48 | 13.86
18:40 | 3 | 3 | 0 | 6 | 15 | 2 | 10 | 50 | 2 | 18 | 23 | 12 | 2 | 10 | 1 | 2 | 10 | 18 | 8 | 3 | 3 | 10 | 11 | 49 | 34 | 9 | 10 | 25 | 10 | 20 | 7 | 28 | 45 | 235 | 32 | 27 | 31 | 14 | 32 | 61 | 18:40 | 36 | 36 | 0 | 72 | 180 | 24 | 120 | 600 | 24 | 216 | 276 | 144 | 24 | 120 | 12 | 24 | 120 | 216 | 96 | 36 | 36 | 120 | 132 | 588 | 408 | 108 | 120 | 300 | 120 | 240 | 84 | 336 | 540 | 2820 | 384 | 324 | 372 | 168 | 384 | 732 |  | 18:40 | 27 | 27 | 0 | 54 | 135 | 0 | 18 | 90 | 450 | 18 | 162 | 0 | 207 | 108 | 18 | 90 | 9 | 0 | 18 | 90 | 162 | 72 | 27 | 0 | 27 | 90 | 99 | 441 | 306 | 0 | 81 | 90 | 225 | 90 | 180 | 0 | 63 | 252 | 405 | 937.5 | 288 | 0 | 243 | 279 | 126 | 288 | 549 | 10692 | 6841.5 | 21384 | 13683 | 21.384 | 13.683
18:45 | 3 | 6 | 0 | 7 | 14 | 3 | 10 | 91 | 1 | 19 | 28 | 11 | 10 | 10 | 2 | 2 | 9 | 29 | 8 | 4 | 2 | 11 | 10 | 23 | 26 | 4 | 11 | 25 | 10 | 78 | 7 | 17 | 47 | 209 | 34 | 27 | 37 | 17 | 33 | 71 | 18:45 | 36 | 72 | 0 | 84 | 168 | 36 | 120 | 1092 | 12 | 228 | 336 | 132 | 120 | 120 | 24 | 24 | 108 | 348 | 96 | 48 | 24 | 132 | 120 | 276 | 312 | 48 | 132 | 300 | 120 | 936 | 84 | 204 | 564 | 2508 | 408 | 324 | 444 | 204 | 396 | 852 |  | 18:45 | 27 | 54 | 0 | 63 | 126 | 0 | 27 | 90 | 819 | 9 | 171 | 0 | 252 | 99 | 90 | 90 | 18 | 0 | 18 | 81 | 261 | 72 | 36 | 0 | 18 | 99 | 90 | 207 | 234 | 0 | 36 | 99 | 225 | 90 | 702 | 0 | 63 | 153 | 423 | 937.5 | 306 | 0 | 243 | 333 | 153 | 297 | 639 | 11592 | 7750.5 | 23184 | 15501 | 23.184 | 15.501
18:50 | 3 | 0 | 0 | 16 | 15 | 3 | 10 | 26 | 1 | 25 | 28 | 10 | 12 | 9 | 2 | 1 | 8 | 27 | 1 | 3 | 3 | 10 | 11 | 24 | 27 | 0 | 10 | 25 | 9 | 48 | 7 | 18 | 43 | 143 | 42 | 26 | 37 | 26 | 31 | 49 | 18:50 | 36 | 0 | 0 | 192 | 180 | 36 | 120 | 312 | 12 | 300 | 336 | 120 | 144 | 108 | 24 | 12 | 96 | 324 | 12 | 36 | 36 | 120 | 132 | 288 | 324 | 0 | 120 | 300 | 108 | 576 | 84 | 216 | 516 | 1716 | 504 | 312 | 444 | 312 | 372 | 588 |  | 18:50 | 27 | 0 | 0 | 144 | 135 | 0 | 27 | 90 | 234 | 9 | 225 | 0 | 252 | 90 | 108 | 81 | 18 | 0 | 9 | 72 | 243 | 9 | 27 | 0 | 27 | 90 | 99 | 216 | 243 | 0 | 0 | 90 | 225 | 81 | 432 | 0 | 63 | 162 | 387 | 937.5 | 378 | 0 | 234 | 333 | 234 | 279 | 441 | 9468 | 6751.5 | 18936 | 13503 | 18.936 | 13.503
18:55 | 2 | 0 | 0 | 18 | 14 | 3 | 10 | 41 | 2 | 27 | 28 | 10 | 12 | 10 | 4 | 2 | 9 | 27 | 0 | 2 | 3 | 10 | 10 | 23 | 26 | 0 | 10 | 24 | 3 | 17 | 7 | 24 | 54 | 143 | 37 | 21 | 36 | 26 | 32 | 28 | 18:55 | 24 | 0 | 0 | 216 | 168 | 36 | 120 | 492 | 24 | 324 | 336 | 120 | 144 | 120 | 48 | 24 | 108 | 324 | 0 | 24 | 36 | 120 | 120 | 276 | 312 | 0 | 120 | 288 | 36 | 204 | 84 | 288 | 648 | 1716 | 444 | 252 | 432 | 312 | 384 | 336 |  | 18:55 | 18 | 0 | 0 | 162 | 126 | 0 | 27 | 90 | 369 | 18 | 243 | 0 | 252 | 90 | 108 | 90 | 36 | 0 | 18 | 81 | 243 | 0 | 18 | 0 | 27 | 90 | 90 | 207 | 234 | 0 | 0 | 90 | 216 | 27 | 153 | 0 | 63 | 216 | 486 | 937.5 | 333 | 0 | 189 | 324 | 234 | 288 | 252 | 9060 | 6445.5 | 18120 | 12891 | 18.12 | 12.891
19:00 | 2 | 1 | 2 | 17 | 15 | 3 | 10 | 129 | 2 | 28 | 28 | 9 | 9 | 13 | 2 | 2 | 6 | 26 | 0 | 2 | 3 | 8 | 10 | 23 | 26 | 1 | 10 | 26 | 2 | 17 | 7 | 25 | 53 | 142 | 36 | 16 | 37 | 25 | 24 | 36 | 19:00 | 24 | 12 | 24 | 204 | 180 | 36 | 120 | 1548 | 24 | 336 | 336 | 108 | 108 | 156 | 24 | 24 | 72 | 312 | 0 | 24 | 36 | 96 | 120 | 276 | 312 | 12 | 120 | 312 | 24 | 204 | 84 | 300 | 636 | 1704 | 432 | 192 | 444 | 300 | 288 | 432 |  | 19:00 | 18 | 9 | 18 | 153 | 135 | 0 | 27 | 90 | 937.5 | 18 | 252 | 0 | 252 | 81 | 81 | 117 | 18 | 0 | 18 | 54 | 234 | 0 | 18 | 0 | 27 | 72 | 90 | 207 | 234 | 0 | 9 | 90 | 234 | 18 | 153 | 0 | 63 | 225 | 477 | 937.5 | 324 | 0 | 144 | 333 | 225 | 216 | 324 | 9996 | 6933 | 19992 | 13866 | 19.992 | 13.866
19:05 | 4 | 2 | 2 | 18 | 12 | 4 | 7 | 25 | 2 | 26 | 28 | 10 | 18 | 18 | 2 | 2 | 1 | 26 | 0 | 1 | 3 | 3 | 8 | 21 | 26 | 0 | 10 | 25 | 3 | 18 | 16 | 26 | 61 | 72 | 36 | 16 | 66 | 24 | 22 | 36 | 19:05 | 48 | 24 | 24 | 216 | 144 | 48 | 84 | 300 | 24 | 312 | 336 | 120 | 216 | 216 | 24 | 24 | 12 | 312 | 0 | 12 | 36 | 36 | 96 | 252 | 312 | 0 | 120 | 300 | 36 | 216 | 192 | 312 | 732 | 864 | 432 | 192 | 792 | 288 | 264 | 432 |  | 19:05 | 36 | 18 | 18 | 162 | 108 | 0 | 36 | 63 | 225 | 18 | 234 | 0 | 252 | 90 | 162 | 162 | 18 | 0 | 18 | 9 | 234 | 0 | 9 | 0 | 27 | 27 | 72 | 189 | 234 | 0 | 0 | 90 | 225 | 27 | 162 | 0 | 144 | 234 | 549 | 648 | 324 | 0 | 144 | 594 | 216 | 198 | 324 | 8400 | 6300 | 16800 | 12600 | 16.8 | 12.6
19:10 | 11 | 3 | 2 | 17 | 7 | 2 | 2 | 26 | 3 | 23 | 27 | 9 | 20 | 19 | 2 | 2 | 2 | 26 | 0 | 5 | 3 | 3 | 2 | 10 | 27 | 0 | 11 | 25 | 3 | 17 | 19 | 25 | 43 | 75 | 36 | 18 | 38 | 22 | 211 | 36 | 19:10 | 132 | 36 | 24 | 204 | 84 | 24 | 24 | 312 | 36 | 276 | 324 | 108 | 240 | 228 | 24 | 24 | 24 | 312 | 0 | 60 | 36 | 36 | 24 | 120 | 324 | 0 | 132 | 300 | 36 | 204 | 228 | 300 | 516 | 900 | 432 | 216 | 456 | 264 | 2532 | 432 |  | 19:10 | 99 | 27 | 18 | 153 | 63 | 0 | 18 | 18 | 234 | 27 | 207 | 0 | 243 | 81 | 180 | 171 | 18 | 0 | 18 | 18 | 234 | 0 | 45 | 0 | 27 | 27 | 18 | 90 | 243 | 0 | 0 | 99 | 225 | 27 | 153 | 0 | 171 | 225 | 387 | 675 | 324 | 0 | 162 | 342 | 198 | 937.5 | 324 | 9984 | 6526.5 | 19968 | 13053 | 19.968 | 13.053
19:15 | 11 | 2 | 1 | 17 | 7 | 2 | 2 | 26 | 8 | 22 | 27 | 9 | 18 | 18 | 2 | 1 | 2 | 24 | 0 | 13 | 13 | 3 | 3 | 9 | 27 | 0 | 14 | 25 | 3 | 17 | 18 | 24 | 41 | 152 | 35 | 16 | 37 | 14 | 100 | 35 | 19:15 | 132 | 24 | 12 | 204 | 84 | 24 | 24 | 312 | 96 | 264 | 324 | 108 | 216 | 216 | 24 | 12 | 24 | 288 | 0 | 156 | 156 | 36 | 36 | 108 | 324 | 0 | 168 | 300 | 36 | 204 | 216 | 288 | 492 | 1824 | 420 | 192 | 444 | 168 | 1200 | 420 |  | 19:15 | 99 | 18 | 9 | 153 | 63 | 0 | 18 | 18 | 234 | 72 | 198 | 0 | 243 | 81 | 162 | 162 | 18 | 0 | 9 | 18 | 216 | 0 | 117 | 0 | 117 | 27 | 27 | 81 | 243 | 0 | 0 | 126 | 225 | 27 | 153 | 0 | 162 | 216 | 369 | 937.5 | 315 | 0 | 144 | 333 | 126 | 900 | 315 | 9576 | 6751.5 | 19152 | 13503 | 19.152 | 13.503
19:20 | 10 | 2 | 1 | 126 | 6 | 2 | 2 | 24 | 10 | 18 | 20 | 9 | 17 | 18 | 1 | 2 | 2 | 25 | 0 | 11 | 12 | 3 | 3 | 10 | 27 | 1 | 20 | 26 | 2 | 17 | 18 | 30 | 41 | 173 | 23 | 16 | 28 | 14 | 19 | 35 | 19:20 | 120 | 24 | 12 | 1512 | 72 | 24 | 24 | 288 | 120 | 216 | 240 | 108 | 204 | 216 | 12 | 24 | 24 | 300 | 0 | 132 | 144 | 36 | 36 | 120 | 324 | 12 | 240 | 312 | 24 | 204 | 216 | 360 | 492 | 2076 | 276 | 192 | 336 | 168 | 228 | 420 |  | 19:20 | 90 | 18 | 9 | 937.5 | 54 | 0 | 18 | 18 | 216 | 90 | 162 | 0 | 180 | 81 | 153 | 162 | 9 | 0 | 18 | 18 | 225 | 0 | 99 | 0 | 108 | 27 | 27 | 90 | 243 | 0 | 9 | 180 | 234 | 18 | 153 | 0 | 162 | 270 | 369 | 937.5 | 207 | 0 | 144 | 252 | 126 | 171 | 315 | 9888 | 6600 | 19776 | 13200 | 19.776 | 13.2
19:25 | 10 | 2 | 1 | 27 | 6 | 2 | 6 | 17 | 10 | 17 | 19 | 6 | 18 | 18 | 2 | 2 | 13 | 25 | 0 | 15 | 11 | 2 | 3 | 12 | 27 | 0 | 19 | 24 | 3 | 17 | 17 | 35 | 41 | 153 | 16 | 17 | 23 | 14 | 20 | 35 | 19:25 | 120 | 24 | 12 | 324 | 72 | 24 | 72 | 204 | 120 | 204 | 228 | 72 | 216 | 216 | 24 | 24 | 156 | 300 | 0 | 180 | 132 | 24 | 36 | 144 | 324 | 0 | 228 | 288 | 36 | 204 | 204 | 420 | 492 | 1836 | 192 | 204 | 276 | 168 | 240 | 420 |  | 19:25 | 90 | 18 | 9 | 243 | 54 | 0 | 18 | 54 | 153 | 90 | 153 | 0 | 171 | 54 | 162 | 162 | 18 | 0 | 18 | 117 | 225 | 0 | 135 | 0 | 99 | 18 | 27 | 108 | 243 | 0 | 0 | 171 | 216 | 27 | 153 | 0 | 153 | 315 | 369 | 937.5 | 144 | 0 | 153 | 207 | 126 | 180 | 315 | 8460 | 5905.5 | 16920 | 11811 | 16.92 | 11.811
19:30 | 24 | 1 | 1 | 15 | 7 | 2 | 10 | 18 | 11 | 18 | 19 | 1 | 17 | 18 | 2 | 2 | 24 | 25 | 0 | 34 | 11 | 3 | 2 | 24 | 27 | 0 | 18 | 30 | 3 | 18 | 14 | 35 | 40 | 151 | 15 | 28 | 23 | 15 | 61 | 33 | 19:30 | 288 | 12 | 12 | 180 | 84 | 24 | 120 | 216 | 132 | 216 | 228 | 12 | 204 | 216 | 24 | 24 | 288 | 300 | 0 | 408 | 132 | 36 | 24 | 288 | 324 | 0 | 216 | 360 | 36 | 216 | 168 | 420 | 480 | 1812 | 180 | 336 | 276 | 180 | 732 | 396 |  | 19:30 | 216 | 9 | 9 | 135 | 63 | 0 | 18 | 90 | 162 | 99 | 162 | 0 | 171 | 9 | 153 | 162 | 18 | 0 | 18 | 216 | 225 | 0 | 306 | 0 | 99 | 27 | 18 | 216 | 243 | 0 | 0 | 162 | 270 | 27 | 162 | 0 | 126 | 315 | 360 | 937.5 | 135 | 0 | 252 | 207 | 135 | 549 | 297 | 9600 | 6778.5 | 19200 | 13557 | 19.2 | 13.557
19:35 | 23 | 1 | 3 | 14 | 6 | 2 | 11 | 18 | 20 | 17 | 19 | 2 | 20 | 22 | 1 | 1 | 23 | 26 | 0 | 33 | 11 | 3 | 3 | 24 | 28 | 0 | 18 | 105 | 2 | 17 | 6 | 36 | 34 | 68 | 15 | 27 | 23 | 14 | 93 | 21 | 19:35 | 276 | 12 | 36 | 168 | 72 | 24 | 132 | 216 | 240 | 204 | 228 | 24 | 240 | 264 | 12 | 12 | 276 | 312 | 0 | 396 | 132 | 36 | 36 | 288 | 336 | 0 | 216 | 1260 | 24 | 204 | 72 | 432 | 408 | 816 | 180 | 324 | 276 | 168 | 1116 | 252 |  | 19:35 | 207 | 9 | 27 | 126 | 54 | 0 | 18 | 99 | 162 | 180 | 153 | 0 | 171 | 18 | 180 | 198 | 9 | 0 | 9 | 207 | 234 | 0 | 297 | 0 | 99 | 27 | 27 | 216 | 252 | 0 | 0 | 162 | 937.5 | 18 | 153 | 0 | 54 | 324 | 306 | 612 | 135 | 0 | 243 | 207 | 126 | 837 | 189 | 9720 | 7282.5 | 19440 | 14565 | 19.44 | 14.565
19:40 | 22 | 2 | 2 | 16 | 6 | 12 | 10 | 17 | 19 | 18 | 19 | 2 | 22 | 29 | 2 | 2 | 30 | 30 | 0 | 35 | 9 | 2 | 3 | 23 | 27 | 1 | 18 | 30 | 3 | 17 | 7 | 37 | 33 | 38 | 15 | 27 | 23 | 16 | 48 | 20 | 19:40 | 264 | 24 | 24 | 192 | 72 | 144 | 120 | 204 | 228 | 216 | 228 | 24 | 264 | 348 | 24 | 24 | 360 | 360 | 0 | 420 | 108 | 24 | 36 | 276 | 324 | 12 | 216 | 360 | 36 | 204 | 84 | 444 | 396 | 456 | 180 | 324 | 276 | 192 | 576 | 240 |  | 19:40 | 198 | 18 | 18 | 144 | 54 | 0 | 108 | 90 | 153 | 171 | 162 | 0 | 171 | 18 | 198 | 261 | 18 | 0 | 18 | 270 | 270 | 0 | 315 | 0 | 81 | 18 | 27 | 207 | 243 | 0 | 9 | 162 | 270 | 27 | 153 | 0 | 63 | 333 | 297 | 342 | 135 | 0 | 243 | 207 | 144 | 432 | 180 | 8304 | 6228 | 16608 | 12456 | 16.608 | 12.456
19:45 | 22 | 3 | 1 | 19 | 4 | 28 | 10 | 18 | 18 | 17 | 20 | 2 | 23 | 33 | 9 | 2 | 26 | 30 | 0 | 38 | 3 | 3 | 22 | 23 | 27 | 0 | 17 | 28 | 3 | 17 | 7 | 76 | 43 | 34 | 16 | 27 | 55 | 26 | 49 | 20 | 19:45 | 264 | 36 | 12 | 228 | 48 | 336 | 120 | 216 | 216 | 204 | 240 | 24 | 276 | 396 | 108 | 24 | 312 | 360 | 0 | 456 | 36 | 36 | 264 | 276 | 324 | 0 | 204 | 336 | 36 | 204 | 84 | 912 | 516 | 408 | 192 | 324 | 660 | 312 | 588 | 240 |  | 19:45 | 198 | 27 | 9 | 171 | 36 | 0 | 252 | 90 | 162 | 162 | 153 | 0 | 180 | 18 | 207 | 297 | 81 | 0 | 18 | 234 | 270 | 0 | 342 | 0 | 27 | 27 | 198 | 207 | 243 | 0 | 0 | 153 | 252 | 27 | 153 | 0 | 63 | 684 | 387 | 306 | 144 | 0 | 243 | 495 | 234 | 441 | 180 | 9828 | 7371 | 19656 | 14742 | 19.656 | 14.742
19:50 | 21 | 18 | 11 | 19 | 17 | 31 | 13 | 17 | 19 | 18 | 19 | 1 | 22 | 29 | 10 | 2 | 25 | 31 | 0 | 136 | 3 | 3 | 45 | 23 | 27 | 0 | 17 | 29 | 3 | 17 | 7 | 30 | 45 | 34 | 27 | 86 | 52 | 26 | 43 | 21 | 19:50 | 252 | 216 | 132 | 228 | 204 | 372 | 156 | 204 | 228 | 216 | 228 | 12 | 264 | 348 | 120 | 24 | 300 | 372 | 0 | 1632 | 36 | 36 | 540 | 276 | 324 | 0 | 204 | 348 | 36 | 204 | 84 | 360 | 540 | 408 | 324 | 1032 | 624 | 312 | 516 | 252 |  | 19:50 | 189 | 162 | 99 | 171 | 153 | 0 | 279 | 117 | 153 | 171 | 162 | 0 | 171 | 9 | 198 | 261 | 90 | 0 | 18 | 225 | 279 | 0 | 937.5 | 0 | 27 | 27 | 405 | 207 | 243 | 0 | 0 | 153 | 261 | 27 | 153 | 0 | 63 | 270 | 405 | 306 | 243 | 0 | 774 | 468 | 234 | 387 | 189 | 11964 | 8686.5 | 23928 | 17373 | 23.928 | 17.373
19:55 | 19 | 19 | 10 | 22 | 21 | 24 | 13 | 18 | 18 | 17 | 19 | 2 | 22 | 25 | 9 | 1 | 22 | 23 | 0 | 23 | 3 | 2 | 165 | 24 | 27 | 0 | 11 | 28 | 3 | 17 | 6 | 25 | 45 | 34 | 33 | 41 | 56 | 26 | 39 | 20 | 19:55 | 228 | 228 | 120 | 264 | 252 | 288 | 156 | 216 | 216 | 204 | 228 | 24 | 264 | 300 | 108 | 12 | 264 | 276 | 0 | 276 | 36 | 24 | 1980 | 288 | 324 | 0 | 132 | 336 | 36 | 204 | 72 | 300 | 540 | 408 | 396 | 492 | 672 | 312 | 468 | 240 |  | 19:55 | 171 | 171 | 90 | 198 | 189 | 0 | 216 | 117 | 162 | 162 | 153 | 0 | 171 | 18 | 198 | 225 | 81 | 0 | 9 | 198 | 207 | 0 | 207 | 0 | 27 | 18 | 937.5 | 216 | 243 | 0 | 0 | 99 | 252 | 27 | 153 | 0 | 54 | 225 | 405 | 306 | 297 | 0 | 369 | 504 | 234 | 351 | 180 | 11184 | 7840.5 | 22368 | 15681 | 22.368 | 15.681
20:00 | 14 | 24 | 9 | 23 | 22 | 30 | 12 | 17 | 18 | 18 | 20 | 2 | 22 | 19 | 10 | 7 | 20 | 24 | 0 | 23 | 3 | 3 | 56 | 32 | 27 | 1 | 10 | 27 | 2 | 17 | 7 | 25 | 45 | 35 | 33 | 20 | 68 | 25 | 38 | 18 | 20:00 | 168 | 288 | 108 | 276 | 264 | 360 | 144 | 204 | 216 | 216 | 240 | 24 | 264 | 228 | 120 | 84 | 240 | 288 | 0 | 276 | 36 | 36 | 672 | 384 | 324 | 12 | 120 | 324 | 24 | 204 | 84 | 300 | 540 | 420 | 396 | 240 | 816 | 300 | 456 | 216 |  | 20:00 | 126 | 216 | 81 | 207 | 198 | 0 | 270 | 108 | 153 | 162 | 162 | 0 | 180 | 18 | 198 | 171 | 90 | 0 | 63 | 180 | 216 | 0 | 207 | 0 | 27 | 27 | 504 | 288 | 243 | 0 | 9 | 90 | 243 | 18 | 153 | 0 | 63 | 225 | 405 | 315 | 297 | 0 | 180 | 612 | 225 | 342 | 162 | 9912 | 7434 | 19824 | 14868 | 19.824 | 14.868
20:05 | 20 | 28 | 9 | 21 | 25 | 33 | 22 | 18 | 19 | 18 | 20 | 1 | 22 | 19 | 9 | 11 | 21 | 27 | 0 | 23 | 3 | 3 | 68 | 32 | 33 | 0 | 10 | 27 | 3 | 17 | 6 | 25 | 45 | 34 | 32 | 17 | 72 | 21 | 69 | 24 | 20:05 | 240 | 336 | 108 | 252 | 300 | 396 | 264 | 216 | 228 | 216 | 240 | 12 | 264 | 228 | 108 | 132 | 252 | 324 | 0 | 276 | 36 | 36 | 816 | 384 | 396 | 0 | 120 | 324 | 36 | 204 | 72 | 300 | 540 | 408 | 384 | 204 | 864 | 252 | 828 | 288 |  | 20:05 | 180 | 252 | 81 | 189 | 225 | 0 | 297 | 198 | 162 | 171 | 162 | 0 | 180 | 9 | 198 | 171 | 81 | 0 | 99 | 189 | 243 | 0 | 207 | 0 | 27 | 27 | 612 | 288 | 297 | 0 | 0 | 90 | 243 | 27 | 153 | 0 | 54 | 225 | 405 | 306 | 288 | 0 | 153 | 648 | 189 | 621 | 216 | 10884 | 8163 | 21768 | 16326 | 21.768 | 16.326
20:10 | 20 | 28 | 9 | 18 | 24 | 32 | 21 | 15 | 18 | 18 | 20 | 2 | 22 | 21 | 9 | 11 | 25 | 24 | 0 | 22 | 3 | 2 | 47 | 32 | 36 | 0 | 9 | 24 | 3 | 17 | 7 | 17 | 46 | 34 | 32 | 16 | 63 | 14 | 48 | 23 | 20:10 | 240 | 336 | 108 | 216 | 288 | 384 | 252 | 180 | 216 | 216 | 240 | 24 | 264 | 252 | 108 | 132 | 300 | 288 | 0 | 264 | 36 | 24 | 564 | 384 | 432 | 0 | 108 | 288 | 36 | 204 | 84 | 204 | 552 | 408 | 384 | 192 | 756 | 168 | 576 | 276 |  | 20:10 | 180 | 252 | 81 | 162 | 216 | 0 | 288 | 189 | 135 | 162 | 162 | 0 | 180 | 18 | 198 | 189 | 81 | 0 | 99 | 225 | 216 | 0 | 198 | 0 | 27 | 18 | 423 | 288 | 324 | 0 | 0 | 81 | 216 | 27 | 153 | 0 | 63 | 153 | 414 | 306 | 288 | 0 | 144 | 567 | 126 | 432 | 207 | 9984 | 7488 | 19968 | 14976 | 19.968 | 14.976
20:15 | 20 | 28 | 9 | 28 | 24 | 31 | 21 | 15 | 18 | 17 | 20 | 1 | 22 | 91 | 10 | 9 | 30 | 24 | 4 | 22 | 3 | 3 | 40 | 31 | 35 | 0 | 10 | 20 | 2 | 17 | 19 | 16 | 47 | 35 | 23 | 16 | 124 | 14 | 43 | 23 | 20:15 | 240 | 336 | 108 | 336 | 288 | 372 | 252 | 180 | 216 | 204 | 240 | 12 | 264 | 1092 | 120 | 108 | 360 | 288 | 48 | 264 | 36 | 36 | 480 | 372 | 420 | 0 | 120 | 240 | 24 | 204 | 228 | 192 | 564 | 420 | 276 | 192 | 1488 | 168 | 516 | 276 |  | 20:15 | 180 | 252 | 81 | 252 | 216 | 0 | 279 | 189 | 135 | 162 | 153 | 0 | 180 | 9 | 198 | 819 | 90 | 0 | 81 | 270 | 216 | 36 | 198 | 0 | 27 | 27 | 360 | 279 | 315 | 0 | 0 | 90 | 180 | 18 | 153 | 0 | 171 | 144 | 423 | 315 | 207 | 0 | 144 | 937.5 | 126 | 387 | 207 | 11580 | 8506.5 | 23160 | 17013 | 23.16 | 17.013
20:20 | 20 | 26 | 9 | 179 | 30 | 32 | 21 | 15 | 18 | 18 | 27 | 1 | 23 | 97 | 9 | 20 | 29 | 24 | 10 | 21 | 3 | 3 | 42 | 30 | 35 | 0 | 10 | 20 | 3 | 17 | 19 | 15 | 36 | 34 | 22 | 16 | 47 | 15 | 38 | 22 | 20:20 | 240 | 312 | 108 | 2148 | 360 | 384 | 252 | 180 | 216 | 216 | 324 | 12 | 276 | 1164 | 108 | 240 | 348 | 288 | 120 | 252 | 36 | 36 | 504 | 360 | 420 | 0 | 120 | 240 | 36 | 204 | 228 | 180 | 432 | 408 | 264 | 192 | 564 | 180 | 456 | 264 |  | 20:20 | 180 | 234 | 81 | 937.5 | 270 | 0 | 288 | 189 | 135 | 162 | 162 | 0 | 243 | 9 | 207 | 873 | 81 | 0 | 180 | 261 | 216 | 90 | 189 | 0 | 27 | 27 | 378 | 270 | 315 | 0 | 0 | 90 | 180 | 27 | 153 | 0 | 171 | 135 | 324 | 306 | 198 | 0 | 144 | 423 | 135 | 342 | 198 | 12672 | 8830.5 | 25344 | 17661 | 25.344 | 17.661
20:25 | 20 | 23 | 8 | 54 | 33 | 31 | 20 | 15 | 17 | 25 | 28 | 2 | 22 | 12 | 6 | 40 | 29 | 24 | 10 | 22 | 3 | 3 | 41 | 31 | 35 | 1 | 10 | 20 | 3 | 17 | 18 | 16 | 33 | 34 | 22 | 16 | 50 | 14 | 30 | 23 | 20:25 | 240 | 276 | 96 | 648 | 396 | 372 | 240 | 180 | 204 | 300 | 336 | 24 | 264 | 144 | 72 | 480 | 348 | 288 | 120 | 264 | 36 | 36 | 492 | 372 | 420 | 12 | 120 | 240 | 36 | 204 | 216 | 192 | 396 | 408 | 264 | 192 | 600 | 168 | 360 | 276 |  | 20:25 | 180 | 207 | 72 | 486 | 297 | 0 | 279 | 180 | 135 | 153 | 225 | 0 | 252 | 18 | 198 | 108 | 54 | 0 | 360 | 261 | 216 | 90 | 198 | 0 | 27 | 27 | 369 | 279 | 315 | 0 | 9 | 90 | 180 | 27 | 153 | 0 | 162 | 144 | 297 | 306 | 198 | 0 | 144 | 450 | 126 | 270 | 207 | 10332 | 7749 | 20664 | 15498 | 20.664 | 15.498
20:30 | 20 | 22 | 9 | 40 | 32 | 32 | 30 | 15 | 17 | 34 | 28 | 2 | 23 | 10 | 1 | 50 | 29 | 24 | 9 | 60 | 15 | 2 | 33 | 30 | 34 | 0 | 10 | 21 | 3 | 17 | 18 | 26 | 31 | 29 | 22 | 19 | 57 | 14 | 27 | 12 | 20:30 | 240 | 264 | 108 | 480 | 384 | 384 | 360 | 180 | 204 | 408 | 336 | 24 | 276 | 120 | 12 | 600 | 348 | 288 | 108 | 720 | 180 | 24 | 396 | 360 | 408 | 0 | 120 | 252 | 36 | 204 | 216 | 312 | 372 | 348 | 264 | 228 | 684 | 168 | 324 | 144 |  | 20:30 | 180 | 198 | 81 | 360 | 288 | 0 | 288 | 270 | 135 | 153 | 306 | 0 | 252 | 18 | 207 | 90 | 9 | 0 | 450 | 261 | 216 | 81 | 540 | 0 | 135 | 18 | 297 | 270 | 306 | 0 | 0 | 90 | 189 | 27 | 153 | 0 | 162 | 234 | 279 | 261 | 198 | 0 | 171 | 513 | 126 | 243 | 108 | 10884 | 8163 | 21768 | 16326 | 21.768 | 16.326
20:35 | 20 | 22 | 3 | 37 | 32 | 31 | 29 | 15 | 10 | 35 | 27 | 1 | 22 | 15 | 2 | 50 | 28 | 24 | 9 | 22 | 21 | 3 | 23 | 30 | 35 | 1 | 10 | 20 | 2 | 17 | 17 | 27 | 24 | 24 | 22 | 28 | 26 | 18 | 27 | 12 | 20:35 | 240 | 264 | 36 | 444 | 384 | 372 | 348 | 180 | 120 | 420 | 324 | 12 | 264 | 180 | 24 | 600 | 336 | 288 | 108 | 264 | 252 | 36 | 276 | 360 | 420 | 12 | 120 | 240 | 24 | 204 | 204 | 324 | 288 | 288 | 264 | 336 | 312 | 216 | 324 | 144 |  | 20:35 | 180 | 198 | 27 | 333 | 288 | 0 | 279 | 261 | 135 | 90 | 315 | 0 | 243 | 9 | 198 | 135 | 18 | 0 | 450 | 252 | 216 | 81 | 198 | 0 | 189 | 27 | 207 | 270 | 315 | 0 | 9 | 90 | 180 | 18 | 153 | 0 | 153 | 243 | 216 | 216 | 198 | 0 | 252 | 234 | 162 | 243 | 108 | 9852 | 7389 | 19704 | 14778 | 19.704 | 14.778
20:40 | 20 | 22 | 0 | 31 | 32 | 31 | 29 | 23 | 11 | 34 | 27 | 2 | 22 | 19 | 2 | 49 | 29 | 25 | 9 | 21 | 25 | 3 | 19 | 23 | 34 | 12 | 10 | 20 | 12 | 17 | 10 | 26 | 24 | 26 | 27 | 28 | 26 | 26 | 27 | 12 | 20:40 | 240 | 264 | 0 | 372 | 384 | 372 | 348 | 276 | 132 | 408 | 324 | 24 | 264 | 228 | 24 | 588 | 348 | 300 | 108 | 252 | 300 | 36 | 228 | 276 | 408 | 144 | 120 | 240 | 144 | 204 | 120 | 312 | 288 | 312 | 324 | 336 | 312 | 312 | 324 | 144 |  | 20:40 | 180 | 198 | 0 | 279 | 288 | 0 | 279 | 261 | 207 | 99 | 306 | 0 | 243 | 18 | 198 | 171 | 18 | 0 | 441 | 261 | 225 | 81 | 189 | 0 | 225 | 27 | 171 | 207 | 306 | 0 | 108 | 90 | 180 | 108 | 153 | 0 | 90 | 234 | 216 | 234 | 243 | 0 | 252 | 234 | 234 | 243 | 108 | 10140 | 7605 | 20280 | 15210 | 20.28 | 15.21
20:45 | 20 | 22 | 0 | 31 | 32 | 29 | 28 | 24 | 11 | 35 | 27 | 9 | 22 | 19 | 2 | 49 | 29 | 24 | 8 | 22 | 17 | 9 | 18 | 24 | 29 | 10 | 10 | 20 | 12 | 17 | 7 | 27 | 22 | 26 | 28 | 27 | 37 | 26 | 27 | 11 | 20:45 | 240 | 264 | 0 | 372 | 384 | 348 | 336 | 288 | 132 | 420 | 324 | 108 | 264 | 228 | 24 | 588 | 348 | 288 | 96 | 264 | 204 | 108 | 216 | 288 | 348 | 120 | 120 | 240 | 144 | 204 | 84 | 324 | 264 | 312 | 336 | 324 | 444 | 312 | 324 | 132 |  | 20:45 | 180 | 198 | 0 | 279 | 288 | 0 | 261 | 252 | 216 | 99 | 315 | 0 | 243 | 81 | 198 | 171 | 18 | 0 | 441 | 261 | 216 | 72 | 198 | 0 | 153 | 81 | 162 | 216 | 261 | 0 | 90 | 90 | 180 | 108 | 153 | 0 | 63 | 243 | 198 | 234 | 252 | 0 | 243 | 333 | 234 | 243 | 99 | 10164 | 7623 | 20328 | 15246 | 20.328 | 15.246
20:50 | 20 | 22 | 0 | 34 | 31 | 24 | 28 | 23 | 10 | 35 | 26 | 69 | 20 | 17 | 1 | 45 | 29 | 31 | 8 | 22 | 21 | 92 | 18 | 23 | 26 | 10 | 10 | 20 | 11 | 17 | 7 | 26 | 17 | 25 | 27 | 26 | 37 | 25 | 27 | 12 | 20:50 | 240 | 264 | 0 | 408 | 372 | 288 | 336 | 276 | 120 | 420 | 312 | 828 | 240 | 204 | 12 | 540 | 348 | 372 | 96 | 264 | 252 | 1104 | 216 | 276 | 312 | 120 | 120 | 240 | 132 | 204 | 84 | 312 | 204 | 300 | 324 | 312 | 444 | 300 | 324 | 144 |  | 20:50 | 180 | 198 | 0 | 306 | 279 | 0 | 216 | 252 | 207 | 90 | 315 | 0 | 234 | 621 | 180 | 153 | 9 | 0 | 405 | 261 | 279 | 72 | 198 | 0 | 189 | 828 | 162 | 207 | 234 | 0 | 90 | 90 | 180 | 99 | 153 | 0 | 63 | 234 | 153 | 225 | 243 | 0 | 234 | 333 | 225 | 243 | 108 | 11664 | 8748 | 23328 | 17496 | 23.328 | 17.496
20:55 | 24 | 22 | 0 | 35 | 32 | 23 | 28 | 23 | 11 | 35 | 26 | 48 | 15 | 17 | 2 | 69 | 24 | 33 | 9 | 21 | 25 | 108 | 17 | 23 | 26 | 9 | 10 | 20 | 11 | 17 | 6 | 26 | 17 | 99 | 27 | 27 | 36 | 25 | 33 | 18 | 20:55 | 288 | 264 | 0 | 420 | 384 | 276 | 336 | 276 | 132 | 420 | 312 | 576 | 180 | 204 | 24 | 828 | 288 | 396 | 108 | 252 | 300 | 1296 | 204 | 276 | 312 | 108 | 120 | 240 | 132 | 204 | 72 | 312 | 204 | 1188 | 324 | 324 | 432 | 300 | 396 | 216 |  | 20:55 | 216 | 198 | 0 | 315 | 288 | 0 | 207 | 252 | 207 | 99 | 315 | 0 | 234 | 432 | 135 | 153 | 18 | 0 | 621 | 216 | 297 | 81 | 189 | 0 | 225 | 937.5 | 153 | 207 | 234 | 0 | 81 | 90 | 180 | 99 | 153 | 0 | 54 | 234 | 153 | 891 | 243 | 0 | 243 | 324 | 225 | 297 | 162 | 12924 | 9658.5 | 25848 | 19317 | 25.848 | 19.317
21:00 | 28 | 22 | 0 | 35 | 31 | 23 | 28 | 23 | 11 | 29 | 27 | 27 | 15 | 19 | 2 | 87 | 22 | 33 | 4 | 22 | 28 | 82 | 17 | 24 | 26 | 10 | 9 | 20 | 10 | 18 | 7 | 16 | 18 | 30 | 26 | 20 | 36 | 21 | 39 | 23 | 21:00 | 336 | 264 | 0 | 420 | 372 | 276 | 336 | 276 | 132 | 348 | 324 | 324 | 180 | 228 | 24 | 1044 | 264 | 396 | 48 | 264 | 336 | 984 | 204 | 288 | 312 | 120 | 108 | 240 | 120 | 216 | 84 | 192 | 216 | 360 | 312 | 240 | 432 | 252 | 468 | 276 |  | 21:00 | 252 | 198 | 0 | 315 | 279 | 0 | 207 | 252 | 207 | 99 | 261 | 0 | 243 | 243 | 135 | 171 | 18 | 0 | 783 | 198 | 297 | 36 | 198 | 0 | 252 | 738 | 153 | 216 | 234 | 0 | 90 | 81 | 180 | 90 | 162 | 0 | 63 | 144 | 162 | 270 | 234 | 0 | 180 | 324 | 189 | 351 | 207 | 11616 | 8712 | 23232 | 17424 | 23.232 | 17.424
21:05 | 29 | 22 | 0 | 35 | 37 | 25 | 28 | 83 | 10 | 26 | 26 | 35 | 15 | 17 | 2 | 31 | 22 | 32 | 0 | 22 | 32 | 23 | 17 | 24 | 27 | 8 | 10 | 20 | 10 | 20 | 7 | 16 | 17 | 32 | 26 | 16 | 36 | 14 | 39 | 23 | 21:05 | 348 | 264 | 0 | 420 | 444 | 300 | 336 | 996 | 120 | 312 | 312 | 420 | 180 | 204 | 24 | 372 | 264 | 384 | 0 | 264 | 384 | 276 | 204 | 288 | 324 | 96 | 120 | 240 | 120 | 240 | 84 | 192 | 204 | 384 | 312 | 192 | 432 | 168 | 468 | 276 |  | 21:05 | 261 | 198 | 0 | 315 | 333 | 0 | 225 | 252 | 747 | 90 | 234 | 0 | 234 | 315 | 135 | 153 | 18 | 0 | 279 | 198 | 288 | 0 | 198 | 0 | 288 | 207 | 153 | 216 | 243 | 0 | 72 | 90 | 180 | 90 | 180 | 0 | 63 | 144 | 153 | 288 | 234 | 0 | 144 | 324 | 126 | 351 | 207 | 10968 | 8226 | 21936 | 16452 | 21.936 | 16.452
21:10 | 24 | 22 | 0 | 34 | 32 | 24 | 28 | 29 | 11 | 26 | 23 | 34 | 15 | 18 | 1 | 20 | 23 | 32 | 0 | 19 | 32 | 22 | 23 | 23 | 26 | 9 | 10 | 20 | 10 | 20 | 7 | 16 | 28 | 32 | 32 | 20 | 28 | 15 | 39 | 23 | 21:10 | 288 | 264 | 0 | 408 | 384 | 288 | 336 | 348 | 132 | 312 | 276 | 408 | 180 | 216 | 12 | 240 | 276 | 384 | 0 | 228 | 384 | 264 | 276 | 276 | 312 | 108 | 120 | 240 | 120 | 240 | 84 | 192 | 336 | 384 | 384 | 240 | 336 | 180 | 468 | 276 |  | 21:10 | 216 | 198 | 0 | 306 | 288 | 0 | 216 | 252 | 261 | 99 | 234 | 0 | 207 | 306 | 135 | 162 | 9 | 0 | 180 | 207 | 288 | 0 | 171 | 0 | 288 | 198 | 207 | 207 | 234 | 0 | 81 | 90 | 180 | 90 | 180 | 0 | 63 | 144 | 252 | 288 | 288 | 0 | 180 | 252 | 135 | 351 | 207 | 10200 | 7650 | 20400 | 15300 | 20.4 | 15.3
21:15 | 22 | 22 | 0 | 34 | 29 | 24 | 27 | 23 | 10 | 26 | 19 | 31 | 16 | 17 | 2 | 21 | 23 | 31 | 0 | 15 | 16 | 23 | 22 | 24 | 27 | 4 | 10 | 20 | 10 | 21 | 7 | 77 | 35 | 32 | 25 | 25 | 95 | 13 | 36 | 22 | 21:15 | 264 | 264 | 0 | 408 | 348 | 288 | 324 | 276 | 120 | 312 | 228 | 372 | 192 | 204 | 24 | 252 | 276 | 372 | 0 | 180 | 192 | 276 | 264 | 288 | 324 | 48 | 120 | 240 | 120 | 252 | 84 | 924 | 420 | 384 | 300 | 300 | 1140 | 156 | 432 | 264 |  | 21:15 | 198 | 198 | 0 | 306 | 261 | 0 | 216 | 243 | 207 | 90 | 234 | 0 | 171 | 279 | 144 | 153 | 18 | 0 | 189 | 207 | 279 | 0 | 135 | 0 | 144 | 207 | 198 | 216 | 243 | 0 | 36 | 90 | 180 | 90 | 189 | 0 | 63 | 693 | 315 | 288 | 225 | 0 | 225 | 855 | 117 | 324 | 198 | 11232 | 8424 | 22464 | 16848 | 22.464 | 16.848
21:20 | 22 | 22 | 0 | 35 | 25 | 24 | 26 | 23 | 11 | 24 | 19 | 31 | 15 | 19 | 2 | 21 | 22 | 31 | 0 | 15 | 15 | 22 | 19 | 23 | 26 | 0 | 10 | 20 | 4 | 20 | 11 | 56 | 35 | 31 | 24 | 24 | 20 | 13 | 36 | 22 | 21:20 | 264 | 264 | 0 | 420 | 300 | 288 | 312 | 276 | 132 | 288 | 228 | 372 | 180 | 228 | 24 | 252 | 264 | 372 | 0 | 180 | 180 | 264 | 228 | 276 | 312 | 0 | 120 | 240 | 48 | 240 | 132 | 672 | 420 | 372 | 288 | 288 | 240 | 156 | 432 | 264 |  | 21:20 | 198 | 198 | 0 | 315 | 225 | 0 | 216 | 234 | 207 | 99 | 216 | 0 | 171 | 279 | 135 | 171 | 18 | 0 | 189 | 198 | 279 | 0 | 135 | 0 | 135 | 198 | 171 | 207 | 234 | 0 | 0 | 90 | 180 | 36 | 180 | 0 | 99 | 504 | 315 | 279 | 216 | 0 | 216 | 180 | 117 | 324 | 198 | 9816 | 7362 | 19632 | 14724 | 19.632 | 14.724
21:25 | 22 | 22 | 0 | 35 | 24 | 24 | 21 | 15 | 11 | 18 | 18 | 32 | 15 | 17 | 1 | 20 | 23 | 32 | 0 | 15 | 15 | 22 | 14 | 23 | 26 | 0 | 9 | 20 | 3 | 20 | 19 | 16 | 34 | 31 | 25 | 24 | 15 | 14 | 73 | 14 | 21:25 | 264 | 264 | 0 | 420 | 288 | 288 | 252 | 180 | 132 | 216 | 216 | 384 | 180 | 204 | 12 | 240 | 276 | 384 | 0 | 180 | 180 | 264 | 168 | 276 | 312 | 0 | 108 | 240 | 36 | 240 | 228 | 192 | 408 | 372 | 300 | 288 | 180 | 168 | 876 | 168 |  | 21:25 | 198 | 198 | 0 | 315 | 216 | 0 | 216 | 189 | 135 | 99 | 162 | 0 | 162 | 288 | 135 | 153 | 9 | 0 | 180 | 207 | 288 | 0 | 135 | 0 | 135 | 198 | 126 | 207 | 234 | 0 | 0 | 81 | 180 | 27 | 180 | 0 | 171 | 144 | 306 | 279 | 225 | 0 | 216 | 135 | 126 | 657 | 126 | 9384 | 7038 | 18768 | 14076 | 18.768 | 14.076
21:30 | 22 | 22 | 0 | 29 | 24 | 24 | 21 | 15 | 11 | 19 | 18 | 31 | 16 | 17 | 1 | 21 | 22 | 32 | 0 | 15 | 15 | 20 | 15 | 24 | 26 | 0 | 9 | 20 | 2 | 20 | 18 | 26 | 35 | 67 | 24 | 24 | 16 | 16 | 82 | 11 | 21:30 | 264 | 264 | 0 | 348 | 288 | 288 | 252 | 180 | 132 | 228 | 216 | 372 | 192 | 204 | 12 | 252 | 264 | 384 | 0 | 180 | 180 | 240 | 180 | 288 | 312 | 0 | 108 | 240 | 24 | 240 | 216 | 312 | 420 | 804 | 288 | 288 | 192 | 192 | 984 | 132 |  | 21:30 | 198 | 198 | 0 | 261 | 216 | 0 | 216 | 189 | 135 | 99 | 171 | 0 | 162 | 279 | 144 | 153 | 9 | 0 | 189 | 198 | 288 | 0 | 135 | 0 | 135 | 180 | 135 | 216 | 234 | 0 | 0 | 81 | 180 | 18 | 180 | 0 | 162 | 234 | 315 | 603 | 216 | 0 | 216 | 144 | 144 | 738 | 99 | 9960 | 7470 | 19920 | 14940 | 19.92 | 14.94
21:35 | 22 | 23 | 0 | 29 | 24 | 24 | 20 | 15 | 11 | 19 | 19 | 32 | 15 | 18 | 2 | 20 | 22 | 27 | 0 | 14 | 15 | 15 | 15 | 23 | 26 | 0 | 10 | 20 | 2 | 21 | 18 | 27 | 34 | 32 | 25 | 34 | 19 | 26 | 87 | 12 | 21:35 | 264 | 276 | 0 | 348 | 288 | 288 | 240 | 180 | 132 | 228 | 228 | 384 | 180 | 216 | 24 | 240 | 264 | 324 | 0 | 168 | 180 | 180 | 180 | 276 | 312 | 0 | 120 | 240 | 24 | 252 | 216 | 324 | 408 | 384 | 300 | 408 | 228 | 312 | 1044 | 144 |  | 21:35 | 198 | 207 | 0 | 261 | 216 | 0 | 216 | 180 | 135 | 99 | 171 | 0 | 171 | 288 | 135 | 162 | 18 | 0 | 180 | 198 | 243 | 0 | 126 | 0 | 135 | 135 | 135 | 207 | 234 | 0 | 0 | 90 | 180 | 18 | 189 | 0 | 162 | 243 | 306 | 288 | 225 | 0 | 306 | 171 | 234 | 783 | 108 | 9804 | 7353 | 19608 | 14706 | 19.608 | 14.706
21:40 | 14 | 22 | 0 | 28 | 24 | 24 | 21 | 15 | 10 | 22 | 19 | 32 | 20 | 18 | 2 | 21 | 22 | 24 | 0 | 15 | 14 | 14 | 15 | 24 | 26 | 0 | 13 | 20 | 3 | 21 | 17 | 28 | 33 | 30 | 31 | 36 | 28 | 26 | 81 | 12 | 21:40 | 168 | 264 | 0 | 336 | 288 | 288 | 252 | 180 | 120 | 264 | 228 | 384 | 240 | 216 | 24 | 252 | 264 | 288 | 0 | 180 | 168 | 168 | 180 | 288 | 312 | 0 | 156 | 240 | 36 | 252 | 204 | 336 | 396 | 360 | 372 | 432 | 336 | 312 | 972 | 144 |  | 21:40 | 126 | 198 | 0 | 252 | 216 | 0 | 216 | 189 | 135 | 90 | 198 | 0 | 171 | 288 | 180 | 162 | 18 | 0 | 189 | 198 | 216 | 0 | 135 | 0 | 126 | 126 | 135 | 216 | 234 | 0 | 0 | 117 | 180 | 27 | 189 | 0 | 153 | 252 | 297 | 270 | 279 | 0 | 324 | 252 | 234 | 729 | 108 | 9900 | 7425 | 19800 | 14850 | 19.8 | 14.85
21:45 | 15 | 23 | 7 | 28 | 24 | 24 | 21 | 15 | 11 | 20 | 20 | 28 | 24 | 18 | 1 | 21 | 22 | 24 | 0 | 15 | 23 | 15 | 14 | 23 | 27 | 0 | 19 | 20 | 2 | 20 | 16 | 27 | 24 | 31 | 27 | 36 | 20 | 25 | 30 | 12 | 21:45 | 180 | 276 | 84 | 336 | 288 | 288 | 252 | 180 | 132 | 240 | 240 | 336 | 288 | 216 | 12 | 252 | 264 | 288 | 0 | 180 | 276 | 180 | 168 | 276 | 324 | 0 | 228 | 240 | 24 | 240 | 192 | 324 | 288 | 372 | 324 | 432 | 240 | 300 | 360 | 144 |  | 21:45 | 135 | 207 | 63 | 252 | 216 | 0 | 216 | 189 | 135 | 99 | 180 | 0 | 180 | 252 | 216 | 162 | 9 | 0 | 189 | 198 | 216 | 0 | 135 | 0 | 207 | 135 | 126 | 207 | 243 | 0 | 0 | 171 | 180 | 18 | 180 | 0 | 144 | 243 | 216 | 279 | 243 | 0 | 324 | 180 | 225 | 270 | 108 | 9264 | 6948 | 18528 | 13896 | 18.528 | 13.896
21:50 | 15 | 22 | 10 | 28 | 24 | 25 | 21 | 15 | 10 | 19 | 19 | 24 | 23 | 17 | 2 | 27 | 20 | 25 | 0 | 15 | 23 | 15 | 13 | 24 | 27 | 0 | 18 | 20 | 2 | 20 | 7 | 27 | 24 | 30 | 27 | 35 | 19 | 25 | 30 | 11 | 21:50 | 180 | 264 | 120 | 336 | 288 | 300 | 252 | 180 | 120 | 228 | 228 | 288 | 276 | 204 | 24 | 324 | 240 | 300 | 0 | 180 | 276 | 180 | 156 | 288 | 324 | 0 | 216 | 240 | 24 | 240 | 84 | 324 | 288 | 360 | 324 | 420 | 228 | 300 | 360 | 132 |  | 21:50 | 135 | 198 | 90 | 252 | 216 | 0 | 225 | 189 | 135 | 90 | 171 | 0 | 171 | 216 | 207 | 153 | 18 | 0 | 243 | 180 | 225 | 0 | 135 | 0 | 207 | 135 | 117 | 216 | 243 | 0 | 0 | 162 | 180 | 18 | 180 | 0 | 63 | 243 | 216 | 270 | 243 | 0 | 315 | 171 | 225 | 270 | 99 | 9096 | 6822 | 18192 | 13644 | 18.192 | 13.644
21:55 | 15 | 22 | 25 | 28 | 24 | 24 | 21 | 15 | 11 | 19 | 20 | 24 | 22 | 17 | 11 | 29 | 21 | 24 | 0 | 14 | 22 | 14 | 9 | 24 | 26 | 0 | 17 | 20 | 3 | 19 | 7 | 27 | 24 | 53 | 25 | 34 | 18 | 21 | 58 | 23 | 21:55 | 180 | 264 | 300 | 336 | 288 | 288 | 252 | 180 | 132 | 228 | 240 | 288 | 264 | 204 | 132 | 348 | 252 | 288 | 0 | 168 | 264 | 168 | 108 | 288 | 312 | 0 | 204 | 240 | 36 | 228 | 84 | 324 | 288 | 636 | 300 | 408 | 216 | 252 | 696 | 276 |  | 21:55 | 135 | 198 | 225 | 252 | 216 | 0 | 216 | 189 | 135 | 99 | 171 | 0 | 180 | 216 | 198 | 153 | 99 | 0 | 261 | 189 | 216 | 0 | 126 | 0 | 198 | 126 | 81 | 216 | 234 | 0 | 0 | 153 | 180 | 27 | 171 | 0 | 63 | 243 | 216 | 477 | 225 | 0 | 306 | 162 | 189 | 522 | 207 | 9960 | 7470 | 19920 | 14940 | 19.92 | 14.94
22:00 | 15 | 19 | 117 | 28 | 24 | 24 | 20 | 15 | 20 | 19 | 20 | 24 | 23 | 24 | 10 | 29 | 20 | 25 | 0 | 17 | 22 | 15 | 11 | 24 | 27 | 0 | 17 | 29 | 2 | 19 | 7 | 27 | 25 | 63 | 27 | 16 | 13 | 14 | 23 | 23 | 22:00 | 180 | 228 | 1404 | 336 | 288 | 288 | 240 | 180 | 240 | 228 | 240 | 288 | 276 | 288 | 120 | 348 | 240 | 300 | 0 | 204 | 264 | 180 | 132 | 288 | 324 | 0 | 204 | 348 | 24 | 228 | 84 | 324 | 300 | 756 | 324 | 192 | 156 | 168 | 276 | 276 |  | 22:00 | 135 | 171 | 937.5 | 252 | 216 | 0 | 216 | 180 | 135 | 180 | 171 | 0 | 180 | 216 | 207 | 216 | 90 | 0 | 261 | 180 | 225 | 0 | 153 | 0 | 198 | 135 | 99 | 216 | 243 | 0 | 0 | 153 | 261 | 18 | 171 | 0 | 63 | 243 | 225 | 567 | 243 | 0 | 144 | 117 | 126 | 207 | 207 | 10764 | 7957.5 | 21528 | 15915 | 21.528 | 15.915
22:05 | 15 | 14 | 28 | 28 | 24 | 24 | 21 | 15 | 19 | 11 | 19 | 24 | 22 | 29 | 10 | 28 | 21 | 25 | 0 | 15 | 22 | 66 | 9 | 24 | 27 | 0 | 17 | 28 | 3 | 20 | 7 | 21 | 24 | 25 | 24 | 16 | 8 | 14 | 19 | 22 | 22:05 | 180 | 168 | 336 | 336 | 288 | 288 | 252 | 180 | 228 | 132 | 228 | 288 | 264 | 348 | 120 | 336 | 252 | 300 | 0 | 180 | 264 | 792 | 108 | 288 | 324 | 0 | 204 | 336 | 36 | 240 | 84 | 252 | 288 | 300 | 288 | 192 | 96 | 168 | 228 | 264 |  | 22:05 | 135 | 126 | 252 | 252 | 216 | 0 | 216 | 189 | 135 | 171 | 99 | 0 | 171 | 216 | 198 | 261 | 90 | 0 | 252 | 189 | 225 | 0 | 135 | 0 | 198 | 594 | 81 | 216 | 243 | 0 | 0 | 153 | 252 | 27 | 180 | 0 | 63 | 189 | 216 | 225 | 216 | 0 | 144 | 72 | 126 | 171 | 198 | 9456 | 7092 | 18912 | 14184 | 18.912 | 14.184
22:10 | 15 | 15 | 28 | 22 | 24 | 32 | 21 | 15 | 19 | 13 | 19 | 24 | 23 | 22 | 10 | 29 | 21 | 24 | 0 | 15 | 23 | 74 | 9 | 24 | 27 | 0 | 18 | 29 | 2 | 82 | 6 | 16 | 50 | 24 | 16 | 15 | 7 | 14 | 19 | 23 | 22:10 | 180 | 180 | 336 | 264 | 288 | 384 | 252 | 180 | 228 | 156 | 228 | 288 | 276 | 264 | 120 | 348 | 252 | 288 | 0 | 180 | 276 | 888 | 108 | 288 | 324 | 0 | 216 | 348 | 24 | 984 | 72 | 192 | 600 | 288 | 192 | 180 | 84 | 168 | 228 | 276 |  | 22:10 | 135 | 135 | 252 | 198 | 216 | 0 | 288 | 189 | 135 | 171 | 117 | 0 | 171 | 216 | 207 | 198 | 90 | 0 | 261 | 189 | 216 | 0 | 135 | 0 | 207 | 666 | 81 | 216 | 243 | 0 | 0 | 162 | 261 | 18 | 738 | 0 | 54 | 144 | 450 | 216 | 144 | 0 | 135 | 63 | 126 | 171 | 207 | 10428 | 7821 | 20856 | 15642 | 20.856 | 15.642
22:15 | 15 | 14 | 27 | 22 | 23 | 32 | 20 | 16 | 18 | 11 | 20 | 24 | 22 | 20 | 9 | 35 | 28 | 24 | 0 | 25 | 22 | 14 | 9 | 23 | 26 | 0 | 17 | 28 | 2 | 51 | 7 | 16 | 59 | 24 | 16 | 15 | 4 | 14 | 18 | 23 | 22:15 | 180 | 168 | 324 | 264 | 276 | 384 | 240 | 192 | 216 | 132 | 240 | 288 | 264 | 240 | 108 | 420 | 336 | 288 | 0 | 300 | 264 | 168 | 108 | 276 | 312 | 0 | 204 | 336 | 24 | 612 | 84 | 192 | 708 | 288 | 192 | 180 | 48 | 168 | 216 | 276 |  | 22:15 | 135 | 126 | 243 | 198 | 207 | 0 | 288 | 180 | 144 | 162 | 99 | 0 | 180 | 216 | 198 | 180 | 81 | 0 | 315 | 252 | 216 | 0 | 225 | 0 | 198 | 126 | 81 | 207 | 234 | 0 | 0 | 153 | 252 | 18 | 459 | 0 | 63 | 144 | 531 | 216 | 144 | 0 | 135 | 36 | 126 | 162 | 207 | 9516 | 7137 | 19032 | 14274 | 19.032 | 14.274
22:20 | 15 | 15 | 27 | 22 | 24 | 32 | 21 | 15 | 18 | 11 | 29 | 24 | 23 | 20 | 10 | 35 | 30 | 24 | 0 | 22 | 22 | 15 | 10 | 24 | 31 | 0 | 11 | 27 | 3 | 20 | 7 | 17 | 25 | 15 | 16 | 14 | 5 | 14 | 18 | 12 | 22:20 | 180 | 180 | 324 | 264 | 288 | 384 | 252 | 180 | 216 | 132 | 348 | 288 | 276 | 240 | 120 | 420 | 360 | 288 | 0 | 264 | 264 | 180 | 120 | 288 | 372 | 0 | 132 | 324 | 36 | 240 | 84 | 204 | 300 | 180 | 192 | 168 | 60 | 168 | 216 | 144 |  | 22:20 | 135 | 135 | 243 | 198 | 216 | 0 | 288 | 189 | 135 | 162 | 99 | 0 | 261 | 216 | 207 | 180 | 90 | 0 | 315 | 270 | 216 | 0 | 198 | 0 | 198 | 135 | 90 | 216 | 279 | 0 | 0 | 99 | 243 | 27 | 180 | 0 | 63 | 153 | 225 | 135 | 144 | 0 | 126 | 45 | 126 | 162 | 108 | 8676 | 6507 | 17352 | 13014 | 17.352 | 13.014
22:25 | 14 | 14 | 27 | 21 | 30 | 32 | 20 | 15 | 18 | 17 | 29 | 24 | 22 | 20 | 9 | 28 | 29 | 24 | 0 | 23 | 21 | 15 | 9 | 33 | 36 | 0 | 14 | 27 | 2 | 20 | 7 | 17 | 26 | 32 | 15 | 13 | 5 | 17 | 18 | 11 | 22:25 | 168 | 168 | 324 | 252 | 360 | 384 | 240 | 180 | 216 | 204 | 348 | 288 | 264 | 240 | 108 | 336 | 348 | 288 | 0 | 276 | 252 | 180 | 108 | 396 | 432 | 0 | 168 | 324 | 24 | 240 | 84 | 204 | 312 | 384 | 180 | 156 | 60 | 204 | 216 | 132 |  | 22:25 | 126 | 126 | 243 | 189 | 270 | 0 | 288 | 180 | 135 | 162 | 153 | 0 | 261 | 216 | 198 | 180 | 81 | 0 | 252 | 261 | 216 | 0 | 207 | 0 | 189 | 135 | 81 | 297 | 324 | 0 | 0 | 126 | 243 | 18 | 180 | 0 | 63 | 153 | 234 | 288 | 135 | 0 | 117 | 45 | 153 | 162 | 99 | 9048 | 6786 | 18096 | 13572 | 18.096 | 13.572
22:30 | 14 | 14 | 28 | 22 | 33 | 31 | 21 | 15 | 18 | 19 | 28 | 24 | 22 | 20 | 9 | 28 | 30 | 25 | 9 | 22 | 22 | 14 | 9 | 32 | 35 | 0 | 13 | 27 | 3 | 20 | 18 | 20 | 27 | 33 | 16 | 17 | 13 | 26 | 15 | 12 | 22:30 | 168 | 168 | 336 | 264 | 396 | 372 | 252 | 180 | 216 | 228 | 336 | 288 | 264 | 240 | 108 | 336 | 360 | 300 | 108 | 264 | 264 | 168 | 108 | 384 | 420 | 0 | 156 | 324 | 36 | 240 | 216 | 240 | 324 | 396 | 192 | 204 | 156 | 312 | 180 | 144 |  | 22:30 | 126 | 126 | 252 | 198 | 297 | 0 | 279 | 189 | 135 | 162 | 171 | 0 | 252 | 216 | 198 | 180 | 81 | 0 | 252 | 270 | 225 | 81 | 198 | 0 | 198 | 126 | 81 | 288 | 315 | 0 | 0 | 117 | 243 | 27 | 180 | 0 | 162 | 180 | 243 | 297 | 144 | 0 | 153 | 117 | 234 | 135 | 108 | 9648 | 7236 | 19296 | 14472 | 19.296 | 14.472
22:35 | 16 | 15 | 20 | 26 | 32 | 31 | 20 | 15 | 18 | 20 | 28 | 24 | 17 | 20 | 2 | 24 | 30 | 28 | 10 | 22 | 22 | 15 | 9 | 32 | 35 | 0 | 74 | 20 | 2 | 21 | 19 | 59 | 26 | 35 | 27 | 24 | 17 | 26 | 9 | 12 | 22:35 | 192 | 180 | 240 | 312 | 384 | 372 | 240 | 180 | 216 | 240 | 336 | 288 | 204 | 240 | 24 | 288 | 360 | 336 | 120 | 264 | 264 | 180 | 108 | 384 | 420 | 0 | 888 | 240 | 24 | 252 | 228 | 708 | 312 | 420 | 324 | 288 | 204 | 312 | 108 | 144 |  | 22:35 | 144 | 135 | 180 | 234 | 288 | 0 | 279 | 180 | 135 | 162 | 180 | 0 | 252 | 216 | 153 | 180 | 18 | 0 | 216 | 270 | 252 | 90 | 198 | 0 | 198 | 135 | 81 | 288 | 315 | 0 | 0 | 666 | 180 | 18 | 189 | 0 | 171 | 531 | 234 | 315 | 243 | 0 | 216 | 153 | 234 | 81 | 108 | 10824 | 8118 | 21648 | 16236 | 21.648 | 16.236
22:40 | 25 | 15 | 20 | 31 | 35 | 32 | 21 | 19 | 17 | 28 | 28 | 24 | 15 | 13 | 2 | 20 | 29 | 33 | 10 | 22 | 21 | 15 | 10 | 31 | 34 | 0 | 95 | 135 | 2 | 20 | 20 | 15 | 27 | 36 | 28 | 24 | 16 | 26 | 6 | 12 | 22:40 | 300 | 180 | 240 | 372 | 420 | 384 | 252 | 228 | 204 | 336 | 336 | 288 | 180 | 156 | 24 | 240 | 348 | 396 | 120 | 264 | 252 | 180 | 120 | 372 | 408 | 0 | 1140 | 1620 | 24 | 240 | 240 | 180 | 324 | 432 | 336 | 288 | 192 | 312 | 72 | 144 |  | 22:40 | 225 | 135 | 180 | 279 | 315 | 0 | 288 | 189 | 171 | 153 | 252 | 0 | 252 | 216 | 135 | 117 | 18 | 0 | 180 | 261 | 297 | 90 | 198 | 0 | 189 | 135 | 90 | 279 | 306 | 0 | 0 | 855 | 937.5 | 18 | 180 | 0 | 180 | 135 | 243 | 324 | 252 | 0 | 216 | 144 | 234 | 54 | 108 | 12144 | 8830.5 | 24288 | 17661 | 24.288 | 17.661
22:45 | 23 | 15 | 20 | 30 | 40 | 31 | 26 | 24 | 15 | 20 | 27 | 24 | 15 | 13 | 2 | 21 | 30 | 32 | 9 | 22 | 22 | 14 | 9 | 32 | 34 | 17 | 12 | 20 | 3 | 20 | 33 | 24 | 25 | 44 | 27 | 23 | 16 | 25 | 5 | 15 | 22:45 | 276 | 180 | 240 | 360 | 480 | 372 | 312 | 288 | 180 | 240 | 324 | 288 | 180 | 156 | 24 | 252 | 360 | 384 | 108 | 264 | 264 | 168 | 108 | 384 | 408 | 204 | 144 | 240 | 36 | 240 | 396 | 288 | 300 | 528 | 324 | 276 | 192 | 300 | 60 | 180 |  | 22:45 | 207 | 135 | 180 | 270 | 360 | 0 | 279 | 234 | 216 | 135 | 180 | 0 | 243 | 216 | 135 | 117 | 18 | 0 | 189 | 270 | 288 | 81 | 198 | 0 | 198 | 126 | 81 | 288 | 306 | 0 | 153 | 108 | 180 | 27 | 180 | 0 | 297 | 216 | 225 | 396 | 243 | 0 | 207 | 144 | 225 | 45 | 135 | 10308 | 7731 | 20616 | 15462 | 20.616 | 15.462
22:50 | 23 | 15 | 20 | 30 | 40 | 32 | 29 | 24 | 10 | 18 | 28 | 24 | 15 | 15 | 2 | 21 | 29 | 31 | 9 | 22 | 22 | 15 | 9 | 31 | 34 | 25 | 13 | 20 | 2 | 19 | 31 | 26 | 19 | 44 | 27 | 24 | 14 | 20 | 4 | 23 | 22:50 | 276 | 180 | 240 | 360 | 480 | 384 | 348 | 288 | 120 | 216 | 336 | 288 | 180 | 180 | 24 | 252 | 348 | 372 | 108 | 264 | 264 | 180 | 108 | 372 | 408 | 300 | 156 | 240 | 24 | 228 | 372 | 312 | 228 | 528 | 324 | 288 | 168 | 240 | 48 | 276 |  | 22:50 | 207 | 135 | 180 | 270 | 360 | 0 | 288 | 261 | 216 | 90 | 162 | 0 | 252 | 216 | 135 | 135 | 18 | 0 | 189 | 261 | 279 | 81 | 198 | 0 | 198 | 135 | 81 | 279 | 306 | 0 | 225 | 117 | 180 | 18 | 171 | 0 | 279 | 234 | 171 | 396 | 243 | 0 | 216 | 126 | 180 | 36 | 207 | 10308 | 7731 | 20616 | 15462 | 20.616 | 15.462
22:55 | 23 | 15 | 20 | 30 | 40 | 27 | 29 | 23 | 11 | 18 | 27 | 24 | 15 | 17 | 1 | 20 | 35 | 32 | 8 | 22 | 22 | 15 | 10 | 31 | 34 | 141 | 12 | 20 | 3 | 24 | 24 | 25 | 16 | 45 | 27 | 19 | 5 | 14 | 8 | 24 | 22:55 | 276 | 180 | 240 | 360 | 480 | 324 | 348 | 276 | 132 | 216 | 324 | 288 | 180 | 204 | 12 | 240 | 420 | 384 | 96 | 264 | 264 | 180 | 120 | 372 | 408 | 1692 | 144 | 240 | 36 | 288 | 288 | 300 | 192 | 540 | 324 | 228 | 60 | 168 | 96 | 288 |  | 22:55 | 207 | 135 | 180 | 270 | 360 | 0 | 243 | 261 | 207 | 99 | 162 | 0 | 243 | 216 | 135 | 153 | 9 | 0 | 180 | 315 | 288 | 72 | 198 | 0 | 198 | 135 | 90 | 279 | 306 | 0 | 937.5 | 108 | 180 | 27 | 216 | 0 | 216 | 225 | 144 | 405 | 243 | 0 | 171 | 45 | 126 | 72 | 216 | 11472 | 8272.5 | 22944 | 16545 | 22.944 | 16.545
23:00 | 22 | 14 | 21 | 29 | 41 | 24 | 29 | 25 | 10 | 18 | 23 | 32 | 16 | 20 | 2 | 20 | 38 | 32 | 8 | 22 | 21 | 15 | 9 | 31 | 29 | 9 | 12 | 20 | 2 | 30 | 23 | 19 | 10 | 43 | 26 | 11 | 5 | 14 | 17 | 23 | 23:00 | 264 | 168 | 252 | 348 | 492 | 288 | 348 | 300 | 120 | 216 | 276 | 384 | 192 | 240 | 24 | 240 | 456 | 384 | 96 | 264 | 252 | 180 | 108 | 372 | 348 | 108 | 144 | 240 | 24 | 360 | 276 | 228 | 120 | 516 | 312 | 132 | 60 | 168 | 204 | 276 |  | 23:00 | 198 | 126 | 189 | 261 | 369 | 0 | 216 | 261 | 225 | 90 | 162 | 0 | 207 | 288 | 144 | 180 | 18 | 0 | 180 | 342 | 288 | 72 | 198 | 0 | 189 | 135 | 81 | 279 | 261 | 0 | 81 | 108 | 180 | 18 | 270 | 0 | 207 | 171 | 90 | 387 | 234 | 0 | 99 | 45 | 126 | 153 | 207 | 9780 | 7335 | 19560 | 14670 | 19.56 | 14.67
23:05 | 22 | 14 | 20 | 30 | 40 | 24 | 29 | 29 | 11 | 18 | 20 | 33 | 17 | 16 | 2 | 21 | 37 | 31 | 9 | 22 | 22 | 15 | 15 | 24 | 27 | 16 | 12 | 20 | 7 | 29 | 32 | 15 | 7 | 44 | 16 | 10 | 5 | 40 | 16 | 22 | 23:05 | 264 | 168 | 240 | 360 | 480 | 288 | 348 | 348 | 132 | 216 | 240 | 396 | 204 | 192 | 24 | 252 | 444 | 372 | 108 | 264 | 264 | 180 | 180 | 288 | 324 | 192 | 144 | 240 | 84 | 348 | 384 | 180 | 84 | 528 | 192 | 120 | 60 | 480 | 192 | 264 |  | 23:05 | 198 | 126 | 180 | 270 | 360 | 0 | 216 | 261 | 261 | 99 | 162 | 0 | 180 | 297 | 153 | 144 | 18 | 0 | 189 | 333 | 279 | 81 | 198 | 0 | 198 | 135 | 135 | 216 | 243 | 0 | 144 | 108 | 180 | 63 | 261 | 0 | 288 | 135 | 63 | 396 | 144 | 0 | 90 | 45 | 360 | 144 | 198 | 10068 | 7551 | 20136 | 15102 | 20.136 | 15.102
23:10 | 22 | 15 | 20 | 29 | 71 | 24 | 29 | 21 | 10 | 18 | 20 | 32 | 24 | 16 | 1 | 20 | 39 | 31 | 4 | 26 | 22 | 14 | 28 | 25 | 27 | 16 | 13 | 19 | 12 | 28 | 31 | 16 | 6 | 45 | 16 | 9 | 4 | 81 | 17 | 18 | 23:10 | 264 | 180 | 240 | 348 | 852 | 288 | 348 | 252 | 120 | 216 | 240 | 384 | 288 | 192 | 12 | 240 | 468 | 372 | 48 | 312 | 264 | 168 | 336 | 300 | 324 | 192 | 156 | 228 | 144 | 336 | 372 | 192 | 72 | 540 | 192 | 108 | 48 | 972 | 204 | 216 |  | 23:10 | 198 | 135 | 180 | 261 | 639 | 0 | 216 | 261 | 189 | 90 | 162 | 0 | 180 | 288 | 216 | 144 | 9 | 0 | 180 | 351 | 279 | 36 | 234 | 0 | 198 | 126 | 252 | 225 | 243 | 0 | 144 | 117 | 171 | 108 | 252 | 0 | 279 | 144 | 54 | 405 | 144 | 0 | 81 | 36 | 729 | 153 | 162 | 11028 | 8271 | 22056 | 16542 | 22.056 | 16.542
23:15 | 21 | 17 | 20 | 30 | 144 | 25 | 28 | 18 | 11 | 18 | 20 | 32 | 15 | 17 | 2 | 21 | 18 | 26 | 1 | 17 | 22 | 23 | 32 | 24 | 27 | 16 | 17 | 19 | 11 | 28 | 32 | 5 | 6 | 44 | 16 | 10 | 5 | 20 | 16 | 12 | 23:15 | 252 | 204 | 240 | 360 | 1728 | 300 | 336 | 216 | 132 | 216 | 240 | 384 | 180 | 204 | 24 | 252 | 216 | 312 | 12 | 204 | 264 | 276 | 384 | 288 | 324 | 192 | 204 | 228 | 132 | 336 | 384 | 60 | 72 | 528 | 192 | 120 | 60 | 240 | 192 | 144 |  | 23:15 | 189 | 153 | 180 | 270 | 937.5 | 0 | 225 | 252 | 162 | 99 | 162 | 0 | 180 | 288 | 135 | 153 | 18 | 0 | 189 | 162 | 234 | 9 | 153 | 0 | 198 | 207 | 288 | 216 | 243 | 0 | 144 | 153 | 171 | 99 | 252 | 0 | 288 | 45 | 54 | 396 | 144 | 0 | 90 | 45 | 180 | 144 | 108 | 10632 | 7615.5 | 21264 | 15231 | 21.264 | 15.231
23:20 | 14 | 24 | 20 | 29 | 53 | 24 | 13 | 8 | 11 | 18 | 20 | 31 | 15 | 16 | 2 | 20 | 9 | 24 | 0 | 13 | 22 | 28 | 27 | 24 | 27 | 15 | 20 | 20 | 11 | 28 | 32 | 5 | 6 | 44 | 15 | 10 | 8 | 21 | 15 | 12 | 23:20 | 168 | 288 | 240 | 348 | 636 | 288 | 156 | 96 | 132 | 216 | 240 | 372 | 180 | 192 | 24 | 240 | 108 | 288 | 0 | 156 | 264 | 336 | 324 | 288 | 324 | 180 | 240 | 240 | 132 | 336 | 384 | 60 | 72 | 528 | 180 | 120 | 96 | 252 | 180 | 144 |  | 23:20 | 126 | 216 | 180 | 261 | 477 | 0 | 216 | 117 | 72 | 99 | 162 | 0 | 180 | 279 | 135 | 144 | 18 | 0 | 180 | 81 | 216 | 0 | 117 | 0 | 198 | 252 | 243 | 216 | 243 | 0 | 135 | 180 | 180 | 99 | 252 | 0 | 288 | 45 | 54 | 396 | 135 | 0 | 90 | 72 | 189 | 135 | 108 | 9048 | 6786 | 18096 | 13572 | 18.096 | 13.572
23:25 | 15 | 23 | 20 | 29 | 31 | 24 | 9 | 6 | 10 | 17 | 19 | 31 | 16 | 16 | 2 | 20 | 9 | 24 | 0 | 7 | 21 | 23 | 11 | 24 | 27 | 14 | 21 | 19 | 11 | 28 | 29 | 5 | 13 | 42 | 17 | 7 | 18 | 23 | 10 | 11 | 23:25 | 180 | 276 | 240 | 348 | 372 | 288 | 108 | 72 | 120 | 204 | 228 | 372 | 192 | 192 | 24 | 240 | 108 | 288 | 0 | 84 | 252 | 276 | 132 | 288 | 324 | 168 | 252 | 228 | 132 | 336 | 348 | 60 | 156 | 504 | 204 | 84 | 216 | 276 | 120 | 132 |  | 23:25 | 135 | 207 | 180 | 261 | 279 | 0 | 216 | 81 | 54 | 90 | 153 | 0 | 171 | 279 | 144 | 144 | 18 | 0 | 180 | 81 | 216 | 0 | 63 | 0 | 189 | 207 | 99 | 216 | 243 | 0 | 126 | 189 | 171 | 99 | 252 | 0 | 261 | 45 | 117 | 378 | 153 | 0 | 63 | 162 | 207 | 90 | 99 | 8424 | 6318 | 16848 | 12636 | 16.848 | 12.636
23:30 | 15 | 22 | 20 | 29 | 26 | 24 | 9 | 1 | 10 | 17 | 20 | 31 | 15 | 20 | 2 | 20 | 9 | 24 | 0 | 6 | 22 | 23 | 10 | 25 | 27 | 14 | 21 | 20 | 15 | 27 | 30 | 5 | 18 | 28 | 25 | 15 | 16 | 21 | 5 | 11 | 23:30 | 180 | 264 | 240 | 348 | 312 | 288 | 108 | 12 | 120 | 204 | 240 | 372 | 180 | 240 | 24 | 240 | 108 | 288 | 0 | 72 | 264 | 276 | 120 | 300 | 324 | 168 | 252 | 240 | 180 | 324 | 360 | 60 | 216 | 336 | 300 | 180 | 192 | 252 | 60 | 132 |  | 23:30 | 135 | 198 | 180 | 261 | 234 | 0 | 216 | 81 | 9 | 90 | 153 | 0 | 180 | 279 | 135 | 180 | 18 | 0 | 180 | 81 | 216 | 0 | 54 | 0 | 198 | 207 | 90 | 225 | 243 | 0 | 126 | 189 | 180 | 135 | 243 | 0 | 270 | 45 | 162 | 252 | 225 | 0 | 135 | 144 | 189 | 45 | 99 | 8376 | 6282 | 16752 | 12564 | 16.752 | 12.564
23:35 | 15 | 22 | 24 | 24 | 23 | 24 | 2 | 0 | 11 | 18 | 19 | 31 | 23 | 25 | 1 | 20 | 9 | 10 | 0 | 3 | 22 | 22 | 10 | 24 | 27 | 14 | 20 | 20 | 17 | 28 | 40 | 5 | 18 | 9 | 28 | 16 | 17 | 21 | 4 | 12 | 23:35 | 180 | 264 | 288 | 288 | 276 | 288 | 24 | 0 | 132 | 216 | 228 | 372 | 276 | 300 | 12 | 240 | 108 | 120 | 0 | 36 | 264 | 264 | 120 | 288 | 324 | 168 | 240 | 240 | 204 | 336 | 480 | 60 | 216 | 108 | 336 | 192 | 204 | 252 | 48 | 144 |  | 23:35 | 135 | 198 | 216 | 216 | 207 | 0 | 216 | 18 | 0 | 99 | 162 | 0 | 171 | 279 | 207 | 225 | 9 | 0 | 180 | 81 | 90 | 0 | 27 | 0 | 198 | 198 | 90 | 216 | 243 | 0 | 126 | 180 | 180 | 153 | 252 | 0 | 360 | 45 | 162 | 81 | 252 | 0 | 144 | 153 | 189 | 36 | 108 | 8136 | 6102 | 16272 | 12204 | 16.272 | 12.204
23:40 | 15 | 22 | 29 | 26 | 23 | 23 | 0 | 0 | 10 | 10 | 20 | 30 | 23 | 23 | 1 | 21 | 8 | 0 | 0 | 0 | 23 | 23 | 10 | 24 | 27 | 7 | 20 | 20 | 15 | 27 | 42 | 4 | 14 | 8 | 27 | 15 | 16 | 21 | 5 | 20 | 23:40 | 180 | 264 | 348 | 312 | 276 | 276 | 0 | 0 | 120 | 120 | 240 | 360 | 276 | 276 | 12 | 252 | 96 | 0 | 0 | 0 | 276 | 276 | 120 | 288 | 324 | 84 | 240 | 240 | 180 | 324 | 504 | 48 | 168 | 96 | 324 | 180 | 192 | 252 | 60 | 240 |  | 23:40 | 135 | 198 | 261 | 234 | 207 | 0 | 207 | 0 | 0 | 90 | 90 | 0 | 180 | 270 | 207 | 207 | 9 | 0 | 189 | 72 | 0 | 0 | 0 | 0 | 207 | 207 | 90 | 216 | 243 | 0 | 63 | 180 | 180 | 135 | 243 | 0 | 378 | 36 | 126 | 72 | 243 | 0 | 135 | 144 | 189 | 45 | 180 | 7824 | 5868 | 15648 | 11736 | 15.648 | 11.736
23:45 | 15 | 23 | 28 | 16 | 24 | 23 | 0 | 0 | 10 | 10 | 20 | 27 | 23 | 23 | 0 | 20 | 8 | 0 | 0 | 0 | 19 | 22 | 10 | 24 | 27 | 7 | 20 | 20 | 11 | 27 | 41 | 5 | 15 | 8 | 27 | 14 | 9 | 13 | 5 | 24 | 23:45 | 180 | 276 | 336 | 192 | 288 | 276 | 0 | 0 | 120 | 120 | 240 | 324 | 276 | 276 | 0 | 240 | 96 | 0 | 0 | 0 | 228 | 264 | 120 | 288 | 324 | 84 | 240 | 240 | 132 | 324 | 492 | 60 | 180 | 96 | 324 | 168 | 108 | 156 | 60 | 288 |  | 23:45 | 135 | 207 | 252 | 144 | 216 | 0 | 207 | 0 | 0 | 90 | 90 | 0 | 180 | 243 | 207 | 207 | 0 | 0 | 180 | 72 | 0 | 0 | 0 | 0 | 171 | 198 | 90 | 216 | 243 | 0 | 63 | 180 | 180 | 99 | 243 | 0 | 369 | 45 | 135 | 72 | 243 | 0 | 126 | 81 | 117 | 45 | 216 | 7416 | 5562 | 14832 | 11124 | 14.832 | 11.124
23:50 | 14 | 22 | 28 | 11 | 24 | 24 | 0 | 0 | 11 | 10 | 20 | 24 | 22 | 23 | 0 | 20 | 1 | 0 | 0 | 0 | 15 | 19 | 2 | 24 | 27 | 7 | 20 | 19 | 7 | 27 | 17 | 5 | 46 | 8 | 27 | 15 | 4 | 10 | 4 | 23 | 23:50 | 168 | 264 | 336 | 132 | 288 | 288 | 0 | 0 | 132 | 120 | 240 | 288 | 264 | 276 | 0 | 240 | 12 | 0 | 0 | 0 | 180 | 228 | 24 | 288 | 324 | 84 | 240 | 228 | 84 | 324 | 204 | 60 | 552 | 96 | 324 | 180 | 48 | 120 | 48 | 276 |  | 23:50 | 126 | 198 | 252 | 99 | 216 | 0 | 216 | 0 | 0 | 99 | 90 | 0 | 180 | 216 | 198 | 207 | 0 | 0 | 180 | 9 | 0 | 0 | 0 | 0 | 135 | 171 | 18 | 216 | 243 | 0 | 63 | 180 | 171 | 63 | 243 | 0 | 153 | 45 | 414 | 72 | 243 | 0 | 135 | 36 | 90 | 36 | 207 | 6960 | 5220 | 13920 | 10440 | 13.92 | 10.44
23:55 | 15 | 22 | 28 | 7 | 23 | 24 | 0 | 0 | 10 | 10 | 19 | 23 | 22 | 23 | 0 | 21 | 0 | 0 | 0 | 0 | 15 | 19 | 3 | 23 | 27 | 7 | 20 | 20 | 7 | 27 | 17 | 17 | 58 | 7 | 21 | 7 | 5 | 10 | 11 | 23 | 23:55 | 180 | 264 | 336 | 84 | 276 | 288 | 0 | 0 | 120 | 120 | 228 | 276 | 264 | 276 | 0 | 252 | 0 | 0 | 0 | 0 | 180 | 228 | 36 | 276 | 324 | 84 | 240 | 240 | 84 | 324 | 204 | 204 | 696 | 84 | 252 | 84 | 60 | 120 | 132 | 276 |  | 23:55 | 135 | 198 | 252 | 63 | 207 | 0 | 216 | 0 | 0 | 90 | 90 | 0 | 171 | 207 | 198 | 207 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 135 | 171 | 27 | 207 | 243 | 0 | 63 | 180 | 180 | 63 | 243 | 0 | 153 | 153 | 522 | 63 | 189 | 0 | 63 | 45 | 90 | 99 | 207 | 7092 | 5319 | 14184 | 10638 | 14.184 | 10.638

## Heating Data
| Current | Insulation | Airtight | Double Glazing | Smart Control | Hour | Current | Insulation | Airtight | Double Glazing | Smart Control
00h30 | 138.7 | 116.4 | 71.97 | 57.03 | 47.13 | 00h30 | 1.7337 | 1.455 | 0.89963 | 0.71288 | 0.58913 | ESP-r results | 80 flats
01h30 | 163.67 | 142.87 | 90.5 | 75.91 | 65.18 | 01h30 | 2.0459 | 1.7859 | 1.1313 | 0.94888 | 0.81475 |  | Heating Req
02h30 | 154.82 | 133.9 | 85.38 | 71.15 | 61.21 | 02h30 | 1.9352 | 1.6738 | 1.0673 | 0.88938 | 0.76513 | Current | 555255.65
03h30 | 159.16 | 137.67 | 88.08 | 73.8 | 63.12 | 03h30 | 1.9895 | 1.7209 | 1.101 | 0.9225 | 0.789 | Insulated | 460455.15
04h30 | 162.23 | 140.41 | 90.13 | 75.54 | 64.7 | 04h30 | 2.0279 | 1.7551 | 1.1266 | 0.94425 | 0.80875 | Airtight | 288572.17
05h30 | 160.08 | 137.98 | 89 | 74.32 | 63.84 | 05h30 | 2.001 | 1.7248 | 1.1125 | 0.929 | 0.798 | Extra Glazing | 214654.49
06h30 | 152.13 | 129.83 | 86.61 | 70.91 | 62.25 | 06h30 | 1.9016 | 1.6229 | 1.0826 | 0.88638 | 0.77812 | Smart Heating | 167003.69
07h30 | 159.04 | 146.69 | 100 | 84.73 | 74.3 | 07h30 | 1.988 | 1.8336 | 1.25 | 1.0591 | 0.92875
08h30 | 177.59 | 154.87 | 103.51 | 86.44 | 75.35 | 08h30 | 2.2199 | 1.9359 | 1.2939 | 1.0805 | 0.94188 | Daily Energy Consumption (kWh)
09h30 | 177.59 | 154.83 | 101.73 | 86.26 | 74.71 | 09h30 | 2.2199 | 1.9354 | 1.2716 | 1.0782 | 0.93388 |  | Old | New
10h30 | 170.63 | 147.5 | 98.23 | 84.55 | 73.66 | 10h30 | 2.1329 | 1.8438 | 1.2279 | 1.0569 | 0.92075 | Winter | 47.4814 | 19.5586
11h30 | 170.63 | 153.11 | 99.9 | 86.09 | 73.16 | 11h30 | 2.1329 | 1.9139 | 1.2488 | 1.0761 | 0.9145 | Transition | 29.7119 | 8.2836
12h30 | 189.36 | 169.06 | 106.88 | 93.27 | 79.23 | 12h30 | 2.367 | 2.1132 | 1.336 | 1.1659 | 0.99038 | Summer | 0 | 0
13h30 | 189.36 | 169.06 | 106.99 | 96.28 | 81.72 | 13h30 | 2.367 | 2.1132 | 1.3374 | 1.2035 | 1.0215 | * 1 household
14h30 | 195.84 | 175.59 | 110.1 | 98.09 | 83.74 | 14h30 | 2.448 | 2.1949 | 1.3762 | 1.2261 | 1.0468
15h30 | 177.92 | 158.02 | 100.23 | 87.2 | 74.17 | 15h30 | 2.224 | 1.9752 | 1.2529 | 1.09 | 0.92712
16h30 | 149.96 | 130.68 | 90.13 | 78.2 | 66.08 | 16h30 | 1.8745 | 1.6335 | 1.1266 | 0.9775 | 0.826 | ESP-r model run for "80 flats" size. Divided by 80 for individual household energy bills
17h30 | 136.73 | 118.13 | 77.04 | 63.26 | 54.17 | 17h30 | 1.7091 | 1.4766 | 0.963 | 0.79075 | 0.67712
18h30 | 135.02 | 116.93 | 77.04 | 63.26 | 54.17 | 18h30 | 1.6878 | 1.4616 | 0.963 | 0.79075 | 0.67712
19h30 | 136.31 | 118.53 | 77.49 | 63.64 | 54.73 | 19h30 | 1.7039 | 1.4816 | 0.96862 | 0.7955 | 0.68412
20h30 | 136.32 | 118.64 | 77.75 | 63.96 | 55.01 | 20h30 | 1.704 | 1.483 | 0.97188 | 0.7995 | 0.68763
21h30 | 136.45 | 118.72 | 77.87 | 64.08 | 55.13 | 21h30 | 1.7056 | 1.484 | 0.97337 | 0.801 | 0.68912
22h30 | 136.75 | 118.88 | 78.09 | 64.17 | 55.22 | 22h30 | 1.7094 | 1.486 | 0.97613 | 0.80212 | 0.69025
23h30 | 132.22 | 114.1 | 75.29 | 61.38 | 52.71 | 23h30 | 1.6527 | 1.4263 | 0.94112 | 0.76725 | 0.65887
00h30 | 102.11 | 84.75 | 74.81 | 60.97 | 52.34 | 00h30 | 1.2764 | 1.0594 | 0.93512 | 0.76213 | 0.65425
01h30 | 95.31 | 78.99 | 49.84 | 36.37 | 29.15 | 01h30 | 1.1914 | 0.98738 | 0.623 | 0.45463 | 0.36438
02h30 | 93.57 | 76.84 | 49.84 | 37.75 | 31.31 | 02h30 | 1.1696 | 0.9605 | 0.623 | 0.47187 | 0.39137
03h30 | 101.89 | 84.23 | 53.75 | 42.37 | 35.88 | 03h30 | 1.2736 | 1.0529 | 0.67188 | 0.52963 | 0.4485
04h30 | 109.32 | 90.95 | 58.33 | 46.63 | 39.76 | 04h30 | 1.3665 | 1.1369 | 0.72913 | 0.58288 | 0.497
05h30 | 99.18 | 80.18 | 52.21 | 40.31 | 33.96 | 05h30 | 1.2397 | 1.0023 | 0.65263 | 0.50387 | 0.4245
06h30 | 84.4 | 64.8 | 47.63 | 34.67 | 27.93 | 06h30 | 1.055 | 0.81 | 0.59537 | 0.43338 | 0.34913
07h30 | 106.44 | 84.81 | 61.65 | 47.28 | 40.75 | 07h30 | 1.3305 | 1.0601 | 0.77063 | 0.591 | 0.50938
08h30 | 105.93 | 82.84 | 61.65 | 47.28 | 40.75 | 08h30 | 1.3241 | 1.0355 | 0.77063 | 0.591 | 0.50938
09h30 | 107.28 | 84.96 | 58.78 | 42.99 | 36.13 | 09h30 | 1.341 | 1.062 | 0.73475 | 0.53738 | 0.45162
10h30 | 116.35 | 94.95 | 61.9 | 48.23 | 40.7 | 10h30 | 1.4544 | 1.1869 | 0.77375 | 0.60288 | 0.50875
11h30 | 126.47 | 105.55 | 66.95 | 53.56 | 45.32 | 11h30 | 1.5809 | 1.3194 | 0.83688 | 0.6695 | 0.5665
12h30 | 145.78 | 125.03 | 79.19 | 65.02 | 55.47 | 12h30 | 1.8222 | 1.5629 | 0.98987 | 0.81275 | 0.69337
13h30 | 155.14 | 134.65 | 93.37 | 78.69 | 67.68 | 13h30 | 1.9392 | 1.6831 | 1.1671 | 0.98362 | 0.846
14h30 | 168.73 | 149.67 | 96.76 | 81.09 | 69.82 | 14h30 | 2.1091 | 1.8709 | 1.2095 | 1.0136 | 0.87275
15h30 | 162.44 | 143.09 | 92.73 | 75.81 | 65.42 | 15h30 | 2.0305 | 1.7886 | 1.1591 | 0.94763 | 0.81775
16h30 | 153.04 | 134.29 | 87.5 | 70.46 | 61.07 | 16h30 | 1.913 | 1.6786 | 1.0938 | 0.88075 | 0.76338
17h30 | 136.58 | 118.31 | 78.33 | 62.19 | 53.85 | 17h30 | 1.7072 | 1.4789 | 0.97913 | 0.77738 | 0.67312
18h30 | 130.37 | 112.42 | 74.71 | 59.35 | 51.4 | 18h30 | 1.6296 | 1.4053 | 0.93388 | 0.74187 | 0.6425
19h30 | 128.47 | 110.61 | 73.75 | 58.35 | 50.39 | 19h30 | 1.6059 | 1.3826 | 0.92188 | 0.72937 | 0.62987
20h30 | 122.13 | 104.12 | 70.22 | 54.23 | 46.64 | 20h30 | 1.5266 | 1.3015 | 0.87775 | 0.67788 | 0.583
21h30 | 121.77 | 103.37 | 69.99 | 53.85 | 46.44 | 21h30 | 1.5221 | 1.2921 | 0.87487 | 0.67312 | 0.5805
22h30 | 129.99 | 111.08 | 74.59 | 58.87 | 51.07 | 22h30 | 1.6249 | 1.3885 | 0.93237 | 0.73587 | 0.63838
23h30 | 127.26 | 107.78 | 72.67 | 57.04 | 49.47 | 23h30 | 1.5908 | 1.3473 | 0.90838 | 0.713 | 0.61838
00h30 | 97.31 | 78.32 | 61.69 | 45.25 | 38.52 | 00h30 | 1.2164 | 0.979 | 0.77112 | 0.56563 | 0.4815
01h30 | 98.29 | 80.09 | 52.28 | 37.66 | 31.3 | 01h30 | 1.2286 | 1.0011 | 0.6535 | 0.47075 | 0.39125
02h30 | 100.72 | 81.81 | 54.35 | 40.9 | 34.75 | 02h30 | 1.259 | 1.0226 | 0.67937 | 0.51125 | 0.43438
03h30 | 114.12 | 93.98 | 61.31 | 48.23 | 41.45 | 03h30 | 1.4265 | 1.1747 | 0.76638 | 0.60288 | 0.51812 | 2112
04h30 | 139.29 | 118.2 | 76.23 | 62.61 | 54.32 | 04h30 | 1.7411 | 1.4775 | 0.95288 | 0.78263 | 0.679
05h30 | 152.66 | 132.28 | 85.2 | 71 | 61.65 | 05h30 | 1.9083 | 1.6535 | 1.065 | 0.8875 | 0.77063
06h30 | 148.8 | 126.33 | 82.06 | 67.58 | 58.56 | 06h30 | 1.86 | 1.5791 | 1.0257 | 0.84475 | 0.732
07h30 | 148.8 | 126.74 | 93.4 | 77.26 | 68.09 | 07h30 | 1.86 | 1.5842 | 1.1675 | 0.96575 | 0.85113
08h30 | 150.83 | 124.84 | 85.57 | 68.55 | 59.46 | 08h30 | 1.8854 | 1.5605 | 1.0696 | 0.85688 | 0.74325
09h30 | 150.83 | 124.84 | 84.4 | 68.55 | 59.89 | 09h30 | 1.8854 | 1.5605 | 1.055 | 0.85688 | 0.74862
10h30 | 155.83 | 130.49 | 84.8 | 68.97 | 59.91 | 10h30 | 1.9479 | 1.6311 | 1.06 | 0.86213 | 0.74887
11h30 | 155.83 | 130.49 | 92.66 | 75.53 | 65.55 | 11h30 | 1.9479 | 1.6311 | 1.1583 | 0.94412 | 0.81937
12h30 | 191.91 | 167.65 | 109 | 91.12 | 79.47 | 12h30 | 2.3989 | 2.0956 | 1.3625 | 1.139 | 0.99338
13h30 | 191.91 | 167.65 | 116.92 | 99.42 | 86.89 | 13h30 | 2.3989 | 2.0956 | 1.4615 | 1.2428 | 1.0861
14h30 | 198.47 | 175.82 | 113.71 | 95.94 | 83.72 | 14h30 | 2.4809 | 2.1978 | 1.4214 | 1.1992 | 1.0465
15h30 | 195.92 | 172.95 | 111.6 | 93.08 | 81.2 | 15h30 | 2.449 | 2.1619 | 1.395 | 1.1635 | 1.015
16h30 | 190.26 | 167.82 | 108.71 | 90.26 | 78.87 | 16h30 | 2.3782 | 2.0978 | 1.3589 | 1.1282 | 0.98587
17h30 | 166.96 | 145.14 | 95.5 | 77.49 | 67.5 | 17h30 | 2.087 | 1.8142 | 1.1938 | 0.96862 | 0.84375
18h30 | 150.74 | 129.37 | 86.19 | 68.43 | 59.43 | 18h30 | 1.8842 | 1.6171 | 1.0774 | 0.85537 | 0.74287
19h30 | 159.09 | 137.97 | 91.79 | 73.49 | 64.22 | 19h30 | 1.9886 | 1.7246 | 1.1474 | 0.91863 | 0.80275
20h30 | 153.6 | 132.52 | 89.02 | 70.1 | 61.26 | 20h30 | 1.92 | 1.6565 | 1.1127 | 0.87625 | 0.76575
21h30 | 134.34 | 113.08 | 77.25 | 59.02 | 51.23 | 21h30 | 1.6792 | 1.4135 | 0.96562 | 0.73775 | 0.64038
22h30 | 123.74 | 102.17 | 72.67 | 56.29 | 49.23 | 22h30 | 1.5468 | 1.2771 | 0.90838 | 0.70362 | 0.61538
23h30 | 121.6 | 99.68 | 68.57 | 51.83 | 44.68 | 23h30 | 1.52 | 1.246 | 0.85713 | 0.64787 | 0.5585
00h30 | 94.9 | 73.71 | 68.57 | 51.83 | 44.68 | 00h30 | 1.1863 | 0.92138 | 0.85713 | 0.64787 | 0.5585
01h30 | 78.73 | 58.5 | 38.65 | 22.55 | 17.41 | 01h30 | 0.98413 | 0.73125 | 0.48313 | 0.28187 | 0.21763
02h30 | 77.99 | 57.18 | 39.6 | 25.13 | 20.78 | 02h30 | 0.97488 | 0.71475 | 0.495 | 0.31412 | 0.25975
03h30 | 100.99 | 79.14 | 52.65 | 37.98 | 32.75 | 03h30 | 1.2624 | 0.98925 | 0.65812 | 0.47475 | 0.40937
04h30 | 119.36 | 96.7 | 64.56 | 48.32 | 41.68 | 04h30 | 1.492 | 1.2087 | 0.807 | 0.604 | 0.521
05h30 | 118.79 | 95.4 | 64.37 | 47.69 | 40.8 | 05h30 | 1.4849 | 1.1925 | 0.80463 | 0.59613 | 0.51
06h30 | 113.91 | 89.79 | 60.92 | 45.05 | 38.31 | 06h30 | 1.4239 | 1.1224 | 0.7615 | 0.56312 | 0.47887
07h30 | 143.09 | 116.74 | 82.94 | 66.21 | 58.38 | 07h30 | 1.7886 | 1.4592 | 1.0368 | 0.82763 | 0.72975
08h30 | 165.38 | 137.31 | 93.6 | 75.38 | 66.15 | 08h30 | 2.0673 | 1.7164 | 1.17 | 0.94225 | 0.82688
09h30 | 168.84 | 143.8 | 98.19 | 80.17 | 70.87 | 09h30 | 2.1105 | 1.7975 | 1.2274 | 1.0021 | 0.88587
10h30 | 154.3 | 127.76 | 86.41 | 69.28 | 60.58 | 10h30 | 1.9287 | 1.597 | 1.0801 | 0.866 | 0.75725
11h30 | 149.33 | 122.72 | 81.79 | 65.68 | 56.91 | 11h30 | 1.8666 | 1.534 | 1.0224 | 0.821 | 0.71137
12h30 | 162.85 | 136.3 | 89.39 | 73.41 | 63.69 | 12h30 | 2.0356 | 1.7038 | 1.1174 | 0.91763 | 0.79612
13h30 | 167.82 | 141.34 | 98.8 | 82.32 | 71.85 | 13h30 | 2.0978 | 1.7668 | 1.235 | 1.029 | 0.89812
14h30 | 189.78 | 164.12 | 108.16 | 91.29 | 80.13 | 14h30 | 2.3723 | 2.0515 | 1.352 | 1.1411 | 1.0016
15h30 | 189.78 | 164.12 | 117.22 | 99.97 | 88.31 | 15h30 | 2.3723 | 2.0515 | 1.4652 | 1.2496 | 1.1039
16h30 | 195.39 | 170.51 | 113.87 | 96.19 | 85.15 | 16h30 | 2.4424 | 2.1314 | 1.4234 | 1.2024 | 1.0644
17h30 | 176.77 | 151.49 | 101.1 | 83.26 | 73.42 | 17h30 | 2.2096 | 1.8936 | 1.2637 | 1.0408 | 0.91775
18h30 | 163.99 | 139.1 | 92.96 | 75.15 | 66.05 | 18h30 | 2.0499 | 1.7388 | 1.162 | 0.93937 | 0.82563
19h30 | 154.66 | 130 | 87.73 | 70 | 61.38 | 19h30 | 1.9332 | 1.625 | 1.0966 | 0.875 | 0.76725
20h30 | 140.18 | 115.59 | 79.04 | 61.66 | 53.8 | 20h30 | 1.7523 | 1.4449 | 0.988 | 0.77075 | 0.6725
21h30 | 127.3 | 102.7 | 71.11 | 54.29 | 47.11 | 21h30 | 1.5913 | 1.2837 | 0.88887 | 0.67863 | 0.58888
22h30 | 121.7 | 97.05 | 67.73 | 50.95 | 44.09 | 22h30 | 1.5212 | 1.2131 | 0.84662 | 0.63687 | 0.55112
23h30 | 124.65 | 99.96 | 69.9 | 52.3 | 45.36 | 23h30 | 1.5581 | 1.2495 | 0.87375 | 0.65375 | 0.567
00h30 | 114.93 | 91.31 | 68.21 | 50.62 | 44.12 | 00h30 | 1.4366 | 1.1414 | 0.85262 | 0.63275 | 0.5515
01h30 | 125.41 | 103.03 | 68.68 | 51.36 | 43.87 | 01h30 | 1.5676 | 1.2879 | 0.8585 | 0.642 | 0.54837
02h30 | 134.6 | 111.89 | 74.52 | 57.78 | 50.13 | 02h30 | 1.6825 | 1.3986 | 0.9315 | 0.72225 | 0.62662
03h30 | 135.66 | 112.2 | 74.65 | 57.85 | 50.12 | 03h30 | 1.6958 | 1.4025 | 0.93312 | 0.72313 | 0.6265
04h30 | 119.68 | 95.68 | 68.82 | 51.42 | 43.85 | 04h30 | 1.496 | 1.196 | 0.86025 | 0.64275 | 0.54812
05h30 | 104.27 | 79.8 | 55.21 | 38.98 | 32.81 | 05h30 | 1.3034 | 0.9975 | 0.69012 | 0.48725 | 0.41013
06h30 | 112.48 | 87.62 | 60.54 | 44.25 | 37.62 | 06h30 | 1.406 | 1.0953 | 0.75675 | 0.55312 | 0.47025
07h30 | 136.7 | 110.05 | 80.34 | 61.94 | 54.62 | 07h30 | 1.7087 | 1.3756 | 1.0043 | 0.77425 | 0.68275
08h30 | 126.07 | 98 | 75 | 56.67 | 49.81 | 08h30 | 1.5759 | 1.225 | 0.9375 | 0.70837 | 0.62262
09h30 | 125.89 | 98.36 | 72.19 | 52.54 | 45.67 | 09h30 | 1.5736 | 1.2295 | 0.90238 | 0.65675 | 0.57088
10h30 | 130.21 | 103.23 | 74.23 | 54.63 | 47.48 | 10h30 | 1.6276 | 1.2904 | 0.92788 | 0.68288 | 0.5935
11h30 | 136.88 | 110.29 | 77.81 | 57.81 | 50.21 | 11h30 | 1.711 | 1.3786 | 0.97262 | 0.72262 | 0.62762
12h30 | 137.74 | 111.48 | 78.31 | 58.46 | 50.72 | 12h30 | 1.7217 | 1.3935 | 0.97888 | 0.73075 | 0.634
13h30 | 148.78 | 123.58 | 88.39 | 69.02 | 60.11 | 13h30 | 1.8598 | 1.5448 | 1.1049 | 0.86275 | 0.75138
14h30 | 170.16 | 144.87 | 98.24 | 79.33 | 69.25 | 14h30 | 2.127 | 1.8109 | 1.228 | 0.99162 | 0.86562
15h30 | 170.16 | 144.87 | 102.94 | 84 | 73.48 | 15h30 | 2.127 | 1.8109 | 1.2868 | 1.05 | 0.9185
16h30 | 200 | 181.71 | 121.44 | 101.77 | 89.65 | 16h30 | 2.5 | 2.2714 | 1.518 | 1.2721 | 1.1206
17h30 | 200 | 181.71 | 130.89 | 118.31 | 104.57 | 17h30 | 2.5 | 2.2714 | 1.6361 | 1.4789 | 1.3071
18h30 | 200 | 200 | 144.53 | 124.72 | 110.34 | 18h30 | 2.5 | 2.5 | 1.8066 | 1.559 | 1.3793
19h30 | 200 | 200 | 144.53 | 136.23 | 121.13 | 19h30 | 2.5 | 2.5 | 1.8066 | 1.7029 | 1.5141
20h30 | 200 | 200 | 147.81 | 127.73 | 113.77 | 20h30 | 2.5 | 2.5 | 1.8476 | 1.5966 | 1.4221
21h30 | 200 | 192.89 | 130.78 | 108.21 | 96.04 | 21h30 | 2.5 | 2.4111 | 1.6347 | 1.3526 | 1.2005
22h30 | 200 | 190.06 | 126.45 | 102.84 | 91.17 | 22h30 | 2.5 | 2.3758 | 1.5806 | 1.2855 | 1.1396
23h30 | 200 | 183.32 | 121.7 | 98.38 | 87.22 | 23h30 | 2.5 | 2.2915 | 1.5212 | 1.2297 | 1.0902
00h30 | 177.34 | 152.31 | 97.11 | 75.01 | 66.06 | 00h30 | 2.2168 | 1.9039 | 1.2139 | 0.93763 | 0.82575
01h30 | 156.56 | 130.79 | 86.31 | 66.26 | 57.37 | 01h30 | 1.957 | 1.6349 | 1.0789 | 0.82825 | 0.71713
02h30 | 135.03 | 109.36 | 73.43 | 66.26 | 57.37 | 02h30 | 1.6879 | 1.367 | 0.91787 | 0.82825 | 0.71713
03h30 | 124.17 | 98.48 | 67.31 | 46.53 | 39.1 | 03h30 | 1.5521 | 1.231 | 0.84137 | 0.58162 | 0.48875
04h30 | 116 | 90.31 | 62.66 | 46.53 | 39.1 | 04h30 | 1.45 | 1.1289 | 0.78325 | 0.58162 | 0.48875
05h30 | 115.5 | 89.79 | 62.47 | 43.5 | 36.85 | 05h30 | 1.4438 | 1.1224 | 0.78087 | 0.54375 | 0.46063
06h30 | 109.06 | 83.29 | 61.12 | 43.5 | 36.85 | 06h30 | 1.3633 | 1.0411 | 0.764 | 0.54375 | 0.46063
07h30 | 108.57 | 81.35 | 63.12 | 44.91 | 39.38 | 07h30 | 1.3571 | 1.0169 | 0.789 | 0.56137 | 0.49225
08h30 | 107.68 | 79.33 | 63.12 | 44.91 | 39.38 | 08h30 | 1.346 | 0.99162 | 0.789 | 0.56137 | 0.49225
09h30 | 125.04 | 97.36 | 70.75 | 52.75 | 46.11 | 09h30 | 1.563 | 1.217 | 0.88438 | 0.65938 | 0.57637
10h30 | 127.35 | 100.31 | 71.76 | 54.11 | 47.31 | 10h30 | 1.5919 | 1.2539 | 0.897 | 0.67637 | 0.59137
11h30 | 126.67 | 100.1 | 70.42 | 53.22 | 46.36 | 11h30 | 1.5834 | 1.2512 | 0.88025 | 0.66525 | 0.5795
12h30 | 141.62 | 115.45 | 79.21 | 62.25 | 54.47 | 12h30 | 1.7703 | 1.4431 | 0.99013 | 0.77812 | 0.68088
13h30 | 148.38 | 122.57 | 83.28 | 66.4 | 58.16 | 13h30 | 1.8547 | 1.5321 | 1.041 | 0.83 | 0.727
14h30 | 137.46 | 111.91 | 76.93 | 60.06 | 52.41 | 14h30 | 1.7183 | 1.3989 | 0.96162 | 0.75075 | 0.65512
15h30 | 135.6 | 110.27 | 76.56 | 58.89 | 51.43 | 15h30 | 1.695 | 1.3784 | 0.957 | 0.73613 | 0.64287
16h30 | 125.26 | 100.15 | 73.1 | 54.84 | 47.88 | 16h30 | 1.5657 | 1.2519 | 0.91375 | 0.6855 | 0.5985
17h30 | 125.79 | 100.88 | 72.08 | 52.86 | 46.16 | 17h30 | 1.5724 | 1.261 | 0.901 | 0.66075 | 0.577
18h30 | 149.68 | 124.91 | 86.49 | 67.45 | 59.33 | 18h30 | 1.871 | 1.5614 | 1.0811 | 0.84313 | 0.74162
19h30 | 157.73 | 133.06 | 91.23 | 71.9 | 63.38 | 19h30 | 1.9716 | 1.6632 | 1.1404 | 0.89875 | 0.79225
20h30 | 107.09 | 83.46 | 76.82 | 57.31 | 50.22 | 20h30 | 1.3386 | 1.0433 | 0.96025 | 0.71637 | 0.62775
21h30 | 57.13 | 32.44 | 30.19 | 8.36 | 5.23 | 21h30 | 0.71413 | 0.4055 | 0.37738 | 0.1045 | 0.065375
22h30 | 57.77 | 33.17 | 32.67 | 11.3 | 8.19 | 22h30 | 0.72213 | 0.41463 | 0.40837 | 0.14125 | 0.10237
23h30 | 56.56 | 31.73 | 30.07 | 10.13 | 7.14 | 23h30 | 0.707 | 0.39663 | 0.37588 | 0.12662 | 0.08925
00h30 | 46.38 | 31 | 27.59 | 7.19 | 4.17 | 00h30 | 0.57975 | 0.3875 | 0.34487 | 0.089875 | 0.052125
01h30 | 42.06 | 17.82 | 17.08 | 0 | 0 | 01h30 | 0.52575 | 0.22275 | 0.2135 | 0 | 0
02h30 | 56.46 | 33.6 | 26.91 | 11.09 | 7.2 | 02h30 | 0.70575 | 0.42 | 0.33637 | 0.13862 | 0.09
03h30 | 77.06 | 53.22 | 38.32 | 23.96 | 19.53 | 03h30 | 0.96325 | 0.66525 | 0.479 | 0.2995 | 0.24413
04h30 | 92 | 67.81 | 47.42 | 32.87 | 27.38 | 04h30 | 1.15 | 0.84762 | 0.59275 | 0.41087 | 0.34225
05h30 | 109.01 | 84.49 | 57.96 | 42.9 | 36.49 | 05h30 | 1.3626 | 1.0561 | 0.7245 | 0.53625 | 0.45613
06h30 | 128.22 | 103.43 | 69.69 | 54.54 | 46.99 | 06h30 | 1.6027 | 1.2929 | 0.87113 | 0.68175 | 0.58737
07h30 | 148.55 | 130.24 | 92.02 | 75.73 | 67.23 | 07h30 | 1.8569 | 1.628 | 1.1502 | 0.94663 | 0.84037
08h30 | 151.78 | 125.15 | 87.12 | 69.97 | 61.38 | 08h30 | 1.8973 | 1.5644 | 1.089 | 0.87462 | 0.76725
09h30 | 151.78 | 139.55 | 96.19 | 78.95 | 69.84 | 09h30 | 1.8973 | 1.7444 | 1.2024 | 0.98687 | 0.873
10h30 | 194.07 | 170.18 | 114.17 | 96.01 | 85.21 | 10h30 | 2.4259 | 2.1273 | 1.4271 | 1.2001 | 1.0651
11h30 | 194.07 | 174.86 | 120.69 | 102.69 | 91.18 | 11h30 | 2.4259 | 2.1858 | 1.5086 | 1.2836 | 1.1398
12h30 | 200 | 178.43 | 118.52 | 101.58 | 90.12 | 12h30 | 2.5 | 2.2304 | 1.4815 | 1.2697 | 1.1265
13h30 | 200 | 178.43 | 127.97 | 111.3 | 99.04 | 13h30 | 2.5 | 2.2304 | 1.5996 | 1.3913 | 1.238
14h30 | 200 | 200 | 137.47 | 120.28 | 107.31 | 14h30 | 2.5 | 2.5 | 1.7184 | 1.5035 | 1.3414
15h30 | 200 | 200 | 142.7 | 125.18 | 111.89 | 15h30 | 2.5 | 2.5 | 1.7837 | 1.5648 | 1.3986
16h30 | 200 | 200 | 155.13 | 137.3 | 123.74 | 16h30 | 2.5 | 2.5 | 1.9391 | 1.7163 | 1.5468
17h30 | 200 | 200 | 163.48 | 149.34 | 135.75 | 17h30 | 2.5 | 2.5 | 2.0435 | 1.8667 | 1.6969
18h30 | 200 | 200 | 180.61 | 162.17 | 147.78 | 18h30 | 2.5 | 2.5 | 2.2576 | 2.0271 | 1.8473
19h30 | 200 | 200 | 180.61 | 173 | 157.83 | 19h30 | 2.5 | 2.5 | 2.2576 | 2.1625 | 1.9729
20h30 | 200 | 200 | 177.33 | 159.62 | 145.24 | 20h30 | 2.5 | 2.5 | 2.2166 | 1.9952 | 1.8155
21h30 | 200 | 200 | 149.84 | 131.5 | 118.23 | 21h30 | 2.5 | 2.5 | 1.873 | 1.6438 | 1.4779
22h30 | 200 | 200 | 134.37 | 116.17 | 103.9 | 22h30 | 2.5 | 2.5 | 1.6796 | 1.4521 | 1.2988
23h30 | 200 | 200 | 128.32 | 110.01 | 98.75 | 23h30 | 2.5 | 2.5 | 1.604 | 1.3751 | 1.2344
00h30 | 186.7 | 158.91 | 95.81 | 78.58 | 68.64 | 00h30 | 2.3338 | 1.9864 | 1.1976 | 0.98225 | 0.858
01h30 | 176.09 | 142.61 | 89.03 | 72.61 | 63.79 | 01h30 | 2.2011 | 1.7826 | 1.1129 | 0.90763 | 0.79737
02h30 | 189.39 | 160.34 | 101.07 | 83.17 | 73.44 | 02h30 | 2.3674 | 2.0042 | 1.2634 | 1.0396 | 0.918
03h30 | 200 | 176.64 | 123.32 | 103.58 | 92.04 | 03h30 | 2.5 | 2.208 | 1.5415 | 1.2948 | 1.1505
04h30 | 200 | 200 | 142.72 | 121.84 | 108.73 | 04h30 | 2.5 | 2.5 | 1.784 | 1.523 | 1.3591
05h30 | 200 | 200 | 151.95 | 130.5 | 116.59 | 05h30 | 2.5 | 2.5 | 1.8994 | 1.6313 | 1.4574
06h30 | 200 | 200 | 141.99 | 120.58 | 107.6 | 06h30 | 2.5 | 2.5 | 1.7749 | 1.5072 | 1.345
07h30 | 200 | 191.59 | 132.38 | 109.5 | 98.87 | 07h30 | 2.5 | 2.3949 | 1.6547 | 1.3687 | 1.2359
08h30 | 200 | 179.85 | 120.99 | 95.81 | 86.4 | 08h30 | 2.5 | 2.2481 | 1.5124 | 1.1976 | 1.08
09h30 | 200 | 188.26 | 132.58 | 106.91 | 96.84 | 09h30 | 2.5 | 2.3533 | 1.6572 | 1.3364 | 1.2105
10h30 | 200 | 200 | 150.05 | 125.49 | 113.33 | 10h30 | 2.5 | 2.5 | 1.8756 | 1.5686 | 1.4166
11h30 | 200 | 200 | 156.9 | 139.37 | 130.5 | 11h30 | 2.5 | 2.5 | 1.9612 | 1.7421 | 1.6313
12h30 | 200 | 200 | 162.73 | 140.06 | 127.08 | 12h30 | 2.5 | 2.5 | 2.0341 | 1.7508 | 1.5885
13h30 | 200 | 200 | 155.19 | 130.31 | 117.64 | 13h30 | 2.5 | 2.5 | 1.9399 | 1.6289 | 1.4705
14h30 | 200 | 200 | 181.45 | 155.39 | 140.55 | 14h30 | 2.5 | 2.5 | 2.2681 | 1.9424 | 1.7569
15h30 | 200 | 200 | 188.99 | 165.15 | 149.99 | 15h30 | 2.5 | 2.5 | 2.3624 | 2.0644 | 1.8749
16h30 | 200 | 200 | 191.38 | 166.38 | 151.2 | 16h30 | 2.5 | 2.5 | 2.3923 | 2.0798 | 1.89
17h30 | 200 | 200 | 191.38 | 166.38 | 151.2 | 17h30 | 2.5 | 2.5 | 2.3923 | 2.0798 | 1.89
18h30 | 200 | 200 | 200 | 177.89 | 162.78 | 18h30 | 2.5 | 2.5 | 2.5 | 2.2236 | 2.0347
19h30 | 200 | 200 | 200 | 174.54 | 160.06 | 19h30 | 2.5 | 2.5 | 2.5 | 2.1818 | 2.0008
20h30 | 200 | 200 | 195.91 | 168.28 | 154.43 | 20h30 | 2.5 | 2.5 | 2.4489 | 2.1035 | 1.9304
21h30 | 200 | 200 | 184.24 | 156.29 | 143.2 | 21h30 | 2.5 | 2.5 | 2.303 | 1.9536 | 1.79
22h30 | 200 | 200 | 147.91 | 120.62 | 109.88 | 22h30 | 2.5 | 2.5 | 1.8489 | 1.5077 | 1.3735
23h30 | 200 | 175.86 | 113.78 | 87.18 | 78.75 | 23h30 | 2.5 | 2.1982 | 1.4223 | 1.0897 | 0.98438
00h30 | 179.85 | 141.17 | 82.12 | 57.38 | 54.92 | 00h30 | 2.2481 | 1.7646 | 1.0265 | 0.71725 | 0.6865
01h30 | 169.99 | 129.65 | 79 | 56.34 | 49.52 | 01h30 | 2.1249 | 1.6206 | 0.9875 | 0.70425 | 0.619
02h30 | 124.93 | 86.13 | 54.23 | 50.18 | 49.52 | 02h30 | 1.5616 | 1.0766 | 0.67788 | 0.62725 | 0.619
03h30 | 81.91 | 44.59 | 30.44 | 3.46 | 0 | 03h30 | 1.0239 | 0.55737 | 0.3805 | 0.04325 | 0
04h30 | 108.01 | 71.81 | 47.61 | 25.98 | 21.11 | 04h30 | 1.3501 | 0.89763 | 0.59513 | 0.32475 | 0.26388
05h30 | 134.02 | 98.7 | 64.3 | 42.53 | 36.62 | 05h30 | 1.6752 | 1.2337 | 0.80375 | 0.53163 | 0.45775
06h30 | 144.71 | 110.17 | 71.76 | 51.01 | 44.56 | 06h30 | 1.8089 | 1.3771 | 0.897 | 0.63762 | 0.557
07h30 | 171.59 | 149.54 | 102.21 | 79.54 | 71.73 | 07h30 | 2.1449 | 1.8693 | 1.2776 | 0.99425 | 0.89663
08h30 | 180.85 | 147.6 | 99.36 | 75.89 | 67.66 | 08h30 | 2.2606 | 1.845 | 1.242 | 0.94863 | 0.84575
09h30 | 170.98 | 137.23 | 93.27 | 71.18 | 63.43 | 09h30 | 2.1372 | 1.7154 | 1.1659 | 0.88975 | 0.79287
10h30 | 152.9 | 119.14 | 81.8 | 60 | 52.98 | 10h30 | 1.9112 | 1.4892 | 1.0225 | 0.75 | 0.66225
11h30 | 146.65 | 113.9 | 78.49 | 56.67 | 49.71 | 11h30 | 1.8331 | 1.4238 | 0.98113 | 0.70837 | 0.62138
12h30 | 160.39 | 128.76 | 87.25 | 65.31 | 57.39 | 12h30 | 2.0049 | 1.6095 | 1.0906 | 0.81637 | 0.71737
13h30 | 153.5 | 122.84 | 83.47 | 61.74 | 53.98 | 13h30 | 1.9187 | 1.5355 | 1.0434 | 0.77175 | 0.67475
14h30 | 135.64 | 105.7 | 73.14 | 52.07 | 45.15 | 14h30 | 1.6955 | 1.3213 | 0.91425 | 0.65087 | 0.56437
15h30 | 128.82 | 99.54 | 69.73 | 49.16 | 42.57 | 15h30 | 1.6102 | 1.2443 | 0.87162 | 0.6145 | 0.53212
16h30 | 136.52 | 107.99 | 75.3 | 54.6 | 47.59 | 16h30 | 1.7065 | 1.3499 | 0.94125 | 0.6825 | 0.59488
17h30 | 147.78 | 120 | 83.05 | 61.83 | 54.2 | 17h30 | 1.8473 | 1.5 | 1.0381 | 0.77287 | 0.6775
18h30 | 138.57 | 111.44 | 78.04 | 57.01 | 49.82 | 18h30 | 1.7321 | 1.393 | 0.9755 | 0.71262 | 0.62275
19h30 | 115.65 | 88.96 | 63.87 | 44.64 | 38.55 | 19h30 | 1.4456 | 1.112 | 0.79837 | 0.558 | 0.48187
20h30 | 99.77 | 73.43 | 53.57 | 36.48 | 31.15 | 20h30 | 1.2471 | 0.91787 | 0.66963 | 0.456 | 0.38938
21h30 | 102.2 | 76.19 | 54.99 | 38.32 | 32.88 | 21h30 | 1.2775 | 0.95237 | 0.68737 | 0.479 | 0.411
22h30 | 122.97 | 97.29 | 68.16 | 50.54 | 44.05 | 22h30 | 1.5371 | 1.2161 | 0.852 | 0.63175 | 0.55063
23h30 | 135.69 | 110.29 | 76.57 | 58.05 | 50.87 | 23h30 | 1.6961 | 1.3786 | 0.95713 | 0.72562 | 0.63587
00h30 | 111.47 | 87.28 | 61.21 | 38.82 | 33.09 | 00h30 | 1.3934 | 1.091 | 0.76513 | 0.48525 | 0.41363
01h30 | 110.96 | 88.06 | 59.37 | 42.97 | 36.57 | 01h30 | 1.387 | 1.1007 | 0.74213 | 0.53712 | 0.45713
02h30 | 109.01 | 85.94 | 59.37 | 42.6 | 36.57 | 02h30 | 1.3626 | 1.0742 | 0.74213 | 0.5325 | 0.45713
03h30 | 104.51 | 80.96 | 54.9 | 40.28 | 34.2 | 03h30 | 1.3064 | 1.012 | 0.68625 | 0.5035 | 0.4275
04h30 | 107.84 | 84.06 | 57.53 | 42.02 | 35.77 | 04h30 | 1.348 | 1.0508 | 0.71913 | 0.52525 | 0.44712
05h30 | 112.64 | 88.65 | 60.79 | 44.67 | 38.1 | 05h30 | 1.408 | 1.1081 | 0.75987 | 0.55837 | 0.47625
06h30 | 116.54 | 92.33 | 63.46 | 47.11 | 40.3 | 06h30 | 1.4567 | 1.1541 | 0.79325 | 0.58888 | 0.50375
07h30 | 143.09 | 119.79 | 86.42 | 68.65 | 60.99 | 07h30 | 1.7886 | 1.4974 | 1.0802 | 0.85813 | 0.76238
08h30 | 153.98 | 127.46 | 89.56 | 70.41 | 62.06 | 08h30 | 1.9247 | 1.5933 | 1.1195 | 0.88013 | 0.77575
09h30 | 153.98 | 132.96 | 95.3 | 76.07 | 67.47 | 09h30 | 1.9247 | 1.662 | 1.1912 | 0.95088 | 0.84337
10h30 | 161.91 | 136.87 | 95.08 | 76.02 | 67.24 | 10h30 | 2.0239 | 1.7109 | 1.1885 | 0.95025 | 0.8405
11h30 | 153.05 | 127.47 | 88.2 | 69.85 | 61.4 | 11h30 | 1.9131 | 1.5934 | 1.1025 | 0.87313 | 0.7675
12h30 | 145.08 | 119.37 | 82.35 | 64.68 | 56.79 | 12h30 | 1.8135 | 1.4921 | 1.0294 | 0.8085 | 0.70988
13h30 | 148.02 | 122.83 | 84.16 | 66.51 | 58.16 | 13h30 | 1.8502 | 1.5354 | 1.052 | 0.83137 | 0.727
14h30 | 150.82 | 126.01 | 86.14 | 68.39 | 59.81 | 14h30 | 1.8853 | 1.5751 | 1.0768 | 0.85488 | 0.74762
15h30 | 145.81 | 121.31 | 83.43 | 65.9 | 57.55 | 15h30 | 1.8226 | 1.5164 | 1.0429 | 0.82375 | 0.71937
16h30 | 139.6 | 115.33 | 79.83 | 63.05 | 55.91 | 16h30 | 1.745 | 1.4416 | 0.99787 | 0.78812 | 0.69888
17h30 | 136.29 | 112.29 | 77.73 | 61.4 | 53.52 | 17h30 | 1.7036 | 1.4036 | 0.97162 | 0.7675 | 0.669
18h30 | 129.36 | 105.61 | 76.98 | 61.4 | 53.52 | 18h30 | 1.617 | 1.3201 | 0.96225 | 0.7675 | 0.669
19h30 | 114.65 | 91.09 | 64.5 | 48.81 | 41.91 | 19h30 | 1.4331 | 1.1386 | 0.80625 | 0.61013 | 0.52387
20h30 | 105.96 | 82.54 | 64.5 | 48.81 | 41.91 | 20h30 | 1.3245 | 1.0317 | 0.80625 | 0.61013 | 0.52387
21h30 | 104.33 | 81.04 | 58.04 | 42.23 | 35.98 | 21h30 | 1.3041 | 1.013 | 0.7255 | 0.52787 | 0.44975
22h30 | 104.18 | 81.01 | 58.42 | 42.26 | 36.13 | 22h30 | 1.3022 | 1.0126 | 0.73025 | 0.52825 | 0.45162
23h30 | 109.43 | 86.35 | 61.31 | 44.85 | 38.48 | 23h30 | 1.3679 | 1.0794 | 0.76638 | 0.56063 | 0.481
00h30 | 96.7 | 75.63 | 60.94 | 44.82 | 38.33 | 00h30 | 1.2087 | 0.94537 | 0.76175 | 0.56025 | 0.47913
01h30 | 107.67 | 87.03 | 57.32 | 43.11 | 35.74 | 01h30 | 1.3459 | 1.0879 | 0.7165 | 0.53887 | 0.44675
02h30 | 119.13 | 98.31 | 64.45 | 51.02 | 43.44 | 02h30 | 1.4891 | 1.2289 | 0.80563 | 0.63775 | 0.543
03h30 | 126.98 | 105.6 | 68.81 | 55.03 | 46.95 | 03h30 | 1.5873 | 1.32 | 0.86013 | 0.68788 | 0.58688
04h30 | 131.83 | 110.18 | 72.11 | 58.18 | 49.28 | 04h30 | 1.6479 | 1.3773 | 0.90138 | 0.72725 | 0.616
05h30 | 132.74 | 110.85 | 72.55 | 59.08 | 49.83 | 05h30 | 1.6592 | 1.3856 | 0.90687 | 0.7385 | 0.62287
06h30 | 134.77 | 112.68 | 73.64 | 60.57 | 51.15 | 06h30 | 1.6846 | 1.4085 | 0.9205 | 0.75713 | 0.63938
07h30 | 140.36 | 117.69 | 93.04 | 78.76 | 69.02 | 07h30 | 1.7545 | 1.4711 | 1.163 | 0.9845 | 0.86275
08h30 | 151.79 | 127.92 | 88.62 | 73.25 | 63.71 | 08h30 | 1.8974 | 1.599 | 1.1078 | 0.91563 | 0.79638
09h30 | 141.44 | 117.14 | 80.7 | 66.33 | 57.63 | 09h30 | 1.768 | 1.4643 | 1.0088 | 0.82913 | 0.72037
10h30 | 130.29 | 106.99 | 73.6 | 59.28 | 51.6 | 10h30 | 1.6286 | 1.3374 | 0.92 | 0.741 | 0.645
11h30 | 129.6 | 107.16 | 70.9 | 56.72 | 47.76 | 11h30 | 1.62 | 1.3395 | 0.88625 | 0.709 | 0.597
12h30 | 130.35 | 108.41 | 71.81 | 57.04 | 47.79 | 12h30 | 1.6294 | 1.3551 | 0.89763 | 0.713 | 0.59737
13h30 | 117.46 | 95.99 | 64.7 | 49.92 | 41.31 | 13h30 | 1.4683 | 1.1999 | 0.80875 | 0.624 | 0.51638
14h30 | 101.63 | 80.75 | 63.79 | 49.6 | 41.29 | 14h30 | 1.2704 | 1.0094 | 0.79737 | 0.62 | 0.51612
15h30 | 107.06 | 86.76 | 59.4 | 44.03 | 36.42 | 15h30 | 1.3382 | 1.0845 | 0.7425 | 0.55037 | 0.45525
16h30 | 113.05 | 93.21 | 63.74 | 48.66 | 40.89 | 16h30 | 1.4131 | 1.1651 | 0.79675 | 0.60825 | 0.51113
17h30 | 111.48 | 92.05 | 62.43 | 47.55 | 40.07 | 17h30 | 1.3935 | 1.1506 | 0.78038 | 0.59437 | 0.50087
18h30 | 110.93 | 91.86 | 62.65 | 47.89 | 40.38 | 18h30 | 1.3866 | 1.1482 | 0.78312 | 0.59862 | 0.50475
19h30 | 107.66 | 88.86 | 61.17 | 46.21 | 38.94 | 19h30 | 1.3458 | 1.1107 | 0.76462 | 0.57763 | 0.48675
20h30 | 107.12 | 88.44 | 61.24 | 45.82 | 38.81 | 20h30 | 1.339 | 1.1055 | 0.7655 | 0.57275 | 0.48512
21h30 | 115.67 | 97.02 | 66.83 | 50.76 | 43.47 | 21h30 | 1.4459 | 1.2127 | 0.83537 | 0.6345 | 0.54338
22h30 | 110.66 | 91.94 | 64.07 | 47.76 | 40.89 | 22h30 | 1.3833 | 1.1493 | 0.80088 | 0.597 | 0.51113
23h30 | 86.22 | 67.34 | 48.94 | 33.69 | 28.21 | 23h30 | 1.0777 | 0.84175 | 0.61175 | 0.42113 | 0.35263
00h30 | 60.79 | 62.8 | 47.08 | 32.12 | 26.13 | 00h30 | 0.75987 | 0.785 | 0.5885 | 0.4015 | 0.32662
01h30 | 70.88 | 53.17 | 34.91 | 21.38 | 16.29 | 01h30 | 0.886 | 0.66463 | 0.43638 | 0.26725 | 0.20363
02h30 | 87.94 | 70.42 | 46.77 | 34.12 | 28.72 | 02h30 | 1.0993 | 0.88025 | 0.58462 | 0.4265 | 0.359
03h30 | 112.03 | 92.74 | 60.37 | 47.97 | 41.3 | 03h30 | 1.4004 | 1.1592 | 0.75462 | 0.59962 | 0.51625
04h30 | 109.28 | 89.65 | 59.09 | 46.31 | 39.38 | 04h30 | 1.366 | 1.1206 | 0.73862 | 0.57888 | 0.49225
05h30 | 93.52 | 73.4 | 49.76 | 36.66 | 30.64 | 05h30 | 1.169 | 0.9175 | 0.622 | 0.45825 | 0.383
06h30 | 92.71 | 72.14 | 49.44 | 35.88 | 29.86 | 06h30 | 1.1589 | 0.90175 | 0.618 | 0.4485 | 0.37325
07h30 | 113.5 | 98.51 | 71.49 | 56.42 | 49.31 | 07h30 | 1.4187 | 1.2314 | 0.89363 | 0.70525 | 0.61638
08h30 | 132.88 | 109.64 | 76.03 | 60.52 | 52.23 | 08h30 | 1.661 | 1.3705 | 0.95037 | 0.7565 | 0.65287
09h30 | 132.88 | 114.61 | 78.51 | 64.09 | 55.68 | 09h30 | 1.661 | 1.4326 | 0.98137 | 0.80112 | 0.696
10h30 | 119.97 | 97.35 | 66.02 | 52.23 | 44.58 | 10h30 | 1.4996 | 1.2169 | 0.82525 | 0.65287 | 0.55725
11h30 | 105.94 | 82.98 | 55.85 | 42.77 | 35.6 | 11h30 | 1.3242 | 1.0373 | 0.69812 | 0.53463 | 0.445
12h30 | 116.07 | 92.98 | 61.53 | 48.6 | 40.6 | 12h30 | 1.4509 | 1.1623 | 0.76912 | 0.6075 | 0.5075
13h30 | 130.09 | 109.06 | 71.53 | 58.43 | 49.16 | 13h30 | 1.6261 | 1.3633 | 0.89412 | 0.73037 | 0.6145
14h30 | 129.07 | 107.36 | 70.63 | 57.93 | 48.46 | 14h30 | 1.6134 | 1.342 | 0.88287 | 0.72413 | 0.60575
15h30 | 123.33 | 101.8 | 67.36 | 54.92 | 45.72 | 15h30 | 1.5416 | 1.2725 | 0.842 | 0.6865 | 0.5715
16h30 | 129.46 | 108.29 | 71.59 | 58.79 | 49.3 | 16h30 | 1.6182 | 1.3536 | 0.89487 | 0.73487 | 0.61625
17h30 | 135.2 | 117.92 | 77.72 | 64.56 | 54.77 | 17h30 | 1.69 | 1.474 | 0.9715 | 0.807 | 0.68463
18h30 | 141.42 | 121.72 | 80.36 | 66.72 | 57.06 | 18h30 | 1.7677 | 1.5215 | 1.0045 | 0.834 | 0.71325
19h30 | 141.42 | 121.92 | 81.04 | 66.43 | 57.02 | 19h30 | 1.7677 | 1.524 | 1.013 | 0.83037 | 0.71275
20h30 | 140.19 | 120.16 | 80.4 | 65.12 | 55.95 | 20h30 | 1.7524 | 1.502 | 1.005 | 0.814 | 0.69937
21h30 | 123.1 | 103.1 | 69.97 | 55.28 | 47.16 | 21h30 | 1.5388 | 1.2888 | 0.87462 | 0.691 | 0.5895
22h30 | 97.41 | 79.51 | 56.65 | 42.67 | 36.53 | 22h30 | 1.2176 | 0.99387 | 0.70813 | 0.53338 | 0.45663
23h30 | 91.05 | 70.94 | 50.03 | 36.23 | 30.09 | 23h30 | 1.1381 | 0.88675 | 0.62538 | 0.45288 | 0.37612
00h30 | 81.08 | 70.94 | 50.03 | 36.23 | 30.09 | 00h30 | 1.0135 | 0.88675 | 0.62538 | 0.45288 | 0.37612
01h30 | 92.11 | 74.6 | 47.79 | 35.73 | 28.49 | 01h30 | 1.1514 | 0.9325 | 0.59737 | 0.44662 | 0.35613
02h30 | 98.61 | 80.53 | 52.09 | 40.84 | 33.52 | 02h30 | 1.2326 | 1.0066 | 0.65112 | 0.5105 | 0.419
03h30 | 100.37 | 81.04 | 52.41 | 41.35 | 33.94 | 03h30 | 1.2546 | 1.013 | 0.65512 | 0.51687 | 0.42425
04h30 | 98.03 | 78.34 | 51.07 | 39.99 | 32.43 | 04h30 | 1.2254 | 0.97925 | 0.63838 | 0.49988 | 0.40537
05h30 | 99.66 | 79.61 | 52 | 40.92 | 32.93 | 05h30 | 1.2457 | 0.99513 | 0.65 | 0.5115 | 0.41163
06h30 | 104.46 | 84.13 | 54.86 | 43.76 | 35.21 | 06h30 | 1.3057 | 1.0516 | 0.68575 | 0.547 | 0.44012
07h30 | 113.49 | 107.76 | 75.68 | 63.23 | 53.41 | 07h30 | 1.4186 | 1.347 | 0.946 | 0.79038 | 0.66763
08h30 | 131.94 | 111.23 | 75.05 | 61.73 | 51.24 | 08h30 | 1.6493 | 1.3904 | 0.93812 | 0.77163 | 0.6405
09h30 | 131.94 | 109.73 | 74.25 | 61.58 | 51.52 | 09h30 | 1.6493 | 1.3716 | 0.92812 | 0.76975 | 0.644
10h30 | 130.33 | 107.13 | 71.52 | 59.29 | 49.05 | 10h30 | 1.6291 | 1.3391 | 0.894 | 0.74113 | 0.61313
11h30 | 130.33 | 108.63 | 74.04 | 62.08 | 51.15 | 11h30 | 1.6291 | 1.3579 | 0.9255 | 0.776 | 0.63938
12h30 | 140.07 | 118.68 | 77.62 | 65.68 | 54.13 | 12h30 | 1.7509 | 1.4835 | 0.97025 | 0.821 | 0.67663
13h30 | 140.07 | 118.68 | 78.85 | 66.89 | 54.92 | 13h30 | 1.7509 | 1.4835 | 0.98562 | 0.83613 | 0.6865
14h30 | 148.37 | 127.89 | 82.54 | 70.56 | 57.6 | 14h30 | 1.8546 | 1.5986 | 1.0317 | 0.882 | 0.72
15h30 | 148.37 | 127.89 | 89.76 | 77.23 | 63.7 | 15h30 | 1.8546 | 1.5986 | 1.122 | 0.96537 | 0.79625
16h30 | 152.83 | 133.44 | 88.29 | 74.68 | 62.45 | 16h30 | 1.9104 | 1.668 | 1.1036 | 0.9335 | 0.78063
17h30 | 131.88 | 112.45 | 74.44 | 60.97 | 50.91 | 17h30 | 1.6485 | 1.4056 | 0.9305 | 0.76213 | 0.63638
18h30 | 116.08 | 97.12 | 66.19 | 53.45 | 45.34 | 18h30 | 1.451 | 1.214 | 0.82737 | 0.66812 | 0.56675
19h30 | 107.9 | 89.29 | 59.94 | 47.13 | 39.28 | 19h30 | 1.3487 | 1.1161 | 0.74925 | 0.58913 | 0.491
20h30 | 101.58 | 83.19 | 59.94 | 47.13 | 39.28 | 20h30 | 1.2697 | 1.0399 | 0.74925 | 0.58913 | 0.491
21h30 | 96.29 | 77.99 | 53.5 | 40.1 | 33.43 | 21h30 | 1.2036 | 0.97488 | 0.66875 | 0.50125 | 0.41787
22h30 | 91.22 | 72.94 | 53.5 | 40.1 | 33.43 | 22h30 | 1.1402 | 0.91175 | 0.66875 | 0.50125 | 0.41787
23h30 | 94.6 | 76.28 | 52.28 | 38.96 | 32.43 | 23h30 | 1.1825 | 0.9535 | 0.6535 | 0.487 | 0.40537
00h30 | 81.98 | 69.32 | 52.28 | 38.96 | 32.43 | 00h30 | 1.0248 | 0.8665 | 0.6535 | 0.487 | 0.40537
01h30 | 78.51 | 62.44 | 40.76 | 26.88 | 20.97 | 01h30 | 0.98137 | 0.7805 | 0.5095 | 0.336 | 0.26212
02h30 | 70.16 | 62.44 | 40.76 | 26.88 | 20.97 | 02h30 | 0.877 | 0.7805 | 0.5095 | 0.336 | 0.26212
03h30 | 70.58 | 52.08 | 35.69 | 21.68 | 17.97 | 03h30 | 0.88225 | 0.651 | 0.44612 | 0.271 | 0.22462
04h30 | 73.21 | 55.13 | 38.21 | 24.75 | 19.74 | 04h30 | 0.91512 | 0.68912 | 0.47763 | 0.30938 | 0.24675
05h30 | 89.33 | 70.04 | 47.36 | 33.65 | 27.61 | 05h30 | 1.1166 | 0.8755 | 0.592 | 0.42063 | 0.34513
06h30 | 98.86 | 79.16 | 53.22 | 39.04 | 32.42 | 06h30 | 1.2357 | 0.9895 | 0.66525 | 0.488 | 0.40525
07h30 | 110.97 | 89.29 | 65.74 | 49.83 | 43.06 | 07h30 | 1.3871 | 1.1161 | 0.82175 | 0.62287 | 0.53825
08h30 | 107.67 | 84.61 | 60.23 | 44.05 | 36.94 | 08h30 | 1.3459 | 1.0576 | 0.75287 | 0.55063 | 0.46175
09h30 | 99.5 | 77.27 | 54.24 | 40 | 33.44 | 09h30 | 1.2437 | 0.96588 | 0.678 | 0.5 | 0.418
10h30 | 85.97 | 69.78 | 51.38 | 37.31 | 32.99 | 10h30 | 1.0746 | 0.87225 | 0.64225 | 0.46637 | 0.41237
11h30 | 66.89 | 44.56 | 30.89 | 16.91 | 11.24 | 11h30 | 0.83613 | 0.557 | 0.38612 | 0.21138 | 0.1405
12h30 | 73.36 | 52.69 | 36.01 | 23.58 | 17.74 | 12h30 | 0.917 | 0.65863 | 0.45012 | 0.29475 | 0.22175
13h30 | 78.96 | 58.72 | 38.61 | 27.42 | 21 | 13h30 | 0.987 | 0.734 | 0.48263 | 0.34275 | 0.2625
14h30 | 74.46 | 54.78 | 35.87 | 24.97 | 18.92 | 14h30 | 0.93075 | 0.68475 | 0.44838 | 0.31212 | 0.2365
15h30 | 77.69 | 58.47 | 39.07 | 26.75 | 20.81 | 15h30 | 0.97113 | 0.73088 | 0.48838 | 0.33437 | 0.26012
16h30 | 101.33 | 82.49 | 55.21 | 41.05 | 33.88 | 16h30 | 1.2666 | 1.0311 | 0.69012 | 0.51313 | 0.4235
17h30 | 103.95 | 85.59 | 58 | 43.39 | 36.12 | 17h30 | 1.2994 | 1.0699 | 0.725 | 0.54238 | 0.4515
18h30 | 90.76 | 72.83 | 50.48 | 36.13 | 29.73 | 18h30 | 1.1345 | 0.91038 | 0.631 | 0.45162 | 0.37162
19h30 | 93.85 | 76.16 | 52.49 | 38.28 | 31.8 | 19h30 | 1.1731 | 0.952 | 0.65612 | 0.4785 | 0.3975
20h30 | 103.93 | 86.29 | 58.48 | 44.67 | 37.58 | 20h30 | 1.2991 | 1.0786 | 0.731 | 0.55837 | 0.46975
21h30 | 110.61 | 92.9 | 62.25 | 48.92 | 41.29 | 21h30 | 1.3826 | 1.1612 | 0.77812 | 0.6115 | 0.51612
22h30 | 113.98 | 96.09 | 64.1 | 50.83 | 42.92 | 22h30 | 1.4247 | 1.2011 | 0.80125 | 0.63538 | 0.5365
23h30 | 114.3 | 96.15 | 64.17 | 50.79 | 42.88 | 23h30 | 1.4287 | 1.2019 | 0.80212 | 0.63487 | 0.536
00h30 | 94 | 76.63 | 46.47 | 33.76 | 26.28 | 00h30 | 1.175 | 0.95788 | 0.58088 | 0.422 | 0.3285
01h30 | 92.45 | 76.17 | 48.89 | 37.71 | 30.9 | 01h30 | 1.1556 | 0.95212 | 0.61113 | 0.47137 | 0.38625
02h30 | 87.88 | 71.2 | 47.77 | 35.55 | 29.31 | 02h30 | 1.0985 | 0.89 | 0.59713 | 0.44438 | 0.36638
03h30 | 90.84 | 73.2 | 47.56 | 36.64 | 30.59 | 03h30 | 1.1355 | 0.915 | 0.5945 | 0.458 | 0.38238
04h30 | 100.94 | 82.58 | 53.91 | 42.11 | 35.53 | 04h30 | 1.2617 | 1.0322 | 0.67388 | 0.52638 | 0.44412
05h30 | 105.34 | 86.33 | 56.43 | 44.37 | 37.38 | 05h30 | 1.3168 | 1.0791 | 0.70537 | 0.55463 | 0.46725
06h30 | 101.08 | 81.49 | 53.94 | 41.49 | 34.65 | 06h30 | 1.2635 | 1.0186 | 0.67425 | 0.51863 | 0.43312
07h30 | 106.84 | 99.45 | 71.01 | 56.4 | 48.53 | 07h30 | 1.3355 | 1.2431 | 0.88762 | 0.705 | 0.60662
08h30 | 134.1 | 112.38 | 77.26 | 60.65 | 51.51 | 08h30 | 1.6763 | 1.4047 | 0.96575 | 0.75813 | 0.64387
09h30 | 134.1 | 121.75 | 85.35 | 68.57 | 59.41 | 09h30 | 1.6763 | 1.5219 | 1.0669 | 0.85713 | 0.74262
10h30 | 139.85 | 117.99 | 80.69 | 64.21 | 55.45 | 10h30 | 1.7481 | 1.4749 | 1.0086 | 0.80263 | 0.69312
11h30 | 135.18 | 112.11 | 75.89 | 60.23 | 51.87 | 11h30 | 1.6898 | 1.4014 | 0.94863 | 0.75287 | 0.64838
12h30 | 136.19 | 112.56 | 75.28 | 60.37 | 51.98 | 12h30 | 1.7024 | 1.407 | 0.941 | 0.75462 | 0.64975
13h30 | 128.06 | 104.72 | 70.25 | 55.87 | 47.91 | 13h30 | 1.6007 | 1.309 | 0.87813 | 0.69837 | 0.59888
14h30 | 115.67 | 92.53 | 65.41 | 52.87 | 46.26 | 14h30 | 1.4459 | 1.1566 | 0.81763 | 0.66087 | 0.57825
15h30 | 108.61 | 85.58 | 58.91 | 44.3 | 37.41 | 15h30 | 1.3576 | 1.0697 | 0.73638 | 0.55375 | 0.46763
16h30 | 100.07 | 79.33 | 58.91 | 44.3 | 37.41 | 16h30 | 1.2509 | 0.99162 | 0.73638 | 0.55375 | 0.46763
17h30 | 100.34 | 77.24 | 54.28 | 39.17 | 33.04 | 17h30 | 1.2543 | 0.9655 | 0.6785 | 0.48962 | 0.413
18h30 | 112.46 | 89.26 | 62.06 | 46.98 | 40.28 | 18h30 | 1.4058 | 1.1158 | 0.77575 | 0.58725 | 0.5035
19h30 | 108.48 | 85.24 | 59.37 | 44.41 | 38 | 19h30 | 1.356 | 1.0655 | 0.74213 | 0.55512 | 0.475
20h30 | 88.54 | 73.22 | 51.59 | 36.6 | 30.77 | 20h30 | 1.1067 | 0.91525 | 0.64487 | 0.4575 | 0.38462
21h30 | 86.12 | 62.44 | 45.76 | 30.6 | 25.48 | 21h30 | 1.0765 | 0.7805 | 0.572 | 0.3825 | 0.3185
22h30 | 93.95 | 70.69 | 51.01 | 35.77 | 30.25 | 22h30 | 1.1744 | 0.88362 | 0.63762 | 0.44712 | 0.37812
23h30 | 106.11 | 82.08 | 58.29 | 42.25 | 36.16 | 23h30 | 1.3264 | 1.026 | 0.72862 | 0.52812 | 0.452
00h30 | 104.68 | 81.51 | 53.04 | 37.08 | 31.39 | 00h30 | 1.3085 | 1.0189 | 0.663 | 0.4635 | 0.39237
01h30 | 106.63 | 85.01 | 56.79 | 41.92 | 35.86 | 01h30 | 1.3329 | 1.0626 | 0.70988 | 0.524 | 0.44825
02h30 | 88.12 | 77.33 | 56.79 | 41.92 | 35.86 | 02h30 | 1.1015 | 0.96662 | 0.70988 | 0.524 | 0.44825
03h30 | 58.67 | 34.01 | 25.03 | 9.7 | 4.69 | 03h30 | 0.73337 | 0.42512 | 0.31288 | 0.12125 | 0.058625
04h30 | 58.67 | 34.01 | 25.03 | 9.7 | 6.64 | 04h30 | 0.73337 | 0.42512 | 0.31288 | 0.12125 | 0.083
05h30 | 54.3 | 29.53 | 23.99 | 10.91 | 7.79 | 05h30 | 0.67875 | 0.36912 | 0.29988 | 0.13637 | 0.097375
06h30 | 59.77 | 35.33 | 27.42 | 14.21 | 10.62 | 06h30 | 0.74713 | 0.44162 | 0.34275 | 0.17763 | 0.13275
07h30 | 94.58 | 68.29 | 53.29 | 39.15 | 33.91 | 07h30 | 1.1823 | 0.85362 | 0.66612 | 0.48938 | 0.42388
08h30 | 131.07 | 103.16 | 72.49 | 56.81 | 49.08 | 08h30 | 1.6384 | 1.2895 | 0.90612 | 0.71013 | 0.6135
09h30 | 141.96 | 140.67 | 97.91 | 81.2 | 71.56 | 09h30 | 1.7745 | 1.7584 | 1.2239 | 1.015 | 0.8945
10h30 | 181.37 | 160.66 | 108.24 | 90.14 | 79.5 | 10h30 | 2.2671 | 2.0082 | 1.353 | 1.1267 | 0.99375
11h30 | 181.37 | 160.66 | 109.06 | 90.59 | 79.7 | 11h30 | 2.2671 | 2.0082 | 1.3633 | 1.1324 | 0.99625
12h30 | 180.12 | 153.52 | 102.68 | 84.61 | 74.02 | 12h30 | 2.2515 | 1.919 | 1.2835 | 1.0576 | 0.92525
13h30 | 152.03 | 125.22 | 85 | 67.29 | 58.19 | 13h30 | 1.9004 | 1.5653 | 1.0625 | 0.84113 | 0.72737
14h30 | 142.76 | 116.08 | 79.22 | 61.73 | 53.08 | 14h30 | 1.7845 | 1.451 | 0.99025 | 0.77163 | 0.6635
15h30 | 160.57 | 134.39 | 90.38 | 72.9 | 63.23 | 15h30 | 2.0071 | 1.6799 | 1.1298 | 0.91125 | 0.79038
16h30 | 166.7 | 140.91 | 94.59 | 77.05 | 67.11 | 16h30 | 2.0838 | 1.7614 | 1.1824 | 0.96313 | 0.83888
17h30 | 168.51 | 143.13 | 96.11 | 78.56 | 68.61 | 17h30 | 2.1064 | 1.7891 | 1.2014 | 0.982 | 0.85762
18h30 | 170.34 | 145.36 | 97.63 | 79.8 | 69.86 | 18h30 | 2.1292 | 1.817 | 1.2204 | 0.9975 | 0.87325
19h30 | 153.34 | 128.68 | 87.64 | 69.85 | 60.87 | 19h30 | 1.9167 | 1.6085 | 1.0955 | 0.87313 | 0.76087
20h30 | 116.62 | 92.16 | 65.22 | 48.54 | 41.64 | 20h30 | 1.4578 | 1.152 | 0.81525 | 0.60675 | 0.5205
21h30 | 93.81 | 69.48 | 50.93 | 35.58 | 29.96 | 21h30 | 1.1726 | 0.8685 | 0.63662 | 0.44475 | 0.3745
22h30 | 109.21 | 85.03 | 60.04 | 44.92 | 38.33 | 22h30 | 1.3651 | 1.0629 | 0.7505 | 0.5615 | 0.47913
23h30 | 145.99 | 121.99 | 82.68 | 66.41 | 57.62 | 23h30 | 1.8249 | 1.5249 | 1.0335 | 0.83013 | 0.72025
00h30 | 144.65 | 121.98 | 77.06 | 60.2 | 50.39 | 00h30 | 1.8081 | 1.5248 | 0.96325 | 0.7525 | 0.62987
01h30 | 146.39 | 125.17 | 81.47 | 65.57 | 56.17 | 01h30 | 1.8299 | 1.5646 | 1.0184 | 0.81963 | 0.70212
02h30 | 129.62 | 108.25 | 73.87 | 59.98 | 52.03 | 02h30 | 1.6202 | 1.3531 | 0.92337 | 0.74975 | 0.65038
03h30 | 110.96 | 89.01 | 60.41 | 43.96 | 36.38 | 03h30 | 1.387 | 1.1126 | 0.75513 | 0.5495 | 0.45475
04h30 | 111.94 | 89.65 | 61.36 | 45.19 | 37.92 | 04h30 | 1.3993 | 1.1206 | 0.767 | 0.56488 | 0.474
05h30 | 79.31 | 56.77 | 41.84 | 25.18 | 20.11 | 05h30 | 0.99138 | 0.70962 | 0.523 | 0.31475 | 0.25138
06h30 | 85.53 | 62.8 | 45.9 | 28.88 | 23.38 | 06h30 | 1.0691 | 0.785 | 0.57375 | 0.361 | 0.29225
07h30 | 146.58 | 121.89 | 92.77 | 74 | 64.85 | 07h30 | 1.8322 | 1.5236 | 1.1596 | 0.925 | 0.81063
08h30 | 108.58 | 100 | 87.76 | 69.07 | 60.03 | 08h30 | 1.3573 | 1.25 | 1.097 | 0.86338 | 0.75038
09h30 | 58.41 | 31.59 | 31.21 | 9.5 | 6.13 | 09h30 | 0.73013 | 0.39487 | 0.39012 | 0.11875 | 0.076625
10h30 | 56.41 | 32.19 | 31.32 | 10.83 | 7.59 | 10h30 | 0.70513 | 0.40237 | 0.3915 | 0.13537 | 0.094875
11h30 | 54.41 | 29.48 | 28.49 | 7.88 | 4.82 | 11h30 | 0.68012 | 0.3685 | 0.35613 | 0.0985 | 0.06025
12h30 | 109.76 | 85.65 | 61.74 | 42.01 | 35.24 | 12h30 | 1.372 | 1.0706 | 0.77175 | 0.52512 | 0.4405
13h30 | 108.02 | 84.43 | 60.62 | 41.37 | 34.62 | 13h30 | 1.3502 | 1.0554 | 0.75775 | 0.51712 | 0.43275
14h30 | 49.55 | 27.67 | 27.26 | 6.55 | 3.48 | 14h30 | 0.61938 | 0.34587 | 0.34075 | 0.081875 | 0.0435
15h30 | 49.92 | 27 | 26.43 | 7.09 | 3.98 | 15h30 | 0.624 | 0.3375 | 0.33037 | 0.088625 | 0.04975
16h30 | 50.46 | 28.04 | 27.53 | 7.77 | 4.63 | 16h30 | 0.63075 | 0.3505 | 0.34413 | 0.097125 | 0.057875
17h30 | 49.41 | 27.11 | 26.62 | 7.99 | 4.85 | 17h30 | 0.61762 | 0.33887 | 0.33275 | 0.099875 | 0.060625
18h30 | 48.55 | 26.56 | 26.1 | 7.83 | 4.73 | 18h30 | 0.60688 | 0.332 | 0.32625 | 0.097875 | 0.059125
19h30 | 48.65 | 26.93 | 26.5 | 7.75 | 4.66 | 19h30 | 0.60813 | 0.33663 | 0.33125 | 0.096875 | 0.05825
20h30 | 48.38 | 26.84 | 26.44 | 7.71 | 4.61 | 20h30 | 0.60475 | 0.3355 | 0.3305 | 0.096375 | 0.057625
21h30 | 47.75 | 26.35 | 25.98 | 7.5 | 4.4 | 21h30 | 0.59688 | 0.32937 | 0.32475 | 0.09375 | 0.055
22h30 | 47.15 | 25.96 | 25.55 | 7.16 | 4.06 | 22h30 | 0.58937 | 0.3245 | 0.31938 | 0.0895 | 0.05075
23h30 | 47.21 | 26.12 | 25.81 | 6.87 | 3.74 | 23h30 | 0.59013 | 0.3265 | 0.32262 | 0.085875 | 0.04675
00h30 | 44.95 | 26.12 | 25.72 | 6.09 | 2.88 | 00h30 | 0.56188 | 0.3265 | 0.3215 | 0.076125 | 0.036
01h30 | 33.45 | 13.7 | 13.46 | 0 | 0 | 01h30 | 0.41813 | 0.17125 | 0.16825 | 0 | 0
02h30 | 33.45 | 14.41 | 14.19 | 0 | 0 | 02h30 | 0.41813 | 0.18013 | 0.17738 | 0 | 0
03h30 | 32.54 | 13.88 | 13.67 | 0 | 0 | 03h30 | 0.40675 | 0.1735 | 0.17087 | 0 | 0
04h30 | 33.6 | 14.64 | 14.44 | 0 | 0 | 04h30 | 0.42 | 0.183 | 0.1805 | 0 | 0
05h30 | 71.65 | 52.65 | 37.38 | 22.56 | 15.33 | 05h30 | 0.89563 | 0.65812 | 0.46725 | 0.282 | 0.19162
06h30 | 106.34 | 87.3 | 58.31 | 43.68 | 34.53 | 06h30 | 1.3293 | 1.0913 | 0.72888 | 0.546 | 0.43162
07h30 | 120.79 | 100.38 | 72.23 | 56.05 | 46.45 | 07h30 | 1.5099 | 1.2548 | 0.90287 | 0.70063 | 0.58062
08h30 | 117.91 | 96.51 | 67.95 | 50.7 | 41.03 | 08h30 | 1.4739 | 1.2064 | 0.84937 | 0.63375 | 0.51287
09h30 | 81.71 | 61.14 | 46.81 | 30.22 | 23.84 | 09h30 | 1.0214 | 0.76425 | 0.58513 | 0.37775 | 0.298
10h30 | 82.67 | 62.89 | 46.64 | 30.5 | 23.66 | 10h30 | 1.0334 | 0.78612 | 0.583 | 0.38125 | 0.29575
11h30 | 120.31 | 101.15 | 68.7 | 53.01 | 42.74 | 11h30 | 1.5039 | 1.2644 | 0.85875 | 0.66263 | 0.53425
12h30 | 121.88 | 103.3 | 69.3 | 54 | 43.33 | 12h30 | 1.5235 | 1.2913 | 0.86625 | 0.675 | 0.54163
13h30 | 121.93 | 103.93 | 69.18 | 54.12 | 43.21 | 13h30 | 1.5241 | 1.2991 | 0.86475 | 0.6765 | 0.54012
14h30 | 86.53 | 67.77 | 50.6 | 37.07 | 29.02 | 14h30 | 1.0816 | 0.84713 | 0.6325 | 0.46337 | 0.36275
15h30 | 34.51 | 16.97 | 16.83 | 0.44 | 0 | 15h30 | 0.43138 | 0.21213 | 0.21038 | 0.0055 | 0
16h30 | 36.22 | 19.66 | 19.52 | 3.28 | 0 | 16h30 | 0.45275 | 0.24575 | 0.244 | 0.041 | 0
17h30 | 36.14 | 20.14 | 20.01 | 3.05 | 0 | 17h30 | 0.45175 | 0.25175 | 0.25012 | 0.038125 | 0
18h30 | 36.28 | 20.57 | 20.45 | 3.39 | 0 | 18h30 | 0.4535 | 0.25712 | 0.25562 | 0.042375 | 0
19h30 | 35.67 | 20.25 | 20.13 | 3.25 | 0 | 19h30 | 0.44588 | 0.25312 | 0.25162 | 0.040625 | 0
20h30 | 35.36 | 20.15 | 20.04 | 3.04 | 0 | 20h30 | 0.442 | 0.25188 | 0.2505 | 0.038 | 0
21h30 | 35.22 | 20.16 | 20.05 | 2.98 | 0 | 21h30 | 0.44025 | 0.252 | 0.25062 | 0.03725 | 0
22h30 | 35.09 | 20.14 | 20.03 | 2.85 | 0 | 22h30 | 0.43862 | 0.25175 | 0.25038 | 0.035625 | 0
23h30 | 35.01 | 20.15 | 20.05 | 2.85 | 0 | 23h30 | 0.43762 | 0.25188 | 0.25062 | 0.035625 | 0
00h30 | 33.6 | 17.16 | 17.04 | 0 | 0 | 00h30 | 0.42 | 0.2145 | 0.213 | 0 | 0
01h30 | 21.41 | 8.01 | 7.92 | 0 | 0 | 01h30 | 0.26763 | 0.10013 | 0.099 | 0 | 0
02h30 | 22.47 | 9.65 | 9.57 | 0 | 0 | 02h30 | 0.28087 | 0.12062 | 0.11962 | 0 | 0
03h30 | 23.21 | 10.36 | 10.28 | 0 | 0 | 03h30 | 0.29013 | 0.1295 | 0.1285 | 0 | 0
04h30 | 25.8 | 12.56 | 12.48 | 0 | 0 | 04h30 | 0.3225 | 0.157 | 0.156 | 0 | 0
05h30 | 26.84 | 13.26 | 13.18 | 0 | 0 | 05h30 | 0.3355 | 0.16575 | 0.16475 | 0 | 0
06h30 | 26.95 | 13.04 | 12.96 | 0 | 0 | 06h30 | 0.33687 | 0.163 | 0.162 | 0 | 0
07h30 | 43.93 | 28.54 | 28.46 | 10.92 | 6.26 | 07h30 | 0.54912 | 0.35675 | 0.35575 | 0.1365 | 0.07825
08h30 | 41.31 | 24.93 | 24.83 | 10.92 | 6.26 | 08h30 | 0.51638 | 0.31162 | 0.31038 | 0.1365 | 0.07825
09h30 | 40.39 | 24.29 | 24.2 | 4.71 | 0.05 | 09h30 | 0.50487 | 0.30362 | 0.3025 | 0.058875 | 0.000625
10h30 | 39.24 | 24.29 | 24.2 | 4.71 | 0.05 | 10h30 | 0.4905 | 0.30362 | 0.3025 | 0.058875 | 0.000625
11h30 | 31.64 | 15.83 | 15.75 | 0.05 | 0 | 11h30 | 0.3955 | 0.19787 | 0.19687 | 0.000625 | 0
12h30 | 31.64 | 15.83 | 15.75 | 0.05 | 0 | 12h30 | 0.3955 | 0.19787 | 0.19687 | 0.000625 | 0
13h30 | 27.15 | 12.36 | 12.29 | 0 | 0 | 13h30 | 0.33937 | 0.1545 | 0.15363 | 0 | 0
14h30 | 27.15 | 12.36 | 12.29 | 0 | 0 | 14h30 | 0.33937 | 0.1545 | 0.15363 | 0 | 0
15h30 | 26.99 | 12.85 | 12.78 | 0 | 0 | 15h30 | 0.33737 | 0.16062 | 0.15975 | 0 | 0
16h30 | 58.76 | 44.7 | 32.58 | 16.79 | 9.1 | 16h30 | 0.7345 | 0.55875 | 0.40725 | 0.20988 | 0.11375
17h30 | 88.79 | 74.89 | 50.95 | 36.03 | 27.3 | 17h30 | 1.1099 | 0.93612 | 0.63687 | 0.45038 | 0.34125
18h30 | 102.55 | 88.78 | 59.38 | 44.53 | 35.04 | 18h30 | 1.2819 | 1.1098 | 0.74225 | 0.55663 | 0.438
19h30 | 140.05 | 126.39 | 82.45 | 66.78 | 54.9 | 19h30 | 1.7506 | 1.5799 | 1.0306 | 0.83475 | 0.68625
20h30 | 157.38 | 143.69 | 93.23 | 76.98 | 63.96 | 20h30 | 1.9672 | 1.7961 | 1.1654 | 0.96225 | 0.7995
21h30 | 136.72 | 122.87 | 80.65 | 64.79 | 53.4 | 21h30 | 1.709 | 1.5359 | 1.0081 | 0.80988 | 0.6675
22h30 | 130.1 | 115.97 | 76.41 | 60.86 | 50.26 | 22h30 | 1.6262 | 1.4496 | 0.95513 | 0.76075 | 0.62825
23h30 | 135 | 120.55 | 79.1 | 63.79 | 52.82 | 23h30 | 1.6875 | 1.5069 | 0.98875 | 0.79737 | 0.66025
00h30 | 97.5 | 83.62 | 50.53 | 36.89 | 30.06 | 00h30 | 1.2188 | 1.0453 | 0.63162 | 0.46113 | 0.37575
01h30 | 85.18 | 72.2 | 46.07 | 34.62 | 26.39 | 01h30 | 1.0648 | 0.9025 | 0.57588 | 0.43275 | 0.32987
02h30 | 90.49 | 77.16 | 49.39 | 38.31 | 29.96 | 02h30 | 1.1311 | 0.9645 | 0.61738 | 0.47887 | 0.3745
03h30 | 100.04 | 85.8 | 55.18 | 43.35 | 34.47 | 03h30 | 1.2505 | 1.0725 | 0.68975 | 0.54187 | 0.43088
04h30 | 103.51 | 88.56 | 57.31 | 44.71 | 36.1 | 04h30 | 1.2939 | 1.107 | 0.71637 | 0.55888 | 0.45125
05h30 | 101.31 | 85.71 | 56.01 | 42.81 | 34.8 | 05h30 | 1.2664 | 1.0714 | 0.70012 | 0.53512 | 0.435
06h30 | 104.55 | 88.36 | 58.05 | 44.29 | 36.28 | 06h30 | 1.3069 | 1.1045 | 0.72562 | 0.55363 | 0.4535
07h30 | 114.83 | 96.66 | 69.26 | 52.91 | 45.01 | 07h30 | 1.4354 | 1.2083 | 0.86575 | 0.66138 | 0.56263
08h30 | 103.73 | 84.02 | 59.68 | 42.03 | 38.33 | 08h30 | 1.2966 | 1.0502 | 0.746 | 0.52538 | 0.47913
09h30 | 114.96 | 95.59 | 66.88 | 50.11 | 40.61 | 09h30 | 1.437 | 1.1949 | 0.836 | 0.62638 | 0.50762
10h30 | 112.42 | 93.36 | 64.3 | 49.78 | 40.61 | 10h30 | 1.4053 | 1.167 | 0.80375 | 0.62225 | 0.50762
11h30 | 98.74 | 79.98 | 54.73 | 39.41 | 30.48 | 11h30 | 1.2343 | 0.99975 | 0.68412 | 0.49262 | 0.381
12h30 | 95.84 | 77.33 | 53.19 | 39.41 | 30.48 | 12h30 | 1.198 | 0.96662 | 0.66487 | 0.49262 | 0.381
13h30 | 97.74 | 79.42 | 53.23 | 38.5 | 29.45 | 13h30 | 1.2217 | 0.99275 | 0.66538 | 0.48125 | 0.36812
14h30 | 95.98 | 77.88 | 53.23 | 38.5 | 29.45 | 14h30 | 1.1998 | 0.9735 | 0.66538 | 0.48125 | 0.36812
15h30 | 97.73 | 79.85 | 53.57 | 38.99 | 29.9 | 15h30 | 1.2216 | 0.99813 | 0.66963 | 0.48738 | 0.37375
16h30 | 102.86 | 85.19 | 57.31 | 42.37 | 33.15 | 16h30 | 1.2857 | 1.0649 | 0.71637 | 0.52963 | 0.41437
17h30 | 104.68 | 87.28 | 58.82 | 43.7 | 34.47 | 17h30 | 1.3085 | 1.091 | 0.73525 | 0.54625 | 0.43088
18h30 | 106.91 | 89.78 | 60.4 | 45.3 | 35.91 | 18h30 | 1.3364 | 1.1222 | 0.755 | 0.56625 | 0.44888
19h30 | 110.63 | 93.72 | 62.8 | 47.65 | 37.97 | 19h30 | 1.3829 | 1.1715 | 0.785 | 0.59562 | 0.47463
20h30 | 112.36 | 95.6 | 64.04 | 48.66 | 39 | 20h30 | 1.4045 | 1.195 | 0.8005 | 0.60825 | 0.4875
21h30 | 73.39 | 56.71 | 40.87 | 25.22 | 18.73 | 21h30 | 0.91738 | 0.70888 | 0.51087 | 0.31525 | 0.23412
22h30 | 51.87 | 36.48 | 34.3 | 19.21 | 13.01 | 22h30 | 0.64838 | 0.456 | 0.42875 | 0.24013 | 0.16262
23h30 | 33.73 | 15.76 | 16 | 0 | 0 | 23h30 | 0.42163 | 0.197 | 0.2 | 0 | 0
00h30 | 33.73 | 15.76 | 16 | 0 | 0 | 00h30 | 0.42163 | 0.197 | 0.2 | 0 | 0
01h30 | 19.86 | 5.03 | 5 | 0 | 0 | 01h30 | 0.24825 | 0.062875 | 0.0625 | 0 | 0
02h30 | 23.05 | 8.92 | 8.91 | 0 | 0 | 02h30 | 0.28813 | 0.1115 | 0.11138 | 0 | 0
03h30 | 23.04 | 8.73 | 8.71 | 0 | 0 | 03h30 | 0.288 | 0.10912 | 0.10887 | 0 | 0
04h30 | 24.2 | 9.3 | 9.28 | 0 | 0 | 04h30 | 0.3025 | 0.11625 | 0.116 | 0 | 0
05h30 | 25.51 | 10.22 | 10.2 | 0 | 0 | 05h30 | 0.31888 | 0.12775 | 0.1275 | 0 | 0
06h30 | 27.09 | 11.52 | 11.49 | 0 | 0 | 06h30 | 0.33863 | 0.144 | 0.14363 | 0 | 0
07h30 | 105.93 | 99.96 | 70.66 | 52.71 | 41.76 | 07h30 | 1.3241 | 1.2495 | 0.88325 | 0.65887 | 0.522
08h30 | 173.91 | 158.58 | 103.08 | 86.34 | 70.65 | 08h30 | 2.1739 | 1.9823 | 1.2885 | 1.0793 | 0.88313
09h30 | 163.71 | 145.89 | 94.52 | 78.92 | 63.6 | 09h30 | 2.0464 | 1.8236 | 1.1815 | 0.9865 | 0.795
10h30 | 159.24 | 141.39 | 90.26 | 75.23 | 60.73 | 10h30 | 1.9905 | 1.7674 | 1.1282 | 0.94037 | 0.75913
11h30 | 167.97 | 150.77 | 95.59 | 80.2 | 65.05 | 11h30 | 2.0996 | 1.8846 | 1.1949 | 1.0025 | 0.81312
12h30 | 177.11 | 160.42 | 101.18 | 85.89 | 69.98 | 12h30 | 2.2139 | 2.0053 | 1.2648 | 1.0736 | 0.87475
13h30 | 178.58 | 163.16 | 102.14 | 87.48 | 71.11 | 13h30 | 2.2323 | 2.0395 | 1.2768 | 1.0935 | 0.88887
14h30 | 188.18 | 173.03 | 107.51 | 93.19 | 76.06 | 14h30 | 2.3523 | 2.1629 | 1.3439 | 1.1649 | 0.95075
15h30 | 188.18 | 179.39 | 112.17 | 97.45 | 80.29 | 15h30 | 2.3523 | 2.2424 | 1.4021 | 1.2181 | 1.0036
16h30 | 184.12 | 171.32 | 107.91 | 92.58 | 76.79 | 16h30 | 2.3015 | 2.1415 | 1.3489 | 1.1572 | 0.95988
17h30 | 163.66 | 149.11 | 95.08 | 79.68 | 66.06 | 17h30 | 2.0457 | 1.8639 | 1.1885 | 0.996 | 0.82575
18h30 | 145.23 | 130.44 | 83.96 | 68.86 | 56.82 | 18h30 | 1.8154 | 1.6305 | 1.0495 | 0.86075 | 0.71025
19h30 | 136.24 | 121.67 | 78.87 | 63.64 | 52.69 | 19h30 | 1.703 | 1.5209 | 0.98587 | 0.7955 | 0.65863
20h30 | 125.62 | 111.03 | 72.88 | 57.13 | 47.34 | 20h30 | 1.5702 | 1.3879 | 0.911 | 0.71413 | 0.59175
21h30 | 129.58 | 114.83 | 75.68 | 59.25 | 49.68 | 21h30 | 1.6198 | 1.4354 | 0.946 | 0.74062 | 0.621
22h30 | 139.96 | 124.96 | 82.35 | 65.13 | 55.27 | 22h30 | 1.7495 | 1.562 | 1.0294 | 0.81412 | 0.69088
23h30 | 121.44 | 106.1 | 71.38 | 53.85 | 45.23 | 23h30 | 1.518 | 1.3262 | 0.89225 | 0.67312 | 0.56537
00h30 | 98.07 | 83.31 | 51.71 | 35.3 | 27.46 | 00h30 | 1.2259 | 1.0414 | 0.64638 | 0.44125 | 0.34325
01h30 | 128.77 | 114.9 | 73.28 | 58.88 | 49.33 | 01h30 | 1.6096 | 1.4363 | 0.916 | 0.736 | 0.61662
02h30 | 141.27 | 126.92 | 80.72 | 66.97 | 56.3 | 02h30 | 1.7659 | 1.5865 | 1.009 | 0.83713 | 0.70375
03h30 | 117.62 | 102.22 | 66.29 | 52.15 | 43.22 | 03h30 | 1.4703 | 1.2777 | 0.82862 | 0.65187 | 0.54025
04h30 | 91.79 | 75.51 | 50.56 | 37.59 | 30.62 | 04h30 | 1.1474 | 0.94388 | 0.632 | 0.46987 | 0.38275
05h30 | 87.77 | 70.67 | 48.04 | 32.35 | 26.52 | 05h30 | 1.0971 | 0.88338 | 0.6005 | 0.40437 | 0.3315
06h30 | 90.23 | 72.38 | 49.46 | 34 | 28.02 | 06h30 | 1.1279 | 0.90475 | 0.61825 | 0.425 | 0.35025
07h30 | 118.44 | 98.44 | 71.28 | 53.13 | 45.99 | 07h30 | 1.4805 | 1.2305 | 0.891 | 0.66412 | 0.57488
08h30 | 140.02 | 118.36 | 81.28 | 61.55 | 52.26 | 08h30 | 1.7503 | 1.4795 | 1.016 | 0.76938 | 0.65325
09h30 | 152.78 | 136.29 | 94.63 | 76.38 | 65.4 | 09h30 | 1.9098 | 1.7036 | 1.1829 | 0.95475 | 0.8175
10h30 | 159.14 | 139.69 | 91.84 | 75.1 | 63.59 | 10h30 | 1.9892 | 1.7461 | 1.148 | 0.93875 | 0.79487
11h30 | 146.94 | 126.62 | 81.75 | 66.2 | 54.96 | 11h30 | 1.8368 | 1.5828 | 1.0219 | 0.8275 | 0.687
12h30 | 135.5 | 115.02 | 73.83 | 59.07 | 49 | 12h30 | 1.6938 | 1.4378 | 0.92288 | 0.73838 | 0.6125
13h30 | 131.79 | 111.83 | 71.47 | 57.39 | 46.17 | 13h30 | 1.6474 | 1.3979 | 0.89338 | 0.71737 | 0.57712
14h30 | 128.84 | 109.4 | 69.9 | 55.86 | 46.17 | 14h30 | 1.6105 | 1.3675 | 0.87375 | 0.69825 | 0.57712
15h30 | 115.66 | 96.6 | 62.95 | 48.01 | 38.33 | 15h30 | 1.4458 | 1.2075 | 0.78687 | 0.60013 | 0.47913
16h30 | 70.9 | 70.94 | 61.55 | 47.88 | 38.33 | 16h30 | 0.88625 | 0.88675 | 0.76938 | 0.5985 | 0.47913
17h30 | 36.58 | 15.07 | 13.95 | 0 | 0 | 17h30 | 0.45725 | 0.18837 | 0.17438 | 0 | 0
18h30 | 36.69 | 18.92 | 18.73 | 0.93 | 0 | 18h30 | 0.45863 | 0.2365 | 0.23412 | 0.011625 | 0
19h30 | 36.42 | 17.56 | 17.17 | 0.93 | 0 | 19h30 | 0.45525 | 0.2195 | 0.21463 | 0.011625 | 0
20h30 | 74.38 | 56.01 | 40.56 | 23.33 | 16.78 | 20h30 | 0.92975 | 0.70012 | 0.507 | 0.29163 | 0.20975
21h30 | 74.96 | 56.73 | 41.32 | 23.89 | 17.92 | 21h30 | 0.937 | 0.70913 | 0.5165 | 0.29862 | 0.224
22h30 | 38.05 | 19.83 | 19.59 | 1.45 | 1.14 | 22h30 | 0.47563 | 0.24788 | 0.24488 | 0.018125 | 0.01425
23h30 | 38.63 | 20.34 | 20.12 | 1.7 | 0 | 23h30 | 0.48287 | 0.25425 | 0.2515 | 0.02125 | 0
00h30 | 37.47 | 14.95 | 13.68 | 0.8 | 0 | 00h30 | 0.46837 | 0.18688 | 0.171 | 0.01 | 0
01h30 | 25.93 | 9.53 | 9.53 | 0 | 0 | 01h30 | 0.32412 | 0.11912 | 0.11912 | 0 | 0
02h30 | 90.94 | 74.75 | 49.47 | 31.37 | 21.88 | 02h30 | 1.1367 | 0.93437 | 0.61838 | 0.39213 | 0.2735
03h30 | 157.44 | 141.1 | 89.64 | 74.28 | 61.22 | 03h30 | 1.968 | 1.7637 | 1.1205 | 0.9285 | 0.76525
04h30 | 162.36 | 145.29 | 92.72 | 76.71 | 63.73 | 04h30 | 2.0295 | 1.8161 | 1.159 | 0.95888 | 0.79663
05h30 | 159.88 | 142.31 | 91.4 | 74.76 | 62.6 | 05h30 | 1.9985 | 1.7789 | 1.1425 | 0.9345 | 0.7825
06h30 | 152.9 | 134.9 | 87.35 | 70.2 | 59.03 | 06h30 | 1.9112 | 1.6863 | 1.0919 | 0.8775 | 0.73787
07h30 | 108.48 | 88.65 | 65.66 | 46 | 39.12 | 07h30 | 1.356 | 1.1081 | 0.82075 | 0.575 | 0.489
08h30 | 47.28 | 26.64 | 26.69 | 16.76 | 18.3 | 08h30 | 0.591 | 0.333 | 0.33363 | 0.2095 | 0.22875
09h30 | 84.45 | 63.62 | 48.31 | 27.41 | 18.74 | 09h30 | 1.0556 | 0.79525 | 0.60388 | 0.34263 | 0.23425
10h30 | 108.82 | 88.44 | 61.76 | 44.17 | 35.36 | 10h30 | 1.3602 | 1.1055 | 0.772 | 0.55212 | 0.442
11h30 | 98.92 | 78.85 | 54.81 | 37.5 | 29.17 | 11h30 | 1.2365 | 0.98562 | 0.68512 | 0.46875 | 0.36462
12h30 | 105.32 | 85.74 | 57.93 | 41.54 | 32.25 | 12h30 | 1.3165 | 1.0717 | 0.72413 | 0.51925 | 0.40313
13h30 | 115.35 | 96.25 | 63.57 | 47.55 | 37.2 | 13h30 | 1.4419 | 1.2031 | 0.79463 | 0.59437 | 0.465
14h30 | 123.12 | 104.37 | 68.57 | 52.06 | 41.38 | 14h30 | 1.539 | 1.3046 | 0.85713 | 0.65075 | 0.51725
15h30 | 123.18 | 104.63 | 69.33 | 52.29 | 42.03 | 15h30 | 1.5397 | 1.3079 | 0.86662 | 0.65363 | 0.52538
16h30 | 118.01 | 99.67 | 66.99 | 49.69 | 40.17 | 16h30 | 1.4751 | 1.2459 | 0.83737 | 0.62113 | 0.50213
17h30 | 76.62 | 58.55 | 42.8 | 25.27 | 22.02 | 17h30 | 0.95775 | 0.73188 | 0.535 | 0.31588 | 0.27525
18h30 | 41.51 | 23.69 | 23.57 | 2.57 | 0 | 18h30 | 0.51887 | 0.29613 | 0.29463 | 0.032125 | 0
19h30 | 39.79 | 22.08 | 22.02 | 2.82 | 0 | 19h30 | 0.49738 | 0.276 | 0.27525 | 0.03525 | 0
20h30 | 40.06 | 22.65 | 22.58 | 3.11 | 0 | 20h30 | 0.50075 | 0.28313 | 0.28225 | 0.038875 | 0
21h30 | 38.4 | 20.93 | 20.87 | 2.96 | 0 | 21h30 | 0.48 | 0.26162 | 0.26088 | 0.037 | 0
22h30 | 38.12 | 20.36 | 20.3 | 2.69 | 0 | 22h30 | 0.4765 | 0.2545 | 0.25375 | 0.033625 | 0
23h30 | 37.92 | 20.21 | 20.15 | 2.62 | 0 | 23h30 | 0.474 | 0.25262 | 0.25188 | 0.03275 | 0
00h30 | 37.92 | 20.21 | 20.15 | 2.61 | 0 | 00h30 | 0.474 | 0.25262 | 0.25188 | 0.032625 | 0
01h30 | 25.21 | 8.4 | 8.35 | 0 | 0 | 01h30 | 0.31512 | 0.105 | 0.10437 | 0 | 0
02h30 | 26.66 | 10.81 | 10.77 | 0 | 0 | 02h30 | 0.33325 | 0.13512 | 0.13462 | 0 | 0
03h30 | 26.51 | 10.38 | 10.34 | 0 | 0 | 03h30 | 0.33137 | 0.12975 | 0.12925 | 0 | 0
04h30 | 27.9 | 11.11 | 11.07 | 0 | 0 | 04h30 | 0.34875 | 0.13887 | 0.13837 | 0 | 0
05h30 | 29.56 | 12.32 | 12.28 | 0 | 0 | 05h30 | 0.3695 | 0.154 | 0.1535 | 0 | 0
06h30 | 30.93 | 13.32 | 13.28 | 0 | 0 | 06h30 | 0.38662 | 0.1665 | 0.166 | 0 | 0
07h30 | 47.57 | 28.15 | 28.11 | 10.84 | 5.9 | 07h30 | 0.59462 | 0.35187 | 0.35137 | 0.1355 | 0.07375
08h30 | 44.21 | 24 | 23.95 | 10.84 | 5.9 | 08h30 | 0.55263 | 0.3 | 0.29938 | 0.1355 | 0.07375
09h30 | 44.62 | 24.4 | 24.35 | 4.83 | 0 | 09h30 | 0.55775 | 0.305 | 0.30438 | 0.060375 | 0
10h30 | 64.97 | 45.28 | 35.28 | 18.5 | 12.17 | 10h30 | 0.81212 | 0.566 | 0.441 | 0.23125 | 0.15213
11h30 | 92.46 | 73.12 | 50.38 | 34.95 | 26.47 | 11h30 | 1.1558 | 0.914 | 0.62975 | 0.43688 | 0.33087
12h30 | 93.36 | 74.36 | 50.12 | 35.91 | 27.15 | 12h30 | 1.167 | 0.9295 | 0.6265 | 0.44888 | 0.33937
13h30 | 82.71 | 64.03 | 43.26 | 30 | 22.01 | 13h30 | 1.0339 | 0.80037 | 0.54075 | 0.375 | 0.27513
14h30 | 72.31 | 54 | 37.13 | 23.98 | 16.87 | 14h30 | 0.90387 | 0.675 | 0.46413 | 0.29975 | 0.21088
15h30 | 50.07 | 32.1 | 24.49 | 10.63 | 7.7 | 15h30 | 0.62587 | 0.40125 | 0.30612 | 0.13287 | 0.09625
16h30 | 38.35 | 20 | 19.96 | 2.03 | 0 | 16h30 | 0.47937 | 0.25 | 0.2495 | 0.025375 | 0
17h30 | 33.89 | 16.25 | 16.21 | 0.8 | 0 | 17h30 | 0.42362 | 0.20312 | 0.20262 | 0.01 | 0
18h30 | 34.47 | 17.43 | 17.39 | 1.61 | 0 | 18h30 | 0.43088 | 0.21788 | 0.21738 | 0.020125 | 0
19h30 | 52.49 | 35.71 | 28 | 12.96 | 7.04 | 19h30 | 0.65612 | 0.44638 | 0.35 | 0.162 | 0.088
20h30 | 64.34 | 47.59 | 34.88 | 20.39 | 14.14 | 20h30 | 0.80425 | 0.59488 | 0.436 | 0.25488 | 0.17675
21h30 | 62.92 | 46.16 | 33.81 | 19.82 | 13.63 | 21h30 | 0.7865 | 0.577 | 0.42262 | 0.24775 | 0.17037
22h30 | 67.42 | 50.62 | 36.41 | 22.62 | 16.34 | 22h30 | 0.84275 | 0.63275 | 0.45513 | 0.28275 | 0.20425
23h30 | 59.12 | 42.22 | 31.32 | 17.77 | 12.18 | 23h30 | 0.739 | 0.52775 | 0.3915 | 0.22212 | 0.15225
00h30 | 42.19 | 24.72 | 20.65 | 6.72 | 2.38 | 00h30 | 0.52738 | 0.309 | 0.25812 | 0.084 | 0.02975
01h30 | 27.89 | 12.67 | 9.44 | 0 | 0 | 01h30 | 0.34863 | 0.15837 | 0.118 | 0 | 0
02h30 | 27.89 | 12.67 | 9.44 | 0 | 0 | 02h30 | 0.34863 | 0.15837 | 0.118 | 0 | 0
03h30 | 34.9 | 19.01 | 15.11 | 2.14 | 0 | 03h30 | 0.43625 | 0.23763 | 0.18887 | 0.02675 | 0
04h30 | 53.83 | 37.83 | 26.03 | 15.04 | 9.42 | 04h30 | 0.67288 | 0.47287 | 0.32538 | 0.188 | 0.11775
05h30 | 66.7 | 50.29 | 34.2 | 22.14 | 16.76 | 05h30 | 0.83375 | 0.62862 | 0.4275 | 0.27675 | 0.2095
06h30 | 82.36 | 65.46 | 44.05 | 30.69 | 24.01 | 06h30 | 1.0295 | 0.81825 | 0.55063 | 0.38362 | 0.30012
07h30 | 113.57 | 94.71 | 67.86 | 51.76 | 43.72 | 07h30 | 1.4196 | 1.1839 | 0.84825 | 0.647 | 0.5465
08h30 | 117.56 | 97.18 | 67.36 | 49.82 | 40.47 | 08h30 | 1.4695 | 1.2147 | 0.842 | 0.62275 | 0.50587
09h30 | 81.17 | 61.25 | 46.04 | 29.42 | 22.34 | 09h30 | 1.0146 | 0.76562 | 0.5755 | 0.36775 | 0.27925
10h30 | 81.57 | 62.05 | 45.39 | 29.22 | 21.79 | 10h30 | 1.0196 | 0.77563 | 0.56737 | 0.36525 | 0.27237
11h30 | 137.6 | 118.41 | 78 | 62.8 | 50.42 | 11h30 | 1.72 | 1.4801 | 0.975 | 0.785 | 0.63025
12h30 | 157.84 | 138.97 | 89.27 | 75.09 | 60.37 | 12h30 | 1.973 | 1.7371 | 1.1159 | 0.93863 | 0.75462
13h30 | 159.22 | 153.98 | 97.54 | 83.89 | 67.86 | 13h30 | 1.9903 | 1.9247 | 1.2192 | 1.0486 | 0.84825
14h30 | 177.82 | 164.08 | 103.13 | 89.89 | 72.95 | 14h30 | 2.2228 | 2.051 | 1.2891 | 1.1236 | 0.91187
15h30 | 177.82 | 167.93 | 105.59 | 92.47 | 75.75 | 15h30 | 2.2228 | 2.0991 | 1.3199 | 1.1559 | 0.94688
16h30 | 177.14 | 161.29 | 102.2 | 88.62 | 73.5 | 16h30 | 2.2142 | 2.0161 | 1.2775 | 1.1078 | 0.91875
17h30 | 158.25 | 140.58 | 90.44 | 76.23 | 63.22 | 17h30 | 1.9781 | 1.7572 | 1.1305 | 0.95288 | 0.79025
18h30 | 131.83 | 114.08 | 75.13 | 60.05 | 49.37 | 18h30 | 1.6479 | 1.426 | 0.93912 | 0.75062 | 0.61713
19h30 | 119.03 | 101.76 | 68.24 | 52.3 | 42.74 | 19h30 | 1.4879 | 1.272 | 0.853 | 0.65375 | 0.53425
20h30 | 135.03 | 118.01 | 78.3 | 61.84 | 51.17 | 20h30 | 1.6879 | 1.4751 | 0.97875 | 0.773 | 0.63962
21h30 | 149.38 | 132.49 | 87.13 | 70.38 | 58.55 | 21h30 | 1.8673 | 1.6561 | 1.0891 | 0.87975 | 0.73188
22h30 | 155.34 | 138.51 | 90.6 | 74.04 | 61.25 | 22h30 | 1.9418 | 1.7314 | 1.1325 | 0.9255 | 0.76562
23h30 | 161.9 | 145.09 | 94.27 | 78.02 | 64.16 | 23h30 | 2.0238 | 1.8136 | 1.1784 | 0.97525 | 0.802
00h30 | 138.24 | 122.42 | 74.39 | 59.22 | 45.69 | 00h30 | 1.728 | 1.5303 | 0.92988 | 0.74025 | 0.57112
01h30 | 145.59 | 131.05 | 81.94 | 69 | 54.93 | 01h30 | 1.8199 | 1.6381 | 1.0243 | 0.8625 | 0.68663
02h30 | 138.91 | 124.25 | 77.74 | 66.2 | 52.76 | 02h30 | 1.7364 | 1.5531 | 0.97175 | 0.8275 | 0.6595
03h30 | 108.48 | 93.2 | 59.19 | 47.85 | 37.53 | 03h30 | 1.356 | 1.165 | 0.73987 | 0.59813 | 0.46913
04h30 | 91.77 | 76.12 | 51.97 | 38.69 | 35.23 | 04h30 | 1.1471 | 0.9515 | 0.64963 | 0.48363 | 0.44038
05h30 | 77.52 | 61.56 | 40.48 | 28.48 | 20.6 | 05h30 | 0.969 | 0.7695 | 0.506 | 0.356 | 0.2575
06h30 | 67.64 | 51.38 | 40.48 | 28.48 | 20.6 | 06h30 | 0.8455 | 0.64225 | 0.506 | 0.356 | 0.2575
07h30 | 95.7 | 77.71 | 56.21 | 42.46 | 35.32 | 07h30 | 1.1963 | 0.97137 | 0.70263 | 0.53075 | 0.4415
08h30 | 114.79 | 95.61 | 65.09 | 51.36 | 41.25 | 08h30 | 1.4349 | 1.1951 | 0.81363 | 0.642 | 0.51562
09h30 | 123.4 | 105.11 | 68.87 | 56.17 | 46.13 | 09h30 | 1.5425 | 1.3139 | 0.86087 | 0.70212 | 0.57663
10h30 | 118.56 | 101.06 | 64.6 | 52.74 | 42.63 | 10h30 | 1.482 | 1.2632 | 0.8075 | 0.65925 | 0.53287
11h30 | 120.38 | 103.23 | 65.47 | 53.34 | 43.08 | 11h30 | 1.5048 | 1.2904 | 0.81837 | 0.66675 | 0.5385
12h30 | 124.47 | 107.49 | 68.23 | 56.06 | 45.33 | 12h30 | 1.5559 | 1.3436 | 0.85288 | 0.70075 | 0.56663
13h30 | 118.34 | 101.68 | 64.66 | 53.04 | 42.61 | 13h30 | 1.4792 | 1.271 | 0.80825 | 0.663 | 0.53263
14h30 | 101.68 | 85.42 | 57.29 | 44.85 | 37.93 | 14h30 | 1.271 | 1.0677 | 0.71613 | 0.56063 | 0.47413
15h30 | 87.17 | 71.2 | 46.26 | 34.71 | 26.54 | 15h30 | 1.0896 | 0.89 | 0.57825 | 0.43388 | 0.33175
16h30 | 69.73 | 69.02 | 46.26 | 34.71 | 26.54 | 16h30 | 0.87162 | 0.86275 | 0.57825 | 0.43388 | 0.33175
17h30 | 36.31 | 18.12 | 15.07 | 1.76 | 0 | 17h30 | 0.45387 | 0.2265 | 0.18837 | 0.022 | 0
18h30 | 38.95 | 23.3 | 18.7 | 6.89 | 2.66 | 18h30 | 0.48688 | 0.29125 | 0.23375 | 0.086125 | 0.03325
19h30 | 51.12 | 34.8 | 25.73 | 13.48 | 9.01 | 19h30 | 0.639 | 0.435 | 0.32162 | 0.1685 | 0.11263
20h30 | 48.94 | 32.78 | 25.07 | 11.91 | 7.47 | 20h30 | 0.61175 | 0.40975 | 0.31338 | 0.14888 | 0.093375
21h30 | 41.35 | 25.07 | 20.37 | 7.69 | 3.77 | 21h30 | 0.51687 | 0.31338 | 0.25462 | 0.096125 | 0.047125
22h30 | 40.89 | 21.92 | 17.4 | 4.13 | 2.64 | 22h30 | 0.51113 | 0.274 | 0.2175 | 0.051625 | 0.033
23h30 | 29.64 | 12.9 | 13.34 | 0.26 | 0 | 23h30 | 0.3705 | 0.16125 | 0.16675 | 0.00325 | 0
00h30 | 30.24 | 14.5 | 13.34 | 0.26 | 0 | 00h30 | 0.378 | 0.18125 | 0.16675 | 0.00325 | 0
01h30 | 49.76 | 35.5 | 23.08 | 12.57 | 7.01 | 01h30 | 0.622 | 0.44375 | 0.2885 | 0.15712 | 0.087625
02h30 | 55.99 | 41.36 | 27.08 | 18.04 | 12.99 | 02h30 | 0.69988 | 0.517 | 0.3385 | 0.2255 | 0.16237
03h30 | 67.48 | 51.94 | 33.5 | 24.01 | 17.49 | 03h30 | 0.8435 | 0.64925 | 0.41875 | 0.30012 | 0.21863
04h30 | 66.03 | 49.83 | 32.86 | 22.4 | 16.35 | 04h30 | 0.82537 | 0.62287 | 0.41075 | 0.28 | 0.20438
05h30 | 58.17 | 41.39 | 28.22 | 17.09 | 11.96 | 05h30 | 0.72713 | 0.51738 | 0.35275 | 0.21363 | 0.1495
06h30 | 52.79 | 36.05 | 24.86 | 13.23 | 7.11 | 06h30 | 0.65987 | 0.45062 | 0.31075 | 0.16537 | 0.088875
07h30 | 42.34 | 21.88 | 22.67 | 8.47 | 6.16 | 07h30 | 0.52925 | 0.2735 | 0.28337 | 0.10587 | 0.077
08h30 | 42.34 | 21.88 | 22.67 | 8.47 | 6.16 | 08h30 | 0.52925 | 0.2735 | 0.28337 | 0.10587 | 0.077
09h30 | 64.27 | 43.92 | 33.36 | 19.39 | 13.01 | 09h30 | 0.80337 | 0.549 | 0.417 | 0.24238 | 0.16262
10h30 | 106 | 86.37 | 58.14 | 44.49 | 35 | 10h30 | 1.325 | 1.0796 | 0.72675 | 0.55612 | 0.4375
11h30 | 110.14 | 91 | 59.94 | 46.56 | 36.26 | 11h30 | 1.3767 | 1.1375 | 0.74925 | 0.582 | 0.45325
12h30 | 99.16 | 80.45 | 53.02 | 39.97 | 30.31 | 12h30 | 1.2395 | 1.0056 | 0.66275 | 0.49962 | 0.37888
13h30 | 98.9 | 80.66 | 52.6 | 40.03 | 29.84 | 13h30 | 1.2363 | 1.0083 | 0.6575 | 0.50038 | 0.373
14h30 | 97.4 | 79.61 | 51.63 | 39.45 | 29 | 14h30 | 1.2175 | 0.99513 | 0.64538 | 0.49312 | 0.3625
15h30 | 98.98 | 81.58 | 52.97 | 40.6 | 30.14 | 15h30 | 1.2372 | 1.0197 | 0.66212 | 0.5075 | 0.37675
16h30 | 103.12 | 86.1 | 56.12 | 43.35 | 32.66 | 16h30 | 1.289 | 1.0762 | 0.7015 | 0.54187 | 0.40825
17h30 | 66.91 | 50.31 | 34.96 | 21.96 | 17.72 | 17h30 | 0.83637 | 0.62887 | 0.437 | 0.2745 | 0.2215
18h30 | 33.52 | 14.94 | 14.93 | 1.28 | 0 | 18h30 | 0.419 | 0.18675 | 0.18663 | 0.016 | 0
19h30 | 27.94 | 12.19 | 12.22 | 0 | 0 | 19h30 | 0.34925 | 0.15238 | 0.15275 | 0 | 0
20h30 | 28.03 | 12.63 | 12.64 | 0 | 0 | 20h30 | 0.35037 | 0.15787 | 0.158 | 0 | 0
21h30 | 26.85 | 11.98 | 11.99 | 0 | 0 | 21h30 | 0.33563 | 0.14975 | 0.14988 | 0 | 0
22h30 | 26.77 | 11.68 | 11.7 | 0 | 0 | 22h30 | 0.33463 | 0.146 | 0.14625 | 0 | 0
23h30 | 26.18 | 11.62 | 11.63 | 0 | 0 | 23h30 | 0.32725 | 0.14525 | 0.14538 | 0 | 0
00h30 | 26.18 | 11.48 | 11.51 | 0 | 0 | 00h30 | 0.32725 | 0.1435 | 0.14388 | 0 | 0
01h30 | 45.18 | 32.13 | 19.31 | 6.86 | 0 | 01h30 | 0.56475 | 0.40163 | 0.24138 | 0.08575 | 0
02h30 | 82.5 | 70.7 | 43.84 | 33.54 | 21.98 | 02h30 | 1.0312 | 0.88375 | 0.548 | 0.41925 | 0.27475
03h30 | 88.43 | 76.66 | 47.73 | 37.78 | 26.28 | 03h30 | 1.1054 | 0.95825 | 0.59662 | 0.47225 | 0.3285
04h30 | 89.41 | 77.14 | 48.52 | 38.15 | 27.08 | 04h30 | 1.1176 | 0.96425 | 0.6065 | 0.47687 | 0.3385
05h30 | 81.61 | 69.01 | 43.88 | 33.41 | 23.49 | 05h30 | 1.0201 | 0.86262 | 0.5485 | 0.41763 | 0.29363
06h30 | 47.91 | 35.04 | 23.64 | 13.11 | 7.01 | 06h30 | 0.59888 | 0.438 | 0.2955 | 0.16387 | 0.087625
07h30 | 67.1 | 52.48 | 39.86 | 26.34 | 22.25 | 07h30 | 0.83875 | 0.656 | 0.49825 | 0.32925 | 0.27813
08h30 | 96.58 | 80.7 | 54.67 | 39.33 | 31.3 | 08h30 | 1.2072 | 1.0088 | 0.68337 | 0.49162 | 0.39125
09h30 | 97.17 | 81.9 | 55.7 | 41.74 | 31.13 | 09h30 | 1.2146 | 1.0237 | 0.69625 | 0.52175 | 0.38912
10h30 | 63.09 | 48.61 | 35.82 | 21.99 | 15.78 | 10h30 | 0.78863 | 0.60762 | 0.44775 | 0.27487 | 0.19725
11h30 | 25.24 | 10.51 | 10.5 | 0 | 0 | 11h30 | 0.3155 | 0.13137 | 0.13125 | 0 | 0
12h30 | 25.24 | 10.51 | 10.5 | 0 | 0 | 12h30 | 0.3155 | 0.13137 | 0.13125 | 0 | 0
13h30 | 22.65 | 8.86 | 8.85 | 0 | 0 | 13h30 | 0.28313 | 0.11075 | 0.11063 | 0 | 0
14h30 | 62.35 | 48.79 | 32.91 | 18.96 | 9.81 | 14h30 | 0.77938 | 0.60987 | 0.41137 | 0.237 | 0.12262
15h30 | 103.26 | 89.93 | 57.87 | 44.68 | 32.98 | 15h30 | 1.2908 | 1.1241 | 0.72337 | 0.5585 | 0.41225
16h30 | 97.68 | 84.48 | 54.98 | 41.38 | 30.47 | 16h30 | 1.221 | 1.056 | 0.68725 | 0.51725 | 0.38088
17h30 | 86.03 | 72.97 | 48.18 | 34.93 | 25.19 | 17h30 | 1.0754 | 0.91212 | 0.60225 | 0.43662 | 0.31488
18h30 | 87.84 | 74.94 | 49.36 | 36.24 | 26.38 | 18h30 | 1.098 | 0.93675 | 0.617 | 0.453 | 0.32975
19h30 | 97.67 | 84.86 | 55.4 | 42.1 | 31.37 | 19h30 | 1.2209 | 1.0608 | 0.6925 | 0.52625 | 0.39213
20h30 | 97.69 | 84.92 | 55.45 | 42.13 | 31.43 | 20h30 | 1.2211 | 1.0615 | 0.69312 | 0.52663 | 0.39287
21h30 | 92.88 | 80.06 | 52.54 | 39.23 | 29.18 | 21h30 | 1.161 | 1.0008 | 0.65675 | 0.49038 | 0.36475
22h30 | 89.37 | 76.47 | 50.52 | 37 | 27.6 | 22h30 | 1.1171 | 0.95588 | 0.6315 | 0.4625 | 0.345
23h30 | 85.43 | 72.4 | 48.27 | 34.51 | 25.76 | 23h30 | 1.0679 | 0.905 | 0.60337 | 0.43138 | 0.322
00h30 | 60.64 | 48.43 | 28.02 | 19.74 | 18.79 | 00h30 | 0.758 | 0.60537 | 0.35025 | 0.24675 | 0.23488
01h30 | 61.31 | 50.31 | 31.91 | 20.5 | 13.31 | 01h30 | 0.76638 | 0.62887 | 0.39887 | 0.25625 | 0.16637
02h30 | 64.33 | 53.2 | 34 | 23.64 | 17.19 | 02h30 | 0.80412 | 0.665 | 0.425 | 0.2955 | 0.21488
03h30 | 42.52 | 30.59 | 20.98 | 9.9 | 4.19 | 03h30 | 0.5315 | 0.38238 | 0.26225 | 0.12375 | 0.052375
04h30 | 38.66 | 26.1 | 18.76 | 7.51 | 2.59 | 04h30 | 0.48325 | 0.32625 | 0.2345 | 0.093875 | 0.032375
05h30 | 61.31 | 48.22 | 31.96 | 20.91 | 14.28 | 05h30 | 0.76638 | 0.60275 | 0.3995 | 0.26138 | 0.1785
06h30 | 69.5 | 55.92 | 36.83 | 25.44 | 18.17 | 06h30 | 0.86875 | 0.699 | 0.46037 | 0.318 | 0.22712
07h30 | 64.07 | 48.53 | 38.1 | 23.4 | 20.07 | 07h30 | 0.80088 | 0.60662 | 0.47625 | 0.2925 | 0.25088
08h30 | 49.06 | 33.5 | 33.22 | 18.12 | 13.91 | 08h30 | 0.61325 | 0.41875 | 0.41525 | 0.2265 | 0.17388
09h30 | 32.38 | 14.61 | 14.62 | 0 | 0 | 09h30 | 0.40475 | 0.18263 | 0.18275 | 0 | 0
10h30 | 32.38 | 15.37 | 15.35 | 0 | 0 | 10h30 | 0.40475 | 0.19212 | 0.19187 | 0 | 0
11h30 | 28.03 | 12.4 | 12.4 | 0 | 0 | 11h30 | 0.35037 | 0.155 | 0.155 | 0 | 0
12h30 | 28.03 | 11.63 | 11.67 | 0 | 0 | 12h30 | 0.35037 | 0.14538 | 0.14588 | 0 | 0
13h30 | 21.1 | 6.26 | 6.24 | 0 | 0 | 13h30 | 0.26375 | 0.07825 | 0.078 | 0 | 0
14h30 | 21.1 | 6.26 | 6.24 | 0 | 0 | 14h30 | 0.26375 | 0.07825 | 0.078 | 0 | 0
15h30 | 17.81 | 3.75 | 3.74 | 0 | 0 | 15h30 | 0.22262 | 0.046875 | 0.04675 | 0 | 0
16h30 | 20.83 | 7.07 | 7.06 | 0 | 0 | 16h30 | 0.26038 | 0.088375 | 0.08825 | 0 | 0
17h30 | 51.43 | 38.01 | 26.52 | 10.68 | 1.97 | 17h30 | 0.64287 | 0.47513 | 0.3315 | 0.1335 | 0.024625
18h30 | 79.79 | 66.67 | 43.96 | 29.88 | 20.39 | 18h30 | 0.99738 | 0.83337 | 0.5495 | 0.3735 | 0.25488
19h30 | 82.46 | 69.63 | 45.85 | 31.54 | 22.23 | 19h30 | 1.0308 | 0.87038 | 0.57312 | 0.39425 | 0.27787
20h30 | 54.88 | 42.27 | 29.71 | 15.14 | 8.39 | 20h30 | 0.686 | 0.52838 | 0.37138 | 0.18925 | 0.10487
21h30 | 23.86 | 11.34 | 11.33 | 2.8 | 4.58 | 21h30 | 0.29825 | 0.14175 | 0.14163 | 0.035 | 0.05725
22h30 | 62.52 | 49.95 | 34.58 | 17.94 | 7.37 | 22h30 | 0.7815 | 0.62438 | 0.43225 | 0.22425 | 0.092125
23h30 | 103.16 | 90.46 | 59.03 | 44.19 | 33.51 | 23h30 | 1.2895 | 1.1307 | 0.73787 | 0.55237 | 0.41887
00h30 | 84.07 | 72.16 | 42.3 | 28.19 | 26.15 | 00h30 | 1.0509 | 0.902 | 0.52875 | 0.35237 | 0.32688
01h30 | 79.3 | 68.61 | 42.83 | 30.95 | 20.8 | 01h30 | 0.99125 | 0.85762 | 0.53538 | 0.38688 | 0.26
02h30 | 72.84 | 62.03 | 38.84 | 29 | 20.8 | 02h30 | 0.9105 | 0.77538 | 0.4855 | 0.3625 | 0.26
03h30 | 72.75 | 61.14 | 38.65 | 27.55 | 17.68 | 03h30 | 0.90938 | 0.76425 | 0.48313 | 0.34437 | 0.221
04h30 | 75.9 | 63.65 | 40.58 | 29.26 | 19.78 | 04h30 | 0.94875 | 0.79563 | 0.50725 | 0.36575 | 0.24725
05h30 | 49.22 | 36.43 | 24.63 | 12.92 | 6.23 | 05h30 | 0.61525 | 0.45537 | 0.30788 | 0.1615 | 0.077875
06h30 | 29.16 | 15.55 | 15.55 | 11.2 | 4.13 | 06h30 | 0.3645 | 0.19437 | 0.19437 | 0.14 | 0.051625
07h30 | 37.28 | 21.48 | 21.47 | 3.44 | 1.58 | 07h30 | 0.466 | 0.2685 | 0.26837 | 0.043 | 0.01975
08h30 | 37.28 | 21.48 | 21.47 | 3.44 | 1.58 | 08h30 | 0.466 | 0.2685 | 0.26837 | 0.043 | 0.01975
09h30 | 66.25 | 49.83 | 36.73 | 20.13 | 12.35 | 09h30 | 0.82812 | 0.62287 | 0.45913 | 0.25162 | 0.15438
10h30 | 96.86 | 80.93 | 54.35 | 38.89 | 29.06 | 10h30 | 1.2107 | 1.0116 | 0.67937 | 0.48612 | 0.36325
11h30 | 93.28 | 77.57 | 51.29 | 36.75 | 26.79 | 11h30 | 1.166 | 0.96962 | 0.64112 | 0.45937 | 0.33487
12h30 | 87.73 | 72.27 | 47.45 | 33.38 | 23.93 | 12h30 | 1.0966 | 0.90338 | 0.59313 | 0.41725 | 0.29912
13h30 | 84.64 | 69.38 | 45.35 | 31.59 | 22.45 | 13h30 | 1.058 | 0.86725 | 0.56688 | 0.39487 | 0.28063
14h30 | 82.94 | 67.87 | 44.37 | 30.71 | 21.75 | 14h30 | 1.0368 | 0.84837 | 0.55463 | 0.38388 | 0.27187
15h30 | 53.33 | 38.38 | 26.89 | 14.51 | 13.15 | 15h30 | 0.66663 | 0.47975 | 0.33613 | 0.18138 | 0.16437
16h30 | 29.97 | 14.1 | 14.08 | 0 | 0 | 16h30 | 0.37462 | 0.17625 | 0.176 | 0 | 0
17h30 | 49.44 | 34.55 | 25.15 | 10.67 | 3.61 | 17h30 | 0.618 | 0.43188 | 0.31438 | 0.13337 | 0.045125
18h30 | 66.07 | 51.46 | 35.6 | 21.61 | 14.46 | 18h30 | 0.82588 | 0.64325 | 0.445 | 0.27013 | 0.18075
19h30 | 42.3 | 27.84 | 21.36 | 10.95 | 10.85 | 19h30 | 0.52875 | 0.348 | 0.267 | 0.13687 | 0.13562
20h30 | 26.6 | 12.1 | 12.09 | 0 | 0 | 20h30 | 0.3325 | 0.15125 | 0.15113 | 0 | 0
21h30 | 27.11 | 12.57 | 12.55 | 0 | 0 | 21h30 | 0.33887 | 0.15712 | 0.15687 | 0 | 0
22h30 | 59.17 | 44.52 | 31.97 | 16.6 | 8.94 | 22h30 | 0.73962 | 0.5565 | 0.39963 | 0.2075 | 0.11175
23h30 | 100.72 | 85.88 | 56.97 | 41.81 | 32.21 | 23h30 | 1.259 | 1.0735 | 0.71213 | 0.52263 | 0.40263
00h30 | 80.89 | 66.88 | 39.44 | 25.83 | 23.27 | 00h30 | 1.0111 | 0.836 | 0.493 | 0.32288 | 0.29087
01h30 | 68.64 | 55.88 | 35.34 | 24.13 | 15.75 | 01h30 | 0.858 | 0.6985 | 0.44175 | 0.30162 | 0.19687
02h30 | 57 | 44.05 | 32.29 | 23.51 | 15.75 | 02h30 | 0.7125 | 0.55063 | 0.40363 | 0.29387 | 0.19687
03h30 | 42.9 | 29.08 | 18.81 | 8.1 | 2.95 | 03h30 | 0.53625 | 0.3635 | 0.23513 | 0.10125 | 0.036875
04h30 | 41.37 | 26.79 | 18.81 | 8.1 | 2.95 | 04h30 | 0.51712 | 0.33487 | 0.23513 | 0.10125 | 0.036875
05h30 | 49.98 | 34.39 | 22.82 | 12.62 | 6.96 | 05h30 | 0.62475 | 0.42988 | 0.28525 | 0.15775 | 0.087
06h30 | 71.45 | 56.06 | 36.52 | 25.64 | 18.09 | 06h30 | 0.89312 | 0.70075 | 0.4565 | 0.3205 | 0.22612
07h30 | 85.85 | 68.42 | 49.85 | 36.15 | 30.56 | 07h30 | 1.0731 | 0.85525 | 0.62313 | 0.45188 | 0.382
08h30 | 78.36 | 59.27 | 42.19 | 26.69 | 20.9 | 08h30 | 0.9795 | 0.74087 | 0.52738 | 0.33363 | 0.26125
09h30 | 92.12 | 73.57 | 50.88 | 36.59 | 27.5 | 09h30 | 1.1515 | 0.91963 | 0.636 | 0.45737 | 0.34375
10h30 | 108.84 | 90.76 | 59.84 | 46.35 | 35.54 | 10h30 | 1.3605 | 1.1345 | 0.748 | 0.57937 | 0.44425
11h30 | 129.56 | 111.97 | 71.27 | 58.54 | 45.09 | 11h30 | 1.6195 | 1.3996 | 0.89087 | 0.73175 | 0.56363
12h30 | 150.95 | 133.8 | 83.33 | 71.34 | 55.31 | 12h30 | 1.8869 | 1.6725 | 1.0416 | 0.89175 | 0.69137
13h30 | 152.09 | 144.79 | 89.4 | 77.91 | 60.82 | 13h30 | 1.9011 | 1.8099 | 1.1175 | 0.97388 | 0.76025
14h30 | 150.04 | 136.65 | 84.27 | 73.21 | 56.97 | 14h30 | 1.8755 | 1.7081 | 1.0534 | 0.91512 | 0.71213
15h30 | 145.88 | 129.88 | 80.27 | 69.23 | 54.27 | 15h30 | 1.8235 | 1.6235 | 1.0034 | 0.86538 | 0.67837
16h30 | 146.25 | 129.92 | 81.08 | 69.11 | 55.22 | 16h30 | 1.8281 | 1.624 | 1.0135 | 0.86387 | 0.69025
17h30 | 146.31 | 130.4 | 82.17 | 69.63 | 56.35 | 17h30 | 1.8289 | 1.63 | 1.0271 | 0.87038 | 0.70437
18h30 | 147.73 | 132.16 | 83.57 | 71.02 | 58 | 18h30 | 1.8466 | 1.652 | 1.0446 | 0.88775 | 0.725
19h30 | 151.83 | 138.99 | 88.16 | 74.8 | 61.7 | 19h30 | 1.8979 | 1.7374 | 1.102 | 0.935 | 0.77125
20h30 | 164.87 | 150.39 | 95.47 | 81.34 | 67.6 | 20h30 | 2.0609 | 1.8799 | 1.1934 | 1.0168 | 0.845
21h30 | 164.87 | 151.7 | 96.23 | 82.39 | 68.39 | 21h30 | 2.0609 | 1.8962 | 1.2029 | 1.0299 | 0.85488
22h30 | 166.39 | 151.56 | 95.97 | 82.51 | 68.35 | 22h30 | 2.0799 | 1.8945 | 1.1996 | 1.0314 | 0.85437
23h30 | 166.39 | 151.42 | 95.82 | 82.44 | 68.31 | 23h30 | 2.0799 | 1.8927 | 1.1978 | 1.0305 | 0.85388
00h30 | 132.31 | 117.7 | 69.37 | 57.56 | 44.63 | 00h30 | 1.6539 | 1.4712 | 0.86713 | 0.7195 | 0.55788
01h30 | 116.78 | 103.45 | 63.33 | 53.68 | 41.89 | 01h30 | 1.4598 | 1.2931 | 0.79163 | 0.671 | 0.52363
02h30 | 115.92 | 102.44 | 63.12 | 53.69 | 41.87 | 02h30 | 1.449 | 1.2805 | 0.789 | 0.67112 | 0.52338
03h30 | 130.04 | 115.71 | 71.66 | 61.69 | 48.97 | 03h30 | 1.6255 | 1.4464 | 0.89575 | 0.77112 | 0.61213
04h30 | 133.57 | 118.62 | 73.74 | 63.51 | 50.73 | 04h30 | 1.6696 | 1.4828 | 0.92175 | 0.79387 | 0.63413
05h30 | 128.49 | 113 | 70.66 | 60.11 | 48.21 | 05h30 | 1.6061 | 1.4125 | 0.88325 | 0.75138 | 0.60262
06h30 | 129.97 | 114 | 71.45 | 60.76 | 48.73 | 06h30 | 1.6246 | 1.425 | 0.89312 | 0.7595 | 0.60913
07h30 | 136.46 | 125.67 | 93.26 | 79.85 | 68.63 | 07h30 | 1.7058 | 1.5709 | 1.1658 | 0.99813 | 0.85788
08h30 | 162.27 | 145.44 | 95.4 | 80.91 | 67.86 | 08h30 | 2.0284 | 1.818 | 1.1925 | 1.0114 | 0.84825
09h30 | 162.27 | 145.44 | 101.84 | 88.97 | 72.14 | 09h30 | 2.0284 | 1.818 | 1.273 | 1.1121 | 0.90175
10h30 | 184.98 | 167.01 | 107.57 | 94.79 | 76.89 | 10h30 | 2.3123 | 2.0876 | 1.3446 | 1.1849 | 0.96113
11h30 | 184.57 | 166.08 | 103.72 | 91.76 | 73.28 | 11h30 | 2.3071 | 2.076 | 1.2965 | 1.147 | 0.916
12h30 | 161.48 | 143.39 | 88.46 | 77.91 | 66.4 | 12h30 | 2.0185 | 1.7924 | 1.1058 | 0.97388 | 0.83
13h30 | 135.51 | 118.12 | 72.54 | 62.68 | 47.4 | 13h30 | 1.6939 | 1.4765 | 0.90675 | 0.7835 | 0.5925
14h30 | 125.35 | 108.64 | 72.54 | 62.68 | 47.4 | 14h30 | 1.5669 | 1.358 | 0.90675 | 0.7835 | 0.5925
15h30 | 125.17 | 109.13 | 66.93 | 57.51 | 42.06 | 15h30 | 1.5646 | 1.3641 | 0.83662 | 0.71888 | 0.52575
16h30 | 122.16 | 106.54 | 66.93 | 57.51 | 42.06 | 16h30 | 1.527 | 1.3317 | 0.83662 | 0.71888 | 0.52575
17h30 | 112.81 | 97.57 | 60.19 | 50.47 | 37.25 | 17h30 | 1.4101 | 1.2196 | 0.75238 | 0.63087 | 0.46563
18h30 | 110.95 | 96.25 | 60.19 | 50.47 | 37.3 | 18h30 | 1.3869 | 1.2031 | 0.75238 | 0.63087 | 0.46625
19h30 | 120.85 | 106.67 | 66.04 | 56.19 | 42.71 | 19h30 | 1.5106 | 1.3334 | 0.8255 | 0.70237 | 0.53387
20h30 | 117.85 | 104.08 | 66.04 | 56.19 | 42.66 | 20h30 | 1.4731 | 1.301 | 0.8255 | 0.70237 | 0.53325
21h30 | 107.04 | 93.57 | 58.26 | 48.56 | 36.6 | 21h30 | 1.338 | 1.1696 | 0.72825 | 0.607 | 0.4575
22h30 | 106.14 | 92.88 | 58.26 | 48.56 | 36.6 | 22h30 | 1.3268 | 1.161 | 0.72825 | 0.607 | 0.4575
23h30 | 106.1 | 92.99 | 57.91 | 48.17 | 36.57 | 23h30 | 1.3262 | 1.1624 | 0.72388 | 0.60213 | 0.45713
00h30 | 78.78 | 66.83 | 57.91 | 48.17 | 36.57 | 00h30 | 0.98475 | 0.83537 | 0.72388 | 0.60213 | 0.45713
01h30 | 77.65 | 67.52 | 38.98 | 30.23 | 19.8 | 01h30 | 0.97062 | 0.844 | 0.48725 | 0.37788 | 0.2475
02h30 | 83.99 | 74.04 | 43.41 | 35.98 | 24.49 | 02h30 | 1.0499 | 0.9255 | 0.54263 | 0.44975 | 0.30612
03h30 | 90.67 | 79.93 | 47.3 | 40.34 | 27.28 | 03h30 | 1.1334 | 0.99913 | 0.59125 | 0.50425 | 0.341
04h30 | 90.04 | 78.85 | 46.86 | 40.07 | 27.33 | 04h30 | 1.1255 | 0.98562 | 0.58575 | 0.50087 | 0.34163
05h30 | 86.77 | 75.19 | 44.89 | 38.02 | 26.14 | 05h30 | 1.0846 | 0.93988 | 0.56112 | 0.47525 | 0.32675
06h30 | 91.34 | 79.41 | 47.7 | 40.67 | 28.66 | 06h30 | 1.1418 | 0.99262 | 0.59625 | 0.50838 | 0.35825
07h30 | 122.78 | 108.71 | 70.56 | 62.8 | 50.61 | 07h30 | 1.5348 | 1.3589 | 0.882 | 0.785 | 0.63262
08h30 | 129.88 | 114.41 | 71.38 | 62.05 | 48.8 | 08h30 | 1.6235 | 1.4301 | 0.89225 | 0.77563 | 0.61
09h30 | 128.45 | 113.84 | 71.46 | 61.47 | 46.94 | 09h30 | 1.6056 | 1.423 | 0.89325 | 0.76838 | 0.58675
10h30 | 121.17 | 107.07 | 66.35 | 56.93 | 42.56 | 10h30 | 1.5146 | 1.3384 | 0.82937 | 0.71162 | 0.532
11h30 | 112 | 98.32 | 60.29 | 51.34 | 37.65 | 11h30 | 1.4 | 1.229 | 0.75362 | 0.64175 | 0.47063
12h30 | 109.53 | 96.24 | 58.48 | 49.86 | 36.57 | 12h30 | 1.3691 | 1.203 | 0.731 | 0.62325 | 0.45713
13h30 | 113.28 | 100.39 | 60.6 | 52.25 | 37.59 | 13h30 | 1.416 | 1.2549 | 0.7575 | 0.65312 | 0.46987
14h30 | 103.82 | 92.4 | 59.9 | 50.9 | 37.59 | 14h30 | 1.2977 | 1.155 | 0.74875 | 0.63625 | 0.46987
15h30 | 96.31 | 84.23 | 51.09 | 42.41 | 29.78 | 15h30 | 1.2039 | 1.0529 | 0.63862 | 0.53012 | 0.37225
16h30 | 102.12 | 90.06 | 54.94 | 46.33 | 33.57 | 16h30 | 1.2765 | 1.1258 | 0.68675 | 0.57913 | 0.41963
17h30 | 104.71 | 92.79 | 56.61 | 47.98 | 35.2 | 17h30 | 1.3089 | 1.1599 | 0.70762 | 0.59975 | 0.44
18h30 | 102.69 | 91.01 | 55.75 | 47.05 | 34.71 | 18h30 | 1.2836 | 1.1376 | 0.69688 | 0.58813 | 0.43388
19h30 | 101.65 | 90.15 | 55.42 | 46.47 | 34.5 | 19h30 | 1.2706 | 1.1269 | 0.69275 | 0.58088 | 0.43125
20h30 | 102.58 | 91.19 | 56.3 | 46.93 | 35.13 | 20h30 | 1.2822 | 1.1399 | 0.70375 | 0.58662 | 0.43912
21h30 | 98.24 | 86.88 | 53.77 | 44.39 | 33.04 | 21h30 | 1.228 | 1.086 | 0.67212 | 0.55488 | 0.413
22h30 | 95.45 | 84.05 | 52.03 | 42.8 | 31.91 | 22h30 | 1.1931 | 1.0506 | 0.65038 | 0.535 | 0.39887
23h30 | 104.01 | 92.55 | 57.28 | 47.77 | 36.24 | 23h30 | 1.3001 | 1.1569 | 0.716 | 0.59713 | 0.453
00h30 | 92.16 | 90.29 | 55.15 | 45.91 | 33.43 | 00h30 | 1.152 | 1.1286 | 0.68937 | 0.57388 | 0.41787
01h30 | 96.65 | 89.49 | 52.55 | 44.79 | 31.45 | 01h30 | 1.2081 | 1.1186 | 0.65687 | 0.55988 | 0.39313
02h30 | 98.88 | 90.38 | 53.95 | 46.54 | 32.51 | 02h30 | 1.236 | 1.1298 | 0.67437 | 0.58175 | 0.40637
03h30 | 98.77 | 89.04 | 53.27 | 45.48 | 31.83 | 03h30 | 1.2346 | 1.113 | 0.66587 | 0.5685 | 0.39787
04h30 | 100.3 | 89.94 | 53.92 | 46.43 | 32.83 | 04h30 | 1.2537 | 1.1242 | 0.674 | 0.58037 | 0.41037
05h30 | 105.8 | 94.93 | 57.18 | 49.57 | 35.85 | 05h30 | 1.3225 | 1.1866 | 0.71475 | 0.61962 | 0.44812
06h30 | 116.04 | 104.7 | 63.4 | 55.45 | 41.1 | 06h30 | 1.4505 | 1.3088 | 0.7925 | 0.69312 | 0.51375
07h30 | 117.85 | 111.56 | 90.34 | 81.56 | 66.77 | 07h30 | 1.4731 | 1.3945 | 1.1293 | 1.0195 | 0.83462
08h30 | 151.04 | 138.5 | 92.06 | 81.25 | 65.83 | 08h30 | 1.888 | 1.7312 | 1.1507 | 1.0156 | 0.82288
09h30 | 151.04 | 138.5 | 89.79 | 78.34 | 62.06 | 09h30 | 1.888 | 1.7312 | 1.1224 | 0.97925 | 0.77575
10h30 | 151.77 | 138.21 | 84.71 | 74.56 | 57.83 | 10h30 | 1.8971 | 1.7276 | 1.0589 | 0.932 | 0.72288
11h30 | 147.86 | 133.86 | 81.04 | 71.71 | 53.97 | 11h30 | 1.8482 | 1.6732 | 1.013 | 0.89638 | 0.67463
12h30 | 142.55 | 128.8 | 77.39 | 68.6 | 51.84 | 12h30 | 1.7819 | 1.61 | 0.96737 | 0.8575 | 0.648
13h30 | 130.13 | 117.08 | 69.59 | 61.42 | 44.86 | 13h30 | 1.6266 | 1.4635 | 0.86987 | 0.76775 | 0.56075
14h30 | 118.89 | 106.53 | 68.33 | 60.03 | 44.86 | 14h30 | 1.4861 | 1.3316 | 0.85413 | 0.75038 | 0.56075
15h30 | 123.24 | 111.19 | 66.71 | 57.28 | 42.39 | 15h30 | 1.5405 | 1.3899 | 0.83388 | 0.716 | 0.52987
16h30 | 136.72 | 124.71 | 75.46 | 65.77 | 50.67 | 16h30 | 1.709 | 1.5589 | 0.94325 | 0.82212 | 0.63338
17h30 | 134.6 | 122.75 | 74.46 | 64.85 | 50.83 | 17h30 | 1.6825 | 1.5344 | 0.93075 | 0.81063 | 0.63538
18h30 | 114.23 | 102.64 | 65.71 | 56.36 | 42.56 | 18h30 | 1.4279 | 1.283 | 0.82137 | 0.7045 | 0.532
19h30 | 101.74 | 90.34 | 55.79 | 45.5 | 35.45 | 19h30 | 1.2717 | 1.1293 | 0.69737 | 0.56875 | 0.44312
20h30 | 101.95 | 90.57 | 56.3 | 45.89 | 36.19 | 20h30 | 1.2744 | 1.1321 | 0.70375 | 0.57363 | 0.45238
21h30 | 103.83 | 92.31 | 57.49 | 46.74 | 37.41 | 21h30 | 1.2979 | 1.1539 | 0.71862 | 0.58425 | 0.46763
22h30 | 103.21 | 91.46 | 57.39 | 46.35 | 37.3 | 22h30 | 1.2901 | 1.1433 | 0.71737 | 0.57937 | 0.46625
23h30 | 100.17 | 88.08 | 55.71 | 44.18 | 35.73 | 23h30 | 1.2521 | 1.101 | 0.69637 | 0.55225 | 0.44662
00h30 | 77.17 | 72.68 | 55.3 | 44.18 | 35.09 | 00h30 | 0.96462 | 0.9085 | 0.69125 | 0.55225 | 0.43862
01h30 | 81.38 | 71.05 | 41.34 | 30.36 | 23.49 | 01h30 | 1.0172 | 0.88813 | 0.51675 | 0.3795 | 0.29363
02h30 | 83.68 | 72.9 | 44.59 | 34.6 | 27.2 | 02h30 | 1.046 | 0.91125 | 0.55737 | 0.4325 | 0.34
03h30 | 77.97 | 65.91 | 40.75 | 30.97 | 23.09 | 03h30 | 0.97462 | 0.82388 | 0.50938 | 0.38712 | 0.28863
04h30 | 70.74 | 64.06 | 37.5 | 26.73 | 19.38 | 04h30 | 0.88425 | 0.80075 | 0.46875 | 0.33413 | 0.24225
05h30 | 55.92 | 40.39 | 26.21 | 16.64 | 11.21 | 05h30 | 0.699 | 0.50487 | 0.32762 | 0.208 | 0.14012
06h30 | 55.92 | 40.39 | 26.21 | 16.64 | 11.21 | 06h30 | 0.699 | 0.50487 | 0.32762 | 0.208 | 0.14012
07h30 | 78.12 | 60.01 | 43.66 | 31.02 | 26.87 | 07h30 | 0.9765 | 0.75013 | 0.54575 | 0.38775 | 0.33587
08h30 | 85.85 | 66.66 | 44.68 | 31.2 | 26.87 | 08h30 | 1.0731 | 0.83325 | 0.5585 | 0.39 | 0.33587
09h30 | 76.04 | 57.88 | 37.05 | 26.5 | 19.54 | 09h30 | 0.9505 | 0.7235 | 0.46313 | 0.33125 | 0.24425
10h30 | 77.67 | 61.4 | 36.03 | 26.91 | 20.21 | 10h30 | 0.97088 | 0.7675 | 0.45038 | 0.33637 | 0.25262
11h30 | 90.57 | 75.29 | 43.59 | 34.53 | 26.27 | 11h30 | 1.1321 | 0.94112 | 0.54487 | 0.43162 | 0.32837
12h30 | 105.27 | 89.57 | 53.27 | 42.94 | 32.53 | 12h30 | 1.3159 | 1.1196 | 0.66587 | 0.53675 | 0.40663
13h30 | 102.29 | 86.75 | 52.06 | 41.52 | 31.26 | 13h30 | 1.2786 | 1.0844 | 0.65075 | 0.519 | 0.39075
14h30 | 89.29 | 74.89 | 44.78 | 34.41 | 25.11 | 14h30 | 1.1161 | 0.93612 | 0.55975 | 0.43012 | 0.31388
15h30 | 90.94 | 77.5 | 46.47 | 35.44 | 26.22 | 15h30 | 1.1367 | 0.96875 | 0.58088 | 0.443 | 0.32775
16h30 | 90.13 | 76.96 | 46.92 | 35.18 | 26.62 | 16h30 | 1.1266 | 0.962 | 0.5865 | 0.43975 | 0.33275
17h30 | 81.04 | 67.77 | 42.46 | 30.19 | 23.23 | 17h30 | 1.013 | 0.84713 | 0.53075 | 0.37738 | 0.29037
18h30 | 70.81 | 55.74 | 39.61 | 28.57 | 22.02 | 18h30 | 0.88513 | 0.69675 | 0.49512 | 0.35713 | 0.27525
19h30 | 61.04 | 47.7 | 30.16 | 16.61 | 12.07 | 19h30 | 0.763 | 0.59625 | 0.377 | 0.20763 | 0.15088
20h30 | 67.88 | 54.97 | 35.69 | 23.4 | 17.67 | 20h30 | 0.8485 | 0.68712 | 0.44612 | 0.2925 | 0.22087
21h30 | 64.41 | 51.52 | 33.39 | 21.36 | 15.86 | 21h30 | 0.80512 | 0.644 | 0.41737 | 0.267 | 0.19825
22h30 | 59.66 | 46.39 | 30.47 | 18.31 | 13.07 | 22h30 | 0.74575 | 0.57988 | 0.38088 | 0.22887 | 0.16337
23h30 | 51.16 | 37.39 | 25.49 | 12.73 | 8.25 | 23h30 | 0.6395 | 0.46737 | 0.31862 | 0.15912 | 0.10312
00h30 | 49.06 | 35.26 | 22.88 | 9 | 5.45 | 00h30 | 0.61325 | 0.44075 | 0.286 | 0.1125 | 0.068125
01h30 | 46.95 | 33.94 | 19.72 | 10.18 | 4.99 | 01h30 | 0.58688 | 0.42425 | 0.2465 | 0.12725 | 0.062375
02h30 | 49.33 | 37.38 | 23.43 | 13.49 | 7.46 | 02h30 | 0.61662 | 0.46725 | 0.29287 | 0.16862 | 0.09325
03h30 | 61 | 48.35 | 30.31 | 19.72 | 13.32 | 03h30 | 0.7625 | 0.60437 | 0.37888 | 0.2465 | 0.1665
04h30 | 76.4 | 62.24 | 39.02 | 28.71 | 21.71 | 04h30 | 0.955 | 0.778 | 0.48775 | 0.35887 | 0.27137
05h30 | 72.97 | 57.73 | 36.62 | 26.46 | 19.89 | 05h30 | 0.91212 | 0.72162 | 0.45775 | 0.33075 | 0.24863
06h30 | 58.38 | 42.2 | 27.55 | 17.43 | 12.08 | 06h30 | 0.72975 | 0.5275 | 0.34437 | 0.21788 | 0.151
07h30 | 74.93 | 55.69 | 41.42 | 30.16 | 25.88 | 07h30 | 0.93663 | 0.69612 | 0.51775 | 0.377 | 0.3235
08h30 | 77.96 | 56.71 | 39.33 | 26.9 | 22.83 | 08h30 | 0.9745 | 0.70888 | 0.49162 | 0.33625 | 0.28537
09h30 | 78.03 | 57.86 | 38.95 | 25.57 | 19.12 | 09h30 | 0.97537 | 0.72325 | 0.48688 | 0.31962 | 0.239
10h30 | 72.12 | 55.03 | 37.69 | 25.57 | 19.12 | 10h30 | 0.9015 | 0.68788 | 0.47113 | 0.31962 | 0.239
11h30 | 69.47 | 50.36 | 30.73 | 19.34 | 13.27 | 11h30 | 0.86838 | 0.6295 | 0.38412 | 0.24175 | 0.16587
12h30 | 75.59 | 56.84 | 34.75 | 24.14 | 17.53 | 12h30 | 0.94488 | 0.7105 | 0.43438 | 0.30175 | 0.21912
13h30 | 75.5 | 57.03 | 34.28 | 24.64 | 17.97 | 13h30 | 0.94375 | 0.71288 | 0.4285 | 0.308 | 0.22462
14h30 | 69.7 | 51.89 | 31.06 | 21.54 | 15.21 | 14h30 | 0.87125 | 0.64863 | 0.38825 | 0.26925 | 0.19012
15h30 | 74.49 | 57.01 | 34.92 | 24.24 | 17.69 | 15h30 | 0.93112 | 0.71262 | 0.4365 | 0.303 | 0.22112
16h30 | 84.07 | 66.7 | 41.9 | 30.19 | 23.2 | 16h30 | 1.0509 | 0.83375 | 0.52375 | 0.37738 | 0.29
17h30 | 85.58 | 68.5 | 43.97 | 31.51 | 24.51 | 17h30 | 1.0697 | 0.85625 | 0.54963 | 0.39387 | 0.30638
18h30 | 75.36 | 57.78 | 38.22 | 25.12 | 18.91 | 18h30 | 0.942 | 0.72225 | 0.47775 | 0.314 | 0.23638
19h30 | 59.38 | 42.86 | 29.49 | 16.48 | 11.33 | 19h30 | 0.74225 | 0.53575 | 0.36862 | 0.206 | 0.14163
20h30 | 59.7 | 43.24 | 29.78 | 17.01 | 11.89 | 20h30 | 0.74625 | 0.5405 | 0.37225 | 0.21263 | 0.14863
21h30 | 74.97 | 58.49 | 39.29 | 26.06 | 20.13 | 21h30 | 0.93712 | 0.73113 | 0.49112 | 0.32575 | 0.25162
22h30 | 83.81 | 67.09 | 44.96 | 31.04 | 24.65 | 22h30 | 1.0476 | 0.83862 | 0.562 | 0.388 | 0.30812
23h30 | 80.13 | 63.09 | 42.82 | 28.74 | 22.59 | 23h30 | 1.0016 | 0.78863 | 0.53525 | 0.35925 | 0.28237
00h30 | 70.97 | 53.8 | 34.83 | 21.98 | 16.09 | 00h30 | 0.88713 | 0.6725 | 0.43538 | 0.27475 | 0.20112
01h30 | 59.25 | 43.33 | 27.21 | 15.6 | 10.63 | 01h30 | 0.74062 | 0.54163 | 0.34013 | 0.195 | 0.13287
02h30 | 62.73 | 47.38 | 30.74 | 20.33 | 14.89 | 02h30 | 0.78412 | 0.59225 | 0.38425 | 0.25412 | 0.18613
03h30 | 87.05 | 70.84 | 45.49 | 33.9 | 26.92 | 03h30 | 1.0881 | 0.8855 | 0.56863 | 0.42375 | 0.3365
04h30 | 108.89 | 91.5 | 58.81 | 46.21 | 38.24 | 04h30 | 1.3611 | 1.1438 | 0.73513 | 0.57763 | 0.478
05h30 | 110.96 | 92.57 | 59.9 | 47.05 | 39.23 | 05h30 | 1.387 | 1.1571 | 0.74875 | 0.58813 | 0.49038
06h30 | 114.33 | 95.02 | 61.62 | 48.67 | 41.1 | 06h30 | 1.4291 | 1.1878 | 0.77025 | 0.60837 | 0.51375
07h30 | 128.71 | 110.53 | 76.87 | 60.7 | 55.2 | 07h30 | 1.6089 | 1.3816 | 0.96088 | 0.75875 | 0.69
08h30 | 123.51 | 99.66 | 68.19 | 50.54 | 44.69 | 08h30 | 1.5439 | 1.2457 | 0.85237 | 0.63175 | 0.55863
09h30 | 118.74 | 94.95 | 65.48 | 49.64 | 41.68 | 09h30 | 1.4843 | 1.1869 | 0.8185 | 0.6205 | 0.521
10h30 | 106.96 | 83.04 | 57.26 | 41.67 | 34.74 | 10h30 | 1.337 | 1.038 | 0.71575 | 0.52087 | 0.43425
11h30 | 103.83 | 80.1 | 54.62 | 39.45 | 32.21 | 11h30 | 1.2979 | 1.0012 | 0.68275 | 0.49312 | 0.40263
12h30 | 109.58 | 85.95 | 57.15 | 43.04 | 35.15 | 12h30 | 1.3698 | 1.0744 | 0.71437 | 0.538 | 0.43938
13h30 | 103.56 | 80.07 | 52.79 | 39.62 | 31.72 | 13h30 | 1.2945 | 1.0009 | 0.65987 | 0.49525 | 0.3965
14h30 | 96.21 | 72.92 | 48.59 | 35.5 | 28.78 | 14h30 | 1.2026 | 0.9115 | 0.60737 | 0.44375 | 0.35975
15h30 | 94.62 | 71.55 | 47.37 | 34.1 | 26.21 | 15h30 | 1.1827 | 0.89438 | 0.59213 | 0.42625 | 0.32762
16h30 | 87.46 | 68.49 | 47.37 | 34.1 | 26.21 | 16h30 | 1.0933 | 0.85613 | 0.59213 | 0.42625 | 0.32762
17h30 | 77.07 | 54.29 | 37.46 | 23.78 | 17.3 | 17h30 | 0.96337 | 0.67863 | 0.46825 | 0.29725 | 0.21625
18h30 | 77.44 | 54.95 | 38.5 | 24.84 | 18.7 | 18h30 | 0.968 | 0.68688 | 0.48125 | 0.3105 | 0.23375
19h30 | 85.94 | 63.45 | 43.8 | 29.82 | 23.23 | 19h30 | 1.0742 | 0.79312 | 0.5475 | 0.37275 | 0.29037
20h30 | 86.8 | 64.66 | 44.56 | 30.85 | 24.16 | 20h30 | 1.085 | 0.80825 | 0.557 | 0.38562 | 0.302
21h30 | 76.98 | 55.09 | 38.64 | 25.4 | 19.38 | 21h30 | 0.96225 | 0.68863 | 0.483 | 0.3175 | 0.24225
22h30 | 72.79 | 53.22 | 36.84 | 23.32 | 17.05 | 22h30 | 0.90987 | 0.66525 | 0.4605 | 0.2915 | 0.21313
23h30 | 54.64 | 32.36 | 24.69 | 11.72 | 7.33 | 23h30 | 0.683 | 0.4045 | 0.30862 | 0.1465 | 0.091625
00h30 | 54.64 | 32.36 | 24.69 | 11.72 | 7.33 | 00h30 | 0.683 | 0.4045 | 0.30862 | 0.1465 | 0.091625
01h30 | 22.41 | 1.21 | 1.36 | 0 | 0 | 01h30 | 0.28013 | 0.015125 | 0.017 | 0 | 0
02h30 | 31.98 | 13.59 | 10.16 | 0 | 0 | 02h30 | 0.39975 | 0.16987 | 0.127 | 0 | 0
03h30 | 34.86 | 16.92 | 12.4 | 2.37 | 0 | 03h30 | 0.43575 | 0.2115 | 0.155 | 0.029625 | 0
04h30 | 34.1 | 15.3 | 11.83 | 2.37 | 0 | 04h30 | 0.42625 | 0.19125 | 0.14788 | 0.029625 | 0
05h30 | 32.95 | 13.65 | 11.16 | 1.11 | 0 | 05h30 | 0.41187 | 0.17062 | 0.1395 | 0.013875 | 0
06h30 | 36.66 | 16.94 | 13.43 | 3.02 | 0 | 06h30 | 0.45825 | 0.21175 | 0.16787 | 0.03775 | 0
07h30 | 56.85 | 34.88 | 30.07 | 16.96 | 14.18 | 07h30 | 0.71062 | 0.436 | 0.37588 | 0.212 | 0.17725
08h30 | 53.65 | 30.07 | 24.97 | 15.06 | 14.18 | 08h30 | 0.67063 | 0.37588 | 0.31212 | 0.18825 | 0.17725
09h30 | 50.11 | 27.37 | 23.42 | 9.99 | 4.66 | 09h30 | 0.62638 | 0.34213 | 0.29275 | 0.12487 | 0.05825
10h30 | 48.97 | 26.89 | 22.11 | 9.99 | 4.96 | 10h30 | 0.61213 | 0.33613 | 0.27637 | 0.12487 | 0.062
11h30 | 76.85 | 55.31 | 38.74 | 25.05 | 18.55 | 11h30 | 0.96062 | 0.69137 | 0.48425 | 0.31312 | 0.23187
12h30 | 108.08 | 87.05 | 57.55 | 43.65 | 34.61 | 12h30 | 1.351 | 1.0881 | 0.71937 | 0.54563 | 0.43262
13h30 | 118.08 | 97.54 | 63.39 | 49.74 | 39.72 | 13h30 | 1.476 | 1.2192 | 0.79238 | 0.62175 | 0.4965
14h30 | 121.64 | 101.64 | 65.33 | 52.06 | 41.43 | 14h30 | 1.5205 | 1.2705 | 0.81663 | 0.65075 | 0.51787
15h30 | 128.13 | 108.55 | 69.51 | 55.95 | 45.09 | 15h30 | 1.6016 | 1.3569 | 0.86887 | 0.69937 | 0.56363
16h30 | 150.49 | 131.08 | 84.02 | 69.21 | 57.67 | 16h30 | 1.8811 | 1.6385 | 1.0502 | 0.86513 | 0.72088
17h30 | 165.33 | 162.12 | 103.95 | 87.84 | 75.02 | 17h30 | 2.0666 | 2.0265 | 1.2994 | 1.098 | 0.93775
18h30 | 185.82 | 171.16 | 110.18 | 93.5 | 80.59 | 18h30 | 2.3228 | 2.1395 | 1.3773 | 1.1687 | 1.0074
19h30 | 176.47 | 157.96 | 102.66 | 85.64 | 73.86 | 19h30 | 2.2059 | 1.9745 | 1.2833 | 1.0705 | 0.92325
20h30 | 172.55 | 152.8 | 100.01 | 82.35 | 71.18 | 20h30 | 2.1569 | 1.91 | 1.2501 | 1.0294 | 0.88975
21h30 | 167.81 | 148.36 | 97.7 | 79.61 | 68.88 | 21h30 | 2.0976 | 1.8545 | 1.2212 | 0.99513 | 0.861
22h30 | 133.13 | 113.57 | 76.97 | 58.88 | 50.29 | 22h30 | 1.6641 | 1.4196 | 0.96213 | 0.736 | 0.62862
23h30 | 100.25 | 80.44 | 57.23 | 39.11 | 32.54 | 23h30 | 1.2531 | 1.0055 | 0.71537 | 0.48888 | 0.40675
00h30 | 53.04 | 44.22 | 35.04 | 23.31 | 17.6 | 00h30 | 0.663 | 0.55275 | 0.438 | 0.29137 | 0.22
01h30 | 30.44 | 10.96 | 10.75 | 0 | 0 | 01h30 | 0.3805 | 0.137 | 0.13437 | 0 | 0
02h30 | 60.08 | 41.74 | 30.46 | 13.36 | 8.09 | 02h30 | 0.751 | 0.52175 | 0.38075 | 0.167 | 0.10113
03h30 | 95.84 | 75.84 | 51.32 | 35.89 | 29.72 | 03h30 | 1.198 | 0.948 | 0.6415 | 0.44862 | 0.3715
04h30 | 102.73 | 82.19 | 55.77 | 39.41 | 33.06 | 04h30 | 1.2841 | 1.0274 | 0.69712 | 0.49262 | 0.41325
05h30 | 71.56 | 50.36 | 37.13 | 20.27 | 16.01 | 05h30 | 0.8945 | 0.6295 | 0.46413 | 0.25338 | 0.20012
06h30 | 40.32 | 18.49 | 18.46 | 3.38 | 4.58 | 06h30 | 0.504 | 0.23112 | 0.23075 | 0.04225 | 0.05725
07h30 | 58.07 | 34.03 | 34 | 14.58 | 9.61 | 07h30 | 0.72588 | 0.42538 | 0.425 | 0.18225 | 0.12012
08h30 | 60.33 | 34.78 | 31.11 | 14.58 | 9.61 | 08h30 | 0.75413 | 0.43475 | 0.38888 | 0.18225 | 0.12012
09h30 | 58.69 | 34.51 | 27.39 | 12.13 | 7.77 | 09h30 | 0.73362 | 0.43138 | 0.34237 | 0.15163 | 0.097125
10h30 | 51.13 | 28.49 | 24.8 | 12.13 | 7.77 | 10h30 | 0.63913 | 0.35613 | 0.31 | 0.15163 | 0.097125
11h30 | 43.75 | 20.68 | 12.43 | 0 | 0 | 11h30 | 0.54688 | 0.2585 | 0.15538 | 0 | 0
12h30 | 88.05 | 66.71 | 42.03 | 28.37 | 20.42 | 12h30 | 1.1006 | 0.83388 | 0.52538 | 0.35463 | 0.25525
13h30 | 112.45 | 92.26 | 57.3 | 44.7 | 35.18 | 13h30 | 1.4056 | 1.1533 | 0.71625 | 0.55875 | 0.43975
14h30 | 109.85 | 91.11 | 56.12 | 43.75 | 34.45 | 14h30 | 1.3731 | 1.1389 | 0.7015 | 0.54688 | 0.43062
15h30 | 106.14 | 88.93 | 54.64 | 41.79 | 33.23 | 15h30 | 1.3268 | 1.1116 | 0.683 | 0.52238 | 0.41537
16h30 | 113.58 | 97.13 | 60.48 | 46.22 | 37.59 | 16h30 | 1.4198 | 1.2141 | 0.756 | 0.57775 | 0.46987
17h30 | 74.11 | 57.74 | 38.99 | 31.85 | 24.06 | 17h30 | 0.92637 | 0.72175 | 0.48738 | 0.39813 | 0.30075
18h30 | 58.04 | 41.98 | 30.9 | 9.57 | 5.98 | 18h30 | 0.7255 | 0.52475 | 0.38625 | 0.11962 | 0.07475
19h30 | 84.95 | 69.36 | 47.22 | 31.57 | 24.7 | 19h30 | 1.0619 | 0.867 | 0.59025 | 0.39463 | 0.30875
20h30 | 82.71 | 67.4 | 46.08 | 29.84 | 23.42 | 20h30 | 1.0339 | 0.8425 | 0.576 | 0.373 | 0.29275
21h30 | 78.38 | 63.08 | 43.71 | 27.48 | 21.29 | 21h30 | 0.97975 | 0.7885 | 0.54638 | 0.3435 | 0.26613
22h30 | 80.71 | 65.2 | 45.1 | 29 | 22.64 | 22h30 | 1.0089 | 0.815 | 0.56375 | 0.3625 | 0.283
23h30 | 89.48 | 73.63 | 50.48 | 33.93 | 27.07 | 23h30 | 1.1185 | 0.92038 | 0.631 | 0.42412 | 0.33837
00h30 | 56.31 | 36.17 | 24.05 | 24.58 | 21.01 | 00h30 | 0.70388 | 0.45212 | 0.30062 | 0.30725 | 0.26262
01h30 | 21.34 | 7.35 | 7.32 | 0 | 0 | 01h30 | 0.26675 | 0.091875 | 0.0915 | 0 | 0
02h30 | 23.53 | 8.94 | 8.93 | 0 | 0 | 02h30 | 0.29413 | 0.11175 | 0.11163 | 0 | 0
03h30 | 25.35 | 10.06 | 10.04 | 0 | 0 | 03h30 | 0.31688 | 0.12575 | 0.1255 | 0 | 0
04h30 | 27.85 | 11.51 | 11.5 | 0 | 0 | 04h30 | 0.34813 | 0.14388 | 0.14375 | 0 | 0
05h30 | 30.65 | 13.48 | 13.46 | 0 | 0 | 05h30 | 0.38312 | 0.1685 | 0.16825 | 0 | 0
06h30 | 33.03 | 15.06 | 15.05 | 0 | 0 | 06h30 | 0.41287 | 0.18825 | 0.18812 | 0 | 0
07h30 | 50.03 | 29.72 | 29.7 | 9.55 | 4.91 | 07h30 | 0.62538 | 0.3715 | 0.37125 | 0.11937 | 0.061375
08h30 | 45.37 | 25.08 | 25.05 | 9.55 | 4.91 | 08h30 | 0.56712 | 0.3135 | 0.31312 | 0.11937 | 0.061375
09h30 | 44.31 | 22.28 | 22.26 | 2.49 | 0 | 09h30 | 0.55388 | 0.2785 | 0.27825 | 0.031125 | 0
10h30 | 41.89 | 22.28 | 22.26 | 2.49 | 0 | 10h30 | 0.52363 | 0.2785 | 0.27825 | 0.031125 | 0
11h30 | 60.16 | 38.35 | 29.84 | 12.09 | 6.42 | 11h30 | 0.752 | 0.47937 | 0.373 | 0.15113 | 0.08025
12h30 | 79.55 | 58.43 | 41.43 | 24.1 | 17.67 | 12h30 | 0.99438 | 0.73037 | 0.51787 | 0.30125 | 0.22087
13h30 | 83.04 | 62 | 43.15 | 26.25 | 19.55 | 13h30 | 1.038 | 0.775 | 0.53938 | 0.32812 | 0.24438
14h30 | 87.64 | 66.74 | 46.04 | 29.13 | 22.11 | 14h30 | 1.0955 | 0.83425 | 0.5755 | 0.36412 | 0.27637
15h30 | 88.1 | 67.36 | 46.66 | 29.72 | 22.68 | 15h30 | 1.1013 | 0.842 | 0.58325 | 0.3715 | 0.2835
16h30 | 64.11 | 42.91 | 32.55 | 15.23 | 9.87 | 16h30 | 0.80137 | 0.53638 | 0.40687 | 0.19037 | 0.12337
17h30 | 39.09 | 18.61 | 18.59 | 0.79 | 1 | 17h30 | 0.48862 | 0.23262 | 0.23237 | 0.009875 | 0.0125
18h30 | 39.52 | 19.13 | 19.11 | 1.43 | 0 | 18h30 | 0.494 | 0.23913 | 0.23888 | 0.017875 | 0
19h30 | 61.75 | 41.51 | 32.51 | 15.14 | 9.51 | 19h30 | 0.77187 | 0.51887 | 0.40637 | 0.18925 | 0.11887
20h30 | 82.5 | 62.25 | 44.98 | 27.73 | 21.39 | 20h30 | 1.0312 | 0.77812 | 0.56225 | 0.34663 | 0.26737
21h30 | 80.58 | 60.27 | 43.66 | 26.89 | 20.38 | 21h30 | 1.0072 | 0.75338 | 0.54575 | 0.33613 | 0.25475
22h30 | 77.36 | 56.95 | 41.37 | 25.35 | 19.15 | 22h30 | 0.967 | 0.71188 | 0.51712 | 0.31688 | 0.23938
23h30 | 66.81 | 46.27 | 34.71 | 19.26 | 13.75 | 23h30 | 0.83513 | 0.57837 | 0.43388 | 0.24075 | 0.17188
00h30 | 48.85 | 27.96 | 23.64 | 7.17 | 3.1 | 00h30 | 0.61062 | 0.3495 | 0.2955 | 0.089625 | 0.03875
01h30 | 40.01 | 21.79 | 16.08 | 2.71 | 0 | 01h30 | 0.50013 | 0.27237 | 0.201 | 0.033875 | 0
02h30 | 40.01 | 21.79 | 16.08 | 2.71 | 0 | 02h30 | 0.50013 | 0.27237 | 0.201 | 0.033875 | 0
03h30 | 53.31 | 32.75 | 24.91 | 9.76 | 5.99 | 03h30 | 0.66638 | 0.40937 | 0.31138 | 0.122 | 0.074875
04h30 | 83.88 | 64.36 | 44.18 | 28.99 | 23.44 | 04h30 | 1.0485 | 0.8045 | 0.55225 | 0.36238 | 0.293
05h30 | 92.32 | 72.47 | 49.72 | 34.03 | 27.92 | 05h30 | 1.154 | 0.90587 | 0.6215 | 0.42538 | 0.349
06h30 | 89.92 | 69.48 | 48.25 | 32.24 | 26.38 | 06h30 | 1.124 | 0.8685 | 0.60313 | 0.403 | 0.32975
07h30 | 92.4 | 69.85 | 54.32 | 36.83 | 30.29 | 07h30 | 1.155 | 0.87313 | 0.679 | 0.46037 | 0.37862
08h30 | 67.75 | 43.56 | 36.52 | 19.39 | 14.39 | 08h30 | 0.84688 | 0.5445 | 0.4565 | 0.24238 | 0.17988
09h30 | 50.14 | 26.45 | 25.07 | 9.41 | 5.2 | 09h30 | 0.62675 | 0.33063 | 0.31338 | 0.11762 | 0.065
10h30 | 52.48 | 29.27 | 25.45 | 10.33 | 6.08 | 10h30 | 0.656 | 0.36588 | 0.31812 | 0.12912 | 0.076
11h30 | 61.78 | 38.92 | 30.3 | 15.32 | 10.33 | 11h30 | 0.77225 | 0.4865 | 0.37875 | 0.1915 | 0.12912
12h30 | 55.93 | 33.77 | 29.91 | 14.4 | 9.45 | 12h30 | 0.69912 | 0.42212 | 0.37388 | 0.18 | 0.11812
13h30 | 36.98 | 14.21 | 14.03 | 0 | 0 | 13h30 | 0.46225 | 0.17763 | 0.17538 | 0 | 0
14h30 | 36.98 | 14.8 | 14.78 | 0.08 | 0 | 14h30 | 0.46225 | 0.185 | 0.18475 | 0.001 | 0
15h30 | 49.43 | 27.89 | 22.48 | 8.14 | 3.05 | 15h30 | 0.61787 | 0.34863 | 0.281 | 0.10175 | 0.038125
16h30 | 63.19 | 41.78 | 31.18 | 16.81 | 11.63 | 16h30 | 0.78987 | 0.52225 | 0.38975 | 0.21013 | 0.14538
17h30 | 56.93 | 35.72 | 27.68 | 13.83 | 8.84 | 17h30 | 0.71162 | 0.4465 | 0.346 | 0.17288 | 0.1105
18h30 | 57.34 | 36.35 | 28.13 | 14.55 | 9.65 | 18h30 | 0.71675 | 0.45437 | 0.35163 | 0.18188 | 0.12062
19h30 | 75.22 | 54.49 | 39.37 | 25.18 | 19.25 | 19h30 | 0.94025 | 0.68112 | 0.49212 | 0.31475 | 0.24063
20h30 | 99.4 | 78.84 | 54.33 | 39.58 | 32.12 | 20h30 | 1.2425 | 0.9855 | 0.67912 | 0.49475 | 0.4015
21h30 | 115.05 | 94.58 | 63.85 | 49.09 | 40.66 | 21h30 | 1.4381 | 1.1823 | 0.79812 | 0.61362 | 0.50825
22h30 | 110.51 | 90.05 | 61.07 | 46.5 | 38.38 | 22h30 | 1.3814 | 1.1256 | 0.76338 | 0.58125 | 0.47975
23h30 | 92.6 | 72.09 | 50.12 | 35.96 | 29.02 | 23h30 | 1.1575 | 0.90112 | 0.6265 | 0.4495 | 0.36275
00h30 | 58.8 | 37.15 | 28.03 | 14.68 | 9.02 | 00h30 | 0.735 | 0.46437 | 0.35037 | 0.1835 | 0.11275
01h30 | 54.06 | 36.03 | 24.19 | 12.49 | 8.19 | 01h30 | 0.67575 | 0.45038 | 0.30238 | 0.15613 | 0.10237
02h30 | 60.71 | 42.61 | 29.17 | 17.9 | 13.37 | 02h30 | 0.75887 | 0.53263 | 0.36462 | 0.22375 | 0.16712
03h30 | 64.95 | 46.3 | 31.56 | 19.89 | 15.09 | 03h30 | 0.81188 | 0.57875 | 0.3945 | 0.24863 | 0.18862
04h30 | 65.57 | 46.34 | 32.02 | 19.98 | 15.24 | 04h30 | 0.81963 | 0.57925 | 0.40025 | 0.24975 | 0.1905
05h30 | 65.82 | 46.15 | 32.19 | 20.02 | 15.14 | 05h30 | 0.82275 | 0.57688 | 0.40237 | 0.25025 | 0.18925
06h30 | 65.01 | 44.97 | 31.57 | 19.42 | 14.48 | 06h30 | 0.81263 | 0.56212 | 0.39463 | 0.24275 | 0.181
07h30 | 83.9 | 61.93 | 47.57 | 33.81 | 27.28 | 07h30 | 1.0488 | 0.77412 | 0.59462 | 0.42262 | 0.341
08h30 | 83.77 | 60.41 | 44.65 | 29.43 | 22.61 | 08h30 | 1.0471 | 0.75513 | 0.55812 | 0.36788 | 0.28263
09h30 | 79.96 | 57.36 | 43.06 | 28.2 | 22.26 | 09h30 | 0.9995 | 0.717 | 0.53825 | 0.3525 | 0.27825
10h30 | 84.78 | 62.8 | 45.03 | 30.77 | 24.28 | 10h30 | 1.0597 | 0.785 | 0.56288 | 0.38462 | 0.3035
11h30 | 105.49 | 84.02 | 56.73 | 43.01 | 34.83 | 11h30 | 1.3186 | 1.0502 | 0.70913 | 0.53763 | 0.43538
12h30 | 115.93 | 94.95 | 62.62 | 49.17 | 40.07 | 12h30 | 1.4491 | 1.1869 | 0.78275 | 0.61462 | 0.50087
13h30 | 115.01 | 94.51 | 61.83 | 48.8 | 39.6 | 13h30 | 1.4376 | 1.1814 | 0.77287 | 0.61 | 0.495
14h30 | 109.12 | 89.04 | 58.34 | 45.48 | 36.79 | 14h30 | 1.364 | 1.113 | 0.72925 | 0.5685 | 0.45987
15h30 | 112.15 | 92.38 | 60.55 | 47.59 | 38.9 | 15h30 | 1.4019 | 1.1547 | 0.75687 | 0.59488 | 0.48625
16h30 | 133.73 | 114.23 | 74.25 | 60.86 | 50.93 | 16h30 | 1.6716 | 1.4279 | 0.92812 | 0.76075 | 0.63662
17h30 | 137.27 | 130.07 | 84.67 | 70.18 | 59.39 | 17h30 | 1.7159 | 1.6259 | 1.0584 | 0.87725 | 0.74238
18h30 | 154.44 | 138.14 | 90.34 | 74.67 | 63.55 | 18h30 | 1.9305 | 1.7268 | 1.1293 | 0.93337 | 0.79438
19h30 | 154.44 | 144.75 | 101.2 | 85.08 | 73.52 | 19h30 | 1.9305 | 1.8094 | 1.265 | 1.0635 | 0.919
20h30 | 176.68 | 159.68 | 105.12 | 89.15 | 77.58 | 20h30 | 2.2085 | 1.996 | 1.314 | 1.1144 | 0.96975
21h30 | 167.94 | 148.68 | 97.47 | 81.55 | 70.66 | 21h30 | 2.0993 | 1.8585 | 1.2184 | 1.0194 | 0.88325
22h30 | 149.52 | 129.42 | 85.41 | 69.47 | 59.8 | 22h30 | 1.869 | 1.6178 | 1.0676 | 0.86838 | 0.7475
23h30 | 130.11 | 110.11 | 73.85 | 58.16 | 49.71 | 23h30 | 1.6264 | 1.3764 | 0.92312 | 0.727 | 0.62138
00h30 | 103.91 | 84.86 | 56.35 | 42.47 | 35.87 | 00h30 | 1.2989 | 1.0608 | 0.70437 | 0.53087 | 0.44838
01h30 | 111.94 | 94.09 | 60.55 | 47.39 | 39.91 | 01h30 | 1.3993 | 1.1761 | 0.75687 | 0.59237 | 0.49888
02h30 | 127.24 | 109.05 | 69.79 | 57.47 | 49.66 | 02h30 | 1.5905 | 1.3631 | 0.87238 | 0.71837 | 0.62075
03h30 | 130.89 | 111.78 | 71.72 | 58.91 | 51.02 | 03h30 | 1.6361 | 1.3973 | 0.8965 | 0.73638 | 0.63775
04h30 | 125.97 | 106.15 | 68.88 | 55.65 | 48.09 | 04h30 | 1.5746 | 1.3269 | 0.861 | 0.69563 | 0.60113
05h30 | 133.59 | 113.15 | 73.55 | 59.9 | 51.73 | 05h30 | 1.6699 | 1.4144 | 0.91938 | 0.74875 | 0.64663
06h30 | 147.21 | 126.19 | 82 | 67.54 | 58.53 | 06h30 | 1.8401 | 1.5774 | 1.025 | 0.84425 | 0.73162
07h30 | 156.05 | 137.53 | 101.04 | 84.49 | 74.53 | 07h30 | 1.9506 | 1.7191 | 1.263 | 1.0561 | 0.93163
08h30 | 159.2 | 136.07 | 91.58 | 74.57 | 64.48 | 08h30 | 1.99 | 1.7009 | 1.1447 | 0.93212 | 0.806
09h30 | 159.2 | 136.07 | 89.85 | 74.33 | 64.15 | 09h30 | 1.99 | 1.7009 | 1.1231 | 0.92912 | 0.80188
10h30 | 172.53 | 149.49 | 95.15 | 80.24 | 68.69 | 10h30 | 2.1566 | 1.8686 | 1.1894 | 1.003 | 0.85862
11h30 | 172.53 | 149.49 | 100 | 85.69 | 73.07 | 11h30 | 2.1566 | 1.8686 | 1.25 | 1.0711 | 0.91338
12h30 | 173.13 | 151.12 | 96.26 | 82.21 | 69.64 | 12h30 | 2.1641 | 1.889 | 1.2032 | 1.0276 | 0.8705
13h30 | 159.26 | 137.81 | 86.23 | 72.76 | 61.05 | 13h30 | 1.9908 | 1.7226 | 1.0779 | 0.9095 | 0.76313
14h30 | 145.03 | 125.65 | 79.28 | 65.78 | 56.37 | 14h30 | 1.8129 | 1.5706 | 0.991 | 0.82225 | 0.70462
15h30 | 139.7 | 122.55 | 72.52 | 62.09 | 51.45 | 15h30 | 1.7463 | 1.5319 | 0.9065 | 0.77612 | 0.64312
16h30 | 147.21 | 130.32 | 77.7 | 67.46 | 56.74 | 16h30 | 1.8401 | 1.629 | 0.97125 | 0.84325 | 0.70925
17h30 | 163.99 | 146.22 | 89.38 | 77.04 | 66.78 | 17h30 | 2.0499 | 1.8277 | 1.1173 | 0.963 | 0.83475
18h30 | 179.98 | 162.37 | 101.21 | 87.25 | 76.37 | 18h30 | 2.2498 | 2.0296 | 1.2651 | 1.0906 | 0.95462
19h30 | 182.4 | 162.88 | 106.8 | 92.45 | 80.42 | 19h30 | 2.28 | 2.036 | 1.335 | 1.1556 | 1.0052
20h30 | 175.69 | 158.83 | 101.61 | 86.48 | 75.14 | 20h30 | 2.1961 | 1.9854 | 1.2701 | 1.081 | 0.93925
21h30 | 157.97 | 141.37 | 90.69 | 75.55 | 65.37 | 21h30 | 1.9746 | 1.7671 | 1.1336 | 0.94437 | 0.81712
22h30 | 153.11 | 136.53 | 87.41 | 72.77 | 62.88 | 22h30 | 1.9139 | 1.7066 | 1.0926 | 0.90963 | 0.786
23h30 | 156.16 | 139.17 | 89.1 | 74.64 | 64.6 | 23h30 | 1.952 | 1.7396 | 1.1138 | 0.933 | 0.8075
00h30 | 130.24 | 113.86 | 80.55 | 67.8 | 57.5 | 00h30 | 1.628 | 1.4232 | 1.0069 | 0.8475 | 0.71875
01h30 | 118.45 | 103.03 | 64.64 | 51.1 | 43.84 | 01h30 | 1.4806 | 1.2879 | 0.808 | 0.63875 | 0.548
02h30 | 107.68 | 91.59 | 64.64 | 51.1 | 43.84 | 02h30 | 1.346 | 1.1449 | 0.808 | 0.63875 | 0.548
03h30 | 106.21 | 88.78 | 55.94 | 43.69 | 37 | 03h30 | 1.3276 | 1.1098 | 0.69925 | 0.54612 | 0.4625
04h30 | 117.36 | 98.83 | 64.1 | 50.43 | 43.23 | 04h30 | 1.467 | 1.2354 | 0.80125 | 0.63038 | 0.54038
05h30 | 134.14 | 114.61 | 73.88 | 59.48 | 51.37 | 05h30 | 1.6767 | 1.4326 | 0.9235 | 0.7435 | 0.64212
06h30 | 138.33 | 117.86 | 76.3 | 61.45 | 53.28 | 06h30 | 1.7291 | 1.4732 | 0.95375 | 0.76812 | 0.666
07h30 | 149.46 | 128.25 | 88.41 | 71.16 | 63.41 | 07h30 | 1.8682 | 1.6031 | 1.1051 | 0.8895 | 0.79263
08h30 | 150.31 | 125.7 | 83.94 | 65.85 | 57.29 | 08h30 | 1.8789 | 1.5713 | 1.0493 | 0.82312 | 0.71613
09h30 | 150.31 | 127.99 | 85.13 | 68.76 | 58.91 | 09h30 | 1.8789 | 1.5999 | 1.0641 | 0.8595 | 0.73638
10h30 | 166.52 | 143.19 | 92.63 | 76.56 | 65.74 | 10h30 | 2.0815 | 1.7899 | 1.1579 | 0.957 | 0.82175
11h30 | 166.52 | 143.19 | 113.62 | 110.49 | 96.66 | 11h30 | 2.0815 | 1.7899 | 1.4203 | 1.3811 | 1.2083
12h30 | 200 | 200 | 158.16 | 144.8 | 127.69 | 12h30 | 2.5 | 2.5 | 1.977 | 1.81 | 1.5961
13h30 | 200 | 200 | 158.16 | 145.52 | 131.83 | 13h30 | 2.5 | 2.5 | 1.977 | 1.819 | 1.6479
14h30 | 200 | 200 | 151.11 | 135.38 | 119.84 | 14h30 | 2.5 | 2.5 | 1.8889 | 1.6923 | 1.498
15h30 | 200 | 200 | 151.11 | 135.38 | 119.84 | 15h30 | 2.5 | 2.5 | 1.8889 | 1.6923 | 1.498
16h30 | 200 | 200 | 159.73 | 141.38 | 125.28 | 16h30 | 2.5 | 2.5 | 1.9966 | 1.7672 | 1.566
17h30 | 200 | 200 | 155.87 | 136.12 | 120.61 | 17h30 | 2.5 | 2.5 | 1.9484 | 1.7015 | 1.5076
18h30 | 200 | 200 | 161.66 | 140.55 | 124.83 | 18h30 | 2.5 | 2.5 | 2.0208 | 1.7569 | 1.5604
19h30 | 200 | 200 | 165.52 | 145.8 | 134.69 | 19h30 | 2.5 | 2.5 | 2.069 | 1.8225 | 1.6836
20h30 | 200 | 200 | 172.4 | 150.74 | 135.14 | 20h30 | 2.5 | 2.5 | 2.155 | 1.8842 | 1.6892
21h30 | 200 | 200 | 169.86 | 147.64 | 131.59 | 21h30 | 2.5 | 2.5 | 2.1233 | 1.8455 | 1.6449
22h30 | 200 | 200 | 167.68 | 145.28 | 128.2 | 22h30 | 2.5 | 2.5 | 2.096 | 1.816 | 1.6025
23h30 | 200 | 200 | 166.88 | 144.42 | 127.68 | 23h30 | 2.5 | 2.5 | 2.086 | 1.8053 | 1.596
00h30 | 200 | 200 | 153.63 | 132.64 | 116.21 | 00h30 | 2.5 | 2.5 | 1.9204 | 1.658 | 1.4526
01h30 | 200 | 200 | 156.85 | 136.6 | 122.79 | 01h30 | 2.5 | 2.5 | 1.9606 | 1.7075 | 1.5349
02h30 | 200 | 200 | 141.49 | 125.21 | 110.88 | 02h30 | 2.5 | 2.5 | 1.7686 | 1.5651 | 1.386
03h30 | 200 | 184.51 | 115.62 | 99.31 | 87.8 | 03h30 | 2.5 | 2.3064 | 1.4452 | 1.2414 | 1.0975
04h30 | 200 | 169.21 | 102.91 | 86.28 | 76.59 | 04h30 | 2.5 | 2.1151 | 1.2864 | 1.0785 | 0.95737
05h30 | 200 | 184.69 | 117.85 | 100.44 | 88.68 | 05h30 | 2.5 | 2.3086 | 1.4731 | 1.2555 | 1.1085
06h30 | 200 | 200 | 129.27 | 111.76 | 98.79 | 06h30 | 2.5 | 2.5 | 1.6159 | 1.397 | 1.2349
07h30 | 200 | 200 | 136.85 | 118.49 | 105.37 | 07h30 | 2.5 | 2.5 | 1.7106 | 1.4811 | 1.3171
08h30 | 200 | 195.84 | 125.34 | 106.29 | 95.26 | 08h30 | 2.5 | 2.448 | 1.5668 | 1.3286 | 1.1907
09h30 | 200 | 195.84 | 126.54 | 108.45 | 95.91 | 09h30 | 2.5 | 2.448 | 1.5817 | 1.3556 | 1.1989
10h30 | 200 | 200 | 137.39 | 120.59 | 106.34 | 10h30 | 2.5 | 2.5 | 1.7174 | 1.5074 | 1.3293
11h30 | 200 | 200 | 139.65 | 123.43 | 110.43 | 11h30 | 2.5 | 2.5 | 1.7456 | 1.5429 | 1.3804
12h30 | 200 | 200 | 150.16 | 133.87 | 118.03 | 12h30 | 2.5 | 2.5 | 1.877 | 1.6734 | 1.4754
13h30 | 200 | 200 | 150.16 | 133.87 | 118.03 | 13h30 | 2.5 | 2.5 | 1.877 | 1.6734 | 1.4754
14h30 | 200 | 200 | 149.99 | 135.18 | 118.47 | 14h30 | 2.5 | 2.5 | 1.8749 | 1.6898 | 1.4809
15h30 | 200 | 200 | 142.32 | 128.2 | 112.64 | 15h30 | 2.5 | 2.5 | 1.779 | 1.6025 | 1.408
16h30 | 200 | 200 | 142.56 | 127.37 | 112.88 | 16h30 | 2.5 | 2.5 | 1.782 | 1.5921 | 1.411
17h30 | 200 | 200 | 150.23 | 134.36 | 118.71 | 17h30 | 2.5 | 2.5 | 1.8779 | 1.6795 | 1.4839
18h30 | 200 | 200 | 165.28 | 149.28 | 131.91 | 18h30 | 2.5 | 2.5 | 2.066 | 1.866 | 1.6489
19h30 | 200 | 200 | 151.61 | 135.93 | 119.64 | 19h30 | 2.5 | 2.5 | 1.8951 | 1.6991 | 1.4955
20h30 | 200 | 200 | 137.69 | 121.76 | 107.04 | 20h30 | 2.5 | 2.5 | 1.7211 | 1.522 | 1.338
21h30 | 200 | 200 | 134.56 | 118.62 | 103.92 | 21h30 | 2.5 | 2.5 | 1.682 | 1.4828 | 1.299
22h30 | 200 | 200 | 130.22 | 114.55 | 100.11 | 22h30 | 2.5 | 2.5 | 1.6278 | 1.4319 | 1.2514
23h30 | 200 | 200 | 128.05 | 112.28 | 98.1 | 23h30 | 2.5 | 2.5 | 1.6006 | 1.4035 | 1.2263
00h30 | 200 | 184.45 | 107.58 | 92.71 | 82.6 | 00h30 | 2.5 | 2.3056 | 1.3447 | 1.1589 | 1.0325
01h30 | 200 | 181.49 | 108.04 | 95.16 | 82.11 | 01h30 | 2.5 | 2.2686 | 1.3505 | 1.1895 | 1.0264
02h30 | 200 | 175.38 | 105.29 | 92.79 | 82.11 | 02h30 | 2.5 | 2.1923 | 1.3161 | 1.1599 | 1.0264
03h30 | 189.59 | 163.47 | 99.02 | 85.72 | 74.27 | 03h30 | 2.3699 | 2.0434 | 1.2377 | 1.0715 | 0.92837
04h30 | 182.62 | 156.39 | 95.38 | 81.63 | 74.27 | 04h30 | 2.2828 | 1.9549 | 1.1923 | 1.0204 | 0.92837
05h30 | 193.03 | 167.89 | 102.88 | 88.73 | 76.82 | 05h30 | 2.4129 | 2.0986 | 1.286 | 1.1091 | 0.96025
06h30 | 200 | 188.84 | 116.08 | 101.47 | 88.58 | 06h30 | 2.5 | 2.3605 | 1.451 | 1.2684 | 1.1073
07h30 | 200 | 192.21 | 133.35 | 117.75 | 111.12 | 07h30 | 2.5 | 2.4026 | 1.6669 | 1.4719 | 1.389
08h30 | 200 | 200 | 148.66 | 132.25 | 115.75 | 08h30 | 2.5 | 2.5 | 1.8582 | 1.6531 | 1.4469
09h30 | 200 | 200 | 148.66 | 132.25 | 116.39 | 09h30 | 2.5 | 2.5 | 1.8582 | 1.6531 | 1.4549
10h30 | 200 | 200 | 144.87 | 130.54 | 113.34 | 10h30 | 2.5 | 2.5 | 1.8109 | 1.6318 | 1.4167
11h30 | 200 | 200 | 136.43 | 123.07 | 105.66 | 11h30 | 2.5 | 2.5 | 1.7054 | 1.5384 | 1.3208
12h30 | 200 | 200 | 137.26 | 124.16 | 105.57 | 12h30 | 2.5 | 2.5 | 1.7158 | 1.552 | 1.3196
13h30 | 200 | 200 | 138.7 | 126.17 | 107.17 | 13h30 | 2.5 | 2.5 | 1.7337 | 1.5771 | 1.3396
14h30 | 200 | 200 | 140.89 | 128.56 | 109.62 | 14h30 | 2.5 | 2.5 | 1.7611 | 1.607 | 1.3702
15h30 | 200 | 200 | 147.88 | 134.01 | 115.7 | 15h30 | 2.5 | 2.5 | 1.8485 | 1.6751 | 1.4463
16h30 | 200 | 200 | 154.24 | 140.06 | 120.85 | 16h30 | 2.5 | 2.5 | 1.928 | 1.7508 | 1.5106
17h30 | 200 | 200 | 148.35 | 134.12 | 115.78 | 17h30 | 2.5 | 2.5 | 1.8544 | 1.6765 | 1.4472
18h30 | 200 | 200 | 132.22 | 118.03 | 101.5 | 18h30 | 2.5 | 2.5 | 1.6527 | 1.4754 | 1.2688
19h30 | 200 | 200 | 123.18 | 108.94 | 93.5 | 19h30 | 2.5 | 2.5 | 1.5397 | 1.3618 | 1.1687
20h30 | 200 | 200 | 134.2 | 119.92 | 103.02 | 20h30 | 2.5 | 2.5 | 1.6775 | 1.499 | 1.2877
21h30 | 200 | 200 | 138.95 | 124.48 | 106.86 | 21h30 | 2.5 | 2.5 | 1.7369 | 1.556 | 1.3357
22h30 | 200 | 200 | 128.44 | 113.44 | 97.33 | 22h30 | 2.5 | 2.5 | 1.6055 | 1.418 | 1.2166
23h30 | 200 | 194.83 | 120.37 | 104.67 | 90 | 23h30 | 2.5 | 2.4354 | 1.5046 | 1.3084 | 1.125
00h30 | 172.31 | 152.18 | 88.42 | 80.77 | 83.44 | 00h30 | 2.1539 | 1.9022 | 1.1053 | 1.0096 | 1.043
01h30 | 149.9 | 126.96 | 76.7 | 63.52 | 50.89 | 01h30 | 1.8738 | 1.587 | 0.95875 | 0.794 | 0.63613
02h30 | 147.16 | 124.32 | 75.5 | 63.52 | 51.09 | 02h30 | 1.8395 | 1.554 | 0.94375 | 0.794 | 0.63862
03h30 | 144.1 | 121.39 | 74.12 | 61.48 | 50.57 | 03h30 | 1.8013 | 1.5174 | 0.9265 | 0.7685 | 0.63213
04h30 | 131.88 | 109.29 | 68.65 | 61.48 | 50.37 | 04h30 | 1.6485 | 1.3661 | 0.85813 | 0.7685 | 0.62962
05h30 | 128.23 | 105.75 | 65.83 | 50.26 | 42.15 | 05h30 | 1.6029 | 1.3219 | 0.82288 | 0.62825 | 0.52687
06h30 | 134.49 | 112.13 | 70.29 | 56.01 | 46.15 | 06h30 | 1.6811 | 1.4016 | 0.87862 | 0.70012 | 0.57688
07h30 | 161.45 | 137.74 | 91.43 | 74.65 | 63.65 | 07h30 | 2.0181 | 1.7217 | 1.1429 | 0.93312 | 0.79563
08h30 | 164.23 | 139.54 | 90.33 | 72.26 | 60.25 | 08h30 | 2.0529 | 1.7443 | 1.1291 | 0.90325 | 0.75313
09h30 | 163.25 | 139.48 | 90.54 | 73.6 | 61.58 | 09h30 | 2.0406 | 1.7435 | 1.1318 | 0.92 | 0.76975
10h30 | 136.7 | 113.77 | 87.18 | 70.24 | 60.99 | 10h30 | 1.7087 | 1.4221 | 1.0897 | 0.878 | 0.76238
11h30 | 118.06 | 95.84 | 62.47 | 45.38 | 35.85 | 11h30 | 1.4757 | 1.198 | 0.78087 | 0.56725 | 0.44812
12h30 | 122.61 | 101.15 | 65.09 | 49.17 | 39.38 | 12h30 | 1.5326 | 1.2644 | 0.81363 | 0.61462 | 0.49225
13h30 | 140.45 | 119.72 | 75.06 | 59.87 | 48.54 | 13h30 | 1.7556 | 1.4965 | 0.93825 | 0.74838 | 0.60675
14h30 | 159.38 | 139.22 | 87.07 | 71.67 | 58.97 | 14h30 | 1.9923 | 1.7403 | 1.0884 | 0.89587 | 0.73713
15h30 | 154.05 | 134.35 | 84.58 | 69.18 | 56.88 | 15h30 | 1.9256 | 1.6794 | 1.0573 | 0.86475 | 0.711
16h30 | 147.69 | 128.41 | 81.32 | 66.37 | 54.52 | 16h30 | 1.8461 | 1.6051 | 1.0165 | 0.82962 | 0.6815
17h30 | 150.67 | 131.75 | 83.6 | 69.05 | 57.25 | 17h30 | 1.8834 | 1.6469 | 1.045 | 0.86313 | 0.71562
18h30 | 158.61 | 140.03 | 88.86 | 74.46 | 62.69 | 18h30 | 1.9826 | 1.7504 | 1.1107 | 0.93075 | 0.78363
19h30 | 162.84 | 144.53 | 91.89 | 77.41 | 65.66 | 19h30 | 2.0355 | 1.8066 | 1.1486 | 0.96762 | 0.82075
20h30 | 162.79 | 144.66 | 92.15 | 77.73 | 66 | 20h30 | 2.0349 | 1.8082 | 1.1519 | 0.97162 | 0.825
21h30 | 153.63 | 135.58 | 86.76 | 72.45 | 61.21 | 21h30 | 1.9204 | 1.6947 | 1.0845 | 0.90563 | 0.76513
22h30 | 144.77 | 126.7 | 81.58 | 67.09 | 56.33 | 22h30 | 1.8096 | 1.5837 | 1.0197 | 0.83862 | 0.70413
23h30 | 147.5 | 129.34 | 83.49 | 68.46 | 57.69 | 23h30 | 1.8438 | 1.6167 | 1.0436 | 0.85575 | 0.72113
00h30 | 124.96 | 107.67 | 71.77 | 55.3 | 45.17 | 00h30 | 1.562 | 1.3459 | 0.89712 | 0.69125 | 0.56463
01h30 | 119.62 | 103.46 | 65.56 | 51.9 | 42.56 | 01h30 | 1.4952 | 1.2933 | 0.8195 | 0.64875 | 0.532
02h30 | 122.24 | 105.81 | 67.03 | 54.49 | 44.84 | 02h30 | 1.528 | 1.3226 | 0.83788 | 0.68112 | 0.5605
03h30 | 126.23 | 109.02 | 68.87 | 56.11 | 46.37 | 03h30 | 1.5779 | 1.3627 | 0.86087 | 0.70137 | 0.57962
04h30 | 114.7 | 96.89 | 67.4 | 53.52 | 44.09 | 04h30 | 1.4338 | 1.2111 | 0.8425 | 0.669 | 0.55112
05h30 | 89.67 | 71.33 | 46.79 | 32.33 | 26.07 | 05h30 | 1.1209 | 0.89163 | 0.58488 | 0.40413 | 0.32588
06h30 | 73.75 | 59.3 | 46.79 | 32.33 | 26.07 | 06h30 | 0.92188 | 0.74125 | 0.58488 | 0.40413 | 0.32588
07h30 | 69.32 | 48.9 | 39.12 | 22.99 | 18.16 | 07h30 | 0.8665 | 0.61125 | 0.489 | 0.28737 | 0.227
08h30 | 74.66 | 53.07 | 40.28 | 24.58 | 18.78 | 08h30 | 0.93325 | 0.66338 | 0.5035 | 0.30725 | 0.23475
09h30 | 113.97 | 96.57 | 64.95 | 50.2 | 41.53 | 09h30 | 1.4246 | 1.2071 | 0.81188 | 0.6275 | 0.51912
10h30 | 143.43 | 122.96 | 79.54 | 65.68 | 54.98 | 10h30 | 1.7929 | 1.537 | 0.99425 | 0.821 | 0.68725
11h30 | 143.43 | 130.56 | 90.93 | 76.8 | 64.9 | 11h30 | 1.7929 | 1.632 | 1.1366 | 0.96 | 0.81125
12h30 | 165.57 | 147.4 | 95.54 | 80.21 | 68.15 | 12h30 | 2.0696 | 1.8425 | 1.1943 | 1.0026 | 0.85188
13h30 | 165.57 | 147.4 | 95.24 | 79.45 | 67.45 | 13h30 | 2.0696 | 1.8425 | 1.1905 | 0.99313 | 0.84313
14h30 | 173.31 | 153.16 | 97.14 | 81.45 | 69.38 | 14h30 | 2.1664 | 1.9145 | 1.2143 | 1.0181 | 0.86725
15h30 | 169.4 | 149.34 | 95.29 | 79.37 | 67.72 | 15h30 | 2.1175 | 1.8667 | 1.1911 | 0.99213 | 0.8465
16h30 | 160.58 | 140.57 | 90.59 | 74.29 | 63.27 | 16h30 | 2.0072 | 1.7571 | 1.1324 | 0.92863 | 0.79087
17h30 | 146.6 | 126.81 | 82.89 | 66.46 | 56.25 | 17h30 | 1.8325 | 1.5851 | 1.0361 | 0.83075 | 0.70312
18h30 | 112.38 | 92.75 | 65.34 | 49.07 | 41.44 | 18h30 | 1.4047 | 1.1594 | 0.81675 | 0.61338 | 0.518
19h30 | 89.06 | 69.47 | 48.85 | 32.11 | 25.72 | 19h30 | 1.1133 | 0.86838 | 0.61062 | 0.40137 | 0.3215
20h30 | 86.91 | 67.26 | 48.85 | 32.11 | 25.72 | 20h30 | 1.0864 | 0.84075 | 0.61062 | 0.40137 | 0.3215
21h30 | 64.04 | 44.24 | 34.15 | 17.19 | 12.71 | 21h30 | 0.8005 | 0.553 | 0.42688 | 0.21488 | 0.15887
22h30 | 42.4 | 36.13 | 34.15 | 17.19 | 12.71 | 22h30 | 0.53 | 0.45162 | 0.42688 | 0.21488 | 0.15887
23h30 | 50.75 | 28.52 | 24 | 6.89 | 3.24 | 23h30 | 0.63438 | 0.3565 | 0.3 | 0.086125 | 0.0405
00h30 | 44.27 | 28.52 | 24 | 6.89 | 3.24 | 00h30 | 0.55337 | 0.3565 | 0.3 | 0.086125 | 0.0405
01h30 | 31 | 10.18 | 8.18 | 0 | 0 | 01h30 | 0.3875 | 0.12725 | 0.10225 | 0 | 0
02h30 | 45.14 | 25.81 | 19.08 | 5.76 | 1.71 | 02h30 | 0.56425 | 0.32262 | 0.2385 | 0.072 | 0.021375
03h30 | 54.73 | 34.63 | 24.68 | 12.74 | 9.26 | 03h30 | 0.68412 | 0.43288 | 0.3085 | 0.15925 | 0.11575
04h30 | 52 | 31.14 | 23.18 | 10.3 | 7.54 | 04h30 | 0.65 | 0.38925 | 0.28975 | 0.12875 | 0.09425
05h30 | 50.44 | 28.88 | 22.27 | 9.01 | 5.92 | 05h30 | 0.6305 | 0.361 | 0.27837 | 0.11263 | 0.074
06h30 | 56.13 | 33.95 | 25.65 | 12.24 | 8.8 | 06h30 | 0.70163 | 0.42438 | 0.32062 | 0.153 | 0.11
07h30 | 74.7 | 50.43 | 41.52 | 26.26 | 21.59 | 07h30 | 0.93375 | 0.63038 | 0.519 | 0.32825 | 0.26987
08h30 | 65.41 | 39.76 | 31.83 | 19.7 | 18.71 | 08h30 | 0.81763 | 0.497 | 0.39787 | 0.24625 | 0.23387
09h30 | 50.25 | 25.77 | 21.57 | 7.22 | 2.79 | 09h30 | 0.62813 | 0.32212 | 0.26963 | 0.09025 | 0.034875
10h30 | 42.43 | 19.24 | 18.47 | 7.22 | 2.79 | 10h30 | 0.53038 | 0.2405 | 0.23087 | 0.09025 | 0.034875
11h30 | 41.78 | 18.34 | 12.8 | 0 | 0 | 11h30 | 0.52225 | 0.22925 | 0.16 | 0 | 0
12h30 | 41.78 | 18.62 | 13.13 | 0.68 | 0 | 12h30 | 0.52225 | 0.23275 | 0.16412 | 0.0085 | 0
13h30 | 64.31 | 44.16 | 27.64 | 15.55 | 8.48 | 13h30 | 0.80388 | 0.552 | 0.3455 | 0.19437 | 0.106
14h30 | 102.51 | 83.46 | 50.7 | 38.7 | 29.65 | 14h30 | 1.2814 | 1.0433 | 0.63375 | 0.48375 | 0.37062
15h30 | 64.96 | 46.51 | 29.79 | 23.82 | 21.16 | 15h30 | 0.812 | 0.58137 | 0.37238 | 0.29775 | 0.2645
16h30 | 28.52 | 10.65 | 10.19 | 0 | 0 | 16h30 | 0.3565 | 0.13312 | 0.12737 | 0 | 0
17h30 | 81.89 | 64.98 | 43.93 | 26.86 | 18.48 | 17h30 | 1.0236 | 0.81225 | 0.54912 | 0.33575 | 0.231
18h30 | 140.5 | 124.49 | 80.4 | 63.72 | 52.24 | 18h30 | 1.7563 | 1.5561 | 1.005 | 0.7965 | 0.653
19h30 | 155.93 | 140.56 | 90.65 | 72.81 | 60.49 | 19h30 | 1.9491 | 1.757 | 1.1331 | 0.91012 | 0.75613
20h30 | 174.53 | 159.47 | 102.51 | 84.21 | 70.77 | 20h30 | 2.1816 | 1.9934 | 1.2814 | 1.0526 | 0.88462
21h30 | 178.97 | 172.85 | 110.97 | 92.12 | 77.94 | 21h30 | 2.2371 | 2.1606 | 1.3871 | 1.1515 | 0.97425
22h30 | 177.93 | 165.35 | 106.67 | 87.73 | 74.09 | 22h30 | 2.2241 | 2.0669 | 1.3334 | 1.0966 | 0.92612
23h30 | 102.03 | 86.79 | 59.46 | 43.85 | 40.19 | 23h30 | 1.2754 | 1.0849 | 0.74325 | 0.54812 | 0.50238
00h30 | 24.09 | 12.13 | 11.65 | 0 | 0 | 00h30 | 0.30112 | 0.15163 | 0.14563 | 0 | 0
01h30 | 64.83 | 49.78 | 32.41 | 15.67 | 7.05 | 01h30 | 0.81037 | 0.62225 | 0.40513 | 0.19587 | 0.088125
02h30 | 106.93 | 92.63 | 58.72 | 45.3 | 34.03 | 02h30 | 1.3366 | 1.1579 | 0.734 | 0.56625 | 0.42538
03h30 | 110.45 | 95.23 | 60.51 | 47.41 | 36.09 | 03h30 | 1.3806 | 1.1904 | 0.75638 | 0.59262 | 0.45112
04h30 | 115.83 | 99.94 | 63.83 | 50.26 | 39.05 | 04h30 | 1.4479 | 1.2492 | 0.79788 | 0.62825 | 0.48812
05h30 | 114.47 | 97.98 | 63.17 | 48.97 | 38.54 | 05h30 | 1.4309 | 1.2248 | 0.78963 | 0.61213 | 0.48175
06h30 | 71.92 | 54.94 | 38.07 | 22.72 | 16.44 | 06h30 | 0.899 | 0.68675 | 0.47587 | 0.284 | 0.2055
07h30 | 47.6 | 28.81 | 28.48 | 9.56 | 8.02 | 07h30 | 0.595 | 0.36012 | 0.356 | 0.1195 | 0.10025
08h30 | 42.67 | 24.29 | 23.95 | 3.34 | 0.18 | 08h30 | 0.53338 | 0.30362 | 0.29938 | 0.04175 | 0.00225
09h30 | 37.73 | 18.55 | 18.24 | 0 | 0 | 09h30 | 0.47163 | 0.23187 | 0.228 | 0 | 0
10h30 | 37.73 | 18.55 | 18.24 | 0 | 0 | 10h30 | 0.47163 | 0.23187 | 0.228 | 0 | 0
11h30 | 32.28 | 14.03 | 13.74 | 0 | 0 | 11h30 | 0.4035 | 0.17538 | 0.17175 | 0 | 0
12h30 | 98.02 | 80.31 | 53.24 | 35.87 | 25.3 | 12h30 | 1.2252 | 1.0039 | 0.6655 | 0.44838 | 0.31625
13h30 | 153.17 | 136.14 | 86.07 | 70.4 | 55.78 | 13h30 | 1.9146 | 1.7018 | 1.0759 | 0.88 | 0.69725
14h30 | 148.63 | 132.29 | 82.96 | 68.05 | 53.07 | 14h30 | 1.8579 | 1.6536 | 1.037 | 0.85062 | 0.66338
15h30 | 161.21 | 153.8 | 96.05 | 80.41 | 64.95 | 15h30 | 2.0151 | 1.9225 | 1.2006 | 1.0051 | 0.81188
16h30 | 177.84 | 164.85 | 103.92 | 86.61 | 71.74 | 16h30 | 2.223 | 2.0606 | 1.299 | 1.0826 | 0.89675
17h30 | 166.21 | 150.93 | 96.53 | 78.89 | 65.19 | 17h30 | 2.0776 | 1.8866 | 1.2066 | 0.98613 | 0.81488
18h30 | 157.33 | 141.58 | 91.45 | 73.71 | 61.02 | 18h30 | 1.9666 | 1.7697 | 1.1431 | 0.92138 | 0.76275
19h30 | 157.75 | 142.33 | 92.2 | 74.23 | 61.53 | 19h30 | 1.9719 | 1.7791 | 1.1525 | 0.92788 | 0.76912
20h30 | 161.77 | 146.45 | 94.72 | 76.87 | 63.76 | 20h30 | 2.0221 | 1.8306 | 1.184 | 0.96088 | 0.797
21h30 | 170.82 | 155.44 | 100.34 | 82.13 | 68.59 | 21h30 | 2.1353 | 1.943 | 1.2543 | 1.0266 | 0.85737
22h30 | 175.87 | 160.33 | 103.51 | 84.98 | 71.14 | 22h30 | 2.1984 | 2.0041 | 1.2939 | 1.0622 | 0.88925
23h30 | 178.04 | 163.16 | 105.3 | 86.77 | 72.75 | 23h30 | 2.2255 | 2.0395 | 1.3162 | 1.0846 | 0.90938
00h30 | 161.4 | 146.59 | 89.4 | 71.95 | 58.15 | 00h30 | 2.0175 | 1.8324 | 1.1175 | 0.89938 | 0.72688
01h30 | 155.88 | 141.92 | 89.17 | 73.96 | 60.47 | 01h30 | 1.9485 | 1.774 | 1.1146 | 0.9245 | 0.75587
02h30 | 180.31 | 166.01 | 103.8 | 89.42 | 74 | 02h30 | 2.2539 | 2.0751 | 1.2975 | 1.1178 | 0.925
03h30 | 185.83 | 180.65 | 120.24 | 105.24 | 88.52 | 03h30 | 2.3229 | 2.2581 | 1.503 | 1.3155 | 1.1065
04h30 | 171.16 | 159.06 | 102.85 | 87.24 | 73.22 | 04h30 | 2.1395 | 1.9883 | 1.2856 | 1.0905 | 0.91525
05h30 | 171.16 | 159.06 | 107.44 | 91.14 | 77.17 | 05h30 | 2.1395 | 1.9883 | 1.343 | 1.1393 | 0.96462
06h30 | 200 | 189.49 | 121.27 | 104.63 | 89.02 | 06h30 | 2.5 | 2.3686 | 1.5159 | 1.3079 | 1.1127
07h30 | 188.55 | 171.34 | 113.89 | 95.65 | 82.89 | 07h30 | 2.3569 | 2.1418 | 1.4236 | 1.1956 | 1.0361
08h30 | 156.69 | 137.2 | 87.63 | 69.43 | 57.98 | 08h30 | 1.9586 | 1.715 | 1.0954 | 0.86787 | 0.72475
09h30 | 168.14 | 155.35 | 99.72 | 83.86 | 69.38 | 09h30 | 2.1018 | 1.9419 | 1.2465 | 1.0482 | 0.86725
10h30 | 200 | 195.97 | 121.4 | 105.31 | 88.54 | 10h30 | 2.5 | 2.4496 | 1.5175 | 1.3164 | 1.1067
11h30 | 200 | 195.97 | 134.1 | 117.35 | 98.93 | 11h30 | 2.5 | 2.4496 | 1.6763 | 1.4669 | 1.2366
12h30 | 199.84 | 186.47 | 120.71 | 104 | 86.8 | 12h30 | 2.498 | 2.3309 | 1.5089 | 1.3 | 1.085
13h30 | 158.03 | 140.44 | 88.71 | 72.48 | 58.92 | 13h30 | 1.9754 | 1.7555 | 1.1089 | 0.906 | 0.7365
14h30 | 83.25 | 65.92 | 66.67 | 54.4 | 51.31 | 14h30 | 1.0406 | 0.824 | 0.83337 | 0.68 | 0.64138
15h30 | 27.47 | 11.95 | 4.75 | 0 | 0 | 15h30 | 0.34337 | 0.14938 | 0.059375 | 0 | 0
16h30 | 72.15 | 55.6 | 37.65 | 18.93 | 10.59 | 16h30 | 0.90187 | 0.695 | 0.47063 | 0.23663 | 0.13237
17h30 | 120.95 | 104.77 | 66.2 | 49.74 | 39.28 | 17h30 | 1.5119 | 1.3096 | 0.8275 | 0.62175 | 0.491
18h30 | 127.97 | 111.83 | 71.59 | 54.05 | 43.83 | 18h30 | 1.5996 | 1.3979 | 0.89487 | 0.67563 | 0.54788
19h30 | 81.37 | 65.37 | 44.25 | 26.68 | 19.72 | 19h30 | 1.0171 | 0.81712 | 0.55312 | 0.3335 | 0.2465
20h30 | 99.08 | 83.17 | 54.81 | 37.85 | 28.29 | 20h30 | 1.2385 | 1.0396 | 0.68512 | 0.47313 | 0.35363
21h30 | 156.25 | 140.38 | 88.38 | 72.86 | 56.82 | 21h30 | 1.9531 | 1.7548 | 1.1047 | 0.91075 | 0.71025
22h30 | 159.64 | 143.78 | 89.56 | 75.43 | 56.62 | 22h30 | 1.9955 | 1.7973 | 1.1195 | 0.94288 | 0.70775
23h30 | 189.93 | 174.01 | 107.47 | 93.58 | 72.35 | 23h30 | 2.3741 | 2.1751 | 1.3434 | 1.1698 | 0.90438
00h30 | 192.08 | 190.15 | 122.1 | 108.78 | 86.74 | 00h30 | 2.401 | 2.3769 | 1.5263 | 1.3598 | 1.0842
01h30 | 200 | 200 | 145.78 | 133.86 | 110.62 | 01h30 | 2.5 | 2.5 | 1.8222 | 1.6732 | 1.3827
02h30 | 200 | 200 | 136.79 | 125.36 | 103.34 | 02h30 | 2.5 | 2.5 | 1.7099 | 1.567 | 1.2917
03h30 | 197.89 | 187.73 | 117.65 | 105.98 | 87.69 | 03h30 | 2.4736 | 2.3466 | 1.4706 | 1.3248 | 1.0961
04h30 | 169.65 | 153.05 | 94.85 | 82.59 | 67.95 | 04h30 | 2.1206 | 1.9131 | 1.1856 | 1.0324 | 0.84937
05h30 | 145.37 | 128.86 | 80.13 | 67.09 | 54.72 | 05h30 | 1.8171 | 1.6107 | 1.0016 | 0.83862 | 0.684
06h30 | 123.71 | 107.2 | 67.85 | 54.03 | 43.85 | 06h30 | 1.5464 | 1.34 | 0.84813 | 0.67537 | 0.54812
07h30 | 143.49 | 125.24 | 84.78 | 67.76 | 58.93 | 07h30 | 1.7936 | 1.5655 | 1.0597 | 0.847 | 0.73662
08h30 | 193.38 | 181.58 | 124.15 | 104.42 | 89.82 | 08h30 | 2.4173 | 2.2698 | 1.5519 | 1.3053 | 1.1227
09h30 | 200 | 200 | 153.03 | 135.22 | 114.37 | 09h30 | 2.5 | 2.5 | 1.9129 | 1.6903 | 1.4296
10h30 | 200 | 190.68 | 127.03 | 112.51 | 92.97 | 10h30 | 2.5 | 2.3835 | 1.5879 | 1.4064 | 1.1621
11h30 | 200 | 190.53 | 116.32 | 102.97 | 83.86 | 11h30 | 2.5 | 2.3816 | 1.454 | 1.2871 | 1.0482
12h30 | 200 | 199.85 | 130.7 | 116.94 | 95.63 | 12h30 | 2.5 | 2.4981 | 1.6338 | 1.4618 | 1.1954
13h30 | 200 | 200 | 132.81 | 119.52 | 97.99 | 13h30 | 2.5 | 2.5 | 1.6601 | 1.494 | 1.2249
14h30 | 200 | 200 | 125.12 | 112.47 | 92.57 | 14h30 | 2.5 | 2.5 | 1.564 | 1.4059 | 1.1571
15h30 | 200 | 188.9 | 113.53 | 101.37 | 82.86 | 15h30 | 2.5 | 2.3613 | 1.4191 | 1.2671 | 1.0357
16h30 | 186.19 | 170.79 | 102.01 | 90.36 | 73.52 | 16h30 | 2.3274 | 2.1349 | 1.2751 | 1.1295 | 0.919
17h30 | 172.83 | 156.82 | 94.76 | 82.16 | 68.13 | 17h30 | 2.1604 | 1.9603 | 1.1845 | 1.027 | 0.85162
18h30 | 165.34 | 149.83 | 92.03 | 77.88 | 65.32 | 18h30 | 2.0667 | 1.8729 | 1.1504 | 0.9735 | 0.8165
19h30 | 175.34 | 160.33 | 99.41 | 84.14 | 70.86 | 19h30 | 2.1917 | 2.0041 | 1.2426 | 1.0517 | 0.88575
20h30 | 188.13 | 173.38 | 108.02 | 91.77 | 77.78 | 20h30 | 2.3516 | 2.1673 | 1.3502 | 1.1471 | 0.97225
21h30 | 182.46 | 167.72 | 104.88 | 88.66 | 74.84 | 21h30 | 2.2807 | 2.0965 | 1.311 | 1.1082 | 0.9355
22h30 | 173.25 | 158.38 | 99.23 | 83.45 | 69.87 | 22h30 | 2.1656 | 1.9797 | 1.2404 | 1.0431 | 0.87338
23h30 | 171.35 | 156.25 | 98.13 | 82.12 | 68.69 | 23h30 | 2.1419 | 1.9531 | 1.2266 | 1.0265 | 0.85862
00h30 | 138.9 | 124.54 | 73.43 | 66.91 | 63.05 | 00h30 | 1.7363 | 1.5568 | 0.91787 | 0.83637 | 0.78812
01h30 | 130.03 | 116.85 | 71.66 | 59.1 | 47.37 | 01h30 | 1.6254 | 1.4606 | 0.89575 | 0.73875 | 0.59213
02h30 | 136.12 | 122.66 | 75.39 | 63.24 | 50.96 | 02h30 | 1.7015 | 1.5333 | 0.94237 | 0.7905 | 0.637
03h30 | 144.05 | 129.61 | 80.05 | 67.01 | 53.11 | 03h30 | 1.8006 | 1.6201 | 1.0006 | 0.83762 | 0.66387
04h30 | 140.49 | 125.29 | 77.88 | 64.86 | 51.73 | 04h30 | 1.7561 | 1.5661 | 0.9735 | 0.81075 | 0.64663
05h30 | 119.7 | 103.86 | 65.36 | 52.24 | 41.12 | 05h30 | 1.4963 | 1.2982 | 0.817 | 0.653 | 0.514
06h30 | 107 | 90.63 | 59.18 | 50.24 | 38.91 | 06h30 | 1.3375 | 1.1329 | 0.73975 | 0.628 | 0.48638
07h30 | 125.83 | 107.39 | 73.76 | 57.49 | 48.3 | 07h30 | 1.5729 | 1.3424 | 0.922 | 0.71862 | 0.60375
08h30 | 86.17 | 72.23 | 73.76 | 57.49 | 48.3 | 08h30 | 1.0771 | 0.90287 | 0.922 | 0.71862 | 0.60375
09h30 | 37.99 | 17.53 | 13.51 | 0 | 0 | 09h30 | 0.47487 | 0.21912 | 0.16887 | 0 | 0
10h30 | 37.99 | 17.53 | 14.65 | 0 | 0 | 10h30 | 0.47487 | 0.21912 | 0.18313 | 0 | 0
11h30 | 56.48 | 37.9 | 25.78 | 10.16 | 3.52 | 11h30 | 0.706 | 0.47375 | 0.32225 | 0.127 | 0.044
12h30 | 81.99 | 63.92 | 40.75 | 26.48 | 18.77 | 12h30 | 1.0249 | 0.799 | 0.50938 | 0.331 | 0.23463
13h30 | 87.79 | 70.35 | 44.6 | 30.21 | 22.21 | 13h30 | 1.0974 | 0.87938 | 0.5575 | 0.37762 | 0.27763
14h30 | 93.99 | 76.91 | 48.77 | 34.06 | 25.8 | 14h30 | 1.1749 | 0.96137 | 0.60962 | 0.42575 | 0.3225
15h30 | 60.72 | 43.98 | 29.45 | 20.16 | 18.85 | 15h30 | 0.759 | 0.54975 | 0.36812 | 0.252 | 0.23563
16h30 | 29 | 11.42 | 10.48 | 0 | 0 | 16h30 | 0.3625 | 0.14275 | 0.131 | 0 | 0
17h30 | 28.42 | 12.31 | 11.42 | 0 | 0 | 17h30 | 0.35525 | 0.15388 | 0.14275 | 0 | 0
18h30 | 28.42 | 12.3 | 11.31 | 0 | 0 | 18h30 | 0.35525 | 0.15375 | 0.14138 | 0 | 0
19h30 | 27.46 | 11.88 | 11.12 | 0 | 0 | 19h30 | 0.34325 | 0.1485 | 0.139 | 0 | 0
20h30 | 27.46 | 11.91 | 11.16 | 0 | 0 | 20h30 | 0.34325 | 0.14888 | 0.1395 | 0 | 0
21h30 | 27.65 | 12.33 | 11.64 | 0 | 0 | 21h30 | 0.34563 | 0.15413 | 0.1455 | 0 | 0
22h30 | 27.85 | 12.62 | 11.97 | 0 | 0 | 22h30 | 0.34813 | 0.15775 | 0.14963 | 0 | 0
23h30 | 27.27 | 12.18 | 11.57 | 0 | 0 | 23h30 | 0.34087 | 0.15225 | 0.14463 | 0 | 0
00h30 | 27.08 | 11.86 | 9.98 | 0 | 0 | 00h30 | 0.3385 | 0.14825 | 0.12475 | 0 | 0
01h30 | 13.52 | 0 | 0 | 0 | 0 | 01h30 | 0.169 | 0 | 0 | 0 | 0
02h30 | 15.41 | 3.21 | 2.83 | 0 | 0 | 02h30 | 0.19262 | 0.040125 | 0.035375 | 0 | 0
03h30 | 15.75 | 3.68 | 3.38 | 0 | 0 | 03h30 | 0.19687 | 0.046 | 0.04225 | 0 | 0
04h30 | 89.76 | 77.24 | 47.95 | 29.37 | 14.39 | 04h30 | 1.122 | 0.9655 | 0.59937 | 0.36712 | 0.17988
05h30 | 175.9 | 176.77 | 123.55 | 108.97 | 84.62 | 05h30 | 2.1987 | 2.2096 | 1.5444 | 1.3621 | 1.0577
06h30 | 200 | 200 | 155.05 | 139.49 | 114 | 06h30 | 2.5 | 2.5 | 1.9381 | 1.7436 | 1.425
07h30 | 200 | 200 | 172.15 | 156.48 | 134.57 | 07h30 | 2.5 | 2.5 | 2.1519 | 1.956 | 1.6821
08h30 | 200 | 200 | 161.05 | 144.04 | 123.81 | 08h30 | 2.5 | 2.5 | 2.0131 | 1.8005 | 1.5476
09h30 | 200 | 200 | 147.99 | 130.38 | 110.33 | 09h30 | 2.5 | 2.5 | 1.8499 | 1.6298 | 1.3791
10h30 | 200 | 200 | 145.7 | 129.55 | 109.28 | 10h30 | 2.5 | 2.5 | 1.8213 | 1.6194 | 1.366
11h30 | 200 | 200 | 155.71 | 140.62 | 118.58 | 11h30 | 2.5 | 2.5 | 1.9464 | 1.7577 | 1.4823
12h30 | 200 | 200 | 168.87 | 154.27 | 130.81 | 12h30 | 2.5 | 2.5 | 2.1109 | 1.9284 | 1.6351
13h30 | 200 | 200 | 173.06 | 159.09 | 135.61 | 13h30 | 2.5 | 2.5 | 2.1633 | 1.9886 | 1.6951
14h30 | 200 | 200 | 171.36 | 158.62 | 134.78 | 14h30 | 2.5 | 2.5 | 2.142 | 1.9828 | 1.6847
15h30 | 200 | 200 | 163.63 | 151.56 | 127.75 | 15h30 | 2.5 | 2.5 | 2.0454 | 1.8945 | 1.5969
16h30 | 200 | 200 | 149.03 | 136.7 | 114.84 | 16h30 | 2.5 | 2.5 | 1.8629 | 1.7087 | 1.4355
17h30 | 200 | 200 | 141.02 | 127.95 | 108.65 | 17h30 | 2.5 | 2.5 | 1.7628 | 1.5994 | 1.3581
18h30 | 200 | 199.26 | 124.51 | 110.27 | 94.22 | 18h30 | 2.5 | 2.4907 | 1.5564 | 1.3784 | 1.1778
19h30 | 186.97 | 172.27 | 103.92 | 88.5 | 75.4 | 19h30 | 2.3371 | 2.1534 | 1.299 | 1.1062 | 0.9425
20h30 | 179.63 | 162.01 | 97.4 | 80.89 | 68.93 | 20h30 | 2.2454 | 2.0251 | 1.2175 | 1.0111 | 0.86162
21h30 | 179.52 | 161.36 | 98.25 | 80.87 | 69.02 | 21h30 | 2.244 | 2.017 | 1.2281 | 1.0109 | 0.86275
22h30 | 176.71 | 158.88 | 97.42 | 79.81 | 67.99 | 22h30 | 2.2089 | 1.986 | 1.2178 | 0.99762 | 0.84988
23h30 | 163.2 | 145.34 | 89.75 | 72.07 | 61.14 | 23h30 | 2.04 | 1.8168 | 1.1219 | 0.90087 | 0.76425
00h30 | 112.15 | 95.18 | 54.34 | 53.48 | 52.6 | 00h30 | 1.4019 | 1.1898 | 0.67925 | 0.6685 | 0.6575
01h30 | 85.89 | 70.07 | 42.68 | 26.26 | 15.93 | 01h30 | 1.0736 | 0.87587 | 0.5335 | 0.32825 | 0.19912
02h30 | 82.15 | 65.96 | 41.03 | 26.52 | 18.61 | 02h30 | 1.0269 | 0.8245 | 0.51287 | 0.3315 | 0.23262
03h30 | 59.11 | 41.94 | 27.44 | 11.63 | 5.62 | 03h30 | 0.73887 | 0.52425 | 0.343 | 0.14538 | 0.07025
04h30 | 32.85 | 14.89 | 25.97 | 11.37 | 2.94 | 04h30 | 0.41063 | 0.18613 | 0.32462 | 0.14213 | 0.03675
05h30 | 48.67 | 29.99 | 16.74 | 0 | 0 | 05h30 | 0.60837 | 0.37488 | 0.20925 | 0 | 0
06h30 | 64.07 | 44.71 | 29.92 | 14.57 | 9.88 | 06h30 | 0.80088 | 0.55888 | 0.374 | 0.18213 | 0.1235
07h30 | 88.57 | 67.06 | 48.01 | 32.41 | 27.75 | 07h30 | 1.1071 | 0.83825 | 0.60013 | 0.40513 | 0.34687
08h30 | 98.74 | 75.81 | 50.1 | 32.9 | 26.81 | 08h30 | 1.2343 | 0.94763 | 0.62625 | 0.41125 | 0.33513
09h30 | 100.49 | 78.71 | 50.37 | 33.88 | 25.99 | 09h30 | 1.2561 | 0.98388 | 0.62962 | 0.4235 | 0.32488
10h30 | 98.08 | 77.36 | 47.71 | 32.31 | 24.38 | 10h30 | 1.226 | 0.967 | 0.59637 | 0.40387 | 0.30475
11h30 | 111.31 | 91 | 55.58 | 40.59 | 31.39 | 11h30 | 1.3914 | 1.1375 | 0.69475 | 0.50738 | 0.39237
12h30 | 124.47 | 104.43 | 63.85 | 48.92 | 38.25 | 12h30 | 1.5559 | 1.3054 | 0.79812 | 0.6115 | 0.47813
13h30 | 126.55 | 107.21 | 65.35 | 50.87 | 39.68 | 13h30 | 1.5819 | 1.3401 | 0.81688 | 0.63587 | 0.496
14h30 | 122.88 | 104.39 | 63.51 | 49.29 | 38.19 | 14h30 | 1.536 | 1.3049 | 0.79387 | 0.61613 | 0.47737
15h30 | 123.5 | 105.51 | 64.87 | 49.85 | 39.13 | 15h30 | 1.5437 | 1.3189 | 0.81088 | 0.62313 | 0.48912
16h30 | 147.54 | 129.87 | 80.61 | 64.56 | 52.83 | 16h30 | 1.8442 | 1.6234 | 1.0076 | 0.807 | 0.66038
17h30 | 164.28 | 146.98 | 91.81 | 75.23 | 62.74 | 17h30 | 2.0535 | 1.8373 | 1.1476 | 0.94037 | 0.78425
18h30 | 156 | 139.05 | 87.56 | 71.01 | 59.31 | 18h30 | 1.95 | 1.7381 | 1.0945 | 0.88762 | 0.74138
19h30 | 154.91 | 138.22 | 87.29 | 70.97 | 59.31 | 19h30 | 1.9364 | 1.7277 | 1.0911 | 0.88713 | 0.74138
20h30 | 165.44 | 148.88 | 94.03 | 77.43 | 65.04 | 20h30 | 2.068 | 1.861 | 1.1754 | 0.96788 | 0.813
21h30 | 167.73 | 161.08 | 101.79 | 84.58 | 71.2 | 21h30 | 2.0966 | 2.0135 | 1.2724 | 1.0573 | 0.89
22h30 | 183.18 | 169.45 | 107.19 | 89.47 | 75.32 | 22h30 | 2.2898 | 2.1181 | 1.3399 | 1.1184 | 0.9415
23h30 | 164.84 | 148.34 | 94.86 | 76.7 | 64.03 | 23h30 | 2.0605 | 1.8542 | 1.1858 | 0.95875 | 0.80037
00h30 | 125.39 | 108.64 | 65.22 | 48.54 | 38.09 | 00h30 | 1.5674 | 1.358 | 0.81525 | 0.60675 | 0.47613
01h30 | 117.49 | 102.09 | 63.87 | 49.84 | 39.73 | 01h30 | 1.4686 | 1.2761 | 0.79837 | 0.623 | 0.49662
02h30 | 109.83 | 94.12 | 59.17 | 46.08 | 35.74 | 02h30 | 1.3729 | 1.1765 | 0.73962 | 0.576 | 0.44675
03h30 | 120.89 | 104.28 | 65.76 | 52.36 | 41.58 | 03h30 | 1.5111 | 1.3035 | 0.822 | 0.6545 | 0.51975
04h30 | 131.66 | 114.39 | 72.23 | 58.49 | 47.01 | 04h30 | 1.6458 | 1.4299 | 0.90287 | 0.73113 | 0.58762
05h30 | 141.14 | 123.29 | 78.01 | 63.76 | 51.97 | 05h30 | 1.7643 | 1.5411 | 0.97513 | 0.797 | 0.64963
06h30 | 147.69 | 129.3 | 82.16 | 67.18 | 55.36 | 06h30 | 1.8461 | 1.6162 | 1.027 | 0.83975 | 0.692
07h30 | 153.38 | 140.58 | 94.98 | 76.48 | 67.14 | 07h30 | 1.9172 | 1.7572 | 1.1872 | 0.956 | 0.83925
08h30 | 147.35 | 126.89 | 84.48 | 64.05 | 55.43 | 08h30 | 1.8419 | 1.5861 | 1.056 | 0.80063 | 0.69288
09h30 | 143.45 | 122.39 | 81.57 | 62.91 | 51.25 | 09h30 | 1.7931 | 1.5299 | 1.0196 | 0.78638 | 0.64062
10h30 | 124.78 | 103.66 | 73.11 | 55.64 | 51.25 | 10h30 | 1.5597 | 1.2957 | 0.91387 | 0.6955 | 0.64062
11h30 | 104.66 | 84.22 | 55.63 | 39.52 | 28.61 | 11h30 | 1.3082 | 1.0528 | 0.69537 | 0.494 | 0.35763
12h30 | 75.97 | 74.77 | 55.63 | 39.52 | 28.61 | 12h30 | 0.94963 | 0.93463 | 0.69537 | 0.494 | 0.35763
13h30 | 27.47 | 3.4 | 3.49 | 0 | 0 | 13h30 | 0.34337 | 0.0425 | 0.043625 | 0 | 0
14h30 | 27.47 | 7.58 | 7 | 0 | 0 | 14h30 | 0.34337 | 0.09475 | 0.0875 | 0 | 0
15h30 | 24.34 | 6.13 | 5.73 | 0 | 0 | 15h30 | 0.30425 | 0.076625 | 0.071625 | 0 | 0
16h30 | 26 | 8.18 | 7.73 | 0 | 0 | 16h30 | 0.325 | 0.10225 | 0.096625 | 0 | 0
17h30 | 27.29 | 10.05 | 9.59 | 0 | 0 | 17h30 | 0.34113 | 0.12562 | 0.11987 | 0 | 0
18h30 | 28.12 | 11.38 | 10.93 | 0 | 0 | 18h30 | 0.3515 | 0.14225 | 0.13662 | 0 | 0
19h30 | 29.09 | 12.89 | 12.45 | 0 | 0 | 19h30 | 0.36362 | 0.16112 | 0.15563 | 0 | 0
20h30 | 30.38 | 14.62 | 14.2 | 0 | 0 | 20h30 | 0.37975 | 0.18275 | 0.1775 | 0 | 0
21h30 | 30.64 | 15.1 | 14.69 | 0 | 0 | 21h30 | 0.383 | 0.18875 | 0.18363 | 0 | 0
22h30 | 30.26 | 14.81 | 14.4 | 0 | 0 | 22h30 | 0.37825 | 0.18513 | 0.18 | 0 | 0
23h30 | 31.8 | 16.42 | 16.03 | 0 | 0 | 23h30 | 0.3975 | 0.20525 | 0.20037 | 0 | 0
00h30 | 28.4 | 7.43 | 7.73 | 0 | 0 | 00h30 | 0.355 | 0.092875 | 0.096625 | 0 | 0
01h30 | 21.22 | 8.36 | 7.95 | 0 | 0 | 01h30 | 0.26525 | 0.1045 | 0.099375 | 0 | 0
02h30 | 22.6 | 9.3 | 9.04 | 0 | 0 | 02h30 | 0.2825 | 0.11625 | 0.113 | 0 | 0
03h30 | 23.36 | 9.87 | 9.56 | 0 | 0 | 03h30 | 0.292 | 0.12337 | 0.1195 | 0 | 0
04h30 | 24.06 | 9.72 | 9.41 | 0 | 0 | 04h30 | 0.30075 | 0.1215 | 0.11762 | 0 | 0
05h30 | 25.07 | 10.11 | 9.8 | 0 | 0 | 05h30 | 0.31338 | 0.12637 | 0.1225 | 0 | 0
06h30 | 26.31 | 10.84 | 10.54 | 0 | 0 | 06h30 | 0.32887 | 0.1355 | 0.13175 | 0 | 0
07h30 | 43.41 | 26.01 | 25.67 | 4.69 | 0 | 07h30 | 0.54263 | 0.32512 | 0.32088 | 0.058625 | 0
08h30 | 40.09 | 24.49 | 24 | 4.69 | 0 | 08h30 | 0.50113 | 0.30612 | 0.3 | 0.058625 | 0
09h30 | 37.58 | 18.93 | 18.61 | 0 | 0 | 09h30 | 0.46975 | 0.23663 | 0.23262 | 0 | 0
10h30 | 37.58 | 18.93 | 18.61 | 0 | 0 | 10h30 | 0.46975 | 0.23663 | 0.23262 | 0 | 0
11h30 | 61.39 | 43.93 | 30.29 | 12.18 | 2.41 | 11h30 | 0.76738 | 0.54912 | 0.37862 | 0.15225 | 0.030125
12h30 | 91.25 | 74.46 | 47.75 | 31.78 | 21.78 | 12h30 | 1.1406 | 0.93075 | 0.59688 | 0.39725 | 0.27225
13h30 | 86.75 | 70.58 | 45.13 | 29.36 | 20.15 | 13h30 | 1.0844 | 0.88225 | 0.56412 | 0.367 | 0.25188
14h30 | 95.81 | 80.03 | 50.64 | 35.54 | 25.37 | 14h30 | 1.1976 | 1.0004 | 0.633 | 0.44425 | 0.31712
15h30 | 106.82 | 91.37 | 57.63 | 42.65 | 32.11 | 15h30 | 1.3353 | 1.1421 | 0.72037 | 0.53312 | 0.40137
16h30 | 101.47 | 86.31 | 55.22 | 39.82 | 30.25 | 16h30 | 1.2684 | 1.0789 | 0.69025 | 0.49775 | 0.37812
17h30 | 94.82 | 79.92 | 52.14 | 36.28 | 27.42 | 17h30 | 1.1852 | 0.999 | 0.65175 | 0.4535 | 0.34275
18h30 | 98.02 | 83.36 | 54.89 | 38.47 | 29.5 | 18h30 | 1.2252 | 1.042 | 0.68612 | 0.48087 | 0.36875
19h30 | 108.26 | 93.74 | 61.51 | 44.82 | 34.93 | 19h30 | 1.3533 | 1.1718 | 0.76887 | 0.56025 | 0.43662
20h30 | 120.17 | 105.66 | 68.94 | 52.02 | 41.35 | 20h30 | 1.5021 | 1.3208 | 0.86175 | 0.65025 | 0.51687
21h30 | 127.99 | 113.34 | 73.94 | 56.47 | 45.51 | 21h30 | 1.5999 | 1.4167 | 0.92425 | 0.70588 | 0.56888
22h30 | 124.79 | 109.86 | 72.2 | 54.39 | 43.91 | 22h30 | 1.5599 | 1.3733 | 0.9025 | 0.67988 | 0.54888
23h30 | 127.2 | 111.9 | 73.81 | 55.6 | 45.35 | 23h30 | 1.59 | 1.3987 | 0.92263 | 0.695 | 0.56688
00h30 | 115.98 | 101.29 | 61.76 | 44.64 | 34.93 | 00h30 | 1.4498 | 1.2661 | 0.772 | 0.558 | 0.43662
01h30 | 104.79 | 91.06 | 58.44 | 43.28 | 34.28 | 01h30 | 1.3099 | 1.1382 | 0.7305 | 0.541 | 0.4285
02h30 | 88.08 | 73.85 | 48.49 | 33.72 | 25.02 | 02h30 | 1.101 | 0.92312 | 0.60613 | 0.4215 | 0.31275
03h30 | 86.44 | 71.1 | 47.25 | 32.47 | 24.31 | 03h30 | 1.0805 | 0.88875 | 0.59062 | 0.40587 | 0.30388
04h30 | 93.61 | 77.39 | 51.36 | 36.33 | 28.05 | 04h30 | 1.1701 | 0.96737 | 0.642 | 0.45413 | 0.35063
05h30 | 100.78 | 83.72 | 55.76 | 39.82 | 31.58 | 05h30 | 1.2597 | 1.0465 | 0.697 | 0.49775 | 0.39475
06h30 | 96.57 | 78.69 | 53.24 | 36.72 | 29.21 | 06h30 | 1.2071 | 0.98362 | 0.6655 | 0.459 | 0.36512
07h30 | 79.09 | 59.13 | 47.21 | 27.47 | 24.06 | 07h30 | 0.98862 | 0.73913 | 0.59013 | 0.34337 | 0.30075
08h30 | 58.55 | 38.87 | 38.62 | 16.99 | 12.75 | 08h30 | 0.73188 | 0.48588 | 0.48275 | 0.21238 | 0.15937
09h30 | 41.73 | 19.38 | 19.19 | 0 | 0 | 09h30 | 0.52163 | 0.24225 | 0.23988 | 0 | 0
10h30 | 41.73 | 19.38 | 19.19 | 0 | 0 | 10h30 | 0.52163 | 0.24225 | 0.23988 | 0 | 0
11h30 | 34.9 | 14.78 | 14.62 | 0 | 0 | 11h30 | 0.43625 | 0.18475 | 0.18275 | 0 | 0
12h30 | 34.9 | 14.78 | 14.62 | 0 | 0 | 12h30 | 0.43625 | 0.18475 | 0.18275 | 0 | 0
13h30 | 32.57 | 13.29 | 13.13 | 0 | 0 | 13h30 | 0.40713 | 0.16612 | 0.16412 | 0 | 0
14h30 | 32.57 | 13.53 | 13.38 | 0 | 0 | 14h30 | 0.40713 | 0.16912 | 0.16725 | 0 | 0
15h30 | 33.16 | 14.82 | 14.67 | 0 | 0 | 15h30 | 0.4145 | 0.18525 | 0.18338 | 0 | 0
16h30 | 35.33 | 17.33 | 17.19 | 0 | 0 | 16h30 | 0.44162 | 0.21663 | 0.21488 | 0 | 0
17h30 | 36.72 | 19.02 | 18.88 | 0 | 0 | 17h30 | 0.459 | 0.23775 | 0.236 | 0 | 0
18h30 | 37.32 | 19.9 | 19.76 | 0 | 0 | 18h30 | 0.4665 | 0.24875 | 0.247 | 0 | 0
19h30 | 37.52 | 20.35 | 20.21 | 0 | 0 | 19h30 | 0.469 | 0.25438 | 0.25262 | 0 | 0
20h30 | 36.71 | 19.69 | 19.55 | 0 | 0 | 20h30 | 0.45887 | 0.24613 | 0.24438 | 0 | 0
21h30 | 35 | 18.05 | 17.91 | 0 | 0 | 21h30 | 0.4375 | 0.22562 | 0.22387 | 0 | 0
22h30 | 109.15 | 92.31 | 61.91 | 42.7 | 28.47 | 22h30 | 1.3644 | 1.1539 | 0.77387 | 0.53375 | 0.35587
23h30 | 169.79 | 153.08 | 97.86 | 80.06 | 61.71 | 23h30 | 2.1224 | 1.9135 | 1.2232 | 1.0008 | 0.77138
00h30 | 115.59 | 100.04 | 59.46 | 44.04 | 33.24 | 00h30 | 1.4449 | 1.2505 | 0.74325 | 0.5505 | 0.4155
01h30 | 99.23 | 85.19 | 53.06 | 40.06 | 27.35 | 01h30 | 1.2404 | 1.0649 | 0.66325 | 0.50075 | 0.34187
02h30 | 124.32 | 110.34 | 68.51 | 55.95 | 39.96 | 02h30 | 1.554 | 1.3793 | 0.85637 | 0.69937 | 0.4995
03h30 | 147 | 139.85 | 86.55 | 74.18 | 55.11 | 03h30 | 1.8375 | 1.7481 | 1.0819 | 0.92725 | 0.68888
04h30 | 162.74 | 150.67 | 93.28 | 80.83 | 61.01 | 04h30 | 2.0343 | 1.8834 | 1.166 | 1.0104 | 0.76262
05h30 | 162.74 | 155.5 | 96.54 | 83.65 | 63.66 | 05h30 | 2.0343 | 1.9438 | 1.2067 | 1.0456 | 0.79575
06h30 | 188.81 | 176.15 | 109.6 | 95.69 | 75.84 | 06h30 | 2.3601 | 2.2019 | 1.37 | 1.1961 | 0.948
07h30 | 188.81 | 180.8 | 143.32 | 125.87 | 107.27 | 07h30 | 2.3601 | 2.26 | 1.7915 | 1.5734 | 1.3409
08h30 | 200 | 200 | 138.41 | 119.94 | 100.43 | 08h30 | 2.5 | 2.5 | 1.7301 | 1.4992 | 1.2554
09h30 | 200 | 200 | 129.32 | 113.35 | 92.25 | 09h30 | 2.5 | 2.5 | 1.6165 | 1.4169 | 1.1531
10h30 | 200 | 200 | 123.3 | 109.36 | 88.23 | 10h30 | 2.5 | 2.5 | 1.5413 | 1.367 | 1.1029
11h30 | 200 | 200 | 125.54 | 113.53 | 90.56 | 11h30 | 2.5 | 2.5 | 1.5693 | 1.4191 | 1.132
12h30 | 200 | 200 | 138.7 | 127.4 | 102.53 | 12h30 | 2.5 | 2.5 | 1.7337 | 1.5925 | 1.2816
13h30 | 200 | 200 | 146.04 | 141.55 | 115.67 | 13h30 | 2.5 | 2.5 | 1.8255 | 1.7694 | 1.4459
14h30 | 200 | 200 | 145.88 | 137.01 | 111.27 | 14h30 | 2.5 | 2.5 | 1.8235 | 1.7126 | 1.3909
15h30 | 200 | 200 | 127.33 | 117.14 | 93.83 | 15h30 | 2.5 | 2.5 | 1.5916 | 1.4643 | 1.1729
16h30 | 200 | 196.2 | 116.72 | 105.93 | 84.99 | 16h30 | 2.5 | 2.4525 | 1.459 | 1.3241 | 1.0624
17h30 | 200 | 196.2 | 119.57 | 108.36 | 88.72 | 17h30 | 2.5 | 2.4525 | 1.4946 | 1.3545 | 1.109
18h30 | 200 | 193.54 | 117.42 | 105.5 | 88.21 | 18h30 | 2.5 | 2.4192 | 1.4678 | 1.3188 | 1.1026
19h30 | 197.06 | 185.12 | 112.55 | 99.74 | 84.34 | 19h30 | 2.4632 | 2.314 | 1.4069 | 1.2468 | 1.0542
20h30 | 197.06 | 191.58 | 118.01 | 104.54 | 89.17 | 20h30 | 2.4632 | 2.3948 | 1.4751 | 1.3068 | 1.1146
21h30 | 200 | 196.88 | 120.88 | 106.9 | 91.52 | 21h30 | 2.5 | 2.461 | 1.511 | 1.3362 | 1.144
22h30 | 200 | 189.86 | 116.84 | 102.38 | 87.51 | 22h30 | 2.5 | 2.3733 | 1.4605 | 1.2797 | 1.0939
23h30 | 200 | 192.98 | 120.16 | 105.71 | 90.41 | 23h30 | 2.5 | 2.4122 | 1.502 | 1.3214 | 1.1301
00h30 | 184.87 | 173.08 | 101.64 | 88.87 | 75.38 | 00h30 | 2.3109 | 2.1635 | 1.2705 | 1.1109 | 0.94225
01h30 | 166.43 | 153.84 | 93.66 | 80.99 | 67.95 | 01h30 | 2.0804 | 1.923 | 1.1707 | 1.0124 | 0.84937
02h30 | 143.58 | 130.37 | 80.32 | 70.96 | 64.11 | 02h30 | 1.7948 | 1.6296 | 1.004 | 0.887 | 0.80137
03h30 | 129.95 | 115.61 | 71.73 | 58.35 | 47.21 | 03h30 | 1.6244 | 1.4451 | 0.89663 | 0.72937 | 0.59013
04h30 | 136.3 | 120.91 | 75.51 | 61.96 | 51.1 | 04h30 | 1.7038 | 1.5114 | 0.94388 | 0.7745 | 0.63875
05h30 | 145.2 | 128.88 | 80.83 | 66.72 | 54.75 | 05h30 | 1.815 | 1.611 | 1.0104 | 0.834 | 0.68437
06h30 | 151.46 | 134.32 | 84.66 | 70.08 | 58.18 | 06h30 | 1.8933 | 1.679 | 1.0582 | 0.876 | 0.72725
07h30 | 174.63 | 160.35 | 106.78 | 90.81 | 79.3 | 07h30 | 2.1829 | 2.0044 | 1.3348 | 1.1351 | 0.99125
08h30 | 172.51 | 153.45 | 96.64 | 83.84 | 71.97 | 08h30 | 2.1564 | 1.9181 | 1.208 | 1.048 | 0.89963
09h30 | 160.72 | 141.75 | 87.13 | 71.97 | 58.88 | 09h30 | 2.009 | 1.7719 | 1.0891 | 0.89963 | 0.736
10h30 | 165.81 | 147.59 | 88.76 | 75.74 | 60.63 | 10h30 | 2.0726 | 1.8449 | 1.1095 | 0.94675 | 0.75787
11h30 | 174.67 | 156.9 | 93.81 | 81.83 | 64.67 | 11h30 | 2.1834 | 1.9612 | 1.1726 | 1.0229 | 0.80837
12h30 | 160.87 | 143.25 | 92.05 | 78.07 | 62.92 | 12h30 | 2.0109 | 1.7906 | 1.1506 | 0.97588 | 0.7865
13h30 | 157.06 | 140.23 | 83.35 | 73.32 | 57.22 | 13h30 | 1.9632 | 1.7529 | 1.0419 | 0.9165 | 0.71525
14h30 | 162.56 | 147.49 | 86.53 | 77.09 | 60.26 | 14h30 | 2.032 | 1.8436 | 1.0816 | 0.96362 | 0.75325
15h30 | 163.25 | 150.65 | 87.76 | 76.87 | 60.32 | 15h30 | 2.0406 | 1.8831 | 1.097 | 0.96088 | 0.754
16h30 | 157.81 | 146.3 | 85.75 | 73.39 | 57.96 | 16h30 | 1.9726 | 1.8288 | 1.0719 | 0.91738 | 0.7245
17h30 | 153.5 | 140.45 | 83.37 | 72.02 | 57.03 | 17h30 | 1.9187 | 1.7556 | 1.0421 | 0.90025 | 0.71288
18h30 | 164.76 | 150.74 | 90.72 | 79.94 | 65.39 | 18h30 | 2.0595 | 1.8842 | 1.134 | 0.99925 | 0.81737
19h30 | 169.73 | 156.21 | 95.17 | 82.89 | 68.88 | 19h30 | 2.1216 | 1.9526 | 1.1896 | 1.0361 | 0.861
20h30 | 161.96 | 148.65 | 91.48 | 77.96 | 64.79 | 20h30 | 2.0245 | 1.8581 | 1.1435 | 0.9745 | 0.80988
21h30 | 147.52 | 134.15 | 83.19 | 69.08 | 57.22 | 21h30 | 1.844 | 1.6769 | 1.0399 | 0.8635 | 0.71525
22h30 | 155.39 | 141.73 | 87.88 | 73.65 | 61.46 | 22h30 | 1.9424 | 1.7716 | 1.0985 | 0.92063 | 0.76825
23h30 | 171.47 | 157.39 | 97.36 | 83.13 | 69.92 | 23h30 | 2.1434 | 1.9674 | 1.217 | 1.0391 | 0.874
00h30 | 149.79 | 136.51 | 87.85 | 75.29 | 60.72 | 00h30 | 1.8724 | 1.7064 | 1.0981 | 0.94112 | 0.759
01h30 | 151.3 | 138 | 85.33 | 72.63 | 57.87 | 01h30 | 1.8913 | 1.725 | 1.0666 | 0.90787 | 0.72337
02h30 | 158.66 | 146.74 | 89.84 | 76.02 | 60.08 | 02h30 | 1.9832 | 1.8342 | 1.123 | 0.95025 | 0.751
03h30 | 160.9 | 146.74 | 92.98 | 79.41 | 63.71 | 03h30 | 2.0112 | 1.8342 | 1.1623 | 0.99262 | 0.79638
04h30 | 160.49 | 146.13 | 90.17 | 77.32 | 62.24 | 04h30 | 2.0061 | 1.8266 | 1.1271 | 0.9665 | 0.778
05h30 | 149.66 | 133.9 | 82.55 | 70.21 | 55.93 | 05h30 | 1.8707 | 1.6738 | 1.0319 | 0.87762 | 0.69912
06h30 | 151.23 | 134.66 | 82.89 | 70.77 | 56.62 | 06h30 | 1.8904 | 1.6832 | 1.0361 | 0.88462 | 0.70775
07h30 | 162.06 | 146.89 | 102.04 | 91.91 | 77.92 | 07h30 | 2.0257 | 1.8361 | 1.2755 | 1.1489 | 0.974
08h30 | 180.2 | 162.43 | 100.35 | 90.06 | 76.49 | 08h30 | 2.2525 | 2.0304 | 1.2544 | 1.1258 | 0.95613
09h30 | 180.2 | 162.43 | 100.35 | 91.49 | 74.9 | 09h30 | 2.2525 | 2.0304 | 1.2544 | 1.1436 | 0.93625
10h30 | 181.42 | 164.97 | 100 | 91.49 | 74.9 | 10h30 | 2.2677 | 2.0621 | 1.25 | 1.1436 | 0.93625
11h30 | 175.11 | 159.02 | 93.38 | 83.7 | 65.56 | 11h30 | 2.1889 | 1.9877 | 1.1672 | 1.0462 | 0.8195
12h30 | 168.36 | 152.51 | 93.38 | 83.7 | 65.56 | 12h30 | 2.1045 | 1.9064 | 1.1672 | 1.0462 | 0.8195
13h30 | 154.59 | 139.58 | 82.06 | 72.08 | 54.58 | 13h30 | 1.9324 | 1.7448 | 1.0257 | 0.901 | 0.68225
14h30 | 145.97 | 132.21 | 82.06 | 72.08 | 54.58 | 14h30 | 1.8246 | 1.6526 | 1.0257 | 0.901 | 0.68225
15h30 | 137.96 | 125.45 | 73.26 | 63.57 | 47.29 | 15h30 | 1.7245 | 1.5681 | 0.91575 | 0.79463 | 0.59113
16h30 | 125.94 | 114.3 | 73.26 | 63.57 | 47.29 | 16h30 | 1.5742 | 1.4287 | 0.91575 | 0.79463 | 0.59113
17h30 | 116.63 | 104.52 | 60.9 | 51.43 | 38.39 | 17h30 | 1.4579 | 1.3065 | 0.76125 | 0.64287 | 0.47987
18h30 | 115.49 | 102.89 | 61.53 | 51.43 | 39.47 | 18h30 | 1.4436 | 1.2861 | 0.76912 | 0.64287 | 0.49338
19h30 | 127.77 | 115.43 | 69.05 | 58.9 | 46.72 | 19h30 | 1.5971 | 1.4429 | 0.86313 | 0.73625 | 0.584
20h30 | 136.61 | 124.39 | 74.89 | 64.42 | 52.05 | 20h30 | 1.7076 | 1.5549 | 0.93612 | 0.80525 | 0.65063
21h30 | 131.08 | 118.79 | 72.01 | 60.94 | 49.5 | 21h30 | 1.6385 | 1.4849 | 0.90012 | 0.76175 | 0.61875
22h30 | 122.1 | 109.58 | 67.03 | 55.42 | 44.78 | 22h30 | 1.5263 | 1.3698 | 0.83788 | 0.69275 | 0.55975
23h30 | 123.42 | 110.56 | 68.23 | 55.36 | 45.27 | 23h30 | 1.5428 | 1.382 | 0.85288 | 0.692 | 0.56588
00h30 | 110.98 | 98.99 | 66.74 | 55.36 | 43.57 | 00h30 | 1.3873 | 1.2374 | 0.83425 | 0.692 | 0.54463
01h30 | 115.79 | 105.66 | 63.36 | 51.42 | 39.21 | 01h30 | 1.4474 | 1.3208 | 0.792 | 0.64275 | 0.49012
02h30 | 116.38 | 106.19 | 64.26 | 51.42 | 39.21 | 02h30 | 1.4547 | 1.3274 | 0.80325 | 0.64275 | 0.49012
03h30 | 118.63 | 106.76 | 65.15 | 51.13 | 39.56 | 03h30 | 1.4829 | 1.3345 | 0.81437 | 0.63913 | 0.4945
04h30 | 124.36 | 111.08 | 68.19 | 54.89 | 42.95 | 04h30 | 1.5545 | 1.3885 | 0.85237 | 0.68612 | 0.53687
05h30 | 135.74 | 121.4 | 74.51 | 61.87 | 49.06 | 05h30 | 1.6967 | 1.5175 | 0.93137 | 0.77338 | 0.61325
06h30 | 146.75 | 131.48 | 80.8 | 68.3 | 54.81 | 06h30 | 1.8344 | 1.6435 | 1.01 | 0.85375 | 0.68512
07h30 | 157.63 | 141.41 | 100.72 | 88.46 | 75.35 | 07h30 | 1.9704 | 1.7676 | 1.259 | 1.1058 | 0.94188
08h30 | 162.87 | 144.58 | 91.57 | 78.28 | 66.22 | 08h30 | 2.0359 | 1.8073 | 1.1446 | 0.9785 | 0.82775
09h30 | 144.95 | 126.65 | 77.52 | 64.33 | 51.87 | 09h30 | 1.8119 | 1.5831 | 0.969 | 0.80412 | 0.64838
10h30 | 122.36 | 105.46 | 76.45 | 64.33 | 51.87 | 10h30 | 1.5295 | 1.3182 | 0.95562 | 0.80412 | 0.64838
11h30 | 118.42 | 102.46 | 59.15 | 48.19 | 36.55 | 11h30 | 1.4803 | 1.2808 | 0.73938 | 0.60237 | 0.45687
12h30 | 137.5 | 121.74 | 71.56 | 60.62 | 46.6 | 12h30 | 1.7188 | 1.5217 | 0.8945 | 0.75775 | 0.5825
13h30 | 148.73 | 133.41 | 78.17 | 67.94 | 51.73 | 13h30 | 1.8591 | 1.6676 | 0.97713 | 0.84925 | 0.64663
14h30 | 144.32 | 129.76 | 76.01 | 66.14 | 50.43 | 14h30 | 1.804 | 1.622 | 0.95012 | 0.82675 | 0.63038
15h30 | 144.37 | 130.32 | 76.65 | 66.48 | 51.14 | 15h30 | 1.8046 | 1.629 | 0.95813 | 0.831 | 0.63925
16h30 | 143.78 | 129.81 | 76.96 | 66.64 | 51.85 | 16h30 | 1.7973 | 1.6226 | 0.962 | 0.833 | 0.64812
17h30 | 134.96 | 120.94 | 72.3 | 62.06 | 48.38 | 17h30 | 1.687 | 1.5117 | 0.90375 | 0.77575 | 0.60475
18h30 | 133.23 | 119.26 | 71.85 | 61.44 | 48.42 | 18h30 | 1.6654 | 1.4908 | 0.89812 | 0.768 | 0.60525
19h30 | 130.89 | 117 | 70.92 | 60.08 | 47.68 | 19h30 | 1.6361 | 1.4625 | 0.8865 | 0.751 | 0.596
20h30 | 128.62 | 114.71 | 69.88 | 58.62 | 46.82 | 20h30 | 1.6078 | 1.4339 | 0.8735 | 0.73275 | 0.58525
21h30 | 131.94 | 117.89 | 72.09 | 60.4 | 48.73 | 21h30 | 1.6493 | 1.4736 | 0.90112 | 0.755 | 0.60913
22h30 | 128.81 | 114.51 | 70.35 | 58.3 | 47.2 | 22h30 | 1.6101 | 1.4314 | 0.87938 | 0.72875 | 0.59
23h30 | 120.61 | 105.99 | 65.42 | 53.25 | 42.92 | 23h30 | 1.5076 | 1.3249 | 0.81775 | 0.66563 | 0.5365
00h30 | 90.1 | 76.51 | 58.11 | 46.64 | 35.81 | 00h30 | 1.1262 | 0.95637 | 0.72637 | 0.583 | 0.44762
01h30 | 80.9 | 69.39 | 40.11 | 30.51 | 20.68 | 01h30 | 1.0112 | 0.86738 | 0.50138 | 0.38138 | 0.2585
02h30 | 73.89 | 67.69 | 40.11 | 30.51 | 20.68 | 02h30 | 0.92363 | 0.84613 | 0.50138 | 0.38138 | 0.2585
03h30 | 72.23 | 58.35 | 35.17 | 23.86 | 15.42 | 03h30 | 0.90287 | 0.72937 | 0.43962 | 0.29825 | 0.19275
04h30 | 70.18 | 58.35 | 35.17 | 23.86 | 15.42 | 04h30 | 0.87725 | 0.72937 | 0.43962 | 0.29825 | 0.19275
05h30 | 70.73 | 55.06 | 33.9 | 23.33 | 15.58 | 05h30 | 0.88413 | 0.68825 | 0.42375 | 0.29163 | 0.19475
06h30 | 83.32 | 67.43 | 41.82 | 30.78 | 22.22 | 06h30 | 1.0415 | 0.84288 | 0.52275 | 0.38475 | 0.27775
07h30 | 105.73 | 86.94 | 58.66 | 47.88 | 39.67 | 07h30 | 1.3216 | 1.0868 | 0.73325 | 0.5985 | 0.49588
08h30 | 88.12 | 74.58 | 50.74 | 40.42 | 33.04 | 08h30 | 1.1015 | 0.93225 | 0.63425 | 0.50525 | 0.413
09h30 | 84.91 | 66.04 | 41.4 | 27.08 | 19.2 | 09h30 | 1.0614 | 0.8255 | 0.5175 | 0.3385 | 0.24
10h30 | 104.55 | 86.98 | 52.54 | 40.72 | 31.42 | 10h30 | 1.3069 | 1.0873 | 0.65675 | 0.509 | 0.39275
11h30 | 119.21 | 102.21 | 60.2 | 49.91 | 38.15 | 11h30 | 1.4901 | 1.2776 | 0.7525 | 0.62387 | 0.47687
12h30 | 121.11 | 104.84 | 61.6 | 51.26 | 38.16 | 12h30 | 1.5139 | 1.3105 | 0.77 | 0.64075 | 0.477
13h30 | 116.77 | 101.47 | 59.41 | 48.85 | 36.07 | 13h30 | 1.4596 | 1.2684 | 0.74262 | 0.61062 | 0.45088
14h30 | 100.67 | 87.62 | 50.3 | 39.59 | 27.59 | 14h30 | 1.2584 | 1.0953 | 0.62875 | 0.49488 | 0.34487
15h30 | 79.72 | 68.8 | 38 | 26.53 | 15.83 | 15h30 | 0.9965 | 0.86 | 0.475 | 0.33163 | 0.19787
16h30 | 71.61 | 60.71 | 34.57 | 20.96 | 12.09 | 16h30 | 0.89512 | 0.75887 | 0.43212 | 0.262 | 0.15113
17h30 | 73.98 | 63.14 | 36.73 | 23.94 | 15.16 | 17h30 | 0.92475 | 0.78925 | 0.45913 | 0.29925 | 0.1895
18h30 | 73.98 | 61.5 | 36.73 | 23.78 | 15.48 | 18h30 | 0.92475 | 0.76875 | 0.45913 | 0.29725 | 0.1935
19h30 | 41.31 | 28.39 | 17.86 | 6.08 | 1.21 | 19h30 | 0.51638 | 0.35487 | 0.22325 | 0.076 | 0.015125
20h30 | 41.31 | 28.39 | 17.86 | 6.08 | 0.89 | 20h30 | 0.51638 | 0.35487 | 0.22325 | 0.076 | 0.011125
21h30 | 22.71 | 7.11 | 6.53 | 0 | 0 | 21h30 | 0.28387 | 0.088875 | 0.081625 | 0 | 0
22h30 | 29.97 | 17.23 | 11.93 | 0 | 0 | 22h30 | 0.37462 | 0.21538 | 0.14913 | 0 | 0
23h30 | 20.02 | 10.12 | 5.85 | 0 | 0 | 23h30 | 0.25025 | 0.1265 | 0.073125 | 0 | 0
00h30 | 12.76 | 0 | 0.45 | 0 | 0 | 00h30 | 0.1595 | 0 | 0.005625 | 0 | 0
01h30 | 28.38 | 17.51 | 9.81 | 0 | 0 | 01h30 | 0.35475 | 0.21887 | 0.12262 | 0 | 0
02h30 | 39.53 | 29.16 | 18.28 | 4.06 | 0 | 02h30 | 0.49412 | 0.3645 | 0.2285 | 0.05075 | 0
03h30 | 40.8 | 29.12 | 18.24 | 5.11 | 0 | 03h30 | 0.51 | 0.364 | 0.228 | 0.063875 | 0
04h30 | 43.07 | 29.97 | 19.11 | 5.99 | 0 | 04h30 | 0.53838 | 0.37462 | 0.23888 | 0.074875 | 0
05h30 | 48.11 | 33.54 | 21.34 | 9.28 | 2.94 | 05h30 | 0.60137 | 0.41925 | 0.26675 | 0.116 | 0.03675
06h30 | 51.47 | 35.59 | 22.78 | 11.15 | 4.88 | 06h30 | 0.64338 | 0.44488 | 0.28475 | 0.13937 | 0.061
07h30 | 74.91 | 55.37 | 39.78 | 29.25 | 23.24 | 07h30 | 0.93637 | 0.69212 | 0.49725 | 0.36562 | 0.2905
08h30 | 80.59 | 58.83 | 38.54 | 26.74 | 21.3 | 08h30 | 1.0074 | 0.73538 | 0.48175 | 0.33425 | 0.26625
09h30 | 86.06 | 65.6 | 42.25 | 28.62 | 21.07 | 09h30 | 1.0757 | 0.82 | 0.52812 | 0.35775 | 0.26338
10h30 | 77.3 | 57.55 | 35.86 | 24.33 | 21.07 | 10h30 | 0.96625 | 0.71937 | 0.44825 | 0.30412 | 0.26338
11h30 | 71.33 | 52.21 | 31.39 | 20.62 | 12.84 | 11h30 | 0.89163 | 0.65263 | 0.39237 | 0.25775 | 0.1605
12h30 | 73.94 | 55.52 | 32.5 | 23.05 | 15.06 | 12h30 | 0.92425 | 0.694 | 0.40625 | 0.28813 | 0.18825
13h30 | 73.06 | 55.43 | 31.84 | 23 | 13.71 | 13h30 | 0.91325 | 0.69288 | 0.398 | 0.2875 | 0.17137
14h30 | 75.54 | 58.68 | 33.42 | 24.86 | 14.81 | 14h30 | 0.94425 | 0.7335 | 0.41775 | 0.31075 | 0.18513
15h30 | 75.97 | 60.46 | 33.84 | 25.48 | 14.98 | 15h30 | 0.94963 | 0.75575 | 0.423 | 0.3185 | 0.18725
16h30 | 68.55 | 54.62 | 30.04 | 21.2 | 11.65 | 16h30 | 0.85688 | 0.68275 | 0.3755 | 0.265 | 0.14563
17h30 | 72.97 | 58.69 | 33.71 | 23.36 | 14.11 | 17h30 | 0.91212 | 0.73362 | 0.42137 | 0.292 | 0.17638
18h30 | 91.77 | 76.46 | 45.82 | 35.4 | 25.52 | 18h30 | 1.1471 | 0.95575 | 0.57275 | 0.4425 | 0.319
19h30 | 106.94 | 91.75 | 55.76 | 45.33 | 34.95 | 19h30 | 1.3368 | 1.1469 | 0.697 | 0.56663 | 0.43688
20h30 | 101.07 | 86.22 | 53.04 | 41.75 | 32.42 | 20h30 | 1.2634 | 1.0777 | 0.663 | 0.52187 | 0.40525
21h30 | 86.01 | 71.32 | 44.63 | 32.52 | 24.79 | 21h30 | 1.0751 | 0.8915 | 0.55788 | 0.4065 | 0.30988
22h30 | 79.3 | 64.57 | 41.04 | 28.25 | 21.54 | 22h30 | 0.99125 | 0.80712 | 0.513 | 0.35313 | 0.26925
23h30 | 86.41 | 71.5 | 45.6 | 32.26 | 25.2 | 23h30 | 1.0801 | 0.89375 | 0.57 | 0.40325 | 0.315
00h30 | 87.84 | 74.11 | 41.86 | 30.25 | 21.46 | 00h30 | 1.098 | 0.92637 | 0.52325 | 0.37812 | 0.26825
01h30 | 109.76 | 98.19 | 60.06 | 47.56 | 36.58 | 01h30 | 1.372 | 1.2274 | 0.75075 | 0.5945 | 0.45725
02h30 | 124.7 | 113.02 | 69.78 | 54.86 | 42.59 | 02h30 | 1.5588 | 1.4127 | 0.87225 | 0.68575 | 0.53238
03h30 | 133.18 | 119.74 | 74.25 | 60.08 | 47.76 | 03h30 | 1.6647 | 1.4968 | 0.92812 | 0.751 | 0.597
04h30 | 125.24 | 110.54 | 68.79 | 55.5 | 43.6 | 04h30 | 1.5655 | 1.3818 | 0.85987 | 0.69375 | 0.545
05h30 | 114.48 | 98.91 | 61.66 | 49.23 | 37.73 | 05h30 | 1.431 | 1.2364 | 0.77075 | 0.61538 | 0.47163
06h30 | 112.07 | 95.74 | 59.68 | 47.7 | 36.07 | 06h30 | 1.4009 | 1.1967 | 0.746 | 0.59625 | 0.45088
07h30 | 123.6 | 116.72 | 77.38 | 65.62 | 54.18 | 07h30 | 1.545 | 1.459 | 0.96725 | 0.82025 | 0.67725
08h30 | 129.57 | 111.29 | 71 | 62.24 | 52.1 | 08h30 | 1.6196 | 1.3911 | 0.8875 | 0.778 | 0.65125
09h30 | 121.96 | 102.5 | 64.77 | 50.71 | 37.8 | 09h30 | 1.5245 | 1.2812 | 0.80963 | 0.63387 | 0.4725
10h30 | 125.64 | 106.17 | 65.22 | 52.67 | 39.01 | 10h30 | 1.5705 | 1.3271 | 0.81525 | 0.65838 | 0.48762
11h30 | 131.92 | 113.53 | 68.63 | 56.77 | 42.41 | 11h30 | 1.649 | 1.4191 | 0.85788 | 0.70962 | 0.53012
12h30 | 130.13 | 112.65 | 68.18 | 56.63 | 41.8 | 12h30 | 1.6266 | 1.4081 | 0.85225 | 0.70788 | 0.5225
13h30 | 116.12 | 99.8 | 58.82 | 49.4 | 34.74 | 13h30 | 1.4515 | 1.2475 | 0.73525 | 0.6175 | 0.43425
14h30 | 97.57 | 82.92 | 58.82 | 47.58 | 34.15 | 14h30 | 1.2196 | 1.0365 | 0.73525 | 0.59475 | 0.42688
15h30 | 89.02 | 75.79 | 42.01 | 34.86 | 21.56 | 15h30 | 1.1127 | 0.94737 | 0.52512 | 0.43575 | 0.2695
16h30 | 93.99 | 80.61 | 46.11 | 38.2 | 24.59 | 16h30 | 1.1749 | 1.0076 | 0.57637 | 0.4775 | 0.30738
17h30 | 109.28 | 95.44 | 56.24 | 46.57 | 33.25 | 17h30 | 1.366 | 1.193 | 0.703 | 0.58213 | 0.41563
18h30 | 124.13 | 110.67 | 66.84 | 55.94 | 42.59 | 18h30 | 1.5516 | 1.3834 | 0.8355 | 0.69925 | 0.53238
19h30 | 128.46 | 115.41 | 70.57 | 58.53 | 45.76 | 19h30 | 1.6058 | 1.4426 | 0.88213 | 0.73162 | 0.572
20h30 | 106.72 | 93.92 | 58.29 | 45.81 | 35.32 | 20h30 | 1.334 | 1.174 | 0.72862 | 0.57263 | 0.4415
21h30 | 87.56 | 74.85 | 47.24 | 33.71 | 25.74 | 21h30 | 1.0945 | 0.93563 | 0.5905 | 0.42137 | 0.32175
22h30 | 91.86 | 79.08 | 50.11 | 36.27 | 28.06 | 22h30 | 1.1482 | 0.9885 | 0.62638 | 0.45337 | 0.35075
23h30 | 91.02 | 78.05 | 49.68 | 35.6 | 27.43 | 23h30 | 1.1378 | 0.97562 | 0.621 | 0.445 | 0.34287
00h30 | 75.73 | 73.51 | 44.4 | 33.03 | 23.19 | 00h30 | 0.94663 | 0.91887 | 0.555 | 0.41287 | 0.28987
01h30 | 61.88 | 49.24 | 28.51 | 15.16 | 9.71 | 01h30 | 0.7735 | 0.6155 | 0.35637 | 0.1895 | 0.12137
02h30 | 61.88 | 49.24 | 28.51 | 15.16 | 9.71 | 02h30 | 0.7735 | 0.6155 | 0.35637 | 0.1895 | 0.12137
03h30 | 44.16 | 28.91 | 20.6 | 8.57 | 2.28 | 03h30 | 0.552 | 0.36138 | 0.2575 | 0.10712 | 0.0285
04h30 | 51.4 | 38.19 | 25.37 | 12.4 | 5.94 | 04h30 | 0.6425 | 0.47737 | 0.31712 | 0.155 | 0.07425
05h30 | 18.95 | 9.28 | 6.05 | 3.83 | 3.66 | 05h30 | 0.23688 | 0.116 | 0.075625 | 0.047875 | 0.04575
06h30 | 20.85 | 5.45 | 6.78 | 0 | 0 | 06h30 | 0.26062 | 0.068125 | 0.08475 | 0 | 0
07h30 | 74.35 | 57.7 | 42.44 | 25.07 | 18.24 | 07h30 | 0.92937 | 0.72125 | 0.5305 | 0.31338 | 0.228
08h30 | 103.36 | 84.81 | 54.94 | 39.75 | 31.35 | 08h30 | 1.292 | 1.0601 | 0.68675 | 0.49688 | 0.39187
09h30 | 100.07 | 82.56 | 52.47 | 37.08 | 28.48 | 09h30 | 1.2509 | 1.032 | 0.65587 | 0.4635 | 0.356
10h30 | 102.49 | 85.78 | 52.95 | 39.13 | 29.65 | 10h30 | 1.2811 | 1.0722 | 0.66187 | 0.48912 | 0.37062
11h30 | 108.27 | 92.06 | 56.24 | 42.9 | 31.96 | 11h30 | 1.3534 | 1.1507 | 0.703 | 0.53625 | 0.3995
12h30 | 109.21 | 93.39 | 56.81 | 43.8 | 32.35 | 12h30 | 1.3651 | 1.1674 | 0.71013 | 0.5475 | 0.40437
13h30 | 111.34 | 96.26 | 58.11 | 45.42 | 33.7 | 13h30 | 1.3918 | 1.2032 | 0.72637 | 0.56775 | 0.42125
14h30 | 135.02 | 120.72 | 72.72 | 59.59 | 46.06 | 14h30 | 1.6878 | 1.509 | 0.909 | 0.74487 | 0.57575
15h30 | 132 | 118 | 71.55 | 57.93 | 45.01 | 15h30 | 1.65 | 1.475 | 0.89438 | 0.72413 | 0.56263
16h30 | 109.36 | 95.33 | 58.74 | 44.84 | 34.18 | 16h30 | 1.367 | 1.1916 | 0.73425 | 0.5605 | 0.42725
17h30 | 113.3 | 99.21 | 62.01 | 47.52 | 37.14 | 17h30 | 1.4163 | 1.2401 | 0.77512 | 0.594 | 0.46425
18h30 | 70.76 | 60.3 | 41.15 | 28.83 | 20.93 | 18h30 | 0.8845 | 0.75375 | 0.51438 | 0.36038 | 0.26162
19h30 | 70.49 | 55.48 | 36.72 | 17.83 | 13.06 | 19h30 | 0.88113 | 0.6935 | 0.459 | 0.22287 | 0.16325
20h30 | 118.95 | 104.7 | 66.84 | 50.35 | 40.44 | 20h30 | 1.4869 | 1.3088 | 0.8355 | 0.62938 | 0.5055
21h30 | 132.61 | 117.9 | 74.83 | 58.23 | 47.45 | 21h30 | 1.6576 | 1.4737 | 0.93537 | 0.72788 | 0.59313
22h30 | 139.99 | 125.21 | 79.54 | 62.62 | 51.19 | 22h30 | 1.7499 | 1.5651 | 0.99425 | 0.78275 | 0.63987
23h30 | 122 | 106.87 | 68.51 | 51.87 | 41.68 | 23h30 | 1.525 | 1.3359 | 0.85637 | 0.64838 | 0.521
00h30 | 86.01 | 71.77 | 41.42 | 27.43 | 19.33 | 00h30 | 1.0751 | 0.89712 | 0.51775 | 0.34287 | 0.24163
01h30 | 80.44 | 68.03 | 42.12 | 29.11 | 20.58 | 01h30 | 1.0055 | 0.85037 | 0.5265 | 0.36388 | 0.25725
02h30 | 74.63 | 62.03 | 38.72 | 25.1 | 15.54 | 02h30 | 0.93288 | 0.77538 | 0.484 | 0.31375 | 0.19425
03h30 | 89.18 | 75.18 | 46.8 | 34.01 | 23.6 | 03h30 | 1.1147 | 0.93975 | 0.585 | 0.42512 | 0.295
04h30 | 109.38 | 94.56 | 58.74 | 46.09 | 34.12 | 04h30 | 1.3673 | 1.182 | 0.73425 | 0.57612 | 0.4265
05h30 | 118.04 | 102.52 | 63.88 | 51.13 | 38.85 | 05h30 | 1.4755 | 1.2815 | 0.7985 | 0.63913 | 0.48562
06h30 | 129.74 | 113.61 | 70.95 | 57.95 | 45.08 | 06h30 | 1.6218 | 1.4201 | 0.88687 | 0.72437 | 0.5635
07h30 | 145.93 | 135.88 | 89.42 | 76.12 | 63.86 | 07h30 | 1.8241 | 1.6985 | 1.1178 | 0.9515 | 0.79825
08h30 | 137.82 | 120.13 | 76.07 | 61.47 | 50.33 | 08h30 | 1.7228 | 1.5016 | 0.95088 | 0.76838 | 0.62913
09h30 | 137.82 | 120.69 | 75.8 | 60.51 | 48.47 | 09h30 | 1.7228 | 1.5086 | 0.9475 | 0.75638 | 0.60588
10h30 | 157.56 | 139.87 | 86.01 | 71.88 | 58.06 | 10h30 | 1.9695 | 1.7484 | 1.0751 | 0.8985 | 0.72575
11h30 | 156.89 | 140.04 | 84.9 | 72.1 | 57.51 | 11h30 | 1.9611 | 1.7505 | 1.0613 | 0.90125 | 0.71888
12h30 | 134.97 | 118.86 | 71.73 | 59.5 | 45.77 | 12h30 | 1.6871 | 1.4857 | 0.89663 | 0.74375 | 0.57212
13h30 | 118.49 | 103.09 | 62.05 | 50.16 | 37.16 | 13h30 | 1.4811 | 1.2886 | 0.77563 | 0.627 | 0.4645
14h30 | 100 | 85.39 | 55.03 | 39.63 | 32.38 | 14h30 | 1.25 | 1.0674 | 0.68788 | 0.49538 | 0.40475
15h30 | 49.79 | 35.78 | 21.42 | 9.8 | 2.97 | 15h30 | 0.62238 | 0.44725 | 0.26775 | 0.1225 | 0.037125
16h30 | 32.63 | 25.32 | 21.42 | 8.84 | 2.97 | 16h30 | 0.40787 | 0.3165 | 0.26775 | 0.1105 | 0.037125
17h30 | 50.21 | 31.68 | 18.94 | 3.36 | 0 | 17h30 | 0.62762 | 0.396 | 0.23675 | 0.042 | 0
18h30 | 99.29 | 85.6 | 53.87 | 39.68 | 30.31 | 18h30 | 1.2411 | 1.07 | 0.67337 | 0.496 | 0.37888
19h30 | 122.23 | 108.71 | 67.61 | 54.72 | 43.96 | 19h30 | 1.5279 | 1.3589 | 0.84513 | 0.684 | 0.5495
20h30 | 154.52 | 140.91 | 87.18 | 74.03 | 61.33 | 20h30 | 1.9315 | 1.7614 | 1.0897 | 0.92537 | 0.76663
21h30 | 181.37 | 173.5 | 107.05 | 93.52 | 78.78 | 21h30 | 2.2671 | 2.1688 | 1.3381 | 1.169 | 0.98475
22h30 | 200 | 187.38 | 128.09 | 114.15 | 97.14 | 22h30 | 2.5 | 2.3422 | 1.6011 | 1.4269 | 1.2143
23h30 | 200 | 200 | 137.94 | 123.77 | 105.54 | 23h30 | 2.5 | 2.5 | 1.7243 | 1.5471 | 1.3193
00h30 | 175.35 | 167.06 | 100.8 | 88.84 | 73.3 | 00h30 | 2.1919 | 2.0882 | 1.26 | 1.1105 | 0.91625
01h30 | 147.4 | 135.39 | 81.35 | 70.34 | 56.09 | 01h30 | 1.8425 | 1.6924 | 1.0169 | 0.87925 | 0.70112
02h30 | 124.61 | 111.19 | 67.25 | 55.67 | 40.98 | 02h30 | 1.5576 | 1.3899 | 0.84062 | 0.69588 | 0.51225
03h30 | 97.24 | 82.79 | 50.16 | 39.71 | 27.74 | 03h30 | 1.2155 | 1.0349 | 0.627 | 0.49638 | 0.34675
04h30 | 77.07 | 61.84 | 37.73 | 27.59 | 17.87 | 04h30 | 0.96337 | 0.773 | 0.47163 | 0.34487 | 0.22337
05h30 | 82.33 | 66.48 | 40.91 | 30.42 | 20.27 | 05h30 | 1.0291 | 0.831 | 0.51138 | 0.38025 | 0.25338
06h30 | 86.7 | 70.38 | 43.64 | 32.72 | 22.15 | 06h30 | 1.0837 | 0.87975 | 0.5455 | 0.409 | 0.27687
07h30 | 66.29 | 47.59 | 35.21 | 24.01 | 17.91 | 07h30 | 0.82862 | 0.59488 | 0.44012 | 0.30012 | 0.22387
08h30 | 29.9 | 21.77 | 20.6 | 7.17 | 7.19 | 08h30 | 0.37375 | 0.27213 | 0.2575 | 0.089625 | 0.089875
09h30 | 27.02 | 6.12 | 5.77 | 0 | 0 | 09h30 | 0.33775 | 0.0765 | 0.072125 | 0 | 0
10h30 | 26.65 | 6.12 | 5.77 | 0 | 0 | 10h30 | 0.33313 | 0.0765 | 0.072125 | 0 | 0
11h30 | 19.55 | 2.41 | 2.11 | 0 | 0 | 11h30 | 0.24438 | 0.030125 | 0.026375 | 0 | 0
12h30 | 19.55 | 2.41 | 2.11 | 0 | 0 | 12h30 | 0.24438 | 0.030125 | 0.026375 | 0 | 0
13h30 | 75.69 | 60.56 | 35.79 | 18.01 | 6.43 | 13h30 | 0.94612 | 0.757 | 0.44738 | 0.22512 | 0.080375
14h30 | 135.37 | 121.15 | 72.58 | 58.77 | 41.97 | 14h30 | 1.6921 | 1.5144 | 0.90725 | 0.73462 | 0.52463
15h30 | 73.91 | 60.59 | 36.79 | 40.75 | 35.54 | 15h30 | 0.92388 | 0.75738 | 0.45987 | 0.50938 | 0.44425
16h30 | 16.2 | 2.8 | 2.53 | 0 | 0 | 16h30 | 0.2025 | 0.035 | 0.031625 | 0 | 0
17h30 | 90.78 | 77.5 | 48.36 | 27.67 | 15.53 | 17h30 | 1.1347 | 0.96875 | 0.6045 | 0.34587 | 0.19412
18h30 | 188.81 | 174.7 | 114.04 | 97.91 | 77.92 | 18h30 | 2.3601 | 2.1837 | 1.4255 | 1.2239 | 0.974
19h30 | 200 | 200 | 137.23 | 121.01 | 98.82 | 19h30 | 2.5 | 2.5 | 1.7154 | 1.5126 | 1.2352
20h30 | 200 | 200 | 150.41 | 134.1 | 111.27 | 20h30 | 2.5 | 2.5 | 1.8801 | 1.6763 | 1.3909
21h30 | 200 | 200 | 159.95 | 142.94 | 120.34 | 21h30 | 2.5 | 2.5 | 1.9994 | 1.7868 | 1.5043
22h30 | 200 | 200 | 158.47 | 140.61 | 118.93 | 22h30 | 2.5 | 2.5 | 1.9809 | 1.7576 | 1.4866
23h30 | 200 | 200 | 154.43 | 136.05 | 115.37 | 23h30 | 2.5 | 2.5 | 1.9304 | 1.7006 | 1.4421
00h30 | 200 | 199.68 | 125.05 | 108.79 | 89.38 | 00h30 | 2.5 | 2.496 | 1.5631 | 1.3599 | 1.1173
01h30 | 186 | 175.38 | 106.6 | 91.47 | 72.93 | 01h30 | 2.325 | 2.1923 | 1.3325 | 1.1434 | 0.91163
02h30 | 186 | 175.71 | 111.77 | 95.82 | 75.36 | 02h30 | 2.325 | 2.1964 | 1.3971 | 1.1978 | 0.942
03h30 | 200 | 200 | 123.84 | 108.94 | 86.65 | 03h30 | 2.5 | 2.5 | 1.548 | 1.3618 | 1.0831
04h30 | 196.34 | 185.31 | 112.9 | 99.04 | 78.18 | 04h30 | 2.4543 | 2.3164 | 1.4112 | 1.238 | 0.97725
05h30 | 196.34 | 185.31 | 113.79 | 100.04 | 80.03 | 05h30 | 2.4543 | 2.3164 | 1.4224 | 1.2505 | 1.0004
06h30 | 199.35 | 183.6 | 112.67 | 98.23 | 79.67 | 06h30 | 2.4919 | 2.295 | 1.4084 | 1.2279 | 0.99587
07h30 | 199.35 | 182.71 | 115.88 | 101.56 | 85.42 | 07h30 | 2.4919 | 2.2839 | 1.4485 | 1.2695 | 1.0677
08h30 | 186 | 167.98 | 100.65 | 87.17 | 72.63 | 08h30 | 2.325 | 2.0997 | 1.2581 | 1.0896 | 0.90787
09h30 | 186 | 168.87 | 106.15 | 92.84 | 75.01 | 09h30 | 2.325 | 2.1109 | 1.3269 | 1.1605 | 0.93763
10h30 | 200 | 186.24 | 110.91 | 97.46 | 75.64 | 10h30 | 2.5 | 2.328 | 1.3864 | 1.2183 | 0.9455
11h30 | 193.25 | 179.68 | 104.99 | 91.7 | 70.16 | 11h30 | 2.4156 | 2.246 | 1.3124 | 1.1462 | 0.877
12h30 | 192.6 | 178.83 | 105.24 | 92.05 | 70.35 | 12h30 | 2.4075 | 2.2354 | 1.3155 | 1.1506 | 0.87938
13h30 | 196.88 | 184.29 | 108.56 | 95.29 | 72.59 | 13h30 | 2.461 | 2.3036 | 1.357 | 1.1911 | 0.90738
14h30 | 197.52 | 197.56 | 115.77 | 101.84 | 79.75 | 14h30 | 2.469 | 2.4695 | 1.4471 | 1.273 | 0.99687
15h30 | 178.52 | 173.19 | 99.97 | 86.05 | 67.21 | 15h30 | 2.2315 | 2.1649 | 1.2496 | 1.0756 | 0.84013
16h30 | 143.81 | 135.24 | 76.96 | 63.83 | 47.57 | 16h30 | 1.7976 | 1.6905 | 0.962 | 0.79788 | 0.59462
17h30 | 165.29 | 160.71 | 95.88 | 82 | 64.48 | 17h30 | 2.0661 | 2.0089 | 1.1985 | 1.025 | 0.806
18h30 | 200 | 200 | 121.22 | 106.76 | 87.29 | 18h30 | 2.5 | 2.5 | 1.5152 | 1.3345 | 1.0911
19h30 | 200 | 200 | 121.08 | 107.48 | 88.49 | 19h30 | 2.5 | 2.5 | 1.5135 | 1.3435 | 1.1061
20h30 | 190.22 | 181.68 | 109.78 | 96.38 | 79.52 | 20h30 | 2.3777 | 2.271 | 1.3722 | 1.2047 | 0.994
21h30 | 174.26 | 163.2 | 99.07 | 85.13 | 70.61 | 21h30 | 2.1782 | 2.04 | 1.2384 | 1.0641 | 0.88262
22h30 | 162.66 | 151.28 | 92.27 | 78.17 | 64.7 | 22h30 | 2.0332 | 1.891 | 1.1534 | 0.97713 | 0.80875
23h30 | 176.02 | 163.68 | 99.93 | 85.82 | 71.32 | 23h30 | 2.2003 | 2.046 | 1.2491 | 1.0728 | 0.8915
00h30 | 164.53 | 152.55 | 88.01 | 75.25 | 59.01 | 00h30 | 2.0566 | 1.9069 | 1.1001 | 0.94063 | 0.73762
01h30 | 147.83 | 137.73 | 82.64 | 68.68 | 53.38 | 01h30 | 1.8479 | 1.7216 | 1.033 | 0.8585 | 0.66725
02h30 | 136.59 | 126.38 | 76.29 | 60.29 | 46.9 | 02h30 | 1.7074 | 1.5797 | 0.95362 | 0.75362 | 0.58625
03h30 | 150.09 | 138.41 | 84.03 | 68.94 | 55.39 | 03h30 | 1.8761 | 1.7301 | 1.0504 | 0.86175 | 0.69237
04h30 | 164.32 | 151.2 | 92.16 | 77.71 | 63.56 | 04h30 | 2.054 | 1.89 | 1.152 | 0.97137 | 0.7945
05h30 | 170.12 | 156.77 | 95.79 | 81.9 | 67.65 | 05h30 | 2.1265 | 1.9596 | 1.1974 | 1.0237 | 0.84562
06h30 | 179.66 | 164.49 | 100.63 | 86.96 | 72.46 | 06h30 | 2.2458 | 2.0561 | 1.2579 | 1.087 | 0.90575
07h30 | 179.66 | 167.79 | 119.57 | 109.71 | 94.72 | 07h30 | 2.2458 | 2.0974 | 1.4946 | 1.3714 | 1.184
08h30 | 200 | 197.36 | 123.74 | 110.25 | 94.64 | 08h30 | 2.5 | 2.467 | 1.5468 | 1.3781 | 1.183
09h30 | 200 | 197.36 | 123.74 | 110.84 | 93.76 | 09h30 | 2.5 | 2.467 | 1.5468 | 1.3855 | 1.172
10h30 | 200 | 200 | 121.81 | 109.33 | 90.59 | 10h30 | 2.5 | 2.5 | 1.5226 | 1.3666 | 1.1324
11h30 | 200 | 200 | 121.81 | 110.36 | 90.63 | 11h30 | 2.5 | 2.5 | 1.5226 | 1.3795 | 1.1329
12h30 | 200 | 200 | 124.32 | 111.27 | 91.15 | 12h30 | 2.5 | 2.5 | 1.554 | 1.3909 | 1.1394
13h30 | 200 | 200 | 123.46 | 110.32 | 89.95 | 13h30 | 2.5 | 2.5 | 1.5433 | 1.379 | 1.1244
14h30 | 200 | 200 | 121.85 | 108.92 | 88.35 | 14h30 | 2.5 | 2.5 | 1.5231 | 1.3615 | 1.1044
15h30 | 200 | 200 | 122.7 | 113.07 | 91.67 | 15h30 | 2.5 | 2.5 | 1.5337 | 1.4134 | 1.1459
16h30 | 200 | 200 | 137.79 | 125.34 | 102.76 | 16h30 | 2.5 | 2.5 | 1.7224 | 1.5668 | 1.2845
17h30 | 200 | 200 | 137.79 | 132.57 | 110.39 | 17h30 | 2.5 | 2.5 | 1.7224 | 1.6571 | 1.3799
18h30 | 200 | 200 | 139.66 | 127.88 | 107.76 | 18h30 | 2.5 | 2.5 | 1.7457 | 1.5985 | 1.347
19h30 | 200 | 200 | 128.55 | 116.4 | 98.68 | 19h30 | 2.5 | 2.5 | 1.6069 | 1.455 | 1.2335
20h30 | 200 | 200 | 128.37 | 115.62 | 98.46 | 20h30 | 2.5 | 2.5 | 1.6046 | 1.4452 | 1.2308
21h30 | 200 | 200 | 139.48 | 126.98 | 108.93 | 21h30 | 2.5 | 2.5 | 1.7435 | 1.5873 | 1.3616
22h30 | 200 | 200 | 150.76 | 136.56 | 117.87 | 22h30 | 2.5 | 2.5 | 1.8845 | 1.707 | 1.4734
23h30 | 200 | 200 | 150.76 | 137.8 | 127.12 | 23h30 | 2.5 | 2.5 | 1.8845 | 1.7225 | 1.589
00h30 | 200 | 200 | 134.55 | 120.02 | 102.68 | 00h30 | 2.5 | 2.5 | 1.6819 | 1.5003 | 1.2835
01h30 | 200 | 199.84 | 122.27 | 106.78 | 89.79 | 01h30 | 2.5 | 2.498 | 1.5284 | 1.3348 | 1.1224
02h30 | 191.65 | 178.2 | 106.63 | 91.56 | 82.63 | 02h30 | 2.3956 | 2.2275 | 1.3329 | 1.1445 | 1.0329
03h30 | 169.15 | 149.8 | 90.38 | 75.97 | 63.05 | 03h30 | 2.1144 | 1.8725 | 1.1298 | 0.94963 | 0.78812
04h30 | 163.5 | 142.99 | 86.43 | 72.81 | 63.05 | 04h30 | 2.0438 | 1.7874 | 1.0804 | 0.91012 | 0.78812
05h30 | 167.46 | 146.48 | 88.47 | 75.67 | 62.45 | 05h30 | 2.0932 | 1.831 | 1.1059 | 0.94588 | 0.78063
06h30 | 165.04 | 143.67 | 87.1 | 74.15 | 62.45 | 06h30 | 2.063 | 1.7959 | 1.0888 | 0.92688 | 0.78063
07h30 | 165.8 | 143.41 | 90.67 | 78.14 | 66.54 | 07h30 | 2.0725 | 1.7926 | 1.1334 | 0.97675 | 0.83175
08h30 | 131.87 | 110.59 | 77.08 | 78.03 | 66.54 | 08h30 | 1.6484 | 1.3824 | 0.9635 | 0.97537 | 0.83175
09h30 | 120.5 | 103.25 | 55.41 | 41.02 | 32.42 | 09h30 | 1.5063 | 1.2906 | 0.69263 | 0.51275 | 0.40525
10h30 | 135.58 | 120.08 | 65.43 | 52.18 | 39.43 | 10h30 | 1.6947 | 1.501 | 0.81788 | 0.65225 | 0.49288
11h30 | 153.32 | 137.68 | 76.51 | 63.62 | 47.82 | 11h30 | 1.9165 | 1.721 | 0.95637 | 0.79525 | 0.59775
12h30 | 158.46 | 143.14 | 81.4 | 68.33 | 52.54 | 12h30 | 1.9808 | 1.7893 | 1.0175 | 0.85413 | 0.65675
13h30 | 139.51 | 125.12 | 71.15 | 58.18 | 43.67 | 13h30 | 1.7439 | 1.564 | 0.88938 | 0.72725 | 0.54587
14h30 | 114.43 | 101.23 | 56.51 | 44.03 | 31.93 | 14h30 | 1.4304 | 1.2654 | 0.70637 | 0.55037 | 0.39913
15h30 | 89.65 | 77.07 | 42.73 | 29.52 | 19.56 | 15h30 | 1.1206 | 0.96337 | 0.53412 | 0.369 | 0.2445
16h30 | 65.9 | 53.28 | 42.46 | 27.8 | 19.56 | 16h30 | 0.82375 | 0.666 | 0.53075 | 0.3475 | 0.2445
17h30 | 37.93 | 24.52 | 11.66 | 0.04 | 0 | 17h30 | 0.47413 | 0.3065 | 0.14575 | 0.0005 | 0
18h30 | 56.2 | 42.09 | 25.97 | 12.74 | 4.42 | 18h30 | 0.7025 | 0.52612 | 0.32462 | 0.15925 | 0.05525
19h30 | 127.43 | 113.06 | 67.94 | 54.71 | 44.27 | 19h30 | 1.5929 | 1.4132 | 0.84925 | 0.68388 | 0.55337
20h30 | 173 | 158.38 | 95.34 | 82.69 | 68.88 | 20h30 | 2.1625 | 1.9797 | 1.1918 | 1.0336 | 0.861
21h30 | 179.44 | 164.5 | 100.2 | 85.58 | 71.92 | 21h30 | 2.243 | 2.0562 | 1.2525 | 1.0697 | 0.899
22h30 | 99.36 | 91.09 | 58.48 | 44.9 | 42.89 | 22h30 | 1.242 | 1.1386 | 0.731 | 0.56125 | 0.53612
23h30 | 64.6 | 46.51 | 30.55 | 12 | 4.8 | 23h30 | 0.8075 | 0.58137 | 0.38188 | 0.15 | 0.06
00h30 | 95.98 | 81.02 | 46.01 | 31.51 | 21.51 | 00h30 | 1.1998 | 1.0128 | 0.57512 | 0.39387 | 0.26887
01h30 | 107.4 | 94.21 | 56.92 | 42.57 | 31.35 | 01h30 | 1.3425 | 1.1776 | 0.7115 | 0.53212 | 0.39187
02h30 | 108.77 | 95.13 | 58.18 | 41.64 | 31.14 | 02h30 | 1.3596 | 1.1891 | 0.72725 | 0.5205 | 0.38925
03h30 | 120.7 | 105.23 | 64.8 | 49.22 | 38.49 | 03h30 | 1.5088 | 1.3154 | 0.81 | 0.61525 | 0.48113
04h30 | 129.01 | 111.98 | 69.3 | 54.13 | 43.05 | 04h30 | 1.6126 | 1.3998 | 0.86625 | 0.67663 | 0.53812
05h30 | 126.94 | 108.64 | 67.46 | 52.82 | 42.2 | 05h30 | 1.5868 | 1.358 | 0.84325 | 0.66025 | 0.5275
06h30 | 122.67 | 103.39 | 64.37 | 50.33 | 40.27 | 06h30 | 1.5334 | 1.2924 | 0.80463 | 0.62913 | 0.50338
07h30 | 134.54 | 112.65 | 74.05 | 61.84 | 52.62 | 07h30 | 1.6818 | 1.4081 | 0.92563 | 0.773 | 0.65775
08h30 | 120.56 | 97.45 | 59.81 | 47.59 | 39.4 | 08h30 | 1.507 | 1.2181 | 0.74762 | 0.59488 | 0.4925
09h30 | 117.45 | 96.52 | 57.75 | 45.16 | 36.01 | 09h30 | 1.4681 | 1.2065 | 0.72188 | 0.5645 | 0.45012
10h30 | 119.65 | 100.82 | 58.57 | 47.38 | 35.85 | 10h30 | 1.4956 | 1.2603 | 0.73213 | 0.59225 | 0.44812
11h30 | 120.91 | 103.43 | 59.4 | 48.16 | 35.1 | 11h30 | 1.5114 | 1.2929 | 0.7425 | 0.602 | 0.43875
12h30 | 123.83 | 106.94 | 61.63 | 50.05 | 36.54 | 12h30 | 1.5479 | 1.3368 | 0.77038 | 0.62562 | 0.45675
13h30 | 132.08 | 116.58 | 66.85 | 55.81 | 41.58 | 13h30 | 1.651 | 1.4572 | 0.83562 | 0.69763 | 0.51975
14h30 | 135.9 | 121.96 | 69.88 | 58.28 | 44.6 | 14h30 | 1.6987 | 1.5245 | 0.8735 | 0.7285 | 0.5575
15h30 | 129.7 | 116.18 | 68.13 | 53.87 | 41.83 | 15h30 | 1.6213 | 1.4523 | 0.85162 | 0.67337 | 0.52287
16h30 | 130.64 | 116.84 | 70.14 | 55.47 | 43.61 | 16h30 | 1.633 | 1.4605 | 0.87675 | 0.69337 | 0.54512
17h30 | 137.48 | 128.04 | 77.38 | 64.03 | 51.76 | 17h30 | 1.7185 | 1.6005 | 0.96725 | 0.80037 | 0.647
18h30 | 153.38 | 140.16 | 85.31 | 71.96 | 59.59 | 18h30 | 1.9172 | 1.752 | 1.0664 | 0.8995 | 0.74487
19h30 | 153.38 | 143.35 | 88.03 | 74.24 | 62.51 | 19h30 | 1.9172 | 1.7919 | 1.1004 | 0.928 | 0.78138
20h30 | 141.29 | 127.47 | 78.77 | 65.26 | 54.9 | 20h30 | 1.7661 | 1.5934 | 0.98462 | 0.81575 | 0.68625
21h30 | 120.36 | 105.58 | 65.58 | 52.64 | 43.96 | 21h30 | 1.5045 | 1.3197 | 0.81975 | 0.658 | 0.5495
22h30 | 121.58 | 106.03 | 66.46 | 52.49 | 44.39 | 22h30 | 1.5197 | 1.3254 | 0.83075 | 0.65612 | 0.55488
23h30 | 131.06 | 114.99 | 72.85 | 57.07 | 48.6 | 23h30 | 1.6382 | 1.4374 | 0.91063 | 0.71337 | 0.6075
00h30 | 107.99 | 92.74 | 61.32 | 43.34 | 35.98 | 00h30 | 1.3499 | 1.1592 | 0.7665 | 0.54175 | 0.44975
01h30 | 109.57 | 96.2 | 59.01 | 45.57 | 34.94 | 01h30 | 1.3696 | 1.2025 | 0.73762 | 0.56963 | 0.43675
02h30 | 112.53 | 98.76 | 61.29 | 45.66 | 35.12 | 02h30 | 1.4066 | 1.2345 | 0.76612 | 0.57075 | 0.439
03h30 | 110.63 | 94.89 | 58.93 | 44.48 | 34.03 | 03h30 | 1.3829 | 1.1861 | 0.73662 | 0.556 | 0.42538
04h30 | 96.46 | 82.28 | 56.65 | 44.4 | 33.85 | 04h30 | 1.2058 | 1.0285 | 0.70813 | 0.555 | 0.42312
05h30 | 79.88 | 61.43 | 37.78 | 25.49 | 17.78 | 05h30 | 0.9985 | 0.76787 | 0.47225 | 0.31862 | 0.22225
06h30 | 85.52 | 66.5 | 42.5 | 29.73 | 21.3 | 06h30 | 1.069 | 0.83125 | 0.53125 | 0.37162 | 0.26625
07h30 | 113.89 | 97.81 | 64.9 | 52.8 | 43.68 | 07h30 | 1.4236 | 1.2226 | 0.81125 | 0.66 | 0.546
08h30 | 119.18 | 98.07 | 60.18 | 48.57 | 40.15 | 08h30 | 1.4897 | 1.2259 | 0.75225 | 0.60713 | 0.50187
09h30 | 114.3 | 94.32 | 54.95 | 44.52 | 32.81 | 09h30 | 1.4287 | 1.179 | 0.68688 | 0.5565 | 0.41013
10h30 | 114.55 | 95.1 | 55.1 | 45.23 | 32.81 | 10h30 | 1.4319 | 1.1887 | 0.68875 | 0.56537 | 0.41013
11h30 | 119.43 | 102.29 | 59.1 | 49.86 | 34.95 | 11h30 | 1.4929 | 1.2786 | 0.73875 | 0.62325 | 0.43688
12h30 | 113.65 | 96.63 | 58.96 | 49.15 | 34.95 | 12h30 | 1.4206 | 1.2079 | 0.737 | 0.61438 | 0.43688
13h30 | 101.06 | 85.57 | 47.53 | 39.59 | 24.47 | 13h30 | 1.2632 | 1.0696 | 0.59413 | 0.49488 | 0.30588
14h30 | 98.43 | 85.43 | 47.53 | 39.59 | 24.47 | 14h30 | 1.2304 | 1.0679 | 0.59413 | 0.49488 | 0.30588
15h30 | 94.9 | 83.51 | 44.43 | 35.45 | 19.42 | 15h30 | 1.1863 | 1.0439 | 0.55537 | 0.44312 | 0.24275
16h30 | 91.67 | 83.18 | 44.43 | 35.45 | 19.42 | 16h30 | 1.1459 | 1.0397 | 0.55537 | 0.44312 | 0.24275
17h30 | 95.53 | 85.55 | 47.56 | 37.14 | 22.64 | 17h30 | 1.1941 | 1.0694 | 0.5945 | 0.46425 | 0.283
18h30 | 99.79 | 89.17 | 51.43 | 41.17 | 27.39 | 18h30 | 1.2474 | 1.1146 | 0.64287 | 0.51462 | 0.34237
19h30 | 111.13 | 100.06 | 58.64 | 48.82 | 35.2 | 19h30 | 1.3891 | 1.2508 | 0.733 | 0.61025 | 0.44
20h30 | 127.66 | 116.57 | 69.14 | 58.9 | 44.59 | 20h30 | 1.5958 | 1.4571 | 0.86425 | 0.73625 | 0.55737
21h30 | 128.57 | 120.14 | 75.82 | 65.04 | 50.49 | 21h30 | 1.6071 | 1.5017 | 0.94775 | 0.813 | 0.63113
22h30 | 140.13 | 129.91 | 79.19 | 67.86 | 53.78 | 22h30 | 1.7516 | 1.6239 | 0.98987 | 0.84825 | 0.67225
23h30 | 134.54 | 122.94 | 74.83 | 63.04 | 50.4 | 23h30 | 1.6818 | 1.5368 | 0.93537 | 0.788 | 0.63
00h30 | 106.52 | 96.09 | 57.1 | 46.11 | 32.98 | 00h30 | 1.3315 | 1.2011 | 0.71375 | 0.57637 | 0.41225
01h30 | 112.11 | 103.06 | 63.29 | 50.35 | 37.23 | 01h30 | 1.4014 | 1.2882 | 0.79112 | 0.62938 | 0.46537
02h30 | 134.55 | 125.98 | 76.12 | 60.92 | 46.35 | 02h30 | 1.6819 | 1.5748 | 0.9515 | 0.7615 | 0.57937
03h30 | 134.55 | 125.98 | 88.11 | 73.28 | 57.29 | 03h30 | 1.6819 | 1.5748 | 1.1014 | 0.916 | 0.71613
04h30 | 155.64 | 148.31 | 92.48 | 78.02 | 61.6 | 04h30 | 1.9455 | 1.8539 | 1.156 | 0.97525 | 0.77
05h30 | 155.64 | 148.31 | 90.17 | 76.28 | 60.34 | 05h30 | 1.9455 | 1.8539 | 1.1271 | 0.9535 | 0.75425
06h30 | 153.88 | 140.72 | 85.44 | 72.54 | 57.07 | 06h30 | 1.9235 | 1.759 | 1.068 | 0.90675 | 0.71337
07h30 | 153.88 | 140.72 | 103.24 | 93.11 | 77.45 | 07h30 | 1.9235 | 1.759 | 1.2905 | 1.1639 | 0.96813
08h30 | 176.31 | 159.73 | 101.44 | 90.01 | 74.13 | 08h30 | 2.2039 | 1.9966 | 1.268 | 1.1251 | 0.92663
09h30 | 176.31 | 158.83 | 98.53 | 84.57 | 68.97 | 09h30 | 2.2039 | 1.9854 | 1.2316 | 1.0571 | 0.86213
10h30 | 166.73 | 149.6 | 89.4 | 78.01 | 62.66 | 10h30 | 2.0841 | 1.87 | 1.1175 | 0.97513 | 0.78325
11h30 | 139.83 | 123.62 | 72.18 | 63.13 | 47.73 | 11h30 | 1.7479 | 1.5453 | 0.90225 | 0.78912 | 0.59662
12h30 | 127.04 | 111.75 | 70.65 | 61.22 | 47.2 | 12h30 | 1.588 | 1.3969 | 0.88313 | 0.76525 | 0.59
13h30 | 119.61 | 105.62 | 59.99 | 51.84 | 37.18 | 13h30 | 1.4951 | 1.3202 | 0.74987 | 0.648 | 0.46475
14h30 | 100.75 | 89.21 | 59.99 | 51.84 | 37.18 | 14h30 | 1.2594 | 1.1151 | 0.74987 | 0.648 | 0.46475
15h30 | 80.21 | 70.22 | 37.49 | 26.83 | 14.86 | 15h30 | 1.0026 | 0.87775 | 0.46863 | 0.33537 | 0.18575
16h30 | 68.27 | 58.49 | 37.49 | 26.83 | 14.86 | 16h30 | 0.85337 | 0.73113 | 0.46863 | 0.33537 | 0.18575
17h30 | 92.12 | 82.85 | 46.07 | 32.74 | 22.05 | 17h30 | 1.1515 | 1.0356 | 0.57588 | 0.40925 | 0.27563
18h30 | 102.69 | 93.1 | 54.67 | 41.68 | 30.95 | 18h30 | 1.2836 | 1.1638 | 0.68337 | 0.521 | 0.38688
19h30 | 90.01 | 79.45 | 46.95 | 35.17 | 26.2 | 19h30 | 1.1251 | 0.99313 | 0.58688 | 0.43962 | 0.3275
20h30 | 108.3 | 97.4 | 58.22 | 46.57 | 36.97 | 20h30 | 1.3538 | 1.2175 | 0.72775 | 0.58213 | 0.46213
21h30 | 121.82 | 110.76 | 66.97 | 54.52 | 44.24 | 21h30 | 1.5228 | 1.3845 | 0.83713 | 0.6815 | 0.553
22h30 | 105.82 | 94.41 | 57.23 | 45.32 | 36.11 | 22h30 | 1.3228 | 1.1801 | 0.71537 | 0.5665 | 0.45138
23h30 | 87.26 | 75.34 | 45.64 | 34.4 | 26.77 | 23h30 | 1.0908 | 0.94175 | 0.5705 | 0.43 | 0.33463
00h30 | 67.5 | 56.57 | 35.49 | 23.25 | 15.22 | 00h30 | 0.84375 | 0.70713 | 0.44362 | 0.29063 | 0.19025
01h30 | 88.82 | 79.5 | 45.86 | 34.29 | 24.72 | 01h30 | 1.1102 | 0.99375 | 0.57325 | 0.42862 | 0.309
02h30 | 98.43 | 88.84 | 52.71 | 39.07 | 29.06 | 02h30 | 1.2304 | 1.1105 | 0.65887 | 0.48838 | 0.36325
03h30 | 97.04 | 86.26 | 51.39 | 38.21 | 28.72 | 03h30 | 1.213 | 1.0782 | 0.64238 | 0.47763 | 0.359
04h30 | 86.71 | 74.71 | 45.03 | 33.42 | 24.37 | 04h30 | 1.0839 | 0.93388 | 0.56288 | 0.41775 | 0.30462
05h30 | 77.94 | 64.67 | 39.25 | 27.22 | 19.85 | 05h30 | 0.97425 | 0.80837 | 0.49062 | 0.34025 | 0.24813
06h30 | 86.03 | 71.74 | 43.59 | 32.05 | 24.17 | 06h30 | 1.0754 | 0.89675 | 0.54487 | 0.40063 | 0.30212
07h30 | 106.99 | 89.46 | 58.39 | 48.62 | 40.6 | 07h30 | 1.3374 | 1.1182 | 0.72988 | 0.60775 | 0.5075
08h30 | 96.72 | 81.04 | 53.55 | 43.79 | 36.28 | 08h30 | 1.209 | 1.013 | 0.66938 | 0.54737 | 0.4535
09h30 | 94.56 | 79.68 | 42.73 | 34.4 | 24.98 | 09h30 | 1.182 | 0.996 | 0.53412 | 0.43 | 0.31225
10h30 | 102.05 | 88.59 | 48.76 | 38.49 | 27.02 | 10h30 | 1.2756 | 1.1074 | 0.6095 | 0.48113 | 0.33775
11h30 | 113.86 | 100.11 | 57.01 | 43.96 | 31.53 | 11h30 | 1.4232 | 1.2514 | 0.71262 | 0.5495 | 0.39413
12h30 | 122.06 | 108.54 | 62.69 | 49.76 | 36.24 | 12h30 | 1.5257 | 1.3567 | 0.78363 | 0.622 | 0.453
13h30 | 122.78 | 110.1 | 63.2 | 50.95 | 36.98 | 13h30 | 1.5348 | 1.3762 | 0.79 | 0.63687 | 0.46225
14h30 | 111.91 | 100.35 | 56.11 | 44.24 | 30.53 | 14h30 | 1.3989 | 1.2544 | 0.70137 | 0.553 | 0.38162
15h30 | 107.99 | 96.9 | 52.59 | 40.97 | 27.11 | 15h30 | 1.3499 | 1.2112 | 0.65738 | 0.51213 | 0.33887
16h30 | 106.36 | 95.57 | 52.05 | 39.75 | 26.81 | 16h30 | 1.3295 | 1.1946 | 0.65063 | 0.49688 | 0.33513
17h30 | 97.67 | 87.62 | 49.39 | 36.39 | 24.74 | 17h30 | 1.2209 | 1.0953 | 0.61738 | 0.45487 | 0.30925
18h30 | 85.46 | 81.37 | 45.3 | 34.44 | 24.74 | 18h30 | 1.0682 | 1.0171 | 0.56625 | 0.4305 | 0.30925
19h30 | 72.68 | 61.28 | 35.86 | 24.77 | 17.01 | 19h30 | 0.9085 | 0.766 | 0.44825 | 0.30962 | 0.21263
20h30 | 71.87 | 61.28 | 35.86 | 25.32 | 17.83 | 20h30 | 0.89838 | 0.766 | 0.44825 | 0.3165 | 0.22287
21h30 | 66.95 | 54.78 | 31.89 | 22.49 | 15.18 | 21h30 | 0.83688 | 0.68475 | 0.39863 | 0.28113 | 0.18975
22h30 | 66.25 | 54.78 | 31.89 | 21.93 | 14.88 | 22h30 | 0.82812 | 0.68475 | 0.39863 | 0.27413 | 0.186
23h30 | 82.9 | 69.57 | 42.15 | 30.72 | 23.54 | 23h30 | 1.0362 | 0.86962 | 0.52687 | 0.384 | 0.29425
00h30 | 80.07 | 69.57 | 42.15 | 30.72 | 23.03 | 00h30 | 1.0009 | 0.86962 | 0.52687 | 0.384 | 0.28787
01h30 | 94.83 | 84.85 | 50.11 | 35.97 | 26.61 | 01h30 | 1.1854 | 1.0606 | 0.62638 | 0.44962 | 0.33263
02h30 | 102.24 | 91.24 | 55.25 | 39.58 | 30.3 | 02h30 | 1.278 | 1.1405 | 0.69063 | 0.49475 | 0.37875
03h30 | 107.41 | 96.36 | 58.84 | 43.47 | 33.85 | 03h30 | 1.3426 | 1.2045 | 0.7355 | 0.54338 | 0.42312
04h30 | 121.6 | 108.28 | 66.67 | 51.78 | 41.09 | 04h30 | 1.52 | 1.3535 | 0.83337 | 0.64725 | 0.51362
05h30 | 121.6 | 118.31 | 73.76 | 59.3 | 47.7 | 05h30 | 1.52 | 1.4789 | 0.922 | 0.74125 | 0.59625
06h30 | 137.87 | 124.5 | 76.65 | 62.84 | 50.59 | 06h30 | 1.7234 | 1.5562 | 0.95813 | 0.7855 | 0.63238
07h30 | 137.87 | 124.5 | 95.54 | 84.39 | 71.8 | 07h30 | 1.7234 | 1.5562 | 1.1943 | 1.0549 | 0.8975
08h30 | 168.28 | 148.69 | 94.09 | 82.01 | 68.93 | 08h30 | 2.1035 | 1.8586 | 1.1761 | 1.0251 | 0.86162
09h30 | 168.28 | 148.69 | 97.98 | 83.78 | 69.67 | 09h30 | 2.1035 | 1.8586 | 1.2248 | 1.0473 | 0.87087
10h30 | 179.19 | 158.8 | 96.81 | 84.97 | 69.23 | 10h30 | 2.2399 | 1.985 | 1.2101 | 1.0621 | 0.86538
11h30 | 175.41 | 154.76 | 92.01 | 81.64 | 64.65 | 11h30 | 2.1926 | 1.9345 | 1.1501 | 1.0205 | 0.80812
12h30 | 163.78 | 143.87 | 84.61 | 74.48 | 57.66 | 12h30 | 2.0473 | 1.7984 | 1.0576 | 0.931 | 0.72075
13h30 | 145.92 | 127.19 | 74.29 | 64.12 | 48.69 | 13h30 | 1.824 | 1.5899 | 0.92863 | 0.8015 | 0.60862
14h30 | 132.54 | 114.81 | 68.45 | 57.01 | 45.16 | 14h30 | 1.6567 | 1.4351 | 0.85562 | 0.71262 | 0.5645
15h30 | 124.02 | 106.98 | 62.11 | 51.89 | 38.26 | 15h30 | 1.5502 | 1.3373 | 0.77638 | 0.64863 | 0.47825
16h30 | 121.6 | 104.78 | 62.11 | 51.89 | 38.26 | 16h30 | 1.52 | 1.3097 | 0.77638 | 0.64863 | 0.47825
17h30 | 128.3 | 111.39 | 65.69 | 55.76 | 41.72 | 17h30 | 1.6038 | 1.3924 | 0.82112 | 0.697 | 0.5215
18h30 | 146.8 | 129.91 | 77.46 | 67.58 | 52.35 | 18h30 | 1.835 | 1.6239 | 0.96825 | 0.84475 | 0.65438
19h30 | 156.26 | 139.61 | 83.55 | 73.75 | 58.11 | 19h30 | 1.9532 | 1.7451 | 1.0444 | 0.92188 | 0.72637
20h30 | 145.13 | 128.76 | 77.29 | 67.36 | 52.89 | 20h30 | 1.8141 | 1.6095 | 0.96613 | 0.842 | 0.66112
21h30 | 137.27 | 121.11 | 73.03 | 62.63 | 49.29 | 21h30 | 1.7159 | 1.5139 | 0.91287 | 0.78287 | 0.61613
22h30 | 139.15 | 123.07 | 74.8 | 63.37 | 50.48 | 22h30 | 1.7394 | 1.5384 | 0.935 | 0.79212 | 0.631
23h30 | 129.52 | 113.41 | 69.47 | 57.35 | 45.66 | 23h30 | 1.619 | 1.4176 | 0.86838 | 0.71688 | 0.57075
00h30 | 100.55 | 85.92 | 62.19 | 51.17 | 39.05 | 00h30 | 1.2569 | 1.074 | 0.77738 | 0.63962 | 0.48812
01h30 | 121.89 | 109.75 | 65.08 | 54.35 | 40.66 | 01h30 | 1.5236 | 1.3719 | 0.8135 | 0.67937 | 0.50825
02h30 | 135.4 | 123.56 | 74.28 | 61.94 | 47.01 | 02h30 | 1.6925 | 1.5445 | 0.9285 | 0.77425 | 0.58762
03h30 | 123.99 | 110.86 | 66.89 | 54.1 | 41 | 03h30 | 1.5499 | 1.3858 | 0.83613 | 0.67625 | 0.5125
04h30 | 125.21 | 110.97 | 67.25 | 55.35 | 42.82 | 04h30 | 1.5651 | 1.3871 | 0.84062 | 0.69188 | 0.53525
05h30 | 146.02 | 129.39 | 79.86 | 67.47 | 53.85 | 05h30 | 1.8253 | 1.6174 | 0.99825 | 0.84337 | 0.67312
06h30 | 166.95 | 151.03 | 92.61 | 79.49 | 64.25 | 06h30 | 2.0869 | 1.8879 | 1.1576 | 0.99362 | 0.80312
07h30 | 167.7 | 151.03 | 109.23 | 96.95 | 81.19 | 07h30 | 2.0962 | 1.8879 | 1.3654 | 1.2119 | 1.0149
08h30 | 157.7 | 144.35 | 86.91 | 77.94 | 62.62 | 08h30 | 1.9712 | 1.8044 | 1.0864 | 0.97425 | 0.78275
09h30 | 132.41 | 119.93 | 66.85 | 55.93 | 39.99 | 09h30 | 1.6551 | 1.4991 | 0.83562 | 0.69912 | 0.49988
10h30 | 126.91 | 114.69 | 66.85 | 54.07 | 39.99 | 10h30 | 1.5864 | 1.4336 | 0.83562 | 0.67588 | 0.49988
11h30 | 121.42 | 109.42 | 61.86 | 47.68 | 33.51 | 11h30 | 1.5177 | 1.3678 | 0.77325 | 0.596 | 0.41887
12h30 | 109.48 | 98.06 | 61.86 | 47.68 | 33.51 | 12h30 | 1.3685 | 1.2257 | 0.77325 | 0.596 | 0.41887
13h30 | 102.64 | 92.04 | 52.3 | 38.24 | 25.66 | 13h30 | 1.283 | 1.1505 | 0.65375 | 0.478 | 0.32075
14h30 | 94.61 | 84.73 | 52.3 | 38.24 | 25.66 | 14h30 | 1.1826 | 1.0591 | 0.65375 | 0.478 | 0.32075
15h30 | 89.05 | 79.34 | 42.23 | 28.78 | 17.16 | 15h30 | 1.1131 | 0.99175 | 0.52787 | 0.35975 | 0.2145
16h30 | 86.46 | 77.33 | 42.23 | 28.78 | 17.16 | 16h30 | 1.0808 | 0.96662 | 0.52787 | 0.35975 | 0.2145
17h30 | 99.98 | 92.04 | 52.04 | 37.22 | 26.01 | 17h30 | 1.2497 | 1.1505 | 0.6505 | 0.46525 | 0.32512
18h30 | 105.72 | 98.05 | 57.75 | 43.2 | 32.06 | 18h30 | 1.3215 | 1.2256 | 0.72188 | 0.54 | 0.40075
19h30 | 95.1 | 86.81 | 51.8 | 37.96 | 28.28 | 19h30 | 1.1887 | 1.0851 | 0.6475 | 0.4745 | 0.3535
20h30 | 92.34 | 83.3 | 50.26 | 36.53 | 27.72 | 20h30 | 1.1542 | 1.0413 | 0.62825 | 0.45663 | 0.3465
21h30 | 118.45 | 108.59 | 65.98 | 52.03 | 41.96 | 21h30 | 1.4806 | 1.3574 | 0.82475 | 0.65038 | 0.5245
22h30 | 141.86 | 131.23 | 80.03 | 65.92 | 54.71 | 22h30 | 1.7732 | 1.6404 | 1.0004 | 0.824 | 0.68388
23h30 | 136.36 | 124.87 | 76.63 | 62.36 | 51.93 | 23h30 | 1.7045 | 1.5609 | 0.95788 | 0.7795 | 0.64912
00h30 | 109.15 | 98.46 | 58.43 | 43.92 | 33.7 | 00h30 | 1.3644 | 1.2308 | 0.73037 | 0.549 | 0.42125
01h30 | 100.96 | 91.59 | 54.85 | 39.93 | 30 | 01h30 | 1.262 | 1.1449 | 0.68563 | 0.49912 | 0.375
02h30 | 86.51 | 76.5 | 54.85 | 39.93 | 30 | 02h30 | 1.0814 | 0.95625 | 0.68563 | 0.49912 | 0.375
03h30 | 78.51 | 67.18 | 38.75 | 26.72 | 18.31 | 03h30 | 0.98137 | 0.83975 | 0.48438 | 0.334 | 0.22887
04h30 | 82.62 | 70.07 | 41.94 | 29.54 | 20.8 | 04h30 | 1.0328 | 0.87587 | 0.52425 | 0.36925 | 0.26
05h30 | 85.56 | 71.75 | 42.87 | 30.37 | 21.34 | 05h30 | 1.0695 | 0.89687 | 0.53587 | 0.37962 | 0.26675
06h30 | 79.3 | 66.8 | 39.68 | 27.55 | 18.86 | 06h30 | 0.99125 | 0.835 | 0.496 | 0.34437 | 0.23575
07h30 | 91.34 | 72.41 | 47.22 | 39.09 | 30.33 | 07h30 | 1.1418 | 0.90512 | 0.59025 | 0.48862 | 0.37912
08h30 | 95.52 | 74.39 | 47.22 | 39.09 | 30.33 | 08h30 | 1.194 | 0.92988 | 0.59025 | 0.48862 | 0.37912
09h30 | 102.34 | 83.73 | 48.61 | 38.76 | 28.09 | 09h30 | 1.2792 | 1.0466 | 0.60762 | 0.4845 | 0.35113
10h30 | 109.62 | 94.19 | 53.59 | 43.01 | 29.54 | 10h30 | 1.3702 | 1.1774 | 0.66987 | 0.53763 | 0.36925
11h30 | 114.44 | 100.45 | 57.03 | 44.47 | 29.35 | 11h30 | 1.4305 | 1.2556 | 0.71288 | 0.55588 | 0.36688
12h30 | 110.88 | 96.93 | 55.13 | 42.78 | 28.02 | 12h30 | 1.386 | 1.2116 | 0.68912 | 0.53475 | 0.35025
13h30 | 107.19 | 94.26 | 53.06 | 41.03 | 26.14 | 13h30 | 1.3399 | 1.1783 | 0.66325 | 0.51287 | 0.32675
14h30 | 100.05 | 88.43 | 49.98 | 38.47 | 26.02 | 14h30 | 1.2506 | 1.1054 | 0.62475 | 0.48087 | 0.32525
15h30 | 104.15 | 93.01 | 50.19 | 37.93 | 23.38 | 15h30 | 1.3019 | 1.1626 | 0.62738 | 0.47413 | 0.29225
16h30 | 116.18 | 105.64 | 58.39 | 44.91 | 29.92 | 16h30 | 1.4523 | 1.3205 | 0.72988 | 0.56137 | 0.374
17h30 | 121.9 | 112.64 | 64.57 | 50.4 | 35.8 | 17h30 | 1.5237 | 1.408 | 0.80712 | 0.63 | 0.4475
18h30 | 112.92 | 103.96 | 61.27 | 47.27 | 34.82 | 18h30 | 1.4115 | 1.2995 | 0.76587 | 0.59088 | 0.43525
19h30 | 116.05 | 106.58 | 63.72 | 50.41 | 38.65 | 19h30 | 1.4506 | 1.3322 | 0.7965 | 0.63013 | 0.48313
20h30 | 128.63 | 118.54 | 71.18 | 58.49 | 46.06 | 20h30 | 1.6079 | 1.4817 | 0.88975 | 0.73113 | 0.57575
21h30 | 111.9 | 101.27 | 61.09 | 48.51 | 37.68 | 21h30 | 1.3987 | 1.2659 | 0.76362 | 0.60637 | 0.471
22h30 | 112.25 | 101.05 | 61.39 | 48.48 | 38.13 | 22h30 | 1.4031 | 1.2631 | 0.76738 | 0.606 | 0.47663
23h30 | 128.98 | 118.56 | 72.22 | 59.24 | 47.83 | 23h30 | 1.6122 | 1.482 | 0.90275 | 0.7405 | 0.59788
00h30 | 108.15 | 99.78 | 59.55 | 47.34 | 34.41 | 00h30 | 1.3519 | 1.2472 | 0.74438 | 0.59175 | 0.43012
01h30 | 106.09 | 96.98 | 57.78 | 43.05 | 31.97 | 01h30 | 1.3261 | 1.2123 | 0.72225 | 0.53812 | 0.39963
02h30 | 103.58 | 96.98 | 57.78 | 43.05 | 31.97 | 02h30 | 1.2948 | 1.2123 | 0.72225 | 0.53812 | 0.39963
03h30 | 101.66 | 90.55 | 55 | 39.75 | 30.41 | 03h30 | 1.2708 | 1.1319 | 0.6875 | 0.49688 | 0.38012
04h30 | 96.41 | 90.55 | 55 | 39.75 | 30.41 | 04h30 | 1.2051 | 1.1319 | 0.6875 | 0.49688 | 0.38012
05h30 | 90.22 | 75.92 | 46.22 | 33.74 | 25.58 | 05h30 | 1.1278 | 0.949 | 0.57775 | 0.42175 | 0.31975
06h30 | 98.81 | 84.16 | 51.73 | 38.51 | 29.68 | 06h30 | 1.2351 | 1.052 | 0.64663 | 0.48137 | 0.371
07h30 | 108.99 | 97.68 | 63.67 | 52.44 | 43.42 | 07h30 | 1.3624 | 1.221 | 0.79587 | 0.6555 | 0.54275
08h30 | 100 | 89.43 | 58.15 | 47.67 | 39.31 | 08h30 | 1.25 | 1.1179 | 0.72688 | 0.59588 | 0.49138
09h30 | 85.32 | 64.93 | 35.91 | 23.34 | 16.31 | 09h30 | 1.0665 | 0.81163 | 0.44888 | 0.29175 | 0.20388
10h30 | 85.32 | 65.48 | 36.46 | 26.61 | 17.39 | 10h30 | 1.0665 | 0.8185 | 0.45575 | 0.33263 | 0.21738
11h30 | 75.44 | 59.66 | 31.97 | 23.28 | 11.71 | 11h30 | 0.943 | 0.74575 | 0.39963 | 0.291 | 0.14638
12h30 | 76.47 | 61.36 | 32.5 | 24.2 | 10.66 | 12h30 | 0.95588 | 0.767 | 0.40625 | 0.3025 | 0.13325
13h30 | 85.5 | 71.52 | 37.99 | 29.95 | 14.6 | 13h30 | 1.0688 | 0.894 | 0.47487 | 0.37438 | 0.1825
14h30 | 91.08 | 78.15 | 41.07 | 32.94 | 17.34 | 14h30 | 1.1385 | 0.97688 | 0.51338 | 0.41175 | 0.21675
15h30 | 103.11 | 90.91 | 48.89 | 39.69 | 24.1 | 15h30 | 1.2889 | 1.1364 | 0.61113 | 0.49612 | 0.30125
16h30 | 119.84 | 108.46 | 61.14 | 50.17 | 34.06 | 16h30 | 1.498 | 1.3558 | 0.76425 | 0.62713 | 0.42575
17h30 | 120.06 | 109.18 | 63.26 | 51.7 | 36.55 | 17h30 | 1.5008 | 1.3647 | 0.79075 | 0.64625 | 0.45687
18h30 | 109.47 | 98.56 | 57.7 | 46.88 | 33.42 | 18h30 | 1.3684 | 1.232 | 0.72125 | 0.586 | 0.41775
19h30 | 97.21 | 86.05 | 50.47 | 40.33 | 28.7 | 19h30 | 1.2151 | 1.0756 | 0.63087 | 0.50413 | 0.35875
20h30 | 86.22 | 74.81 | 43.88 | 34.22 | 24.35 | 20h30 | 1.0777 | 0.93512 | 0.5485 | 0.42775 | 0.30438
21h30 | 84.43 | 72.82 | 42.9 | 33.4 | 24.12 | 21h30 | 1.0554 | 0.91025 | 0.53625 | 0.4175 | 0.3015
22h30 | 82.65 | 68.25 | 38.65 | 28.47 | 20.18 | 22h30 | 1.0331 | 0.85313 | 0.48313 | 0.35587 | 0.25225
23h30 | 63.15 | 50.22 | 29.55 | 20.78 | 13.64 | 23h30 | 0.78938 | 0.62775 | 0.36938 | 0.25975 | 0.1705
00h30 | 63.15 | 50.22 | 29.55 | 18.99 | 12.35 | 00h30 | 0.78938 | 0.62775 | 0.36938 | 0.23738 | 0.15438
01h30 | 59.91 | 50.87 | 27.73 | 15.81 | 7.81 | 01h30 | 0.74887 | 0.63587 | 0.34663 | 0.19762 | 0.097625
02h30 | 65.56 | 57.18 | 33.82 | 19.8 | 11.7 | 02h30 | 0.8195 | 0.71475 | 0.42275 | 0.2475 | 0.14625
03h30 | 71.25 | 60.97 | 36.25 | 23.2 | 14.94 | 03h30 | 0.89062 | 0.76213 | 0.45312 | 0.29 | 0.18675
04h30 | 74.78 | 63.67 | 38.32 | 25.86 | 17.6 | 04h30 | 0.93475 | 0.79587 | 0.479 | 0.32325 | 0.22
05h30 | 81.7 | 69.65 | 42.34 | 30.05 | 21.57 | 05h30 | 1.0212 | 0.87062 | 0.52925 | 0.37562 | 0.26963
06h30 | 87.65 | 74.81 | 45.83 | 33.12 | 24.54 | 06h30 | 1.0956 | 0.93512 | 0.57288 | 0.414 | 0.30675
07h30 | 95.12 | 79.52 | 53.3 | 42.35 | 34.63 | 07h30 | 1.189 | 0.994 | 0.66625 | 0.52938 | 0.43288
08h30 | 80.22 | 65.36 | 41.65 | 32.62 | 25.12 | 08h30 | 1.0028 | 0.817 | 0.52063 | 0.40775 | 0.314
09h30 | 73.62 | 56.99 | 31.66 | 22.79 | 15.41 | 09h30 | 0.92025 | 0.71237 | 0.39575 | 0.28487 | 0.19262
10h30 | 73.39 | 56.99 | 31.66 | 22.79 | 15.41 | 10h30 | 0.91738 | 0.71237 | 0.39575 | 0.28487 | 0.19262
11h30 | 69.71 | 56.1 | 28.53 | 19.7 | 8.92 | 11h30 | 0.87138 | 0.70125 | 0.35663 | 0.24625 | 0.1115
12h30 | 69.71 | 56.1 | 28.53 | 19.7 | 8.92 | 12h30 | 0.87138 | 0.70125 | 0.35663 | 0.24625 | 0.1115
13h30 | 50.98 | 38.94 | 17.3 | 10.28 | 0 | 13h30 | 0.63725 | 0.48675 | 0.21625 | 0.1285 | 0
14h30 | 50.98 | 38.94 | 17.3 | 10.28 | 0 | 14h30 | 0.63725 | 0.48675 | 0.21625 | 0.1285 | 0
15h30 | 34.08 | 23.31 | 4.05 | 0 | 0 | 15h30 | 0.426 | 0.29137 | 0.050625 | 0 | 0
16h30 | 34.08 | 23.31 | 4.05 | 0 | 0 | 16h30 | 0.426 | 0.29137 | 0.050625 | 0 | 0
17h30 | 32.35 | 21.92 | 4.2 | 0 | 0 | 17h30 | 0.40437 | 0.274 | 0.0525 | 0 | 0
18h30 | 41.07 | 32.3 | 13.1 | 5.66 | 0 | 18h30 | 0.51338 | 0.40375 | 0.16375 | 0.07075 | 0
19h30 | 45.64 | 38.29 | 18.34 | 10.42 | 0.5 | 19h30 | 0.5705 | 0.47863 | 0.22925 | 0.13025 | 0.00625
20h30 | 53.03 | 46.32 | 23.97 | 16.09 | 5.96 | 20h30 | 0.66287 | 0.579 | 0.29962 | 0.20112 | 0.0745
21h30 | 65.38 | 59.04 | 32.41 | 23.82 | 13.38 | 21h30 | 0.81725 | 0.738 | 0.40513 | 0.29775 | 0.16725
22h30 | 69.25 | 62.96 | 35.42 | 26.39 | 16.41 | 22h30 | 0.86562 | 0.787 | 0.44275 | 0.32987 | 0.20513
23h30 | 70.17 | 63.65 | 36.26 | 27.21 | 17.99 | 23h30 | 0.87713 | 0.79563 | 0.45325 | 0.34013 | 0.22487
00h30 | 63.11 | 57.77 | 28.37 | 17.63 | 9.51 | 00h30 | 0.78887 | 0.72213 | 0.35463 | 0.22037 | 0.11887
01h30 | 72.98 | 66.13 | 36.9 | 24.88 | 14.86 | 01h30 | 0.91225 | 0.82663 | 0.46125 | 0.311 | 0.18575
02h30 | 73.07 | 63.85 | 35.47 | 23.92 | 14.86 | 02h30 | 0.91338 | 0.79812 | 0.44338 | 0.299 | 0.18575
03h30 | 79.89 | 71.56 | 41.22 | 29.43 | 20.03 | 03h30 | 0.99862 | 0.8945 | 0.51525 | 0.36788 | 0.25038
04h30 | 88.75 | 80.56 | 47.62 | 35.27 | 25.76 | 04h30 | 1.1094 | 1.007 | 0.59525 | 0.44088 | 0.322
05h30 | 94.32 | 85.43 | 51.11 | 38.96 | 29.42 | 05h30 | 1.179 | 1.0679 | 0.63887 | 0.487 | 0.36775
06h30 | 94.17 | 84.45 | 50.12 | 38.88 | 29.45 | 06h30 | 1.1771 | 1.0556 | 0.6265 | 0.486 | 0.36812
07h30 | 105.69 | 95.13 | 60.1 | 50.35 | 41.05 | 07h30 | 1.3211 | 1.1891 | 0.75125 | 0.62938 | 0.51313
08h30 | 95.4 | 83.96 | 47.87 | 41.25 | 35.3 | 08h30 | 1.1925 | 1.0495 | 0.59837 | 0.51562 | 0.44125
09h30 | 89.64 | 77.75 | 42.51 | 33.52 | 22.84 | 09h30 | 1.1205 | 0.97188 | 0.53138 | 0.419 | 0.2855
10h30 | 87.79 | 75.63 | 41.1 | 33.52 | 22.84 | 10h30 | 1.0974 | 0.94537 | 0.51375 | 0.419 | 0.2855
11h30 | 93.93 | 81.57 | 44.13 | 34.99 | 22.68 | 11h30 | 1.1741 | 1.0196 | 0.55163 | 0.43738 | 0.2835
12h30 | 99.04 | 86.84 | 47.34 | 38.6 | 25.14 | 12h30 | 1.238 | 1.0855 | 0.59175 | 0.4825 | 0.31425
13h30 | 99.43 | 87.57 | 47.11 | 39.19 | 24.92 | 13h30 | 1.2429 | 1.0946 | 0.58888 | 0.48988 | 0.3115
14h30 | 98.24 | 86.56 | 45.4 | 38.06 | 23.23 | 14h30 | 1.228 | 1.082 | 0.5675 | 0.47575 | 0.29037
15h30 | 99.9 | 88.31 | 46 | 38.32 | 23.4 | 15h30 | 1.2488 | 1.1039 | 0.575 | 0.479 | 0.2925
16h30 | 103.33 | 92.58 | 49.87 | 40.73 | 26.57 | 16h30 | 1.2916 | 1.1572 | 0.62338 | 0.50913 | 0.33213
17h30 | 107.02 | 97.21 | 54.4 | 44.8 | 31.13 | 17h30 | 1.3377 | 1.2151 | 0.68 | 0.56 | 0.38912
18h30 | 106.58 | 97 | 55.37 | 46.2 | 33.2 | 18h30 | 1.3322 | 1.2125 | 0.69212 | 0.5775 | 0.415
19h30 | 102.39 | 92.8 | 53.48 | 44.42 | 32.32 | 19h30 | 1.2799 | 1.16 | 0.6685 | 0.55525 | 0.404
20h30 | 102.75 | 92.99 | 53.96 | 44.91 | 33.17 | 20h30 | 1.2844 | 1.1624 | 0.6745 | 0.56137 | 0.41463
21h30 | 101.67 | 91.53 | 53.34 | 44.36 | 32.86 | 21h30 | 1.2709 | 1.1441 | 0.66675 | 0.5545 | 0.41075
22h30 | 99.1 | 88.35 | 51.84 | 42.55 | 31.9 | 22h30 | 1.2388 | 1.1044 | 0.648 | 0.53187 | 0.39875
23h30 | 97.74 | 86.08 | 51.11 | 41.11 | 31.4 | 23h30 | 1.2217 | 1.076 | 0.63887 | 0.51387 | 0.3925
00h30 | 83.46 | 71.85 | 45.79 | 36.13 | 25.49 | 00h30 | 1.0433 | 0.89812 | 0.57237 | 0.45162 | 0.31862
01h30 | 88.06 | 78.46 | 44.36 | 32.83 | 22.48 | 01h30 | 1.1007 | 0.98075 | 0.5545 | 0.41037 | 0.281
02h30 | 94.05 | 83.07 | 48.29 | 36.35 | 25.49 | 02h30 | 1.1756 | 1.0384 | 0.60362 | 0.45437 | 0.31862
03h30 | 94.34 | 83.03 | 48.05 | 36.3 | 25.98 | 03h30 | 1.1792 | 1.0379 | 0.60062 | 0.45375 | 0.32475
04h30 | 100.44 | 88.34 | 52.17 | 40.54 | 30.21 | 04h30 | 1.2555 | 1.1042 | 0.65212 | 0.50675 | 0.37762
05h30 | 112.09 | 99.65 | 59.63 | 47.9 | 37.14 | 05h30 | 1.4011 | 1.2456 | 0.74538 | 0.59875 | 0.46425
06h30 | 116.21 | 102.44 | 61.65 | 49.92 | 39.21 | 06h30 | 1.4526 | 1.2805 | 0.77063 | 0.624 | 0.49012
07h30 | 116.21 | 110.34 | 70.22 | 60.29 | 50.02 | 07h30 | 1.4526 | 1.3793 | 0.87775 | 0.75362 | 0.62525
08h30 | 116.9 | 101.6 | 60.15 | 51.58 | 40.7 | 08h30 | 1.4612 | 1.27 | 0.75187 | 0.64475 | 0.50875
09h30 | 116.9 | 103.96 | 59.43 | 51.44 | 38.47 | 09h30 | 1.4612 | 1.2995 | 0.74287 | 0.643 | 0.48087
10h30 | 120.88 | 106.84 | 59.43 | 50.37 | 38.47 | 10h30 | 1.511 | 1.3355 | 0.74287 | 0.62962 | 0.48087
11h30 | 114.24 | 99.73 | 53.97 | 44.05 | 30.26 | 11h30 | 1.428 | 1.2466 | 0.67463 | 0.55063 | 0.37825
12h30 | 116.33 | 102.27 | 56.27 | 45.73 | 32.2 | 12h30 | 1.4541 | 1.2784 | 0.70337 | 0.57163 | 0.4025
13h30 | 118.81 | 105.54 | 58.38 | 47.51 | 33.79 | 13h30 | 1.4851 | 1.3193 | 0.72975 | 0.59388 | 0.42238
14h30 | 114.28 | 101.55 | 56.08 | 45.83 | 31.86 | 14h30 | 1.4285 | 1.2694 | 0.701 | 0.57288 | 0.39825
15h30 | 118.44 | 105.38 | 57.27 | 47.72 | 32.22 | 15h30 | 1.4805 | 1.3173 | 0.71588 | 0.5965 | 0.40275
16h30 | 127.46 | 113.41 | 60.23 | 49.97 | 33.97 | 16h30 | 1.5933 | 1.4176 | 0.75287 | 0.62462 | 0.42462
17h30 | 127.46 | 113.41 | 64.03 | 52.54 | 37.32 | 17h30 | 1.5933 | 1.4176 | 0.80037 | 0.65675 | 0.4665
18h30 | 126.17 | 116.17 | 66.36 | 54.03 | 40.4 | 18h30 | 1.5771 | 1.4521 | 0.8295 | 0.67537 | 0.505
19h30 | 118.33 | 109.93 | 63.78 | 51.65 | 40.06 | 19h30 | 1.4791 | 1.3741 | 0.79725 | 0.64563 | 0.50075
20h30 | 111.04 | 102.42 | 60.01 | 48.21 | 38.16 | 20h30 | 1.388 | 1.2803 | 0.75013 | 0.60262 | 0.477
21h30 | 105.82 | 96.82 | 57.15 | 45.59 | 36.08 | 21h30 | 1.3228 | 1.2103 | 0.71437 | 0.56988 | 0.451
22h30 | 107.35 | 97.72 | 58.09 | 46.54 | 37.07 | 22h30 | 1.3419 | 1.2215 | 0.72613 | 0.58175 | 0.46337
23h30 | 108.83 | 98.24 | 58.61 | 47.34 | 38.03 | 23h30 | 1.3604 | 1.228 | 0.73262 | 0.59175 | 0.47537
00h30 | 88.41 | 88.68 | 56.14 | 46.09 | 34.09 | 00h30 | 1.1051 | 1.1085 | 0.70175 | 0.57612 | 0.42612
01h30 | 85.07 | 76.16 | 42.55 | 29.93 | 21.25 | 01h30 | 1.0634 | 0.952 | 0.53187 | 0.37412 | 0.26562
02h30 | 85.07 | 76.16 | 42.55 | 29.93 | 21.25 | 02h30 | 1.0634 | 0.952 | 0.53187 | 0.37412 | 0.26562
03h30 | 84.13 | 72.02 | 41.55 | 28.62 | 20.83 | 03h30 | 1.0516 | 0.90025 | 0.51938 | 0.35775 | 0.26038
04h30 | 84.13 | 72.02 | 41.55 | 28.62 | 20.83 | 04h30 | 1.0516 | 0.90025 | 0.51938 | 0.35775 | 0.26038
05h30 | 76.8 | 62.36 | 38.09 | 24.24 | 17.5 | 05h30 | 0.96 | 0.7795 | 0.47613 | 0.303 | 0.21875
06h30 | 78.88 | 63.9 | 39.09 | 25.31 | 18.51 | 06h30 | 0.986 | 0.79875 | 0.48862 | 0.31638 | 0.23137
07h30 | 94.09 | 77.75 | 50.89 | 39 | 31.81 | 07h30 | 1.1761 | 0.97188 | 0.63613 | 0.4875 | 0.39763
08h30 | 92 | 76.21 | 49.89 | 37.93 | 30.81 | 08h30 | 1.15 | 0.95263 | 0.62362 | 0.47413 | 0.38512
09h30 | 75.37 | 58.62 | 27.42 | 20.76 | 11.82 | 09h30 | 0.94212 | 0.73275 | 0.34275 | 0.2595 | 0.14775
10h30 | 77.55 | 62.43 | 30.17 | 22.17 | 11.82 | 10h30 | 0.96937 | 0.78038 | 0.37712 | 0.27713 | 0.14775
11h30 | 88.73 | 72.43 | 36.57 | 27.22 | 15.53 | 11h30 | 1.1091 | 0.90538 | 0.45713 | 0.34025 | 0.19412
12h30 | 91.71 | 76.06 | 39.37 | 30.42 | 18.27 | 12h30 | 1.1464 | 0.95075 | 0.49212 | 0.38025 | 0.22837
13h30 | 93.13 | 78.26 | 40.33 | 32.11 | 19.5 | 13h30 | 1.1641 | 0.97825 | 0.50413 | 0.40137 | 0.24375
14h30 | 106.63 | 92.49 | 48.74 | 40.08 | 26.06 | 14h30 | 1.3329 | 1.1561 | 0.60925 | 0.501 | 0.32575
15h30 | 118.67 | 107.76 | 58.49 | 48.37 | 33.22 | 15h30 | 1.4834 | 1.347 | 0.73113 | 0.60462 | 0.41525
16h30 | 127.2 | 115.45 | 63.85 | 53.12 | 37.88 | 16h30 | 1.59 | 1.4431 | 0.79812 | 0.664 | 0.4735
17h30 | 127.2 | 122.76 | 69.66 | 58.62 | 43.1 | 17h30 | 1.59 | 1.5345 | 0.87075 | 0.73275 | 0.53875
18h30 | 135.39 | 126.48 | 73.38 | 62.2 | 47.04 | 18h30 | 1.6924 | 1.581 | 0.91725 | 0.7775 | 0.588
19h30 | 135.39 | 125.31 | 73.56 | 62.35 | 48.08 | 19h30 | 1.6924 | 1.5664 | 0.9195 | 0.77938 | 0.601
20h30 | 140.14 | 129.08 | 76.36 | 64.98 | 50.74 | 20h30 | 1.7517 | 1.6135 | 0.9545 | 0.81225 | 0.63425
21h30 | 140.14 | 136.86 | 82.91 | 71.64 | 56.87 | 21h30 | 1.7517 | 1.7107 | 1.0364 | 0.8955 | 0.71088
22h30 | 152.49 | 143.05 | 85.5 | 74.38 | 59.62 | 22h30 | 1.9061 | 1.7881 | 1.0688 | 0.92975 | 0.74525
23h30 | 152.49 | 140.82 | 84.15 | 73.18 | 58.92 | 23h30 | 1.9061 | 1.7603 | 1.0519 | 0.91475 | 0.7365
00h30 | 131.06 | 120.06 | 67.19 | 54.91 | 40.44 | 00h30 | 1.6382 | 1.5008 | 0.83988 | 0.68637 | 0.5055
01h30 | 128.51 | 118.46 | 69.59 | 56.07 | 41.39 | 01h30 | 1.6064 | 1.4808 | 0.86987 | 0.70088 | 0.51738
02h30 | 131.74 | 119.78 | 69.96 | 57.02 | 42.33 | 02h30 | 1.6467 | 1.4972 | 0.8745 | 0.71275 | 0.52912
03h30 | 134.29 | 123.61 | 74.79 | 62.46 | 47.62 | 03h30 | 1.6786 | 1.5451 | 0.93488 | 0.78075 | 0.59525
04h30 | 143.16 | 130.64 | 78.06 | 65.83 | 51.52 | 04h30 | 1.7895 | 1.633 | 0.97575 | 0.82288 | 0.644
05h30 | 143.16 | 130.64 | 80.03 | 67.43 | 53.8 | 05h30 | 1.7895 | 1.633 | 1.0004 | 0.84288 | 0.6725
06h30 | 148.4 | 134.18 | 81.23 | 68.52 | 54.45 | 06h30 | 1.855 | 1.6772 | 1.0154 | 0.8565 | 0.68063
07h30 | 148.4 | 134.18 | 98.36 | 87.42 | 72.7 | 07h30 | 1.855 | 1.6772 | 1.2295 | 1.0928 | 0.90875
08h30 | 162 | 146.28 | 89.3 | 79.86 | 65.87 | 08h30 | 2.025 | 1.8285 | 1.1162 | 0.99825 | 0.82337
09h30 | 159.13 | 142.69 | 83.53 | 73.16 | 58.58 | 09h30 | 1.9891 | 1.7836 | 1.0441 | 0.9145 | 0.73225
10h30 | 154.29 | 138.76 | 79.98 | 68.73 | 55.08 | 10h30 | 1.9286 | 1.7345 | 0.99975 | 0.85913 | 0.6885
11h30 | 146.54 | 131.83 | 75.01 | 64.11 | 47.18 | 11h30 | 1.8317 | 1.6479 | 0.93763 | 0.80137 | 0.58975
12h30 | 136.11 | 121.83 | 71.26 | 62.66 | 47.18 | 12h30 | 1.7014 | 1.5229 | 0.89075 | 0.78325 | 0.58975
13h30 | 123.87 | 110.44 | 61.44 | 52.32 | 34.71 | 13h30 | 1.5484 | 1.3805 | 0.768 | 0.654 | 0.43388
14h30 | 116.11 | 103.35 | 61.44 | 52.32 | 34.71 | 14h30 | 1.4514 | 1.2919 | 0.768 | 0.654 | 0.43388
15h30 | 119.47 | 105.97 | 56.03 | 46.45 | 27.33 | 15h30 | 1.4934 | 1.3246 | 0.70037 | 0.58062 | 0.34163
16h30 | 129.56 | 115.22 | 60 | 49.91 | 30.63 | 16h30 | 1.6195 | 1.4403 | 0.75 | 0.62387 | 0.38288
17h30 | 128.99 | 116.06 | 61.52 | 50.79 | 33.33 | 17h30 | 1.6124 | 1.4507 | 0.769 | 0.63487 | 0.41663
18h30 | 89.71 | 81.55 | 57.54 | 47.33 | 30.03 | 18h30 | 1.1214 | 1.0194 | 0.71925 | 0.59162 | 0.37538
19h30 | 50.72 | 42.29 | 21.11 | 11.25 | 3.22 | 19h30 | 0.634 | 0.52863 | 0.26388 | 0.14062 | 0.04025
20h30 | 48.8 | 42.29 | 21.86 | 11.72 | 4.13 | 20h30 | 0.61 | 0.52863 | 0.27325 | 0.1465 | 0.051625
21h30 | 54.98 | 45.93 | 25.67 | 13.42 | 6.9 | 21h30 | 0.68725 | 0.57412 | 0.32088 | 0.16775 | 0.08625
22h30 | 77.17 | 67.9 | 39.42 | 27.21 | 19.05 | 22h30 | 0.96462 | 0.84875 | 0.49275 | 0.34013 | 0.23813
23h30 | 106.86 | 96.75 | 57.27 | 45.06 | 34.63 | 23h30 | 1.3357 | 1.2094 | 0.71588 | 0.56325 | 0.43288
00h30 | 102.67 | 95.15 | 51.45 | 37.53 | 25.24 | 00h30 | 1.2834 | 1.1894 | 0.64312 | 0.46913 | 0.3155
01h30 | 110.46 | 102.78 | 59.06 | 44.4 | 30.76 | 01h30 | 1.3807 | 1.2848 | 0.73825 | 0.555 | 0.3845
02h30 | 118.98 | 108.17 | 62.13 | 48.62 | 34.21 | 02h30 | 1.4872 | 1.3521 | 0.77663 | 0.60775 | 0.42762
03h30 | 127.88 | 116.9 | 68.12 | 54.92 | 39.86 | 03h30 | 1.5985 | 1.4612 | 0.8515 | 0.6865 | 0.49825
04h30 | 131.74 | 120.19 | 70.35 | 58.04 | 42.46 | 04h30 | 1.6467 | 1.5024 | 0.87938 | 0.7255 | 0.53075
05h30 | 138.23 | 129.05 | 78.19 | 66.72 | 50.9 | 05h30 | 1.7279 | 1.6131 | 0.97737 | 0.834 | 0.63625
06h30 | 148.74 | 136.74 | 81.35 | 69.94 | 54.67 | 06h30 | 1.8593 | 1.7092 | 1.0169 | 0.87425 | 0.68337
07h30 | 148.74 | 136.74 | 93.75 | 83.68 | 69.43 | 07h30 | 1.8593 | 1.7092 | 1.1719 | 1.046 | 0.86787
08h30 | 156.32 | 141.65 | 84.54 | 77.01 | 62.86 | 08h30 | 1.954 | 1.7706 | 1.0568 | 0.96262 | 0.78575
09h30 | 154.23 | 139.87 | 80.35 | 71.67 | 57.31 | 09h30 | 1.9279 | 1.7484 | 1.0044 | 0.89587 | 0.71637
10h30 | 163.09 | 149.47 | 84.97 | 73.79 | 58.67 | 10h30 | 2.0386 | 1.8684 | 1.0621 | 0.92237 | 0.73337
11h30 | 165.18 | 151.25 | 89.32 | 78.52 | 61.28 | 11h30 | 2.0648 | 1.8906 | 1.1165 | 0.9815 | 0.766
12h30 | 165.78 | 152.34 | 87.48 | 77.59 | 59.32 | 12h30 | 2.0722 | 1.9042 | 1.0935 | 0.96988 | 0.7415
13h30 | 165.78 | 152.34 | 105.93 | 95.75 | 77.45 | 13h30 | 2.0722 | 1.9042 | 1.3241 | 1.1969 | 0.96813
14h30 | 195.73 | 182.59 | 110.17 | 99.1 | 81.01 | 14h30 | 2.4466 | 2.2824 | 1.3771 | 1.2388 | 1.0126
15h30 | 179.95 | 167.23 | 94.13 | 83.09 | 65.23 | 15h30 | 2.2494 | 2.0904 | 1.1766 | 1.0386 | 0.81537
16h30 | 184.22 | 173.1 | 96.15 | 85.09 | 66.53 | 16h30 | 2.3028 | 2.1637 | 1.2019 | 1.0636 | 0.83162
17h30 | 184.83 | 173.84 | 98.24 | 86.02 | 68.27 | 17h30 | 2.3104 | 2.173 | 1.228 | 1.0753 | 0.85337
18h30 | 171.19 | 161.25 | 93.48 | 80.01 | 64.85 | 18h30 | 2.1399 | 2.0156 | 1.1685 | 1.0001 | 0.81063
19h30 | 176.42 | 166.36 | 98.92 | 84.79 | 70.75 | 19h30 | 2.2052 | 2.0795 | 1.2365 | 1.0599 | 0.88438
20h30 | 190.06 | 188.43 | 113.38 | 98.92 | 84.1 | 20h30 | 2.3758 | 2.3554 | 1.4172 | 1.2365 | 1.0513
21h30 | 200 | 197.94 | 120.07 | 106.29 | 90.47 | 21h30 | 2.5 | 2.4743 | 1.5009 | 1.3286 | 1.1309
22h30 | 195.94 | 185.61 | 111.87 | 99.34 | 84.21 | 22h30 | 2.4493 | 2.3201 | 1.3984 | 1.2417 | 1.0526
23h30 | 160.76 | 146.77 | 88.45 | 76.28 | 63.84 | 23h30 | 2.0095 | 1.8346 | 1.1056 | 0.9535 | 0.798
00h30 | 131.23 | 118.49 | 69.99 | 57.94 | 48.97 | 00h30 | 1.6404 | 1.4811 | 0.87487 | 0.72425 | 0.61213
01h30 | 147.72 | 136.43 | 81.67 | 65.87 | 52.45 | 01h30 | 1.8465 | 1.7054 | 1.0209 | 0.82337 | 0.65563
02h30 | 116.15 | 103.48 | 81.67 | 65.87 | 52.45 | 02h30 | 1.4519 | 1.2935 | 1.0209 | 0.82337 | 0.65563
03h30 | 99.06 | 85.26 | 48.64 | 37.7 | 27.14 | 03h30 | 1.2383 | 1.0657 | 0.608 | 0.47125 | 0.33925
04h30 | 121.58 | 106.63 | 64.19 | 52.02 | 40.28 | 04h30 | 1.5197 | 1.3329 | 0.80237 | 0.65025 | 0.5035
05h30 | 137.28 | 121.16 | 73.39 | 57.52 | 46.66 | 05h30 | 1.716 | 1.5145 | 0.91738 | 0.719 | 0.58325
06h30 | 127.26 | 110.47 | 66.57 | 52.52 | 41.86 | 06h30 | 1.5908 | 1.3809 | 0.83213 | 0.6565 | 0.52325
07h30 | 122.13 | 103.16 | 66.4 | 54.69 | 45.76 | 07h30 | 1.5266 | 1.2895 | 0.83 | 0.68363 | 0.572
08h30 | 121.73 | 99.61 | 60.37 | 49.1 | 40.39 | 08h30 | 1.5216 | 1.2451 | 0.75462 | 0.61375 | 0.50487
09h30 | 135.02 | 112.93 | 67.48 | 56.01 | 45.77 | 09h30 | 1.6878 | 1.4116 | 0.8435 | 0.70012 | 0.57212
10h30 | 145.21 | 125.12 | 73.3 | 62.73 | 50.26 | 10h30 | 1.8151 | 1.564 | 0.91625 | 0.78412 | 0.62825
11h30 | 140.59 | 122.05 | 70.61 | 59.95 | 46.91 | 11h30 | 1.7574 | 1.5256 | 0.88262 | 0.74938 | 0.58637
12h30 | 130.48 | 112.93 | 64.85 | 53.98 | 41.14 | 12h30 | 1.631 | 1.4116 | 0.81063 | 0.67475 | 0.51425
13h30 | 131.65 | 115.35 | 65.68 | 54.94 | 42.23 | 13h30 | 1.6456 | 1.4419 | 0.821 | 0.68675 | 0.52787
14h30 | 119.86 | 104.97 | 62.92 | 50.45 | 40.53 | 14h30 | 1.4983 | 1.3121 | 0.7865 | 0.63062 | 0.50662
15h30 | 118.35 | 104.25 | 56.89 | 46.17 | 33.46 | 15h30 | 1.4794 | 1.3031 | 0.71113 | 0.57712 | 0.41825
16h30 | 142.95 | 129.34 | 71.94 | 60.77 | 46.53 | 16h30 | 1.7869 | 1.6167 | 0.89925 | 0.75962 | 0.58162
17h30 | 159.81 | 149.31 | 90.59 | 78.08 | 62.83 | 17h30 | 1.9976 | 1.8664 | 1.1324 | 0.976 | 0.78538
18h30 | 182.66 | 171.09 | 102.43 | 89.24 | 74.62 | 18h30 | 2.2832 | 2.1386 | 1.2804 | 1.1155 | 0.93275
19h30 | 182.66 | 171.09 | 103.31 | 90.12 | 76.93 | 19h30 | 2.2832 | 2.1386 | 1.2914 | 1.1265 | 0.96162
20h30 | 193.61 | 179.27 | 108.97 | 95.17 | 81.99 | 20h30 | 2.4201 | 2.2409 | 1.3621 | 1.1896 | 1.0249
21h30 | 193.61 | 179.27 | 111.31 | 97.75 | 84.16 | 21h30 | 2.4201 | 2.2409 | 1.3914 | 1.2219 | 1.052
22h30 | 191.7 | 176.59 | 107.95 | 95.01 | 81.49 | 22h30 | 2.3963 | 2.2074 | 1.3494 | 1.1876 | 1.0186
23h30 | 191.7 | 176.59 | 115.13 | 102.3 | 88.11 | 23h30 | 2.3963 | 2.2074 | 1.4391 | 1.2788 | 1.1014
00h30 | 200 | 187.16 | 109.41 | 97.41 | 81.14 | 00h30 | 2.5 | 2.3395 | 1.3676 | 1.2176 | 1.0143
01h30 | 200 | 187.16 | 112.3 | 99.2 | 82.34 | 01h30 | 2.5 | 2.3395 | 1.4038 | 1.24 | 1.0292
02h30 | 181.21 | 167.15 | 100.64 | 85.72 | 70.89 | 02h30 | 2.2651 | 2.0894 | 1.258 | 1.0715 | 0.88613
03h30 | 164.61 | 149.32 | 90.65 | 75.81 | 62.99 | 03h30 | 2.0576 | 1.8665 | 1.1331 | 0.94763 | 0.78738
04h30 | 157.03 | 140.27 | 85.96 | 71.16 | 59.4 | 04h30 | 1.9629 | 1.7534 | 1.0745 | 0.8895 | 0.7425
05h30 | 150.32 | 131.96 | 81.44 | 67.18 | 56.21 | 05h30 | 1.879 | 1.6495 | 1.018 | 0.83975 | 0.70263
06h30 | 138.15 | 119.39 | 74.33 | 62.14 | 50.96 | 06h30 | 1.7269 | 1.4924 | 0.92912 | 0.77675 | 0.637
07h30 | 155.02 | 134.88 | 85.12 | 74.13 | 63.07 | 07h30 | 1.9378 | 1.686 | 1.064 | 0.92663 | 0.78838
08h30 | 168.14 | 146.64 | 86.34 | 77.63 | 64.33 | 08h30 | 2.1018 | 1.833 | 1.0793 | 0.97037 | 0.80412
09h30 | 174.58 | 157.3 | 95.78 | 85.33 | 69.8 | 09h30 | 2.1822 | 1.9663 | 1.1972 | 1.0666 | 0.8725
10h30 | 177.77 | 162.39 | 94.61 | 81.82 | 68.55 | 10h30 | 2.2221 | 2.0299 | 1.1826 | 1.0228 | 0.85688
11h30 | 160.23 | 143.09 | 82.61 | 69.93 | 55.55 | 11h30 | 2.0029 | 1.7886 | 1.0326 | 0.87413 | 0.69437
12h30 | 143.11 | 126.26 | 82.56 | 69.93 | 55.55 | 12h30 | 1.7889 | 1.5782 | 1.032 | 0.87413 | 0.69437
13h30 | 137.91 | 122.08 | 70.49 | 59.71 | 45.06 | 13h30 | 1.7239 | 1.526 | 0.88113 | 0.74638 | 0.56325
14h30 | 166.07 | 151.63 | 87.36 | 75.3 | 60.11 | 14h30 | 2.0759 | 1.8954 | 1.092 | 0.94125 | 0.75138
15h30 | 188.81 | 175.11 | 107.38 | 93.59 | 76.83 | 15h30 | 2.3601 | 2.1889 | 1.3422 | 1.1699 | 0.96037
16h30 | 184.45 | 171.47 | 99.78 | 85.63 | 68.91 | 16h30 | 2.3056 | 2.1434 | 1.2472 | 1.0704 | 0.86138
17h30 | 171.42 | 159.56 | 92.12 | 77.15 | 62.08 | 17h30 | 2.1427 | 1.9945 | 1.1515 | 0.96437 | 0.776
18h30 | 180.35 | 168.84 | 100.18 | 84.2 | 69.94 | 18h30 | 2.2544 | 2.1105 | 1.2523 | 1.0525 | 0.87425
19h30 | 172.52 | 160.28 | 96.64 | 81.65 | 68.72 | 19h30 | 2.1565 | 2.0035 | 1.208 | 1.0206 | 0.859
20h30 | 177.36 | 164.09 | 99.02 | 85.87 | 73.28 | 20h30 | 2.217 | 2.0511 | 1.2377 | 1.0734 | 0.916
21h30 | 198.22 | 184.56 | 116.9 | 104.5 | 90.83 | 21h30 | 2.4777 | 2.307 | 1.4612 | 1.3062 | 1.1354
22h30 | 192.96 | 179.78 | 109.02 | 96.41 | 83.56 | 22h30 | 2.412 | 2.2473 | 1.3627 | 1.2051 | 1.0445
23h30 | 167.32 | 152.07 | 92.14 | 79.27 | 67.92 | 23h30 | 2.0915 | 1.9009 | 1.1518 | 0.99087 | 0.849
00h30 | 141.6 | 126.85 | 80.33 | 68.45 | 55.63 | 00h30 | 1.77 | 1.5856 | 1.0041 | 0.85562 | 0.69537
01h30 | 143.54 | 130.61 | 78.1 | 64.03 | 52.52 | 01h30 | 1.7942 | 1.6326 | 0.97625 | 0.80037 | 0.6565
02h30 | 147.93 | 134.29 | 80.7 | 65.77 | 54.1 | 02h30 | 1.8491 | 1.6786 | 1.0088 | 0.82212 | 0.67625
03h30 | 146.03 | 130.93 | 78.65 | 64.3 | 53.2 | 03h30 | 1.8254 | 1.6366 | 0.98313 | 0.80375 | 0.665
04h30 | 145.71 | 129.2 | 78.43 | 64.57 | 53.74 | 04h30 | 1.8214 | 1.615 | 0.98037 | 0.80712 | 0.67175
05h30 | 145.11 | 127.13 | 77.68 | 64.16 | 53.57 | 05h30 | 1.8139 | 1.5891 | 0.971 | 0.802 | 0.66963
06h30 | 133.17 | 114.76 | 75.3 | 62.15 | 51.45 | 06h30 | 1.6646 | 1.4345 | 0.94125 | 0.77687 | 0.64312
07h30 | 144.31 | 123.8 | 77.34 | 67.58 | 57.76 | 07h30 | 1.8039 | 1.5475 | 0.96675 | 0.84475 | 0.722
08h30 | 152.41 | 128.66 | 77.34 | 67.58 | 57.76 | 08h30 | 1.9051 | 1.6082 | 0.96675 | 0.84475 | 0.722
09h30 | 164.42 | 141.14 | 84.4 | 73.15 | 60.71 | 09h30 | 2.0553 | 1.7643 | 1.055 | 0.91438 | 0.75887
10h30 | 163.42 | 142.77 | 84.4 | 73.15 | 60.71 | 10h30 | 2.0427 | 1.7846 | 1.055 | 0.91438 | 0.75887
11h30 | 156.24 | 137.21 | 80.83 | 67.59 | 54.1 | 11h30 | 1.953 | 1.7151 | 1.0104 | 0.84488 | 0.67625
12h30 | 154.75 | 136.06 | 80.83 | 67.59 | 54.1 | 12h30 | 1.9344 | 1.7007 | 1.0104 | 0.84488 | 0.67625
13h30 | 161.46 | 143.88 | 85.07 | 71.37 | 56.7 | 13h30 | 2.0183 | 1.7985 | 1.0634 | 0.89212 | 0.70875
14h30 | 158.56 | 143.15 | 85.07 | 71.37 | 56.7 | 14h30 | 1.982 | 1.7894 | 1.0634 | 0.89212 | 0.70875
15h30 | 147.02 | 132.93 | 75.68 | 62.35 | 46.61 | 15h30 | 1.8377 | 1.6616 | 0.946 | 0.77938 | 0.58262
16h30 | 140.03 | 126.37 | 75.68 | 62.35 | 46.61 | 16h30 | 1.7504 | 1.5796 | 0.946 | 0.77938 | 0.58262
17h30 | 140.3 | 127.33 | 73.5 | 59.08 | 45.04 | 17h30 | 1.7537 | 1.5916 | 0.91875 | 0.7385 | 0.563
18h30 | 152.49 | 139.55 | 82.79 | 68.14 | 54.61 | 18h30 | 1.9061 | 1.7444 | 1.0349 | 0.85175 | 0.68263
19h30 | 158.73 | 144.77 | 87.25 | 73.13 | 60.55 | 19h30 | 1.9841 | 1.8096 | 1.0906 | 0.91412 | 0.75687
20h30 | 139.52 | 124.72 | 77.96 | 64.07 | 51.55 | 20h30 | 1.744 | 1.559 | 0.9745 | 0.80088 | 0.64438
21h30 | 116.12 | 100.94 | 61.03 | 48.98 | 40.04 | 21h30 | 1.4515 | 1.2617 | 0.76287 | 0.61225 | 0.5005
22h30 | 115.34 | 99.78 | 61.03 | 49.18 | 40.46 | 22h30 | 1.4418 | 1.2472 | 0.76287 | 0.61475 | 0.50575
23h30 | 124.76 | 108.67 | 66.04 | 54.51 | 45.66 | 23h30 | 1.5595 | 1.3584 | 0.8255 | 0.68137 | 0.57075
00h30 | 107.09 | 92.39 | 66.04 | 54.31 | 44.67 | 00h30 | 1.3386 | 1.1549 | 0.8255 | 0.67888 | 0.55837
01h30 | 110.91 | 98.16 | 57.3 | 44.58 | 35.6 | 01h30 | 1.3864 | 1.227 | 0.71625 | 0.55725 | 0.445
02h30 | 114.62 | 101.36 | 61.71 | 47.38 | 38.1 | 02h30 | 1.4327 | 1.267 | 0.77138 | 0.59225 | 0.47625
03h30 | 113.6 | 98.89 | 60.21 | 45.53 | 36.86 | 03h30 | 1.42 | 1.2361 | 0.75262 | 0.56912 | 0.46075
04h30 | 109.26 | 93.12 | 57.21 | 43.26 | 35.15 | 04h30 | 1.3658 | 1.164 | 0.71513 | 0.54075 | 0.43938
05h30 | 108.76 | 91.08 | 56.44 | 42.91 | 35.03 | 05h30 | 1.3595 | 1.1385 | 0.7055 | 0.53638 | 0.43788
06h30 | 96.39 | 78.19 | 55.04 | 42.37 | 34.24 | 06h30 | 1.2049 | 0.97737 | 0.688 | 0.52963 | 0.428
07h30 | 94.84 | 75.48 | 47.23 | 37.08 | 30.78 | 07h30 | 1.1855 | 0.9435 | 0.59037 | 0.4635 | 0.38475
08h30 | 82.36 | 74.02 | 47.23 | 37.08 | 30.78 | 08h30 | 1.0295 | 0.92525 | 0.59037 | 0.4635 | 0.38475
09h30 | 74.45 | 55.32 | 27.13 | 19.14 | 11.03 | 09h30 | 0.93063 | 0.6915 | 0.33913 | 0.23925 | 0.13787
10h30 | 70.34 | 55.32 | 27.13 | 19.14 | 11.03 | 10h30 | 0.87925 | 0.6915 | 0.33913 | 0.23925 | 0.13787
11h30 | 68.5 | 51.58 | 25.13 | 12.89 | 4.73 | 11h30 | 0.85625 | 0.64475 | 0.31412 | 0.16112 | 0.059125
12h30 | 74.97 | 58.83 | 30.45 | 18.56 | 9.71 | 12h30 | 0.93712 | 0.73538 | 0.38062 | 0.232 | 0.12137
13h30 | 81.14 | 65.84 | 34.3 | 23.23 | 13.49 | 13h30 | 1.0143 | 0.823 | 0.42875 | 0.29037 | 0.16862
14h30 | 81.09 | 66.69 | 32.96 | 23.56 | 12.9 | 14h30 | 1.0136 | 0.83362 | 0.412 | 0.2945 | 0.16125
15h30 | 79.9 | 65.38 | 30.26 | 21.37 | 10.42 | 15h30 | 0.99875 | 0.81725 | 0.37825 | 0.26713 | 0.13025
16h30 | 85.95 | 71.35 | 33.43 | 23.98 | 12.81 | 16h30 | 1.0744 | 0.89187 | 0.41787 | 0.29975 | 0.16012
17h30 | 104.28 | 91.31 | 47.14 | 36.73 | 24.71 | 17h30 | 1.3035 | 1.1414 | 0.58925 | 0.45913 | 0.30888
18h30 | 128.24 | 117.81 | 66.46 | 53.86 | 41.57 | 18h30 | 1.603 | 1.4726 | 0.83075 | 0.67325 | 0.51963
19h30 | 127.27 | 118.05 | 69.48 | 55.31 | 43.95 | 19h30 | 1.5909 | 1.4756 | 0.8685 | 0.69137 | 0.54937
20h30 | 96.22 | 86.89 | 51.33 | 38.69 | 29.66 | 20h30 | 1.2027 | 1.0861 | 0.64163 | 0.48363 | 0.37075
21h30 | 69.03 | 59.39 | 34.63 | 23.5 | 16.85 | 21h30 | 0.86287 | 0.74238 | 0.43288 | 0.29375 | 0.21063
22h30 | 78.85 | 68.66 | 40.75 | 29.16 | 22.33 | 22h30 | 0.98562 | 0.85825 | 0.50938 | 0.3645 | 0.27913
23h30 | 94.13 | 82.88 | 49.81 | 38.16 | 30.63 | 23h30 | 1.1766 | 1.036 | 0.62262 | 0.477 | 0.38288
00h30 | 78.93 | 67 | 36.04 | 23.4 | 15.79 | 00h30 | 0.98662 | 0.8375 | 0.4505 | 0.2925 | 0.19737
01h30 | 78.13 | 68.66 | 40.76 | 25.56 | 17.94 | 01h30 | 0.97662 | 0.85825 | 0.5095 | 0.3195 | 0.22425
02h30 | 78.13 | 65.87 | 40.08 | 25.56 | 17.94 | 02h30 | 0.97662 | 0.82337 | 0.501 | 0.3195 | 0.22425
03h30 | 52.34 | 40.88 | 24.03 | 10.35 | 5 | 03h30 | 0.65425 | 0.511 | 0.30038 | 0.12937 | 0.0625
04h30 | 52.34 | 40.88 | 24.03 | 10.35 | 5 | 04h30 | 0.65425 | 0.511 | 0.30038 | 0.12937 | 0.0625
05h30 | 48.62 | 32.5 | 20.9 | 7.96 | 3.41 | 05h30 | 0.60775 | 0.40625 | 0.26125 | 0.0995 | 0.042625
06h30 | 57.43 | 41.43 | 25.96 | 12.94 | 7.73 | 06h30 | 0.71788 | 0.51787 | 0.3245 | 0.16175 | 0.096625
07h30 | 68.64 | 52.08 | 35.42 | 23.83 | 18.75 | 07h30 | 0.858 | 0.651 | 0.44275 | 0.29788 | 0.23438
08h30 | 59.83 | 43.14 | 30.37 | 18.85 | 14.43 | 08h30 | 0.74787 | 0.53925 | 0.37962 | 0.23563 | 0.18038
09h30 | 9.53 | 0 | 0 | 0 | 0 | 09h30 | 0.11912 | 0 | 0 | 0 | 0
10h30 | 52.53 | 31.61 | 15.74 | 0 | 0 | 10h30 | 0.65663 | 0.39513 | 0.19675 | 0 | 0
11h30 | 96.53 | 80.24 | 46.74 | 29.76 | 21.23 | 11h30 | 1.2066 | 1.003 | 0.58425 | 0.372 | 0.26538
12h30 | 97.88 | 80.96 | 47.07 | 31.76 | 22.72 | 12h30 | 1.2235 | 1.012 | 0.58837 | 0.397 | 0.284
13h30 | 92.81 | 76.64 | 43.7 | 29.25 | 19.44 | 13h30 | 1.1601 | 0.958 | 0.54625 | 0.36562 | 0.243
14h30 | 87.53 | 72.32 | 39.58 | 27.26 | 17.95 | 14h30 | 1.0941 | 0.904 | 0.49475 | 0.34075 | 0.22437
15h30 | 42.16 | 28 | 11.95 | 0 | 0 | 15h30 | 0.527 | 0.35 | 0.14938 | 0 | 0
16h30 | 43.53 | 28.22 | 10.7 | 0 | 0 | 16h30 | 0.54412 | 0.35275 | 0.13375 | 0 | 0
17h30 | 103.29 | 89.25 | 49.34 | 32.69 | 23.09 | 17h30 | 1.2911 | 1.1156 | 0.61675 | 0.40863 | 0.28863
18h30 | 131.78 | 119.09 | 70.73 | 52.24 | 41.25 | 18h30 | 1.6473 | 1.4886 | 0.88413 | 0.653 | 0.51562
19h30 | 136.55 | 123.71 | 75.62 | 57.39 | 46.33 | 19h30 | 1.7069 | 1.5464 | 0.94525 | 0.71737 | 0.57913
20h30 | 121.1 | 107.46 | 66.59 | 49.3 | 39.96 | 20h30 | 1.5137 | 1.3433 | 0.83237 | 0.61625 | 0.4995
21h30 | 105.08 | 90.52 | 56.75 | 40.05 | 32.02 | 21h30 | 1.3135 | 1.1315 | 0.70937 | 0.50062 | 0.40025
22h30 | 90.44 | 74.81 | 47.42 | 31.61 | 24.65 | 22h30 | 1.1305 | 0.93512 | 0.59275 | 0.39513 | 0.30812
23h30 | 76.1 | 59.5 | 38.43 | 23.06 | 17.17 | 23h30 | 0.95125 | 0.74375 | 0.48037 | 0.28825 | 0.21463
00h30 | 51.3 | 36.02 | 24.7 | 20.03 | 12.75 | 00h30 | 0.64125 | 0.45025 | 0.30875 | 0.25038 | 0.15937
01h30 | 37.25 | 23.64 | 14.57 | 0 | 0 | 01h30 | 0.46563 | 0.2955 | 0.18213 | 0 | 0
02h30 | 39.81 | 25.16 | 17.26 | 0 | 0 | 02h30 | 0.49762 | 0.3145 | 0.21575 | 0 | 0
03h30 | 57.88 | 41.55 | 26.59 | 9.84 | 4.04 | 03h30 | 0.7235 | 0.51938 | 0.33237 | 0.123 | 0.0505
04h30 | 56.38 | 38.47 | 24.77 | 9.84 | 4.23 | 04h30 | 0.70475 | 0.48087 | 0.30962 | 0.123 | 0.052875
05h30 | 60.92 | 41.37 | 27.04 | 11.84 | 6.31 | 05h30 | 0.7615 | 0.51712 | 0.338 | 0.148 | 0.078875
06h30 | 55.91 | 40.31 | 26.16 | 11.84 | 6.12 | 06h30 | 0.69888 | 0.50387 | 0.327 | 0.148 | 0.0765
07h30 | 54.34 | 30.34 | 22.33 | 11.53 | 7.45 | 07h30 | 0.67925 | 0.37925 | 0.27913 | 0.14413 | 0.093125
08h30 | 44.27 | 30.34 | 22.33 | 11.53 | 7.45 | 08h30 | 0.55337 | 0.37925 | 0.27913 | 0.14413 | 0.093125
09h30 | 19.25 | 0 | 0 | 0 | 0 | 09h30 | 0.24063 | 0 | 0 | 0 | 0
10h30 | 28.13 | 5.79 | 0 | 0 | 0 | 10h30 | 0.35163 | 0.072375 | 0 | 0 | 0
11h30 | 48.26 | 29.75 | 13.47 | 0 | 0 | 11h30 | 0.60325 | 0.37188 | 0.16837 | 0 | 0
12h30 | 89.4 | 69.83 | 39.04 | 27.46 | 16.36 | 12h30 | 1.1175 | 0.87287 | 0.488 | 0.34325 | 0.2045
13h30 | 118.92 | 100.29 | 57.54 | 42.3 | 30.68 | 13h30 | 1.4865 | 1.2536 | 0.71925 | 0.52875 | 0.3835
14h30 | 127.09 | 109.63 | 63.12 | 48.32 | 34.53 | 14h30 | 1.5886 | 1.3704 | 0.789 | 0.604 | 0.43162
15h30 | 134.53 | 117.92 | 68.46 | 53.71 | 39.27 | 15h30 | 1.6816 | 1.474 | 0.85575 | 0.67138 | 0.49088
16h30 | 151 | 134.71 | 79.37 | 64.88 | 49.56 | 16h30 | 1.8875 | 1.6839 | 0.99213 | 0.811 | 0.6195
17h30 | 162.06 | 145.61 | 86.81 | 72.77 | 57.32 | 17h30 | 2.0257 | 1.8201 | 1.0851 | 0.90963 | 0.7165
18h30 | 163.41 | 146.32 | 88.06 | 74.26 | 59.48 | 18h30 | 2.0426 | 1.829 | 1.1007 | 0.92825 | 0.7435
19h30 | 165.62 | 147.99 | 89.74 | 75.93 | 61.67 | 19h30 | 2.0703 | 1.8499 | 1.1218 | 0.94912 | 0.77087
20h30 | 170.22 | 152.43 | 92.99 | 78.88 | 64.87 | 20h30 | 2.1277 | 1.9054 | 1.1624 | 0.986 | 0.81088
21h30 | 180.61 | 165.3 | 101.13 | 86.87 | 72.49 | 21h30 | 2.2576 | 2.0663 | 1.2641 | 1.0859 | 0.90612
22h30 | 177.93 | 160.35 | 98.49 | 84.16 | 70.63 | 22h30 | 2.2241 | 2.0044 | 1.2311 | 1.052 | 0.88287
23h30 | 161.73 | 142.99 | 88.54 | 73.72 | 61.74 | 23h30 | 2.0216 | 1.7874 | 1.1067 | 0.9215 | 0.77175
00h30 | 148.91 | 132.28 | 77.1 | 62.99 | 49.54 | 00h30 | 1.8614 | 1.6535 | 0.96375 | 0.78738 | 0.61925
01h30 | 165.11 | 153.13 | 93.31 | 77.58 | 62.27 | 01h30 | 2.0639 | 1.9141 | 1.1664 | 0.96975 | 0.77838
02h30 | 185.94 | 171.73 | 105.08 | 87.08 | 70.89 | 02h30 | 2.3243 | 2.1466 | 1.3135 | 1.0885 | 0.88613
03h30 | 185.94 | 180.08 | 110.9 | 93.85 | 76.89 | 03h30 | 2.3243 | 2.251 | 1.3862 | 1.1731 | 0.96113
04h30 | 166.27 | 151.38 | 93.61 | 77.27 | 62.67 | 04h30 | 2.0784 | 1.8922 | 1.1701 | 0.96588 | 0.78338
05h30 | 166.27 | 150.1 | 93.09 | 77.09 | 63 | 05h30 | 2.0784 | 1.8762 | 1.1636 | 0.96362 | 0.7875
06h30 | 196.82 | 177.22 | 109.39 | 93.96 | 77.39 | 06h30 | 2.4602 | 2.2153 | 1.3674 | 1.1745 | 0.96737
07h30 | 196.82 | 178.5 | 122.99 | 109.51 | 92.69 | 07h30 | 2.4602 | 2.2313 | 1.5374 | 1.3689 | 1.1586
08h30 | 194.94 | 172.31 | 109.39 | 95.14 | 79.09 | 08h30 | 2.4367 | 2.1539 | 1.3674 | 1.1892 | 0.98862
09h30 | 194.94 | 172.17 | 107.04 | 91.25 | 74.69 | 09h30 | 2.4367 | 2.1521 | 1.338 | 1.1406 | 0.93363
10h30 | 200 | 181.32 | 110.67 | 96.25 | 77.62 | 10h30 | 2.5 | 2.2665 | 1.3834 | 1.2031 | 0.97025
11h30 | 200 | 181.46 | 113.03 | 99.75 | 79.32 | 11h30 | 2.5 | 2.2683 | 1.4129 | 1.2469 | 0.9915
12h30 | 200 | 183.31 | 111.7 | 98.98 | 78.14 | 12h30 | 2.5 | 2.2914 | 1.3962 | 1.2372 | 0.97675
13h30 | 197.77 | 179.11 | 107.79 | 95.35 | 74.89 | 13h30 | 2.4721 | 2.2389 | 1.3474 | 1.1919 | 0.93612
14h30 | 190.54 | 171.52 | 102.8 | 90.75 | 70.95 | 14h30 | 2.3817 | 2.144 | 1.285 | 1.1344 | 0.88687
15h30 | 173.7 | 155.31 | 93.04 | 81.23 | 63.01 | 15h30 | 2.1713 | 1.9414 | 1.163 | 1.0154 | 0.78763
16h30 | 159.53 | 141.72 | 85.13 | 73.39 | 56.61 | 16h30 | 1.9941 | 1.7715 | 1.0641 | 0.91738 | 0.70762
17h30 | 145.19 | 127.69 | 77.03 | 65.54 | 50.34 | 17h30 | 1.8149 | 1.5961 | 0.96288 | 0.81925 | 0.62925
18h30 | 123.48 | 106.21 | 64.49 | 53.17 | 41.95 | 18h30 | 1.5435 | 1.3276 | 0.80612 | 0.66463 | 0.52438
19h30 | 106.87 | 89.86 | 55.1 | 43.5 | 33.53 | 19h30 | 1.3359 | 1.1233 | 0.68875 | 0.54375 | 0.41913
20h30 | 96.91 | 80.18 | 49.57 | 37.76 | 33.53 | 20h30 | 1.2114 | 1.0023 | 0.61962 | 0.472 | 0.41913
21h30 | 98.77 | 82.24 | 51.08 | 38.98 | 29.76 | 21h30 | 1.2346 | 1.028 | 0.6385 | 0.48725 | 0.372
22h30 | 107.38 | 90.9 | 56.77 | 43.98 | 35.53 | 22h30 | 1.3422 | 1.1362 | 0.70962 | 0.54975 | 0.44412
23h30 | 113.14 | 96.6 | 60.72 | 47.35 | 38.78 | 23h30 | 1.4143 | 1.2075 | 0.759 | 0.59188 | 0.48475
00h30 | 94.5 | 79.25 | 54.04 | 37.62 | 33.01 | 00h30 | 1.1812 | 0.99062 | 0.6755 | 0.47025 | 0.41263
01h30 | 96.99 | 83.97 | 50.4 | 39.19 | 29.94 | 01h30 | 1.2124 | 1.0496 | 0.63 | 0.48988 | 0.37425
02h30 | 99.07 | 85.92 | 52.72 | 40.23 | 30.59 | 02h30 | 1.2384 | 1.074 | 0.659 | 0.50287 | 0.38238
03h30 | 93.95 | 79.22 | 49 | 36.95 | 27.8 | 03h30 | 1.1744 | 0.99025 | 0.6125 | 0.46187 | 0.3475
04h30 | 90.32 | 74.57 | 46.69 | 35.91 | 27.15 | 04h30 | 1.129 | 0.93212 | 0.58362 | 0.44888 | 0.33937
05h30 | 95.43 | 78.82 | 49.29 | 37.69 | 29.03 | 05h30 | 1.1929 | 0.98525 | 0.61613 | 0.47113 | 0.36288
06h30 | 92.51 | 75.77 | 49.29 | 37.69 | 29.03 | 06h30 | 1.1564 | 0.94712 | 0.61613 | 0.47113 | 0.36288
07h30 | 105.76 | 87.71 | 56.55 | 47.67 | 38.67 | 07h30 | 1.322 | 1.0964 | 0.70688 | 0.59588 | 0.48337
08h30 | 106.2 | 87.51 | 56.55 | 47.67 | 38.67 | 08h30 | 1.3275 | 1.0939 | 0.70688 | 0.59588 | 0.48337
09h30 | 105.45 | 89.01 | 49.91 | 41.5 | 29.77 | 09h30 | 1.3181 | 1.1126 | 0.62387 | 0.51875 | 0.37212
10h30 | 98.75 | 84.19 | 49.91 | 41.5 | 29.77 | 10h30 | 1.2344 | 1.0524 | 0.62387 | 0.51875 | 0.37212
11h30 | 94.08 | 80.3 | 44.84 | 33.86 | 21.54 | 11h30 | 1.176 | 1.0037 | 0.5605 | 0.42325 | 0.26925
12h30 | 90.57 | 77.35 | 44.84 | 33.86 | 21.54 | 12h30 | 1.1321 | 0.96688 | 0.5605 | 0.42325 | 0.26925
13h30 | 85.55 | 73.17 | 40.75 | 29.56 | 18.02 | 13h30 | 1.0694 | 0.91463 | 0.50938 | 0.3695 | 0.22525
14h30 | 78.44 | 67.13 | 40.75 | 29.56 | 18.02 | 14h30 | 0.9805 | 0.83913 | 0.50938 | 0.3695 | 0.22525
15h30 | 68.53 | 58.11 | 30.62 | 20.54 | 10 | 15h30 | 0.85662 | 0.72637 | 0.38275 | 0.25675 | 0.125
16h30 | 63.78 | 55.59 | 30.62 | 20.54 | 10 | 16h30 | 0.79725 | 0.69488 | 0.38275 | 0.25675 | 0.125
17h30 | 70.32 | 60.08 | 33.84 | 23 | 13.21 | 17h30 | 0.879 | 0.751 | 0.423 | 0.2875 | 0.16512
18h30 | 76.57 | 65.68 | 38.18 | 27.94 | 18.12 | 18h30 | 0.95713 | 0.821 | 0.47725 | 0.34925 | 0.2265
19h30 | 75.76 | 64.42 | 37.79 | 27.82 | 18.62 | 19h30 | 0.947 | 0.80525 | 0.47237 | 0.34775 | 0.23275
20h30 | 71.1 | 59.7 | 35.19 | 25.36 | 17.04 | 20h30 | 0.88875 | 0.74625 | 0.43988 | 0.317 | 0.213
21h30 | 68.14 | 56.55 | 33.4 | 23.91 | 15.99 | 21h30 | 0.85175 | 0.70688 | 0.4175 | 0.29888 | 0.19987
22h30 | 75.12 | 63.23 | 37.41 | 28.29 | 19.85 | 22h30 | 0.939 | 0.79038 | 0.46763 | 0.35363 | 0.24813
23h30 | 88.98 | 76.71 | 45.72 | 36.38 | 27.13 | 23h30 | 1.1122 | 0.95888 | 0.5715 | 0.45475 | 0.33913
00h30 | 77.19 | 69.14 | 39.97 | 29.52 | 19.95 | 00h30 | 0.96488 | 0.86425 | 0.49962 | 0.369 | 0.24938
01h30 | 78.88 | 69.74 | 40 | 29.35 | 19.2 | 01h30 | 0.986 | 0.87175 | 0.5 | 0.36688 | 0.24
02h30 | 75.12 | 69.74 | 40 | 29.35 | 19.2 | 02h30 | 0.939 | 0.87175 | 0.5 | 0.36688 | 0.24
03h30 | 75.18 | 64.69 | 37.87 | 26.36 | 17.23 | 03h30 | 0.93975 | 0.80863 | 0.47337 | 0.3295 | 0.21538
04h30 | 78.67 | 67.17 | 40.05 | 28.67 | 19.61 | 04h30 | 0.98337 | 0.83962 | 0.50062 | 0.35837 | 0.24513
05h30 | 81.85 | 69.12 | 41.69 | 30.34 | 21.4 | 05h30 | 1.0231 | 0.864 | 0.52112 | 0.37925 | 0.2675
06h30 | 79.75 | 66.64 | 40.09 | 29.23 | 20.6 | 06h30 | 0.99687 | 0.833 | 0.50113 | 0.36538 | 0.2575
07h30 | 91.72 | 74.5 | 49.69 | 41.24 | 33.25 | 07h30 | 1.1465 | 0.93125 | 0.62113 | 0.5155 | 0.41563
08h30 | 89.22 | 74.5 | 49.1 | 40.03 | 31.68 | 08h30 | 1.1153 | 0.93125 | 0.61375 | 0.50038 | 0.396
09h30 | 100.62 | 82.65 | 49.99 | 38.12 | 28.03 | 09h30 | 1.2577 | 1.0331 | 0.62487 | 0.4765 | 0.35037
10h30 | 97.94 | 82.65 | 49.99 | 38.12 | 28.03 | 10h30 | 1.2243 | 1.0331 | 0.62487 | 0.4765 | 0.35037
11h30 | 72.7 | 56.36 | 31.19 | 22.82 | 12.43 | 11h30 | 0.90875 | 0.7045 | 0.38988 | 0.28525 | 0.15538
12h30 | 72.7 | 56.36 | 31.19 | 22.82 | 12.43 | 12h30 | 0.90875 | 0.7045 | 0.38988 | 0.28525 | 0.15538
13h30 | 64.33 | 49.05 | 26.45 | 17.26 | 7.69 | 13h30 | 0.80412 | 0.61313 | 0.33063 | 0.21575 | 0.096125
14h30 | 64.33 | 49.05 | 26.45 | 17.26 | 7.69 | 14h30 | 0.80412 | 0.61313 | 0.33063 | 0.21575 | 0.096125
15h30 | 50.39 | 36.93 | 19.71 | 10.4 | 2.02 | 15h30 | 0.62987 | 0.46163 | 0.24638 | 0.13 | 0.02525
16h30 | 52.56 | 40.05 | 21.89 | 12.82 | 4.29 | 16h30 | 0.657 | 0.50062 | 0.27363 | 0.16025 | 0.053625
17h30 | 59.28 | 47.04 | 26.45 | 17.58 | 8.51 | 17h30 | 0.741 | 0.588 | 0.33063 | 0.21975 | 0.10637
18h30 | 69.42 | 57.03 | 32.92 | 24.28 | 14.87 | 18h30 | 0.86775 | 0.71288 | 0.4115 | 0.3035 | 0.18588
19h30 | 79.7 | 67.29 | 39.6 | 30.83 | 21.23 | 19h30 | 0.99625 | 0.84113 | 0.495 | 0.38538 | 0.26538
20h30 | 79.58 | 67.22 | 39.95 | 30.99 | 21.89 | 20h30 | 0.99475 | 0.84025 | 0.49938 | 0.38738 | 0.27363
21h30 | 82 | 69.65 | 41.66 | 32.54 | 23.5 | 21h30 | 1.025 | 0.87062 | 0.52075 | 0.40675 | 0.29375
22h30 | 87.57 | 75.1 | 45.17 | 35.78 | 26.51 | 22h30 | 1.0946 | 0.93875 | 0.56463 | 0.44725 | 0.33137
23h30 | 91.56 | 78.87 | 47.69 | 37.96 | 28.62 | 23h30 | 1.1445 | 0.98587 | 0.59613 | 0.4745 | 0.35775
00h30 | 73.82 | 60.82 | 35.19 | 25.43 | 16.32 | 00h30 | 0.92275 | 0.76025 | 0.43988 | 0.31788 | 0.204
01h30 | 71.31 | 61.64 | 35.38 | 26.43 | 15.24 | 01h30 | 0.89138 | 0.7705 | 0.44225 | 0.33037 | 0.1905
02h30 | 71.31 | 61.72 | 36.03 | 26.43 | 15.24 | 02h30 | 0.89138 | 0.7715 | 0.45038 | 0.33037 | 0.1905
03h30 | 80 | 69.76 | 41.14 | 30.12 | 19.59 | 03h30 | 1 | 0.872 | 0.51425 | 0.3765 | 0.24488
04h30 | 86.35 | 75.24 | 44.9 | 34.16 | 23.39 | 04h30 | 1.0794 | 0.9405 | 0.56125 | 0.427 | 0.29237
05h30 | 86.09 | 74.11 | 44.55 | 33.95 | 23.51 | 05h30 | 1.0761 | 0.92637 | 0.55688 | 0.42438 | 0.29387
06h30 | 87.31 | 74.86 | 44.87 | 34.64 | 23.93 | 06h30 | 1.0914 | 0.93575 | 0.56088 | 0.433 | 0.29912
07h30 | 107.56 | 98.32 | 63.33 | 54.6 | 43.26 | 07h30 | 1.3445 | 1.229 | 0.79163 | 0.6825 | 0.54075
08h30 | 126.3 | 110.16 | 66.76 | 57.2 | 44.51 | 08h30 | 1.5788 | 1.377 | 0.8345 | 0.715 | 0.55637
09h30 | 126.3 | 116.04 | 70.08 | 58.97 | 45.17 | 09h30 | 1.5788 | 1.4505 | 0.876 | 0.73713 | 0.56463
10h30 | 118.23 | 104.35 | 61.93 | 52.1 | 39.7 | 10h30 | 1.4779 | 1.3044 | 0.77412 | 0.65125 | 0.49625
11h30 | 118.04 | 103.77 | 60.51 | 51.23 | 36.52 | 11h30 | 1.4755 | 1.2971 | 0.75638 | 0.64038 | 0.4565
12h30 | 109.31 | 96.88 | 60.51 | 50.77 | 36.52 | 12h30 | 1.3664 | 1.211 | 0.75638 | 0.63462 | 0.4565
13h30 | 104.83 | 92.49 | 52.74 | 43.09 | 29.46 | 13h30 | 1.3104 | 1.1561 | 0.65925 | 0.53863 | 0.36825
14h30 | 105.31 | 94.6 | 54.09 | 43.09 | 29.46 | 14h30 | 1.3164 | 1.1825 | 0.67612 | 0.53863 | 0.36825
15h30 | 93.35 | 83.72 | 46.83 | 34.58 | 21.68 | 15h30 | 1.1669 | 1.0465 | 0.58537 | 0.43225 | 0.271
16h30 | 91.44 | 82.21 | 45.92 | 34.58 | 21.68 | 16h30 | 1.143 | 1.0276 | 0.574 | 0.43225 | 0.271
17h30 | 49.4 | 40.42 | 22.44 | 8.97 | 1.36 | 17h30 | 0.6175 | 0.50525 | 0.2805 | 0.11213 | 0.017
18h30 | 41.34 | 39.83 | 22.01 | 8.97 | 1.36 | 18h30 | 0.51675 | 0.49788 | 0.27513 | 0.11213 | 0.017
19h30 | 54.92 | 32.69 | 21.73 | 10.24 | 5.89 | 19h30 | 0.6865 | 0.40863 | 0.27163 | 0.128 | 0.073625
20h30 | 128 | 116.74 | 71.73 | 56.7 | 45.74 | 20h30 | 1.6 | 1.4592 | 0.89663 | 0.70875 | 0.57175
21h30 | 159.83 | 149.24 | 91.86 | 76.99 | 63.73 | 21h30 | 1.9979 | 1.8655 | 1.1482 | 0.96237 | 0.79663
22h30 | 182.49 | 165.2 | 105.99 | 89.81 | 75.79 | 22h30 | 2.2811 | 2.065 | 1.3249 | 1.1226 | 0.94737
23h30 | 190.52 | 177.08 | 110.98 | 94.15 | 80.02 | 23h30 | 2.3815 | 2.2135 | 1.3873 | 1.1769 | 1.0003
00h30 | 160.07 | 148.34 | 87.69 | 72.62 | 58.04 | 00h30 | 2.0009 | 1.8542 | 1.0961 | 0.90775 | 0.7255
01h30 | 165.3 | 165.49 | 100.84 | 85.15 | 68.25 | 01h30 | 2.0663 | 2.0686 | 1.2605 | 1.0644 | 0.85313
02h30 | 200 | 194.23 | 118.73 | 100.89 | 82.52 | 02h30 | 2.5 | 2.4279 | 1.4841 | 1.2611 | 1.0315
03h30 | 199.53 | 188.55 | 115.67 | 98.54 | 81.39 | 03h30 | 2.4941 | 2.3569 | 1.4459 | 1.2317 | 1.0174
04h30 | 199.53 | 187.19 | 115.11 | 98.7 | 81.79 | 04h30 | 2.4941 | 2.3399 | 1.4389 | 1.2337 | 1.0224
05h30 | 181.51 | 166.88 | 103.23 | 87.14 | 71.85 | 05h30 | 2.2689 | 2.086 | 1.2904 | 1.0893 | 0.89812
06h30 | 156.79 | 140.91 | 87.92 | 71.77 | 58.5 | 06h30 | 1.9599 | 1.7614 | 1.099 | 0.89712 | 0.73125
07h30 | 175.28 | 166.06 | 108.12 | 92.79 | 79.67 | 07h30 | 2.191 | 2.0758 | 1.3515 | 1.1599 | 0.99587
08h30 | 194.28 | 175.3 | 110.73 | 93.3 | 79.74 | 08h30 | 2.4285 | 2.1913 | 1.3841 | 1.1663 | 0.99675
09h30 | 194.28 | 181.91 | 116.37 | 96.38 | 82.14 | 09h30 | 2.4285 | 2.2739 | 1.4546 | 1.2047 | 1.0268
10h30 | 116.64 | 100 | 70.88 | 57.6 | 50.8 | 10h30 | 1.458 | 1.25 | 0.886 | 0.72 | 0.635
11h30 | 30.66 | 10.59 | 9.6 | 0 | 0 | 11h30 | 0.38325 | 0.13237 | 0.12 | 0 | 0
12h30 | 30.08 | 10.59 | 10.16 | 0 | 0 | 12h30 | 0.376 | 0.13237 | 0.127 | 0 | 0
13h30 | 28.07 | 8.55 | 8.35 | 0 | 0 | 13h30 | 0.35087 | 0.10687 | 0.10437 | 0 | 0
14h30 | 26.46 | 8.55 | 7.79 | 0 | 0 | 14h30 | 0.33075 | 0.10687 | 0.097375 | 0 | 0
15h30 | 26.54 | 7.66 | 7.61 | 0 | 0 | 15h30 | 0.33175 | 0.09575 | 0.095125 | 0 | 0
16h30 | 27.67 | 9.24 | 9.05 | 0 | 0 | 16h30 | 0.34587 | 0.1155 | 0.11313 | 0 | 0
17h30 | 29.34 | 10.76 | 10.63 | 0 | 0 | 17h30 | 0.36675 | 0.1345 | 0.13287 | 0 | 0
18h30 | 31.1 | 12.35 | 12.21 | 0 | 0 | 18h30 | 0.38875 | 0.15438 | 0.15263 | 0 | 0
19h30 | 32.2 | 13.31 | 13.17 | 0 | 0 | 19h30 | 0.4025 | 0.16637 | 0.16462 | 0 | 0
20h30 | 85.75 | 66.82 | 45.63 | 20.68 | 11.73 | 20h30 | 1.0719 | 0.83525 | 0.57037 | 0.2585 | 0.14663
21h30 | 142.74 | 123.73 | 80.22 | 58.43 | 47.63 | 21h30 | 1.7842 | 1.5466 | 1.0028 | 0.73037 | 0.59537
22h30 | 143.35 | 124.14 | 80.94 | 58.9 | 48.88 | 22h30 | 1.7919 | 1.5517 | 1.0117 | 0.73625 | 0.611
23h30 | 135.49 | 116 | 76.36 | 54.24 | 45.25 | 23h30 | 1.6936 | 1.45 | 0.9545 | 0.678 | 0.56563
00h30 | 106.53 | 88.09 | 53.63 | 34.95 | 32.27 | 00h30 | 1.3316 | 1.1011 | 0.67038 | 0.43688 | 0.40337
01h30 | 64.42 | 47.51 | 31.84 | 14.92 | 7.11 | 01h30 | 0.80525 | 0.59388 | 0.398 | 0.1865 | 0.088875
02h30 | 25.85 | 18.33 | 18.36 | 13.07 | 7.11 | 02h30 | 0.32312 | 0.22912 | 0.2295 | 0.16337 | 0.088875
03h30 | 27.95 | 6.48 | 6.35 | 0 | 0 | 03h30 | 0.34937 | 0.081 | 0.079375 | 0 | 0
04h30 | 67.42 | 48.64 | 33.57 | 10.74 | 3.92 | 04h30 | 0.84275 | 0.608 | 0.41963 | 0.13425 | 0.049
05h30 | 106.53 | 86.36 | 56.22 | 38.34 | 29.34 | 05h30 | 1.3316 | 1.0795 | 0.70275 | 0.47925 | 0.36675
06h30 | 113.54 | 92.98 | 60.23 | 42.17 | 31.74 | 06h30 | 1.4192 | 1.1623 | 0.75287 | 0.52712 | 0.39675
07h30 | 146.05 | 123.38 | 83.92 | 65.68 | 55.23 | 07h30 | 1.8256 | 1.5422 | 1.049 | 0.821 | 0.69037
08h30 | 168.27 | 144.08 | 93.41 | 73.01 | 61.07 | 08h30 | 2.1034 | 1.801 | 1.1676 | 0.91263 | 0.76338
09h30 | 172.7 | 157.3 | 100.7 | 79.76 | 66.25 | 09h30 | 2.1587 | 1.9663 | 1.2588 | 0.997 | 0.82812
10h30 | 166.36 | 146.23 | 92.55 | 73.3 | 60.56 | 10h30 | 2.0795 | 1.8279 | 1.1569 | 0.91625 | 0.757
11h30 | 143.5 | 122.13 | 77.21 | 58.88 | 47.84 | 11h30 | 1.7937 | 1.5266 | 0.96513 | 0.736 | 0.598
12h30 | 128.62 | 107.53 | 67.96 | 50.27 | 41.38 | 12h30 | 1.6078 | 1.3441 | 0.8495 | 0.62838 | 0.51725
13h30 | 145.96 | 125.81 | 78.24 | 61.85 | 48.9 | 13h30 | 1.8245 | 1.5726 | 0.978 | 0.77312 | 0.61125
14h30 | 165.26 | 145.86 | 89.74 | 74.3 | 59.91 | 14h30 | 2.0657 | 1.8233 | 1.1218 | 0.92875 | 0.74887
15h30 | 152.22 | 133.39 | 82.84 | 66.33 | 53.82 | 15h30 | 1.9027 | 1.6674 | 1.0355 | 0.82913 | 0.67275
16h30 | 153.82 | 135.38 | 84.71 | 67.59 | 54.77 | 16h30 | 1.9227 | 1.6923 | 1.0589 | 0.84488 | 0.68463
17h30 | 172.36 | 164.65 | 102.69 | 85.53 | 70.98 | 17h30 | 2.1545 | 2.0581 | 1.2836 | 1.0691 | 0.88725
18h30 | 186.01 | 171.09 | 107.53 | 89.01 | 75.4 | 18h30 | 2.3251 | 2.1386 | 1.3441 | 1.1126 | 0.9425
19h30 | 173.07 | 155.82 | 99.17 | 79.94 | 67.88 | 19h30 | 2.1634 | 1.9478 | 1.2396 | 0.99925 | 0.8485
20h30 | 160.51 | 142.43 | 91.47 | 72.32 | 61.42 | 20h30 | 2.0064 | 1.7804 | 1.1434 | 0.904 | 0.76775
21h30 | 135.63 | 117.33 | 76.84 | 57.25 | 48.02 | 21h30 | 1.6954 | 1.4666 | 0.9605 | 0.71562 | 0.60025
22h30 | 108.91 | 90.57 | 61.04 | 41.35 | 38.1 | 22h30 | 1.3614 | 1.1321 | 0.763 | 0.51687 | 0.47625
23h30 | 104.9 | 86.21 | 58.58 | 38.87 | 30.05 | 23h30 | 1.3113 | 1.0776 | 0.73225 | 0.48588 | 0.37562
00h30 | 80.38 | 62.59 | 40.52 | 38.37 | 30.05 | 00h30 | 1.0048 | 0.78238 | 0.5065 | 0.47963 | 0.37562
01h30 | 82.86 | 66.31 | 43.63 | 23.49 | 18.03 | 01h30 | 1.0357 | 0.82888 | 0.54538 | 0.29363 | 0.22537
02h30 | 113.75 | 96.74 | 62.58 | 45.7 | 37.84 | 02h30 | 1.4219 | 1.2092 | 0.78225 | 0.57125 | 0.473
03h30 | 140.28 | 122.1 | 78.34 | 61.08 | 50.24 | 03h30 | 1.7535 | 1.5263 | 0.97925 | 0.7635 | 0.628
04h30 | 119.88 | 100.8 | 65.98 | 48.91 | 39.76 | 04h30 | 1.4985 | 1.26 | 0.82475 | 0.61138 | 0.497
05h30 | 100.1 | 80.22 | 53.94 | 36.81 | 29.25 | 05h30 | 1.2512 | 1.0028 | 0.67425 | 0.46013 | 0.36562
06h30 | 102.8 | 82.43 | 55.12 | 38.25 | 30.42 | 06h30 | 1.285 | 1.0304 | 0.689 | 0.47813 | 0.38025
07h30 | 116.16 | 93.8 | 66.79 | 49.21 | 42.19 | 07h30 | 1.452 | 1.1725 | 0.83488 | 0.61513 | 0.52738
08h30 | 99.6 | 75.58 | 59.03 | 37.72 | 31.69 | 08h30 | 1.245 | 0.94475 | 0.73787 | 0.4715 | 0.39613
09h30 | 64.02 | 40.83 | 30.12 | 11.61 | 6.05 | 09h30 | 0.80025 | 0.51038 | 0.3765 | 0.14513 | 0.075625
10h30 | 45.17 | 39.17 | 30.12 | 11.61 | 6.05 | 10h30 | 0.56463 | 0.48962 | 0.3765 | 0.14513 | 0.075625
11h30 | 34.73 | 7.76 | 5.15 | 0 | 0 | 11h30 | 0.43412 | 0.097 | 0.064375 | 0 | 0
12h30 | 57.07 | 36.42 | 22.72 | 7.32 | 0.28 | 12h30 | 0.71337 | 0.45525 | 0.284 | 0.0915 | 0.0035
13h30 | 42.23 | 28.66 | 17.57 | 7.32 | 0.28 | 13h30 | 0.52787 | 0.35825 | 0.21962 | 0.0915 | 0.0035
14h30 | 41.17 | 22.3 | 12.29 | 0 | 0 | 14h30 | 0.51462 | 0.27875 | 0.15363 | 0 | 0
15h30 | 77.39 | 62.85 | 35.83 | 23.75 | 14.24 | 15h30 | 0.96737 | 0.78563 | 0.44788 | 0.29688 | 0.178
16h30 | 83.61 | 70.67 | 40.34 | 27.04 | 17.35 | 16h30 | 1.0451 | 0.88338 | 0.50425 | 0.338 | 0.21688
17h30 | 70.81 | 58 | 33.43 | 19.72 | 11.27 | 17h30 | 0.88513 | 0.725 | 0.41787 | 0.2465 | 0.14088
18h30 | 84.74 | 70.69 | 42.55 | 29.21 | 20.8 | 18h30 | 1.0593 | 0.88362 | 0.53187 | 0.36512 | 0.26
19h30 | 103.58 | 88.82 | 54.67 | 42.09 | 32.75 | 19h30 | 1.2948 | 1.1102 | 0.68337 | 0.52612 | 0.40937
20h30 | 108.91 | 94.72 | 58.95 | 46 | 37.13 | 20h30 | 1.3614 | 1.184 | 0.73687 | 0.575 | 0.46413
21h30 | 113.63 | 99.67 | 62.42 | 48.93 | 40.29 | 21h30 | 1.4204 | 1.2459 | 0.78025 | 0.61162 | 0.50362
22h30 | 101.24 | 87.25 | 55.32 | 41.53 | 33.97 | 22h30 | 1.2655 | 1.0906 | 0.6915 | 0.51912 | 0.42462
23h30 | 92.96 | 78.72 | 50.67 | 36.2 | 29.73 | 23h30 | 1.162 | 0.984 | 0.63338 | 0.4525 | 0.37162
00h30 | 85.78 | 72.42 | 41.86 | 28.96 | 21.7 | 00h30 | 1.0722 | 0.90525 | 0.52325 | 0.362 | 0.27125
01h30 | 101.93 | 90.35 | 56.33 | 42.94 | 34.28 | 01h30 | 1.2741 | 1.1294 | 0.70413 | 0.53675 | 0.4285
02h30 | 104.85 | 92.77 | 58.41 | 42.85 | 34.11 | 02h30 | 1.3106 | 1.1596 | 0.73013 | 0.53563 | 0.42638
03h30 | 112.32 | 98.28 | 62.26 | 47.23 | 38.35 | 03h30 | 1.404 | 1.2285 | 0.77825 | 0.59037 | 0.47937
04h30 | 130.12 | 114.69 | 72.63 | 57.56 | 47.8 | 04h30 | 1.6265 | 1.4336 | 0.90787 | 0.7195 | 0.5975
05h30 | 137.74 | 121.11 | 76.6 | 62.01 | 51.68 | 05h30 | 1.7217 | 1.5139 | 0.9575 | 0.77512 | 0.646
06h30 | 130.14 | 112.59 | 70.91 | 57.62 | 47.2 | 06h30 | 1.6267 | 1.4074 | 0.88638 | 0.72025 | 0.59
07h30 | 140.29 | 129.75 | 85.69 | 73.29 | 63 | 07h30 | 1.7536 | 1.6219 | 1.0711 | 0.91612 | 0.7875
08h30 | 152.5 | 132.11 | 82.57 | 69.63 | 58.29 | 08h30 | 1.9062 | 1.6514 | 1.0321 | 0.87038 | 0.72862
09h30 | 152.5 | 138.18 | 84.52 | 71.5 | 58.32 | 09h30 | 1.9062 | 1.7272 | 1.0565 | 0.89375 | 0.729
10h30 | 172.76 | 154.06 | 93.29 | 80.62 | 65.19 | 10h30 | 2.1595 | 1.9258 | 1.1661 | 1.0077 | 0.81488
11h30 | 172.76 | 158.55 | 109.91 | 97.97 | 79.23 | 11h30 | 2.1595 | 1.9819 | 1.3739 | 1.2246 | 0.99038
12h30 | 200 | 192.7 | 119.97 | 109.33 | 88.18 | 12h30 | 2.5 | 2.4087 | 1.4996 | 1.3666 | 1.1022
13h30 | 200 | 192.7 | 117.76 | 107.77 | 86.05 | 13h30 | 2.5 | 2.4087 | 1.472 | 1.3471 | 1.0756
14h30 | 200 | 189.17 | 112.78 | 102.95 | 81.6 | 14h30 | 2.5 | 2.3646 | 1.4098 | 1.2869 | 1.02
15h30 | 200 | 189.17 | 115.75 | 104.95 | 83.56 | 15h30 | 2.5 | 2.3646 | 1.4469 | 1.3119 | 1.0445
16h30 | 200 | 200 | 133.79 | 122.17 | 99.56 | 16h30 | 2.5 | 2.5 | 1.6724 | 1.5271 | 1.2445
17h30 | 200 | 200 | 147.92 | 136.5 | 113.44 | 17h30 | 2.5 | 2.5 | 1.849 | 1.7063 | 1.418
18h30 | 200 | 200 | 150.26 | 138.36 | 116.38 | 18h30 | 2.5 | 2.5 | 1.8782 | 1.7295 | 1.4547
19h30 | 200 | 200 | 152.17 | 139 | 125.54 | 19h30 | 2.5 | 2.5 | 1.9021 | 1.7375 | 1.5693
20h30 | 200 | 200 | 164.58 | 151.06 | 130.43 | 20h30 | 2.5 | 2.5 | 2.0572 | 1.8882 | 1.6304
21h30 | 200 | 200 | 161.32 | 146.37 | 125.95 | 21h30 | 2.5 | 2.5 | 2.0165 | 1.8296 | 1.5744
22h30 | 200 | 200 | 154.31 | 138.52 | 119.19 | 22h30 | 2.5 | 2.5 | 1.9289 | 1.7315 | 1.4899
23h30 | 200 | 200 | 142.35 | 126.45 | 108.3 | 23h30 | 2.5 | 2.5 | 1.7794 | 1.5806 | 1.3538
00h30 | 200 | 190.91 | 115.11 | 100.84 | 84.41 | 00h30 | 2.5 | 2.3864 | 1.4389 | 1.2605 | 1.0551
01h30 | 200 | 190.91 | 115.43 | 101.69 | 84.03 | 01h30 | 2.5 | 2.3864 | 1.4429 | 1.2711 | 1.0504
02h30 | 200 | 192.07 | 116.14 | 101.56 | 81.77 | 02h30 | 2.5 | 2.4009 | 1.4518 | 1.2695 | 1.0221
03h30 | 200 | 192.07 | 118.45 | 104.33 | 84.99 | 03h30 | 2.5 | 2.4009 | 1.4806 | 1.3041 | 1.0624
04h30 | 200 | 194.94 | 119.07 | 104.96 | 86.19 | 04h30 | 2.5 | 2.4367 | 1.4884 | 1.312 | 1.0774
05h30 | 200 | 193.66 | 118.08 | 103.96 | 85.56 | 05h30 | 2.5 | 2.4207 | 1.476 | 1.2995 | 1.0695
06h30 | 200 | 197.4 | 120.43 | 106.12 | 87.55 | 06h30 | 2.5 | 2.4675 | 1.5054 | 1.3265 | 1.0944
07h30 | 200 | 198.68 | 134 | 120.27 | 108.25 | 07h30 | 2.5 | 2.4835 | 1.675 | 1.5034 | 1.3531
08h30 | 200 | 200 | 133.88 | 117.49 | 100.77 | 08h30 | 2.5 | 2.5 | 1.6735 | 1.4686 | 1.2596
09h30 | 200 | 200 | 132.53 | 114.99 | 97.18 | 09h30 | 2.5 | 2.5 | 1.6566 | 1.4374 | 1.2147
10h30 | 200 | 200 | 143.81 | 127.18 | 107.64 | 10h30 | 2.5 | 2.5 | 1.7976 | 1.5897 | 1.3455
11h30 | 200 | 200 | 141.16 | 125.42 | 106.48 | 11h30 | 2.5 | 2.5 | 1.7645 | 1.5677 | 1.331
12h30 | 200 | 192.18 | 120.7 | 105.98 | 95.26 | 12h30 | 2.5 | 2.4022 | 1.5088 | 1.3248 | 1.1907
13h30 | 188.98 | 169.21 | 101.53 | 87.99 | 73.43 | 13h30 | 2.3622 | 2.1151 | 1.2691 | 1.0999 | 0.91787
14h30 | 181.03 | 159.27 | 94.55 | 81.85 | 73.43 | 14h30 | 2.2629 | 1.9909 | 1.1819 | 1.0231 | 0.91787
15h30 | 164.3 | 143.54 | 85.78 | 73.05 | 60.22 | 15h30 | 2.0537 | 1.7942 | 1.0722 | 0.91312 | 0.75275
16h30 | 140.96 | 121.18 | 72.92 | 68.96 | 60.22 | 16h30 | 1.762 | 1.5148 | 0.9115 | 0.862 | 0.75275
17h30 | 139.09 | 119.92 | 72.93 | 57.45 | 46.33 | 17h30 | 1.7386 | 1.499 | 0.91163 | 0.71813 | 0.57913
18h30 | 148.71 | 129.96 | 79.88 | 64.86 | 52.74 | 18h30 | 1.8589 | 1.6245 | 0.9985 | 0.81075 | 0.65925
19h30 | 151.75 | 133.36 | 82.62 | 66.81 | 54.95 | 19h30 | 1.8969 | 1.667 | 1.0328 | 0.83513 | 0.68688
20h30 | 145.22 | 127.12 | 79.29 | 63.58 | 52.26 | 20h30 | 1.8153 | 1.589 | 0.99113 | 0.79475 | 0.65325
21h30 | 145.45 | 127.52 | 79.83 | 64 | 52.51 | 21h30 | 1.8181 | 1.594 | 0.99787 | 0.8 | 0.65638
22h30 | 154.86 | 137.02 | 85.85 | 69.74 | 57.42 | 22h30 | 1.9358 | 1.7127 | 1.0731 | 0.87175 | 0.71775
23h30 | 155.43 | 137.55 | 86.51 | 70.06 | 57.65 | 23h30 | 1.9429 | 1.7194 | 1.0814 | 0.87575 | 0.72062
00h30 | 134.36 | 117.6 | 72.01 | 60.14 | 49.02 | 00h30 | 1.6795 | 1.47 | 0.90012 | 0.75175 | 0.61275
01h30 | 138 | 122.73 | 75.5 | 61.44 | 49.08 | 01h30 | 1.725 | 1.5341 | 0.94375 | 0.768 | 0.6135
02h30 | 135.51 | 120.03 | 75.5 | 61.44 | 49.08 | 02h30 | 1.6939 | 1.5004 | 0.94375 | 0.768 | 0.6135
03h30 | 136.24 | 119.83 | 74.13 | 60.72 | 48.18 | 03h30 | 1.703 | 1.4979 | 0.92663 | 0.759 | 0.60225
04h30 | 148.6 | 131.52 | 81.7 | 68.14 | 54.9 | 04h30 | 1.8575 | 1.644 | 1.0212 | 0.85175 | 0.68625
05h30 | 161.98 | 144.37 | 89.72 | 75.82 | 61.71 | 05h30 | 2.0248 | 1.8046 | 1.1215 | 0.94775 | 0.77138
06h30 | 166.18 | 148.23 | 92.36 | 77.99 | 63.72 | 06h30 | 2.0772 | 1.8529 | 1.1545 | 0.97488 | 0.7965
07h30 | 174.23 | 166.07 | 110.2 | 95.74 | 82.25 | 07h30 | 2.1779 | 2.0759 | 1.3775 | 1.1967 | 1.0281
08h30 | 192.37 | 174.84 | 111.34 | 93.59 | 79.68 | 08h30 | 2.4046 | 2.1855 | 1.3918 | 1.1699 | 0.996
09h30 | 192.37 | 174.84 | 111.34 | 95.31 | 80.14 | 09h30 | 2.4046 | 2.1855 | 1.3918 | 1.1914 | 1.0017
10h30 | 195.72 | 176.14 | 110.53 | 94.28 | 79.19 | 10h30 | 2.4465 | 2.2018 | 1.3816 | 1.1785 | 0.98987
11h30 | 185.06 | 165.41 | 102.69 | 86.83 | 72.61 | 11h30 | 2.3133 | 2.0676 | 1.2836 | 1.0854 | 0.90763
12h30 | 170.41 | 151.2 | 93.35 | 80.42 | 67.4 | 12h30 | 2.1301 | 1.89 | 1.1669 | 1.0052 | 0.8425
13h30 | 162.79 | 144.28 | 88.78 | 73.6 | 61.01 | 13h30 | 2.0349 | 1.8035 | 1.1098 | 0.92 | 0.76262
14h30 | 152.47 | 134.56 | 87.59 | 73.6 | 61.01 | 14h30 | 1.9059 | 1.682 | 1.0949 | 0.92 | 0.76262
15h30 | 150.92 | 133.49 | 82.37 | 66.7 | 55.1 | 15h30 | 1.8865 | 1.6686 | 1.0296 | 0.83375 | 0.68875
16h30 | 161.25 | 144.14 | 89.31 | 73.55 | 61.48 | 16h30 | 2.0156 | 1.8017 | 1.1164 | 0.91938 | 0.7685
17h30 | 171.72 | 154.74 | 96.25 | 79.77 | 67.16 | 17h30 | 2.1465 | 1.9343 | 1.2031 | 0.99713 | 0.8395
18h30 | 176.09 | 159.15 | 99.86 | 82.86 | 70.01 | 18h30 | 2.2011 | 1.9894 | 1.2483 | 1.0357 | 0.87513
19h30 | 167.55 | 150.61 | 95.23 | 78.12 | 65.65 | 19h30 | 2.0944 | 1.8826 | 1.1904 | 0.9765 | 0.82063
20h30 | 160.89 | 143.93 | 91.5 | 74.36 | 62.2 | 20h30 | 2.0111 | 1.7991 | 1.1438 | 0.9295 | 0.7775
21h30 | 165.26 | 148.18 | 94.34 | 76.9 | 64.42 | 21h30 | 2.0657 | 1.8522 | 1.1792 | 0.96125 | 0.80525
22h30 | 172.13 | 154.82 | 98.67 | 80.83 | 68.03 | 22h30 | 2.1516 | 1.9352 | 1.2334 | 1.0104 | 0.85037
23h30 | 171.6 | 153.98 | 98.46 | 80.37 | 67.79 | 23h30 | 2.145 | 1.9247 | 1.2308 | 1.0046 | 0.84737
00h30 | 144.48 | 127.69 | 87.32 | 70.26 | 58.39 | 00h30 | 1.806 | 1.5961 | 1.0915 | 0.87825 | 0.72988
01h30 | 139.85 | 124.33 | 78.05 | 63.41 | 51.42 | 01h30 | 1.7481 | 1.5541 | 0.97562 | 0.79263 | 0.64275
02h30 | 138.48 | 122.6 | 78.05 | 63.41 | 51.42 | 02h30 | 1.731 | 1.5325 | 0.97562 | 0.79263 | 0.64275
03h30 | 146.34 | 129.41 | 80.97 | 66.8 | 54.12 | 03h30 | 1.8293 | 1.6176 | 1.0121 | 0.835 | 0.6765
04h30 | 153.72 | 136.01 | 85.51 | 71.06 | 58.52 | 04h30 | 1.9215 | 1.7001 | 1.0689 | 0.88825 | 0.7315
05h30 | 149.22 | 130.85 | 82.52 | 68.23 | 55.92 | 05h30 | 1.8653 | 1.6356 | 1.0315 | 0.85288 | 0.699
06h30 | 146.32 | 127.51 | 80.53 | 66.31 | 54.25 | 06h30 | 1.829 | 1.5939 | 1.0066 | 0.82888 | 0.67812
07h30 | 161.68 | 142.48 | 102.57 | 87.15 | 75.47 | 07h30 | 2.021 | 1.781 | 1.2821 | 1.0894 | 0.94337
08h30 | 186.06 | 164.99 | 106.98 | 89.13 | 75.95 | 08h30 | 2.3258 | 2.0624 | 1.3373 | 1.1141 | 0.94937
09h30 | 186.06 | 164.99 | 106.98 | 94.02 | 78.96 | 09h30 | 2.3258 | 2.0624 | 1.3373 | 1.1752 | 0.987
10h30 | 199.21 | 178.78 | 112.87 | 95.98 | 80.74 | 10h30 | 2.4901 | 2.2348 | 1.4109 | 1.1998 | 1.0092
11h30 | 195.95 | 175.61 | 109.22 | 92.68 | 77.69 | 11h30 | 2.4494 | 2.1951 | 1.3653 | 1.1585 | 0.97113
12h30 | 181.07 | 161.33 | 99.7 | 86.4 | 72.71 | 12h30 | 2.2634 | 2.0166 | 1.2463 | 1.08 | 0.90887
13h30 | 181.97 | 162.99 | 100.31 | 85.02 | 71.06 | 13h30 | 2.2746 | 2.0374 | 1.2539 | 1.0628 | 0.88825
14h30 | 197.64 | 184.05 | 113.26 | 97.24 | 82.29 | 14h30 | 2.4705 | 2.3006 | 1.4158 | 1.2155 | 1.0286
15h30 | 200 | 185.56 | 116.31 | 99.76 | 84.56 | 15h30 | 2.5 | 2.3195 | 1.4539 | 1.247 | 1.057
16h30 | 189.85 | 173.25 | 108.1 | 91.35 | 77.21 | 16h30 | 2.3731 | 2.1656 | 1.3513 | 1.1419 | 0.96513
17h30 | 185.63 | 168.16 | 105.16 | 88.19 | 74.41 | 17h30 | 2.3204 | 2.102 | 1.3145 | 1.1024 | 0.93012
18h30 | 183.8 | 166.3 | 104.6 | 87.22 | 73.52 | 18h30 | 2.2975 | 2.0787 | 1.3075 | 1.0902 | 0.919
19h30 | 178.77 | 161.36 | 102.24 | 84.6 | 71.25 | 19h30 | 2.2346 | 2.017 | 1.278 | 1.0575 | 0.89062
20h30 | 173.36 | 155.97 | 99.3 | 81.77 | 68.64 | 20h30 | 2.167 | 1.9496 | 1.2412 | 1.0221 | 0.858
21h30 | 170.16 | 152.7 | 97.52 | 79.82 | 67.04 | 21h30 | 2.127 | 1.9087 | 1.219 | 0.99775 | 0.838
22h30 | 174.29 | 156.66 | 100.07 | 82.29 | 69.22 | 22h30 | 2.1786 | 1.9583 | 1.2509 | 1.0286 | 0.86525
23h30 | 174.78 | 156.91 | 100.35 | 82.56 | 69.47 | 23h30 | 2.1848 | 1.9614 | 1.2544 | 1.032 | 0.86838
00h30 | 138.01 | 121.03 | 93.2 | 80.09 | 66.91 | 00h30 | 1.7251 | 1.5129 | 1.165 | 1.0011 | 0.83637
01h30 | 125.61 | 109.93 | 69.67 | 53.15 | 42.26 | 01h30 | 1.5701 | 1.3741 | 0.87087 | 0.66438 | 0.52825
02h30 | 126.04 | 110.05 | 69.67 | 55.17 | 44.31 | 02h30 | 1.5755 | 1.3756 | 0.87087 | 0.68963 | 0.55388
03h30 | 122.73 | 105.78 | 66.31 | 52.91 | 42 | 03h30 | 1.5341 | 1.3222 | 0.82888 | 0.66138 | 0.525
04h30 | 113.52 | 95.87 | 66.31 | 50.89 | 39.95 | 04h30 | 1.419 | 1.1984 | 0.82888 | 0.63613 | 0.49938
05h30 | 97.73 | 79.51 | 51.22 | 37.42 | 29.26 | 05h30 | 1.2216 | 0.99387 | 0.64025 | 0.46775 | 0.36575
06h30 | 89.31 | 70.75 | 51.22 | 37.42 | 29.26 | 06h30 | 1.1164 | 0.88438 | 0.64025 | 0.46775 | 0.36575
07h30 | 126.14 | 105.74 | 72.36 | 55.93 | 47.3 | 07h30 | 1.5768 | 1.3217 | 0.9045 | 0.69912 | 0.59125
08h30 | 134.4 | 112.64 | 73.81 | 56.3 | 47.3 | 08h30 | 1.68 | 1.408 | 0.92263 | 0.70375 | 0.59125
09h30 | 111.66 | 90.74 | 59.55 | 43.08 | 33.89 | 09h30 | 1.3958 | 1.1342 | 0.74438 | 0.5385 | 0.42362
10h30 | 112.23 | 92.11 | 59.01 | 43.22 | 34.21 | 10h30 | 1.4029 | 1.1514 | 0.73762 | 0.54025 | 0.42762
11h30 | 138.28 | 118.88 | 74.05 | 58.98 | 47.82 | 11h30 | 1.7285 | 1.486 | 0.92563 | 0.73725 | 0.59775
12h30 | 146.61 | 128 | 78.94 | 64.79 | 52.61 | 12h30 | 1.8326 | 1.6 | 0.98675 | 0.80988 | 0.65763
13h30 | 142.14 | 124.35 | 76.19 | 62.48 | 50.6 | 13h30 | 1.7768 | 1.5544 | 0.95237 | 0.781 | 0.6325
14h30 | 113.8 | 96.73 | 70.38 | 56.16 | 45.49 | 14h30 | 1.4225 | 1.2091 | 0.87975 | 0.702 | 0.56863
15h30 | 89.02 | 72.53 | 44.32 | 29.21 | 21.31 | 15h30 | 1.1127 | 0.90663 | 0.554 | 0.36512 | 0.26637
16h30 | 85.53 | 69.53 | 44.32 | 30.16 | 21.96 | 16h30 | 1.0691 | 0.86913 | 0.554 | 0.377 | 0.2745
17h30 | 97.99 | 82.35 | 50.94 | 37.91 | 28.78 | 17h30 | 1.2249 | 1.0294 | 0.63675 | 0.47387 | 0.35975
18h30 | 112.47 | 97.07 | 60.69 | 46.96 | 36.92 | 18h30 | 1.4059 | 1.2134 | 0.75862 | 0.587 | 0.4615
19h30 | 95.2 | 79.98 | 51.15 | 36.85 | 28.44 | 19h30 | 1.19 | 0.99975 | 0.63938 | 0.46063 | 0.3555
20h30 | 76.97 | 62.96 | 41.4 | 26.85 | 19.66 | 20h30 | 0.96213 | 0.787 | 0.5175 | 0.33563 | 0.24575
21h30 | 83.19 | 68.25 | 44.73 | 30.09 | 22.54 | 21h30 | 1.0399 | 0.85313 | 0.55912 | 0.37612 | 0.28175
22h30 | 105.13 | 90.16 | 58.35 | 43.16 | 34.07 | 22h30 | 1.3141 | 1.127 | 0.72937 | 0.5395 | 0.42588
23h30 | 132.21 | 117.01 | 74.78 | 59.3 | 48.28 | 23h30 | 1.6526 | 1.4626 | 0.93475 | 0.74125 | 0.6035
00h30 | 130.65 | 116.38 | 68.78 | 54.44 | 42.7 | 00h30 | 1.6331 | 1.4547 | 0.85975 | 0.6805 | 0.53375
01h30 | 131.45 | 118.5 | 73.06 | 60.22 | 47.98 | 01h30 | 1.6431 | 1.4812 | 0.91325 | 0.75275 | 0.59975
02h30 | 117.39 | 104.19 | 65.43 | 52.33 | 42.04 | 02h30 | 1.4674 | 1.3024 | 0.81788 | 0.65412 | 0.5255
03h30 | 116.78 | 102.62 | 63.9 | 51.95 | 40.1 | 03h30 | 1.4598 | 1.2828 | 0.79875 | 0.64938 | 0.50125
04h30 | 125.84 | 110.95 | 69.26 | 57.11 | 44.78 | 04h30 | 1.573 | 1.3869 | 0.86575 | 0.71388 | 0.55975
05h30 | 129.74 | 115.29 | 75.13 | 62.65 | 49.73 | 05h30 | 1.6218 | 1.4411 | 0.93912 | 0.78312 | 0.62162
06h30 | 148.84 | 133.42 | 83.86 | 70.96 | 57.39 | 06h30 | 1.8605 | 1.6678 | 1.0482 | 0.887 | 0.71737
07h30 | 148.84 | 133.42 | 109.07 | 94.78 | 81.4 | 07h30 | 1.8605 | 1.6678 | 1.3634 | 1.1847 | 1.0175
08h30 | 177.68 | 159.36 | 106.71 | 90.46 | 76.64 | 08h30 | 2.221 | 1.992 | 1.3339 | 1.1307 | 0.958
09h30 | 166 | 146.02 | 93.43 | 78.15 | 63.66 | 09h30 | 2.075 | 1.8253 | 1.1679 | 0.97688 | 0.79575
10h30 | 146.55 | 129.19 | 81.7 | 68.68 | 56.09 | 10h30 | 1.8319 | 1.6149 | 1.0212 | 0.8585 | 0.70112
11h30 | 125.72 | 110 | 64.19 | 54.19 | 41.05 | 11h30 | 1.5715 | 1.375 | 0.80237 | 0.67737 | 0.51313
12h30 | 106.82 | 92.16 | 64.19 | 54.19 | 41.05 | 12h30 | 1.3353 | 1.152 | 0.80237 | 0.67737 | 0.51313
13h30 | 105.13 | 91.87 | 50.43 | 42.4 | 30.75 | 13h30 | 1.3141 | 1.1484 | 0.63038 | 0.53 | 0.38438
14h30 | 106.21 | 95.63 | 52.37 | 43.52 | 30.75 | 14h30 | 1.3276 | 1.1954 | 0.65463 | 0.544 | 0.38438
15h30 | 101.86 | 93.14 | 50.05 | 39.9 | 24.03 | 15h30 | 1.2732 | 1.1643 | 0.62562 | 0.49875 | 0.30038
16h30 | 101.68 | 93.27 | 50.12 | 39.54 | 24.49 | 16h30 | 1.271 | 1.1659 | 0.6265 | 0.49425 | 0.30612
17h30 | 121.23 | 113.69 | 64.09 | 52.28 | 37.2 | 17h30 | 1.5154 | 1.4211 | 0.80112 | 0.6535 | 0.465
18h30 | 142.34 | 135.18 | 79.63 | 66.75 | 51.67 | 18h30 | 1.7792 | 1.6898 | 0.99538 | 0.83437 | 0.64587
19h30 | 148.91 | 140.86 | 84.53 | 72.06 | 57.99 | 19h30 | 1.8614 | 1.7608 | 1.0566 | 0.90075 | 0.72488
20h30 | 143.13 | 134.62 | 81.47 | 69.23 | 56.67 | 20h30 | 1.7891 | 1.6827 | 1.0184 | 0.86538 | 0.70837
21h30 | 128.51 | 120.04 | 73.26 | 60.65 | 49.63 | 21h30 | 1.6064 | 1.5005 | 0.91575 | 0.75813 | 0.62038
22h30 | 118.93 | 110.2 | 67.7 | 54.93 | 44.91 | 22h30 | 1.4866 | 1.3775 | 0.84625 | 0.68663 | 0.56137
23h30 | 117.72 | 108.49 | 67.01 | 53.95 | 44.2 | 23h30 | 1.4715 | 1.3561 | 0.83762 | 0.67437 | 0.5525
00h30 | 94.76 | 86.02 | 58.06 | 47.27 | 35.31 | 00h30 | 1.1845 | 1.0753 | 0.72575 | 0.59088 | 0.44138
01h30 | 81.17 | 73.76 | 44.14 | 30.9 | 21.77 | 01h30 | 1.0146 | 0.922 | 0.55175 | 0.38625 | 0.27213
02h30 | 59.44 | 62.22 | 44.14 | 30.9 | 21.77 | 02h30 | 0.743 | 0.77775 | 0.55175 | 0.38625 | 0.27213
03h30 | 54.68 | 43.3 | 24.72 | 13.29 | 6.65 | 03h30 | 0.6835 | 0.54125 | 0.309 | 0.16612 | 0.083125
04h30 | 63.67 | 52.85 | 32.94 | 20.22 | 12.81 | 04h30 | 0.79587 | 0.66063 | 0.41175 | 0.25275 | 0.16012
05h30 | 63.14 | 50.77 | 32.01 | 18.03 | 11.27 | 05h30 | 0.78925 | 0.63462 | 0.40013 | 0.22537 | 0.14088
06h30 | 58.89 | 45.49 | 28.68 | 15.71 | 9.27 | 06h30 | 0.73613 | 0.56863 | 0.3585 | 0.19637 | 0.11588
07h30 | 53.67 | 36.69 | 27.76 | 16.77 | 12.31 | 07h30 | 0.67087 | 0.45863 | 0.347 | 0.20963 | 0.15388
08h30 | 47.63 | 32.41 | 22.88 | 12.15 | 8.15 | 08h30 | 0.59537 | 0.40513 | 0.286 | 0.15188 | 0.10187
09h30 | 42.99 | 21.83 | 15.34 | 0 | 0 | 09h30 | 0.53738 | 0.27287 | 0.19175 | 0 | 0
10h30 | 77.9 | 60.64 | 37.25 | 23.69 | 16.05 | 10h30 | 0.97375 | 0.758 | 0.46563 | 0.29613 | 0.20062
11h30 | 98.59 | 82.87 | 49.44 | 37.35 | 28.41 | 11h30 | 1.2324 | 1.0359 | 0.618 | 0.46687 | 0.35513
12h30 | 103.07 | 87.37 | 51.94 | 40 | 30.07 | 12h30 | 1.2884 | 1.0921 | 0.64925 | 0.5 | 0.37588
13h30 | 96 | 80.77 | 47.33 | 36.36 | 26.21 | 13h30 | 1.2 | 1.0096 | 0.59162 | 0.4545 | 0.32762
14h30 | 87.03 | 72.8 | 41.82 | 31.31 | 20.88 | 14h30 | 1.0879 | 0.91 | 0.52275 | 0.39137 | 0.261
15h30 | 80.88 | 67.32 | 38.36 | 27.85 | 16.98 | 15h30 | 1.011 | 0.8415 | 0.4795 | 0.34813 | 0.21225
16h30 | 75.68 | 62.61 | 35.41 | 25.34 | 14.32 | 16h30 | 0.946 | 0.78263 | 0.44262 | 0.31675 | 0.179
17h30 | 74.44 | 61.39 | 34.88 | 25.28 | 14.05 | 17h30 | 0.9305 | 0.76738 | 0.436 | 0.316 | 0.17563
18h30 | 84.6 | 71.19 | 41.42 | 31.95 | 20.34 | 18h30 | 1.0575 | 0.88987 | 0.51775 | 0.39937 | 0.25425
19h30 | 91.26 | 77.77 | 46.18 | 36.32 | 25.34 | 19h30 | 1.1407 | 0.97213 | 0.57725 | 0.454 | 0.31675
20h30 | 89.55 | 76.19 | 45.86 | 35.53 | 25.57 | 20h30 | 1.1194 | 0.95237 | 0.57325 | 0.44412 | 0.31962
21h30 | 97.7 | 84.46 | 51.46 | 40.3 | 30.62 | 21h30 | 1.2212 | 1.0557 | 0.64325 | 0.50375 | 0.38275
22h30 | 118.3 | 105.01 | 64.93 | 51.9 | 41.96 | 22h30 | 1.4788 | 1.3126 | 0.81163 | 0.64875 | 0.5245
23h30 | 132.41 | 118.92 | 74.37 | 59.74 | 49.55 | 23h30 | 1.6551 | 1.4865 | 0.92963 | 0.74675 | 0.61938
00h30 | 100.75 | 88.35 | 50.75 | 38.94 | 28.52 | 00h30 | 1.2594 | 1.1044 | 0.63438 | 0.48675 | 0.3565
01h30 | 83.93 | 73.54 | 45.16 | 33.12 | 23.61 | 01h30 | 1.0491 | 0.91925 | 0.5645 | 0.414 | 0.29513
02h30 | 82.64 | 72.25 | 44.81 | 29.95 | 21.44 | 02h30 | 1.033 | 0.90312 | 0.56012 | 0.37438 | 0.268
03h30 | 89.17 | 77.17 | 48.07 | 34.26 | 25.4 | 03h30 | 1.1146 | 0.96462 | 0.60088 | 0.42825 | 0.3175
04h30 | 90.61 | 77.23 | 48.25 | 35.14 | 26.17 | 04h30 | 1.1326 | 0.96537 | 0.60313 | 0.43925 | 0.32712
05h30 | 85.4 | 70.97 | 44.49 | 31.95 | 23.48 | 05h30 | 1.0675 | 0.88713 | 0.55612 | 0.39937 | 0.2935
06h30 | 83.48 | 68.29 | 42.63 | 30.74 | 22.38 | 06h30 | 1.0435 | 0.85362 | 0.53287 | 0.38425 | 0.27975
07h30 | 106.96 | 88.77 | 59.28 | 49.05 | 40.28 | 07h30 | 1.337 | 1.1096 | 0.741 | 0.61313 | 0.5035
08h30 | 104.02 | 84.12 | 52.09 | 41.36 | 36.24 | 08h30 | 1.3002 | 1.0515 | 0.65112 | 0.517 | 0.453
09h30 | 101.46 | 83.46 | 50.1 | 38.93 | 29.17 | 09h30 | 1.2683 | 1.0433 | 0.62625 | 0.48662 | 0.36462
10h30 | 98.59 | 82.4 | 47.28 | 38.42 | 29.17 | 10h30 | 1.2324 | 1.03 | 0.591 | 0.48025 | 0.36462
11h30 | 86.7 | 72.45 | 40.17 | 31.56 | 20.51 | 11h30 | 1.0837 | 0.90563 | 0.50213 | 0.3945 | 0.25638
12h30 | 71.67 | 57.91 | 40.17 | 27.8 | 20.51 | 12h30 | 0.89587 | 0.72388 | 0.50213 | 0.3475 | 0.25638
13h30 | 64.44 | 52.52 | 25.43 | 18.58 | 8.01 | 13h30 | 0.8055 | 0.6565 | 0.31788 | 0.23225 | 0.10013
14h30 | 64.44 | 52.84 | 25.43 | 18.58 | 8.01 | 14h30 | 0.8055 | 0.6605 | 0.31788 | 0.23225 | 0.10013
15h30 | 58.91 | 48.4 | 21.35 | 12.97 | 0.6 | 15h30 | 0.73638 | 0.605 | 0.26687 | 0.16212 | 0.0075
16h30 | 58.91 | 43.39 | 21.35 | 12.97 | 0.6 | 16h30 | 0.73638 | 0.54238 | 0.26687 | 0.16212 | 0.0075
17h30 | 48.68 | 40.37 | 18.34 | 9.25 | 0 | 17h30 | 0.6085 | 0.50462 | 0.22925 | 0.11563 | 0
18h30 | 51.57 | 44.04 | 23 | 12.86 | 4.21 | 18h30 | 0.64463 | 0.5505 | 0.2875 | 0.16075 | 0.052625
19h30 | 55.11 | 48.45 | 26.82 | 16.79 | 9.03 | 19h30 | 0.68888 | 0.60562 | 0.33525 | 0.20988 | 0.11288
20h30 | 52.51 | 45.7 | 26.08 | 16.06 | 9.22 | 20h30 | 0.65638 | 0.57125 | 0.326 | 0.20075 | 0.11525
21h30 | 42.87 | 35.73 | 20.75 | 10.49 | 4.81 | 21h30 | 0.53587 | 0.44662 | 0.25938 | 0.13112 | 0.060125
22h30 | 42.58 | 34.82 | 16.83 | 7.61 | 0.41 | 22h30 | 0.53225 | 0.43525 | 0.21038 | 0.095125 | 0.005125
23h30 | 17.14 | 6.51 | 4.96 | 0 | 0 | 23h30 | 0.21425 | 0.081375 | 0.062 | 0 | 0
00h30 | 17.14 | 6.51 | 4.96 | 0 | 0 | 00h30 | 0.21425 | 0.081375 | 0.062 | 0 | 0
01h30 | 11.23 | 5.97 | 0 | 0 | 0 | 01h30 | 0.14037 | 0.074625 | 0 | 0 | 0
02h30 | 26.82 | 21.01 | 11.05 | 0 | 0 | 02h30 | 0.33525 | 0.26262 | 0.13812 | 0 | 0
03h30 | 33.63 | 25.69 | 14.24 | 1.92 | 0 | 03h30 | 0.42037 | 0.32112 | 0.178 | 0.024 | 0
04h30 | 36.67 | 27.98 | 15.99 | 3.45 | 0 | 04h30 | 0.45837 | 0.34975 | 0.19987 | 0.043125 | 0
05h30 | 40.01 | 30.43 | 17.83 | 5.45 | 0 | 05h30 | 0.50013 | 0.38038 | 0.22287 | 0.068125 | 0
06h30 | 36.02 | 26 | 14.03 | 3.93 | 0 | 06h30 | 0.45025 | 0.325 | 0.17538 | 0.049125 | 0
07h30 | 44.45 | 34.05 | 21.3 | 12.07 | 5.26 | 07h30 | 0.55563 | 0.42562 | 0.26625 | 0.15088 | 0.06575
08h30 | 37.27 | 26.63 | 12.3 | 12.07 | 5.26 | 08h30 | 0.46587 | 0.33287 | 0.15375 | 0.15088 | 0.06575
09h30 | 36.64 | 25.42 | 8.56 | 0 | 0 | 09h30 | 0.458 | 0.31775 | 0.107 | 0 | 0
10h30 | 29.18 | 19.93 | 8.56 | 0 | 0 | 10h30 | 0.36475 | 0.24913 | 0.107 | 0 | 0
11h30 | 11.56 | 0 | 0 | 0 | 0 | 11h30 | 0.1445 | 0 | 0 | 0 | 0
12h30 | 11.56 | 0 | 0 | 0 | 0 | 12h30 | 0.1445 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 7.46 | 1.82 | 0 | 0 | 0 | 20h30 | 0.09325 | 0.02275 | 0 | 0 | 0
21h30 | 7.46 | 1.82 | 0 | 0 | 0 | 21h30 | 0.09325 | 0.02275 | 0 | 0 | 0
22h30 | 8.97 | 6.56 | 0 | 0 | 0 | 22h30 | 0.11213 | 0.082 | 0 | 0 | 0
23h30 | 36.4 | 32.87 | 14.9 | 0 | 0 | 23h30 | 0.455 | 0.41087 | 0.18625 | 0 | 0
00h30 | 27.43 | 26.32 | 14.9 | 0 | 0 | 00h30 | 0.34287 | 0.329 | 0.18625 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 1.17 | 0 | 0 | 0 | 0 | 04h30 | 0.014625 | 0 | 0 | 0 | 0
05h30 | 3.28 | 0 | 0 | 0 | 0 | 05h30 | 0.041 | 0 | 0 | 0 | 0
06h30 | 24.95 | 13.81 | 4.01 | 0 | 0 | 06h30 | 0.31188 | 0.17263 | 0.050125 | 0 | 0
07h30 | 71.83 | 64.04 | 40.46 | 20.74 | 8.31 | 07h30 | 0.89787 | 0.8005 | 0.50575 | 0.25925 | 0.10387
08h30 | 85.29 | 75.8 | 44.27 | 24.46 | 11.46 | 08h30 | 1.0661 | 0.9475 | 0.55337 | 0.30575 | 0.14325
09h30 | 100.66 | 88.97 | 50.99 | 30.87 | 15.41 | 09h30 | 1.2583 | 1.1121 | 0.63738 | 0.38588 | 0.19262
10h30 | 104.25 | 92.67 | 50.83 | 32.07 | 16.34 | 10h30 | 1.3031 | 1.1584 | 0.63538 | 0.40087 | 0.20425
11h30 | 110.48 | 98.11 | 52.84 | 34.78 | 18.86 | 11h30 | 1.381 | 1.2264 | 0.6605 | 0.43475 | 0.23575
12h30 | 114.2 | 101.45 | 54.69 | 37.1 | 21.08 | 12h30 | 1.4275 | 1.2681 | 0.68363 | 0.46375 | 0.2635
13h30 | 110.04 | 97.2 | 51.52 | 35.32 | 19.37 | 13h30 | 1.3755 | 1.215 | 0.644 | 0.4415 | 0.24213
14h30 | 109.05 | 96.27 | 50.91 | 34.81 | 19.07 | 14h30 | 1.3631 | 1.2034 | 0.63638 | 0.43512 | 0.23838
15h30 | 107.88 | 95.88 | 52.07 | 34.74 | 20.16 | 15h30 | 1.3485 | 1.1985 | 0.65087 | 0.43425 | 0.252
16h30 | 106.88 | 95.82 | 53.34 | 36.45 | 22.35 | 16h30 | 1.336 | 1.1978 | 0.66675 | 0.45563 | 0.27937
17h30 | 102.55 | 91.96 | 51.82 | 35.95 | 22.45 | 17h30 | 1.2819 | 1.1495 | 0.64775 | 0.44938 | 0.28063
18h30 | 95.13 | 84.71 | 48.58 | 32.42 | 20.77 | 18h30 | 1.1891 | 1.0589 | 0.60725 | 0.40525 | 0.25962
19h30 | 92.87 | 82.16 | 48.28 | 31.97 | 21.53 | 19h30 | 1.1609 | 1.027 | 0.6035 | 0.39963 | 0.26913
20h30 | 93.25 | 81.88 | 48.56 | 33.49 | 23.46 | 20h30 | 1.1656 | 1.0235 | 0.607 | 0.41863 | 0.29325
21h30 | 83.61 | 71.41 | 42.44 | 28.34 | 19.43 | 21h30 | 1.0451 | 0.89263 | 0.5305 | 0.35425 | 0.24288
22h30 | 68.83 | 55.57 | 35.23 | 21.9 | 11.52 | 22h30 | 0.86038 | 0.69463 | 0.44038 | 0.27375 | 0.144
23h30 | 68.92 | 54.43 | 33.27 | 18.01 | 11.21 | 23h30 | 0.8615 | 0.68037 | 0.41587 | 0.22512 | 0.14012
00h30 | 66.81 | 53.92 | 33.27 | 18.01 | 10.69 | 00h30 | 0.83513 | 0.674 | 0.41587 | 0.22512 | 0.13362
01h30 | 81.83 | 70.1 | 41.58 | 23.31 | 14.24 | 01h30 | 1.0229 | 0.87625 | 0.51975 | 0.29137 | 0.178
02h30 | 84.74 | 71.44 | 42.79 | 25.01 | 15.88 | 02h30 | 1.0593 | 0.893 | 0.53487 | 0.31262 | 0.1985
03h30 | 84.68 | 70.23 | 42.22 | 25.37 | 16.28 | 03h30 | 1.0585 | 0.87787 | 0.52775 | 0.31712 | 0.2035
04h30 | 88.25 | 72.59 | 44.05 | 28.03 | 19.02 | 04h30 | 1.1031 | 0.90738 | 0.55063 | 0.35037 | 0.23775
05h30 | 90.07 | 73.25 | 44.72 | 29.14 | 20.33 | 05h30 | 1.1259 | 0.91563 | 0.559 | 0.36425 | 0.25412
06h30 | 86.73 | 69.07 | 41.82 | 27.29 | 18.32 | 06h30 | 1.0841 | 0.86338 | 0.52275 | 0.34113 | 0.229
07h30 | 120.82 | 103.24 | 66.8 | 54.77 | 44.3 | 07h30 | 1.5103 | 1.2905 | 0.835 | 0.68463 | 0.55375
08h30 | 144.27 | 121.03 | 73.48 | 62.49 | 50.68 | 08h30 | 1.8034 | 1.5129 | 0.9185 | 0.78112 | 0.6335
09h30 | 137.63 | 113.59 | 68.13 | 57.2 | 44.82 | 09h30 | 1.7204 | 1.4199 | 0.85162 | 0.715 | 0.56025
10h30 | 115.91 | 93.4 | 61.32 | 46.96 | 36.07 | 10h30 | 1.4489 | 1.1675 | 0.7665 | 0.587 | 0.45088
11h30 | 97.28 | 76.63 | 42.56 | 34.01 | 21.76 | 11h30 | 1.216 | 0.95788 | 0.532 | 0.42512 | 0.272
12h30 | 81.21 | 71.79 | 42.56 | 34.01 | 21.76 | 12h30 | 1.0151 | 0.89738 | 0.532 | 0.42512 | 0.272
13h30 | 77.48 | 60.91 | 30.39 | 23.4 | 10.14 | 13h30 | 0.9685 | 0.76138 | 0.37988 | 0.2925 | 0.12675
14h30 | 80.72 | 65.03 | 33.13 | 25.03 | 10.38 | 14h30 | 1.009 | 0.81288 | 0.41413 | 0.31288 | 0.12975
15h30 | 84.31 | 69.26 | 35.43 | 26.04 | 10.45 | 15h30 | 1.0539 | 0.86575 | 0.44288 | 0.3255 | 0.13062
16h30 | 90.04 | 75.82 | 40.3 | 30.66 | 15.11 | 16h30 | 1.1255 | 0.94775 | 0.50375 | 0.38325 | 0.18887
17h30 | 94.32 | 80.74 | 44.43 | 34.8 | 19.73 | 17h30 | 1.179 | 1.0092 | 0.55537 | 0.435 | 0.24663
18h30 | 101.19 | 88.06 | 49.79 | 40.39 | 25.6 | 18h30 | 1.2649 | 1.1007 | 0.62238 | 0.50487 | 0.32
19h30 | 112.8 | 99.93 | 57.71 | 48.2 | 33.29 | 19h30 | 1.41 | 1.2491 | 0.72137 | 0.6025 | 0.41613
20h30 | 126.32 | 113.48 | 66.35 | 56.86 | 41.28 | 20h30 | 1.579 | 1.4185 | 0.82937 | 0.71075 | 0.516
21h30 | 130.22 | 117.33 | 68.98 | 59.51 | 44.24 | 21h30 | 1.6278 | 1.4666 | 0.86225 | 0.74387 | 0.553
22h30 | 131.31 | 118.36 | 69.85 | 60.37 | 45.69 | 22h30 | 1.6414 | 1.4795 | 0.87313 | 0.75462 | 0.57112
23h30 | 136.94 | 131.33 | 77.89 | 68.38 | 53.19 | 23h30 | 1.7118 | 1.6416 | 0.97362 | 0.85475 | 0.66487
00h30 | 136.21 | 126.89 | 70.57 | 60.46 | 43.91 | 00h30 | 1.7026 | 1.5861 | 0.88213 | 0.75575 | 0.54888
01h30 | 136.21 | 128.14 | 76.9 | 65.08 | 47.88 | 01h30 | 1.7026 | 1.6018 | 0.96125 | 0.8135 | 0.5985
02h30 | 131.67 | 121.69 | 71.55 | 59.21 | 42.59 | 02h30 | 1.6459 | 1.5211 | 0.89438 | 0.74013 | 0.53238
03h30 | 121.82 | 111.19 | 65.1 | 53.72 | 37.88 | 03h30 | 1.5228 | 1.3899 | 0.81375 | 0.6715 | 0.4735
04h30 | 116.21 | 104.77 | 61.47 | 50.46 | 35.47 | 04h30 | 1.4526 | 1.3096 | 0.76838 | 0.63075 | 0.44338
05h30 | 108.96 | 97.02 | 57.16 | 46.26 | 32.56 | 05h30 | 1.362 | 1.2127 | 0.7145 | 0.57825 | 0.407
06h30 | 97.13 | 84.84 | 50.99 | 41.95 | 29.33 | 06h30 | 1.2141 | 1.0605 | 0.63738 | 0.52438 | 0.36662
07h30 | 111.3 | 97.85 | 61.89 | 52.44 | 40.76 | 07h30 | 1.3913 | 1.2231 | 0.77363 | 0.6555 | 0.5095
08h30 | 99.24 | 94.74 | 61.89 | 52.44 | 40.76 | 08h30 | 1.2405 | 1.1843 | 0.77363 | 0.6555 | 0.5095
09h30 | 93.39 | 77.44 | 44.58 | 31.76 | 22.79 | 09h30 | 1.1674 | 0.968 | 0.55725 | 0.397 | 0.28487
10h30 | 109.58 | 94.67 | 55.46 | 44.22 | 32.21 | 10h30 | 1.3698 | 1.1834 | 0.69325 | 0.55275 | 0.40263
11h30 | 116.22 | 102.82 | 59.39 | 48.58 | 34.84 | 11h30 | 1.4527 | 1.2853 | 0.74238 | 0.60725 | 0.4355
12h30 | 116.61 | 104.34 | 59.67 | 48.71 | 34.76 | 12h30 | 1.4576 | 1.3042 | 0.74587 | 0.60888 | 0.4345
13h30 | 118.74 | 111.47 | 62.93 | 52.79 | 37.85 | 13h30 | 1.4843 | 1.3934 | 0.78663 | 0.65987 | 0.47313
14h30 | 110.49 | 100.56 | 55 | 45.64 | 30.67 | 14h30 | 1.3811 | 1.257 | 0.6875 | 0.5705 | 0.38338
15h30 | 94.79 | 84.22 | 44.69 | 34.84 | 20.78 | 15h30 | 1.1849 | 1.0528 | 0.55863 | 0.4355 | 0.25975
16h30 | 99.51 | 89.4 | 48.72 | 37.77 | 24.05 | 16h30 | 1.2439 | 1.1175 | 0.609 | 0.47213 | 0.30062
17h30 | 111.88 | 102.51 | 57.73 | 46.98 | 32.44 | 17h30 | 1.3985 | 1.2814 | 0.72162 | 0.58725 | 0.4055
18h30 | 121.44 | 112.36 | 64.68 | 54.43 | 39.49 | 18h30 | 1.518 | 1.4045 | 0.8085 | 0.68037 | 0.49362
19h30 | 124.77 | 122.88 | 72.48 | 61.92 | 47.34 | 19h30 | 1.5596 | 1.536 | 0.906 | 0.774 | 0.59175
20h30 | 135.7 | 127.92 | 75.71 | 65.46 | 51.18 | 20h30 | 1.6963 | 1.599 | 0.94637 | 0.81825 | 0.63975
21h30 | 135.7 | 127.92 | 81.14 | 71.39 | 56.73 | 21h30 | 1.6963 | 1.599 | 1.0143 | 0.89238 | 0.70913
22h30 | 164.16 | 155.28 | 92.98 | 83.16 | 67.49 | 22h30 | 2.052 | 1.941 | 1.1623 | 1.0395 | 0.84362
23h30 | 164.16 | 155.28 | 101.47 | 90.7 | 75.48 | 23h30 | 2.052 | 1.941 | 1.2684 | 1.1338 | 0.9435
00h30 | 142.64 | 133.32 | 77.24 | 64.73 | 51.45 | 00h30 | 1.783 | 1.6665 | 0.9655 | 0.80912 | 0.64312
01h30 | 125.59 | 116.02 | 69.82 | 55.12 | 43.43 | 01h30 | 1.5699 | 1.4503 | 0.87275 | 0.689 | 0.54287
02h30 | 122.1 | 111.69 | 67.27 | 51.77 | 41 | 02h30 | 1.5263 | 1.3961 | 0.84088 | 0.64712 | 0.5125
03h30 | 121.23 | 109.76 | 66.66 | 52.24 | 41.89 | 03h30 | 1.5154 | 1.372 | 0.83325 | 0.653 | 0.52363
04h30 | 113.48 | 100.81 | 64.16 | 50.43 | 41.28 | 04h30 | 1.4185 | 1.2601 | 0.802 | 0.63038 | 0.516
05h30 | 92.43 | 78.55 | 47.79 | 35.23 | 27.16 | 05h30 | 1.1554 | 0.98188 | 0.59737 | 0.44038 | 0.3395
06h30 | 87.08 | 72.24 | 47.79 | 35.23 | 27.16 | 06h30 | 1.0885 | 0.903 | 0.59737 | 0.44038 | 0.3395
07h30 | 120.37 | 102.12 | 66.52 | 54.58 | 46.08 | 07h30 | 1.5046 | 1.2765 | 0.8315 | 0.68225 | 0.576
08h30 | 94.32 | 88.4 | 66.52 | 54.58 | 46.08 | 08h30 | 1.179 | 1.105 | 0.8315 | 0.68225 | 0.576
09h30 | 69.39 | 42.19 | 22.82 | 1.94 | 0 | 09h30 | 0.86738 | 0.52738 | 0.28525 | 0.02425 | 0
10h30 | 69.39 | 47.67 | 27.98 | 12.3 | 6.36 | 10h30 | 0.86738 | 0.59588 | 0.34975 | 0.15375 | 0.0795
11h30 | 15.26 | 5.48 | 5.16 | 10.36 | 6.36 | 11h30 | 0.19075 | 0.0685 | 0.0645 | 0.1295 | 0.0795
12h30 | 15.37 | 0 | 0 | 0 | 0 | 12h30 | 0.19212 | 0 | 0 | 0 | 0
13h30 | 12.66 | 0 | 0 | 0 | 0 | 13h30 | 0.15825 | 0 | 0 | 0 | 0
14h30 | 12.55 | 0 | 0 | 0 | 0 | 14h30 | 0.15687 | 0 | 0 | 0 | 0
15h30 | 64.94 | 50.65 | 28.25 | 2.43 | 0 | 15h30 | 0.81175 | 0.63313 | 0.35313 | 0.030375 | 0
16h30 | 126.8 | 114.32 | 67.18 | 46.93 | 34.63 | 16h30 | 1.585 | 1.429 | 0.83975 | 0.58662 | 0.43288
17h30 | 74.04 | 63.67 | 38.93 | 44.5 | 34.63 | 17h30 | 0.9255 | 0.79587 | 0.48662 | 0.55625 | 0.43288
18h30 | 15.97 | 1.44 | 1.26 | 0 | 0 | 18h30 | 0.19962 | 0.018 | 0.01575 | 0 | 0
19h30 | 52.92 | 37.86 | 24.34 | 0 | 0 | 19h30 | 0.6615 | 0.47325 | 0.30425 | 0 | 0
20h30 | 55.13 | 39.19 | 25.63 | 7.16 | 1.14 | 20h30 | 0.68912 | 0.48988 | 0.32038 | 0.0895 | 0.01425
21h30 | 49.08 | 32.83 | 22.03 | 7.16 | 1.14 | 21h30 | 0.6135 | 0.41037 | 0.27537 | 0.0895 | 0.01425
22h30 | 81.83 | 65.12 | 41.26 | 25.04 | 18.08 | 22h30 | 1.0229 | 0.814 | 0.51575 | 0.313 | 0.226
23h30 | 92.23 | 74.94 | 47.33 | 31.78 | 24.28 | 23h30 | 1.1529 | 0.93675 | 0.59162 | 0.39725 | 0.3035
00h30 | 77.28 | 61.19 | 34.19 | 18.3 | 10.47 | 00h30 | 0.966 | 0.76487 | 0.42738 | 0.22875 | 0.13087
01h30 | 84.88 | 70.84 | 43.48 | 26.49 | 18.18 | 01h30 | 1.061 | 0.8855 | 0.5435 | 0.33113 | 0.22725
02h30 | 87.51 | 73.1 | 45.13 | 27.28 | 19.24 | 02h30 | 1.0939 | 0.91375 | 0.56412 | 0.341 | 0.2405
03h30 | 75.5 | 59.41 | 37.31 | 20.67 | 13.65 | 03h30 | 0.94375 | 0.74262 | 0.46637 | 0.25838 | 0.17062
04h30 | 72.94 | 55.24 | 35.19 | 19.22 | 12.69 | 04h30 | 0.91175 | 0.6905 | 0.43988 | 0.24025 | 0.15862
05h30 | 83.7 | 64.69 | 41.08 | 25.43 | 18.43 | 05h30 | 1.0462 | 0.80863 | 0.5135 | 0.31788 | 0.23037
06h30 | 72.27 | 53.84 | 33.35 | 18.36 | 14.07 | 06h30 | 0.90338 | 0.673 | 0.41687 | 0.2295 | 0.17588
07h30 | 75.17 | 55.79 | 37.85 | 24.94 | 18.25 | 07h30 | 0.93963 | 0.69737 | 0.47313 | 0.31175 | 0.22812
08h30 | 82.07 | 58.85 | 37.4 | 23.58 | 18.25 | 08h30 | 1.0259 | 0.73562 | 0.4675 | 0.29475 | 0.22812
09h30 | 91.28 | 66.87 | 41.19 | 27.88 | 20.41 | 09h30 | 1.141 | 0.83588 | 0.51487 | 0.3485 | 0.25512
10h30 | 89.79 | 67.1 | 41.19 | 27.9 | 20.41 | 10h30 | 1.1224 | 0.83875 | 0.51487 | 0.34875 | 0.25512
11h30 | 82.97 | 62.38 | 35.78 | 24.02 | 15.68 | 11h30 | 1.0371 | 0.77975 | 0.44725 | 0.30025 | 0.196
12h30 | 74.36 | 55.5 | 35.78 | 21.53 | 15.68 | 12h30 | 0.9295 | 0.69375 | 0.44725 | 0.26913 | 0.196
13h30 | 78.04 | 60.56 | 32.76 | 20.84 | 12.18 | 13h30 | 0.9755 | 0.757 | 0.4095 | 0.2605 | 0.15225
14h30 | 87.63 | 71.12 | 40.59 | 27.44 | 17.5 | 14h30 | 1.0954 | 0.889 | 0.50738 | 0.343 | 0.21875
15h30 | 100.43 | 84.35 | 48.8 | 35.84 | 24.47 | 15h30 | 1.2554 | 1.0544 | 0.61 | 0.448 | 0.30588
16h30 | 117.18 | 101.32 | 59.21 | 47.39 | 34.9 | 16h30 | 1.4647 | 1.2665 | 0.74013 | 0.59237 | 0.43625
17h30 | 130.75 | 114.84 | 67.88 | 56.4 | 43.53 | 17h30 | 1.6344 | 1.4355 | 0.8485 | 0.705 | 0.54412
18h30 | 141.25 | 125.1 | 74.82 | 63.39 | 50.33 | 18h30 | 1.7656 | 1.5637 | 0.93525 | 0.79238 | 0.62913
19h30 | 146.07 | 138.4 | 83.56 | 71.96 | 58.51 | 19h30 | 1.8259 | 1.73 | 1.0445 | 0.8995 | 0.73137
20h30 | 162.86 | 148.95 | 90.72 | 78.23 | 64.8 | 20h30 | 2.0358 | 1.8619 | 1.134 | 0.97788 | 0.81
21h30 | 162.86 | 151.4 | 92.89 | 79.5 | 66.29 | 21h30 | 2.0358 | 1.8925 | 1.1611 | 0.99375 | 0.82862
22h30 | 170.58 | 155.49 | 95.64 | 82.06 | 68.68 | 22h30 | 2.1322 | 1.9436 | 1.1955 | 1.0257 | 0.8585
23h30 | 164.35 | 148.06 | 91.12 | 77.96 | 65.02 | 23h30 | 2.0544 | 1.8507 | 1.139 | 0.9745 | 0.81275
00h30 | 120.52 | 104.51 | 59.12 | 49.1 | 36.13 | 00h30 | 1.5065 | 1.3064 | 0.739 | 0.61375 | 0.45162
01h30 | 105.76 | 92.33 | 55.03 | 44.28 | 31.58 | 01h30 | 1.322 | 1.1541 | 0.68788 | 0.5535 | 0.39475
02h30 | 97.98 | 84.67 | 51.95 | 39.17 | 29.25 | 02h30 | 1.2248 | 1.0584 | 0.64938 | 0.48962 | 0.36562
03h30 | 84.24 | 69.63 | 42.05 | 29.51 | 19.78 | 03h30 | 1.053 | 0.87038 | 0.52563 | 0.36888 | 0.24725
04h30 | 79.52 | 63.79 | 42.05 | 29.51 | 19.78 | 04h30 | 0.994 | 0.79737 | 0.52563 | 0.36888 | 0.24725
05h30 | 80.7 | 63.92 | 38.77 | 26.89 | 18.52 | 05h30 | 1.0088 | 0.799 | 0.48462 | 0.33613 | 0.2315
06h30 | 73.69 | 63.58 | 38.77 | 26.89 | 18.52 | 06h30 | 0.92112 | 0.79475 | 0.48462 | 0.33613 | 0.2315
07h30 | 60.73 | 40.23 | 30.41 | 17.44 | 13.17 | 07h30 | 0.75913 | 0.50287 | 0.38012 | 0.218 | 0.16462
08h30 | 85.47 | 64.25 | 41.83 | 27 | 20.71 | 08h30 | 1.0684 | 0.80312 | 0.52287 | 0.3375 | 0.25888
09h30 | 131.99 | 112.23 | 70.57 | 55.15 | 45 | 09h30 | 1.6499 | 1.4029 | 0.88213 | 0.68937 | 0.5625
10h30 | 127.41 | 107.59 | 66.16 | 52.64 | 42.3 | 10h30 | 1.5926 | 1.3449 | 0.827 | 0.658 | 0.52875
11h30 | 126.68 | 107.67 | 64.96 | 52.83 | 41.75 | 11h30 | 1.5835 | 1.3459 | 0.812 | 0.66038 | 0.52187
12h30 | 123.52 | 105.31 | 62.8 | 51.29 | 39.97 | 12h30 | 1.544 | 1.3164 | 0.785 | 0.64112 | 0.49962
13h30 | 121.72 | 104.49 | 61.7 | 50.68 | 39.09 | 13h30 | 1.5215 | 1.3061 | 0.77125 | 0.6335 | 0.48862
14h30 | 116.42 | 99.93 | 58.85 | 47.77 | 36.34 | 14h30 | 1.4552 | 1.2491 | 0.73562 | 0.59713 | 0.45425
15h30 | 103.52 | 87.61 | 51.77 | 40.29 | 30.04 | 15h30 | 1.294 | 1.0951 | 0.64712 | 0.50362 | 0.3755
16h30 | 101.09 | 85.85 | 50.78 | 39.46 | 29.71 | 16h30 | 1.2636 | 1.0731 | 0.63475 | 0.49325 | 0.37138
17h30 | 99.49 | 84.63 | 50.26 | 39.01 | 29.21 | 17h30 | 1.2436 | 1.0579 | 0.62825 | 0.48762 | 0.36512
18h30 | 90.88 | 75.85 | 49.25 | 37.24 | 29.21 | 18h30 | 1.136 | 0.94812 | 0.61562 | 0.4655 | 0.36512
19h30 | 94.63 | 79.22 | 49.1 | 35.65 | 28.11 | 19h30 | 1.1829 | 0.99025 | 0.61375 | 0.44562 | 0.35137
20h30 | 91.87 | 77.3 | 49.1 | 35.65 | 28.11 | 20h30 | 1.1484 | 0.96625 | 0.61375 | 0.44562 | 0.35137
21h30 | 86.14 | 70.39 | 45.97 | 30.19 | 24.2 | 21h30 | 1.0768 | 0.87987 | 0.57463 | 0.37738 | 0.3025
22h30 | 97.1 | 81.07 | 52.77 | 36.64 | 30.2 | 22h30 | 1.2138 | 1.0134 | 0.65963 | 0.458 | 0.3775
23h30 | 88.86 | 72.32 | 47.67 | 31.62 | 25.87 | 23h30 | 1.1107 | 0.904 | 0.59588 | 0.39525 | 0.32338
00h30 | 72.74 | 61.64 | 40.87 | 25.17 | 19.88 | 00h30 | 0.90925 | 0.7705 | 0.51087 | 0.31462 | 0.2485
01h30 | 31.07 | 12.21 | 6.97 | 0 | 0 | 01h30 | 0.38838 | 0.15263 | 0.087125 | 0 | 0
02h30 | 31.07 | 12.21 | 6.97 | 0 | 0 | 02h30 | 0.38838 | 0.15263 | 0.087125 | 0 | 0
03h30 | 18.33 | 3.27 | 4.75 | 0 | 0 | 03h30 | 0.22912 | 0.040875 | 0.059375 | 0 | 0
04h30 | 30.47 | 13.32 | 10.37 | 0 | 0 | 04h30 | 0.38088 | 0.1665 | 0.12962 | 0 | 0
05h30 | 45.76 | 28.04 | 19.59 | 5.14 | 0 | 05h30 | 0.572 | 0.3505 | 0.24488 | 0.06425 | 0
06h30 | 44.08 | 26.68 | 17.59 | 5.14 | 0 | 06h30 | 0.551 | 0.3335 | 0.21987 | 0.06425 | 0
07h30 | 53.12 | 35.46 | 25.23 | 12.79 | 7.33 | 07h30 | 0.664 | 0.44325 | 0.31538 | 0.15987 | 0.091625
08h30 | 74.71 | 55.86 | 32.05 | 20.87 | 12.76 | 08h30 | 0.93388 | 0.69825 | 0.40063 | 0.26088 | 0.1595
09h30 | 91.48 | 73.34 | 42.33 | 29.63 | 19.58 | 09h30 | 1.1435 | 0.91675 | 0.52912 | 0.37038 | 0.24475
10h30 | 59.43 | 44.24 | 31.89 | 21.55 | 14.15 | 10h30 | 0.74287 | 0.553 | 0.39863 | 0.26937 | 0.17688
11h30 | 9.67 | 0 | 0 | 0 | 0 | 11h30 | 0.12087 | 0 | 0 | 0 | 0
12h30 | 51.14 | 31.32 | 15.35 | 0 | 0 | 12h30 | 0.63925 | 0.3915 | 0.19187 | 0 | 0
13h30 | 102.33 | 87.4 | 50.14 | 36.4 | 23.63 | 13h30 | 1.2791 | 1.0925 | 0.62675 | 0.455 | 0.29537
14h30 | 114.74 | 100.71 | 58.14 | 44.8 | 29.92 | 14h30 | 1.4343 | 1.2589 | 0.72675 | 0.56 | 0.374
15h30 | 115.04 | 101.7 | 58.94 | 45.75 | 30.21 | 15h30 | 1.438 | 1.2712 | 0.73675 | 0.57188 | 0.37762
16h30 | 116.85 | 103.9 | 60.67 | 47.73 | 32.96 | 16h30 | 1.4606 | 1.2988 | 0.75838 | 0.59662 | 0.412
17h30 | 119.26 | 106.25 | 62.82 | 49.85 | 36.09 | 17h30 | 1.4908 | 1.3281 | 0.78525 | 0.62313 | 0.45112
18h30 | 103.43 | 89.77 | 53.96 | 40.75 | 29.8 | 18h30 | 1.2929 | 1.1221 | 0.6745 | 0.50938 | 0.3725
19h30 | 84.57 | 70.39 | 43.32 | 29.84 | 21.31 | 19h30 | 1.0571 | 0.87987 | 0.5415 | 0.373 | 0.26637
20h30 | 85.93 | 71.65 | 44.82 | 30.92 | 22.84 | 20h30 | 1.0741 | 0.89563 | 0.56025 | 0.3865 | 0.2855
21h30 | 94.4 | 79.93 | 50.45 | 35.83 | 27.56 | 21h30 | 1.18 | 0.99913 | 0.63062 | 0.44788 | 0.3445
22h30 | 102.25 | 87.48 | 55.51 | 40.28 | 31.68 | 22h30 | 1.2781 | 1.0935 | 0.69388 | 0.5035 | 0.396
23h30 | 105.41 | 90.22 | 57.48 | 41.94 | 33.31 | 23h30 | 1.3176 | 1.1278 | 0.7185 | 0.52425 | 0.41637
00h30 | 83.05 | 68.93 | 39.18 | 35.13 | 24.92 | 00h30 | 1.0381 | 0.86162 | 0.48975 | 0.43912 | 0.3115
01h30 | 77.92 | 65.88 | 40.63 | 25.16 | 16.29 | 01h30 | 0.974 | 0.8235 | 0.50787 | 0.3145 | 0.20363
02h30 | 68.99 | 56.87 | 36.14 | 25.16 | 16.29 | 02h30 | 0.86238 | 0.71088 | 0.45175 | 0.3145 | 0.20363
03h30 | 56.22 | 42.51 | 26.84 | 11.51 | 4.85 | 03h30 | 0.70275 | 0.53138 | 0.3355 | 0.14388 | 0.060625
04h30 | 44.54 | 33.68 | 26.84 | 11.51 | 4.85 | 04h30 | 0.55675 | 0.421 | 0.3355 | 0.14388 | 0.060625
05h30 | 44.28 | 26.56 | 14.82 | 4.37 | 0 | 05h30 | 0.5535 | 0.332 | 0.18525 | 0.054625 | 0
06h30 | 61.91 | 45.2 | 28.4 | 15.93 | 9.13 | 06h30 | 0.77387 | 0.565 | 0.355 | 0.19912 | 0.11413
07h30 | 102.91 | 82.45 | 55.37 | 43.97 | 36.23 | 07h30 | 1.2864 | 1.0306 | 0.69212 | 0.54963 | 0.45288
08h30 | 117.14 | 94.66 | 60.23 | 45.99 | 37.45 | 08h30 | 1.4643 | 1.1832 | 0.75287 | 0.57488 | 0.46813
09h30 | 137.94 | 127.56 | 80.39 | 63.37 | 52.93 | 09h30 | 1.7243 | 1.5945 | 1.0049 | 0.79212 | 0.66163
10h30 | 162.84 | 145.49 | 89.26 | 75.04 | 62.9 | 10h30 | 2.0355 | 1.8186 | 1.1158 | 0.938 | 0.78625
11h30 | 156.86 | 137.97 | 83.53 | 70.64 | 57.99 | 11h30 | 1.9607 | 1.7246 | 1.0441 | 0.883 | 0.72488
12h30 | 143.27 | 124.53 | 75.03 | 62.17 | 49.57 | 12h30 | 1.7909 | 1.5566 | 0.93788 | 0.77712 | 0.61962
13h30 | 126.02 | 108.18 | 64.71 | 52.36 | 40.38 | 13h30 | 1.5753 | 1.3522 | 0.80888 | 0.6545 | 0.50475
14h30 | 109.72 | 93.2 | 54.75 | 43.02 | 31.84 | 14h30 | 1.3715 | 1.165 | 0.68437 | 0.53775 | 0.398
15h30 | 91.4 | 77 | 44.11 | 32.2 | 21.7 | 15h30 | 1.1425 | 0.9625 | 0.55137 | 0.4025 | 0.27125
16h30 | 83.07 | 69.6 | 39.8 | 27.19 | 18.35 | 16h30 | 1.0384 | 0.87 | 0.4975 | 0.33987 | 0.22937
17h30 | 84.42 | 69.92 | 40.66 | 28.81 | 19.24 | 17h30 | 1.0553 | 0.874 | 0.50825 | 0.36012 | 0.2405
18h30 | 89.87 | 74.47 | 44.09 | 33.48 | 24.04 | 18h30 | 1.1234 | 0.93088 | 0.55112 | 0.4185 | 0.3005
19h30 | 94.66 | 79.16 | 47.87 | 36.9 | 28.18 | 19h30 | 1.1832 | 0.9895 | 0.59837 | 0.46125 | 0.35225
20h30 | 101.94 | 86.49 | 53.22 | 41.36 | 32.98 | 20h30 | 1.2743 | 1.0811 | 0.66525 | 0.517 | 0.41225
21h30 | 112.07 | 96.65 | 59.97 | 47.53 | 38.99 | 21h30 | 1.4009 | 1.2081 | 0.74962 | 0.59413 | 0.48738
22h30 | 116.39 | 100.83 | 62.99 | 49.99 | 41.57 | 22h30 | 1.4549 | 1.2604 | 0.78738 | 0.62487 | 0.51963
23h30 | 114.2 | 98.35 | 62.1 | 48.15 | 40.26 | 23h30 | 1.4275 | 1.2294 | 0.77625 | 0.60188 | 0.50325
00h30 | 88 | 73.24 | 45.78 | 34.13 | 28.08 | 00h30 | 1.1 | 0.9155 | 0.57225 | 0.42662 | 0.351
01h30 | 84.94 | 72.21 | 44.73 | 31.14 | 22.69 | 01h30 | 1.0617 | 0.90263 | 0.55912 | 0.38925 | 0.28363
02h30 | 80.76 | 68.28 | 44.73 | 31.14 | 22.69 | 02h30 | 1.0095 | 0.8535 | 0.55912 | 0.38925 | 0.28363
03h30 | 79.63 | 64.63 | 41.13 | 26.33 | 19.43 | 03h30 | 0.99538 | 0.80788 | 0.51413 | 0.32913 | 0.24288
04h30 | 70.92 | 64.63 | 41.13 | 26.33 | 19.43 | 04h30 | 0.8865 | 0.80788 | 0.51413 | 0.32913 | 0.24288
05h30 | 42.45 | 22.45 | 14.71 | 3.86 | 0 | 05h30 | 0.53063 | 0.28063 | 0.18388 | 0.04825 | 0
06h30 | 39.88 | 22.45 | 14.71 | 3.86 | 0 | 06h30 | 0.4985 | 0.28063 | 0.18388 | 0.04825 | 0
07h30 | 13.07 | 0 | 0 | 0 | 0 | 07h30 | 0.16337 | 0 | 0 | 0 | 0
08h30 | 13.07 | 0 | 0 | 0 | 0 | 08h30 | 0.16337 | 0 | 0 | 0 | 0
09h30 | 18.77 | 3.39 | 0 | 0 | 0 | 09h30 | 0.23463 | 0.042375 | 0 | 0 | 0
10h30 | 33.14 | 20.01 | 3.8 | 0 | 0 | 10h30 | 0.41425 | 0.25012 | 0.0475 | 0 | 0
11h30 | 33.02 | 18.15 | 4.32 | 0 | 0 | 11h30 | 0.41275 | 0.22687 | 0.054 | 0 | 0
12h30 | 33.79 | 19.89 | 4.72 | 0 | 0 | 12h30 | 0.42238 | 0.24863 | 0.059 | 0 | 0
13h30 | 36.2 | 23.08 | 6.19 | 0 | 0 | 13h30 | 0.4525 | 0.2885 | 0.077375 | 0 | 0
14h30 | 28.69 | 15.46 | 1.99 | 0 | 0 | 14h30 | 0.35863 | 0.19325 | 0.024875 | 0 | 0
15h30 | 23.01 | 10.74 | 0 | 0 | 0 | 15h30 | 0.28763 | 0.13425 | 0 | 0 | 0
16h30 | 28.23 | 15.51 | 0 | 0 | 0 | 16h30 | 0.35287 | 0.19387 | 0 | 0 | 0
17h30 | 44.29 | 33.94 | 13.34 | 0.82 | 0 | 17h30 | 0.55363 | 0.42425 | 0.16675 | 0.01025 | 0
18h30 | 58.67 | 50.55 | 25.82 | 12.16 | 1.42 | 18h30 | 0.73337 | 0.63187 | 0.32275 | 0.152 | 0.01775
19h30 | 74.77 | 68.16 | 37.71 | 24.46 | 12.91 | 19h30 | 0.93463 | 0.852 | 0.47137 | 0.30575 | 0.16137
20h30 | 84 | 77.94 | 44.24 | 31.87 | 19.81 | 20h30 | 1.05 | 0.97425 | 0.553 | 0.39837 | 0.24763
21h30 | 68.18 | 62.19 | 35.31 | 23.17 | 12.93 | 21h30 | 0.85225 | 0.77738 | 0.44138 | 0.28963 | 0.16162
22h30 | 40.32 | 34.04 | 18.86 | 6.88 | 4.61 | 22h30 | 0.504 | 0.4255 | 0.23575 | 0.086 | 0.057625
23h30 | 16.12 | 13.76 | 4.43 | 2.45 | 0 | 23h30 | 0.2015 | 0.172 | 0.055375 | 0.030625 | 0
00h30 | 7.51 | 0 | 1.88 | 0 | 0 | 00h30 | 0.093875 | 0 | 0.0235 | 0 | 0
01h30 | 22.62 | 14.35 | 5 | 0 | 0 | 01h30 | 0.28275 | 0.17938 | 0.0625 | 0 | 0
02h30 | 22.62 | 14.35 | 5 | 0 | 0 | 02h30 | 0.28275 | 0.17938 | 0.0625 | 0 | 0
03h30 | 11.27 | 2.55 | 0 | 0 | 0 | 03h30 | 0.14088 | 0.031875 | 0 | 0 | 0
04h30 | 11.27 | 2.55 | 0 | 0 | 0 | 04h30 | 0.14088 | 0.031875 | 0 | 0 | 0
05h30 | 6.84 | 0 | 0 | 0 | 0 | 05h30 | 0.0855 | 0 | 0 | 0 | 0
06h30 | 10.53 | 0 | 0 | 0 | 0 | 06h30 | 0.13162 | 0 | 0 | 0 | 0
07h30 | 26.3 | 13.09 | 10.16 | 0 | 0 | 07h30 | 0.32875 | 0.16362 | 0.127 | 0 | 0
08h30 | 22.6 | 13.09 | 10.16 | 0 | 0 | 08h30 | 0.2825 | 0.16362 | 0.127 | 0 | 0
09h30 | 12.81 | 0 | 0 | 0 | 0 | 09h30 | 0.16012 | 0 | 0 | 0 | 0
10h30 | 29.31 | 14.75 | 2 | 0 | 0 | 10h30 | 0.36638 | 0.18438 | 0.025 | 0 | 0
11h30 | 46.11 | 33.39 | 13.02 | 1.58 | 0 | 11h30 | 0.57637 | 0.41737 | 0.16275 | 0.01975 | 0
12h30 | 58.37 | 44.24 | 17.64 | 7.57 | 0 | 12h30 | 0.72962 | 0.553 | 0.2205 | 0.094625 | 0
13h30 | 65.69 | 52.06 | 22.19 | 11.34 | 0 | 13h30 | 0.82112 | 0.65075 | 0.27737 | 0.14175 | 0
14h30 | 66.54 | 51.09 | 19.36 | 9.18 | 0 | 14h30 | 0.83175 | 0.63862 | 0.242 | 0.11475 | 0
15h30 | 63.28 | 45.75 | 11.75 | 3.84 | 0 | 15h30 | 0.791 | 0.57188 | 0.14688 | 0.048 | 0
16h30 | 58.46 | 41.9 | 7.95 | 0 | 0 | 16h30 | 0.73075 | 0.52375 | 0.099375 | 0 | 0
17h30 | 67.29 | 53.14 | 12.05 | 1.68 | 0 | 17h30 | 0.84113 | 0.66425 | 0.15063 | 0.021 | 0
18h30 | 98.2 | 86.89 | 35.5 | 24.72 | 6.88 | 18h30 | 1.2275 | 1.0861 | 0.44375 | 0.309 | 0.086
19h30 | 123 | 114.55 | 57.72 | 45.33 | 25.27 | 19h30 | 1.5375 | 1.4319 | 0.7215 | 0.56663 | 0.31588
20h30 | 113.81 | 107.53 | 57.27 | 44.37 | 26.66 | 20h30 | 1.4226 | 1.3441 | 0.71588 | 0.55463 | 0.33325
21h30 | 95.78 | 90.65 | 48.53 | 36.49 | 21.51 | 21h30 | 1.1972 | 1.1331 | 0.60662 | 0.45613 | 0.26887
22h30 | 96.67 | 91.97 | 50.25 | 38.08 | 24.13 | 22h30 | 1.2084 | 1.1496 | 0.62813 | 0.476 | 0.30162
23h30 | 102.64 | 97.93 | 54.93 | 42.05 | 28.64 | 23h30 | 1.283 | 1.2241 | 0.68663 | 0.52563 | 0.358
00h30 | 76.3 | 70.29 | 33.9 | 19.37 | 17.75 | 00h30 | 0.95375 | 0.87862 | 0.42375 | 0.24213 | 0.22187
01h30 | 60.21 | 52.81 | 26.69 | 11.39 | 0.61 | 01h30 | 0.75262 | 0.66012 | 0.33363 | 0.14238 | 0.007625
02h30 | 53.03 | 45.2 | 22.99 | 10.41 | 0.61 | 02h30 | 0.66287 | 0.565 | 0.28737 | 0.13012 | 0.007625
03h30 | 58.81 | 50.46 | 26.99 | 12.09 | 1.76 | 03h30 | 0.73513 | 0.63075 | 0.33737 | 0.15113 | 0.022
04h30 | 62.97 | 54.17 | 30.29 | 15.19 | 5.41 | 04h30 | 0.78712 | 0.67712 | 0.37862 | 0.18987 | 0.067625
05h30 | 68.64 | 59.59 | 34.06 | 18.98 | 9.11 | 05h30 | 0.858 | 0.74487 | 0.42575 | 0.23725 | 0.11388
06h30 | 70.63 | 60.74 | 33.8 | 19.93 | 9.54 | 06h30 | 0.88287 | 0.75925 | 0.4225 | 0.24913 | 0.11925
07h30 | 83.91 | 74.29 | 45.14 | 33.14 | 22.5 | 07h30 | 1.0489 | 0.92863 | 0.56425 | 0.41425 | 0.28125
08h30 | 78.59 | 68.85 | 42.1 | 29.09 | 18.41 | 08h30 | 0.98237 | 0.86062 | 0.52625 | 0.36362 | 0.23012
09h30 | 80.68 | 69.16 | 35.87 | 25.55 | 12.49 | 09h30 | 1.0085 | 0.8645 | 0.44838 | 0.31938 | 0.15613
10h30 | 85.11 | 72.52 | 36.83 | 26.73 | 12.49 | 10h30 | 1.0639 | 0.9065 | 0.46037 | 0.33413 | 0.15613
11h30 | 81.4 | 68.29 | 33.02 | 23.72 | 8.44 | 11h30 | 1.0175 | 0.85362 | 0.41275 | 0.2965 | 0.1055
12h30 | 72.4 | 59.3 | 32.05 | 22.54 | 8.44 | 12h30 | 0.905 | 0.74125 | 0.40063 | 0.28175 | 0.1055
13h30 | 64.81 | 51.7 | 22.96 | 15.17 | 0.28 | 13h30 | 0.81012 | 0.64625 | 0.287 | 0.18962 | 0.0035
14h30 | 59.81 | 46.73 | 22.96 | 15.17 | 0.28 | 14h30 | 0.74762 | 0.58413 | 0.287 | 0.18962 | 0.0035
15h30 | 66.41 | 54.13 | 24.61 | 16.19 | 1.16 | 15h30 | 0.83013 | 0.67663 | 0.30762 | 0.20237 | 0.0145
16h30 | 87.46 | 76.42 | 39.06 | 29.6 | 14.06 | 16h30 | 1.0933 | 0.95525 | 0.48825 | 0.37 | 0.17575
17h30 | 100.93 | 91.1 | 49.21 | 38.52 | 23.16 | 17h30 | 1.2616 | 1.1387 | 0.61513 | 0.4815 | 0.2895
18h30 | 106.26 | 97.38 | 54.43 | 43.12 | 28.15 | 18h30 | 1.3282 | 1.2172 | 0.68037 | 0.539 | 0.35187
19h30 | 109.77 | 101.28 | 57.78 | 46.35 | 31.86 | 19h30 | 1.3721 | 1.266 | 0.72225 | 0.57937 | 0.39825
20h30 | 99.64 | 91.1 | 52.19 | 41.01 | 27.75 | 20h30 | 1.2455 | 1.1387 | 0.65238 | 0.51262 | 0.34687
21h30 | 90.89 | 82.04 | 46.93 | 36.23 | 24.01 | 21h30 | 1.1361 | 1.0255 | 0.58662 | 0.45288 | 0.30012
22h30 | 84.63 | 75.31 | 43.02 | 32.69 | 21.26 | 22h30 | 1.0579 | 0.94137 | 0.53775 | 0.40863 | 0.26575
23h30 | 78.04 | 68.06 | 38.84 | 28.82 | 18.55 | 23h30 | 0.9755 | 0.85075 | 0.4855 | 0.36025 | 0.23187
00h30 | 62.92 | 54.01 | 28.67 | 19.68 | 7.5 | 00h30 | 0.7865 | 0.67512 | 0.35837 | 0.246 | 0.09375
01h30 | 49.28 | 39.47 | 18.98 | 7.58 | 0 | 01h30 | 0.616 | 0.49338 | 0.23725 | 0.09475 | 0
02h30 | 49.28 | 39.47 | 18.98 | 7.58 | 0 | 02h30 | 0.616 | 0.49338 | 0.23725 | 0.09475 | 0
03h30 | 48.62 | 37.61 | 19.34 | 7.68 | 0 | 03h30 | 0.60775 | 0.47013 | 0.24175 | 0.096 | 0
04h30 | 53.56 | 41.97 | 22.66 | 11.36 | 2.91 | 04h30 | 0.6695 | 0.52463 | 0.28325 | 0.142 | 0.036375
05h30 | 55.79 | 43.74 | 23.87 | 13.03 | 3.96 | 05h30 | 0.69737 | 0.54675 | 0.29838 | 0.16287 | 0.0495
06h30 | 58.79 | 46.29 | 24.89 | 14.37 | 4.78 | 06h30 | 0.73487 | 0.57862 | 0.31112 | 0.17963 | 0.05975
07h30 | 85.34 | 72.87 | 46.12 | 35.85 | 25.5 | 07h30 | 1.0668 | 0.91087 | 0.5765 | 0.44812 | 0.31875
08h30 | 100.24 | 85.44 | 50.08 | 41.04 | 28.75 | 08h30 | 1.253 | 1.068 | 0.626 | 0.513 | 0.35938
09h30 | 108.67 | 92.84 | 53.29 | 44.92 | 31.01 | 09h30 | 1.3584 | 1.1605 | 0.66612 | 0.5615 | 0.38762
10h30 | 100.2 | 86.54 | 48.1 | 39.24 | 25.27 | 10h30 | 1.2525 | 1.0817 | 0.60125 | 0.4905 | 0.31588
11h30 | 90.95 | 77.91 | 42.33 | 32.95 | 19.48 | 11h30 | 1.1369 | 0.97388 | 0.52912 | 0.41187 | 0.2435
12h30 | 82.11 | 69.27 | 39.23 | 28.42 | 18.26 | 12h30 | 1.0264 | 0.86587 | 0.49038 | 0.35525 | 0.22825
13h30 | 74.23 | 61.91 | 32.01 | 23.34 | 10.95 | 13h30 | 0.92788 | 0.77387 | 0.40013 | 0.29175 | 0.13687
14h30 | 68.7 | 57.37 | 32.01 | 23.34 | 10.95 | 14h30 | 0.85875 | 0.71713 | 0.40013 | 0.29175 | 0.13687
15h30 | 67.9 | 56.65 | 28.46 | 19.15 | 7.18 | 15h30 | 0.84875 | 0.70813 | 0.35575 | 0.23938 | 0.08975
16h30 | 71.79 | 61.13 | 32.03 | 22.41 | 10.34 | 16h30 | 0.89738 | 0.76413 | 0.40037 | 0.28013 | 0.12925
17h30 | 72.43 | 62.32 | 32.93 | 23.62 | 11.75 | 17h30 | 0.90538 | 0.779 | 0.41163 | 0.29525 | 0.14688
18h30 | 71.8 | 62.12 | 33.67 | 24.18 | 13.05 | 18h30 | 0.8975 | 0.7765 | 0.42087 | 0.30225 | 0.16312
19h30 | 74.21 | 64.61 | 36.33 | 26.24 | 16.22 | 19h30 | 0.92763 | 0.80763 | 0.45413 | 0.328 | 0.20275
20h30 | 76.78 | 66.91 | 38.81 | 28.08 | 19.14 | 20h30 | 0.95975 | 0.83637 | 0.48512 | 0.351 | 0.23925
21h30 | 66.22 | 55.87 | 32.74 | 22.11 | 14.54 | 21h30 | 0.82775 | 0.69837 | 0.40925 | 0.27637 | 0.18175
22h30 | 60.39 | 49.29 | 25.95 | 16.45 | 7.16 | 22h30 | 0.75487 | 0.61613 | 0.32438 | 0.20563 | 0.0895
23h30 | 27.15 | 11.15 | 6.91 | 0 | 0 | 23h30 | 0.33937 | 0.13937 | 0.086375 | 0 | 0
00h30 | 27.15 | 11.15 | 6.91 | 0 | 0 | 00h30 | 0.33937 | 0.13937 | 0.086375 | 0 | 0
01h30 | 35.79 | 27.17 | 13.69 | 0.32 | 0 | 01h30 | 0.44738 | 0.33963 | 0.17112 | 0.004 | 0
02h30 | 57.47 | 48 | 28.37 | 14.84 | 7.56 | 02h30 | 0.71837 | 0.6 | 0.35463 | 0.1855 | 0.0945
03h30 | 43.46 | 32.65 | 18.62 | 14.52 | 7.56 | 03h30 | 0.54325 | 0.40813 | 0.23275 | 0.1815 | 0.0945
04h30 | 25.57 | 13.83 | 7.75 | 0 | 0 | 04h30 | 0.31962 | 0.17288 | 0.096875 | 0 | 0
05h30 | 39.76 | 27.18 | 15.74 | 3.23 | 0 | 05h30 | 0.497 | 0.33975 | 0.19675 | 0.040375 | 0
06h30 | 56.2 | 43.2 | 23.98 | 12.9 | 4.96 | 06h30 | 0.7025 | 0.54 | 0.29975 | 0.16125 | 0.062
07h30 | 65.78 | 52.38 | 32.35 | 22.99 | 14.57 | 07h30 | 0.82225 | 0.65475 | 0.40437 | 0.28737 | 0.18213
08h30 | 47.95 | 34.34 | 20.31 | 13.32 | 9.61 | 08h30 | 0.59937 | 0.42925 | 0.25388 | 0.1665 | 0.12012
09h30 | 35.45 | 21.4 | 6.15 | 0 | 0 | 09h30 | 0.44312 | 0.2675 | 0.076875 | 0 | 0
10h30 | 33.06 | 21.4 | 6.15 | 0 | 0 | 10h30 | 0.41325 | 0.2675 | 0.076875 | 0 | 0
11h30 | 22.86 | 9.17 | 0 | 0 | 0 | 11h30 | 0.28575 | 0.11463 | 0 | 0 | 0
12h30 | 28.33 | 14.53 | 0 | 0 | 0 | 12h30 | 0.35413 | 0.18163 | 0 | 0 | 0
13h30 | 34.06 | 20.27 | 2.59 | 0 | 0 | 13h30 | 0.42575 | 0.25338 | 0.032375 | 0 | 0
14h30 | 35.59 | 22.29 | 3.06 | 0 | 0 | 14h30 | 0.44488 | 0.27863 | 0.03825 | 0 | 0
15h30 | 39.18 | 26.76 | 6.2 | 0.51 | 0 | 15h30 | 0.48975 | 0.3345 | 0.0775 | 0.006375 | 0
16h30 | 45.83 | 34.88 | 11.96 | 5.67 | 0 | 16h30 | 0.57288 | 0.436 | 0.1495 | 0.070875 | 0
17h30 | 50.44 | 40.98 | 16.7 | 9.7 | 0 | 17h30 | 0.6305 | 0.51225 | 0.20875 | 0.12125 | 0
18h30 | 58.37 | 50.37 | 23.79 | 15.84 | 0.83 | 18h30 | 0.72962 | 0.62962 | 0.29738 | 0.198 | 0.010375
19h30 | 58.31 | 51.61 | 26.12 | 17.07 | 3.15 | 19h30 | 0.72888 | 0.64512 | 0.3265 | 0.21338 | 0.039375
20h30 | 56.21 | 50.48 | 26.79 | 16.61 | 4.29 | 20h30 | 0.70263 | 0.631 | 0.33487 | 0.20763 | 0.053625
21h30 | 76.28 | 70.98 | 40.11 | 29.08 | 16.22 | 21h30 | 0.9535 | 0.88725 | 0.50138 | 0.3635 | 0.20275
22h30 | 79.2 | 73.85 | 42.56 | 31.11 | 18.83 | 22h30 | 0.99 | 0.92312 | 0.532 | 0.38888 | 0.23538
23h30 | 36.85 | 31.14 | 17.94 | 12.86 | 4.57 | 23h30 | 0.46063 | 0.38925 | 0.22425 | 0.16075 | 0.057125
00h30 | 14.44 | 4.51 | 1.49 | 0 | 0 | 00h30 | 0.1805 | 0.056375 | 0.018625 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 21.25 | 13.26 | 5.65 | 0 | 0 | 02h30 | 0.26562 | 0.16575 | 0.070625 | 0 | 0
03h30 | 39.33 | 31.08 | 17.22 | 1.18 | 0 | 03h30 | 0.49162 | 0.3885 | 0.21525 | 0.01475 | 0
04h30 | 44.43 | 35.55 | 20.44 | 5.14 | 0 | 04h30 | 0.55537 | 0.44438 | 0.2555 | 0.06425 | 0
05h30 | 66.66 | 57.19 | 33.97 | 17.48 | 7.25 | 05h30 | 0.83325 | 0.71488 | 0.42462 | 0.2185 | 0.090625
06h30 | 81.3 | 70.99 | 41.4 | 26.21 | 14.4 | 06h30 | 1.0163 | 0.88738 | 0.5175 | 0.32762 | 0.18
07h30 | 99.43 | 88.7 | 55.14 | 41.93 | 29.86 | 07h30 | 1.2429 | 1.1087 | 0.68925 | 0.52412 | 0.37325
08h30 | 106.66 | 95.41 | 54.3 | 41.55 | 28.74 | 08h30 | 1.3333 | 1.1926 | 0.67875 | 0.51938 | 0.35925
09h30 | 114.5 | 102.35 | 57.17 | 43.71 | 29.59 | 09h30 | 1.4312 | 1.2794 | 0.71462 | 0.54638 | 0.36988
10h30 | 118.54 | 105.53 | 57.44 | 43.96 | 29.43 | 10h30 | 1.4817 | 1.3191 | 0.718 | 0.5495 | 0.36788
11h30 | 129.45 | 116.18 | 63.78 | 49.82 | 34.76 | 11h30 | 1.6181 | 1.4523 | 0.79725 | 0.62275 | 0.4345
12h30 | 134.01 | 121.19 | 67.18 | 53.48 | 37.71 | 12h30 | 1.6751 | 1.5149 | 0.83975 | 0.6685 | 0.47137
13h30 | 148.84 | 136.05 | 75.4 | 62.28 | 46.32 | 13h30 | 1.8605 | 1.7006 | 0.9425 | 0.7785 | 0.579
14h30 | 129.49 | 115.79 | 62.5 | 48.55 | 37.49 | 14h30 | 1.6186 | 1.4474 | 0.78125 | 0.60688 | 0.46863
15h30 | 91.54 | 77.23 | 38.78 | 24.21 | 13 | 15h30 | 1.1442 | 0.96537 | 0.48475 | 0.30262 | 0.1625
16h30 | 85.4 | 71.37 | 34.54 | 21.74 | 13 | 16h30 | 1.0675 | 0.89212 | 0.43175 | 0.27175 | 0.1625
17h30 | 99.96 | 86.79 | 43.66 | 30.08 | 17.62 | 17h30 | 1.2495 | 1.0849 | 0.54575 | 0.376 | 0.22025
18h30 | 106.57 | 94.96 | 50.22 | 36.64 | 24.21 | 18h30 | 1.3321 | 1.187 | 0.62775 | 0.458 | 0.30262
19h30 | 93.21 | 83.69 | 46.53 | 31.42 | 20.79 | 19h30 | 1.1651 | 1.0461 | 0.58162 | 0.39275 | 0.25988
20h30 | 112.68 | 104.53 | 60.64 | 46.27 | 34.9 | 20h30 | 1.4085 | 1.3066 | 0.758 | 0.57837 | 0.43625
21h30 | 106.6 | 98.45 | 56.93 | 44.63 | 33.91 | 21h30 | 1.3325 | 1.2306 | 0.71162 | 0.55788 | 0.42388
22h30 | 81.91 | 73.34 | 42.24 | 29.99 | 21.36 | 22h30 | 1.0239 | 0.91675 | 0.528 | 0.37488 | 0.267
23h30 | 83.96 | 74.67 | 43.59 | 31.12 | 22.6 | 23h30 | 1.0495 | 0.93337 | 0.54487 | 0.389 | 0.2825
00h30 | 63.14 | 54.25 | 35.61 | 24.35 | 14.46 | 00h30 | 0.78925 | 0.67812 | 0.44512 | 0.30438 | 0.18075
01h30 | 62.24 | 51.76 | 27.23 | 12.88 | 5.08 | 01h30 | 0.778 | 0.647 | 0.34037 | 0.161 | 0.0635
02h30 | 62.86 | 50.36 | 28.27 | 13.84 | 5.96 | 02h30 | 0.78575 | 0.6295 | 0.35337 | 0.173 | 0.0745
03h30 | 62.03 | 49.81 | 28.1 | 13.33 | 6.02 | 03h30 | 0.77538 | 0.62262 | 0.35125 | 0.16662 | 0.07525
04h30 | 61.04 | 48.24 | 28.34 | 13.11 | 6.26 | 04h30 | 0.763 | 0.603 | 0.35425 | 0.16387 | 0.07825
05h30 | 40.14 | 26.41 | 16.06 | 0.74 | 1.11 | 05h30 | 0.50175 | 0.33013 | 0.20075 | 0.00925 | 0.013875
06h30 | 53.13 | 38.58 | 23.4 | 7.65 | 0.8 | 06h30 | 0.66412 | 0.48225 | 0.2925 | 0.095625 | 0.01
07h30 | 114.79 | 99.19 | 63.99 | 48.72 | 39.9 | 07h30 | 1.4349 | 1.2399 | 0.79988 | 0.609 | 0.49875
08h30 | 145.25 | 129.41 | 77.05 | 61.69 | 49.3 | 08h30 | 1.8156 | 1.6176 | 0.96313 | 0.77112 | 0.61625
09h30 | 154.99 | 143.2 | 85.57 | 70.49 | 56.02 | 09h30 | 1.9374 | 1.79 | 1.0696 | 0.88113 | 0.70025
10h30 | 114.48 | 100 | 63.89 | 49.87 | 45.82 | 10h30 | 1.431 | 1.25 | 0.79863 | 0.62338 | 0.57275
11h30 | 77.8 | 61.36 | 30.36 | 17.79 | 8.33 | 11h30 | 0.9725 | 0.767 | 0.3795 | 0.22237 | 0.10412
12h30 | 81.83 | 65.72 | 33.48 | 20.86 | 11.09 | 12h30 | 1.0229 | 0.8215 | 0.4185 | 0.26075 | 0.13862
13h30 | 83.9 | 68.16 | 33.54 | 21.55 | 10.32 | 13h30 | 1.0488 | 0.852 | 0.41925 | 0.26937 | 0.129
14h30 | 90.04 | 73.74 | 35.63 | 23.51 | 11.84 | 14h30 | 1.1255 | 0.92175 | 0.44538 | 0.29387 | 0.148
15h30 | 93.61 | 76.3 | 36.55 | 22.95 | 11.6 | 15h30 | 1.1701 | 0.95375 | 0.45687 | 0.28687 | 0.145
16h30 | 84.96 | 68.19 | 32.09 | 17.92 | 7.67 | 16h30 | 1.062 | 0.85237 | 0.40113 | 0.224 | 0.095875
17h30 | 102.88 | 88.26 | 45.98 | 31.25 | 20.6 | 17h30 | 1.286 | 1.1033 | 0.57475 | 0.39062 | 0.2575
18h30 | 123.03 | 111.33 | 62.56 | 47.29 | 36 | 18h30 | 1.5379 | 1.3916 | 0.782 | 0.59113 | 0.45
19h30 | 92.67 | 82.71 | 47.44 | 32.57 | 23.57 | 19h30 | 1.1584 | 1.0339 | 0.593 | 0.40713 | 0.29463
20h30 | 58.22 | 57.81 | 30.1 | 16.54 | 7.83 | 20h30 | 0.72775 | 0.72262 | 0.37625 | 0.20675 | 0.097875
21h30 | 50.56 | 39.27 | 23.31 | 9.32 | 3.75 | 21h30 | 0.632 | 0.49088 | 0.29137 | 0.1165 | 0.046875
22h30 | 58.79 | 48.21 | 28.56 | 15.1 | 8.94 | 22h30 | 0.73487 | 0.60262 | 0.357 | 0.18875 | 0.11175
23h30 | 85.26 | 73.32 | 43.96 | 30.97 | 23.73 | 23h30 | 1.0657 | 0.9165 | 0.5495 | 0.38712 | 0.29663
00h30 | 80.1 | 69.52 | 38.71 | 25.2 | 18.55 | 00h30 | 1.0012 | 0.869 | 0.48387 | 0.315 | 0.23187
01h30 | 59.02 | 47.92 | 26.95 | 11.78 | 5.12 | 01h30 | 0.73775 | 0.599 | 0.33687 | 0.14725 | 0.064
02h30 | 54.25 | 42.79 | 26.95 | 11.78 | 5.12 | 02h30 | 0.67812 | 0.53487 | 0.33687 | 0.14725 | 0.064
03h30 | 22.9 | 8.44 | 3.97 | 0 | 0 | 03h30 | 0.28625 | 0.1055 | 0.049625 | 0 | 0
04h30 | 48.84 | 31.86 | 19.39 | 5.96 | 0 | 04h30 | 0.6105 | 0.39825 | 0.24238 | 0.0745 | 0
05h30 | 56.38 | 40.68 | 23.69 | 9.46 | 4.12 | 05h30 | 0.70475 | 0.5085 | 0.29613 | 0.11825 | 0.0515
06h30 | 51.49 | 34.89 | 17.71 | 3.97 | 4.12 | 06h30 | 0.64363 | 0.43612 | 0.22137 | 0.049625 | 0.0515
07h30 | 59.58 | 42.72 | 24.48 | 13.08 | 6.13 | 07h30 | 0.74475 | 0.534 | 0.306 | 0.1635 | 0.076625
08h30 | 57 | 39.83 | 17.07 | 12.61 | 6.13 | 08h30 | 0.7125 | 0.49788 | 0.21338 | 0.15762 | 0.076625
09h30 | 76.77 | 58.25 | 25.76 | 16.15 | 6.28 | 09h30 | 0.95962 | 0.72813 | 0.322 | 0.20187 | 0.0785
10h30 | 95.38 | 75.57 | 34.19 | 25.45 | 13.31 | 10h30 | 1.1923 | 0.94463 | 0.42738 | 0.31812 | 0.16637
11h30 | 98.73 | 79.14 | 36.46 | 27.63 | 14.27 | 11h30 | 1.2341 | 0.98925 | 0.45575 | 0.34537 | 0.17838
12h30 | 102.08 | 84.05 | 40.77 | 31.88 | 18 | 12h30 | 1.276 | 1.0506 | 0.50962 | 0.3985 | 0.225
13h30 | 112.29 | 94.78 | 47.27 | 38.01 | 22.84 | 13h30 | 1.4036 | 1.1847 | 0.59088 | 0.47513 | 0.2855
14h30 | 120.4 | 102.19 | 50.31 | 40.65 | 24.26 | 14h30 | 1.505 | 1.2774 | 0.62887 | 0.50813 | 0.30325
15h30 | 125.85 | 107.86 | 52.43 | 42.31 | 24.65 | 15h30 | 1.5731 | 1.3482 | 0.65538 | 0.52887 | 0.30812
16h30 | 136.38 | 119.84 | 59.45 | 48.9 | 30.79 | 16h30 | 1.7047 | 1.498 | 0.74313 | 0.61125 | 0.38488
17h30 | 145.13 | 130.54 | 67.81 | 55.99 | 38.66 | 17h30 | 1.8141 | 1.6318 | 0.84762 | 0.69988 | 0.48325
18h30 | 129.15 | 116.9 | 63.01 | 49.65 | 34.7 | 18h30 | 1.6144 | 1.4612 | 0.78763 | 0.62062 | 0.43375
19h30 | 56.6 | 46.39 | 23.49 | 16.44 | 14.37 | 19h30 | 0.7075 | 0.57988 | 0.29363 | 0.2055 | 0.17963
20h30 | 13.51 | 3.68 | 3.47 | 0 | 0 | 20h30 | 0.16887 | 0.046 | 0.043375 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 5.35 | 0 | 0 | 0 | 0 | 22h30 | 0.066875 | 0 | 0 | 0 | 0
23h30 | 6.42 | 0 | 0 | 0 | 0 | 23h30 | 0.08025 | 0 | 0 | 0 | 0
00h30 | 1.07 | 0 | 0 | 0 | 0 | 00h30 | 0.013375 | 0 | 0 | 0 | 0
01h30 | 3.24 | 0 | 0 | 0 | 0 | 01h30 | 0.0405 | 0 | 0 | 0 | 0
02h30 | 73.78 | 60.56 | 33.91 | 8.57 | 0 | 02h30 | 0.92225 | 0.757 | 0.42388 | 0.10712 | 0
03h30 | 139.07 | 127.31 | 75.06 | 55.91 | 40.54 | 03h30 | 1.7384 | 1.5914 | 0.93825 | 0.69888 | 0.50675
04h30 | 138.12 | 125.2 | 74.01 | 51.53 | 40.54 | 04h30 | 1.7265 | 1.565 | 0.92512 | 0.64412 | 0.50675
05h30 | 138.37 | 125.06 | 74.32 | 53.77 | 38.78 | 05h30 | 1.7296 | 1.5633 | 0.929 | 0.67212 | 0.48475
06h30 | 141.03 | 127.14 | 75.4 | 55.69 | 39.88 | 06h30 | 1.7629 | 1.5893 | 0.9425 | 0.69612 | 0.4985
07h30 | 170.54 | 156.19 | 98.04 | 79.37 | 63.02 | 07h30 | 2.1317 | 1.9524 | 1.2255 | 0.99213 | 0.78775
08h30 | 172.44 | 155.87 | 94.11 | 77.02 | 61.92 | 08h30 | 2.1555 | 1.9484 | 1.1764 | 0.96275 | 0.774
09h30 | 163.6 | 146.96 | 87.6 | 70.29 | 54.43 | 09h30 | 2.045 | 1.837 | 1.095 | 0.87862 | 0.68037
10h30 | 89.45 | 86.74 | 57.59 | 66.53 | 54.43 | 10h30 | 1.1181 | 1.0842 | 0.71988 | 0.83162 | 0.68037
11h30 | 6.72 | 0 | 0 | 0 | 0 | 11h30 | 0.084 | 0 | 0 | 0 | 0
12h30 | 7.6 | 0 | 0 | 0 | 0 | 12h30 | 0.095 | 0 | 0 | 0 | 0
13h30 | 3.96 | 0 | 0 | 0 | 0 | 13h30 | 0.0495 | 0 | 0 | 0 | 0
14h30 | 3.08 | 0 | 0 | 0 | 0 | 14h30 | 0.0385 | 0 | 0 | 0 | 0
15h30 | 0.73 | 0 | 0 | 0 | 0 | 15h30 | 0.009125 | 0 | 0 | 0 | 0
16h30 | 1.36 | 0 | 0 | 0 | 0 | 16h30 | 0.017 | 0 | 0 | 0 | 0
17h30 | 53.14 | 35.06 | 14.79 | 0 | 0 | 17h30 | 0.66425 | 0.43825 | 0.18488 | 0 | 0
18h30 | 103.89 | 91.26 | 51.51 | 30.76 | 16.9 | 18h30 | 1.2986 | 1.1407 | 0.64387 | 0.3845 | 0.21125
19h30 | 55.71 | 56.2 | 36.72 | 30.76 | 16.9 | 19h30 | 0.69637 | 0.7025 | 0.459 | 0.3845 | 0.21125
20h30 | 9.47 | 0 | 0 | 0 | 0 | 20h30 | 0.11837 | 0 | 0 | 0 | 0
21h30 | 11.13 | 0 | 0 | 0 | 0 | 21h30 | 0.13912 | 0 | 0 | 0 | 0
22h30 | 11.63 | 0 | 0 | 0 | 0 | 22h30 | 0.14538 | 0 | 0 | 0 | 0
23h30 | 11.61 | 0 | 0 | 0 | 0 | 23h30 | 0.14513 | 0 | 0 | 0 | 0
00h30 | 5.97 | 0 | 0 | 0 | 0 | 00h30 | 0.074625 | 0 | 0 | 0 | 0
01h30 | 3.65 | 0 | 0 | 0 | 0 | 01h30 | 0.045625 | 0 | 0 | 0 | 0
02h30 | 7.6 | 0 | 0 | 0 | 0 | 02h30 | 0.095 | 0 | 0 | 0 | 0
03h30 | 9.34 | 0 | 0 | 0 | 0 | 03h30 | 0.11675 | 0 | 0 | 0 | 0
04h30 | 11.27 | 0 | 0 | 0 | 0 | 04h30 | 0.14088 | 0 | 0 | 0 | 0
05h30 | 12.12 | 0 | 0 | 0 | 0 | 05h30 | 0.1515 | 0 | 0 | 0 | 0
06h30 | 10.83 | 0 | 0 | 0 | 0 | 06h30 | 0.13537 | 0 | 0 | 0 | 0
07h30 | 54.41 | 37.03 | 24.34 | 0 | 0 | 07h30 | 0.68012 | 0.46287 | 0.30425 | 0 | 0
08h30 | 81.4 | 63.67 | 36.86 | 15.68 | 3.36 | 08h30 | 1.0175 | 0.79587 | 0.46075 | 0.196 | 0.042
09h30 | 90.61 | 73.42 | 41.8 | 17.38 | 4.53 | 09h30 | 1.1326 | 0.91775 | 0.5225 | 0.21725 | 0.056625
10h30 | 59.05 | 46.78 | 29.28 | 1.7 | 1.17 | 10h30 | 0.73813 | 0.58475 | 0.366 | 0.02125 | 0.014625
11h30 | 2.04 | 0 | 0 | 0 | 0 | 11h30 | 0.0255 | 0 | 0 | 0 | 0
12h30 | 28.87 | 9.51 | 0 | 0 | 0 | 12h30 | 0.36088 | 0.11887 | 0 | 0 | 0
13h30 | 57.8 | 44.14 | 20.51 | 1.1 | 0 | 13h30 | 0.7225 | 0.55175 | 0.25638 | 0.01375 | 0
14h30 | 61.72 | 47.28 | 21.11 | 2.57 | 0 | 14h30 | 0.7715 | 0.591 | 0.26388 | 0.032125 | 0
15h30 | 58.33 | 44.49 | 19.9 | 1.47 | 0 | 15h30 | 0.72913 | 0.55612 | 0.24875 | 0.018375 | 0
16h30 | 57.53 | 44.8 | 21.24 | 0.33 | 0 | 16h30 | 0.71913 | 0.56 | 0.2655 | 0.004125 | 0
17h30 | 60.54 | 49.16 | 24.86 | 4.75 | 0 | 17h30 | 0.75675 | 0.6145 | 0.31075 | 0.059375 | 0
18h30 | 32.53 | 36.2 | 22.92 | 4.42 | 0 | 18h30 | 0.40663 | 0.4525 | 0.2865 | 0.05525 | 0
19h30 | 29.27 | 14.7 | 5.26 | 0 | 0 | 19h30 | 0.36588 | 0.18375 | 0.06575 | 0 | 0
20h30 | 31.06 | 20.34 | 10.59 | 0 | 0 | 20h30 | 0.38825 | 0.25425 | 0.13237 | 0 | 0
21h30 | 7.88 | 5.64 | 5.32 | 0 | 0 | 21h30 | 0.0985 | 0.0705 | 0.0665 | 0 | 0
22h30 | 38.48 | 23.44 | 12 | 0 | 0 | 22h30 | 0.481 | 0.293 | 0.15 | 0 | 0
23h30 | 64.75 | 52.29 | 30.88 | 12.58 | 1.19 | 23h30 | 0.80937 | 0.65363 | 0.386 | 0.15725 | 0.014875
00h30 | 48.58 | 39.3 | 18.88 | 12.58 | 1.19 | 00h30 | 0.60725 | 0.49125 | 0.236 | 0.15725 | 0.014875
01h30 | 57.99 | 49.08 | 27.62 | 4.84 | 0 | 01h30 | 0.72488 | 0.6135 | 0.34525 | 0.0605 | 0
02h30 | 39.84 | 38.62 | 27.62 | 4.84 | 0 | 02h30 | 0.498 | 0.48275 | 0.34525 | 0.0605 | 0
03h30 | 31.15 | 16.35 | 6.5 | 0 | 0 | 03h30 | 0.38938 | 0.20438 | 0.08125 | 0 | 0
04h30 | 59.4 | 46.17 | 26.64 | 7.73 | 0 | 04h30 | 0.7425 | 0.57712 | 0.333 | 0.096625 | 0
05h30 | 56.14 | 42.44 | 24.38 | 7.73 | 0 | 05h30 | 0.70175 | 0.5305 | 0.30475 | 0.096625 | 0
06h30 | 56.1 | 42.26 | 22.89 | 5.15 | 0 | 06h30 | 0.70125 | 0.52825 | 0.28613 | 0.064375 | 0
07h30 | 73.16 | 59.31 | 35.6 | 21.13 | 8.53 | 07h30 | 0.9145 | 0.74138 | 0.445 | 0.26412 | 0.10662
08h30 | 76.66 | 62.26 | 32.97 | 18.95 | 8.53 | 08h30 | 0.95825 | 0.77825 | 0.41213 | 0.23688 | 0.10662
09h30 | 90.7 | 76.17 | 40.86 | 25.86 | 10.73 | 09h30 | 1.1338 | 0.95212 | 0.51075 | 0.32325 | 0.13412
10h30 | 96.82 | 82.58 | 42.56 | 28.63 | 11.11 | 10h30 | 1.2103 | 1.0322 | 0.532 | 0.35787 | 0.13887
11h30 | 102.22 | 88.03 | 45.06 | 31.56 | 12.95 | 11h30 | 1.2777 | 1.1004 | 0.56325 | 0.3945 | 0.16187
12h30 | 114.03 | 100.43 | 53.4 | 39.37 | 21.09 | 12h30 | 1.4254 | 1.2554 | 0.6675 | 0.49212 | 0.26362
13h30 | 108 | 94.74 | 49.22 | 36.26 | 17.94 | 13h30 | 1.35 | 1.1843 | 0.61525 | 0.45325 | 0.22425
14h30 | 87.45 | 72.68 | 33.51 | 22.72 | 9.43 | 14h30 | 1.0931 | 0.9085 | 0.41887 | 0.284 | 0.11787
15h30 | 80.97 | 65.25 | 26.94 | 16.16 | 0 | 15h30 | 1.0121 | 0.81563 | 0.33675 | 0.202 | 0
16h30 | 84.03 | 69.31 | 28.31 | 17.51 | 0 | 16h30 | 1.0504 | 0.86638 | 0.35387 | 0.21887 | 0
17h30 | 89.01 | 75.73 | 32.75 | 21.77 | 2.88 | 17h30 | 1.1126 | 0.94663 | 0.40937 | 0.27213 | 0.036
18h30 | 93.19 | 81.76 | 38.9 | 26.9 | 9.71 | 18h30 | 1.1649 | 1.022 | 0.48625 | 0.33625 | 0.12137
19h30 | 95.36 | 85.8 | 44.4 | 31.34 | 16.15 | 19h30 | 1.192 | 1.0725 | 0.555 | 0.39175 | 0.20187
20h30 | 94.71 | 86.48 | 46.86 | 33.64 | 19.78 | 20h30 | 1.1839 | 1.081 | 0.58575 | 0.4205 | 0.24725
21h30 | 81.23 | 73.81 | 40.55 | 26.94 | 15.18 | 21h30 | 1.0154 | 0.92263 | 0.50687 | 0.33675 | 0.18975
22h30 | 66.72 | 60.09 | 33.36 | 19.12 | 9.25 | 22h30 | 0.834 | 0.75113 | 0.417 | 0.239 | 0.11563
23h30 | 65.48 | 59.12 | 33.42 | 19.19 | 9.91 | 23h30 | 0.8185 | 0.739 | 0.41775 | 0.23988 | 0.12387
00h30 | 47.97 | 40.87 | 20.27 | 18.23 | 5.39 | 00h30 | 0.59962 | 0.51087 | 0.25338 | 0.22787 | 0.067375
01h30 | 67.04 | 57.47 | 30.06 | 14.53 | 4.07 | 01h30 | 0.838 | 0.71837 | 0.37575 | 0.18163 | 0.050875
02h30 | 82.8 | 71.64 | 38.9 | 24.7 | 12.58 | 02h30 | 1.035 | 0.8955 | 0.48625 | 0.30875 | 0.15725
03h30 | 87.41 | 76.74 | 42.56 | 27.4 | 15.69 | 03h30 | 1.0926 | 0.95925 | 0.532 | 0.3425 | 0.19612
04h30 | 87.89 | 77.68 | 43.87 | 29.25 | 17.84 | 04h30 | 1.0986 | 0.971 | 0.54837 | 0.36562 | 0.223
05h30 | 84.99 | 74.69 | 42.37 | 28.25 | 16.92 | 05h30 | 1.0624 | 0.93363 | 0.52963 | 0.35313 | 0.2115
06h30 | 79.09 | 68.03 | 37.89 | 24.46 | 13.23 | 06h30 | 0.98862 | 0.85037 | 0.47363 | 0.30575 | 0.16537
07h30 | 93.52 | 82.78 | 51.54 | 39.21 | 28.24 | 07h30 | 1.169 | 1.0348 | 0.64425 | 0.49012 | 0.353
08h30 | 104.73 | 93.87 | 53.9 | 42.39 | 30.3 | 08h30 | 1.3091 | 1.1734 | 0.67375 | 0.52987 | 0.37875
09h30 | 114.18 | 102.25 | 56.2 | 45.13 | 31.39 | 09h30 | 1.4272 | 1.2781 | 0.7025 | 0.56412 | 0.39237
10h30 | 114.45 | 101.21 | 53.18 | 41.85 | 27.35 | 10h30 | 1.4306 | 1.2651 | 0.66475 | 0.52312 | 0.34187
11h30 | 110.44 | 96.71 | 50.78 | 38.76 | 24.69 | 11h30 | 1.3805 | 1.2089 | 0.63475 | 0.4845 | 0.30862
12h30 | 87.27 | 74.39 | 45.76 | 30.62 | 19.69 | 12h30 | 1.0909 | 0.92988 | 0.572 | 0.38275 | 0.24613
13h30 | 75.88 | 62.99 | 30.56 | 21.09 | 8.39 | 13h30 | 0.9485 | 0.78738 | 0.382 | 0.26362 | 0.10487
14h30 | 108.98 | 95.52 | 49.29 | 39.22 | 24.14 | 14h30 | 1.3622 | 1.194 | 0.61613 | 0.49025 | 0.30175
15h30 | 125.39 | 111.87 | 58.39 | 47.68 | 30.74 | 15h30 | 1.5674 | 1.3984 | 0.72988 | 0.596 | 0.38425
16h30 | 109.2 | 95.86 | 47.94 | 38.44 | 21.87 | 16h30 | 1.365 | 1.1983 | 0.59925 | 0.4805 | 0.27337
17h30 | 100.45 | 87.66 | 43.01 | 33.56 | 18.42 | 17h30 | 1.2556 | 1.0958 | 0.53763 | 0.4195 | 0.23025
18h30 | 94.92 | 83.79 | 42.91 | 31.69 | 18.16 | 18h30 | 1.1865 | 1.0474 | 0.53638 | 0.39613 | 0.227
19h30 | 95.58 | 86.39 | 46.59 | 35.27 | 22.48 | 19h30 | 1.1947 | 1.0799 | 0.58237 | 0.44088 | 0.281
20h30 | 99.38 | 91.45 | 50.89 | 39.85 | 27.32 | 20h30 | 1.2423 | 1.1431 | 0.63613 | 0.49812 | 0.3415
21h30 | 100.29 | 92.66 | 52.44 | 41.08 | 29.1 | 21h30 | 1.2536 | 1.1583 | 0.6555 | 0.5135 | 0.36375
22h30 | 96.52 | 88.71 | 50.64 | 39.14 | 27.86 | 22h30 | 1.2065 | 1.1089 | 0.633 | 0.48925 | 0.34825
23h30 | 89.03 | 80.77 | 46.44 | 34.66 | 24.48 | 23h30 | 1.1129 | 1.0096 | 0.5805 | 0.43325 | 0.306
00h30 | 75.29 | 62.68 | 35.75 | 25 | 14.28 | 00h30 | 0.94112 | 0.7835 | 0.44688 | 0.3125 | 0.1785
01h30 | 60.1 | 50.97 | 25.68 | 12.81 | 4.08 | 01h30 | 0.75125 | 0.63713 | 0.321 | 0.16012 | 0.051
02h30 | 81.42 | 70.59 | 39.02 | 25.68 | 15.38 | 02h30 | 1.0177 | 0.88238 | 0.48775 | 0.321 | 0.19225
03h30 | 90.69 | 79.39 | 44.71 | 31.15 | 20.68 | 03h30 | 1.1336 | 0.99238 | 0.55888 | 0.38938 | 0.2585
04h30 | 83.23 | 72.21 | 41.2 | 27.91 | 18.07 | 04h30 | 1.0404 | 0.90263 | 0.515 | 0.34887 | 0.22587
05h30 | 76.69 | 65.15 | 37.04 | 24.18 | 14.62 | 05h30 | 0.95862 | 0.81437 | 0.463 | 0.30225 | 0.18275
06h30 | 67.71 | 55.28 | 29.27 | 17.65 | 7.7 | 06h30 | 0.84637 | 0.691 | 0.36588 | 0.22062 | 0.09625
07h30 | 89.23 | 77.11 | 45.07 | 35.24 | 23.55 | 07h30 | 1.1154 | 0.96388 | 0.56337 | 0.4405 | 0.29437
08h30 | 94.8 | 82.65 | 43.34 | 34.29 | 21.78 | 08h30 | 1.185 | 1.0331 | 0.54175 | 0.42862 | 0.27225
09h30 | 95.41 | 81.45 | 40.08 | 31.41 | 15.52 | 09h30 | 1.1926 | 1.0181 | 0.501 | 0.39263 | 0.194
10h30 | 88.87 | 73.35 | 39.75 | 29.26 | 15.52 | 10h30 | 1.1109 | 0.91687 | 0.49688 | 0.36575 | 0.194
11h30 | 97.17 | 80.29 | 37.76 | 29.72 | 12.48 | 11h30 | 1.2146 | 1.0036 | 0.472 | 0.3715 | 0.156
12h30 | 104.9 | 89.3 | 43.03 | 35.92 | 17.2 | 12h30 | 1.3113 | 1.1162 | 0.53787 | 0.449 | 0.215
13h30 | 100.34 | 85.34 | 39.28 | 33.59 | 13.89 | 13h30 | 1.2543 | 1.0668 | 0.491 | 0.41987 | 0.17363
14h30 | 95.07 | 80.25 | 34.34 | 29.02 | 9.17 | 14h30 | 1.1884 | 1.0031 | 0.42925 | 0.36275 | 0.11463
15h30 | 87.99 | 74.05 | 28.87 | 23.27 | 2.76 | 15h30 | 1.0999 | 0.92563 | 0.36088 | 0.29087 | 0.0345
16h30 | 90 | 77.19 | 29.14 | 23.89 | 2.83 | 16h30 | 1.125 | 0.96488 | 0.36425 | 0.29862 | 0.035375
17h30 | 95.34 | 83.91 | 32.78 | 27.78 | 6.17 | 17h30 | 1.1918 | 1.0489 | 0.40975 | 0.34725 | 0.077125
18h30 | 110.74 | 101.04 | 45.53 | 39.83 | 19.14 | 18h30 | 1.3842 | 1.263 | 0.56912 | 0.49788 | 0.23925
19h30 | 119.4 | 111.44 | 55.75 | 48.01 | 30.01 | 19h30 | 1.4925 | 1.393 | 0.69688 | 0.60013 | 0.37512
20h30 | 96.86 | 90.13 | 45.63 | 37.06 | 22.93 | 20h30 | 1.2107 | 1.1266 | 0.57037 | 0.46325 | 0.28663
21h30 | 68.86 | 62.8 | 30.74 | 21.92 | 11.38 | 21h30 | 0.86075 | 0.785 | 0.38425 | 0.274 | 0.14225
22h30 | 67.64 | 59.93 | 27.51 | 18.56 | 8.58 | 22h30 | 0.8455 | 0.74913 | 0.34387 | 0.232 | 0.10725
23h30 | 66.13 | 60.44 | 31.36 | 20.98 | 12.2 | 23h30 | 0.82663 | 0.7555 | 0.392 | 0.26225 | 0.1525
00h30 | 66.13 | 60.44 | 31.36 | 20.98 | 9.04 | 00h30 | 0.82663 | 0.7555 | 0.392 | 0.26225 | 0.113
01h30 | 40.57 | 32.78 | 12.12 | 0.91 | 0 | 01h30 | 0.50713 | 0.40975 | 0.1515 | 0.011375 | 0
02h30 | 40.57 | 32.78 | 12.12 | 0.91 | 0 | 02h30 | 0.50713 | 0.40975 | 0.1515 | 0.011375 | 0
03h30 | 10.92 | 3.79 | 0 | 0 | 0 | 03h30 | 0.1365 | 0.047375 | 0 | 0 | 0
04h30 | 10.92 | 3.79 | 0 | 0 | 0 | 04h30 | 0.1365 | 0.047375 | 0 | 0 | 0
05h30 | 0.92 | 0 | 0 | 0 | 0 | 05h30 | 0.0115 | 0 | 0 | 0 | 0
06h30 | 17.32 | 4.8 | 0 | 0 | 0 | 06h30 | 0.2165 | 0.06 | 0 | 0 | 0
07h30 | 38.41 | 27.59 | 14.7 | 4.51 | 0 | 07h30 | 0.48013 | 0.34487 | 0.18375 | 0.056375 | 0
08h30 | 27.27 | 22.79 | 14.7 | 4.51 | 0 | 08h30 | 0.34087 | 0.28487 | 0.18375 | 0.056375 | 0
09h30 | 16.72 | 4 | 0 | 0 | 0 | 09h30 | 0.209 | 0.05 | 0 | 0 | 0
10h30 | 11.46 | 4 | 0 | 0 | 0 | 10h30 | 0.14325 | 0.05 | 0 | 0 | 0
11h30 | 5.58 | 0 | 0 | 0 | 0 | 11h30 | 0.06975 | 0 | 0 | 0 | 0
12h30 | 10.47 | 0 | 0 | 0 | 0 | 12h30 | 0.13087 | 0 | 0 | 0 | 0
13h30 | 9.75 | 0 | 0 | 0 | 0 | 13h30 | 0.12187 | 0 | 0 | 0 | 0
14h30 | 4.86 | 0 | 0 | 0 | 0 | 14h30 | 0.06075 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 7.21 | 0 | 0 | 0 | 0 | 19h30 | 0.090125 | 0 | 0 | 0 | 0
20h30 | 13.22 | 5.64 | 0 | 0 | 0 | 20h30 | 0.16525 | 0.0705 | 0 | 0 | 0
21h30 | 14.16 | 7.06 | 0 | 0 | 0 | 21h30 | 0.177 | 0.08825 | 0 | 0 | 0
22h30 | 8.15 | 1.42 | 0 | 0 | 0 | 22h30 | 0.10187 | 0.01775 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 1.91 | 0 | 0 | 0 | 0 | 07h30 | 0.023875 | 0 | 0 | 0 | 0
08h30 | 5.69 | 0 | 0 | 0 | 0 | 08h30 | 0.071125 | 0 | 0 | 0 | 0
09h30 | 6.23 | 0 | 0 | 0 | 0 | 09h30 | 0.077875 | 0 | 0 | 0 | 0
10h30 | 2.45 | 0 | 0 | 0 | 0 | 10h30 | 0.030625 | 0 | 0 | 0 | 0
11h30 | 0.32 | 0 | 0 | 0 | 0 | 11h30 | 0.004 | 0 | 0 | 0 | 0
12h30 | 0.32 | 0 | 0 | 0 | 0 | 12h30 | 0.004 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0.26 | 0 | 0 | 0 | 0 | 17h30 | 0.00325 | 0 | 0 | 0 | 0
18h30 | 16.89 | 9.64 | 0 | 0 | 0 | 18h30 | 0.21113 | 0.1205 | 0 | 0 | 0
19h30 | 44.82 | 36.79 | 2.27 | 0 | 0 | 19h30 | 0.56025 | 0.45987 | 0.028375 | 0 | 0
20h30 | 61.96 | 54.95 | 12.78 | 0 | 0 | 20h30 | 0.7745 | 0.68688 | 0.15975 | 0 | 0
21h30 | 61.65 | 55.46 | 14.66 | 0 | 0 | 21h30 | 0.77063 | 0.69325 | 0.18325 | 0 | 0
22h30 | 63.49 | 57.5 | 18.07 | 3.39 | 0 | 22h30 | 0.79363 | 0.71875 | 0.22587 | 0.042375 | 0
23h30 | 75.39 | 69.22 | 26.95 | 12.45 | 0 | 23h30 | 0.94237 | 0.86525 | 0.33687 | 0.15563 | 0
00h30 | 65.53 | 58.36 | 15.61 | 9.06 | 0 | 00h30 | 0.81912 | 0.7295 | 0.19512 | 0.11325 | 0
01h30 | 58 | 49.61 | 13.48 | 0 | 0 | 01h30 | 0.725 | 0.62013 | 0.1685 | 0 | 0
02h30 | 45.32 | 36.28 | 10.89 | 0 | 0 | 02h30 | 0.5665 | 0.4535 | 0.13612 | 0 | 0
03h30 | 49.08 | 39.42 | 10.47 | 0 | 0 | 03h30 | 0.6135 | 0.49275 | 0.13087 | 0 | 0
04h30 | 52.65 | 42.32 | 13.34 | 0.18 | 0 | 04h30 | 0.65812 | 0.529 | 0.16675 | 0.00225 | 0
05h30 | 43.11 | 31.77 | 6.09 | 0.18 | 0 | 05h30 | 0.53887 | 0.39713 | 0.076125 | 0.00225 | 0
06h30 | 26.46 | 23.23 | 3.23 | 0 | 0 | 06h30 | 0.33075 | 0.29037 | 0.040375 | 0 | 0
07h30 | 26.76 | 14.22 | 0 | 0 | 0 | 07h30 | 0.3345 | 0.17775 | 0 | 0 | 0
08h30 | 26.76 | 14.22 | 0 | 0 | 0 | 08h30 | 0.3345 | 0.17775 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 1.34 | 0 | 0 | 0 | 0 | 09h30 | 0.01675 | 0 | 0 | 0 | 0
10h30 | 1.34 | 0 | 0 | 0 | 0 | 10h30 | 0.01675 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 6.67 | 0 | 0 | 0 | 0 | 19h30 | 0.083375 | 0 | 0 | 0 | 0
20h30 | 6.67 | 0 | 0 | 0 | 0 | 20h30 | 0.083375 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 16.2 | 0.92 | 0 | 0 | 0 | 01h30 | 0.2025 | 0.0115 | 0 | 0 | 0
02h30 | 38.19 | 18.73 | 0 | 0 | 0 | 02h30 | 0.47737 | 0.23412 | 0 | 0 | 0
03h30 | 35.48 | 17.81 | 0 | 0 | 0 | 03h30 | 0.4435 | 0.22262 | 0 | 0 | 0
04h30 | 43.95 | 24.94 | 0 | 0 | 0 | 04h30 | 0.54937 | 0.31175 | 0 | 0 | 0
05h30 | 56.09 | 36.79 | 0 | 0 | 0 | 05h30 | 0.70112 | 0.45987 | 0 | 0 | 0
06h30 | 57.21 | 37.5 | 0 | 0 | 0 | 06h30 | 0.71513 | 0.46875 | 0 | 0 | 0
07h30 | 77.61 | 58.99 | 19.41 | 0 | 0 | 07h30 | 0.97013 | 0.73738 | 0.24263 | 0 | 0
08h30 | 78.68 | 61.52 | 19.78 | 0 | 0 | 08h30 | 0.9835 | 0.769 | 0.24725 | 0 | 0
09h30 | 65.03 | 47.06 | 9.82 | 0 | 0 | 09h30 | 0.81288 | 0.58825 | 0.12275 | 0 | 0
10h30 | 54.35 | 34.86 | 9.45 | 0 | 0 | 10h30 | 0.67937 | 0.43575 | 0.11812 | 0 | 0
11h30 | 66.14 | 46.59 | 8.43 | 0 | 0 | 11h30 | 0.82675 | 0.58237 | 0.10537 | 0 | 0
12h30 | 73.01 | 54.32 | 13.8 | 0 | 0 | 12h30 | 0.91263 | 0.679 | 0.1725 | 0 | 0
13h30 | 63.51 | 45.37 | 7.69 | 0 | 0 | 13h30 | 0.79387 | 0.56712 | 0.096125 | 0 | 0
14h30 | 44.17 | 26.37 | 2.33 | 0 | 0 | 14h30 | 0.55212 | 0.32963 | 0.029125 | 0 | 0
15h30 | 36.53 | 19.74 | 0 | 0 | 0 | 15h30 | 0.45663 | 0.24675 | 0 | 0 | 0
16h30 | 64.7 | 49.28 | 13.58 | 0 | 0 | 16h30 | 0.80875 | 0.616 | 0.16975 | 0 | 0
17h30 | 91.47 | 77.35 | 31.31 | 10.92 | 0 | 17h30 | 1.1434 | 0.96688 | 0.39137 | 0.1365 | 0
18h30 | 92.56 | 79.65 | 34.22 | 11.97 | 0 | 18h30 | 1.157 | 0.99562 | 0.42775 | 0.14963 | 0
19h30 | 86.53 | 74.67 | 33.1 | 12.18 | 0 | 19h30 | 1.0816 | 0.93337 | 0.41375 | 0.15225 | 0
20h30 | 77.2 | 66.05 | 29.13 | 11.13 | 0 | 20h30 | 0.965 | 0.82563 | 0.36412 | 0.13912 | 0
21h30 | 75.21 | 64.48 | 28.87 | 11.22 | 0 | 21h30 | 0.94012 | 0.806 | 0.36088 | 0.14025 | 0
22h30 | 79.46 | 69.1 | 32.27 | 15.39 | 0 | 22h30 | 0.99325 | 0.86375 | 0.40337 | 0.19237 | 0
23h30 | 75.63 | 65.63 | 30.9 | 14.36 | 0 | 23h30 | 0.94537 | 0.82037 | 0.38625 | 0.1795 | 0
00h30 | 48.16 | 36.21 | 14.97 | 10.19 | 0 | 00h30 | 0.602 | 0.45262 | 0.18713 | 0.12737 | 0
01h30 | 45.4 | 30.93 | 7.66 | 0 | 0 | 01h30 | 0.5675 | 0.38662 | 0.09575 | 0 | 0
02h30 | 39.2 | 27.77 | 7.66 | 0 | 0 | 02h30 | 0.49 | 0.34713 | 0.09575 | 0 | 0
03h30 | 33.12 | 19.52 | 1.98 | 0 | 0 | 03h30 | 0.414 | 0.244 | 0.02475 | 0 | 0
04h30 | 43.39 | 29.71 | 9.23 | 0 | 0 | 04h30 | 0.54238 | 0.37138 | 0.11538 | 0 | 0
05h30 | 45.98 | 31.6 | 10.08 | 0 | 0 | 05h30 | 0.57475 | 0.395 | 0.126 | 0 | 0
06h30 | 35.71 | 21.42 | 2.83 | 0 | 0 | 06h30 | 0.44638 | 0.26775 | 0.035375 | 0 | 0
07h30 | 42.82 | 29.44 | 12.93 | 0 | 0 | 07h30 | 0.53525 | 0.368 | 0.16162 | 0 | 0
08h30 | 43.03 | 31.47 | 12.93 | 0 | 0 | 08h30 | 0.53787 | 0.39337 | 0.16162 | 0 | 0
09h30 | 39.63 | 27.33 | 8.05 | 0 | 0 | 09h30 | 0.49538 | 0.34163 | 0.10063 | 0 | 0
10h30 | 39.43 | 25.3 | 8.05 | 0 | 0 | 10h30 | 0.49288 | 0.31625 | 0.10063 | 0 | 0
11h30 | 14.99 | 9.44 | 0 | 0 | 0 | 11h30 | 0.18738 | 0.118 | 0 | 0 | 0
12h30 | 89.44 | 77.45 | 37.39 | 22.84 | 2.67 | 12h30 | 1.118 | 0.96813 | 0.46737 | 0.2855 | 0.033375
13h30 | 114.17 | 98.2 | 48.52 | 34.46 | 10.1 | 13h30 | 1.4271 | 1.2275 | 0.6065 | 0.43075 | 0.12625
14h30 | 115.95 | 100.44 | 49.23 | 34.06 | 7.85 | 14h30 | 1.4494 | 1.2555 | 0.61538 | 0.42575 | 0.098125
15h30 | 115.53 | 101.53 | 49.74 | 35.25 | 10.48 | 15h30 | 1.4441 | 1.2691 | 0.62175 | 0.44062 | 0.131
16h30 | 104.1 | 91.13 | 44 | 30.5 | 10.05 | 16h30 | 1.3013 | 1.1391 | 0.55 | 0.38125 | 0.12562
17h30 | 95.07 | 83.09 | 40.04 | 26.94 | 5.7 | 17h30 | 1.1884 | 1.0386 | 0.5005 | 0.33675 | 0.07125
18h30 | 80.68 | 69.76 | 33.46 | 20.19 | 5.7 | 18h30 | 1.0085 | 0.872 | 0.41825 | 0.25238 | 0.07125
19h30 | 58.23 | 48.32 | 25.79 | 10.93 | 0 | 19h30 | 0.72788 | 0.604 | 0.32238 | 0.13662 | 0
20h30 | 52.11 | 43.2 | 19.79 | 7.1 | 0 | 20h30 | 0.65138 | 0.54 | 0.24738 | 0.08875 | 0
21h30 | 47.1 | 41.37 | 19.79 | 7.1 | 0 | 21h30 | 0.58875 | 0.51712 | 0.24738 | 0.08875 | 0
22h30 | 34.58 | 26.34 | 10.96 | 0 | 0 | 22h30 | 0.43225 | 0.32925 | 0.137 | 0 | 0
23h30 | 31.77 | 26.34 | 10.96 | 0 | 0 | 23h30 | 0.39713 | 0.32925 | 0.137 | 0 | 0
00h30 | 9.35 | 2.81 | 0 | 0 | 0 | 00h30 | 0.11688 | 0.035125 | 0 | 0 | 0
01h30 | 21.4 | 12.16 | 0 | 0 | 0 | 01h30 | 0.2675 | 0.152 | 0 | 0 | 0
02h30 | 32.43 | 18.3 | 5.44 | 0 | 0 | 02h30 | 0.40537 | 0.22875 | 0.068 | 0 | 0
03h30 | 20.38 | 8.94 | 5.44 | 0 | 0 | 03h30 | 0.25475 | 0.11175 | 0.068 | 0 | 0
04h30 | 2.13 | 0 | 0 | 0 | 0 | 04h30 | 0.026625 | 0 | 0 | 0 | 0
05h30 | 2.28 | 0 | 0 | 0 | 0 | 05h30 | 0.0285 | 0 | 0 | 0 | 0
06h30 | 1.39 | 0 | 0 | 0 | 0 | 06h30 | 0.017375 | 0 | 0 | 0 | 0
07h30 | 35.46 | 19.83 | 8.88 | 0 | 0 | 07h30 | 0.44325 | 0.24788 | 0.111 | 0 | 0
08h30 | 57.59 | 45.02 | 19.63 | 6.32 | 0 | 08h30 | 0.71988 | 0.56275 | 0.24538 | 0.079 | 0
09h30 | 63.77 | 48.1 | 18.05 | 6.32 | 0 | 09h30 | 0.79712 | 0.60125 | 0.22562 | 0.079 | 0
10h30 | 47.36 | 29.71 | 7.3 | 0 | 0 | 10h30 | 0.592 | 0.37138 | 0.09125 | 0 | 0
11h30 | 36.76 | 19.25 | 0 | 0 | 0 | 11h30 | 0.4595 | 0.24063 | 0 | 0 | 0
12h30 | 42.72 | 26.81 | 4.97 | 0 | 0 | 12h30 | 0.534 | 0.33513 | 0.062125 | 0 | 0
13h30 | 51.9 | 36.43 | 9.91 | 0 | 0 | 13h30 | 0.64875 | 0.45537 | 0.12387 | 0 | 0
14h30 | 55.32 | 39.79 | 9.96 | 0 | 0 | 14h30 | 0.6915 | 0.49738 | 0.1245 | 0 | 0
15h30 | 40.01 | 25.2 | 5.02 | 0 | 0 | 15h30 | 0.50013 | 0.315 | 0.06275 | 0 | 0
16h30 | 26.2 | 12.56 | 0 | 0 | 0 | 16h30 | 0.3275 | 0.157 | 0 | 0 | 0
17h30 | 26.57 | 14.33 | 0 | 0 | 0 | 17h30 | 0.33213 | 0.17913 | 0 | 0 | 0
18h30 | 32.3 | 21.64 | 0 | 0 | 0 | 18h30 | 0.40375 | 0.2705 | 0 | 0 | 0
19h30 | 36.85 | 27.73 | 5.89 | 0 | 0 | 19h30 | 0.46063 | 0.34663 | 0.073625 | 0 | 0
20h30 | 35.85 | 27.86 | 8.11 | 0 | 0 | 20h30 | 0.44812 | 0.34825 | 0.10138 | 0 | 0
21h30 | 14.09 | 12.53 | 2.22 | 0 | 0 | 21h30 | 0.17613 | 0.15662 | 0.02775 | 0 | 0
22h30 | 6.84 | 0 | 0 | 0 | 0 | 22h30 | 0.0855 | 0 | 0 | 0 | 0
23h30 | 19.62 | 15.96 | 4.08 | 0 | 0 | 23h30 | 0.24525 | 0.1995 | 0.051 | 0 | 0
00h30 | 48.56 | 41.77 | 15.37 | 0 | 0 | 00h30 | 0.607 | 0.52212 | 0.19212 | 0 | 0
01h30 | 53.08 | 41.6 | 16.43 | 0.31 | 0 | 01h30 | 0.6635 | 0.52 | 0.20538 | 0.003875 | 0
02h30 | 35.39 | 24.34 | 6.57 | 0.31 | 0 | 02h30 | 0.44238 | 0.30425 | 0.082125 | 0.003875 | 0
03h30 | 14.04 | 8.54 | 1.43 | 0 | 0 | 03h30 | 0.1755 | 0.10675 | 0.017875 | 0 | 0
04h30 | 2.79 | 0 | 0 | 0 | 0 | 04h30 | 0.034875 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 19.32 | 6.47 | 0 | 0 | 0 | 06h30 | 0.2415 | 0.080875 | 0 | 0 | 0
07h30 | 53.83 | 44.03 | 25.5 | 7.91 | 0 | 07h30 | 0.67288 | 0.55037 | 0.31875 | 0.098875 | 0
08h30 | 43.83 | 37.56 | 25.5 | 7.91 | 0 | 08h30 | 0.54788 | 0.4695 | 0.31875 | 0.098875 | 0
09h30 | 56.01 | 44.43 | 20.16 | 3.36 | 0 | 09h30 | 0.70012 | 0.55537 | 0.252 | 0.042 | 0
10h30 | 61.57 | 49.11 | 22.06 | 5.64 | 0 | 10h30 | 0.76963 | 0.61387 | 0.27575 | 0.0705 | 0
11h30 | 43.61 | 29.26 | 6.87 | 2.28 | 0 | 11h30 | 0.54512 | 0.36575 | 0.085875 | 0.0285 | 0
12h30 | 44.03 | 29.4 | 6.64 | 0 | 0 | 12h30 | 0.55037 | 0.3675 | 0.083 | 0 | 0
13h30 | 65.37 | 50.44 | 18.67 | 8.45 | 0 | 13h30 | 0.81712 | 0.6305 | 0.23337 | 0.10562 | 0
14h30 | 65.24 | 50.31 | 18.13 | 8.45 | 0 | 14h30 | 0.8155 | 0.62887 | 0.22662 | 0.10562 | 0
15h30 | 52.17 | 38.16 | 11.17 | 0 | 0 | 15h30 | 0.65212 | 0.477 | 0.13962 | 0 | 0
16h30 | 47.54 | 34.8 | 10.05 | 0 | 0 | 16h30 | 0.59425 | 0.435 | 0.12562 | 0 | 0
17h30 | 47.4 | 35.93 | 11.94 | 0.01 | 0 | 17h30 | 0.5925 | 0.44912 | 0.14925 | 0.000125 | 0
18h30 | 43.77 | 34.6 | 12.17 | 0.01 | 0 | 18h30 | 0.54712 | 0.4325 | 0.15213 | 0.000125 | 0
19h30 | 42.12 | 33.22 | 13.82 | 0.46 | 0 | 19h30 | 0.5265 | 0.41525 | 0.17275 | 0.00575 | 0
20h30 | 57.59 | 49.94 | 25.54 | 11.2 | 0 | 20h30 | 0.71988 | 0.62425 | 0.31925 | 0.14 | 0
21h30 | 72.51 | 65.56 | 36.08 | 21.05 | 3.53 | 21h30 | 0.90638 | 0.8195 | 0.451 | 0.26312 | 0.044125
22h30 | 50.14 | 48.83 | 24.13 | 10.31 | 3.53 | 22h30 | 0.62675 | 0.61038 | 0.30162 | 0.12887 | 0.044125
23h30 | 0.3 | 0 | 0 | 0 | 0 | 23h30 | 0.00375 | 0 | 0 | 0 | 0
00h30 | 0.3 | 0 | 0 | 0 | 0 | 00h30 | 0.00375 | 0 | 0 | 0 | 0
01h30 | 30.13 | 19.1 | 6.96 | 0 | 0 | 01h30 | 0.37662 | 0.23875 | 0.087 | 0 | 0
02h30 | 61.14 | 51.41 | 28.15 | 8.45 | 0 | 02h30 | 0.76425 | 0.64263 | 0.35187 | 0.10562 | 0
03h30 | 31.68 | 32.31 | 21.19 | 8.45 | 0 | 03h30 | 0.396 | 0.40387 | 0.26488 | 0.10562 | 0
04h30 | 7.4 | 0 | 0 | 0 | 0 | 04h30 | 0.0925 | 0 | 0 | 0 | 0
05h30 | 6.73 | 0 | 0 | 0 | 0 | 05h30 | 0.084125 | 0 | 0 | 0 | 0
06h30 | 11.34 | 0 | 0 | 0 | 0 | 06h30 | 0.14175 | 0 | 0 | 0 | 0
07h30 | 22.08 | 9 | 3.91 | 0 | 0 | 07h30 | 0.276 | 0.1125 | 0.048875 | 0 | 0
08h30 | 10.74 | 9 | 3.91 | 0 | 0 | 08h30 | 0.13425 | 0.1125 | 0.048875 | 0 | 0
09h30 | 14.95 | 0 | 0 | 0 | 0 | 09h30 | 0.18688 | 0 | 0 | 0 | 0
10h30 | 27.67 | 10.92 | 0 | 0 | 0 | 10h30 | 0.34587 | 0.1365 | 0 | 0 | 0
11h30 | 31.62 | 15.76 | 1.38 | 0 | 0 | 11h30 | 0.39525 | 0.197 | 0.01725 | 0 | 0
12h30 | 31.11 | 14.63 | 1.38 | 0 | 0 | 12h30 | 0.38888 | 0.18288 | 0.01725 | 0 | 0
13h30 | 12.21 | 9.79 | 0 | 0 | 0 | 13h30 | 0.15263 | 0.12237 | 0 | 0 | 0
14h30 | 10.18 | 0 | 0 | 0 | 0 | 14h30 | 0.12725 | 0 | 0 | 0 | 0
15h30 | 28.79 | 12.46 | 0 | 0 | 0 | 15h30 | 0.35988 | 0.15575 | 0 | 0 | 0
16h30 | 18.87 | 12.46 | 0 | 0 | 0 | 16h30 | 0.23588 | 0.15575 | 0 | 0 | 0
17h30 | 25.97 | 9.95 | 0 | 0 | 0 | 17h30 | 0.32462 | 0.12437 | 0 | 0 | 0
18h30 | 48.08 | 34.72 | 10.73 | 0 | 0 | 18h30 | 0.601 | 0.434 | 0.13412 | 0 | 0
19h30 | 46.19 | 34.17 | 13.03 | 0 | 0 | 19h30 | 0.57737 | 0.42712 | 0.16287 | 0 | 0
20h30 | 26.63 | 16.41 | 3.28 | 0 | 0 | 20h30 | 0.33287 | 0.20513 | 0.041 | 0 | 0
21h30 | 31.49 | 22.35 | 7.91 | 0 | 0 | 21h30 | 0.39363 | 0.27937 | 0.098875 | 0 | 0
22h30 | 64.41 | 55.91 | 29.05 | 10.66 | 0 | 22h30 | 0.80512 | 0.69888 | 0.36312 | 0.13325 | 0
23h30 | 82.79 | 74.37 | 40.75 | 22.28 | 4.49 | 23h30 | 1.0349 | 0.92963 | 0.50938 | 0.2785 | 0.056125
00h30 | 67.96 | 58.66 | 26.01 | 11.61 | 4.49 | 00h30 | 0.8495 | 0.73325 | 0.32512 | 0.14513 | 0.056125
01h30 | 76.96 | 65.16 | 32.76 | 13.7 | 0 | 01h30 | 0.962 | 0.8145 | 0.4095 | 0.17125 | 0
02h30 | 85.98 | 72.91 | 37.76 | 19.45 | 0.96 | 02h30 | 1.0748 | 0.91138 | 0.472 | 0.24313 | 0.012
03h30 | 88.37 | 76.13 | 40.99 | 22.54 | 3.56 | 03h30 | 1.1046 | 0.95163 | 0.51238 | 0.28175 | 0.0445
04h30 | 77.11 | 65.42 | 35.48 | 17.51 | 2.6 | 04h30 | 0.96388 | 0.81775 | 0.4435 | 0.21887 | 0.0325
05h30 | 59.3 | 47.46 | 25 | 7.64 | 0 | 05h30 | 0.74125 | 0.59325 | 0.3125 | 0.0955 | 0
06h30 | 63.18 | 50.69 | 26.52 | 9.77 | 0 | 06h30 | 0.78975 | 0.63362 | 0.3315 | 0.12212 | 0
07h30 | 99.84 | 88.14 | 53.94 | 38.53 | 22.27 | 07h30 | 1.248 | 1.1018 | 0.67425 | 0.48163 | 0.27837
08h30 | 106.51 | 94.33 | 53.73 | 39.94 | 22.27 | 08h30 | 1.3314 | 1.1791 | 0.67163 | 0.49925 | 0.27837
09h30 | 117.37 | 103.77 | 57.58 | 44.65 | 24.13 | 09h30 | 1.4671 | 1.2971 | 0.71975 | 0.55812 | 0.30162
10h30 | 132.52 | 118.86 | 64.7 | 51.74 | 29.71 | 10h30 | 1.6565 | 1.4857 | 0.80875 | 0.64675 | 0.37138
11h30 | 144.36 | 135.16 | 74.25 | 60.55 | 37.24 | 11h30 | 1.8045 | 1.6895 | 0.92812 | 0.75687 | 0.4655
12h30 | 150.82 | 138.76 | 76.86 | 63.06 | 39.65 | 12h30 | 1.8853 | 1.7345 | 0.96075 | 0.78825 | 0.49562
13h30 | 140.12 | 127.05 | 69.13 | 56.24 | 33.68 | 13h30 | 1.7515 | 1.5881 | 0.86413 | 0.703 | 0.421
14h30 | 141.65 | 128.06 | 68.87 | 56.24 | 33.02 | 14h30 | 1.7706 | 1.6007 | 0.86087 | 0.703 | 0.41275
15h30 | 152.34 | 144.29 | 78.98 | 65.38 | 41.03 | 15h30 | 1.9042 | 1.8036 | 0.98725 | 0.81725 | 0.51287
16h30 | 157.18 | 146.31 | 81.03 | 67.07 | 42.96 | 16h30 | 1.9647 | 1.8289 | 1.0129 | 0.83837 | 0.537
17h30 | 148.19 | 137.03 | 76.21 | 62.61 | 39.41 | 17h30 | 1.8524 | 1.7129 | 0.95263 | 0.78263 | 0.49262
18h30 | 134.89 | 124.59 | 69.61 | 56.45 | 34.74 | 18h30 | 1.6861 | 1.5574 | 0.87013 | 0.70562 | 0.43425
19h30 | 118.98 | 109.23 | 61.21 | 48.63 | 28.94 | 19h30 | 1.4872 | 1.3654 | 0.76513 | 0.60788 | 0.36175
20h30 | 116.1 | 106.42 | 60.08 | 48.13 | 29.47 | 20h30 | 1.4512 | 1.3302 | 0.751 | 0.60162 | 0.36838
21h30 | 131.37 | 121.49 | 69.57 | 57.89 | 39.18 | 21h30 | 1.6421 | 1.5186 | 0.86962 | 0.72362 | 0.48975
22h30 | 142.64 | 132.45 | 76.77 | 64.79 | 46.27 | 22h30 | 1.783 | 1.6556 | 0.95962 | 0.80988 | 0.57837
23h30 | 146.71 | 136.11 | 79.62 | 67.22 | 49.29 | 23h30 | 1.8339 | 1.7014 | 0.99525 | 0.84025 | 0.61613
00h30 | 123.35 | 113.97 | 61.78 | 51.46 | 37.07 | 00h30 | 1.5419 | 1.4246 | 0.77225 | 0.64325 | 0.46337
01h30 | 115.34 | 105.13 | 59.66 | 44.88 | 28.89 | 01h30 | 1.4418 | 1.3141 | 0.74575 | 0.561 | 0.36112
02h30 | 116.48 | 104.34 | 59.06 | 44.88 | 29.06 | 02h30 | 1.456 | 1.3042 | 0.73825 | 0.561 | 0.36325
03h30 | 123.05 | 111.29 | 64.33 | 49.72 | 33.93 | 03h30 | 1.5381 | 1.3911 | 0.80412 | 0.6215 | 0.42412
04h30 | 120.42 | 108.44 | 63.6 | 49.72 | 33.76 | 04h30 | 1.5052 | 1.3555 | 0.795 | 0.6215 | 0.422
05h30 | 114.75 | 102.26 | 58.51 | 44.82 | 29.28 | 05h30 | 1.4344 | 1.2783 | 0.73137 | 0.56025 | 0.366
06h30 | 105.03 | 90.96 | 58.51 | 44.82 | 29.28 | 06h30 | 1.3129 | 1.137 | 0.73137 | 0.56025 | 0.366
07h30 | 116 | 100.87 | 57.46 | 46.42 | 29 | 07h30 | 1.45 | 1.2609 | 0.71825 | 0.58025 | 0.3625
08h30 | 116.08 | 101.4 | 57.46 | 46.42 | 29 | 08h30 | 1.451 | 1.2675 | 0.71825 | 0.58025 | 0.3625
09h30 | 115.08 | 98.97 | 49.25 | 39.59 | 19.09 | 09h30 | 1.4385 | 1.2371 | 0.61562 | 0.49488 | 0.23863
10h30 | 104.89 | 87.5 | 49.25 | 39.59 | 19.09 | 10h30 | 1.3111 | 1.0938 | 0.61562 | 0.49488 | 0.23863
11h30 | 92.31 | 76.17 | 35.21 | 26.75 | 6.26 | 11h30 | 1.1539 | 0.95212 | 0.44012 | 0.33437 | 0.07825
12h30 | 84.74 | 75.44 | 35.21 | 26.75 | 6.26 | 12h30 | 1.0593 | 0.943 | 0.44012 | 0.33437 | 0.07825
13h30 | 70.96 | 58.72 | 21 | 15.11 | 0 | 13h30 | 0.887 | 0.734 | 0.2625 | 0.18887 | 0
14h30 | 70.96 | 58.72 | 21 | 15.11 | 0 | 14h30 | 0.887 | 0.734 | 0.2625 | 0.18887 | 0
15h30 | 59.34 | 46.98 | 10.07 | 4.23 | 0 | 15h30 | 0.74175 | 0.58725 | 0.12587 | 0.052875 | 0
16h30 | 59.47 | 47.81 | 11.61 | 5.35 | 0 | 16h30 | 0.74338 | 0.59762 | 0.14513 | 0.066875 | 0
17h30 | 61.12 | 51.08 | 14.76 | 8.15 | 0 | 17h30 | 0.764 | 0.6385 | 0.1845 | 0.10187 | 0
18h30 | 74.63 | 66.22 | 26.18 | 18.89 | 2.8 | 18h30 | 0.93288 | 0.82775 | 0.32725 | 0.23613 | 0.035
19h30 | 79.34 | 72.25 | 32.54 | 24.03 | 7.9 | 19h30 | 0.99175 | 0.90312 | 0.40675 | 0.30038 | 0.09875
20h30 | 71.02 | 64.82 | 30.3 | 20.99 | 6.87 | 20h30 | 0.88775 | 0.81025 | 0.37875 | 0.26238 | 0.085875
21h30 | 69.87 | 64.09 | 31.35 | 21.48 | 8.68 | 21h30 | 0.87338 | 0.80112 | 0.39187 | 0.2685 | 0.1085
22h30 | 64.55 | 55.56 | 24.81 | 14.19 | 6.9 | 22h30 | 0.80688 | 0.6945 | 0.31012 | 0.17738 | 0.08625
23h30 | 44.27 | 38.51 | 17.88 | 6.85 | 0 | 23h30 | 0.55337 | 0.48137 | 0.2235 | 0.085625 | 0
00h30 | 44.27 | 38.51 | 13.7 | 5.33 | 0 | 00h30 | 0.55337 | 0.48137 | 0.17125 | 0.066625 | 0
01h30 | 43.46 | 35.67 | 14.01 | 1.31 | 0 | 01h30 | 0.54325 | 0.44588 | 0.17513 | 0.016375 | 0
02h30 | 50.71 | 41.79 | 18.73 | 5.91 | 0 | 02h30 | 0.63387 | 0.52238 | 0.23412 | 0.073875 | 0
03h30 | 57.32 | 47.86 | 23.62 | 10.19 | 0.05 | 03h30 | 0.7165 | 0.59825 | 0.29525 | 0.12737 | 0.000625
04h30 | 52.28 | 42.51 | 21.2 | 8.07 | 0.05 | 04h30 | 0.6535 | 0.53138 | 0.265 | 0.10088 | 0.000625
05h30 | 40.54 | 30.28 | 13.74 | 2.48 | 0 | 05h30 | 0.50675 | 0.3785 | 0.17175 | 0.031 | 0
06h30 | 38.88 | 29.5 | 11.49 | 0.15 | 0 | 06h30 | 0.486 | 0.36875 | 0.14363 | 0.001875 | 0
07h30 | 64.38 | 54.3 | 32.47 | 21.67 | 11.02 | 07h30 | 0.80475 | 0.67875 | 0.40587 | 0.27087 | 0.13775
08h30 | 63.84 | 54.3 | 32.41 | 21.53 | 11.02 | 08h30 | 0.798 | 0.67875 | 0.40513 | 0.26913 | 0.13775
09h30 | 57.04 | 47.08 | 22.67 | 13.21 | 1.01 | 09h30 | 0.713 | 0.5885 | 0.28337 | 0.16512 | 0.012625
10h30 | 57.04 | 47.08 | 22.67 | 13.21 | 1.01 | 10h30 | 0.713 | 0.5885 | 0.28337 | 0.16512 | 0.012625
11h30 | 23.11 | 11.22 | 0 | 0 | 0 | 11h30 | 0.28887 | 0.14025 | 0 | 0 | 0
12h30 | 23.11 | 11.22 | 0 | 0 | 0 | 12h30 | 0.28887 | 0.14025 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 32.97 | 22.24 | 8.31 | 0 | 0 | 23h30 | 0.41213 | 0.278 | 0.10387 | 0 | 0
00h30 | 46.8 | 36.61 | 12.63 | 0 | 0 | 00h30 | 0.585 | 0.45763 | 0.15787 | 0 | 0
01h30 | 44.89 | 29.61 | 10.13 | 0 | 0 | 01h30 | 0.56112 | 0.37012 | 0.12662 | 0 | 0
02h30 | 31.06 | 15.25 | 5.81 | 0 | 0 | 02h30 | 0.38825 | 0.19062 | 0.072625 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0.46 | 0 | 0 | 0 | 0 | 04h30 | 0.00575 | 0 | 0 | 0 | 0
05h30 | 0.46 | 0 | 0 | 0 | 0 | 05h30 | 0.00575 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 12.39 | 0 | 0 | 0 | 0 | 09h30 | 0.15488 | 0 | 0 | 0 | 0
10h30 | 47.56 | 31.97 | 4.19 | 0 | 0 | 10h30 | 0.5945 | 0.39963 | 0.052375 | 0 | 0
11h30 | 51.55 | 31.97 | 4.19 | 0 | 0 | 11h30 | 0.64438 | 0.39963 | 0.052375 | 0 | 0
12h30 | 60.46 | 42.05 | 8.74 | 0 | 0 | 12h30 | 0.75575 | 0.52563 | 0.10925 | 0 | 0
13h30 | 55.34 | 42.05 | 8.74 | 0 | 0 | 13h30 | 0.69175 | 0.52563 | 0.10925 | 0 | 0
14h30 | 50.1 | 35 | 2.55 | 0 | 0 | 14h30 | 0.62625 | 0.4375 | 0.031875 | 0 | 0
15h30 | 50.75 | 35.77 | 2.55 | 0 | 0 | 15h30 | 0.63438 | 0.44712 | 0.031875 | 0 | 0
16h30 | 48.87 | 34.88 | 0.62 | 0 | 0 | 16h30 | 0.61087 | 0.436 | 0.00775 | 0 | 0
17h30 | 52.8 | 40.28 | 3.99 | 0 | 0 | 17h30 | 0.66 | 0.5035 | 0.049875 | 0 | 0
18h30 | 65.09 | 54.17 | 15.24 | 0 | 0 | 18h30 | 0.81363 | 0.67712 | 0.1905 | 0 | 0
19h30 | 76.23 | 66.77 | 27.09 | 7.58 | 0 | 19h30 | 0.95288 | 0.83462 | 0.33863 | 0.09475 | 0
20h30 | 33.4 | 24.91 | 15.23 | 7.58 | 0 | 20h30 | 0.4175 | 0.31138 | 0.19037 | 0.09475 | 0
21h30 | 6.43 | 6.14 | 0 | 0 | 0 | 21h30 | 0.080375 | 0.07675 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 31.18 | 11.38 | 0 | 0 | 0 | 07h30 | 0.38975 | 0.14225 | 0 | 0 | 0
08h30 | 62.27 | 43.54 | 13.26 | 0 | 0 | 08h30 | 0.77838 | 0.54425 | 0.16575 | 0 | 0
09h30 | 63.55 | 41.86 | 13.26 | 0 | 0 | 09h30 | 0.79438 | 0.52325 | 0.16575 | 0 | 0
10h30 | 57.01 | 36.51 | 6.01 | 0 | 0 | 10h30 | 0.71262 | 0.45637 | 0.075125 | 0 | 0
11h30 | 42.54 | 26.81 | 6.01 | 0 | 0 | 11h30 | 0.53175 | 0.33513 | 0.075125 | 0 | 0
12h30 | 58.65 | 41.65 | 10.24 | 0 | 0 | 12h30 | 0.73313 | 0.52063 | 0.128 | 0 | 0
13h30 | 88.25 | 71.61 | 28.28 | 9.35 | 0 | 13h30 | 1.1031 | 0.89512 | 0.3535 | 0.11688 | 0
14h30 | 74.97 | 58.77 | 19.07 | 9.35 | 0 | 14h30 | 0.93712 | 0.73462 | 0.23838 | 0.11688 | 0
15h30 | 39.6 | 28.81 | 1.03 | 0 | 0 | 15h30 | 0.495 | 0.36012 | 0.012875 | 0 | 0
16h30 | 30 | 16.65 | 0 | 0 | 0 | 16h30 | 0.375 | 0.20813 | 0 | 0 | 0
17h30 | 34.54 | 21.37 | 0 | 0 | 0 | 17h30 | 0.43175 | 0.26713 | 0 | 0 | 0
18h30 | 58.2 | 45.94 | 11.76 | 0 | 0 | 18h30 | 0.7275 | 0.57425 | 0.147 | 0 | 0
19h30 | 78.14 | 67.39 | 27.15 | 7.38 | 0 | 19h30 | 0.97675 | 0.84237 | 0.33937 | 0.09225 | 0
20h30 | 73.92 | 64.27 | 28.08 | 7.38 | 0 | 20h30 | 0.924 | 0.80337 | 0.351 | 0.09225 | 0
21h30 | 68.55 | 59.48 | 27.26 | 6.77 | 0 | 21h30 | 0.85688 | 0.7435 | 0.34075 | 0.084625 | 0
22h30 | 73.43 | 64.6 | 31.94 | 11.29 | 0 | 22h30 | 0.91787 | 0.8075 | 0.39925 | 0.14113 | 0
23h30 | 76.57 | 67.79 | 34.78 | 14.7 | 0 | 23h30 | 0.95713 | 0.84737 | 0.43475 | 0.18375 | 0
00h30 | 34.47 | 24.57 | 17.41 | 10.17 | 0 | 00h30 | 0.43088 | 0.30712 | 0.21763 | 0.12712 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 32.37 | 15.9 | 1.27 | 0 | 0 | 06h30 | 0.40463 | 0.19875 | 0.015875 | 0 | 0
07h30 | 87.29 | 74.36 | 42.76 | 24.37 | 6.4 | 07h30 | 1.0911 | 0.9295 | 0.5345 | 0.30462 | 0.08
08h30 | 80.4 | 66.69 | 41.49 | 24.37 | 6.4 | 08h30 | 1.005 | 0.83362 | 0.51863 | 0.30462 | 0.08
09h30 | 66.28 | 52.18 | 24.35 | 4.6 | 0 | 09h30 | 0.8285 | 0.65225 | 0.30438 | 0.0575 | 0
10h30 | 49.73 | 43.95 | 24.35 | 4.6 | 0 | 10h30 | 0.62162 | 0.54937 | 0.30438 | 0.0575 | 0
11h30 | 45.78 | 30.59 | 6.72 | 0 | 0 | 11h30 | 0.57225 | 0.38238 | 0.084 | 0 | 0
12h30 | 69.93 | 53.76 | 21.79 | 5.21 | 0 | 12h30 | 0.87413 | 0.672 | 0.27237 | 0.065125 | 0
13h30 | 99.18 | 82.49 | 38.35 | 21.99 | 2.27 | 13h30 | 1.2397 | 1.0311 | 0.47937 | 0.27487 | 0.028375
14h30 | 91.69 | 75.14 | 33.36 | 16.79 | 2.27 | 14h30 | 1.1461 | 0.93925 | 0.417 | 0.20988 | 0.028375
15h30 | 69.06 | 53.04 | 19.39 | 2.88 | 0 | 15h30 | 0.86325 | 0.663 | 0.24238 | 0.036 | 0
16h30 | 60.47 | 45.18 | 13.89 | 2.88 | 0 | 16h30 | 0.75587 | 0.56475 | 0.17363 | 0.036 | 0
17h30 | 77.65 | 63.39 | 25.45 | 9.71 | 0 | 17h30 | 0.97062 | 0.79238 | 0.31812 | 0.12137 | 0
18h30 | 95.27 | 82.67 | 39.97 | 22.01 | 3.2 | 18h30 | 1.1909 | 1.0334 | 0.49962 | 0.27513 | 0.04
19h30 | 88.23 | 77.33 | 39.42 | 21.32 | 3.2 | 19h30 | 1.1029 | 0.96662 | 0.49275 | 0.2665 | 0.04
20h30 | 79.41 | 69.71 | 36.22 | 19.28 | 1.96 | 20h30 | 0.99262 | 0.87138 | 0.45275 | 0.241 | 0.0245
21h30 | 70.79 | 61.87 | 32.36 | 15.83 | 1.96 | 21h30 | 0.88487 | 0.77338 | 0.4045 | 0.19787 | 0.0245
22h30 | 67.22 | 58.82 | 31.31 | 14.82 | 0.93 | 22h30 | 0.84025 | 0.73525 | 0.39137 | 0.18525 | 0.011625
23h30 | 70.92 | 62.63 | 34.52 | 17.65 | 4.38 | 23h30 | 0.8865 | 0.78287 | 0.4315 | 0.22062 | 0.05475
00h30 | 57.69 | 48.56 | 21.14 | 8.4 | 3.45 | 00h30 | 0.72113 | 0.607 | 0.26425 | 0.105 | 0.043125
01h30 | 66.28 | 54.51 | 27.63 | 9.39 | 0 | 01h30 | 0.8285 | 0.68137 | 0.34537 | 0.11737 | 0
02h30 | 70.3 | 57.11 | 29.27 | 11.91 | 0 | 02h30 | 0.87875 | 0.71388 | 0.36588 | 0.14888 | 0
03h30 | 72.03 | 59.82 | 31.79 | 14.56 | 0.43 | 03h30 | 0.90038 | 0.74775 | 0.39737 | 0.182 | 0.005375
04h30 | 71.08 | 59.33 | 32.03 | 15.52 | 1.66 | 04h30 | 0.8885 | 0.74162 | 0.40037 | 0.194 | 0.02075
05h30 | 68.12 | 55.99 | 29.98 | 14.29 | 1.23 | 05h30 | 0.8515 | 0.69988 | 0.37475 | 0.17863 | 0.015375
06h30 | 65.8 | 52.97 | 27.58 | 12.53 | 0 | 06h30 | 0.8225 | 0.66212 | 0.34475 | 0.15662 | 0
07h30 | 77.84 | 65.41 | 39.03 | 25.56 | 12.59 | 07h30 | 0.973 | 0.81763 | 0.48788 | 0.3195 | 0.15737
08h30 | 68.09 | 63.83 | 38.07 | 23.84 | 12.59 | 08h30 | 0.85113 | 0.79788 | 0.47587 | 0.298 | 0.15737
09h30 | 49.9 | 37.31 | 14.01 | 2.11 | 0 | 09h30 | 0.62375 | 0.46637 | 0.17513 | 0.026375 | 0
10h30 | 49.9 | 37.31 | 14.01 | 2.11 | 0 | 10h30 | 0.62375 | 0.46637 | 0.17513 | 0.026375 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 13.43 | 0 | 0 | 0 | 0 | 12h30 | 0.16787 | 0 | 0 | 0 | 0
13h30 | 16.7 | 0.63 | 0 | 0 | 0 | 13h30 | 0.20875 | 0.007875 | 0 | 0 | 0
14h30 | 32.67 | 15.9 | 0 | 0 | 0 | 14h30 | 0.40837 | 0.19875 | 0 | 0 | 0
15h30 | 31.94 | 15.71 | 0 | 0 | 0 | 15h30 | 0.39925 | 0.19637 | 0 | 0 | 0
16h30 | 53.89 | 38.9 | 8.39 | 0 | 0 | 16h30 | 0.67363 | 0.48625 | 0.10487 | 0 | 0
17h30 | 68.07 | 54.53 | 18.52 | 6.52 | 0 | 17h30 | 0.85088 | 0.68163 | 0.2315 | 0.0815 | 0
18h30 | 61.71 | 49.74 | 17.02 | 6.52 | 0 | 18h30 | 0.77138 | 0.62175 | 0.21275 | 0.0815 | 0
19h30 | 53.48 | 43.06 | 15.67 | 3.08 | 0 | 19h30 | 0.6685 | 0.53825 | 0.19587 | 0.0385 | 0
20h30 | 57.71 | 48.52 | 21.3 | 8.13 | 0 | 20h30 | 0.72137 | 0.6065 | 0.26625 | 0.10162 | 0
21h30 | 70.75 | 62.31 | 30.92 | 17.72 | 3.57 | 21h30 | 0.88438 | 0.77887 | 0.3865 | 0.2215 | 0.044625
22h30 | 78 | 69.96 | 36.49 | 23.11 | 8.12 | 22h30 | 0.975 | 0.8745 | 0.45613 | 0.28887 | 0.1015
23h30 | 83.11 | 75.36 | 40.58 | 26.96 | 12.21 | 23h30 | 1.0389 | 0.942 | 0.50725 | 0.337 | 0.15263
00h30 | 68.42 | 58.74 | 25.69 | 16.52 | 7.66 | 00h30 | 0.85525 | 0.73425 | 0.32112 | 0.2065 | 0.09575
01h30 | 58.87 | 47.23 | 21.89 | 6.51 | 0 | 01h30 | 0.73587 | 0.59037 | 0.27363 | 0.081375 | 0
02h30 | 58.39 | 46.94 | 22.09 | 7.07 | 0 | 02h30 | 0.72988 | 0.58675 | 0.27613 | 0.088375 | 0
03h30 | 66.53 | 55.21 | 28.12 | 13.27 | 0.79 | 03h30 | 0.83162 | 0.69012 | 0.3515 | 0.16587 | 0.009875
04h30 | 63.03 | 51.7 | 26.53 | 12.71 | 0.79 | 04h30 | 0.78787 | 0.64625 | 0.33163 | 0.15887 | 0.009875
05h30 | 67.83 | 55.29 | 27.61 | 14.15 | 0.92 | 05h30 | 0.84788 | 0.69112 | 0.34513 | 0.17688 | 0.0115
06h30 | 69.07 | 54.03 | 25.78 | 14.15 | 0.92 | 06h30 | 0.86338 | 0.67537 | 0.32225 | 0.17688 | 0.0115
07h30 | 83.99 | 68.38 | 34.7 | 23.74 | 8.13 | 07h30 | 1.0499 | 0.85475 | 0.43375 | 0.29675 | 0.10162
08h30 | 61.39 | 46.29 | 34.7 | 23.74 | 8.13 | 08h30 | 0.76738 | 0.57862 | 0.43375 | 0.29675 | 0.10162
09h30 | 37.61 | 21.76 | 1.78 | 0 | 0 | 09h30 | 0.47013 | 0.272 | 0.02225 | 0 | 0
10h30 | 32.52 | 18.74 | 1.78 | 0 | 0 | 10h30 | 0.4065 | 0.23425 | 0.02225 | 0 | 0
11h30 | 40.46 | 25.72 | 0 | 0 | 0 | 11h30 | 0.50575 | 0.3215 | 0 | 0 | 0
12h30 | 29.12 | 25.72 | 0 | 0 | 0 | 12h30 | 0.364 | 0.3215 | 0 | 0 | 0
13h30 | 27.3 | 14.66 | 0 | 0 | 0 | 13h30 | 0.34125 | 0.18325 | 0 | 0 | 0
14h30 | 67.04 | 55.37 | 18.62 | 9.75 | 0 | 14h30 | 0.838 | 0.69212 | 0.23275 | 0.12187 | 0
15h30 | 44.15 | 40.71 | 18.62 | 9.75 | 0 | 15h30 | 0.55188 | 0.50887 | 0.23275 | 0.12187 | 0
16h30 | 37.41 | 29.42 | 1.58 | 0 | 0 | 16h30 | 0.46763 | 0.36775 | 0.01975 | 0 | 0
17h30 | 38.92 | 29.86 | 1.58 | 0 | 0 | 17h30 | 0.4865 | 0.37325 | 0.01975 | 0 | 0
18h30 | 52.27 | 43.63 | 9.98 | 0.46 | 0 | 18h30 | 0.65338 | 0.54538 | 0.12475 | 0.00575 | 0
19h30 | 66.13 | 58.7 | 22.62 | 10.6 | 0 | 19h30 | 0.82663 | 0.73375 | 0.28275 | 0.1325 | 0
20h30 | 50.08 | 43.39 | 16.28 | 10.14 | 0 | 20h30 | 0.626 | 0.54238 | 0.2035 | 0.12675 | 0
21h30 | 30.29 | 27.87 | 3.65 | 0 | 0 | 21h30 | 0.37862 | 0.34837 | 0.045625 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 10.8 | 2.7 | 0 | 0 | 0 | 01h30 | 0.135 | 0.03375 | 0 | 0 | 0
02h30 | 10.8 | 2.7 | 0 | 0 | 0 | 02h30 | 0.135 | 0.03375 | 0 | 0 | 0
03h30 | 16.67 | 4.07 | 0 | 0 | 0 | 03h30 | 0.20838 | 0.050875 | 0 | 0 | 0
04h30 | 21.93 | 9.39 | 0 | 0 | 0 | 04h30 | 0.27413 | 0.11737 | 0 | 0 | 0
05h30 | 29.37 | 16.09 | 1.88 | 0 | 0 | 05h30 | 0.36712 | 0.20112 | 0.0235 | 0 | 0
06h30 | 44.57 | 30.62 | 9.86 | 0 | 0 | 06h30 | 0.55712 | 0.38275 | 0.12325 | 0 | 0
07h30 | 74.24 | 61.16 | 33.27 | 19.12 | 3.55 | 07h30 | 0.928 | 0.7645 | 0.41587 | 0.239 | 0.044375
08h30 | 76.17 | 64.73 | 32.26 | 19.12 | 3.55 | 08h30 | 0.95212 | 0.80912 | 0.40325 | 0.239 | 0.044375
09h30 | 73.65 | 61.65 | 29.27 | 15.66 | 0 | 09h30 | 0.92063 | 0.77063 | 0.36588 | 0.19575 | 0
10h30 | 59.73 | 45.76 | 22.31 | 15.66 | 0 | 10h30 | 0.74662 | 0.572 | 0.27887 | 0.19575 | 0
11h30 | 47.05 | 32.16 | 9.52 | 0 | 0 | 11h30 | 0.58813 | 0.402 | 0.119 | 0 | 0
12h30 | 38.58 | 24.63 | 9.52 | 0 | 0 | 12h30 | 0.48225 | 0.30788 | 0.119 | 0 | 0
13h30 | 18.08 | 3.1 | 0 | 0 | 0 | 13h30 | 0.226 | 0.03875 | 0 | 0 | 0
14h30 | 18.08 | 3.1 | 0 | 0 | 0 | 14h30 | 0.226 | 0.03875 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 2.6 | 0 | 0 | 0 | 0 | 20h30 | 0.0325 | 0 | 0 | 0 | 0
21h30 | 2.6 | 0 | 0 | 0 | 0 | 21h30 | 0.0325 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 8.52 | 0 | 0 | 0 | 0 | 03h30 | 0.1065 | 0 | 0 | 0 | 0
04h30 | 8.52 | 0 | 0 | 0 | 0 | 04h30 | 0.1065 | 0 | 0 | 0 | 0
05h30 | 8.33 | 0 | 0 | 0 | 0 | 05h30 | 0.10412 | 0 | 0 | 0 | 0
06h30 | 12.41 | 0 | 0 | 0 | 0 | 06h30 | 0.15513 | 0 | 0 | 0 | 0
07h30 | 28.97 | 16.14 | 1.22 | 0 | 0 | 07h30 | 0.36212 | 0.20175 | 0.01525 | 0 | 0
08h30 | 24.89 | 16.14 | 1.22 | 0 | 0 | 08h30 | 0.31112 | 0.20175 | 0.01525 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 20.21 | 10.7 | 0 | 0 | 0 | 12h30 | 0.25262 | 0.13375 | 0 | 0 | 0
13h30 | 25.84 | 11.63 | 0 | 0 | 0 | 13h30 | 0.323 | 0.14538 | 0 | 0 | 0
14h30 | 28.35 | 14.47 | 0 | 0 | 0 | 14h30 | 0.35437 | 0.18088 | 0 | 0 | 0
15h30 | 26.01 | 13.68 | 0 | 0 | 0 | 15h30 | 0.32512 | 0.171 | 0 | 0 | 0
16h30 | 21.99 | 10.77 | 0 | 0 | 0 | 16h30 | 0.27487 | 0.13462 | 0 | 0 | 0
17h30 | 20.83 | 10.67 | 0 | 0 | 0 | 17h30 | 0.26038 | 0.13337 | 0 | 0 | 0
18h30 | 2.14 | 0.04 | 0 | 0 | 0 | 18h30 | 0.02675 | 0.0005 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 12.52 | 1.59 | 0 | 0 | 0 | 02h30 | 0.1565 | 0.019875 | 0 | 0 | 0
03h30 | 54.1 | 42.12 | 13.66 | 0 | 0 | 03h30 | 0.67625 | 0.5265 | 0.17075 | 0 | 0
04h30 | 52.88 | 40.54 | 13.66 | 0 | 0 | 04h30 | 0.661 | 0.50675 | 0.17075 | 0 | 0
05h30 | 30.91 | 16.36 | 0 | 0 | 0 | 05h30 | 0.38638 | 0.2045 | 0 | 0 | 0
06h30 | 19.61 | 16.36 | 0 | 0 | 0 | 06h30 | 0.24513 | 0.2045 | 0 | 0 | 0
07h30 | 30.13 | 14.83 | 0 | 0 | 0 | 07h30 | 0.37662 | 0.18538 | 0 | 0 | 0
08h30 | 30.13 | 14.83 | 0 | 0 | 0 | 08h30 | 0.37662 | 0.18538 | 0 | 0 | 0
09h30 | 17.31 | 0.33 | 0 | 0 | 0 | 09h30 | 0.21638 | 0.004125 | 0 | 0 | 0
10h30 | 23.74 | 7.21 | 0 | 0 | 0 | 10h30 | 0.29675 | 0.090125 | 0 | 0 | 0
11h30 | 32.72 | 17.55 | 0 | 0 | 0 | 11h30 | 0.409 | 0.21937 | 0 | 0 | 0
12h30 | 26.29 | 10.68 | 0 | 0 | 0 | 12h30 | 0.32863 | 0.1335 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 5.96 | 0 | 0 | 0 | 0 | 02h30 | 0.0745 | 0 | 0 | 0 | 0
03h30 | 10.18 | 0 | 0 | 0 | 0 | 03h30 | 0.12725 | 0 | 0 | 0 | 0
04h30 | 12.07 | 0 | 0 | 0 | 0 | 04h30 | 0.15088 | 0 | 0 | 0 | 0
05h30 | 8.59 | 0 | 0 | 0 | 0 | 05h30 | 0.10737 | 0 | 0 | 0 | 0
06h30 | 3.37 | 0 | 0 | 0 | 0 | 06h30 | 0.042125 | 0 | 0 | 0 | 0
07h30 | 30.56 | 14.13 | 0 | 0 | 0 | 07h30 | 0.382 | 0.17663 | 0 | 0 | 0
08h30 | 44.19 | 28.29 | 0 | 0 | 0 | 08h30 | 0.55237 | 0.35363 | 0 | 0 | 0
09h30 | 52.76 | 35.67 | 2.45 | 0 | 0 | 09h30 | 0.6595 | 0.44588 | 0.030625 | 0 | 0
10h30 | 47.57 | 29.59 | 2.45 | 0 | 0 | 10h30 | 0.59462 | 0.36988 | 0.030625 | 0 | 0
11h30 | 37.21 | 19.33 | 0 | 0 | 0 | 11h30 | 0.46513 | 0.24163 | 0 | 0 | 0
12h30 | 28.6 | 11.47 | 0 | 0 | 0 | 12h30 | 0.3575 | 0.14338 | 0 | 0 | 0
13h30 | 25.38 | 8.74 | 0 | 0 | 0 | 13h30 | 0.31725 | 0.10925 | 0 | 0 | 0
14h30 | 22.9 | 8.51 | 0 | 0 | 0 | 14h30 | 0.28625 | 0.10637 | 0 | 0 | 0
15h30 | 8.54 | 0 | 0 | 0 | 0 | 15h30 | 0.10675 | 0 | 0 | 0 | 0
16h30 | 8.54 | 0 | 0 | 0 | 0 | 16h30 | 0.10675 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 3.14 | 0 | 0 | 0 | 0 | 23h30 | 0.03925 | 0 | 0 | 0 | 0
00h30 | 3.14 | 0 | 0 | 0 | 0 | 00h30 | 0.03925 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 1.78 | 0 | 0 | 0 | 0 | 03h30 | 0.02225 | 0 | 0 | 0 | 0
04h30 | 1.78 | 0 | 0 | 0 | 0 | 04h30 | 0.02225 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 16.4 | 0 | 0 | 0 | 0 | 07h30 | 0.205 | 0 | 0 | 0 | 0
08h30 | 24.78 | 9.07 | 0 | 0 | 0 | 08h30 | 0.30975 | 0.11338 | 0 | 0 | 0
09h30 | 38.57 | 20.91 | 0 | 0 | 0 | 09h30 | 0.48213 | 0.26138 | 0 | 0 | 0
10h30 | 50.34 | 30.86 | 0.33 | 0 | 0 | 10h30 | 0.62925 | 0.38575 | 0.004125 | 0 | 0
11h30 | 61.04 | 41.16 | 6.25 | 0 | 0 | 11h30 | 0.763 | 0.5145 | 0.078125 | 0 | 0
12h30 | 51.27 | 32.51 | 5.92 | 0 | 0 | 12h30 | 0.64087 | 0.40637 | 0.074 | 0 | 0
13h30 | 12.11 | 10.37 | 0 | 0 | 0 | 13h30 | 0.15138 | 0.12962 | 0 | 0 | 0
14h30 | 1.73 | 0 | 0 | 0 | 0 | 14h30 | 0.021625 | 0 | 0 | 0 | 0
15h30 | 13.11 | 0 | 0 | 0 | 0 | 15h30 | 0.16387 | 0 | 0 | 0 | 0
16h30 | 13.11 | 0 | 0 | 0 | 0 | 16h30 | 0.16387 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 10.7 | 0 | 0 | 0 | 0 | 20h30 | 0.13375 | 0 | 0 | 0 | 0
21h30 | 13.31 | 1.05 | 0 | 0 | 0 | 21h30 | 0.16637 | 0.013125 | 0 | 0 | 0
22h30 | 2.61 | 1.05 | 0 | 0 | 0 | 22h30 | 0.032625 | 0.013125 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 3.95 | 0 | 0 | 0 | 0 | 02h30 | 0.049375 | 0 | 0 | 0 | 0
03h30 | 7.33 | 0 | 0 | 0 | 0 | 03h30 | 0.091625 | 0 | 0 | 0 | 0
04h30 | 8.79 | 0 | 0 | 0 | 0 | 04h30 | 0.10988 | 0 | 0 | 0 | 0
05h30 | 13.37 | 0 | 0 | 0 | 0 | 05h30 | 0.16712 | 0 | 0 | 0 | 0
06h30 | 13.43 | 0 | 0 | 0 | 0 | 06h30 | 0.16787 | 0 | 0 | 0 | 0
07h30 | 21.21 | 4.47 | 0 | 0 | 0 | 07h30 | 0.26512 | 0.055875 | 0 | 0 | 0
08h30 | 15.75 | 4.47 | 0 | 0 | 0 | 08h30 | 0.19687 | 0.055875 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 5.62 | 0 | 0 | 0 | 0 | 10h30 | 0.07025 | 0 | 0 | 0 | 0
11h30 | 13.47 | 0 | 0 | 0 | 0 | 11h30 | 0.16837 | 0 | 0 | 0 | 0
12h30 | 11.42 | 0 | 0 | 0 | 0 | 12h30 | 0.14275 | 0 | 0 | 0 | 0
13h30 | 3.57 | 0 | 0 | 0 | 0 | 13h30 | 0.044625 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 1.66 | 0 | 0 | 0 | 0 | 20h30 | 0.02075 | 0 | 0 | 0 | 0
21h30 | 4.26 | 0 | 0 | 0 | 0 | 21h30 | 0.05325 | 0 | 0 | 0 | 0
22h30 | 2.6 | 0 | 0 | 0 | 0 | 22h30 | 0.0325 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0.41 | 0 | 0 | 0 | 0 | 07h30 | 0.005125 | 0 | 0 | 0 | 0
08h30 | 0.93 | 0 | 0 | 0 | 0 | 08h30 | 0.011625 | 0 | 0 | 0 | 0
09h30 | 0.52 | 0 | 0 | 0 | 0 | 09h30 | 0.0065 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 1.95 | 0 | 0 | 0 | 0 | 20h30 | 0.024375 | 0 | 0 | 0 | 0
21h30 | 10.07 | 0 | 0 | 0 | 0 | 21h30 | 0.12587 | 0 | 0 | 0 | 0
22h30 | 21.56 | 7.28 | 0 | 0 | 0 | 22h30 | 0.2695 | 0.091 | 0 | 0 | 0
23h30 | 25.36 | 10.92 | 0 | 0 | 0 | 23h30 | 0.317 | 0.1365 | 0 | 0 | 0
00h30 | 11.92 | 3.63 | 0 | 0 | 0 | 00h30 | 0.149 | 0.045375 | 0 | 0 | 0
01h30 | 11.26 | 0 | 0 | 0 | 0 | 01h30 | 0.14075 | 0 | 0 | 0 | 0
02h30 | 14.58 | 0 | 0 | 0 | 0 | 02h30 | 0.18225 | 0 | 0 | 0 | 0
03h30 | 10.34 | 0 | 0 | 0 | 0 | 03h30 | 0.12925 | 0 | 0 | 0 | 0
04h30 | 11.76 | 0 | 0 | 0 | 0 | 04h30 | 0.147 | 0 | 0 | 0 | 0
05h30 | 20.05 | 5.28 | 0 | 0 | 0 | 05h30 | 0.25062 | 0.066 | 0 | 0 | 0
06h30 | 22.43 | 6.65 | 0 | 0 | 0 | 06h30 | 0.28037 | 0.083125 | 0 | 0 | 0
07h30 | 39 | 23.58 | 0 | 0 | 0 | 07h30 | 0.4875 | 0.29475 | 0 | 0 | 0
08h30 | 31.88 | 22.21 | 0 | 0 | 0 | 08h30 | 0.3985 | 0.27763 | 0 | 0 | 0
09h30 | 13.34 | 0 | 0 | 0 | 0 | 09h30 | 0.16675 | 0 | 0 | 0 | 0
10h30 | 13.34 | 0 | 0 | 0 | 0 | 10h30 | 0.16675 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 1.36 | 0 | 0 | 0 | 0 | 13h30 | 0.017 | 0 | 0 | 0 | 0
14h30 | 1.36 | 0 | 0 | 0 | 0 | 14h30 | 0.017 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0.4 | 0 | 0 | 0 | 0 | 16h30 | 0.005 | 0 | 0 | 0 | 0
17h30 | 0.4 | 0 | 0 | 0 | 0 | 17h30 | 0.005 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 4.26 | 0 | 0 | 0 | 0 | 19h30 | 0.05325 | 0 | 0 | 0 | 0
20h30 | 14.87 | 7.35 | 0 | 0 | 0 | 20h30 | 0.18588 | 0.091875 | 0 | 0 | 0
21h30 | 19.22 | 11.39 | 0 | 0 | 0 | 21h30 | 0.24025 | 0.14238 | 0 | 0 | 0
22h30 | 19.08 | 11.61 | 0 | 0 | 0 | 22h30 | 0.2385 | 0.14513 | 0 | 0 | 0
23h30 | 13.74 | 7.57 | 0 | 0 | 0 | 23h30 | 0.17175 | 0.094625 | 0 | 0 | 0
00h30 | 3.26 | 0 | 0 | 0 | 0 | 00h30 | 0.04075 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0.13 | 0 | 0 | 0 | 0 | 03h30 | 0.001625 | 0 | 0 | 0 | 0
04h30 | 6.05 | 0 | 0 | 0 | 0 | 04h30 | 0.075625 | 0 | 0 | 0 | 0
05h30 | 5.92 | 0 | 0 | 0 | 0 | 05h30 | 0.074 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 2.11 | 0 | 0 | 0 | 0 | 23h30 | 0.026375 | 0 | 0 | 0 | 0
00h30 | 2.11 | 0 | 0 | 0 | 0 | 00h30 | 0.026375 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 5.97 | 0 | 0 | 0 | 0 | 02h30 | 0.074625 | 0 | 0 | 0 | 0
03h30 | 9.32 | 0 | 0 | 0 | 0 | 03h30 | 0.1165 | 0 | 0 | 0 | 0
04h30 | 10.4 | 0 | 0 | 0 | 0 | 04h30 | 0.13 | 0 | 0 | 0 | 0
05h30 | 11.54 | 0 | 0 | 0 | 0 | 05h30 | 0.14425 | 0 | 0 | 0 | 0
06h30 | 5.93 | 0 | 0 | 0 | 0 | 06h30 | 0.074125 | 0 | 0 | 0 | 0
07h30 | 10.22 | 0 | 0 | 0 | 0 | 07h30 | 0.12775 | 0 | 0 | 0 | 0
08h30 | 8.78 | 0 | 0 | 0 | 0 | 08h30 | 0.10975 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 7.95 | 5.79 | 0 | 0 | 0 | 22h30 | 0.099375 | 0.072375 | 0 | 0 | 0
23h30 | 17.78 | 14.85 | 0 | 0 | 0 | 23h30 | 0.22225 | 0.18563 | 0 | 0 | 0
00h30 | 9.84 | 9.06 | 0 | 0 | 0 | 00h30 | 0.123 | 0.11325 | 0 | 0 | 0
01h30 | 5.95 | 1.78 | 0 | 0 | 0 | 01h30 | 0.074375 | 0.02225 | 0 | 0 | 0
02h30 | 17.41 | 11.63 | 0 | 0 | 0 | 02h30 | 0.21763 | 0.14538 | 0 | 0 | 0
03h30 | 28.96 | 21.94 | 0 | 0 | 0 | 03h30 | 0.362 | 0.27425 | 0 | 0 | 0
04h30 | 28.03 | 20.11 | 0 | 0 | 0 | 04h30 | 0.35037 | 0.25138 | 0 | 0 | 0
05h30 | 22.32 | 13.41 | 0 | 0 | 0 | 05h30 | 0.279 | 0.16762 | 0 | 0 | 0
06h30 | 18.17 | 8.1 | 0 | 0 | 0 | 06h30 | 0.22712 | 0.10125 | 0 | 0 | 0
07h30 | 38.19 | 27.54 | 0 | 0 | 0 | 07h30 | 0.47737 | 0.34425 | 0 | 0 | 0
08h30 | 43.61 | 32.92 | 0 | 0 | 0 | 08h30 | 0.54512 | 0.4115 | 0 | 0 | 0
09h30 | 47.23 | 36 | 0 | 0 | 0 | 09h30 | 0.59037 | 0.45 | 0 | 0 | 0
10h30 | 41.08 | 29.22 | 0 | 0 | 0 | 10h30 | 0.5135 | 0.36525 | 0 | 0 | 0
11h30 | 35.87 | 23.98 | 0 | 0 | 0 | 11h30 | 0.44838 | 0.29975 | 0 | 0 | 0
12h30 | 31.39 | 22.64 | 0 | 0 | 0 | 12h30 | 0.39237 | 0.283 | 0 | 0 | 0
13h30 | 24.55 | 14.21 | 0 | 0 | 0 | 13h30 | 0.30688 | 0.17763 | 0 | 0 | 0
14h30 | 23.38 | 14.21 | 0 | 0 | 0 | 14h30 | 0.29225 | 0.17763 | 0 | 0 | 0
15h30 | 13.48 | 3.77 | 0 | 0 | 0 | 15h30 | 0.1685 | 0.047125 | 0 | 0 | 0
16h30 | 13.48 | 3.77 | 0 | 0 | 0 | 16h30 | 0.1685 | 0.047125 | 0 | 0 | 0
17h30 | 8.61 | 0.34 | 0 | 0 | 0 | 17h30 | 0.10762 | 0.00425 | 0 | 0 | 0
18h30 | 8.92 | 1.78 | 0 | 0 | 0 | 18h30 | 0.1115 | 0.02225 | 0 | 0 | 0
19h30 | 15.52 | 9.44 | 0 | 0 | 0 | 19h30 | 0.194 | 0.118 | 0 | 0 | 0
20h30 | 24.7 | 19.28 | 0 | 0 | 0 | 20h30 | 0.30875 | 0.241 | 0 | 0 | 0
21h30 | 30.11 | 24.9 | 0 | 0 | 0 | 21h30 | 0.37638 | 0.31125 | 0 | 0 | 0
22h30 | 37.97 | 32.65 | 0.85 | 0 | 0 | 22h30 | 0.47463 | 0.40813 | 0.010625 | 0 | 0
23h30 | 45.27 | 39.6 | 6.82 | 0 | 0 | 23h30 | 0.56588 | 0.495 | 0.08525 | 0 | 0
00h30 | 27.91 | 20.58 | 5.97 | 0 | 0 | 00h30 | 0.34887 | 0.25725 | 0.074625 | 0 | 0
01h30 | 27.68 | 19.62 | 0 | 0 | 0 | 01h30 | 0.346 | 0.24525 | 0 | 0 | 0
02h30 | 38.66 | 29.74 | 1.16 | 0 | 0 | 02h30 | 0.48325 | 0.37175 | 0.0145 | 0 | 0
03h30 | 47.23 | 37.69 | 6.69 | 0 | 0 | 03h30 | 0.59037 | 0.47113 | 0.083625 | 0 | 0
04h30 | 45.73 | 35.29 | 5.68 | 0 | 0 | 04h30 | 0.57163 | 0.44112 | 0.071 | 0 | 0
05h30 | 34.63 | 22.76 | 0.15 | 0 | 0 | 05h30 | 0.43288 | 0.2845 | 0.001875 | 0 | 0
06h30 | 25.16 | 15.04 | 0 | 0 | 0 | 06h30 | 0.3145 | 0.188 | 0 | 0 | 0
07h30 | 27.81 | 14.14 | 0 | 0 | 0 | 07h30 | 0.34763 | 0.17675 | 0 | 0 | 0
08h30 | 27.81 | 14.14 | 0 | 0 | 0 | 08h30 | 0.34763 | 0.17675 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 16.62 | 6.48 | 0 | 0 | 0 | 12h30 | 0.20775 | 0.081 | 0 | 0 | 0
13h30 | 16.62 | 6.48 | 0 | 0 | 0 | 13h30 | 0.20775 | 0.081 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0.05 | 0 | 0 | 0 | 0 | 18h30 | 0.000625 | 0 | 0 | 0 | 0
19h30 | 0.54 | 0 | 0 | 0 | 0 | 19h30 | 0.00675 | 0 | 0 | 0 | 0
20h30 | 8.71 | 0.82 | 0 | 0 | 0 | 20h30 | 0.10887 | 0.01025 | 0 | 0 | 0
21h30 | 26.51 | 18.74 | 0 | 0 | 0 | 21h30 | 0.33137 | 0.23425 | 0 | 0 | 0
22h30 | 31.46 | 23.6 | 0 | 0 | 0 | 22h30 | 0.39325 | 0.295 | 0 | 0 | 0
23h30 | 13.17 | 5.68 | 0 | 0 | 0 | 23h30 | 0.16462 | 0.071 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0.68 | 0 | 0 | 0 | 0 | 20h30 | 0.0085 | 0 | 0 | 0 | 0
21h30 | 2.4 | 0 | 0 | 0 | 0 | 21h30 | 0.03 | 0 | 0 | 0 | 0
22h30 | 4.16 | 0 | 0 | 0 | 0 | 22h30 | 0.052 | 0 | 0 | 0 | 0
23h30 | 14.67 | 2.95 | 0 | 0 | 0 | 23h30 | 0.18338 | 0.036875 | 0 | 0 | 0
00h30 | 12.22 | 2.95 | 0 | 0 | 0 | 00h30 | 0.15275 | 0.036875 | 0 | 0 | 0
01h30 | 19.17 | 5.35 | 0 | 0 | 0 | 01h30 | 0.23963 | 0.066875 | 0 | 0 | 0
02h30 | 22.56 | 8.68 | 0 | 0 | 0 | 02h30 | 0.282 | 0.1085 | 0 | 0 | 0
03h30 | 20.05 | 5.76 | 0 | 0 | 0 | 03h30 | 0.25062 | 0.072 | 0 | 0 | 0
04h30 | 16.67 | 2.43 | 0 | 0 | 0 | 04h30 | 0.20838 | 0.030375 | 0 | 0 | 0
05h30 | 17.77 | 2.75 | 0 | 0 | 0 | 05h30 | 0.22212 | 0.034375 | 0 | 0 | 0
06h30 | 23.68 | 8.11 | 0 | 0 | 0 | 06h30 | 0.296 | 0.10138 | 0 | 0 | 0
07h30 | 35.29 | 19.9 | 0 | 0 | 0 | 07h30 | 0.44112 | 0.24875 | 0 | 0 | 0
08h30 | 29.38 | 14.54 | 0 | 0 | 0 | 08h30 | 0.36725 | 0.18175 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 18.38 | 7.89 | 0 | 0 | 0 | 20h30 | 0.22975 | 0.098625 | 0 | 0 | 0
21h30 | 39.97 | 29.18 | 0 | 0 | 0 | 21h30 | 0.49962 | 0.36475 | 0 | 0 | 0
22h30 | 51.19 | 41.05 | 0.6 | 0 | 0 | 22h30 | 0.63987 | 0.51313 | 0.0075 | 0 | 0
23h30 | 29.6 | 19.75 | 0.6 | 0 | 0 | 23h30 | 0.37 | 0.24688 | 0.0075 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 9.04 | 0 | 0 | 0 | 0 | 06h30 | 0.113 | 0 | 0 | 0 | 0
07h30 | 58.27 | 41.2 | 10.24 | 0 | 0 | 07h30 | 0.72837 | 0.515 | 0.128 | 0 | 0
08h30 | 55 | 41.2 | 10.24 | 0 | 0 | 08h30 | 0.6875 | 0.515 | 0.128 | 0 | 0
09h30 | 50.25 | 31.6 | 0 | 0 | 0 | 09h30 | 0.62813 | 0.395 | 0 | 0 | 0
10h30 | 44.47 | 31.6 | 0 | 0 | 0 | 10h30 | 0.55588 | 0.395 | 0 | 0 | 0
11h30 | 10.79 | 0 | 0 | 0 | 0 | 11h30 | 0.13487 | 0 | 0 | 0 | 0
12h30 | 10.79 | 0 | 0 | 0 | 0 | 12h30 | 0.13487 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0.91 | 0 | 0 | 0 | 0 | 17h30 | 0.011375 | 0 | 0 | 0 | 0
18h30 | 45.48 | 33.09 | 1.08 | 0 | 0 | 18h30 | 0.5685 | 0.41363 | 0.0135 | 0 | 0
19h30 | 49.01 | 33.09 | 1.08 | 0 | 0 | 19h30 | 0.61262 | 0.41363 | 0.0135 | 0 | 0
20h30 | 55.03 | 38.36 | 4.2 | 0 | 0 | 20h30 | 0.68788 | 0.4795 | 0.0525 | 0 | 0
21h30 | 68.64 | 53.19 | 16.12 | 0 | 0 | 21h30 | 0.858 | 0.66487 | 0.2015 | 0 | 0
22h30 | 83.99 | 69.1 | 27.36 | 0 | 0 | 22h30 | 1.0499 | 0.86375 | 0.342 | 0 | 0
23h30 | 85.81 | 71.59 | 30.39 | 0 | 0 | 23h30 | 1.0726 | 0.89487 | 0.37988 | 0 | 0
00h30 | 52.07 | 36.08 | 14.95 | 0 | 0 | 00h30 | 0.65087 | 0.451 | 0.18688 | 0 | 0
01h30 | 36.6 | 19.06 | 0 | 0 | 0 | 01h30 | 0.4575 | 0.23825 | 0 | 0 | 0
02h30 | 13.9 | 0.29 | 0 | 0 | 0 | 02h30 | 0.17375 | 0.003625 | 0 | 0 | 0
03h30 | 9.5 | 0 | 0 | 0 | 0 | 03h30 | 0.11875 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 8.14 | 0 | 0 | 0 | 0 | 07h30 | 0.10175 | 0 | 0 | 0 | 0
08h30 | 14.43 | 0 | 0 | 0 | 0 | 08h30 | 0.18038 | 0 | 0 | 0 | 0
09h30 | 6.29 | 0 | 0 | 0 | 0 | 09h30 | 0.078625 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 3.12 | 0 | 0 | 0 | 0 | 18h30 | 0.039 | 0 | 0 | 0 | 0
19h30 | 16.66 | 8.22 | 0 | 0 | 0 | 19h30 | 0.20825 | 0.10275 | 0 | 0 | 0
20h30 | 31.37 | 22.87 | 0 | 0 | 0 | 20h30 | 0.39213 | 0.28587 | 0 | 0 | 0
21h30 | 26.01 | 18.37 | 0 | 0 | 0 | 21h30 | 0.32512 | 0.22962 | 0 | 0 | 0
22h30 | 14.1 | 7.34 | 0 | 0 | 0 | 22h30 | 0.17625 | 0.09175 | 0 | 0 | 0
23h30 | 16.84 | 10.3 | 0 | 0 | 0 | 23h30 | 0.2105 | 0.12875 | 0 | 0 | 0
00h30 | 10.92 | 6.68 | 0 | 0 | 0 | 00h30 | 0.1365 | 0.0835 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 8.51 | 0 | 0 | 0 | 0 | 10h30 | 0.10637 | 0 | 0 | 0 | 0
11h30 | 8.51 | 0 | 0 | 0 | 0 | 11h30 | 0.10637 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 11.62 | 0 | 0 | 0 | 0 | 01h30 | 0.14525 | 0 | 0 | 0 | 0
02h30 | 11.62 | 0 | 0 | 0 | 0 | 02h30 | 0.14525 | 0 | 0 | 0 | 0
03h30 | 18.21 | 0 | 0 | 0 | 0 | 03h30 | 0.22762 | 0 | 0 | 0 | 0
04h30 | 26.75 | 3.69 | 0 | 0 | 0 | 04h30 | 0.33437 | 0.046125 | 0 | 0 | 0
05h30 | 28.97 | 4.55 | 0 | 0 | 0 | 05h30 | 0.36212 | 0.056875 | 0 | 0 | 0
06h30 | 28.54 | 3.81 | 0 | 0 | 0 | 06h30 | 0.35675 | 0.047625 | 0 | 0 | 0
07h30 | 45.68 | 22.01 | 0 | 0 | 0 | 07h30 | 0.571 | 0.27513 | 0 | 0 | 0
08h30 | 39.58 | 19.06 | 0 | 0 | 0 | 08h30 | 0.49475 | 0.23825 | 0 | 0 | 0
09h30 | 30.43 | 6.63 | 0 | 0 | 0 | 09h30 | 0.38038 | 0.082875 | 0 | 0 | 0
10h30 | 28.42 | 6.63 | 0 | 0 | 0 | 10h30 | 0.35525 | 0.082875 | 0 | 0 | 0
11h30 | 8.24 | 0 | 0 | 0 | 0 | 11h30 | 0.103 | 0 | 0 | 0 | 0
12h30 | 8.24 | 0 | 0 | 0 | 0 | 12h30 | 0.103 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 6.38 | 0 | 0 | 0 | 0 | 22h30 | 0.07975 | 0 | 0 | 0 | 0
23h30 | 14.64 | 4.39 | 0 | 0 | 0 | 23h30 | 0.183 | 0.054875 | 0 | 0 | 0
00h30 | 8.25 | 4.39 | 0 | 0 | 0 | 00h30 | 0.10312 | 0.054875 | 0 | 0 | 0
01h30 | 11.33 | 0.27 | 0 | 0 | 0 | 01h30 | 0.14163 | 0.003375 | 0 | 0 | 0
02h30 | 20.7 | 8.45 | 0 | 0 | 0 | 02h30 | 0.25875 | 0.10562 | 0 | 0 | 0
03h30 | 27.23 | 13.74 | 0 | 0 | 0 | 03h30 | 0.34037 | 0.17175 | 0 | 0 | 0
04h30 | 42.81 | 28.93 | 0 | 0 | 0 | 04h30 | 0.53512 | 0.36162 | 0 | 0 | 0
05h30 | 59.66 | 45.07 | 0.47 | 0 | 0 | 05h30 | 0.74575 | 0.56337 | 0.005875 | 0 | 0
06h30 | 49.57 | 34.14 | 0.47 | 0 | 0 | 06h30 | 0.61962 | 0.42675 | 0.005875 | 0 | 0
07h30 | 55.46 | 40.14 | 4.83 | 0 | 0 | 07h30 | 0.69325 | 0.50175 | 0.060375 | 0 | 0
08h30 | 50 | 34.74 | 4.83 | 0 | 0 | 08h30 | 0.625 | 0.43425 | 0.060375 | 0 | 0
09h30 | 14.12 | 7.03 | 0 | 0 | 0 | 09h30 | 0.1765 | 0.087875 | 0 | 0 | 0
10h30 | 6.82 | 0 | 0 | 0 | 0 | 10h30 | 0.08525 | 0 | 0 | 0 | 0
11h30 | 37.75 | 22.77 | 0 | 0 | 0 | 11h30 | 0.47187 | 0.28463 | 0 | 0 | 0
12h30 | 42.57 | 25.27 | 0 | 0 | 0 | 12h30 | 0.53212 | 0.31588 | 0 | 0 | 0
13h30 | 40.57 | 23 | 0 | 0 | 0 | 13h30 | 0.50713 | 0.2875 | 0 | 0 | 0
14h30 | 34.24 | 20.5 | 0 | 0 | 0 | 14h30 | 0.428 | 0.25625 | 0 | 0 | 0
15h30 | 25.95 | 10.26 | 0 | 0 | 0 | 15h30 | 0.32438 | 0.12825 | 0 | 0 | 0
16h30 | 25.36 | 10.26 | 0 | 0 | 0 | 16h30 | 0.317 | 0.12825 | 0 | 0 | 0
17h30 | 9.6 | 0 | 0 | 0 | 0 | 17h30 | 0.12 | 0 | 0 | 0 | 0
18h30 | 9.6 | 0 | 0 | 0 | 0 | 18h30 | 0.12 | 0 | 0 | 0 | 0
19h30 | 17.51 | 5.68 | 0 | 0 | 0 | 19h30 | 0.21887 | 0.071 | 0 | 0 | 0
20h30 | 17.51 | 5.68 | 0 | 0 | 0 | 20h30 | 0.21887 | 0.071 | 0 | 0 | 0
21h30 | 22.11 | 12.26 | 0 | 0 | 0 | 21h30 | 0.27637 | 0.15325 | 0 | 0 | 0
22h30 | 61.66 | 51.69 | 14.95 | 0 | 0 | 22h30 | 0.77075 | 0.64612 | 0.18688 | 0 | 0
23h30 | 57.47 | 48.05 | 14.95 | 0 | 0 | 23h30 | 0.71837 | 0.60062 | 0.18688 | 0 | 0
00h30 | 36.76 | 26.14 | 0 | 0 | 0 | 00h30 | 0.4595 | 0.32675 | 0 | 0 | 0
01h30 | 31.93 | 19.95 | 0 | 0 | 0 | 01h30 | 0.39913 | 0.24938 | 0 | 0 | 0
02h30 | 13.09 | 2.44 | 0 | 0 | 0 | 02h30 | 0.16362 | 0.0305 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 11.2 | 0 | 0 | 0 | 0 | 07h30 | 0.14 | 0 | 0 | 0 | 0
08h30 | 11.2 | 0 | 0 | 0 | 0 | 08h30 | 0.14 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 2.84 | 0 | 0 | 0 | 0 | 20h30 | 0.0355 | 0 | 0 | 0 | 0
21h30 | 14.82 | 7.27 | 0 | 0 | 0 | 21h30 | 0.18525 | 0.090875 | 0 | 0 | 0
22h30 | 13.23 | 7.27 | 0 | 0 | 0 | 22h30 | 0.16537 | 0.090875 | 0 | 0 | 0
23h30 | 1.25 | 0 | 0 | 0 | 0 | 23h30 | 0.015625 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0.76 | 0 | 0 | 0 | 0 | 02h30 | 0.0095 | 0 | 0 | 0 | 0
03h30 | 4.06 | 0 | 0 | 0 | 0 | 03h30 | 0.05075 | 0 | 0 | 0 | 0
04h30 | 9.19 | 0 | 0 | 0 | 0 | 04h30 | 0.11488 | 0 | 0 | 0 | 0
05h30 | 12.79 | 0 | 0 | 0 | 0 | 05h30 | 0.15987 | 0 | 0 | 0 | 0
06h30 | 9.51 | 0 | 0 | 0 | 0 | 06h30 | 0.11887 | 0 | 0 | 0 | 0
07h30 | 28.64 | 11.49 | 0 | 0 | 0 | 07h30 | 0.358 | 0.14363 | 0 | 0 | 0
08h30 | 26.03 | 11.49 | 0 | 0 | 0 | 08h30 | 0.32538 | 0.14363 | 0 | 0 | 0
09h30 | 19.65 | 1.13 | 0 | 0 | 0 | 09h30 | 0.24563 | 0.014125 | 0 | 0 | 0
10h30 | 19.65 | 1.13 | 0 | 0 | 0 | 10h30 | 0.24563 | 0.014125 | 0 | 0 | 0
11h30 | 25.2 | 6.45 | 0 | 0 | 0 | 11h30 | 0.315 | 0.080625 | 0 | 0 | 0
12h30 | 32.53 | 14.78 | 0 | 0 | 0 | 12h30 | 0.40663 | 0.18475 | 0 | 0 | 0
13h30 | 31.01 | 14.28 | 0 | 0 | 0 | 13h30 | 0.38762 | 0.1785 | 0 | 0 | 0
14h30 | 23.68 | 5.94 | 0 | 0 | 0 | 14h30 | 0.296 | 0.07425 | 0 | 0 | 0
15h30 | 12.69 | 0 | 0 | 0 | 0 | 15h30 | 0.15862 | 0 | 0 | 0 | 0
16h30 | 13.81 | 0.74 | 0 | 0 | 0 | 16h30 | 0.17263 | 0.00925 | 0 | 0 | 0
17h30 | 15.66 | 3.45 | 0 | 0 | 0 | 17h30 | 0.19575 | 0.043125 | 0 | 0 | 0
18h30 | 14.54 | 2.71 | 0 | 0 | 0 | 18h30 | 0.18175 | 0.033875 | 0 | 0 | 0
19h30 | 11.48 | 0.96 | 0 | 0 | 0 | 19h30 | 0.1435 | 0.012 | 0 | 0 | 0
20h30 | 13.68 | 3.95 | 0 | 0 | 0 | 20h30 | 0.171 | 0.049375 | 0 | 0 | 0
21h30 | 21.01 | 11.63 | 0 | 0 | 0 | 21h30 | 0.26262 | 0.14538 | 0 | 0 | 0
22h30 | 22.56 | 13.14 | 0 | 0 | 0 | 22h30 | 0.282 | 0.16425 | 0 | 0 | 0
23h30 | 20.4 | 10.9 | 0 | 0 | 0 | 23h30 | 0.255 | 0.13625 | 0 | 0 | 0
00h30 | 16.66 | 6.41 | 0 | 0 | 0 | 00h30 | 0.20825 | 0.080125 | 0 | 0 | 0
01h30 | 2.59 | 0 | 0 | 0 | 0 | 01h30 | 0.032375 | 0 | 0 | 0 | 0
02h30 | 6.58 | 0 | 0 | 0 | 0 | 02h30 | 0.08225 | 0 | 0 | 0 | 0
03h30 | 8.46 | 0 | 0 | 0 | 0 | 03h30 | 0.10575 | 0 | 0 | 0 | 0
04h30 | 8.3 | 0 | 0 | 0 | 0 | 04h30 | 0.10375 | 0 | 0 | 0 | 0
05h30 | 3.83 | 0 | 0 | 0 | 0 | 05h30 | 0.047875 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 4.42 | 0 | 0 | 0 | 0 | 07h30 | 0.05525 | 0 | 0 | 0 | 0
08h30 | 4.42 | 0 | 0 | 0 | 0 | 08h30 | 0.05525 | 0 | 0 | 0 | 0
09h30 | 7.65 | 0 | 0 | 0 | 0 | 09h30 | 0.095625 | 0 | 0 | 0 | 0
10h30 | 11.43 | 0 | 0 | 0 | 0 | 10h30 | 0.14288 | 0 | 0 | 0 | 0
11h30 | 9.64 | 0 | 0 | 0 | 0 | 11h30 | 0.1205 | 0 | 0 | 0 | 0
12h30 | 7.74 | 0 | 0 | 0 | 0 | 12h30 | 0.09675 | 0 | 0 | 0 | 0
13h30 | 1.87 | 0 | 0 | 0 | 0 | 13h30 | 0.023375 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 19.32 | 15.73 | 0 | 0 | 0 | 22h30 | 0.2415 | 0.19662 | 0 | 0 | 0
23h30 | 43.06 | 38.5 | 0 | 0 | 0 | 23h30 | 0.53825 | 0.48125 | 0 | 0 | 0
00h30 | 23.73 | 22.77 | 0 | 0 | 0 | 00h30 | 0.29663 | 0.28463 | 0 | 0 | 0
01h30 | 24.83 | 19.57 | 0 | 0 | 0 | 01h30 | 0.31038 | 0.24463 | 0 | 0 | 0
02h30 | 34.25 | 27.17 | 0 | 0 | 0 | 02h30 | 0.42812 | 0.33963 | 0 | 0 | 0
03h30 | 33.86 | 25.75 | 0 | 0 | 0 | 03h30 | 0.42325 | 0.32188 | 0 | 0 | 0
04h30 | 28.13 | 19.37 | 0 | 0 | 0 | 04h30 | 0.35163 | 0.24213 | 0 | 0 | 0
05h30 | 20.98 | 11.39 | 0 | 0 | 0 | 05h30 | 0.26225 | 0.14238 | 0 | 0 | 0
06h30 | 17.3 | 10.17 | 0 | 0 | 0 | 06h30 | 0.21625 | 0.12712 | 0 | 0 | 0
07h30 | 22.15 | 12 | 0 | 0 | 0 | 07h30 | 0.27687 | 0.15 | 0 | 0 | 0
08h30 | 22.15 | 12 | 0 | 0 | 0 | 08h30 | 0.27687 | 0.15 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 13.04 | 9.01 | 0 | 0 | 0 | 20h30 | 0.163 | 0.11263 | 0 | 0 | 0
21h30 | 21.43 | 16.22 | 0 | 0 | 0 | 21h30 | 0.26787 | 0.20275 | 0 | 0 | 0
22h30 | 26.44 | 21.13 | 0 | 0 | 0 | 22h30 | 0.3305 | 0.26412 | 0 | 0 | 0
23h30 | 27.42 | 22.01 | 0 | 0 | 0 | 23h30 | 0.34275 | 0.27513 | 0 | 0 | 0
00h30 | 9.37 | 8.09 | 0 | 0 | 0 | 00h30 | 0.11713 | 0.10113 | 0 | 0 | 0
01h30 | 6.46 | 0.31 | 0 | 0 | 0 | 01h30 | 0.08075 | 0.003875 | 0 | 0 | 0
02h30 | 6.46 | 0.31 | 0 | 0 | 0 | 02h30 | 0.08075 | 0.003875 | 0 | 0 | 0
03h30 | 5.86 | 0 | 0 | 0 | 0 | 03h30 | 0.07325 | 0 | 0 | 0 | 0
04h30 | 5.86 | 0 | 0 | 0 | 0 | 04h30 | 0.07325 | 0 | 0 | 0 | 0
05h30 | 0.4 | 0 | 0 | 0 | 0 | 05h30 | 0.005 | 0 | 0 | 0 | 0
06h30 | 0.4 | 0 | 0 | 0 | 0 | 06h30 | 0.005 | 0 | 0 | 0 | 0
07h30 | 16.02 | 6.17 | 0 | 0 | 0 | 07h30 | 0.20025 | 0.077125 | 0 | 0 | 0
08h30 | 16.02 | 6.17 | 0 | 0 | 0 | 08h30 | 0.20025 | 0.077125 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 10.77 | 2.75 | 0 | 0 | 0 | 17h30 | 0.13462 | 0.034375 | 0 | 0 | 0
18h30 | 29.69 | 21.39 | 0 | 0 | 0 | 18h30 | 0.37112 | 0.26737 | 0 | 0 | 0
19h30 | 49.98 | 42.36 | 1.4 | 0 | 0 | 19h30 | 0.62475 | 0.5295 | 0.0175 | 0 | 0
20h30 | 63.85 | 57.2 | 10.45 | 0 | 0 | 20h30 | 0.79812 | 0.715 | 0.13062 | 0 | 0
21h30 | 68.94 | 62.61 | 16 | 0 | 0 | 21h30 | 0.86175 | 0.78263 | 0.2 | 0 | 0
22h30 | 72.13 | 65.73 | 20.22 | 0 | 0 | 22h30 | 0.90163 | 0.82163 | 0.25275 | 0 | 0
23h30 | 77.61 | 70.88 | 24.95 | 4.72 | 0 | 23h30 | 0.97013 | 0.886 | 0.31188 | 0.059 | 0
00h30 | 48.99 | 41.09 | 11.67 | 4.72 | 0 | 00h30 | 0.61238 | 0.51362 | 0.14588 | 0.059 | 0
01h30 | 35.96 | 26.79 | 0 | 0 | 0 | 01h30 | 0.4495 | 0.33487 | 0 | 0 | 0
02h30 | 32.18 | 22.5 | 0 | 0 | 0 | 02h30 | 0.40225 | 0.28125 | 0 | 0 | 0
03h30 | 31.72 | 21.59 | 0 | 0 | 0 | 03h30 | 0.3965 | 0.26987 | 0 | 0 | 0
04h30 | 28.15 | 19.07 | 0 | 0 | 0 | 04h30 | 0.35187 | 0.23838 | 0 | 0 | 0
05h30 | 22.66 | 11.53 | 0 | 0 | 0 | 05h30 | 0.28325 | 0.14413 | 0 | 0 | 0
06h30 | 22.66 | 11.53 | 0 | 0 | 0 | 06h30 | 0.28325 | 0.14413 | 0 | 0 | 0
07h30 | 43.3 | 31.4 | 8.48 | 0 | 0 | 07h30 | 0.54125 | 0.3925 | 0.106 | 0 | 0
08h30 | 43.3 | 31.4 | 8.48 | 0 | 0 | 08h30 | 0.54125 | 0.3925 | 0.106 | 0 | 0
09h30 | 28.7 | 16.22 | 0 | 0 | 0 | 09h30 | 0.35875 | 0.20275 | 0 | 0 | 0
10h30 | 28.7 | 16.22 | 0 | 0 | 0 | 10h30 | 0.35875 | 0.20275 | 0 | 0 | 0
11h30 | 16.23 | 3.36 | 0 | 0 | 0 | 11h30 | 0.20287 | 0.042 | 0 | 0 | 0
12h30 | 16.23 | 3.36 | 0 | 0 | 0 | 12h30 | 0.20287 | 0.042 | 0 | 0 | 0
13h30 | 12.03 | 0 | 0 | 0 | 0 | 13h30 | 0.15038 | 0 | 0 | 0 | 0
14h30 | 14.94 | 2.87 | 0 | 0 | 0 | 14h30 | 0.18675 | 0.035875 | 0 | 0 | 0
15h30 | 13.32 | 2.87 | 0 | 0 | 0 | 15h30 | 0.1665 | 0.035875 | 0 | 0 | 0
16h30 | 25.21 | 16.09 | 0 | 0 | 0 | 16h30 | 0.31512 | 0.20112 | 0 | 0 | 0
17h30 | 37.36 | 29.79 | 0 | 0 | 0 | 17h30 | 0.467 | 0.37238 | 0 | 0 | 0
18h30 | 35.25 | 28.94 | 0 | 0 | 0 | 18h30 | 0.44062 | 0.36175 | 0 | 0 | 0
19h30 | 24.27 | 18.89 | 0 | 0 | 0 | 19h30 | 0.30338 | 0.23613 | 0 | 0 | 0
20h30 | 19.11 | 14.29 | 0 | 0 | 0 | 20h30 | 0.23888 | 0.17863 | 0 | 0 | 0
21h30 | 21.38 | 16.8 | 0 | 0 | 0 | 21h30 | 0.26725 | 0.21 | 0 | 0 | 0
22h30 | 28.21 | 23.58 | 1.27 | 0 | 0 | 22h30 | 0.35263 | 0.29475 | 0.015875 | 0 | 0
23h30 | 27.16 | 22.25 | 1.27 | 0 | 0 | 23h30 | 0.3395 | 0.27813 | 0.015875 | 0 | 0
00h30 | 12.79 | 4.82 | 0 | 0 | 0 | 00h30 | 0.15987 | 0.06025 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 4.73 | 0 | 0 | 0 | 0 | 02h30 | 0.059125 | 0 | 0 | 0 | 0
03h30 | 11.13 | 3.71 | 0 | 0 | 0 | 03h30 | 0.13912 | 0.046375 | 0 | 0 | 0
04h30 | 6.41 | 3.71 | 0 | 0 | 0 | 04h30 | 0.080125 | 0.046375 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 42.28 | 34.96 | 0 | 0 | 0 | 15h30 | 0.5285 | 0.437 | 0 | 0 | 0
16h30 | 64.36 | 55.86 | 5.77 | 0 | 0 | 16h30 | 0.8045 | 0.69825 | 0.072125 | 0 | 0
17h30 | 63.8 | 56.12 | 5.77 | 0 | 0 | 17h30 | 0.7975 | 0.7015 | 0.072125 | 0 | 0
18h30 | 48.32 | 42.13 | 0 | 0 | 0 | 18h30 | 0.604 | 0.52663 | 0 | 0 | 0
19h30 | 32.05 | 26.81 | 0 | 0 | 0 | 19h30 | 0.40063 | 0.33513 | 0 | 0 | 0
20h30 | 37.31 | 32.48 | 1.74 | 0 | 0 | 20h30 | 0.46637 | 0.406 | 0.02175 | 0 | 0
21h30 | 34.34 | 29.46 | 1.74 | 0 | 0 | 21h30 | 0.42925 | 0.36825 | 0.02175 | 0 | 0
22h30 | 36.95 | 31.65 | 3.68 | 0 | 0 | 22h30 | 0.46187 | 0.39563 | 0.046 | 0 | 0
23h30 | 43.01 | 37.07 | 8.34 | 0 | 0 | 23h30 | 0.53763 | 0.46337 | 0.10425 | 0 | 0
00h30 | 28.53 | 22.29 | 4.65 | 0 | 0 | 00h30 | 0.35663 | 0.27863 | 0.058125 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 14.43 | 3 | 0 | 0 | 0 | 11h30 | 0.18038 | 0.0375 | 0 | 0 | 0
12h30 | 14.43 | 3 | 0 | 0 | 0 | 12h30 | 0.18038 | 0.0375 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 17.95 | 10.48 | 0 | 0 | 0 | 22h30 | 0.22437 | 0.131 | 0 | 0 | 0
23h30 | 17.95 | 10.48 | 0 | 0 | 0 | 23h30 | 0.22437 | 0.131 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0.43 | 0 | 0 | 0 | 0 | 04h30 | 0.005375 | 0 | 0 | 0 | 0
05h30 | 0.43 | 0 | 0 | 0 | 0 | 05h30 | 0.005375 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 4.78 | 0 | 0 | 0 | 0 | 20h30 | 0.05975 | 0 | 0 | 0 | 0
21h30 | 12.88 | 4.56 | 0 | 0 | 0 | 21h30 | 0.161 | 0.057 | 0 | 0 | 0
22h30 | 27.85 | 18.77 | 0 | 0 | 0 | 22h30 | 0.34813 | 0.23463 | 0 | 0 | 0
23h30 | 39.83 | 30.66 | 0 | 0 | 0 | 23h30 | 0.49788 | 0.38325 | 0 | 0 | 0
00h30 | 20.09 | 16.44 | 0 | 0 | 0 | 00h30 | 0.25112 | 0.2055 | 0 | 0 | 0
01h30 | 16.8 | 7.31 | 0 | 0 | 0 | 01h30 | 0.21 | 0.091375 | 0 | 0 | 0
02h30 | 17.51 | 7.31 | 0 | 0 | 0 | 02h30 | 0.21887 | 0.091375 | 0 | 0 | 0
03h30 | 22.12 | 10.38 | 0 | 0 | 0 | 03h30 | 0.2765 | 0.12975 | 0 | 0 | 0
04h30 | 26.44 | 14.25 | 0 | 0 | 0 | 04h30 | 0.3305 | 0.17813 | 0 | 0 | 0
05h30 | 24.54 | 11.75 | 0 | 0 | 0 | 05h30 | 0.30675 | 0.14688 | 0 | 0 | 0
06h30 | 19.51 | 7.88 | 0 | 0 | 0 | 06h30 | 0.24388 | 0.0985 | 0 | 0 | 0
07h30 | 35.16 | 22.58 | 0 | 0 | 0 | 07h30 | 0.4395 | 0.28225 | 0 | 0 | 0
08h30 | 35.16 | 22.58 | 0 | 0 | 0 | 08h30 | 0.4395 | 0.28225 | 0 | 0 | 0
09h30 | 25.41 | 12.63 | 0 | 0 | 0 | 09h30 | 0.31762 | 0.15787 | 0 | 0 | 0
10h30 | 25.41 | 12.63 | 0 | 0 | 0 | 10h30 | 0.31762 | 0.15787 | 0 | 0 | 0
11h30 | 7.94 | 0 | 0 | 0 | 0 | 11h30 | 0.09925 | 0 | 0 | 0 | 0
12h30 | 7.94 | 0 | 0 | 0 | 0 | 12h30 | 0.09925 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 4.22 | 0.32 | 0 | 0 | 0 | 20h30 | 0.05275 | 0.004 | 0 | 0 | 0
21h30 | 7.99 | 3.66 | 0 | 0 | 0 | 21h30 | 0.099875 | 0.04575 | 0 | 0 | 0
22h30 | 5.59 | 3.34 | 0 | 0 | 0 | 22h30 | 0.069875 | 0.04175 | 0 | 0 | 0
23h30 | 1.82 | 0 | 0 | 0 | 0 | 23h30 | 0.02275 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 11.12 | 1.87 | 0 | 0 | 0 | 23h30 | 0.139 | 0.023375 | 0 | 0 | 0
00h30 | 12.86 | 1.87 | 0 | 0 | 0 | 00h30 | 0.16075 | 0.023375 | 0 | 0 | 0
01h30 | 9.67 | 0 | 0 | 0 | 0 | 01h30 | 0.12087 | 0 | 0 | 0 | 0
02h30 | 7.92 | 0 | 0 | 0 | 0 | 02h30 | 0.099 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 1.25 | 0 | 0 | 0 | 0 | 11h30 | 0.015625 | 0 | 0 | 0 | 0
12h30 | 1.25 | 0 | 0 | 0 | 0 | 12h30 | 0.015625 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 6.2 | 1.31 | 0 | 0 | 0 | 20h30 | 0.0775 | 0.016375 | 0 | 0 | 0
21h30 | 15.49 | 9.75 | 0 | 0 | 0 | 21h30 | 0.19362 | 0.12187 | 0 | 0 | 0
22h30 | 20.91 | 15.16 | 0 | 0 | 0 | 22h30 | 0.26138 | 0.1895 | 0 | 0 | 0
23h30 | 24.08 | 18.31 | 0 | 0 | 0 | 23h30 | 0.301 | 0.22887 | 0 | 0 | 0
00h30 | 12.46 | 11.59 | 0 | 0 | 0 | 00h30 | 0.15575 | 0.14488 | 0 | 0 | 0
01h30 | 4.74 | 0 | 0 | 0 | 0 | 01h30 | 0.05925 | 0 | 0 | 0 | 0
02h30 | 4.74 | 0 | 0 | 0 | 0 | 02h30 | 0.05925 | 0 | 0 | 0 | 0
03h30 | 1.53 | 0 | 0 | 0 | 0 | 03h30 | 0.019125 | 0 | 0 | 0 | 0
04h30 | 4.67 | 0 | 0 | 0 | 0 | 04h30 | 0.058375 | 0 | 0 | 0 | 0
05h30 | 3.14 | 0 | 0 | 0 | 0 | 05h30 | 0.03925 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 8.41 | 0 | 0 | 0 | 0 | 07h30 | 0.10512 | 0 | 0 | 0 | 0
08h30 | 8.41 | 0 | 0 | 0 | 0 | 08h30 | 0.10512 | 0 | 0 | 0 | 0
09h30 | 1.27 | 0 | 0 | 0 | 0 | 09h30 | 0.015875 | 0 | 0 | 0 | 0
10h30 | 1.27 | 0 | 0 | 0 | 0 | 10h30 | 0.015875 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 1.87 | 0 | 0 | 0 | 0 | 12h30 | 0.023375 | 0 | 0 | 0 | 0
13h30 | 1.87 | 0 | 0 | 0 | 0 | 13h30 | 0.023375 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 1.02 | 0 | 0 | 0 | 0 | 19h30 | 0.01275 | 0 | 0 | 0 | 0
20h30 | 1.52 | 0 | 0 | 0 | 0 | 20h30 | 0.019 | 0 | 0 | 0 | 0
21h30 | 0.5 | 0 | 0 | 0 | 0 | 21h30 | 0.00625 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 1.94 | 0 | 0 | 0 | 0 | 23h30 | 0.02425 | 0 | 0 | 0 | 0
00h30 | 1.94 | 0 | 0 | 0 | 0 | 00h30 | 0.02425 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 11.17 | 0 | 0 | 0 | 0 | 23h30 | 0.13962 | 0 | 0 | 0 | 0
00h30 | 11.17 | 0 | 0 | 0 | 0 | 00h30 | 0.13962 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 2.03 | 0 | 0 | 0 | 0 | 08h30 | 0.025375 | 0 | 0 | 0 | 0
09h30 | 3.38 | 0 | 0 | 0 | 0 | 09h30 | 0.04225 | 0 | 0 | 0 | 0
10h30 | 1.34 | 0 | 0 | 0 | 0 | 10h30 | 0.01675 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 3.49 | 0 | 0 | 0 | 0 | 07h30 | 0.043625 | 0 | 0 | 0 | 0
08h30 | 3.49 | 0 | 0 | 0 | 0 | 08h30 | 0.043625 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0.17 | 0 | 0 | 0 | 0 | 07h30 | 0.002125 | 0 | 0 | 0 | 0
08h30 | 0.59 | 0 | 0 | 0 | 0 | 08h30 | 0.007375 | 0 | 0 | 0 | 0
09h30 | 0.45 | 0 | 0 | 0 | 0 | 09h30 | 0.005625 | 0 | 0 | 0 | 0
10h30 | 0.03 | 0 | 0 | 0 | 0 | 10h30 | 0.000375 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 5.42 | 0 | 0 | 0 | 0 | 22h30 | 0.06775 | 0 | 0 | 0 | 0
23h30 | 8.47 | 0 | 0 | 0 | 0 | 23h30 | 0.10587 | 0 | 0 | 0 | 0
00h30 | 3.05 | 0 | 0 | 0 | 0 | 00h30 | 0.038125 | 0 | 0 | 0 | 0
01h30 | 2.62 | 0 | 0 | 0 | 0 | 01h30 | 0.03275 | 0 | 0 | 0 | 0
02h30 | 4.95 | 0 | 0 | 0 | 0 | 02h30 | 0.061875 | 0 | 0 | 0 | 0
03h30 | 9.28 | 0 | 0 | 0 | 0 | 03h30 | 0.116 | 0 | 0 | 0 | 0
04h30 | 16.14 | 0 | 0 | 0 | 0 | 04h30 | 0.20175 | 0 | 0 | 0 | 0
05h30 | 15.32 | 0 | 0 | 0 | 0 | 05h30 | 0.1915 | 0 | 0 | 0 | 0
06h30 | 7.63 | 0 | 0 | 0 | 0 | 06h30 | 0.095375 | 0 | 0 | 0 | 0
07h30 | 16.04 | 0 | 0 | 0 | 0 | 07h30 | 0.2005 | 0 | 0 | 0 | 0
08h30 | 14.53 | 0 | 0 | 0 | 0 | 08h30 | 0.18163 | 0 | 0 | 0 | 0
09h30 | 13.84 | 0 | 0 | 0 | 0 | 09h30 | 0.173 | 0 | 0 | 0 | 0
10h30 | 13.84 | 0 | 0 | 0 | 0 | 10h30 | 0.173 | 0 | 0 | 0 | 0
11h30 | 10.71 | 0 | 0 | 0 | 0 | 11h30 | 0.13387 | 0 | 0 | 0 | 0
12h30 | 14.29 | 0 | 0 | 0 | 0 | 12h30 | 0.17863 | 0 | 0 | 0 | 0
13h30 | 10.86 | 0 | 0 | 0 | 0 | 13h30 | 0.13575 | 0 | 0 | 0 | 0
14h30 | 7.28 | 0 | 0 | 0 | 0 | 14h30 | 0.091 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 7.88 | 0 | 0 | 0 | 0 | 16h30 | 0.0985 | 0 | 0 | 0 | 0
17h30 | 11.52 | 0 | 0 | 0 | 0 | 17h30 | 0.144 | 0 | 0 | 0 | 0
18h30 | 3.64 | 0 | 0 | 0 | 0 | 18h30 | 0.0455 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 16.38 | 6.09 | 0 | 0 | 0 | 22h30 | 0.20475 | 0.076125 | 0 | 0 | 0
23h30 | 21.04 | 7.51 | 0 | 0 | 0 | 23h30 | 0.263 | 0.093875 | 0 | 0 | 0
00h30 | 4.65 | 1.42 | 0 | 0 | 0 | 00h30 | 0.058125 | 0.01775 | 0 | 0 | 0
01h30 | 0.27 | 0 | 0 | 0 | 0 | 01h30 | 0.003375 | 0 | 0 | 0 | 0
02h30 | 0.71 | 0 | 0 | 0 | 0 | 02h30 | 0.008875 | 0 | 0 | 0 | 0
03h30 | 6.3 | 0 | 0 | 0 | 0 | 03h30 | 0.07875 | 0 | 0 | 0 | 0
04h30 | 10.73 | 0 | 0 | 0 | 0 | 04h30 | 0.13412 | 0 | 0 | 0 | 0
05h30 | 8.75 | 0 | 0 | 0 | 0 | 05h30 | 0.10938 | 0 | 0 | 0 | 0
06h30 | 3.88 | 0 | 0 | 0 | 0 | 06h30 | 0.0485 | 0 | 0 | 0 | 0
07h30 | 18.4 | 0 | 0 | 0 | 0 | 07h30 | 0.23 | 0 | 0 | 0 | 0
08h30 | 18.4 | 0 | 0 | 0 | 0 | 08h30 | 0.23 | 0 | 0 | 0 | 0
09h30 | 2.25 | 0 | 0 | 0 | 0 | 09h30 | 0.028125 | 0 | 0 | 0 | 0
10h30 | 2.25 | 0 | 0 | 0 | 0 | 10h30 | 0.028125 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 1.87 | 0 | 0 | 0 | 0 | 19h30 | 0.023375 | 0 | 0 | 0 | 0
20h30 | 14.9 | 7.84 | 0 | 0 | 0 | 20h30 | 0.18625 | 0.098 | 0 | 0 | 0
21h30 | 20.12 | 12.75 | 0 | 0 | 0 | 21h30 | 0.2515 | 0.15937 | 0 | 0 | 0
22h30 | 19.01 | 11.77 | 0 | 0 | 0 | 22h30 | 0.23763 | 0.14713 | 0 | 0 | 0
23h30 | 11.92 | 6.86 | 0 | 0 | 0 | 23h30 | 0.149 | 0.08575 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 2.38 | 0 | 0 | 0 | 0 | 03h30 | 0.02975 | 0 | 0 | 0 | 0
04h30 | 4.52 | 0 | 0 | 0 | 0 | 04h30 | 0.0565 | 0 | 0 | 0 | 0
05h30 | 4.49 | 0 | 0 | 0 | 0 | 05h30 | 0.056125 | 0 | 0 | 0 | 0
06h30 | 2.36 | 0 | 0 | 0 | 0 | 06h30 | 0.0295 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0.98 | 0 | 0 | 0 | 0 | 23h30 | 0.01225 | 0 | 0 | 0 | 0
00h30 | 0.98 | 0 | 0 | 0 | 0 | 00h30 | 0.01225 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 9.13 | 0 | 0 | 0 | 0 | 17h30 | 0.11413 | 0 | 0 | 0 | 0
18h30 | 28.99 | 13.82 | 0 | 0 | 0 | 18h30 | 0.36238 | 0.17275 | 0 | 0 | 0
19h30 | 19.92 | 13.82 | 0 | 0 | 0 | 19h30 | 0.249 | 0.17275 | 0 | 0 | 0
20h30 | 18.28 | 5.53 | 0 | 0 | 0 | 20h30 | 0.2285 | 0.069125 | 0 | 0 | 0
21h30 | 25.8 | 12.43 | 0 | 0 | 0 | 21h30 | 0.3225 | 0.15538 | 0 | 0 | 0
22h30 | 31.83 | 18.03 | 0 | 0 | 0 | 22h30 | 0.39787 | 0.22537 | 0 | 0 | 0
23h30 | 36.36 | 22.87 | 0 | 0 | 0 | 23h30 | 0.4545 | 0.28587 | 0 | 0 | 0
00h30 | 18.33 | 11.74 | 0 | 0 | 0 | 00h30 | 0.22912 | 0.14675 | 0 | 0 | 0
01h30 | 19.54 | 4.84 | 0 | 0 | 0 | 01h30 | 0.24425 | 0.0605 | 0 | 0 | 0
02h30 | 20.8 | 5.22 | 0 | 0 | 0 | 02h30 | 0.26 | 0.06525 | 0 | 0 | 0
03h30 | 34.87 | 18.61 | 0 | 0 | 0 | 03h30 | 0.43588 | 0.23262 | 0 | 0 | 0
04h30 | 46.74 | 30.54 | 0 | 0 | 0 | 04h30 | 0.58425 | 0.38175 | 0 | 0 | 0
05h30 | 45.6 | 29.21 | 0 | 0 | 0 | 05h30 | 0.57 | 0.36512 | 0 | 0 | 0
06h30 | 41.12 | 23.85 | 0 | 0 | 0 | 06h30 | 0.514 | 0.29812 | 0 | 0 | 0
07h30 | 49.64 | 32.16 | 0 | 0 | 0 | 07h30 | 0.6205 | 0.402 | 0 | 0 | 0
08h30 | 37.29 | 25.2 | 0 | 0 | 0 | 08h30 | 0.46613 | 0.315 | 0 | 0 | 0
09h30 | 30.43 | 13.39 | 0 | 0 | 0 | 09h30 | 0.38038 | 0.16737 | 0 | 0 | 0
10h30 | 27.92 | 13.39 | 0 | 0 | 0 | 10h30 | 0.349 | 0.16737 | 0 | 0 | 0
11h30 | 17.63 | 0.23 | 0 | 0 | 0 | 11h30 | 0.22037 | 0.002875 | 0 | 0 | 0
12h30 | 21.71 | 4.76 | 0 | 0 | 0 | 12h30 | 0.27137 | 0.0595 | 0 | 0 | 0
13h30 | 29.73 | 13.84 | 0 | 0 | 0 | 13h30 | 0.37162 | 0.173 | 0 | 0 | 0
14h30 | 28.05 | 13.52 | 0 | 0 | 0 | 14h30 | 0.35063 | 0.169 | 0 | 0 | 0
15h30 | 32.91 | 19.82 | 0 | 0 | 0 | 15h30 | 0.41137 | 0.24775 | 0 | 0 | 0
16h30 | 36.46 | 24.83 | 0 | 0 | 0 | 16h30 | 0.45575 | 0.31038 | 0 | 0 | 0
17h30 | 39.65 | 29.29 | 0 | 0 | 0 | 17h30 | 0.49562 | 0.36612 | 0 | 0 | 0
18h30 | 48.33 | 39.05 | 2.03 | 0 | 0 | 18h30 | 0.60413 | 0.48812 | 0.025375 | 0 | 0
19h30 | 54.84 | 46.38 | 8.03 | 0 | 0 | 19h30 | 0.6855 | 0.57975 | 0.10038 | 0 | 0
20h30 | 52.35 | 44.36 | 8.71 | 0 | 0 | 20h30 | 0.65438 | 0.5545 | 0.10887 | 0 | 0
21h30 | 45.92 | 38.07 | 6.38 | 0 | 0 | 21h30 | 0.574 | 0.47587 | 0.07975 | 0 | 0
22h30 | 47.2 | 39.28 | 8.2 | 0 | 0 | 22h30 | 0.59 | 0.491 | 0.1025 | 0 | 0
23h30 | 46.06 | 37.94 | 8.53 | 0 | 0 | 23h30 | 0.57575 | 0.47425 | 0.10662 | 0 | 0
00h30 | 32.63 | 19.79 | 4.01 | 0 | 0 | 00h30 | 0.40787 | 0.24738 | 0.050125 | 0 | 0
01h30 | 23.15 | 12.37 | 0 | 0 | 0 | 01h30 | 0.28937 | 0.15463 | 0 | 0 | 0
02h30 | 25.33 | 13.89 | 0 | 0 | 0 | 02h30 | 0.31662 | 0.17363 | 0 | 0 | 0
03h30 | 28.95 | 17.41 | 0 | 0 | 0 | 03h30 | 0.36188 | 0.21763 | 0 | 0 | 0
04h30 | 31.2 | 19.59 | 0 | 0 | 0 | 04h30 | 0.39 | 0.24488 | 0 | 0 | 0
05h30 | 31.33 | 19.65 | 0 | 0 | 0 | 05h30 | 0.39163 | 0.24563 | 0 | 0 | 0
06h30 | 27.25 | 15.95 | 0 | 0 | 0 | 06h30 | 0.34063 | 0.19937 | 0 | 0 | 0
07h30 | 42.41 | 30.14 | 8.17 | 0 | 0 | 07h30 | 0.53012 | 0.37675 | 0.10212 | 0 | 0
08h30 | 42.06 | 30.14 | 8.17 | 0 | 0 | 08h30 | 0.52575 | 0.37675 | 0.10212 | 0 | 0
09h30 | 26.02 | 14.5 | 0 | 0 | 0 | 09h30 | 0.32525 | 0.18125 | 0 | 0 | 0
10h30 | 26.02 | 14.5 | 0 | 0 | 0 | 10h30 | 0.32525 | 0.18125 | 0 | 0 | 0
11h30 | 20.9 | 7.41 | 0 | 0 | 0 | 11h30 | 0.26125 | 0.092625 | 0 | 0 | 0
12h30 | 20.9 | 7.41 | 0 | 0 | 0 | 12h30 | 0.26125 | 0.092625 | 0 | 0 | 0
13h30 | 13.93 | 1.55 | 0 | 0 | 0 | 13h30 | 0.17413 | 0.019375 | 0 | 0 | 0
14h30 | 13.93 | 2.23 | 0 | 0 | 0 | 14h30 | 0.17413 | 0.027875 | 0 | 0 | 0
15h30 | 20.99 | 10.7 | 0 | 0 | 0 | 15h30 | 0.26238 | 0.13375 | 0 | 0 | 0
16h30 | 22.09 | 13.08 | 0 | 0 | 0 | 16h30 | 0.27613 | 0.1635 | 0 | 0 | 0
17h30 | 16.93 | 9.2 | 0 | 0 | 0 | 17h30 | 0.21163 | 0.115 | 0 | 0 | 0
18h30 | 15.83 | 6.14 | 0 | 0 | 0 | 18h30 | 0.19787 | 0.07675 | 0 | 0 | 0
19h30 | 4.77 | 0 | 0 | 0 | 0 | 19h30 | 0.059625 | 0 | 0 | 0 | 0
20h30 | 4.77 | 0 | 0 | 0 | 0 | 20h30 | 0.059625 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 6.4 | 2.59 | 0 | 0 | 0 | 22h30 | 0.08 | 0.032375 | 0 | 0 | 0
23h30 | 13.2 | 8.54 | 0 | 0 | 0 | 23h30 | 0.165 | 0.10675 | 0 | 0 | 0
00h30 | 6.8 | 5.95 | 0 | 0 | 0 | 00h30 | 0.085 | 0.074375 | 0 | 0 | 0
01h30 | 11.03 | 3.12 | 0 | 0 | 0 | 01h30 | 0.13787 | 0.039 | 0 | 0 | 0
02h30 | 12.7 | 3.67 | 0 | 0 | 0 | 02h30 | 0.15875 | 0.045875 | 0 | 0 | 0
03h30 | 15.47 | 5.01 | 0 | 0 | 0 | 03h30 | 0.19337 | 0.062625 | 0 | 0 | 0
04h30 | 27.97 | 17.37 | 0 | 0 | 0 | 04h30 | 0.34963 | 0.21713 | 0 | 0 | 0
05h30 | 33.65 | 22.78 | 0.8 | 0 | 0 | 05h30 | 0.42063 | 0.28475 | 0.01 | 0 | 0
06h30 | 39.18 | 27.84 | 3.29 | 0 | 0 | 06h30 | 0.48975 | 0.348 | 0.041125 | 0 | 0
07h30 | 67.5 | 56.98 | 26.88 | 7.06 | 0 | 07h30 | 0.84375 | 0.71225 | 0.336 | 0.08825 | 0
08h30 | 65.91 | 56.91 | 24.39 | 7.06 | 0 | 08h30 | 0.82388 | 0.71137 | 0.30488 | 0.08825 | 0
09h30 | 51.67 | 42.41 | 14.82 | 0 | 0 | 09h30 | 0.64587 | 0.53012 | 0.18525 | 0 | 0
10h30 | 33.58 | 24.49 | 14.82 | 0 | 0 | 10h30 | 0.41975 | 0.30612 | 0.18525 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 8.39 | 0 | 0 | 0 | 0 | 13h30 | 0.10487 | 0 | 0 | 0 | 0
14h30 | 8.39 | 0 | 0 | 0 | 0 | 14h30 | 0.10487 | 0 | 0 | 0 | 0
15h30 | 7.92 | 0 | 0 | 0 | 0 | 15h30 | 0.099 | 0 | 0 | 0 | 0
16h30 | 10.41 | 0 | 0 | 0 | 0 | 16h30 | 0.13012 | 0 | 0 | 0 | 0
17h30 | 8.5 | 0 | 0 | 0 | 0 | 17h30 | 0.10625 | 0 | 0 | 0 | 0
18h30 | 28.3 | 18.68 | 0 | 0 | 0 | 18h30 | 0.35375 | 0.2335 | 0 | 0 | 0
19h30 | 41.22 | 32.45 | 5.25 | 0 | 0 | 19h30 | 0.51525 | 0.40563 | 0.065625 | 0 | 0
20h30 | 39.02 | 31.01 | 5.25 | 0 | 0 | 20h30 | 0.48775 | 0.38762 | 0.065625 | 0 | 0
21h30 | 43.08 | 35.65 | 8.65 | 0 | 0 | 21h30 | 0.5385 | 0.44562 | 0.10812 | 0 | 0
22h30 | 50.82 | 43.67 | 14.63 | 0 | 0 | 22h30 | 0.63525 | 0.54587 | 0.18288 | 0 | 0
23h30 | 56.64 | 49.62 | 19.15 | 1.43 | 0 | 23h30 | 0.708 | 0.62025 | 0.23938 | 0.017875 | 0
00h30 | 43.8 | 35.39 | 13.17 | 1.43 | 0 | 00h30 | 0.5475 | 0.44238 | 0.16462 | 0.017875 | 0
01h30 | 49.68 | 40.08 | 11.91 | 0 | 0 | 01h30 | 0.621 | 0.501 | 0.14888 | 0 | 0
02h30 | 41.88 | 32.57 | 11.91 | 0 | 0 | 02h30 | 0.5235 | 0.40713 | 0.14888 | 0 | 0
03h30 | 34.49 | 25.15 | 4.23 | 0 | 0 | 03h30 | 0.43112 | 0.31438 | 0.052875 | 0 | 0
04h30 | 33.33 | 23.84 | 4.39 | 0 | 0 | 04h30 | 0.41663 | 0.298 | 0.054875 | 0 | 0
05h30 | 30.94 | 21.22 | 3.1 | 0 | 0 | 05h30 | 0.38675 | 0.26525 | 0.03875 | 0 | 0
06h30 | 28.56 | 19.03 | 2.95 | 0 | 0 | 06h30 | 0.357 | 0.23788 | 0.036875 | 0 | 0
07h30 | 40.7 | 30.31 | 11.71 | 0 | 0 | 07h30 | 0.50875 | 0.37888 | 0.14638 | 0 | 0
08h30 | 37.06 | 30.31 | 11.71 | 0 | 0 | 08h30 | 0.46325 | 0.37888 | 0.14638 | 0 | 0
09h30 | 19.11 | 11.14 | 0 | 0 | 0 | 09h30 | 0.23888 | 0.13925 | 0 | 0 | 0
10h30 | 19.11 | 11.14 | 0 | 0 | 0 | 10h30 | 0.23888 | 0.13925 | 0 | 0 | 0
11h30 | 14.77 | 2.98 | 0 | 0 | 0 | 11h30 | 0.18463 | 0.03725 | 0 | 0 | 0
12h30 | 14.77 | 2.98 | 0 | 0 | 0 | 12h30 | 0.18463 | 0.03725 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 3.47 | 0 | 0 | 0 | 0 | 20h30 | 0.043375 | 0 | 0 | 0 | 0
21h30 | 3.47 | 0 | 0 | 0 | 0 | 21h30 | 0.043375 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 15.41 | 3.32 | 0 | 0 | 0 | 03h30 | 0.19262 | 0.0415 | 0 | 0 | 0
04h30 | 20.86 | 8.31 | 0 | 0 | 0 | 04h30 | 0.26075 | 0.10387 | 0 | 0 | 0
05h30 | 5.45 | 4.99 | 0 | 0 | 0 | 05h30 | 0.068125 | 0.062375 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 8.35 | 0 | 0 | 0 | 0 | 07h30 | 0.10437 | 0 | 0 | 0 | 0
08h30 | 8.35 | 0 | 0 | 0 | 0 | 08h30 | 0.10437 | 0 | 0 | 0 | 0
09h30 | 20.53 | 5.93 | 0 | 0 | 0 | 09h30 | 0.25662 | 0.074125 | 0 | 0 | 0
10h30 | 20.53 | 5.93 | 0 | 0 | 0 | 10h30 | 0.25662 | 0.074125 | 0 | 0 | 0
11h30 | 10.59 | 0 | 0 | 0 | 0 | 11h30 | 0.13237 | 0 | 0 | 0 | 0
12h30 | 10.59 | 0 | 0 | 0 | 0 | 12h30 | 0.13237 | 0 | 0 | 0 | 0
13h30 | 3.62 | 0 | 0 | 0 | 0 | 13h30 | 0.04525 | 0 | 0 | 0 | 0
14h30 | 3.62 | 0 | 0 | 0 | 0 | 14h30 | 0.04525 | 0 | 0 | 0 | 0
15h30 | 1.19 | 0 | 0 | 0 | 0 | 15h30 | 0.014875 | 0 | 0 | 0 | 0
16h30 | 8.21 | 0 | 0 | 0 | 0 | 16h30 | 0.10262 | 0 | 0 | 0 | 0
17h30 | 7.76 | 0 | 0 | 0 | 0 | 17h30 | 0.097 | 0 | 0 | 0 | 0
18h30 | 15.65 | 7.13 | 0 | 0 | 0 | 18h30 | 0.19562 | 0.089125 | 0 | 0 | 0
19h30 | 24.8 | 17.44 | 0 | 0 | 0 | 19h30 | 0.31 | 0.218 | 0 | 0 | 0
20h30 | 24.43 | 17.89 | 0 | 0 | 0 | 20h30 | 0.30538 | 0.22362 | 0 | 0 | 0
21h30 | 26.5 | 20.45 | 0 | 0 | 0 | 21h30 | 0.33125 | 0.25562 | 0 | 0 | 0
22h30 | 33.21 | 27.27 | 1.53 | 0 | 0 | 22h30 | 0.41513 | 0.34087 | 0.019125 | 0 | 0
23h30 | 40.69 | 34.65 | 7.06 | 0 | 0 | 23h30 | 0.50862 | 0.43312 | 0.08825 | 0 | 0
00h30 | 22.06 | 20.24 | 5.53 | 0 | 0 | 00h30 | 0.27575 | 0.253 | 0.069125 | 0 | 0
01h30 | 21.39 | 13.58 | 0 | 0 | 0 | 01h30 | 0.26737 | 0.16975 | 0 | 0 | 0
02h30 | 22.93 | 14.42 | 0 | 0 | 0 | 02h30 | 0.28663 | 0.18025 | 0 | 0 | 0
03h30 | 26.32 | 17 | 0 | 0 | 0 | 03h30 | 0.329 | 0.2125 | 0 | 0 | 0
04h30 | 25.35 | 16.16 | 0 | 0 | 0 | 04h30 | 0.31688 | 0.202 | 0 | 0 | 0
05h30 | 23.56 | 13.54 | 0 | 0 | 0 | 05h30 | 0.2945 | 0.16925 | 0 | 0 | 0
06h30 | 28.35 | 17.47 | 0 | 0 | 0 | 06h30 | 0.35437 | 0.21838 | 0 | 0 | 0
07h30 | 47.52 | 36.14 | 11.4 | 0 | 0 | 07h30 | 0.594 | 0.45175 | 0.1425 | 0 | 0
08h30 | 39.54 | 32.21 | 11.4 | 0 | 0 | 08h30 | 0.49425 | 0.40263 | 0.1425 | 0 | 0
09h30 | 12.02 | 0.34 | 0 | 0 | 0 | 09h30 | 0.15025 | 0.00425 | 0 | 0 | 0
10h30 | 12.02 | 0.34 | 0 | 0 | 0 | 10h30 | 0.15025 | 0.00425 | 0 | 0 | 0
11h30 | 10.73 | 0 | 0 | 0 | 0 | 11h30 | 0.13412 | 0 | 0 | 0 | 0
12h30 | 10.73 | 0 | 0 | 0 | 0 | 12h30 | 0.13412 | 0 | 0 | 0 | 0
13h30 | 0.07 | 0 | 0 | 0 | 0 | 13h30 | 0.000875 | 0 | 0 | 0 | 0
14h30 | 0.07 | 0 | 0 | 0 | 0 | 14h30 | 0.000875 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 2.21 | 0 | 0 | 0 | 0 | 17h30 | 0.027625 | 0 | 0 | 0 | 0
18h30 | 7.01 | 2.22 | 0 | 0 | 0 | 18h30 | 0.087625 | 0.02775 | 0 | 0 | 0
19h30 | 7.15 | 2.25 | 0 | 0 | 0 | 19h30 | 0.089375 | 0.028125 | 0 | 0 | 0
20h30 | 3.79 | 0.03 | 0 | 0 | 0 | 20h30 | 0.047375 | 0.000375 | 0 | 0 | 0
21h30 | 1.44 | 0 | 0 | 0 | 0 | 21h30 | 0.018 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 1.4 | 0 | 0 | 0 | 0 | 23h30 | 0.0175 | 0 | 0 | 0 | 0
00h30 | 1.4 | 0 | 0 | 0 | 0 | 00h30 | 0.0175 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 18.55 | 12 | 0 | 0 | 0 | 02h30 | 0.23187 | 0.15 | 0 | 0 | 0
03h30 | 19.58 | 12 | 0 | 0 | 0 | 03h30 | 0.24475 | 0.15 | 0 | 0 | 0
04h30 | 6.93 | 0 | 0 | 0 | 0 | 04h30 | 0.086625 | 0 | 0 | 0 | 0
05h30 | 8.48 | 0 | 0 | 0 | 0 | 05h30 | 0.106 | 0 | 0 | 0 | 0
06h30 | 24.66 | 14.09 | 0 | 0 | 0 | 06h30 | 0.30825 | 0.17613 | 0 | 0 | 0
07h30 | 38.9 | 28.45 | 8.34 | 0 | 0 | 07h30 | 0.48625 | 0.35563 | 0.10425 | 0 | 0
08h30 | 30.89 | 21.8 | 8.34 | 0 | 0 | 08h30 | 0.38612 | 0.2725 | 0.10425 | 0 | 0
09h30 | 27.67 | 18.18 | 0 | 0 | 0 | 09h30 | 0.34587 | 0.22725 | 0 | 0 | 0
10h30 | 21.33 | 10.74 | 0 | 0 | 0 | 10h30 | 0.26663 | 0.13425 | 0 | 0 | 0
11h30 | 15.31 | 3.02 | 0 | 0 | 0 | 11h30 | 0.19137 | 0.03775 | 0 | 0 | 0
12h30 | 10.58 | 3.02 | 0 | 0 | 0 | 12h30 | 0.13225 | 0.03775 | 0 | 0 | 0
13h30 | 5.29 | 0 | 0 | 0 | 0 | 13h30 | 0.066125 | 0 | 0 | 0 | 0
14h30 | 2.73 | 0 | 0 | 0 | 0 | 14h30 | 0.034125 | 0 | 0 | 0 | 0
15h30 | 1.82 | 0 | 0 | 0 | 0 | 15h30 | 0.02275 | 0 | 0 | 0 | 0
16h30 | 3.06 | 0 | 0 | 0 | 0 | 16h30 | 0.03825 | 0 | 0 | 0 | 0
17h30 | 4.35 | 0 | 0 | 0 | 0 | 17h30 | 0.054375 | 0 | 0 | 0 | 0
18h30 | 7.86 | 0 | 0 | 0 | 0 | 18h30 | 0.09825 | 0 | 0 | 0 | 0
19h30 | 13.44 | 5.68 | 0 | 0 | 0 | 19h30 | 0.168 | 0.071 | 0 | 0 | 0
20h30 | 18.37 | 11.11 | 0 | 0 | 0 | 20h30 | 0.22962 | 0.13887 | 0 | 0 | 0
21h30 | 20.31 | 13.53 | 0 | 0 | 0 | 21h30 | 0.25388 | 0.16912 | 0 | 0 | 0
22h30 | 16.41 | 9.89 | 0 | 0 | 0 | 22h30 | 0.20513 | 0.12362 | 0 | 0 | 0
23h30 | 12.77 | 6.34 | 0 | 0 | 0 | 23h30 | 0.15962 | 0.07925 | 0 | 0 | 0
00h30 | 6.56 | 4.56 | 0 | 0 | 0 | 00h30 | 0.082 | 0.057 | 0 | 0 | 0
01h30 | 5.93 | 0 | 0 | 0 | 0 | 01h30 | 0.074125 | 0 | 0 | 0 | 0
02h30 | 7.85 | 0 | 0 | 0 | 0 | 02h30 | 0.098125 | 0 | 0 | 0 | 0
03h30 | 10.12 | 0.73 | 0 | 0 | 0 | 03h30 | 0.1265 | 0.009125 | 0 | 0 | 0
04h30 | 13.2 | 3.65 | 0 | 0 | 0 | 04h30 | 0.165 | 0.045625 | 0 | 0 | 0
05h30 | 16.14 | 6.49 | 0 | 0 | 0 | 05h30 | 0.20175 | 0.081125 | 0 | 0 | 0
06h30 | 15.01 | 5.1 | 0 | 0 | 0 | 06h30 | 0.18762 | 0.06375 | 0 | 0 | 0
07h30 | 30.09 | 21.03 | 4.82 | 0 | 0 | 07h30 | 0.37612 | 0.26288 | 0.06025 | 0 | 0
08h30 | 26.21 | 19.51 | 4.82 | 0 | 0 | 08h30 | 0.32762 | 0.24388 | 0.06025 | 0 | 0
09h30 | 11.36 | 4.11 | 0 | 0 | 0 | 09h30 | 0.142 | 0.051375 | 0 | 0 | 0
10h30 | 11.36 | 4.11 | 0 | 0 | 0 | 10h30 | 0.142 | 0.051375 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 4.7 | 0 | 0 | 0 | 0 | 19h30 | 0.05875 | 0 | 0 | 0 | 0
20h30 | 4.7 | 0 | 0 | 0 | 0 | 20h30 | 0.05875 | 0 | 0 | 0 | 0
21h30 | 6.36 | 1.94 | 0 | 0 | 0 | 21h30 | 0.0795 | 0.02425 | 0 | 0 | 0
22h30 | 34.76 | 29.57 | 6.59 | 0 | 0 | 22h30 | 0.4345 | 0.36962 | 0.082375 | 0 | 0
23h30 | 35 | 27.63 | 6.59 | 0 | 0 | 23h30 | 0.4375 | 0.34537 | 0.082375 | 0 | 0
00h30 | 17.14 | 7.07 | 0 | 0 | 0 | 00h30 | 0.21425 | 0.088375 | 0 | 0 | 0
01h30 | 23.51 | 12.08 | 0 | 0 | 0 | 01h30 | 0.29387 | 0.151 | 0 | 0 | 0
02h30 | 12.96 | 5.01 | 0 | 0 | 0 | 02h30 | 0.162 | 0.062625 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 3.52 | 0 | 0 | 0 | 0 | 04h30 | 0.044 | 0 | 0 | 0 | 0
05h30 | 3.52 | 0 | 0 | 0 | 0 | 05h30 | 0.044 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 2.26 | 0 | 0 | 0 | 0 | 02h30 | 0.02825 | 0 | 0 | 0 | 0
03h30 | 4.66 | 0 | 0 | 0 | 0 | 03h30 | 0.05825 | 0 | 0 | 0 | 0
04h30 | 3.04 | 0 | 0 | 0 | 0 | 04h30 | 0.038 | 0 | 0 | 0 | 0
05h30 | 0.96 | 0 | 0 | 0 | 0 | 05h30 | 0.012 | 0 | 0 | 0 | 0
06h30 | 0.34 | 0 | 0 | 0 | 0 | 06h30 | 0.00425 | 0 | 0 | 0 | 0
07h30 | 10.78 | 0 | 0 | 0 | 0 | 07h30 | 0.13475 | 0 | 0 | 0 | 0
08h30 | 10.78 | 0 | 0 | 0 | 0 | 08h30 | 0.13475 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0.41 | 0 | 0 | 0 | 0 | 23h30 | 0.005125 | 0 | 0 | 0 | 0
00h30 | 0.41 | 0 | 0 | 0 | 0 | 00h30 | 0.005125 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 0 | 0 | 0 | 0 | 0 | 07h30 | 0 | 0 | 0 | 0 | 0
08h30 | 0 | 0 | 0 | 0 | 0 | 08h30 | 0 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 5.9 | 0 | 0 | 0 | 0 | 18h30 | 0.07375 | 0 | 0 | 0 | 0
19h30 | 14.84 | 0 | 0 | 0 | 0 | 19h30 | 0.1855 | 0 | 0 | 0 | 0
20h30 | 16.61 | 0 | 0 | 0 | 0 | 20h30 | 0.20763 | 0 | 0 | 0 | 0
21h30 | 17.12 | 0 | 0 | 0 | 0 | 21h30 | 0.214 | 0 | 0 | 0 | 0
22h30 | 25.58 | 8.75 | 0 | 0 | 0 | 22h30 | 0.31975 | 0.10938 | 0 | 0 | 0
23h30 | 29.52 | 13.43 | 0 | 0 | 0 | 23h30 | 0.369 | 0.16787 | 0 | 0 | 0
00h30 | 13.38 | 4.68 | 0 | 0 | 0 | 00h30 | 0.16725 | 0.0585 | 0 | 0 | 0
01h30 | 14.5 | 0 | 0 | 0 | 0 | 01h30 | 0.18125 | 0 | 0 | 0 | 0
02h30 | 15.15 | 0 | 0 | 0 | 0 | 02h30 | 0.18937 | 0 | 0 | 0 | 0
03h30 | 17.61 | 0.48 | 0 | 0 | 0 | 03h30 | 0.22012 | 0.006 | 0 | 0 | 0
04h30 | 23.02 | 6.14 | 0 | 0 | 0 | 04h30 | 0.28775 | 0.07675 | 0 | 0 | 0
05h30 | 22.53 | 5.87 | 0 | 0 | 0 | 05h30 | 0.28163 | 0.073375 | 0 | 0 | 0
06h30 | 16.47 | 0.21 | 0 | 0 | 0 | 06h30 | 0.20588 | 0.002625 | 0 | 0 | 0
07h30 | 33.97 | 19.13 | 0 | 0 | 0 | 07h30 | 0.42462 | 0.23913 | 0 | 0 | 0
08h30 | 33.97 | 19.13 | 0 | 0 | 0 | 08h30 | 0.42462 | 0.23913 | 0 | 0 | 0
09h30 | 18.4 | 4.69 | 0 | 0 | 0 | 09h30 | 0.23 | 0.058625 | 0 | 0 | 0
10h30 | 18.4 | 4.69 | 0 | 0 | 0 | 10h30 | 0.23 | 0.058625 | 0 | 0 | 0
11h30 | 8.06 | 0 | 0 | 0 | 0 | 11h30 | 0.10075 | 0 | 0 | 0 | 0
12h30 | 8.06 | 0 | 0 | 0 | 0 | 12h30 | 0.10075 | 0 | 0 | 0 | 0
13h30 | 9.07 | 0 | 0 | 0 | 0 | 13h30 | 0.11338 | 0 | 0 | 0 | 0
14h30 | 9.07 | 0 | 0 | 0 | 0 | 14h30 | 0.11338 | 0 | 0 | 0 | 0
15h30 | 3.41 | 0 | 0 | 0 | 0 | 15h30 | 0.042625 | 0 | 0 | 0 | 0
16h30 | 3.41 | 0 | 0 | 0 | 0 | 16h30 | 0.042625 | 0 | 0 | 0 | 0
17h30 | 4.62 | 0 | 0 | 0 | 0 | 17h30 | 0.05775 | 0 | 0 | 0 | 0
18h30 | 5.93 | 0 | 0 | 0 | 0 | 18h30 | 0.074125 | 0 | 0 | 0 | 0
19h30 | 5.46 | 0 | 0 | 0 | 0 | 19h30 | 0.06825 | 0 | 0 | 0 | 0
20h30 | 9.01 | 0 | 0 | 0 | 0 | 20h30 | 0.11263 | 0 | 0 | 0 | 0
21h30 | 12.01 | 3.03 | 0 | 0 | 0 | 21h30 | 0.15013 | 0.037875 | 0 | 0 | 0
22h30 | 13.95 | 4.98 | 0 | 0 | 0 | 22h30 | 0.17438 | 0.06225 | 0 | 0 | 0
23h30 | 14.79 | 6.05 | 0 | 0 | 0 | 23h30 | 0.18488 | 0.075625 | 0 | 0 | 0
00h30 | 7.98 | 4.1 | 0 | 0 | 0 | 00h30 | 0.09975 | 0.05125 | 0 | 0 | 0
01h30 | 4.08 | 0 | 0 | 0 | 0 | 01h30 | 0.051 | 0 | 0 | 0 | 0
02h30 | 6.63 | 0 | 0 | 0 | 0 | 02h30 | 0.082875 | 0 | 0 | 0 | 0
03h30 | 11.81 | 1.02 | 0 | 0 | 0 | 03h30 | 0.14763 | 0.01275 | 0 | 0 | 0
04h30 | 16.88 | 5.6 | 0 | 0 | 0 | 04h30 | 0.211 | 0.07 | 0 | 0 | 0
05h30 | 7.63 | 4.58 | 0 | 0 | 0 | 05h30 | 0.095375 | 0.05725 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 4.07 | 0 | 0 | 0 | 0 | 07h30 | 0.050875 | 0 | 0 | 0 | 0
08h30 | 4.07 | 0 | 0 | 0 | 0 | 08h30 | 0.050875 | 0 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 13.05 | 1.35 | 0 | 0 | 0 | 14h30 | 0.16312 | 0.016875 | 0 | 0 | 0
15h30 | 13.27 | 1.35 | 0 | 0 | 0 | 15h30 | 0.16587 | 0.016875 | 0 | 0 | 0
16h30 | 0.41 | 0 | 0 | 0 | 0 | 16h30 | 0.005125 | 0 | 0 | 0 | 0
17h30 | 0.2 | 0 | 0 | 0 | 0 | 17h30 | 0.0025 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 3.66 | 0 | 0 | 0 | 0 | 21h30 | 0.04575 | 0 | 0 | 0 | 0
22h30 | 23.3 | 13.1 | 0 | 0 | 0 | 22h30 | 0.29125 | 0.16375 | 0 | 0 | 0
23h30 | 22.73 | 13.1 | 0 | 0 | 0 | 23h30 | 0.28413 | 0.16375 | 0 | 0 | 0
00h30 | 6.03 | 0 | 0 | 0 | 0 | 00h30 | 0.075375 | 0 | 0 | 0 | 0
01h30 | 9.66 | 0 | 0 | 0 | 0 | 01h30 | 0.12075 | 0 | 0 | 0 | 0
02h30 | 9.75 | 0 | 0 | 0 | 0 | 02h30 | 0.12187 | 0 | 0 | 0 | 0
03h30 | 17.06 | 3.76 | 0 | 0 | 0 | 03h30 | 0.21325 | 0.047 | 0 | 0 | 0
04h30 | 27.19 | 13.61 | 0 | 0 | 0 | 04h30 | 0.33987 | 0.17012 | 0 | 0 | 0
05h30 | 33.27 | 20.02 | 0 | 0 | 0 | 05h30 | 0.41587 | 0.25025 | 0 | 0 | 0
06h30 | 33.81 | 20.92 | 0 | 0 | 0 | 06h30 | 0.42262 | 0.2615 | 0 | 0 | 0
07h30 | 39.3 | 28.02 | 7.41 | 0 | 0 | 07h30 | 0.49125 | 0.35025 | 0.092625 | 0 | 0
08h30 | 25.58 | 17.27 | 7.41 | 0 | 0 | 08h30 | 0.31975 | 0.21588 | 0.092625 | 0 | 0
09h30 | 19.99 | 10.91 | 0 | 0 | 0 | 09h30 | 0.24988 | 0.13637 | 0 | 0 | 0
10h30 | 27.07 | 16.01 | 0 | 0 | 0 | 10h30 | 0.33837 | 0.20012 | 0 | 0 | 0
11h30 | 27.33 | 14.73 | 0 | 0 | 0 | 11h30 | 0.34163 | 0.18413 | 0 | 0 | 0
12h30 | 20.25 | 9.63 | 0 | 0 | 0 | 12h30 | 0.25312 | 0.12037 | 0 | 0 | 0
13h30 | 11.28 | 0.02 | 0 | 0 | 0 | 13h30 | 0.141 | 0.00025 | 0 | 0 | 0
14h30 | 11.28 | 0.02 | 0 | 0 | 0 | 14h30 | 0.141 | 0.00025 | 0 | 0 | 0
15h30 | 8.69 | 0 | 0 | 0 | 0 | 15h30 | 0.10862 | 0 | 0 | 0 | 0
16h30 | 9.48 | 0.42 | 0 | 0 | 0 | 16h30 | 0.1185 | 0.00525 | 0 | 0 | 0
17h30 | 12.31 | 4.09 | 0 | 0 | 0 | 17h30 | 0.15388 | 0.051125 | 0 | 0 | 0
18h30 | 19.53 | 12.22 | 0 | 0 | 0 | 18h30 | 0.24413 | 0.15275 | 0 | 0 | 0
19h30 | 22.22 | 15.7 | 0 | 0 | 0 | 19h30 | 0.27775 | 0.19625 | 0 | 0 | 0
20h30 | 24 | 17.93 | 0 | 0 | 0 | 20h30 | 0.3 | 0.22412 | 0 | 0 | 0
21h30 | 27.81 | 21.98 | 0.89 | 0 | 0 | 21h30 | 0.34763 | 0.27475 | 0.011125 | 0 | 0
22h30 | 24.86 | 19.13 | 0.89 | 0 | 0 | 22h30 | 0.31075 | 0.23913 | 0.011125 | 0 | 0
23h30 | 26.75 | 21.02 | 2.08 | 0 | 0 | 23h30 | 0.33437 | 0.26275 | 0.026 | 0 | 0
00h30 | 19.91 | 13.08 | 2.08 | 0 | 0 | 00h30 | 0.24888 | 0.1635 | 0.026 | 0 | 0
01h30 | 25.1 | 16.63 | 0 | 0 | 0 | 01h30 | 0.31375 | 0.20788 | 0 | 0 | 0
02h30 | 28.19 | 19.7 | 0 | 0 | 0 | 02h30 | 0.35237 | 0.24625 | 0 | 0 | 0
03h30 | 29.76 | 21.04 | 0.8 | 0 | 0 | 03h30 | 0.372 | 0.263 | 0.01 | 0 | 0
04h30 | 29.67 | 20.72 | 1.34 | 0 | 0 | 04h30 | 0.37088 | 0.259 | 0.01675 | 0 | 0
05h30 | 33.46 | 24.29 | 4.28 | 0 | 0 | 05h30 | 0.41825 | 0.30362 | 0.0535 | 0 | 0
06h30 | 35.91 | 26.49 | 6.15 | 0 | 0 | 06h30 | 0.44888 | 0.33113 | 0.076875 | 0 | 0
07h30 | 55.61 | 47.56 | 25.04 | 4.72 | 0 | 07h30 | 0.69512 | 0.5945 | 0.313 | 0.059 | 0
08h30 | 57.38 | 50.36 | 24.04 | 4.72 | 0 | 08h30 | 0.71725 | 0.6295 | 0.3005 | 0.059 | 0
09h30 | 57.37 | 49.74 | 23.06 | 3.73 | 0 | 09h30 | 0.71713 | 0.62175 | 0.28825 | 0.046625 | 0
10h30 | 56.36 | 48.4 | 21.63 | 3.73 | 0 | 10h30 | 0.7045 | 0.605 | 0.27037 | 0.046625 | 0
11h30 | 55.57 | 47.27 | 20.29 | 1.93 | 0 | 11h30 | 0.69463 | 0.59088 | 0.25362 | 0.024125 | 0
12h30 | 49.38 | 40.87 | 20.29 | 1.93 | 0 | 12h30 | 0.61725 | 0.51087 | 0.25362 | 0.024125 | 0
13h30 | 38.43 | 29.71 | 9.15 | 0 | 0 | 13h30 | 0.48037 | 0.37138 | 0.11438 | 0 | 0
14h30 | 38.43 | 29.71 | 9.15 | 0 | 0 | 14h30 | 0.48037 | 0.37138 | 0.11438 | 0 | 0
15h30 | 25.93 | 19.21 | 1.03 | 0 | 0 | 15h30 | 0.32412 | 0.24013 | 0.012875 | 0 | 0
16h30 | 38.36 | 29.68 | 7.47 | 0 | 0 | 16h30 | 0.4795 | 0.371 | 0.093375 | 0 | 0
17h30 | 45.47 | 35.51 | 11.07 | 0 | 0 | 17h30 | 0.56837 | 0.44388 | 0.13837 | 0 | 0
18h30 | 47 | 38.26 | 14.31 | 0 | 0 | 18h30 | 0.5875 | 0.47825 | 0.17888 | 0 | 0
19h30 | 52.21 | 44.88 | 19.98 | 3.56 | 0 | 19h30 | 0.65263 | 0.561 | 0.24975 | 0.0445 | 0
20h30 | 59.33 | 52.71 | 25.75 | 9.31 | 0 | 20h30 | 0.74162 | 0.65887 | 0.32188 | 0.11638 | 0
21h30 | 68.79 | 62.27 | 32.2 | 15.76 | 0 | 21h30 | 0.85987 | 0.77838 | 0.4025 | 0.197 | 0
22h30 | 77.41 | 70.83 | 37.86 | 21.59 | 0 | 22h30 | 0.96762 | 0.88538 | 0.47325 | 0.26987 | 0
23h30 | 83.15 | 76.36 | 41.72 | 25.38 | 1.55 | 23h30 | 1.0394 | 0.9545 | 0.5215 | 0.31725 | 0.019375
00h30 | 62.42 | 55.81 | 24.16 | 13.8 | 1.55 | 00h30 | 0.78025 | 0.69763 | 0.302 | 0.1725 | 0.019375
01h30 | 61.55 | 52.84 | 24.99 | 7.79 | 0 | 01h30 | 0.76938 | 0.6605 | 0.31238 | 0.097375 | 0
02h30 | 61.33 | 50.6 | 23.62 | 7.79 | 0 | 02h30 | 0.76663 | 0.6325 | 0.29525 | 0.097375 | 0
03h30 | 59.65 | 49.57 | 23.94 | 7.37 | 0 | 03h30 | 0.74562 | 0.61962 | 0.29925 | 0.092125 | 0
04h30 | 56.98 | 47.48 | 23.32 | 7.39 | 0 | 04h30 | 0.71225 | 0.5935 | 0.2915 | 0.092375 | 0
05h30 | 55.15 | 45.91 | 22.81 | 7.37 | 0 | 05h30 | 0.68937 | 0.57388 | 0.28513 | 0.092125 | 0
06h30 | 57.25 | 47.49 | 23.05 | 8.58 | 0 | 06h30 | 0.71562 | 0.59362 | 0.28813 | 0.10725 | 0
07h30 | 73.02 | 64.07 | 36.51 | 24.24 | 4.39 | 07h30 | 0.91275 | 0.80088 | 0.45637 | 0.303 | 0.054875
08h30 | 64.83 | 57.75 | 34.72 | 23.01 | 4.39 | 08h30 | 0.81037 | 0.72188 | 0.434 | 0.28763 | 0.054875
09h30 | 49.76 | 39.81 | 15.29 | 4.94 | 0 | 09h30 | 0.622 | 0.49762 | 0.19112 | 0.06175 | 0
10h30 | 49.76 | 39.81 | 15.29 | 4.94 | 0 | 10h30 | 0.622 | 0.49762 | 0.19112 | 0.06175 | 0
11h30 | 45 | 34.23 | 9.61 | 0.27 | 0 | 11h30 | 0.5625 | 0.42788 | 0.12012 | 0.003375 | 0
12h30 | 45 | 34.23 | 9.61 | 0.27 | 0 | 12h30 | 0.5625 | 0.42788 | 0.12012 | 0.003375 | 0
13h30 | 37.52 | 26.2 | 4.81 | 0 | 0 | 13h30 | 0.469 | 0.3275 | 0.060125 | 0 | 0
14h30 | 37.52 | 26.2 | 4.81 | 0 | 0 | 14h30 | 0.469 | 0.3275 | 0.060125 | 0 | 0
15h30 | 17.58 | 6.31 | 0 | 0 | 0 | 15h30 | 0.21975 | 0.078875 | 0 | 0 | 0
16h30 | 21.91 | 10.74 | 0 | 0 | 0 | 16h30 | 0.27387 | 0.13425 | 0 | 0 | 0
17h30 | 37.87 | 28.63 | 6.83 | 0 | 0 | 17h30 | 0.47337 | 0.35787 | 0.085375 | 0 | 0
18h30 | 37.29 | 29.5 | 8.32 | 0 | 0 | 18h30 | 0.46613 | 0.36875 | 0.104 | 0 | 0
19h30 | 29.09 | 22.32 | 5.27 | 0 | 0 | 19h30 | 0.36362 | 0.279 | 0.065875 | 0 | 0
20h30 | 25.34 | 17.02 | 3.78 | 0 | 0 | 20h30 | 0.31675 | 0.21275 | 0.04725 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 32.46 | 22.83 | 5.72 | 0 | 0 | 06h30 | 0.40575 | 0.28537 | 0.0715 | 0 | 0
07h30 | 88.19 | 80.45 | 47.33 | 29.11 | 8.44 | 07h30 | 1.1024 | 1.0056 | 0.59162 | 0.36388 | 0.1055
08h30 | 70.24 | 59.45 | 41.61 | 29.11 | 8.44 | 08h30 | 0.878 | 0.74313 | 0.52012 | 0.36388 | 0.1055
09h30 | 63.26 | 51.59 | 23.24 | 7.36 | 0 | 09h30 | 0.79075 | 0.64487 | 0.2905 | 0.092 | 0
10h30 | 61.35 | 49.76 | 23.24 | 7.36 | 0 | 10h30 | 0.76687 | 0.622 | 0.2905 | 0.092 | 0
11h30 | 60.94 | 48.64 | 18.21 | 3.62 | 0 | 11h30 | 0.76175 | 0.608 | 0.22762 | 0.04525 | 0
12h30 | 60.68 | 48.64 | 18.26 | 4.61 | 0 | 12h30 | 0.7585 | 0.608 | 0.22825 | 0.057625 | 0
13h30 | 61.81 | 50.01 | 18.89 | 6.03 | 0 | 13h30 | 0.77263 | 0.62513 | 0.23613 | 0.075375 | 0
14h30 | 63.07 | 51.39 | 19.26 | 6.63 | 0 | 14h30 | 0.78838 | 0.64238 | 0.24075 | 0.082875 | 0
15h30 | 68.97 | 57.76 | 22.97 | 10.44 | 0 | 15h30 | 0.86213 | 0.722 | 0.28713 | 0.1305 | 0
16h30 | 76.45 | 66.14 | 28.79 | 16.46 | 0 | 16h30 | 0.95562 | 0.82675 | 0.35988 | 0.20575 | 0
17h30 | 79.53 | 70.23 | 32.6 | 20.03 | 0 | 17h30 | 0.99413 | 0.87787 | 0.4075 | 0.25038 | 0
18h30 | 89.83 | 81.48 | 40.84 | 27.84 | 1.79 | 18h30 | 1.1229 | 1.0185 | 0.5105 | 0.348 | 0.022375
19h30 | 91.86 | 84.3 | 43.76 | 30.66 | 5.14 | 19h30 | 1.1482 | 1.0537 | 0.547 | 0.38325 | 0.06425
20h30 | 86.17 | 79.13 | 41.46 | 28.42 | 5.2 | 20h30 | 1.0771 | 0.98913 | 0.51825 | 0.35525 | 0.065
21h30 | 91.67 | 85.05 | 45.66 | 32.48 | 10.29 | 21h30 | 1.1459 | 1.0631 | 0.57075 | 0.406 | 0.12862
22h30 | 100.59 | 94.27 | 51.82 | 38.4 | 16.53 | 22h30 | 1.2574 | 1.1784 | 0.64775 | 0.48 | 0.20663
23h30 | 95.5 | 89.16 | 49.21 | 35.84 | 15.32 | 23h30 | 1.1938 | 1.1145 | 0.61513 | 0.448 | 0.1915
00h30 | 60.91 | 64.1 | 30.88 | 16.74 | 7.23 | 00h30 | 0.76138 | 0.80125 | 0.386 | 0.20925 | 0.090375
01h30 | 43.96 | 35.71 | 13.69 | 0 | 0 | 01h30 | 0.5495 | 0.44638 | 0.17112 | 0 | 0
02h30 | 43.96 | 35.71 | 13.69 | 0 | 0 | 02h30 | 0.5495 | 0.44638 | 0.17112 | 0 | 0
03h30 | 52.74 | 41.93 | 19.18 | 5.38 | 0 | 03h30 | 0.65925 | 0.52412 | 0.23975 | 0.06725 | 0
04h30 | 61.7 | 51.17 | 25.64 | 12.07 | 0 | 04h30 | 0.77125 | 0.63962 | 0.3205 | 0.15088 | 0
05h30 | 50.47 | 40.3 | 19.75 | 6.69 | 0 | 05h30 | 0.63087 | 0.50375 | 0.24688 | 0.083625 | 0
06h30 | 41.51 | 31.07 | 13.29 | 0 | 0 | 06h30 | 0.51887 | 0.38838 | 0.16612 | 0 | 0
07h30 | 56.56 | 47.08 | 27.72 | 16.76 | 2.32 | 07h30 | 0.707 | 0.5885 | 0.3465 | 0.2095 | 0.029
08h30 | 60.82 | 51.3 | 27.72 | 16.76 | 2.32 | 08h30 | 0.76025 | 0.64125 | 0.3465 | 0.2095 | 0.029
09h30 | 61.38 | 51 | 23.69 | 14.21 | 0 | 09h30 | 0.76725 | 0.6375 | 0.29613 | 0.17763 | 0
10h30 | 58.09 | 46.84 | 23.69 | 14.21 | 0 | 10h30 | 0.72613 | 0.5855 | 0.29613 | 0.17763 | 0
11h30 | 51.2 | 39.93 | 15.9 | 7.39 | 0 | 11h30 | 0.64 | 0.49912 | 0.19875 | 0.092375 | 0
12h30 | 50.23 | 39.88 | 15.9 | 7.39 | 0 | 12h30 | 0.62787 | 0.4985 | 0.19875 | 0.092375 | 0
13h30 | 38.51 | 28.52 | 7.42 | 0 | 0 | 13h30 | 0.48137 | 0.3565 | 0.09275 | 0 | 0
14h30 | 39.45 | 28.52 | 7.42 | 0 | 0 | 14h30 | 0.49312 | 0.3565 | 0.09275 | 0 | 0
15h30 | 49.07 | 37.31 | 12.79 | 4.56 | 0 | 15h30 | 0.61338 | 0.46637 | 0.15987 | 0.057 | 0
16h30 | 49.87 | 39.18 | 14.8 | 5.78 | 0 | 16h30 | 0.62338 | 0.48975 | 0.185 | 0.07225 | 0
17h30 | 45.78 | 36.38 | 14.28 | 4.85 | 0 | 17h30 | 0.57225 | 0.45475 | 0.1785 | 0.060625 | 0
18h30 | 44.04 | 35.16 | 14.74 | 5.3 | 0 | 18h30 | 0.5505 | 0.4395 | 0.18425 | 0.06625 | 0
19h30 | 46.8 | 39.64 | 18.27 | 8.98 | 0 | 19h30 | 0.585 | 0.4955 | 0.22837 | 0.11225 | 0
20h30 | 46.8 | 39.14 | 18.65 | 9.2 | 0 | 20h30 | 0.585 | 0.48925 | 0.23312 | 0.115 | 0
21h30 | 39.03 | 32.53 | 15.39 | 5.37 | 0 | 21h30 | 0.48788 | 0.40663 | 0.19237 | 0.067125 | 0
22h30 | 39.03 | 32.37 | 14.3 | 3.61 | 0 | 22h30 | 0.48788 | 0.40463 | 0.17875 | 0.045125 | 0
23h30 | 36.14 | 29.25 | 14.96 | 3.69 | 0 | 23h30 | 0.45175 | 0.36562 | 0.187 | 0.046125 | 0
00h30 | 36.14 | 29.25 | 13.2 | 3.56 | 0 | 00h30 | 0.45175 | 0.36562 | 0.165 | 0.0445 | 0
01h30 | 24.58 | 16.7 | 4.47 | 0 | 0 | 01h30 | 0.30725 | 0.20875 | 0.055875 | 0 | 0
02h30 | 24.58 | 16.7 | 4.47 | 0 | 0 | 02h30 | 0.30725 | 0.20875 | 0.055875 | 0 | 0
03h30 | 9.44 | 1.39 | 0 | 0 | 0 | 03h30 | 0.118 | 0.017375 | 0 | 0 | 0
04h30 | 23.34 | 14.23 | 4.48 | 0 | 0 | 04h30 | 0.29175 | 0.17788 | 0.056 | 0 | 0
05h30 | 20.39 | 12.83 | 4.48 | 0 | 0 | 05h30 | 0.25488 | 0.16037 | 0.056 | 0 | 0
06h30 | 20.34 | 8.96 | 2.43 | 0 | 0 | 06h30 | 0.25425 | 0.112 | 0.030375 | 0 | 0
07h30 | 31.7 | 20.73 | 14.46 | 0.43 | 0 | 07h30 | 0.39625 | 0.25912 | 0.18075 | 0.005375 | 0
08h30 | 19.22 | 11.77 | 12.03 | 0.43 | 0 | 08h30 | 0.24025 | 0.14713 | 0.15038 | 0.005375 | 0
09h30 | 16.55 | 0 | 0 | 0 | 0 | 09h30 | 0.20688 | 0 | 0 | 0 | 0
10h30 | 15.65 | 1.56 | 0 | 0 | 0 | 10h30 | 0.19562 | 0.0195 | 0 | 0 | 0
11h30 | 15.21 | 2 | 0 | 0 | 0 | 11h30 | 0.19012 | 0.025 | 0 | 0 | 0
12h30 | 16.27 | 3.15 | 0 | 0 | 0 | 12h30 | 0.20338 | 0.039375 | 0 | 0 | 0
13h30 | 16.25 | 3.34 | 0 | 0 | 0 | 13h30 | 0.20312 | 0.04175 | 0 | 0 | 0
14h30 | 16.54 | 4 | 0 | 0 | 0 | 14h30 | 0.20675 | 0.05 | 0 | 0 | 0
15h30 | 20.66 | 8.55 | 0 | 0 | 0 | 15h30 | 0.25825 | 0.10687 | 0 | 0 | 0
16h30 | 29.32 | 17.71 | 4.26 | 0 | 0 | 16h30 | 0.3665 | 0.22137 | 0.05325 | 0 | 0
17h30 | 33.5 | 22.36 | 7.98 | 0 | 0 | 17h30 | 0.41875 | 0.2795 | 0.09975 | 0 | 0
18h30 | 33.4 | 22.57 | 9.05 | 0 | 0 | 18h30 | 0.4175 | 0.28213 | 0.11313 | 0 | 0
19h30 | 40.12 | 29.4 | 14.02 | 0.75 | 0 | 19h30 | 0.5015 | 0.3675 | 0.17525 | 0.009375 | 0
20h30 | 37.04 | 26.31 | 12.61 | 0.75 | 0 | 20h30 | 0.463 | 0.32887 | 0.15762 | 0.009375 | 0
21h30 | 21.24 | 10.34 | 3.91 | 0 | 0 | 21h30 | 0.2655 | 0.12925 | 0.048875 | 0 | 0
22h30 | 14.96 | 3.74 | 0 | 0 | 0 | 22h30 | 0.187 | 0.04675 | 0 | 0 | 0
23h30 | 18.22 | 6.56 | 1.47 | 0 | 0 | 23h30 | 0.22775 | 0.082 | 0.018375 | 0 | 0
00h30 | 17.19 | 3.5 | 1.47 | 0 | 0 | 00h30 | 0.21488 | 0.04375 | 0.018375 | 0 | 0
01h30 | 10.56 | 1.47 | 0 | 0 | 0 | 01h30 | 0.132 | 0.018375 | 0 | 0 | 0
02h30 | 13.9 | 2.93 | 0 | 0 | 0 | 02h30 | 0.17375 | 0.036625 | 0 | 0 | 0
03h30 | 16.04 | 4.77 | 0 | 0 | 0 | 03h30 | 0.2005 | 0.059625 | 0 | 0 | 0
04h30 | 20.19 | 8.6 | 2.38 | 0 | 0 | 04h30 | 0.25238 | 0.1075 | 0.02975 | 0 | 0
05h30 | 21.56 | 9.44 | 3.43 | 0 | 0 | 05h30 | 0.2695 | 0.118 | 0.042875 | 0 | 0
06h30 | 20.73 | 8.06 | 2.42 | 0 | 0 | 06h30 | 0.25912 | 0.10075 | 0.03025 | 0 | 0
07h30 | 38.34 | 24.78 | 17.36 | 0 | 0 | 07h30 | 0.47925 | 0.30975 | 0.217 | 0 | 0
08h30 | 32.85 | 20.88 | 16 | 0 | 0 | 08h30 | 0.41063 | 0.261 | 0.2 | 0 | 0
09h30 | 17.73 | 1.25 | 0 | 0 | 0 | 09h30 | 0.22162 | 0.015625 | 0 | 0 | 0
10h30 | 16.55 | 1.25 | 0 | 0 | 0 | 10h30 | 0.20688 | 0.015625 | 0 | 0 | 0
11h30 | 10.02 | 0 | 0 | 0 | 0 | 11h30 | 0.12525 | 0 | 0 | 0 | 0
12h30 | 23.64 | 10.58 | 0 | 0 | 0 | 12h30 | 0.2955 | 0.13225 | 0 | 0 | 0
13h30 | 13.62 | 10.58 | 0 | 0 | 0 | 13h30 | 0.17025 | 0.13225 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 6.49 | 0 | 0 | 0 | 0 | 22h30 | 0.081125 | 0 | 0 | 0 | 0
23h30 | 8.93 | 0 | 0 | 0 | 0 | 23h30 | 0.11163 | 0 | 0 | 0 | 0
00h30 | 2.44 | 0 | 0 | 0 | 0 | 00h30 | 0.0305 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 3.39 | 0 | 0 | 0 | 0 | 03h30 | 0.042375 | 0 | 0 | 0 | 0
04h30 | 3.39 | 0 | 0 | 0 | 0 | 04h30 | 0.042375 | 0 | 0 | 0 | 0
05h30 | 2.33 | 0 | 0 | 0 | 0 | 05h30 | 0.029125 | 0 | 0 | 0 | 0
06h30 | 3.33 | 0 | 0 | 0 | 0 | 06h30 | 0.041625 | 0 | 0 | 0 | 0
07h30 | 16.21 | 0 | 0 | 0 | 0 | 07h30 | 0.20262 | 0 | 0 | 0 | 0
08h30 | 15.21 | 0 | 0 | 0 | 0 | 08h30 | 0.19012 | 0 | 0 | 0 | 0
09h30 | 2.88 | 0 | 0 | 0 | 0 | 09h30 | 0.036 | 0 | 0 | 0 | 0
10h30 | 2.88 | 0 | 0 | 0 | 0 | 10h30 | 0.036 | 0 | 0 | 0 | 0
11h30 | 1.84 | 0 | 0 | 0 | 0 | 11h30 | 0.023 | 0 | 0 | 0 | 0
12h30 | 5.45 | 0 | 0 | 0 | 0 | 12h30 | 0.068125 | 0 | 0 | 0 | 0
13h30 | 5.45 | 0 | 0 | 0 | 0 | 13h30 | 0.068125 | 0 | 0 | 0 | 0
14h30 | 5.3 | 0 | 0 | 0 | 0 | 14h30 | 0.06625 | 0 | 0 | 0 | 0
15h30 | 3.45 | 0 | 0 | 0 | 0 | 15h30 | 0.043125 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 3.74 | 0 | 0 | 0 | 0 | 21h30 | 0.04675 | 0 | 0 | 0 | 0
22h30 | 8.3 | 0 | 0 | 0 | 0 | 22h30 | 0.10375 | 0 | 0 | 0 | 0
23h30 | 4.93 | 0 | 0 | 0 | 0 | 23h30 | 0.061625 | 0 | 0 | 0 | 0
00h30 | 0.37 | 0 | 0 | 0 | 0 | 00h30 | 0.004625 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 2.96 | 0 | 0 | 0 | 0 | 02h30 | 0.037 | 0 | 0 | 0 | 0
03h30 | 6.36 | 0 | 0 | 0 | 0 | 03h30 | 0.0795 | 0 | 0 | 0 | 0
04h30 | 7.74 | 0 | 0 | 0 | 0 | 04h30 | 0.09675 | 0 | 0 | 0 | 0
05h30 | 7.71 | 0 | 0 | 0 | 0 | 05h30 | 0.096375 | 0 | 0 | 0 | 0
06h30 | 6.54 | 0 | 0 | 0 | 0 | 06h30 | 0.08175 | 0 | 0 | 0 | 0
07h30 | 20.9 | 3.45 | 0 | 0 | 0 | 07h30 | 0.26125 | 0.043125 | 0 | 0 | 0
08h30 | 18.79 | 3.45 | 0 | 0 | 0 | 08h30 | 0.23488 | 0.043125 | 0 | 0 | 0
09h30 | 22.71 | 5.56 | 0 | 0 | 0 | 09h30 | 0.28387 | 0.0695 | 0 | 0 | 0
10h30 | 21.64 | 5.56 | 0 | 0 | 0 | 10h30 | 0.2705 | 0.0695 | 0 | 0 | 0
11h30 | 12.14 | 0 | 0 | 0 | 0 | 11h30 | 0.15175 | 0 | 0 | 0 | 0
12h30 | 12.14 | 0 | 0 | 0 | 0 | 12h30 | 0.15175 | 0 | 0 | 0 | 0
13h30 | 16.63 | 1.87 | 0 | 0 | 0 | 13h30 | 0.20788 | 0.023375 | 0 | 0 | 0
14h30 | 23.21 | 9.19 | 0 | 0 | 0 | 14h30 | 0.29013 | 0.11488 | 0 | 0 | 0
15h30 | 19.56 | 7.32 | 0 | 0 | 0 | 15h30 | 0.2445 | 0.0915 | 0 | 0 | 0
16h30 | 12.99 | 0 | 0 | 0 | 0 | 16h30 | 0.16237 | 0 | 0 | 0 | 0
17h30 | 9.58 | 0 | 0 | 0 | 0 | 17h30 | 0.11975 | 0 | 0 | 0 | 0
18h30 | 9.58 | 0 | 0 | 0 | 0 | 18h30 | 0.11975 | 0 | 0 | 0 | 0
19h30 | 5.36 | 0 | 0 | 0 | 0 | 19h30 | 0.067 | 0 | 0 | 0 | 0
20h30 | 11.74 | 0 | 0 | 0 | 0 | 20h30 | 0.14675 | 0 | 0 | 0 | 0
21h30 | 12.74 | 1.41 | 0 | 0 | 0 | 21h30 | 0.15925 | 0.017625 | 0 | 0 | 0
22h30 | 6.62 | 1.41 | 0 | 0 | 0 | 22h30 | 0.08275 | 0.017625 | 0 | 0 | 0
23h30 | 3.46 | 0 | 0 | 0 | 0 | 23h30 | 0.04325 | 0 | 0 | 0 | 0
00h30 | 3.21 | 0 | 0 | 0 | 0 | 00h30 | 0.040125 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0.52 | 0 | 0 | 0 | 0 | 03h30 | 0.0065 | 0 | 0 | 0 | 0
04h30 | 2.51 | 0 | 0 | 0 | 0 | 04h30 | 0.031375 | 0 | 0 | 0 | 0
05h30 | 3.77 | 0 | 0 | 0 | 0 | 05h30 | 0.047125 | 0 | 0 | 0 | 0
06h30 | 8.7 | 0 | 0 | 0 | 0 | 06h30 | 0.10875 | 0 | 0 | 0 | 0
07h30 | 22.04 | 5.61 | 0.48 | 0 | 0 | 07h30 | 0.2755 | 0.070125 | 0.006 | 0 | 0
08h30 | 17.5 | 5.61 | 0.48 | 0 | 0 | 08h30 | 0.21875 | 0.070125 | 0.006 | 0 | 0
09h30 | 24.34 | 6.57 | 0 | 0 | 0 | 09h30 | 0.30425 | 0.082125 | 0 | 0 | 0
10h30 | 21.94 | 6.57 | 0 | 0 | 0 | 10h30 | 0.27425 | 0.082125 | 0 | 0 | 0
11h30 | 14.37 | 0 | 0 | 0 | 0 | 11h30 | 0.17963 | 0 | 0 | 0 | 0
12h30 | 14.37 | 0 | 0 | 0 | 0 | 12h30 | 0.17963 | 0 | 0 | 0 | 0
13h30 | 7.23 | 0 | 0 | 0 | 0 | 13h30 | 0.090375 | 0 | 0 | 0 | 0
14h30 | 13.01 | 0 | 0 | 0 | 0 | 14h30 | 0.16262 | 0 | 0 | 0 | 0
15h30 | 5.79 | 0 | 0 | 0 | 0 | 15h30 | 0.072375 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 1.93 | 0 | 0 | 0 | 0 | 19h30 | 0.024125 | 0 | 0 | 0 | 0
20h30 | 14.13 | 0 | 0 | 0 | 0 | 20h30 | 0.17663 | 0 | 0 | 0 | 0
21h30 | 24.42 | 13.85 | 0 | 0 | 0 | 21h30 | 0.30525 | 0.17313 | 0 | 0 | 0
22h30 | 23.35 | 13.85 | 1.44 | 0 | 0 | 22h30 | 0.29187 | 0.17313 | 0.018 | 0 | 0
23h30 | 13.22 | 2.38 | 1.44 | 0 | 0 | 23h30 | 0.16525 | 0.02975 | 0.018 | 0 | 0
00h30 | 2.1 | 2.38 | 0 | 0 | 0 | 00h30 | 0.02625 | 0.02975 | 0 | 0 | 0
01h30 | 14.97 | 2.29 | 0 | 0 | 0 | 01h30 | 0.18713 | 0.028625 | 0 | 0 | 0
02h30 | 27.99 | 15.99 | 0.44 | 0 | 0 | 02h30 | 0.34987 | 0.19987 | 0.0055 | 0 | 0
03h30 | 34.4 | 21.95 | 4.97 | 0 | 0 | 03h30 | 0.43 | 0.27437 | 0.062125 | 0 | 0
04h30 | 40.7 | 29.11 | 9.95 | 0 | 0 | 04h30 | 0.50875 | 0.36388 | 0.12437 | 0 | 0
05h30 | 43.48 | 32.11 | 12.87 | 0 | 0 | 05h30 | 0.5435 | 0.40137 | 0.16087 | 0 | 0
06h30 | 35.91 | 24.45 | 8.49 | 0 | 0 | 06h30 | 0.44888 | 0.30562 | 0.10612 | 0 | 0
07h30 | 41.18 | 30.22 | 17.25 | 0 | 0 | 07h30 | 0.51475 | 0.37775 | 0.21563 | 0 | 0
08h30 | 35.73 | 24.02 | 16.21 | 0 | 0 | 08h30 | 0.44662 | 0.30025 | 0.20262 | 0 | 0
09h30 | 39.64 | 27.43 | 9.82 | 0 | 0 | 09h30 | 0.4955 | 0.34287 | 0.12275 | 0 | 0
10h30 | 45.9 | 34.31 | 12.93 | 0 | 0 | 10h30 | 0.57375 | 0.42888 | 0.16162 | 0 | 0
11h30 | 40.9 | 29.12 | 7.35 | 0 | 0 | 11h30 | 0.51125 | 0.364 | 0.091875 | 0 | 0
12h30 | 28.33 | 15.24 | 4.24 | 0 | 0 | 12h30 | 0.35413 | 0.1905 | 0.053 | 0 | 0
13h30 | 25.55 | 14.08 | 0 | 0 | 0 | 13h30 | 0.31938 | 0.176 | 0 | 0 | 0
14h30 | 29.18 | 17.17 | 0 | 0 | 0 | 14h30 | 0.36475 | 0.21463 | 0 | 0 | 0
15h30 | 27.04 | 14.71 | 0 | 0 | 0 | 15h30 | 0.338 | 0.18388 | 0 | 0 | 0
16h30 | 27.11 | 16.17 | 0 | 0 | 0 | 16h30 | 0.33887 | 0.20212 | 0 | 0 | 0
17h30 | 32.19 | 23.02 | 4.45 | 0 | 0 | 17h30 | 0.40237 | 0.28775 | 0.055625 | 0 | 0
18h30 | 39.4 | 31.76 | 11.12 | 0 | 0 | 18h30 | 0.4925 | 0.397 | 0.139 | 0 | 0
19h30 | 41.92 | 35.43 | 14.75 | 0 | 0 | 19h30 | 0.524 | 0.44288 | 0.18438 | 0 | 0
20h30 | 35.16 | 29.49 | 12.24 | 0 | 0 | 20h30 | 0.4395 | 0.36862 | 0.153 | 0 | 0
21h30 | 34.75 | 29.45 | 12.89 | 0 | 0 | 21h30 | 0.43438 | 0.36812 | 0.16112 | 0 | 0
22h30 | 40.93 | 35.75 | 17.25 | 0 | 0 | 22h30 | 0.51162 | 0.44688 | 0.21563 | 0 | 0
23h30 | 21.42 | 16.15 | 8.52 | 0 | 0 | 23h30 | 0.26775 | 0.20187 | 0.1065 | 0 | 0
00h30 | 11.08 | 2.51 | 0 | 0 | 0 | 00h30 | 0.1385 | 0.031375 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 11.91 | 0 | 0 | 0 | 0 | 07h30 | 0.14888 | 0 | 0 | 0 | 0
08h30 | 11.91 | 0 | 0 | 0 | 0 | 08h30 | 0.14888 | 0 | 0 | 0 | 0
09h30 | 1.24 | 0 | 0 | 0 | 0 | 09h30 | 0.0155 | 0 | 0 | 0 | 0
10h30 | 1.24 | 0 | 0 | 0 | 0 | 10h30 | 0.0155 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 9.5 | 0 | 0 | 0 | 0 | 14h30 | 0.11875 | 0 | 0 | 0 | 0
15h30 | 30.73 | 19.66 | 3.81 | 0 | 0 | 15h30 | 0.38412 | 0.24575 | 0.047625 | 0 | 0
16h30 | 25.1 | 19.66 | 3.81 | 0 | 0 | 16h30 | 0.31375 | 0.24575 | 0.047625 | 0 | 0
17h30 | 7.84 | 0 | 0 | 0 | 0 | 17h30 | 0.098 | 0 | 0 | 0 | 0
18h30 | 3.97 | 0 | 0 | 0 | 0 | 18h30 | 0.049625 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0.4 | 0 | 0 | 0 | 0 | 23h30 | 0.005 | 0 | 0 | 0 | 0
00h30 | 0.4 | 0 | 0 | 0 | 0 | 00h30 | 0.005 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 11.35 | 0 | 0 | 0 | 0 | 07h30 | 0.14188 | 0 | 0 | 0 | 0
08h30 | 11.35 | 0 | 0 | 0 | 0 | 08h30 | 0.14188 | 0 | 0 | 0 | 0
09h30 | 3.3 | 0 | 0 | 0 | 0 | 09h30 | 0.04125 | 0 | 0 | 0 | 0
10h30 | 3.3 | 0 | 0 | 0 | 0 | 10h30 | 0.04125 | 0 | 0 | 0 | 0
11h30 | 0.21 | 0 | 0 | 0 | 0 | 11h30 | 0.002625 | 0 | 0 | 0 | 0
12h30 | 19.59 | 1.22 | 0 | 0 | 0 | 12h30 | 0.24488 | 0.01525 | 0 | 0 | 0
13h30 | 35.67 | 22.94 | 6.56 | 0 | 0 | 13h30 | 0.44588 | 0.28675 | 0.082 | 0 | 0
14h30 | 29.97 | 21.73 | 6.56 | 0 | 0 | 14h30 | 0.37462 | 0.27163 | 0.082 | 0 | 0
15h30 | 32.03 | 20.31 | 4.31 | 0 | 0 | 15h30 | 0.40037 | 0.25388 | 0.053875 | 0 | 0
16h30 | 35.91 | 24.7 | 8.12 | 0 | 0 | 16h30 | 0.44888 | 0.30875 | 0.1015 | 0 | 0
17h30 | 33.02 | 22.01 | 7.24 | 0 | 0 | 17h30 | 0.41275 | 0.27513 | 0.0905 | 0 | 0
18h30 | 29.88 | 19.29 | 6.16 | 0 | 0 | 18h30 | 0.3735 | 0.24113 | 0.077 | 0 | 0
19h30 | 37.43 | 27.08 | 11.3 | 0 | 0 | 19h30 | 0.46787 | 0.3385 | 0.14125 | 0 | 0
20h30 | 39.92 | 29.74 | 13.23 | 0 | 0 | 20h30 | 0.499 | 0.37175 | 0.16537 | 0 | 0
21h30 | 31.76 | 21.66 | 8.61 | 0 | 0 | 21h30 | 0.397 | 0.27075 | 0.10762 | 0 | 0
22h30 | 27.83 | 17.72 | 6.42 | 0 | 0 | 22h30 | 0.34787 | 0.2215 | 0.08025 | 0 | 0
23h30 | 14.22 | 4.05 | 2.47 | 0 | 0 | 23h30 | 0.17775 | 0.050625 | 0.030875 | 0 | 0
00h30 | 1.24 | 3.66 | 0 | 0 | 0 | 00h30 | 0.0155 | 0.04575 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 8.81 | 0 | 0 | 0 | 0 | 02h30 | 0.11013 | 0 | 0 | 0 | 0
03h30 | 25.76 | 15.4 | 2.74 | 0 | 0 | 03h30 | 0.322 | 0.1925 | 0.03425 | 0 | 0
04h30 | 26.69 | 15.4 | 4.01 | 0 | 0 | 04h30 | 0.33363 | 0.1925 | 0.050125 | 0 | 0
05h30 | 28.75 | 17.58 | 4.95 | 0 | 0 | 05h30 | 0.35938 | 0.21975 | 0.061875 | 0 | 0
06h30 | 19.02 | 17.58 | 3.68 | 0 | 0 | 06h30 | 0.23775 | 0.21975 | 0.046 | 0 | 0
07h30 | 30.16 | 16.46 | 11.39 | 0 | 0 | 07h30 | 0.377 | 0.20575 | 0.14238 | 0 | 0
08h30 | 40.27 | 27.36 | 13.97 | 0 | 0 | 08h30 | 0.50338 | 0.342 | 0.17463 | 0 | 0
09h30 | 21.64 | 10.9 | 2.58 | 0 | 0 | 09h30 | 0.2705 | 0.13625 | 0.03225 | 0 | 0
10h30 | 19.74 | 7.58 | 1.07 | 0 | 0 | 10h30 | 0.24675 | 0.09475 | 0.013375 | 0 | 0
11h30 | 36.31 | 25.83 | 11.01 | 0 | 0 | 11h30 | 0.45387 | 0.32288 | 0.13762 | 0 | 0
12h30 | 37.37 | 26.87 | 11.48 | 0 | 0 | 12h30 | 0.46713 | 0.33587 | 0.1435 | 0 | 0
13h30 | 42.06 | 31.93 | 14.21 | 0 | 0 | 13h30 | 0.52575 | 0.39913 | 0.17763 | 0 | 0
14h30 | 44.32 | 34.5 | 15.45 | 0 | 0 | 14h30 | 0.554 | 0.43125 | 0.19312 | 0 | 0
15h30 | 42.4 | 32.87 | 14.47 | 0 | 0 | 15h30 | 0.53 | 0.41087 | 0.18088 | 0 | 0
16h30 | 40.08 | 30.84 | 13.61 | 0 | 0 | 16h30 | 0.501 | 0.3855 | 0.17012 | 0 | 0
17h30 | 40.09 | 31.06 | 14.35 | 0 | 0 | 17h30 | 0.50113 | 0.38825 | 0.17938 | 0 | 0
18h30 | 40.27 | 31.26 | 15.07 | 0 | 0 | 18h30 | 0.50338 | 0.39075 | 0.18837 | 0 | 0
19h30 | 28.2 | 19.1 | 8.03 | 0 | 0 | 19h30 | 0.3525 | 0.23875 | 0.10038 | 0 | 0
20h30 | 18.82 | 9.74 | 5.39 | 0 | 0 | 20h30 | 0.23525 | 0.12175 | 0.067375 | 0 | 0
21h30 | 14.11 | 3.46 | 0 | 0 | 0 | 21h30 | 0.17638 | 0.04325 | 0 | 0 | 0
22h30 | 25.93 | 16.15 | 6.18 | 0 | 0 | 22h30 | 0.32412 | 0.20187 | 0.07725 | 0 | 0
23h30 | 29.67 | 20.02 | 9.41 | 0 | 0 | 23h30 | 0.37088 | 0.25025 | 0.11762 | 0 | 0
00h30 | 17.86 | 11.09 | 3.23 | 0 | 0 | 00h30 | 0.22325 | 0.13862 | 0.040375 | 0 | 0
01h30 | 29.87 | 22.74 | 8.19 | 0 | 0 | 01h30 | 0.37338 | 0.28425 | 0.10237 | 0 | 0
02h30 | 38.71 | 28.34 | 12.59 | 0 | 0 | 02h30 | 0.48387 | 0.35425 | 0.15737 | 0 | 0
03h30 | 41.87 | 32.23 | 15.41 | 0 | 0 | 03h30 | 0.52338 | 0.40287 | 0.19262 | 0 | 0
04h30 | 36.47 | 26.86 | 12.86 | 0 | 0 | 04h30 | 0.45587 | 0.33575 | 0.16075 | 0 | 0
05h30 | 32.01 | 22.21 | 10.43 | 0 | 0 | 05h30 | 0.40013 | 0.27763 | 0.13037 | 0 | 0
06h30 | 29.63 | 19.55 | 8.88 | 0 | 0 | 06h30 | 0.37038 | 0.24438 | 0.111 | 0 | 0
07h30 | 48.33 | 37.8 | 25.09 | 9.92 | 0 | 07h30 | 0.60413 | 0.4725 | 0.31362 | 0.124 | 0
08h30 | 47.28 | 36.46 | 24.78 | 9.92 | 0 | 08h30 | 0.591 | 0.45575 | 0.30975 | 0.124 | 0
09h30 | 30.27 | 14.16 | 4.65 | 0 | 0 | 09h30 | 0.37838 | 0.177 | 0.058125 | 0 | 0
10h30 | 30.27 | 14.16 | 4.98 | 0 | 0 | 10h30 | 0.37838 | 0.177 | 0.06225 | 0 | 0
11h30 | 26.79 | 15.15 | 5.72 | 0 | 0 | 11h30 | 0.33487 | 0.18937 | 0.0715 | 0 | 0
12h30 | 29.1 | 18.13 | 6.92 | 0 | 0 | 12h30 | 0.36375 | 0.22662 | 0.0865 | 0 | 0
13h30 | 28.67 | 18.27 | 6.69 | 0 | 0 | 13h30 | 0.35837 | 0.22837 | 0.083625 | 0 | 0
14h30 | 28.11 | 18.07 | 6.34 | 0 | 0 | 14h30 | 0.35137 | 0.22587 | 0.07925 | 0 | 0
15h30 | 25.12 | 15.45 | 4.63 | 0 | 0 | 15h30 | 0.314 | 0.19312 | 0.057875 | 0 | 0
16h30 | 23.38 | 12.66 | 3.45 | 0 | 0 | 16h30 | 0.29225 | 0.15825 | 0.043125 | 0 | 0
17h30 | 21.3 | 11.97 | 3.08 | 0 | 0 | 17h30 | 0.26625 | 0.14963 | 0.0385 | 0 | 0
18h30 | 24.7 | 15.2 | 5.79 | 0 | 0 | 18h30 | 0.30875 | 0.19 | 0.072375 | 0 | 0
19h30 | 21.33 | 11.85 | 4.11 | 0 | 0 | 19h30 | 0.26663 | 0.14813 | 0.051375 | 0 | 0
20h30 | 17.93 | 8.62 | 1.4 | 0 | 0 | 20h30 | 0.22412 | 0.10775 | 0.0175 | 0 | 0
21h30 | 9.02 | 0 | 0 | 0 | 0 | 21h30 | 0.11275 | 0 | 0 | 0 | 0
22h30 | 9.02 | 0 | 0 | 0 | 0 | 22h30 | 0.11275 | 0 | 0 | 0 | 0
23h30 | 9.12 | 0 | 0 | 0 | 0 | 23h30 | 0.114 | 0 | 0 | 0 | 0
00h30 | 9.12 | 0 | 0 | 0 | 0 | 00h30 | 0.114 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0.85 | 0 | 0 | 0 | 0 | 04h30 | 0.010625 | 0 | 0 | 0 | 0
05h30 | 2.31 | 0 | 0 | 0 | 0 | 05h30 | 0.028875 | 0 | 0 | 0 | 0
06h30 | 3.37 | 0 | 0 | 0 | 0 | 06h30 | 0.042125 | 0 | 0 | 0 | 0
07h30 | 17.47 | 0.76 | 0.33 | 0 | 0 | 07h30 | 0.21838 | 0.0095 | 0.004125 | 0 | 0
08h30 | 15.56 | 0.76 | 0.33 | 0 | 0 | 08h30 | 0.1945 | 0.0095 | 0.004125 | 0 | 0
09h30 | 13.35 | 0 | 0 | 0 | 0 | 09h30 | 0.16687 | 0 | 0 | 0 | 0
10h30 | 13.35 | 0 | 0 | 0 | 0 | 10h30 | 0.16687 | 0 | 0 | 0 | 0
11h30 | 14.87 | 0.25 | 0 | 0 | 0 | 11h30 | 0.18588 | 0.003125 | 0 | 0 | 0
12h30 | 14.87 | 0.52 | 0 | 0 | 0 | 12h30 | 0.18588 | 0.0065 | 0 | 0 | 0
13h30 | 0 | 0.28 | 0 | 0 | 0 | 13h30 | 0 | 0.0035 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0.95 | 0 | 0 | 0 | 0 | 18h30 | 0.011875 | 0 | 0 | 0 | 0
19h30 | 12.04 | 0 | 0 | 0 | 0 | 19h30 | 0.1505 | 0 | 0 | 0 | 0
20h30 | 21.25 | 9.96 | 1.02 | 0 | 0 | 20h30 | 0.26562 | 0.1245 | 0.01275 | 0 | 0
21h30 | 16.07 | 9.96 | 1.02 | 0 | 0 | 21h30 | 0.20087 | 0.1245 | 0.01275 | 0 | 0
22h30 | 11.22 | 0 | 0 | 0 | 0 | 22h30 | 0.14025 | 0 | 0 | 0 | 0
23h30 | 11.21 | 0.58 | 0 | 0 | 0 | 23h30 | 0.14012 | 0.00725 | 0 | 0 | 0
00h30 | 5.91 | 0.58 | 0 | 0 | 0 | 00h30 | 0.073875 | 0.00725 | 0 | 0 | 0
01h30 | 7.79 | 0 | 0 | 0 | 0 | 01h30 | 0.097375 | 0 | 0 | 0 | 0
02h30 | 8.15 | 0 | 0 | 0 | 0 | 02h30 | 0.10187 | 0 | 0 | 0 | 0
03h30 | 6.62 | 0 | 0 | 0 | 0 | 03h30 | 0.08275 | 0 | 0 | 0 | 0
04h30 | 7 | 0 | 0 | 0 | 0 | 04h30 | 0.0875 | 0 | 0 | 0 | 0
05h30 | 10.38 | 0 | 0 | 0 | 0 | 05h30 | 0.12975 | 0 | 0 | 0 | 0
06h30 | 20.57 | 8.72 | 0 | 0 | 0 | 06h30 | 0.25712 | 0.109 | 0 | 0 | 0
07h30 | 46.49 | 34.73 | 21.85 | 0 | 0 | 07h30 | 0.58113 | 0.43412 | 0.27313 | 0 | 0
08h30 | 35.55 | 26.01 | 21.85 | 0 | 0 | 08h30 | 0.44438 | 0.32512 | 0.27313 | 0 | 0
09h30 | 16.69 | 0 | 0 | 0 | 0 | 09h30 | 0.20863 | 0 | 0 | 0 | 0
10h30 | 16.69 | 0 | 0 | 0 | 0 | 10h30 | 0.20863 | 0 | 0 | 0 | 0
11h30 | 11.23 | 0 | 0 | 0 | 0 | 11h30 | 0.14037 | 0 | 0 | 0 | 0
12h30 | 13.94 | 2.37 | 0 | 0 | 0 | 12h30 | 0.17425 | 0.029625 | 0 | 0 | 0
13h30 | 13.34 | 2.37 | 0 | 0 | 0 | 13h30 | 0.16675 | 0.029625 | 0 | 0 | 0
14h30 | 10.63 | 0 | 0 | 0 | 0 | 14h30 | 0.13287 | 0 | 0 | 0 | 0
15h30 | 6.32 | 0 | 0 | 0 | 0 | 15h30 | 0.079 | 0 | 0 | 0 | 0
16h30 | 8.5 | 0 | 0 | 0 | 0 | 16h30 | 0.10625 | 0 | 0 | 0 | 0
17h30 | 11.61 | 1.46 | 0 | 0 | 0 | 17h30 | 0.14513 | 0.01825 | 0 | 0 | 0
18h30 | 9.43 | 1.46 | 0 | 0 | 0 | 18h30 | 0.11787 | 0.01825 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 20.35 | 9.99 | 0 | 0 | 0 | 01h30 | 0.25438 | 0.12487 | 0 | 0 | 0
02h30 | 34.16 | 24.16 | 7.59 | 0 | 0 | 02h30 | 0.427 | 0.302 | 0.094875 | 0 | 0
03h30 | 42.82 | 31.75 | 11.03 | 0 | 0 | 03h30 | 0.53525 | 0.39687 | 0.13787 | 0 | 0
04h30 | 44.56 | 34.37 | 13.44 | 0 | 0 | 04h30 | 0.557 | 0.42962 | 0.168 | 0 | 0
05h30 | 46.37 | 36.67 | 15.59 | 0 | 0 | 05h30 | 0.57962 | 0.45837 | 0.19487 | 0 | 0
06h30 | 52.25 | 42.47 | 19.49 | 0 | 0 | 06h30 | 0.65312 | 0.53087 | 0.24363 | 0 | 0
07h30 | 64.04 | 55.13 | 32.83 | 12.93 | 0 | 07h30 | 0.8005 | 0.68912 | 0.41037 | 0.16162 | 0
08h30 | 42.6 | 32.53 | 18.93 | 12.93 | 0 | 08h30 | 0.5325 | 0.40663 | 0.23663 | 0.16162 | 0
09h30 | 33.34 | 17.33 | 4.48 | 0 | 0 | 09h30 | 0.41675 | 0.21663 | 0.056 | 0 | 0
10h30 | 69.22 | 57.47 | 29.82 | 14.12 | 0 | 10h30 | 0.86525 | 0.71837 | 0.37275 | 0.1765 | 0
11h30 | 78.57 | 68.41 | 35.47 | 18.58 | 0 | 11h30 | 0.98213 | 0.85513 | 0.44338 | 0.23225 | 0
12h30 | 74.93 | 64.91 | 32.47 | 15.99 | 0 | 12h30 | 0.93663 | 0.81137 | 0.40587 | 0.19987 | 0
13h30 | 56.74 | 46.86 | 22.34 | 11.53 | 0 | 13h30 | 0.70925 | 0.58575 | 0.27925 | 0.14413 | 0
14h30 | 46.94 | 37.17 | 14.35 | 0.37 | 0 | 14h30 | 0.58675 | 0.46463 | 0.17938 | 0.004625 | 0
15h30 | 46.59 | 37.28 | 15.24 | 0.62 | 0 | 15h30 | 0.58237 | 0.466 | 0.1905 | 0.00775 | 0
16h30 | 60.92 | 52.31 | 25.32 | 10.25 | 0 | 16h30 | 0.7615 | 0.65387 | 0.3165 | 0.12812 | 0
17h30 | 82.17 | 74.06 | 39.59 | 23.98 | 1.58 | 17h30 | 1.0271 | 0.92575 | 0.49488 | 0.29975 | 0.01975
18h30 | 91.18 | 83.28 | 46.43 | 30.52 | 7.06 | 18h30 | 1.1398 | 1.041 | 0.58037 | 0.3815 | 0.08825
19h30 | 85.97 | 78.04 | 43.93 | 28.62 | 6.68 | 19h30 | 1.0746 | 0.9755 | 0.54912 | 0.35775 | 0.0835
20h30 | 75.13 | 67.04 | 37.55 | 22.94 | 3.44 | 20h30 | 0.93912 | 0.838 | 0.46937 | 0.28675 | 0.043
21h30 | 59.93 | 51.56 | 28.5 | 14.23 | 2.24 | 21h30 | 0.74913 | 0.6445 | 0.35625 | 0.17788 | 0.028
22h30 | 49.23 | 40.39 | 22.13 | 8 | 0 | 22h30 | 0.61538 | 0.50487 | 0.27663 | 0.1 | 0
23h30 | 63.71 | 54.22 | 30.8 | 16.8 | 1.46 | 23h30 | 0.79638 | 0.67775 | 0.385 | 0.21 | 0.01825
00h30 | 64.76 | 57.74 | 29.09 | 12.17 | 1.46 | 00h30 | 0.8095 | 0.72175 | 0.36362 | 0.15213 | 0.01825
01h30 | 70.79 | 63.85 | 35.89 | 17.48 | 0 | 01h30 | 0.88487 | 0.79812 | 0.44862 | 0.2185 | 0
02h30 | 63.61 | 54.1 | 28.94 | 17.48 | 0 | 02h30 | 0.79512 | 0.67625 | 0.36175 | 0.2185 | 0
03h30 | 54.59 | 45.13 | 24.27 | 8.85 | 0 | 03h30 | 0.68237 | 0.56412 | 0.30338 | 0.11063 | 0
04h30 | 54.45 | 44.63 | 24.55 | 9.49 | 0 | 04h30 | 0.68063 | 0.55788 | 0.30688 | 0.11862 | 0
05h30 | 57.25 | 46.9 | 26.51 | 11.32 | 0 | 05h30 | 0.71562 | 0.58625 | 0.33137 | 0.1415 | 0
06h30 | 44.41 | 33.85 | 17.59 | 10.68 | 0 | 06h30 | 0.55512 | 0.42312 | 0.21987 | 0.1335 | 0
07h30 | 43.42 | 32.91 | 19.67 | 6.9 | 0 | 07h30 | 0.54275 | 0.41137 | 0.24588 | 0.08625 | 0
08h30 | 38.29 | 26.87 | 18.45 | 6.9 | 0 | 08h30 | 0.47863 | 0.33587 | 0.23062 | 0.08625 | 0
09h30 | 44.3 | 32.74 | 12.89 | 1.41 | 0 | 09h30 | 0.55375 | 0.40925 | 0.16112 | 0.017625 | 0
10h30 | 48.82 | 37.04 | 15.47 | 3.91 | 0 | 10h30 | 0.61025 | 0.463 | 0.19337 | 0.048875 | 0
11h30 | 46.04 | 34.49 | 12.6 | 2.5 | 0 | 11h30 | 0.5755 | 0.43112 | 0.1575 | 0.03125 | 0
12h30 | 41.52 | 27.36 | 10.02 | 0 | 0 | 12h30 | 0.519 | 0.342 | 0.12525 | 0 | 0
13h30 | 37.17 | 26.35 | 7.47 | 0 | 0 | 13h30 | 0.46463 | 0.32937 | 0.093375 | 0 | 0
14h30 | 37.17 | 25.96 | 7.47 | 0 | 0 | 14h30 | 0.46463 | 0.3245 | 0.093375 | 0 | 0
15h30 | 46.51 | 35.18 | 11.24 | 2.23 | 0 | 15h30 | 0.58137 | 0.43975 | 0.1405 | 0.027875 | 0
16h30 | 58.32 | 48.43 | 21.48 | 10.29 | 0 | 16h30 | 0.729 | 0.60537 | 0.2685 | 0.12862 | 0
17h30 | 53.92 | 45.95 | 21.98 | 10.22 | 0 | 17h30 | 0.674 | 0.57437 | 0.27475 | 0.12775 | 0
18h30 | 51.46 | 44.84 | 22.48 | 11.21 | 0 | 18h30 | 0.64325 | 0.5605 | 0.281 | 0.14012 | 0
19h30 | 44.92 | 38.88 | 19.8 | 9.05 | 0 | 19h30 | 0.5615 | 0.486 | 0.2475 | 0.11313 | 0
20h30 | 35.58 | 26.75 | 9.06 | 0 | 0 | 20h30 | 0.44475 | 0.33437 | 0.11325 | 0 | 0
21h30 | 7.83 | 2.36 | 0 | 0 | 0 | 21h30 | 0.097875 | 0.0295 | 0 | 0 | 0
22h30 | 7.83 | 2.36 | 0 | 0 | 0 | 22h30 | 0.097875 | 0.0295 | 0 | 0 | 0
23h30 | 1 | 0 | 0 | 0 | 0 | 23h30 | 0.0125 | 0 | 0 | 0 | 0
00h30 | 1 | 0 | 0 | 0 | 0 | 00h30 | 0.0125 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0.32 | 0 | 0 | 0 | 0 | 02h30 | 0.004 | 0 | 0 | 0 | 0
03h30 | 1.74 | 0 | 0 | 0 | 0 | 03h30 | 0.02175 | 0 | 0 | 0 | 0
04h30 | 3.37 | 0 | 0 | 0 | 0 | 04h30 | 0.042125 | 0 | 0 | 0 | 0
05h30 | 5.54 | 0 | 0 | 0 | 0 | 05h30 | 0.06925 | 0 | 0 | 0 | 0
06h30 | 7.18 | 0 | 0 | 0 | 0 | 06h30 | 0.08975 | 0 | 0 | 0 | 0
07h30 | 20.91 | 4.79 | 4.37 | 0 | 0 | 07h30 | 0.26138 | 0.059875 | 0.054625 | 0 | 0
08h30 | 17.32 | 4.79 | 4.37 | 0 | 0 | 08h30 | 0.2165 | 0.059875 | 0.054625 | 0 | 0
09h30 | 20.48 | 1.65 | 0 | 0 | 0 | 09h30 | 0.256 | 0.020625 | 0 | 0 | 0
10h30 | 24.97 | 9.76 | 0 | 0 | 0 | 10h30 | 0.31212 | 0.122 | 0 | 0 | 0
11h30 | 31.01 | 16.44 | 3.9 | 0 | 0 | 11h30 | 0.38762 | 0.2055 | 0.04875 | 0 | 0
12h30 | 31.55 | 17.09 | 4.17 | 0 | 0 | 12h30 | 0.39437 | 0.21363 | 0.052125 | 0 | 0
13h30 | 34.96 | 21.03 | 5.99 | 0 | 0 | 13h30 | 0.437 | 0.26288 | 0.074875 | 0 | 0
14h30 | 44.68 | 31.31 | 11.34 | 0 | 0 | 14h30 | 0.5585 | 0.39137 | 0.14175 | 0 | 0
15h30 | 58.11 | 45.43 | 20.54 | 6.21 | 0 | 15h30 | 0.72637 | 0.56788 | 0.25675 | 0.077625 | 0
16h30 | 62.11 | 50.3 | 25.09 | 9.47 | 0 | 16h30 | 0.77638 | 0.62875 | 0.31362 | 0.11837 | 0
17h30 | 45.27 | 34.06 | 16.25 | 3.26 | 0 | 17h30 | 0.56588 | 0.42575 | 0.20312 | 0.04075 | 0
18h30 | 26.53 | 14.41 | 6.07 | 0 | 0 | 18h30 | 0.33163 | 0.18013 | 0.075875 | 0 | 0
19h30 | 24.96 | 14.51 | 5 | 0 | 0 | 19h30 | 0.312 | 0.18138 | 0.0625 | 0 | 0
20h30 | 43.77 | 33.2 | 16.94 | 3.91 | 0 | 20h30 | 0.54712 | 0.415 | 0.21175 | 0.048875 | 0
21h30 | 54.53 | 43.98 | 23.63 | 11.46 | 0 | 21h30 | 0.68163 | 0.54975 | 0.29537 | 0.14325 | 0
22h30 | 50.07 | 39.24 | 21.06 | 8.39 | 0 | 22h30 | 0.62587 | 0.4905 | 0.26325 | 0.10487 | 0
23h30 | 42.86 | 31.65 | 16.75 | 4.51 | 0 | 23h30 | 0.53575 | 0.39563 | 0.20938 | 0.056375 | 0
00h30 | 28.51 | 19.22 | 7.39 | 3.67 | 0 | 00h30 | 0.35637 | 0.24025 | 0.092375 | 0.045875 | 0
01h30 | 36.83 | 28.9 | 13.18 | 0 | 0 | 01h30 | 0.46037 | 0.36125 | 0.16475 | 0 | 0
02h30 | 43.05 | 31.85 | 15.53 | 1.25 | 0 | 02h30 | 0.53812 | 0.39813 | 0.19412 | 0.015625 | 0
03h30 | 48.81 | 37.98 | 19.82 | 4.72 | 0 | 03h30 | 0.61013 | 0.47475 | 0.24775 | 0.059 | 0
04h30 | 50.4 | 39.36 | 21.38 | 6.5 | 0 | 04h30 | 0.63 | 0.492 | 0.26725 | 0.08125 | 0
05h30 | 44.52 | 33.05 | 18.06 | 3.83 | 0 | 05h30 | 0.5565 | 0.41313 | 0.22575 | 0.047875 | 0
06h30 | 36.7 | 22.92 | 14.15 | 0.8 | 0 | 06h30 | 0.45875 | 0.2865 | 0.17688 | 0.01 | 0
07h30 | 35.02 | 23.09 | 12.86 | 2.15 | 0 | 07h30 | 0.43775 | 0.28863 | 0.16075 | 0.026875 | 0
08h30 | 35.02 | 23.09 | 12.86 | 2.15 | 0 | 08h30 | 0.43775 | 0.28863 | 0.16075 | 0.026875 | 0
09h30 | 16.45 | 3.5 | 0 | 0 | 0 | 09h30 | 0.20563 | 0.04375 | 0 | 0 | 0
10h30 | 26.01 | 14.29 | 0.45 | 0 | 0 | 10h30 | 0.32512 | 0.17863 | 0.005625 | 0 | 0
11h30 | 28.64 | 16.59 | 2.47 | 0 | 0 | 11h30 | 0.358 | 0.20738 | 0.030875 | 0 | 0
12h30 | 27.92 | 16.57 | 2.01 | 0 | 0 | 12h30 | 0.349 | 0.20713 | 0.025125 | 0 | 0
13h30 | 32.42 | 21.51 | 4.72 | 0 | 0 | 13h30 | 0.40525 | 0.26887 | 0.059 | 0 | 0
14h30 | 34.32 | 23.68 | 5.99 | 0 | 0 | 14h30 | 0.429 | 0.296 | 0.074875 | 0 | 0
15h30 | 28.55 | 18.79 | 3.96 | 0 | 0 | 15h30 | 0.35687 | 0.23488 | 0.0495 | 0 | 0
16h30 | 20.11 | 11.64 | 2.7 | 0 | 0 | 16h30 | 0.25138 | 0.1455 | 0.03375 | 0 | 0
17h30 | 17.42 | 9.9 | 0.35 | 0 | 0 | 17h30 | 0.21775 | 0.12375 | 0.004375 | 0 | 0
18h30 | 19.55 | 12.62 | 3.07 | 0 | 0 | 18h30 | 0.24438 | 0.15775 | 0.038375 | 0 | 0
19h30 | 9.98 | 8.51 | 2.72 | 0 | 0 | 19h30 | 0.12475 | 0.10637 | 0.034 | 0 | 0
20h30 | 5.55 | 0 | 0 | 0 | 0 | 20h30 | 0.069375 | 0 | 0 | 0 | 0
21h30 | 18.31 | 8.72 | 1.01 | 0 | 0 | 21h30 | 0.22887 | 0.109 | 0.012625 | 0 | 0
22h30 | 36.23 | 28.73 | 14.86 | 1.62 | 0 | 22h30 | 0.45288 | 0.35913 | 0.18575 | 0.02025 | 0
23h30 | 24.72 | 20.01 | 13.85 | 1.62 | 0 | 23h30 | 0.309 | 0.25012 | 0.17313 | 0.02025 | 0
00h30 | 6.79 | 0 | 0 | 0 | 0 | 00h30 | 0.084875 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 4.46 | 0 | 0 | 0 | 0 | 04h30 | 0.05575 | 0 | 0 | 0 | 0
05h30 | 15.89 | 4.33 | 0 | 0 | 0 | 05h30 | 0.19862 | 0.054125 | 0 | 0 | 0
06h30 | 24.48 | 13.71 | 4.87 | 0 | 0 | 06h30 | 0.306 | 0.17137 | 0.060875 | 0 | 0
07h30 | 32.46 | 20.84 | 13.1 | 0 | 0 | 07h30 | 0.40575 | 0.2605 | 0.16375 | 0 | 0
08h30 | 25.59 | 13.19 | 8.23 | 0 | 0 | 08h30 | 0.31988 | 0.16487 | 0.10287 | 0 | 0
09h30 | 37.07 | 23.61 | 8.92 | 0 | 0 | 09h30 | 0.46337 | 0.29513 | 0.1115 | 0 | 0
10h30 | 42.08 | 28.99 | 13.39 | 0.86 | 0 | 10h30 | 0.526 | 0.36238 | 0.16737 | 0.01075 | 0
11h30 | 40.07 | 27.52 | 11.51 | 0.86 | 0 | 11h30 | 0.50087 | 0.344 | 0.14388 | 0.01075 | 0
12h30 | 34.65 | 22.58 | 8.32 | 0 | 0 | 12h30 | 0.43312 | 0.28225 | 0.104 | 0 | 0
13h30 | 31.68 | 20.04 | 6.7 | 0 | 0 | 13h30 | 0.396 | 0.2505 | 0.08375 | 0 | 0
14h30 | 31.85 | 20.62 | 7.06 | 0 | 0 | 14h30 | 0.39813 | 0.25775 | 0.08825 | 0 | 0
15h30 | 30.34 | 19.52 | 6.68 | 0 | 0 | 15h30 | 0.37925 | 0.244 | 0.0835 | 0 | 0
16h30 | 32.36 | 21.86 | 8.53 | 0 | 0 | 16h30 | 0.4045 | 0.27325 | 0.10662 | 0 | 0
17h30 | 37.24 | 26.91 | 12.16 | 0.65 | 0 | 17h30 | 0.4655 | 0.33637 | 0.152 | 0.008125 | 0
18h30 | 35.59 | 25.3 | 11.75 | 0.65 | 0 | 18h30 | 0.44488 | 0.31625 | 0.14688 | 0.008125 | 0
19h30 | 31.72 | 21.44 | 9.68 | 0 | 0 | 19h30 | 0.3965 | 0.268 | 0.121 | 0 | 0
20h30 | 25.6 | 17.97 | 6.6 | 0 | 0 | 20h30 | 0.32 | 0.22462 | 0.0825 | 0 | 0
21h30 | 16.43 | 5.4 | 0.32 | 0 | 0 | 21h30 | 0.20538 | 0.0675 | 0.004 | 0 | 0
22h30 | 16.26 | 5.4 | 0.32 | 0 | 0 | 22h30 | 0.20325 | 0.0675 | 0.004 | 0 | 0
23h30 | 7.23 | 0 | 0 | 0 | 0 | 23h30 | 0.090375 | 0 | 0 | 0 | 0
00h30 | 7.23 | 0 | 0 | 0 | 0 | 00h30 | 0.090375 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 4.2 | 0 | 0 | 0 | 0 | 04h30 | 0.0525 | 0 | 0 | 0 | 0
05h30 | 8.38 | 0 | 0 | 0 | 0 | 05h30 | 0.10475 | 0 | 0 | 0 | 0
06h30 | 6.2 | 0 | 0 | 0 | 0 | 06h30 | 0.0775 | 0 | 0 | 0 | 0
07h30 | 18.87 | 6.79 | 2.49 | 0 | 0 | 07h30 | 0.23588 | 0.084875 | 0.031125 | 0 | 0
08h30 | 16.85 | 6.79 | 2.49 | 0 | 0 | 08h30 | 0.21063 | 0.084875 | 0.031125 | 0 | 0
09h30 | 20.76 | 5.88 | 0 | 0 | 0 | 09h30 | 0.2595 | 0.0735 | 0 | 0 | 0
10h30 | 23.7 | 11.53 | 2.07 | 0 | 0 | 10h30 | 0.29625 | 0.14413 | 0.025875 | 0 | 0
11h30 | 19.47 | 8.35 | 2.07 | 0 | 0 | 11h30 | 0.24338 | 0.10437 | 0.025875 | 0 | 0
12h30 | 16.53 | 2.83 | 0 | 0 | 0 | 12h30 | 0.20663 | 0.035375 | 0 | 0 | 0
13h30 | 13.72 | 3.77 | 0 | 0 | 0 | 13h30 | 0.1715 | 0.047125 | 0 | 0 | 0
14h30 | 13.72 | 3.64 | 0 | 0 | 0 | 14h30 | 0.1715 | 0.0455 | 0 | 0 | 0
15h30 | 10.25 | 1.19 | 0 | 0 | 0 | 15h30 | 0.12812 | 0.014875 | 0 | 0 | 0
16h30 | 11.76 | 3.01 | 0 | 0 | 0 | 16h30 | 0.147 | 0.037625 | 0 | 0 | 0
17h30 | 14.78 | 6.48 | 0 | 0 | 0 | 17h30 | 0.18475 | 0.081 | 0 | 0 | 0
18h30 | 18.96 | 10.98 | 1.32 | 0 | 0 | 18h30 | 0.237 | 0.13725 | 0.0165 | 0 | 0
19h30 | 9.39 | 6.33 | 1.32 | 0 | 0 | 19h30 | 0.11737 | 0.079125 | 0.0165 | 0 | 0
20h30 | 3.69 | 0 | 0 | 0 | 0 | 20h30 | 0.046125 | 0 | 0 | 0 | 0
21h30 | 11.32 | 0 | 0 | 0 | 0 | 21h30 | 0.1415 | 0 | 0 | 0 | 0
22h30 | 28.82 | 20.94 | 7.58 | 0 | 0 | 22h30 | 0.36025 | 0.26175 | 0.09475 | 0 | 0
23h30 | 30.13 | 22.96 | 9.57 | 0 | 0 | 23h30 | 0.37662 | 0.287 | 0.11962 | 0 | 0
00h30 | 12.63 | 2.02 | 1.99 | 0 | 0 | 00h30 | 0.15787 | 0.02525 | 0.024875 | 0 | 0
01h30 | 1.6 | 0 | 0 | 0 | 0 | 01h30 | 0.02 | 0 | 0 | 0 | 0
02h30 | 18.14 | 9.39 | 0 | 0 | 0 | 02h30 | 0.22675 | 0.11737 | 0 | 0 | 0
03h30 | 16.54 | 9.39 | 0 | 0 | 0 | 03h30 | 0.20675 | 0.11737 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 9.22 | 0.79 | 0 | 0 | 0 | 05h30 | 0.11525 | 0.009875 | 0 | 0 | 0
06h30 | 11.15 | 3.72 | 0 | 0 | 0 | 06h30 | 0.13937 | 0.0465 | 0 | 0 | 0
07h30 | 19.66 | 12.67 | 7.46 | 0 | 0 | 07h30 | 0.24575 | 0.15837 | 0.09325 | 0 | 0
08h30 | 17.73 | 9.74 | 7.46 | 0 | 0 | 08h30 | 0.22162 | 0.12175 | 0.09325 | 0 | 0
09h30 | 11.39 | 0.22 | 0 | 0 | 0 | 09h30 | 0.14238 | 0.00275 | 0 | 0 | 0
10h30 | 11.39 | 0.22 | 0 | 0 | 0 | 10h30 | 0.14238 | 0.00275 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 4.85 | 0 | 0 | 0 | 0 | 12h30 | 0.060625 | 0 | 0 | 0 | 0
13h30 | 4.91 | 0 | 0 | 0 | 0 | 13h30 | 0.061375 | 0 | 0 | 0 | 0
14h30 | 3.81 | 0 | 0 | 0 | 0 | 14h30 | 0.047625 | 0 | 0 | 0 | 0
15h30 | 5.39 | 0 | 0 | 0 | 0 | 15h30 | 0.067375 | 0 | 0 | 0 | 0
16h30 | 7.38 | 0.57 | 0 | 0 | 0 | 16h30 | 0.09225 | 0.007125 | 0 | 0 | 0
17h30 | 5.75 | 0.57 | 0 | 0 | 0 | 17h30 | 0.071875 | 0.007125 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 2.2 | 0 | 0 | 0 | 0 | 19h30 | 0.0275 | 0 | 0 | 0 | 0
20h30 | 6.5 | 0.02 | 0 | 0 | 0 | 20h30 | 0.08125 | 0.00025 | 0 | 0 | 0
21h30 | 4.31 | 0.02 | 0 | 0 | 0 | 21h30 | 0.053875 | 0.00025 | 0 | 0 | 0
22h30 | 3.83 | 0 | 0 | 0 | 0 | 22h30 | 0.047875 | 0 | 0 | 0 | 0
23h30 | 5.02 | 0 | 0 | 0 | 0 | 23h30 | 0.06275 | 0 | 0 | 0 | 0
00h30 | 1.19 | 0 | 0 | 0 | 0 | 00h30 | 0.014875 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 6.02 | 0 | 0 | 0 | 0 | 02h30 | 0.07525 | 0 | 0 | 0 | 0
03h30 | 9.43 | 0.22 | 0 | 0 | 0 | 03h30 | 0.11787 | 0.00275 | 0 | 0 | 0
04h30 | 11.23 | 1.52 | 0 | 0 | 0 | 04h30 | 0.14037 | 0.019 | 0 | 0 | 0
05h30 | 16.21 | 6.86 | 0 | 0 | 0 | 05h30 | 0.20262 | 0.08575 | 0 | 0 | 0
06h30 | 14.92 | 6.01 | 0 | 0 | 0 | 06h30 | 0.1865 | 0.075125 | 0 | 0 | 0
07h30 | 20.42 | 14.46 | 5.91 | 0 | 0 | 07h30 | 0.25525 | 0.18075 | 0.073875 | 0 | 0
08h30 | 13.9 | 14.02 | 5.91 | 0 | 0 | 08h30 | 0.17375 | 0.17525 | 0.073875 | 0 | 0
09h30 | 5.86 | 0 | 0 | 0 | 0 | 09h30 | 0.07325 | 0 | 0 | 0 | 0
10h30 | 5.86 | 0 | 0 | 0 | 0 | 10h30 | 0.07325 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 8.28 | 4.51 | 0 | 0 | 0 | 16h30 | 0.1035 | 0.056375 | 0 | 0 | 0
17h30 | 8.28 | 4.51 | 0 | 0 | 0 | 17h30 | 0.1035 | 0.056375 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 2.1 | 0 | 0 | 0 | 0 | 02h30 | 0.02625 | 0 | 0 | 0 | 0
03h30 | 6.62 | 0 | 0 | 0 | 0 | 03h30 | 0.08275 | 0 | 0 | 0 | 0
04h30 | 14.86 | 4.16 | 0 | 0 | 0 | 04h30 | 0.18575 | 0.052 | 0 | 0 | 0
05h30 | 17.69 | 7.05 | 0 | 0 | 0 | 05h30 | 0.22112 | 0.088125 | 0 | 0 | 0
06h30 | 9.32 | 2.89 | 0 | 0 | 0 | 06h30 | 0.1165 | 0.036125 | 0 | 0 | 0
07h30 | 14.14 | 4.44 | 0 | 0 | 0 | 07h30 | 0.17675 | 0.0555 | 0 | 0 | 0
08h30 | 12.16 | 4.44 | 0 | 0 | 0 | 08h30 | 0.152 | 0.0555 | 0 | 0 | 0
09h30 | 0 | 0 | 0 | 0 | 0 | 09h30 | 0 | 0 | 0 | 0 | 0
10h30 | 0 | 0 | 0 | 0 | 0 | 10h30 | 0 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 10.97 | 1.89 | 0 | 0 | 0 | 16h30 | 0.13712 | 0.023625 | 0 | 0 | 0
17h30 | 17.28 | 7.97 | 0 | 0 | 0 | 17h30 | 0.216 | 0.099625 | 0 | 0 | 0
18h30 | 12.3 | 6.08 | 0 | 0 | 0 | 18h30 | 0.15375 | 0.076 | 0 | 0 | 0
19h30 | 6.45 | 0 | 0 | 0 | 0 | 19h30 | 0.080625 | 0 | 0 | 0 | 0
20h30 | 10.31 | 1.34 | 0 | 0 | 0 | 20h30 | 0.12887 | 0.01675 | 0 | 0 | 0
21h30 | 17.09 | 8.85 | 0 | 0 | 0 | 21h30 | 0.21363 | 0.11063 | 0 | 0 | 0
22h30 | 15.8 | 7.76 | 0 | 0 | 0 | 22h30 | 0.1975 | 0.097 | 0 | 0 | 0
23h30 | 8.57 | 0.69 | 0 | 0 | 0 | 23h30 | 0.10712 | 0.008625 | 0 | 0 | 0
00h30 | 0 | 0.44 | 0 | 0 | 0 | 00h30 | 0 | 0.0055 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 3.13 | 0 | 0 | 0 | 0 | 04h30 | 0.039125 | 0 | 0 | 0 | 0
05h30 | 5.52 | 0 | 0 | 0 | 0 | 05h30 | 0.069 | 0 | 0 | 0 | 0
06h30 | 7.05 | 0 | 0 | 0 | 0 | 06h30 | 0.088125 | 0 | 0 | 0 | 0
07h30 | 20.81 | 10.65 | 0.95 | 0 | 0 | 07h30 | 0.26012 | 0.13312 | 0.011875 | 0 | 0
08h30 | 16.15 | 10.65 | 0.95 | 0 | 0 | 08h30 | 0.20187 | 0.13312 | 0.011875 | 0 | 0
09h30 | 12.36 | 0.3 | 0 | 0 | 0 | 09h30 | 0.1545 | 0.00375 | 0 | 0 | 0
10h30 | 12.36 | 0.3 | 0 | 0 | 0 | 10h30 | 0.1545 | 0.00375 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 6.1 | 0 | 0 | 0 | 0 | 20h30 | 0.07625 | 0 | 0 | 0 | 0
21h30 | 10.74 | 1.19 | 0 | 0 | 0 | 21h30 | 0.13425 | 0.014875 | 0 | 0 | 0
22h30 | 11 | 1.81 | 0 | 0 | 0 | 22h30 | 0.1375 | 0.022625 | 0 | 0 | 0
23h30 | 7.63 | 0.61 | 0 | 0 | 0 | 23h30 | 0.095375 | 0.007625 | 0 | 0 | 0
00h30 | 1.26 | 0 | 0 | 0 | 0 | 00h30 | 0.01575 | 0 | 0 | 0 | 0
01h30 | 0.07 | 0 | 0 | 0 | 0 | 01h30 | 0.000875 | 0 | 0 | 0 | 0
02h30 | 6.22 | 0 | 0 | 0 | 0 | 02h30 | 0.07775 | 0 | 0 | 0 | 0
03h30 | 11.34 | 0.45 | 0 | 0 | 0 | 03h30 | 0.14175 | 0.005625 | 0 | 0 | 0
04h30 | 12 | 0.45 | 0 | 0 | 0 | 04h30 | 0.15 | 0.005625 | 0 | 0 | 0
05h30 | 10.47 | 0 | 0 | 0 | 0 | 05h30 | 0.13087 | 0 | 0 | 0 | 0
06h30 | 9.3 | 0 | 0 | 0 | 0 | 06h30 | 0.11625 | 0 | 0 | 0 | 0
07h30 | 19.16 | 10.04 | 0 | 0 | 0 | 07h30 | 0.2395 | 0.1255 | 0 | 0 | 0
08h30 | 13.51 | 10.04 | 0 | 0 | 0 | 08h30 | 0.16887 | 0.1255 | 0 | 0 | 0
09h30 | 1.71 | 0 | 0 | 0 | 0 | 09h30 | 0.021375 | 0 | 0 | 0 | 0
10h30 | 1.71 | 0 | 0 | 0 | 0 | 10h30 | 0.021375 | 0 | 0 | 0 | 0
11h30 | 4.78 | 0 | 0 | 0 | 0 | 11h30 | 0.05975 | 0 | 0 | 0 | 0
12h30 | 10.9 | 2.3 | 0 | 0 | 0 | 12h30 | 0.13625 | 0.02875 | 0 | 0 | 0
13h30 | 16.05 | 6.66 | 0 | 0 | 0 | 13h30 | 0.20062 | 0.08325 | 0 | 0 | 0
14h30 | 21.04 | 11.56 | 0 | 0 | 0 | 14h30 | 0.263 | 0.1445 | 0 | 0 | 0
15h30 | 21.61 | 12.69 | 0 | 0 | 0 | 15h30 | 0.27013 | 0.15862 | 0 | 0 | 0
16h30 | 19.87 | 11.49 | 0 | 0 | 0 | 16h30 | 0.24838 | 0.14363 | 0 | 0 | 0
17h30 | 23.55 | 15.62 | 0.84 | 0 | 0 | 17h30 | 0.29437 | 0.19525 | 0.0105 | 0 | 0
18h30 | 25.79 | 18.13 | 3.36 | 0 | 0 | 18h30 | 0.32238 | 0.22662 | 0.042 | 0 | 0
19h30 | 20.46 | 12.9 | 2.52 | 0 | 0 | 19h30 | 0.25575 | 0.16125 | 0.0315 | 0 | 0
20h30 | 16.92 | 9.34 | 0 | 0 | 0 | 20h30 | 0.2115 | 0.11675 | 0 | 0 | 0
21h30 | 8.06 | 4.94 | 0 | 0 | 0 | 21h30 | 0.10075 | 0.06175 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 16.08 | 2.42 | 0 | 0 | 0 | 23h30 | 0.201 | 0.03025 | 0 | 0 | 0
00h30 | 24.45 | 16.65 | 0 | 0 | 0 | 00h30 | 0.30562 | 0.20813 | 0 | 0 | 0
01h30 | 42.89 | 33.73 | 12.6 | 0 | 0 | 01h30 | 0.53612 | 0.42163 | 0.1575 | 0 | 0
02h30 | 51.89 | 40.77 | 15.56 | 0 | 0 | 02h30 | 0.64863 | 0.50962 | 0.1945 | 0 | 0
03h30 | 47.19 | 37.1 | 14.93 | 0 | 0 | 03h30 | 0.58988 | 0.46375 | 0.18663 | 0 | 0
04h30 | 41.47 | 32.24 | 13.1 | 0 | 0 | 04h30 | 0.51838 | 0.403 | 0.16375 | 0 | 0
05h30 | 46.41 | 37.66 | 17.28 | 0 | 0 | 05h30 | 0.58013 | 0.47075 | 0.216 | 0 | 0
06h30 | 54.68 | 45.89 | 22.72 | 1.55 | 0 | 06h30 | 0.6835 | 0.57363 | 0.284 | 0.019375 | 0
07h30 | 71.15 | 62.97 | 37.81 | 18.64 | 0 | 07h30 | 0.88938 | 0.78712 | 0.47263 | 0.233 | 0
08h30 | 58.14 | 50.1 | 31.25 | 17.09 | 0 | 08h30 | 0.72675 | 0.62625 | 0.39062 | 0.21363 | 0
09h30 | 54.14 | 45.19 | 20.97 | 5.1 | 0 | 09h30 | 0.67675 | 0.56488 | 0.26212 | 0.06375 | 0
10h30 | 58.67 | 49.38 | 23.3 | 7.04 | 0 | 10h30 | 0.73337 | 0.61725 | 0.29125 | 0.088 | 0
11h30 | 55.46 | 46.26 | 20.26 | 5.49 | 0 | 11h30 | 0.69325 | 0.57825 | 0.25325 | 0.068625 | 0
12h30 | 44.03 | 33.19 | 17.92 | 3.55 | 0 | 12h30 | 0.55037 | 0.41487 | 0.224 | 0.044375 | 0
13h30 | 36.25 | 27.03 | 8.14 | 0 | 0 | 13h30 | 0.45312 | 0.33787 | 0.10175 | 0 | 0
14h30 | 36.25 | 26.14 | 8.14 | 0 | 0 | 14h30 | 0.45312 | 0.32675 | 0.10175 | 0 | 0
15h30 | 36.14 | 26.83 | 7 | 0 | 0 | 15h30 | 0.45175 | 0.33537 | 0.0875 | 0 | 0
16h30 | 39.39 | 31.26 | 10.84 | 0 | 0 | 16h30 | 0.49238 | 0.39075 | 0.1355 | 0 | 0
17h30 | 44.52 | 37.67 | 16.08 | 2.87 | 0 | 17h30 | 0.5565 | 0.47087 | 0.201 | 0.035875 | 0
18h30 | 44.28 | 38.14 | 17.52 | 4.17 | 0 | 18h30 | 0.5535 | 0.47675 | 0.219 | 0.052125 | 0
19h30 | 38.07 | 32.16 | 14.54 | 1.54 | 0 | 19h30 | 0.47587 | 0.402 | 0.18175 | 0.01925 | 0
20h30 | 35.06 | 25.27 | 10.36 | 0.24 | 0 | 20h30 | 0.43825 | 0.31588 | 0.1295 | 0.003 | 0
21h30 | 31.47 | 25.85 | 11.75 | 0 | 0 | 21h30 | 0.39337 | 0.32312 | 0.14688 | 0 | 0
22h30 | 41.17 | 34.76 | 17.54 | 4.47 | 0 | 22h30 | 0.51462 | 0.4345 | 0.21925 | 0.055875 | 0
23h30 | 43.53 | 37.02 | 19.25 | 6.19 | 0 | 23h30 | 0.54412 | 0.46275 | 0.24063 | 0.077375 | 0
00h30 | 33.83 | 28.11 | 12.36 | 1.73 | 0 | 00h30 | 0.42288 | 0.35137 | 0.1545 | 0.021625 | 0
01h30 | 35.13 | 27.73 | 10.82 | 0 | 0 | 01h30 | 0.43912 | 0.34663 | 0.13525 | 0 | 0
02h30 | 35.13 | 27.73 | 10.82 | 0 | 0 | 02h30 | 0.43912 | 0.34663 | 0.13525 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 21.04 | 11.94 | 2.64 | 0 | 0 | 04h30 | 0.263 | 0.14925 | 0.033 | 0 | 0
05h30 | 44.44 | 37.43 | 19.05 | 4.8 | 0 | 05h30 | 0.5555 | 0.46787 | 0.23813 | 0.06 | 0
06h30 | 41.98 | 32.19 | 16.41 | 4.8 | 0 | 06h30 | 0.52475 | 0.40237 | 0.20513 | 0.06 | 0
07h30 | 31.73 | 22.25 | 14.74 | 1.05 | 0 | 07h30 | 0.39663 | 0.27813 | 0.18425 | 0.013125 | 0
08h30 | 13.16 | 15.56 | 14.74 | 1.05 | 0 | 08h30 | 0.1645 | 0.1945 | 0.18425 | 0.013125 | 0
09h30 | 18.62 | 0 | 0 | 0 | 0 | 09h30 | 0.23275 | 0 | 0 | 0 | 0
10h30 | 53.3 | 41.84 | 19.97 | 8.52 | 0 | 10h30 | 0.66625 | 0.523 | 0.24963 | 0.1065 | 0
11h30 | 54.67 | 44.73 | 21.86 | 9.33 | 0 | 11h30 | 0.68337 | 0.55912 | 0.27325 | 0.11663 | 0
12h30 | 46 | 36.11 | 15.02 | 2.92 | 0 | 12h30 | 0.575 | 0.45138 | 0.18775 | 0.0365 | 0
13h30 | 43.71 | 33.97 | 13.13 | 2.12 | 0 | 13h30 | 0.54638 | 0.42462 | 0.16412 | 0.0265 | 0
14h30 | 46.62 | 36.57 | 13.88 | 3.03 | 0 | 14h30 | 0.58275 | 0.45713 | 0.1735 | 0.037875 | 0
15h30 | 53.23 | 43.15 | 17.84 | 6.79 | 0 | 15h30 | 0.66538 | 0.53938 | 0.223 | 0.084875 | 0
16h30 | 56.63 | 47.83 | 21.98 | 10.28 | 0 | 16h30 | 0.70788 | 0.59788 | 0.27475 | 0.1285 | 0
17h30 | 32.32 | 40.51 | 18.02 | 6.52 | 0 | 17h30 | 0.404 | 0.50638 | 0.22525 | 0.0815 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 34.15 | 21.03 | 7.18 | 0 | 0 | 23h30 | 0.42688 | 0.26288 | 0.08975 | 0 | 0
00h30 | 47.71 | 39.31 | 14.58 | 0.95 | 0 | 00h30 | 0.59637 | 0.49138 | 0.18225 | 0.011875 | 0
01h30 | 22.03 | 18.28 | 7.39 | 0.95 | 0 | 01h30 | 0.27537 | 0.2285 | 0.092375 | 0.011875 | 0
02h30 | 8.46 | 0 | 0 | 0 | 0 | 02h30 | 0.10575 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 37.39 | 25.68 | 10.19 | 0 | 0 | 05h30 | 0.46737 | 0.321 | 0.12737 | 0 | 0
06h30 | 67.22 | 58.56 | 31.71 | 15.43 | 0 | 06h30 | 0.84025 | 0.732 | 0.39637 | 0.19287 | 0
07h30 | 67.87 | 57.33 | 34.31 | 19.87 | 0.99 | 07h30 | 0.84837 | 0.71662 | 0.42888 | 0.24838 | 0.012375
08h30 | 60.28 | 51.08 | 25.5 | 12.07 | 0.99 | 08h30 | 0.7535 | 0.6385 | 0.31875 | 0.15088 | 0.012375
09h30 | 61.62 | 50.93 | 23 | 9.31 | 0 | 09h30 | 0.77025 | 0.63662 | 0.2875 | 0.11638 | 0
10h30 | 58.86 | 46.07 | 18.47 | 5.24 | 0 | 10h30 | 0.73575 | 0.57588 | 0.23087 | 0.0655 | 0
11h30 | 56.07 | 43.34 | 17 | 4.92 | 0 | 11h30 | 0.70088 | 0.54175 | 0.2125 | 0.0615 | 0
12h30 | 58.49 | 46.74 | 19.64 | 8.15 | 0 | 12h30 | 0.73113 | 0.58425 | 0.2455 | 0.10187 | 0
13h30 | 57.24 | 45.52 | 18.43 | 7.58 | 0 | 13h30 | 0.7155 | 0.569 | 0.23037 | 0.09475 | 0
14h30 | 51.44 | 39.41 | 13.15 | 2.84 | 0 | 14h30 | 0.643 | 0.49262 | 0.16437 | 0.0355 | 0
15h30 | 47.28 | 35.73 | 9.81 | 2.06 | 0 | 15h30 | 0.591 | 0.44662 | 0.12262 | 0.02575 | 0
16h30 | 47.63 | 37.33 | 11.72 | 1.11 | 0 | 16h30 | 0.59537 | 0.46663 | 0.1465 | 0.013875 | 0
17h30 | 45.41 | 36.77 | 14.15 | 2.03 | 0 | 17h30 | 0.56763 | 0.45963 | 0.17688 | 0.025375 | 0
18h30 | 44.16 | 36.94 | 16.47 | 3.73 | 0 | 18h30 | 0.552 | 0.46175 | 0.20588 | 0.046625 | 0
19h30 | 41.92 | 35.53 | 16.59 | 4.49 | 0 | 19h30 | 0.524 | 0.44412 | 0.20738 | 0.056125 | 0
20h30 | 35.6 | 29.71 | 13.78 | 1.67 | 0 | 20h30 | 0.445 | 0.37138 | 0.17225 | 0.020875 | 0
21h30 | 46.34 | 40.88 | 21.17 | 8.49 | 0 | 21h30 | 0.57925 | 0.511 | 0.26462 | 0.10612 | 0
22h30 | 57.46 | 52.1 | 28.49 | 15.53 | 0 | 22h30 | 0.71825 | 0.65125 | 0.35613 | 0.19412 | 0
23h30 | 58.24 | 52.53 | 29.17 | 16.13 | 0 | 23h30 | 0.728 | 0.65663 | 0.36462 | 0.20162 | 0
00h30 | 38.89 | 32.88 | 14.88 | 9.09 | 0 | 00h30 | 0.48612 | 0.411 | 0.186 | 0.11363 | 0
01h30 | 45.42 | 37.03 | 17.61 | 2.66 | 0 | 01h30 | 0.56775 | 0.46287 | 0.22012 | 0.03325 | 0
02h30 | 50.88 | 40.49 | 20.09 | 5.99 | 0 | 02h30 | 0.636 | 0.50613 | 0.25112 | 0.074875 | 0
03h30 | 54.13 | 44.41 | 23.22 | 8.32 | 0 | 03h30 | 0.67663 | 0.55512 | 0.29025 | 0.104 | 0
04h30 | 58.65 | 49.43 | 27 | 12.49 | 0 | 04h30 | 0.73313 | 0.61787 | 0.3375 | 0.15613 | 0
05h30 | 63.59 | 54.3 | 30.61 | 16.16 | 0.51 | 05h30 | 0.79487 | 0.67875 | 0.38262 | 0.202 | 0.006375
06h30 | 52.95 | 39.24 | 24.35 | 8.64 | 0.51 | 06h30 | 0.66187 | 0.4905 | 0.30438 | 0.108 | 0.006375
07h30 | 15.15 | 3.88 | 4.34 | 0 | 0 | 07h30 | 0.18937 | 0.0485 | 0.05425 | 0 | 0
08h30 | 15.15 | 3.88 | 4.34 | 0 | 0 | 08h30 | 0.18937 | 0.0485 | 0.05425 | 0 | 0
09h30 | 6.6 | 0 | 0 | 0 | 0 | 09h30 | 0.0825 | 0 | 0 | 0 | 0
10h30 | 37.99 | 22.49 | 8.62 | 0 | 0 | 10h30 | 0.47487 | 0.28113 | 0.10775 | 0 | 0
11h30 | 76.88 | 65.03 | 35.14 | 22.77 | 6.05 | 11h30 | 0.961 | 0.81288 | 0.43925 | 0.28463 | 0.075625
12h30 | 75.31 | 63.62 | 33.81 | 22.77 | 6.05 | 12h30 | 0.94137 | 0.79525 | 0.42262 | 0.28463 | 0.075625
13h30 | 67.12 | 55.9 | 27.86 | 17.16 | 0 | 13h30 | 0.839 | 0.69875 | 0.34825 | 0.2145 | 0
14h30 | 69.7 | 58.72 | 28.78 | 17.92 | 0 | 14h30 | 0.87125 | 0.734 | 0.35975 | 0.224 | 0
15h30 | 35.54 | 25.06 | 9.42 | 0.76 | 0 | 15h30 | 0.44425 | 0.31325 | 0.11775 | 0.0095 | 0
16h30 | 3.14 | 1.18 | 1.19 | 0 | 0 | 16h30 | 0.03925 | 0.01475 | 0.014875 | 0 | 0
17h30 | 0.46 | 0 | 0 | 0 | 0 | 17h30 | 0.00575 | 0 | 0 | 0 | 0
18h30 | 3.7 | 0 | 0 | 0 | 0 | 18h30 | 0.04625 | 0 | 0 | 0 | 0
19h30 | 4.79 | 0 | 0 | 0 | 0 | 19h30 | 0.059875 | 0 | 0 | 0 | 0
20h30 | 5.6 | 0 | 0 | 0 | 0 | 20h30 | 0.07 | 0 | 0 | 0 | 0
21h30 | 51.98 | 39.22 | 20.83 | 0.34 | 0 | 21h30 | 0.64975 | 0.49025 | 0.26038 | 0.00425 | 0
22h30 | 94.21 | 83.5 | 48.7 | 33.09 | 16.64 | 22h30 | 1.1776 | 1.0437 | 0.60875 | 0.41363 | 0.208
23h30 | 78.55 | 67.28 | 39.05 | 32.75 | 16.64 | 23h30 | 0.98188 | 0.841 | 0.48812 | 0.40937 | 0.208
00h30 | 51.36 | 43.02 | 20.11 | 4.59 | 0 | 00h30 | 0.642 | 0.53775 | 0.25138 | 0.057375 | 0
01h30 | 61.49 | 53.6 | 29.92 | 13.2 | 0 | 01h30 | 0.76863 | 0.67 | 0.374 | 0.165 | 0
02h30 | 66.55 | 56.02 | 31 | 13.82 | 0 | 02h30 | 0.83188 | 0.70025 | 0.3875 | 0.17275 | 0
03h30 | 70.41 | 59.92 | 34.22 | 17.68 | 2.01 | 03h30 | 0.88013 | 0.749 | 0.42775 | 0.221 | 0.025125
04h30 | 70.78 | 59.99 | 34.94 | 18.52 | 3.89 | 04h30 | 0.88475 | 0.74987 | 0.43675 | 0.2315 | 0.048625
05h30 | 66.21 | 54.88 | 32.41 | 16.34 | 3.01 | 05h30 | 0.82763 | 0.686 | 0.40513 | 0.20425 | 0.037625
06h30 | 67.02 | 55.18 | 32.72 | 17.13 | 4.23 | 06h30 | 0.83775 | 0.68975 | 0.409 | 0.21413 | 0.052875
07h30 | 89.72 | 76.74 | 50.06 | 36.17 | 23.25 | 07h30 | 1.1215 | 0.95925 | 0.62575 | 0.45212 | 0.29063
08h30 | 83.62 | 69.11 | 40.12 | 29.33 | 20.14 | 08h30 | 1.0453 | 0.86387 | 0.5015 | 0.36662 | 0.25175
09h30 | 75.79 | 62.01 | 34.4 | 22.02 | 9.11 | 09h30 | 0.94737 | 0.77512 | 0.43 | 0.27525 | 0.11388
10h30 | 69.89 | 57.36 | 33.28 | 22.02 | 9.11 | 10h30 | 0.87362 | 0.717 | 0.416 | 0.27525 | 0.11388
11h30 | 76.38 | 63.82 | 34.55 | 22.04 | 7.54 | 11h30 | 0.95475 | 0.79775 | 0.43188 | 0.2755 | 0.09425
12h30 | 87.76 | 75.48 | 41.51 | 29.87 | 13.66 | 12h30 | 1.097 | 0.9435 | 0.51887 | 0.37338 | 0.17075
13h30 | 99.68 | 87.99 | 48.09 | 37.28 | 19.51 | 13h30 | 1.246 | 1.0999 | 0.60113 | 0.466 | 0.24388
14h30 | 107.73 | 96.6 | 52.23 | 42.31 | 22.85 | 14h30 | 1.3466 | 1.2075 | 0.65287 | 0.52887 | 0.28563
15h30 | 104.9 | 94.07 | 49.86 | 40.22 | 20.71 | 15h30 | 1.3113 | 1.1759 | 0.62325 | 0.50275 | 0.25888
16h30 | 105.23 | 94.89 | 50.63 | 40.41 | 22.09 | 16h30 | 1.3154 | 1.1861 | 0.63287 | 0.50513 | 0.27613
17h30 | 103.51 | 93.95 | 51.73 | 40.72 | 23.9 | 17h30 | 1.2939 | 1.1744 | 0.64663 | 0.509 | 0.29875
18h30 | 102.75 | 93.53 | 52.84 | 42.2 | 26.54 | 18h30 | 1.2844 | 1.1691 | 0.6605 | 0.5275 | 0.33175
19h30 | 96.71 | 87.42 | 49.73 | 39.7 | 25.48 | 19h30 | 1.2089 | 1.0928 | 0.62162 | 0.49625 | 0.3185
20h30 | 73.16 | 63.82 | 36.74 | 25.86 | 14.35 | 20h30 | 0.9145 | 0.79775 | 0.45925 | 0.32325 | 0.17938
21h30 | 60.88 | 51.29 | 28.74 | 18.52 | 8.61 | 21h30 | 0.761 | 0.64112 | 0.35925 | 0.2315 | 0.10762
22h30 | 71.55 | 61.48 | 35.37 | 24.86 | 14.34 | 22h30 | 0.89438 | 0.7685 | 0.44212 | 0.31075 | 0.17925
23h30 | 79.04 | 68.29 | 39.71 | 29.21 | 18.37 | 23h30 | 0.988 | 0.85362 | 0.49638 | 0.36512 | 0.22962
00h30 | 60.87 | 52.66 | 33.07 | 22.22 | 10.28 | 00h30 | 0.76087 | 0.65825 | 0.41337 | 0.27775 | 0.1285
01h30 | 67.6 | 59.87 | 32.64 | 19.4 | 7.61 | 01h30 | 0.845 | 0.74838 | 0.408 | 0.2425 | 0.095125
02h30 | 68.15 | 57.95 | 32.64 | 19.4 | 7.63 | 02h30 | 0.85188 | 0.72437 | 0.408 | 0.2425 | 0.095375
03h30 | 66.09 | 55.68 | 30.76 | 18.15 | 7.29 | 03h30 | 0.82612 | 0.696 | 0.3845 | 0.22687 | 0.091125
04h30 | 64.25 | 55.45 | 30.76 | 18.15 | 7.27 | 04h30 | 0.80312 | 0.69312 | 0.3845 | 0.22687 | 0.090875
05h30 | 59.64 | 48.19 | 27.37 | 15.42 | 6.19 | 05h30 | 0.7455 | 0.60237 | 0.34213 | 0.19275 | 0.077375
06h30 | 59.64 | 48.19 | 27.37 | 15.42 | 6.19 | 06h30 | 0.7455 | 0.60237 | 0.34213 | 0.19275 | 0.077375
07h30 | 75.61 | 62.92 | 39.64 | 29.7 | 20.41 | 07h30 | 0.94512 | 0.7865 | 0.4955 | 0.37125 | 0.25512
08h30 | 75.61 | 62.92 | 39.64 | 29.7 | 20.41 | 08h30 | 0.94512 | 0.7865 | 0.4955 | 0.37125 | 0.25512
09h30 | 73.93 | 61.28 | 31.29 | 22.05 | 10.23 | 09h30 | 0.92412 | 0.766 | 0.39113 | 0.27563 | 0.12787
10h30 | 73.93 | 61.28 | 31.29 | 22.05 | 10.23 | 10h30 | 0.92412 | 0.766 | 0.39113 | 0.27563 | 0.12787
11h30 | 58.91 | 46.44 | 20.6 | 12.48 | 0.76 | 11h30 | 0.73638 | 0.5805 | 0.2575 | 0.156 | 0.0095
12h30 | 58.91 | 46.44 | 20.6 | 12.48 | 0.76 | 12h30 | 0.73638 | 0.5805 | 0.2575 | 0.156 | 0.0095
13h30 | 42.2 | 32.22 | 11.51 | 4.06 | 0 | 13h30 | 0.5275 | 0.40275 | 0.14388 | 0.05075 | 0
14h30 | 42.2 | 32.22 | 11.51 | 4.06 | 0 | 14h30 | 0.5275 | 0.40275 | 0.14388 | 0.05075 | 0
15h30 | 38.33 | 27.79 | 9.39 | 1.35 | 0 | 15h30 | 0.47913 | 0.34737 | 0.11737 | 0.016875 | 0
16h30 | 38.33 | 27.79 | 9.39 | 1.35 | 0 | 16h30 | 0.47913 | 0.34737 | 0.11737 | 0.016875 | 0
17h30 | 20.88 | 13.14 | 3.74 | 0 | 0 | 17h30 | 0.261 | 0.16425 | 0.04675 | 0 | 0
18h30 | 20.88 | 13.14 | 3.74 | 0 | 0 | 18h30 | 0.261 | 0.16425 | 0.04675 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 1.85 | 0 | 0 | 0 | 0 | 20h30 | 0.023125 | 0 | 0 | 0 | 0
21h30 | 2.94 | 0 | 0 | 0 | 0 | 21h30 | 0.03675 | 0 | 0 | 0 | 0
22h30 | 4.02 | 0 | 0 | 0 | 0 | 22h30 | 0.05025 | 0 | 0 | 0 | 0
23h30 | 11.78 | 0 | 0 | 0 | 0 | 23h30 | 0.14725 | 0 | 0 | 0 | 0
00h30 | 8.84 | 0 | 0 | 0 | 0 | 00h30 | 0.1105 | 0 | 0 | 0 | 0
01h30 | 20.91 | 12.41 | 2.04 | 0 | 0 | 01h30 | 0.26138 | 0.15513 | 0.0255 | 0 | 0
02h30 | 28 | 16.99 | 6.94 | 0 | 0 | 02h30 | 0.35 | 0.21238 | 0.08675 | 0 | 0
03h30 | 31.2 | 20.51 | 8.76 | 0 | 0 | 03h30 | 0.39 | 0.25638 | 0.1095 | 0 | 0
04h30 | 33.41 | 22.55 | 10.52 | 0 | 0 | 04h30 | 0.41763 | 0.28187 | 0.1315 | 0 | 0
05h30 | 34.12 | 22.91 | 11.04 | 0 | 0 | 05h30 | 0.4265 | 0.28637 | 0.138 | 0 | 0
06h30 | 34.95 | 23.33 | 11.5 | 0 | 0 | 06h30 | 0.43688 | 0.29163 | 0.14375 | 0 | 0
07h30 | 35.26 | 22.9 | 16.78 | 4.24 | 0 | 07h30 | 0.44075 | 0.28625 | 0.20975 | 0.053 | 0
08h30 | 30.03 | 15.87 | 9.65 | 4.24 | 0 | 08h30 | 0.37538 | 0.19837 | 0.12062 | 0.053 | 0
09h30 | 53.67 | 37.48 | 20.03 | 10.5 | 0 | 09h30 | 0.67087 | 0.4685 | 0.25038 | 0.13125 | 0
10h30 | 57.53 | 43.25 | 22.75 | 14.16 | 0.29 | 10h30 | 0.71913 | 0.54063 | 0.28437 | 0.177 | 0.003625
11h30 | 51.62 | 38.7 | 19.34 | 9.21 | 0.29 | 11h30 | 0.64525 | 0.48375 | 0.24175 | 0.11513 | 0.003625
12h30 | 46.55 | 34.47 | 16.62 | 6.61 | 0 | 12h30 | 0.58188 | 0.43088 | 0.20775 | 0.082625 | 0
13h30 | 38.73 | 27.37 | 11.09 | 2.28 | 0 | 13h30 | 0.48413 | 0.34213 | 0.13862 | 0.0285 | 0
14h30 | 35.05 | 25.83 | 11.09 | 1.23 | 0 | 14h30 | 0.43812 | 0.32288 | 0.13862 | 0.015375 | 0
15h30 | 29.81 | 19.79 | 5.95 | 0 | 0 | 15h30 | 0.37262 | 0.24738 | 0.074375 | 0 | 0
16h30 | 35.38 | 25.75 | 10.76 | 1.84 | 0 | 16h30 | 0.44225 | 0.32188 | 0.1345 | 0.023 | 0
17h30 | 44.53 | 35.1 | 17.18 | 8.23 | 0 | 17h30 | 0.55663 | 0.43875 | 0.21475 | 0.10287 | 0
18h30 | 45.75 | 36.53 | 18.63 | 9.72 | 0 | 18h30 | 0.57188 | 0.45663 | 0.23287 | 0.1215 | 0
19h30 | 42.48 | 33.49 | 17 | 8.46 | 0 | 19h30 | 0.531 | 0.41863 | 0.2125 | 0.10575 | 0
20h30 | 37.51 | 28.72 | 14.23 | 5.85 | 0 | 20h30 | 0.46887 | 0.359 | 0.17788 | 0.073125 | 0
21h30 | 39.14 | 30.4 | 15.4 | 6.91 | 0 | 21h30 | 0.48925 | 0.38 | 0.1925 | 0.086375 | 0
22h30 | 47.42 | 38.51 | 20.56 | 11.79 | 0 | 22h30 | 0.59275 | 0.48137 | 0.257 | 0.14738 | 0
23h30 | 54.09 | 44.94 | 24.67 | 15.78 | 1.99 | 23h30 | 0.67612 | 0.56175 | 0.30838 | 0.19725 | 0.024875
00h30 | 44.01 | 34.2 | 16.03 | 10.18 | 1.99 | 00h30 | 0.55012 | 0.4275 | 0.20037 | 0.12725 | 0.024875
01h30 | 38.02 | 30.87 | 14.22 | 3.07 | 0 | 01h30 | 0.47525 | 0.38588 | 0.17775 | 0.038375 | 0
02h30 | 40.03 | 31.58 | 14.84 | 4.14 | 0 | 02h30 | 0.50038 | 0.39475 | 0.1855 | 0.05175 | 0
03h30 | 43.14 | 35.11 | 17.24 | 6.48 | 0 | 03h30 | 0.53925 | 0.43888 | 0.2155 | 0.081 | 0
04h30 | 41.14 | 34.4 | 16.62 | 5.56 | 0 | 04h30 | 0.51425 | 0.43 | 0.20775 | 0.0695 | 0
05h30 | 36.75 | 28.94 | 13.88 | 4.22 | 0 | 05h30 | 0.45937 | 0.36175 | 0.1735 | 0.05275 | 0
06h30 | 36.75 | 28.94 | 13.88 | 4.06 | 0 | 06h30 | 0.45937 | 0.36175 | 0.1735 | 0.05075 | 0
07h30 | 53.16 | 44.63 | 28.67 | 20.78 | 6.1 | 07h30 | 0.6645 | 0.55788 | 0.35837 | 0.25975 | 0.07625
08h30 | 53.51 | 44.63 | 28.67 | 20.78 | 6.1 | 08h30 | 0.66887 | 0.55788 | 0.35837 | 0.25975 | 0.07625
09h30 | 49.1 | 37.96 | 19.58 | 13.34 | 0 | 09h30 | 0.61375 | 0.4745 | 0.24475 | 0.16675 | 0
10h30 | 48.75 | 37.96 | 19.58 | 13.34 | 0 | 10h30 | 0.60938 | 0.4745 | 0.24475 | 0.16675 | 0
11h30 | 32.19 | 23.04 | 8.07 | 2.29 | 0 | 11h30 | 0.40237 | 0.288 | 0.10088 | 0.028625 | 0
12h30 | 32.19 | 23.04 | 8.07 | 2.29 | 0 | 12h30 | 0.40237 | 0.288 | 0.10088 | 0.028625 | 0
13h30 | 19.29 | 13.29 | 0 | 0 | 0 | 13h30 | 0.24113 | 0.16612 | 0 | 0 | 0
14h30 | 22.82 | 16.26 | 1.53 | 0 | 0 | 14h30 | 0.28525 | 0.20325 | 0.019125 | 0 | 0
15h30 | 26 | 17.72 | 3.19 | 0 | 0 | 15h30 | 0.325 | 0.2215 | 0.039875 | 0 | 0
16h30 | 29.01 | 22.35 | 7.12 | 0.49 | 0 | 16h30 | 0.36262 | 0.27937 | 0.089 | 0.006125 | 0
17h30 | 34.1 | 28.65 | 12.03 | 4.6 | 0 | 17h30 | 0.42625 | 0.35813 | 0.15038 | 0.0575 | 0
18h30 | 35.58 | 30.82 | 14.35 | 6.41 | 0 | 18h30 | 0.44475 | 0.38525 | 0.17938 | 0.080125 | 0
19h30 | 37.68 | 33.25 | 16.5 | 8.26 | 0 | 19h30 | 0.471 | 0.41563 | 0.20625 | 0.10325 | 0
20h30 | 34.97 | 30.64 | 15.46 | 6.84 | 0 | 20h30 | 0.43712 | 0.383 | 0.19325 | 0.0855 | 0
21h30 | 28.83 | 24.37 | 12.12 | 3.22 | 0 | 21h30 | 0.36038 | 0.30462 | 0.1515 | 0.04025 | 0
22h30 | 31.8 | 27.03 | 14.02 | 4.97 | 0 | 22h30 | 0.3975 | 0.33787 | 0.17525 | 0.062125 | 0
23h30 | 37.1 | 31.85 | 17.14 | 8.01 | 0 | 23h30 | 0.46375 | 0.39813 | 0.21425 | 0.10013 | 0
00h30 | 28.81 | 22.05 | 8.5 | 5.38 | 0 | 00h30 | 0.36012 | 0.27563 | 0.10625 | 0.06725 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 18.54 | 10.71 | 2.53 | 0 | 0 | 03h30 | 0.23175 | 0.13387 | 0.031625 | 0 | 0
04h30 | 42.84 | 36.94 | 19.49 | 6.39 | 0 | 04h30 | 0.5355 | 0.46175 | 0.24363 | 0.079875 | 0
05h30 | 40.03 | 31.66 | 16.95 | 6.39 | 0 | 05h30 | 0.50038 | 0.39575 | 0.21188 | 0.079875 | 0
06h30 | 35.9 | 27.65 | 13.16 | 2.05 | 0 | 06h30 | 0.44875 | 0.34563 | 0.1645 | 0.025625 | 0
07h30 | 50.82 | 43.26 | 27.81 | 18.47 | 3.42 | 07h30 | 0.63525 | 0.54075 | 0.34763 | 0.23087 | 0.04275
08h30 | 43.23 | 33.81 | 17.88 | 16.42 | 3.42 | 08h30 | 0.54038 | 0.42262 | 0.2235 | 0.20525 | 0.04275
09h30 | 45.86 | 34.79 | 17.41 | 10.62 | 0 | 09h30 | 0.57325 | 0.43488 | 0.21763 | 0.13275 | 0
10h30 | 44.21 | 34.66 | 16.62 | 10.62 | 0 | 10h30 | 0.55263 | 0.43325 | 0.20775 | 0.13275 | 0
11h30 | 32.58 | 23.72 | 9.34 | 1.64 | 0 | 11h30 | 0.40725 | 0.2965 | 0.11675 | 0.0205 | 0
12h30 | 23.97 | 15.33 | 6.91 | 1.64 | 0 | 12h30 | 0.29962 | 0.19162 | 0.086375 | 0.0205 | 0
13h30 | 17.1 | 8.68 | 0 | 0 | 0 | 13h30 | 0.21375 | 0.1085 | 0 | 0 | 0
14h30 | 14.79 | 4.43 | 0 | 0 | 0 | 14h30 | 0.18488 | 0.055375 | 0 | 0 | 0
15h30 | 9.22 | 1.63 | 0 | 0 | 0 | 15h30 | 0.11525 | 0.020375 | 0 | 0 | 0
16h30 | 9.27 | 2.09 | 0 | 0 | 0 | 16h30 | 0.11588 | 0.026125 | 0 | 0 | 0
17h30 | 11.18 | 4.57 | 0 | 0 | 0 | 17h30 | 0.13975 | 0.057125 | 0 | 0 | 0
18h30 | 15.64 | 9.27 | 0.59 | 0 | 0 | 18h30 | 0.1955 | 0.11588 | 0.007375 | 0 | 0
19h30 | 20.45 | 14.3 | 4.39 | 0 | 0 | 19h30 | 0.25562 | 0.17875 | 0.054875 | 0 | 0
20h30 | 23.48 | 17.42 | 6.44 | 0 | 0 | 20h30 | 0.2935 | 0.21775 | 0.0805 | 0 | 0
21h30 | 22.23 | 16.15 | 5.9 | 0 | 0 | 21h30 | 0.27787 | 0.20187 | 0.07375 | 0 | 0
22h30 | 23.15 | 16.99 | 6.52 | 0 | 0 | 22h30 | 0.28937 | 0.21238 | 0.0815 | 0 | 0
23h30 | 23.52 | 17.21 | 6.77 | 0 | 0 | 23h30 | 0.294 | 0.21513 | 0.084625 | 0 | 0
00h30 | 15.08 | 8.1 | 3.51 | 0 | 0 | 00h30 | 0.1885 | 0.10125 | 0.043875 | 0 | 0
01h30 | 5.32 | 0 | 0 | 0 | 0 | 01h30 | 0.0665 | 0 | 0 | 0 | 0
02h30 | 8.36 | 0.16 | 0 | 0 | 0 | 02h30 | 0.1045 | 0.002 | 0 | 0 | 0
03h30 | 14.12 | 5.53 | 0 | 0 | 0 | 03h30 | 0.1765 | 0.069125 | 0 | 0 | 0
04h30 | 19.01 | 10.9 | 0.98 | 0 | 0 | 04h30 | 0.23763 | 0.13625 | 0.01225 | 0 | 0
05h30 | 16.92 | 9.28 | 0.98 | 0 | 0 | 05h30 | 0.2115 | 0.116 | 0.01225 | 0 | 0
06h30 | 15.57 | 8.24 | 0 | 0 | 0 | 06h30 | 0.19462 | 0.103 | 0 | 0 | 0
07h30 | 33.04 | 27.52 | 16.89 | 7.29 | 0 | 07h30 | 0.413 | 0.344 | 0.21113 | 0.091125 | 0
08h30 | 29.89 | 23.05 | 16.89 | 7.29 | 0 | 08h30 | 0.37362 | 0.28813 | 0.21113 | 0.091125 | 0
09h30 | 32.16 | 23.36 | 8.73 | 1.95 | 0 | 09h30 | 0.402 | 0.292 | 0.10912 | 0.024375 | 0
10h30 | 33.36 | 26.04 | 10.84 | 2.6 | 0 | 10h30 | 0.417 | 0.3255 | 0.1355 | 0.0325 | 0
11h30 | 38.82 | 31.94 | 13.97 | 4.88 | 0 | 11h30 | 0.48525 | 0.39925 | 0.17463 | 0.061 | 0
12h30 | 43.54 | 36.78 | 16.35 | 7.61 | 0 | 12h30 | 0.54425 | 0.45975 | 0.20438 | 0.095125 | 0
13h30 | 36.54 | 29.89 | 11.95 | 3.38 | 0 | 13h30 | 0.45675 | 0.37362 | 0.14938 | 0.04225 | 0
14h30 | 27.19 | 22.36 | 7.46 | 0 | 0 | 14h30 | 0.33987 | 0.2795 | 0.09325 | 0 | 0
15h30 | 22.46 | 15.88 | 2.38 | 0 | 0 | 15h30 | 0.28075 | 0.1985 | 0.02975 | 0 | 0
16h30 | 25.04 | 19.07 | 5.27 | 0 | 0 | 16h30 | 0.313 | 0.23838 | 0.065875 | 0 | 0
17h30 | 33.59 | 28.31 | 12.05 | 3.25 | 0 | 17h30 | 0.41987 | 0.35387 | 0.15063 | 0.040625 | 0
18h30 | 40.42 | 35.21 | 17.01 | 8.01 | 0 | 18h30 | 0.50525 | 0.44012 | 0.21263 | 0.10013 | 0
19h30 | 44.31 | 39.14 | 19.87 | 10.56 | 0 | 19h30 | 0.55388 | 0.48925 | 0.24838 | 0.132 | 0
20h30 | 46.41 | 41.18 | 21.37 | 12.04 | 0 | 20h30 | 0.58013 | 0.51475 | 0.26713 | 0.1505 | 0
21h30 | 46.94 | 41.53 | 21.75 | 12.54 | 0 | 21h30 | 0.58675 | 0.51912 | 0.27187 | 0.15675 | 0
22h30 | 44.42 | 38.72 | 20.19 | 11.09 | 0 | 22h30 | 0.55525 | 0.484 | 0.25238 | 0.13862 | 0
23h30 | 39.02 | 32.97 | 16.71 | 7.99 | 0 | 23h30 | 0.48775 | 0.41213 | 0.20888 | 0.099875 | 0
00h30 | 30.02 | 23.64 | 8.93 | 3.19 | 0 | 00h30 | 0.37525 | 0.2955 | 0.11163 | 0.039875 | 0
01h30 | 20.3 | 14.23 | 2.38 | 0 | 0 | 01h30 | 0.25375 | 0.17788 | 0.02975 | 0 | 0
02h30 | 20.3 | 14.23 | 2.38 | 0 | 0 | 02h30 | 0.25375 | 0.17788 | 0.02975 | 0 | 0
03h30 | 19.48 | 11.11 | 1.28 | 0 | 0 | 03h30 | 0.2435 | 0.13887 | 0.016 | 0 | 0
04h30 | 21.55 | 13.66 | 3.37 | 0 | 0 | 04h30 | 0.26937 | 0.17075 | 0.042125 | 0 | 0
05h30 | 22.92 | 15.25 | 4.78 | 0 | 0 | 05h30 | 0.2865 | 0.19062 | 0.05975 | 0 | 0
06h30 | 21.54 | 14.03 | 4.32 | 0 | 0 | 06h30 | 0.26925 | 0.17538 | 0.054 | 0 | 0
07h30 | 35.7 | 29.23 | 18.98 | 9.59 | 0 | 07h30 | 0.44625 | 0.36538 | 0.23725 | 0.11987 | 0
08h30 | 35 | 27.9 | 17.36 | 9.59 | 0 | 08h30 | 0.4375 | 0.34875 | 0.217 | 0.11987 | 0
09h30 | 18.31 | 7.94 | 0.76 | 0 | 0 | 09h30 | 0.22887 | 0.09925 | 0.0095 | 0 | 0
10h30 | 18.31 | 7.94 | 0.76 | 0 | 0 | 10h30 | 0.22887 | 0.09925 | 0.0095 | 0 | 0
11h30 | 28.49 | 20.47 | 7.95 | 0 | 0 | 11h30 | 0.35613 | 0.25588 | 0.099375 | 0 | 0
12h30 | 28.49 | 20.47 | 7.95 | 0 | 0 | 12h30 | 0.35613 | 0.25588 | 0.099375 | 0 | 0
13h30 | 17.37 | 10.49 | 0.4 | 0 | 0 | 13h30 | 0.21713 | 0.13112 | 0.005 | 0 | 0
14h30 | 20.11 | 13.45 | 2.42 | 0 | 0 | 14h30 | 0.25138 | 0.16812 | 0.03025 | 0 | 0
15h30 | 24.69 | 17.81 | 5.39 | 0 | 0 | 15h30 | 0.30862 | 0.22262 | 0.067375 | 0 | 0
16h30 | 21.94 | 14.85 | 3.37 | 0 | 0 | 16h30 | 0.27425 | 0.18563 | 0.042125 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 0 | 0 | 0 | 0 | 0 | 18h30 | 0 | 0 | 0 | 0 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 0 | 0 | 0 | 0 | 0 | 20h30 | 0 | 0 | 0 | 0 | 0
21h30 | 0 | 0 | 0 | 0 | 0 | 21h30 | 0 | 0 | 0 | 0 | 0
22h30 | 0 | 0 | 0 | 0 | 0 | 22h30 | 0 | 0 | 0 | 0 | 0
23h30 | 0 | 0 | 0 | 0 | 0 | 23h30 | 0 | 0 | 0 | 0 | 0
00h30 | 0 | 0 | 0 | 0 | 0 | 00h30 | 0 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0 | 0 | 0 | 0 | 0 | 02h30 | 0 | 0 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 0 | 0 | 0 | 0 | 0 | 04h30 | 0 | 0 | 0 | 0 | 0
05h30 | 0 | 0 | 0 | 0 | 0 | 05h30 | 0 | 0 | 0 | 0 | 0
06h30 | 0 | 0 | 0 | 0 | 0 | 06h30 | 0 | 0 | 0 | 0 | 0
07h30 | 10.24 | 0 | 0 | 0 | 0 | 07h30 | 0.128 | 0 | 0 | 0 | 0
08h30 | 10.24 | 0 | 0 | 0 | 0 | 08h30 | 0.128 | 0 | 0 | 0 | 0
09h30 | 0.19 | 0 | 0 | 0 | 0 | 09h30 | 0.002375 | 0 | 0 | 0 | 0
10h30 | 0.19 | 0 | 0 | 0 | 0 | 10h30 | 0.002375 | 0 | 0 | 0 | 0
11h30 | 0 | 0 | 0 | 0 | 0 | 11h30 | 0 | 0 | 0 | 0 | 0
12h30 | 0 | 0 | 0 | 0 | 0 | 12h30 | 0 | 0 | 0 | 0 | 0
13h30 | 0 | 0 | 0 | 0 | 0 | 13h30 | 0 | 0 | 0 | 0 | 0
14h30 | 0 | 0 | 0 | 0 | 0 | 14h30 | 0 | 0 | 0 | 0 | 0
15h30 | 0 | 0 | 0 | 0 | 0 | 15h30 | 0 | 0 | 0 | 0 | 0
16h30 | 0 | 0 | 0 | 0 | 0 | 16h30 | 0 | 0 | 0 | 0 | 0
17h30 | 0 | 0 | 0 | 0 | 0 | 17h30 | 0 | 0 | 0 | 0 | 0
18h30 | 12.92 | 0 | 0 | 0 | 0 | 18h30 | 0.1615 | 0 | 0 | 0 | 0
19h30 | 26.42 | 16.57 | 4.96 | 0 | 0 | 19h30 | 0.33025 | 0.20713 | 0.062 | 0 | 0
20h30 | 23.42 | 16.57 | 4.96 | 0 | 0 | 20h30 | 0.29275 | 0.20713 | 0.062 | 0 | 0
21h30 | 21.69 | 11.98 | 3.08 | 0 | 0 | 21h30 | 0.27113 | 0.14975 | 0.0385 | 0 | 0
22h30 | 18.45 | 11.98 | 3.08 | 0 | 0 | 22h30 | 0.23062 | 0.14975 | 0.0385 | 0 | 0
23h30 | 9.22 | 0 | 0 | 0 | 0 | 23h30 | 0.11525 | 0 | 0 | 0 | 0
00h30 | 2.54 | 0 | 0 | 0 | 0 | 00h30 | 0.03175 | 0 | 0 | 0 | 0
01h30 | 15.1 | 4.37 | 0 | 0 | 0 | 01h30 | 0.18875 | 0.054625 | 0 | 0 | 0
02h30 | 24.83 | 14.2 | 3.74 | 0 | 0 | 02h30 | 0.31038 | 0.1775 | 0.04675 | 0 | 0
03h30 | 23.28 | 11.7 | 3.74 | 0 | 0 | 03h30 | 0.291 | 0.14625 | 0.04675 | 0 | 0
04h30 | 16.72 | 5.78 | 0 | 0 | 0 | 04h30 | 0.209 | 0.07225 | 0 | 0 | 0
05h30 | 9.81 | 3.91 | 0 | 0 | 0 | 05h30 | 0.12262 | 0.048875 | 0 | 0 | 0
06h30 | 7.28 | 0 | 0 | 0 | 0 | 06h30 | 0.091 | 0 | 0 | 0 | 0
07h30 | 18.88 | 6.51 | 4.24 | 0 | 0 | 07h30 | 0.236 | 0.081375 | 0.053 | 0 | 0
08h30 | 18.23 | 6.51 | 4.24 | 0 | 0 | 08h30 | 0.22787 | 0.081375 | 0.053 | 0 | 0
09h30 | 12.65 | 0 | 0 | 0 | 0 | 09h30 | 0.15812 | 0 | 0 | 0 | 0
10h30 | 12.65 | 0 | 0 | 0 | 0 | 10h30 | 0.15812 | 0 | 0 | 0 | 0
11h30 | 12.52 | 0 | 0 | 0 | 0 | 11h30 | 0.1565 | 0 | 0 | 0 | 0
12h30 | 18.41 | 6.42 | 0 | 0 | 0 | 12h30 | 0.23012 | 0.08025 | 0 | 0 | 0
13h30 | 16.81 | 6.42 | 0 | 0 | 0 | 13h30 | 0.21013 | 0.08025 | 0 | 0 | 0
14h30 | 17.86 | 6.23 | 0 | 0 | 0 | 14h30 | 0.22325 | 0.077875 | 0 | 0 | 0
15h30 | 19.11 | 8.02 | 0 | 0 | 0 | 15h30 | 0.23888 | 0.10025 | 0 | 0 | 0
16h30 | 18.14 | 7.01 | 0.31 | 0 | 0 | 16h30 | 0.22675 | 0.087625 | 0.003875 | 0 | 0
17h30 | 18.59 | 7.37 | 1.19 | 0 | 0 | 17h30 | 0.23237 | 0.092125 | 0.014875 | 0 | 0
18h30 | 13.91 | 2.55 | 0.88 | 0 | 0 | 18h30 | 0.17388 | 0.031875 | 0.011 | 0 | 0
19h30 | 7.71 | 0.39 | 0 | 0 | 0 | 19h30 | 0.096375 | 0.004875 | 0 | 0 | 0
20h30 | 6.42 | 0 | 0 | 0 | 0 | 20h30 | 0.08025 | 0 | 0 | 0 | 0
21h30 | 5.75 | 0 | 0 | 0 | 0 | 21h30 | 0.071875 | 0 | 0 | 0 | 0
22h30 | 8.66 | 0 | 0 | 0 | 0 | 22h30 | 0.10825 | 0 | 0 | 0 | 0
23h30 | 18.26 | 3.61 | 0 | 0 | 0 | 23h30 | 0.22825 | 0.045125 | 0 | 0 | 0
00h30 | 16.41 | 7.1 | 0 | 0 | 0 | 00h30 | 0.20513 | 0.08875 | 0 | 0 | 0
01h30 | 32.87 | 24.23 | 9.58 | 0 | 0 | 01h30 | 0.41087 | 0.30288 | 0.11975 | 0 | 0
02h30 | 41.02 | 29.67 | 13.85 | 0 | 0 | 02h30 | 0.51275 | 0.37088 | 0.17313 | 0 | 0
03h30 | 47.64 | 36.48 | 18.42 | 0 | 0 | 03h30 | 0.5955 | 0.456 | 0.23025 | 0 | 0
04h30 | 48.97 | 37.73 | 19.76 | 0 | 0 | 04h30 | 0.61213 | 0.47163 | 0.247 | 0 | 0
05h30 | 51.76 | 40.3 | 21.81 | 0 | 0 | 05h30 | 0.647 | 0.50375 | 0.27263 | 0 | 0
06h30 | 59.25 | 47.52 | 26.76 | 5.22 | 0 | 06h30 | 0.74062 | 0.594 | 0.3345 | 0.06525 | 0
07h30 | 77.23 | 64.51 | 41.89 | 22.63 | 4.21 | 07h30 | 0.96537 | 0.80637 | 0.52363 | 0.28287 | 0.052625
08h30 | 62.85 | 49.7 | 31.33 | 17.42 | 4.21 | 08h30 | 0.78563 | 0.62125 | 0.39163 | 0.21775 | 0.052625
09h30 | 66.57 | 54.54 | 26.83 | 9.72 | 0 | 09h30 | 0.83213 | 0.68175 | 0.33537 | 0.1215 | 0
10h30 | 78.32 | 66.84 | 33.88 | 15.48 | 0 | 10h30 | 0.979 | 0.8355 | 0.4235 | 0.1935 | 0
11h30 | 80.63 | 69.34 | 35.09 | 18.28 | 0 | 11h30 | 1.0079 | 0.86675 | 0.43862 | 0.2285 | 0
12h30 | 84.56 | 73.93 | 38.46 | 22.6 | 0.22 | 12h30 | 1.057 | 0.92412 | 0.48075 | 0.2825 | 0.00275
13h30 | 80.03 | 69.98 | 35.81 | 20.58 | 0.22 | 13h30 | 1.0004 | 0.87475 | 0.44762 | 0.25725 | 0.00275
14h30 | 66.7 | 56.76 | 26.96 | 12.57 | 0 | 14h30 | 0.83375 | 0.7095 | 0.337 | 0.15712 | 0
15h30 | 54.97 | 45.37 | 20.25 | 5.92 | 0 | 15h30 | 0.68712 | 0.56712 | 0.25312 | 0.074 | 0
16h30 | 53.9 | 45.73 | 22.19 | 7.06 | 0 | 16h30 | 0.67375 | 0.57163 | 0.27737 | 0.08825 | 0
17h30 | 58.13 | 51.01 | 27.05 | 11.92 | 0 | 17h30 | 0.72662 | 0.63762 | 0.33813 | 0.149 | 0
18h30 | 53.19 | 44.38 | 23.54 | 8.7 | 0 | 18h30 | 0.66487 | 0.55475 | 0.29425 | 0.10875 | 0
19h30 | 0 | 0 | 0 | 0 | 0 | 19h30 | 0 | 0 | 0 | 0 | 0
20h30 | 2.98 | 0 | 0 | 0 | 0 | 20h30 | 0.03725 | 0 | 0 | 0 | 0
21h30 | 3.59 | 0 | 0 | 0 | 0 | 21h30 | 0.044875 | 0 | 0 | 0 | 0
22h30 | 4.87 | 0 | 0 | 0 | 0 | 22h30 | 0.060875 | 0 | 0 | 0 | 0
23h30 | 6.91 | 0 | 0 | 0 | 0 | 23h30 | 0.086375 | 0 | 0 | 0 | 0
00h30 | 2.65 | 0 | 0 | 0 | 0 | 00h30 | 0.033125 | 0 | 0 | 0 | 0
01h30 | 19.33 | 8.52 | 0.52 | 0 | 0 | 01h30 | 0.24163 | 0.1065 | 0.0065 | 0 | 0
02h30 | 45.72 | 37.33 | 20.24 | 0 | 0 | 02h30 | 0.5715 | 0.46663 | 0.253 | 0 | 0
03h30 | 26.58 | 28.81 | 19.72 | 0 | 0 | 03h30 | 0.33225 | 0.36012 | 0.2465 | 0 | 0
04h30 | 5.07 | 0 | 0 | 0 | 0 | 04h30 | 0.063375 | 0 | 0 | 0 | 0
05h30 | 6.26 | 0 | 0 | 0 | 0 | 05h30 | 0.07825 | 0 | 0 | 0 | 0
06h30 | 7.35 | 0 | 0 | 0 | 0 | 06h30 | 0.091875 | 0 | 0 | 0 | 0
07h30 | 21.93 | 6.12 | 6.12 | 0 | 0 | 07h30 | 0.27413 | 0.0765 | 0.0765 | 0 | 0
08h30 | 15.96 | 6.12 | 6.12 | 0 | 0 | 08h30 | 0.1995 | 0.0765 | 0.0765 | 0 | 0
09h30 | 14.27 | 0 | 0 | 0 | 0 | 09h30 | 0.17838 | 0 | 0 | 0 | 0
10h30 | 14.27 | 0 | 0 | 0 | 0 | 10h30 | 0.17838 | 0 | 0 | 0 | 0
11h30 | 8.65 | 0 | 0 | 0 | 0 | 11h30 | 0.10812 | 0 | 0 | 0 | 0
12h30 | 8.65 | 0 | 0 | 0 | 0 | 12h30 | 0.10812 | 0 | 0 | 0 | 0
13h30 | 7.51 | 0 | 0 | 0 | 0 | 13h30 | 0.093875 | 0 | 0 | 0 | 0
14h30 | 7.51 | 0 | 0 | 0 | 0 | 14h30 | 0.093875 | 0 | 0 | 0 | 0
15h30 | 6.86 | 0 | 0 | 0 | 0 | 15h30 | 0.08575 | 0 | 0 | 0 | 0
16h30 | 7.06 | 0 | 0 | 0 | 0 | 16h30 | 0.08825 | 0 | 0 | 0 | 0
17h30 | 8.14 | 0 | 0 | 0 | 0 | 17h30 | 0.10175 | 0 | 0 | 0 | 0
18h30 | 9.16 | 0 | 0 | 0 | 0 | 18h30 | 0.1145 | 0 | 0 | 0 | 0
19h30 | 42.65 | 27.9 | 14.49 | 0 | 0 | 19h30 | 0.53312 | 0.34875 | 0.18113 | 0 | 0
20h30 | 68.07 | 54.9 | 31.23 | 11.44 | 0 | 20h30 | 0.85088 | 0.68625 | 0.39038 | 0.143 | 0
21h30 | 68.48 | 55.13 | 31.57 | 11.79 | 0 | 21h30 | 0.856 | 0.68912 | 0.39463 | 0.14738 | 0
22h30 | 78.11 | 64.84 | 37.84 | 17.88 | 0 | 22h30 | 0.97637 | 0.8105 | 0.473 | 0.2235 | 0
23h30 | 78.69 | 65.43 | 38.45 | 19.61 | 1.72 | 23h30 | 0.98362 | 0.81788 | 0.48063 | 0.24513 | 0.0215
00h30 | 61.29 | 50.2 | 24.42 | 4.58 | 1.72 | 00h30 | 0.76612 | 0.6275 | 0.30525 | 0.05725 | 0.0215
01h30 | 68.58 | 59.38 | 33.61 | 11.57 | 0 | 01h30 | 0.85725 | 0.74225 | 0.42013 | 0.14463 | 0
02h30 | 71.04 | 61.42 | 35.17 | 13.1 | 0 | 02h30 | 0.888 | 0.76775 | 0.43962 | 0.16375 | 0
03h30 | 72.19 | 62.23 | 36.26 | 15.54 | 0 | 03h30 | 0.90238 | 0.77787 | 0.45325 | 0.19425 | 0
04h30 | 75.22 | 64.86 | 38.23 | 18.53 | 1.59 | 04h30 | 0.94025 | 0.81075 | 0.47787 | 0.23162 | 0.019875
05h30 | 76.51 | 65.7 | 39.07 | 20.15 | 3.65 | 05h30 | 0.95637 | 0.82125 | 0.48838 | 0.25188 | 0.045625
06h30 | 77.98 | 66.67 | 39.94 | 21.6 | 5.77 | 06h30 | 0.97475 | 0.83337 | 0.49925 | 0.27 | 0.072125
07h30 | 95.36 | 82.58 | 53.42 | 37.42 | 22.31 | 07h30 | 1.192 | 1.0322 | 0.66775 | 0.46775 | 0.27887
08h30 | 80.15 | 67.19 | 40.04 | 28.97 | 18.6 | 08h30 | 1.0019 | 0.83988 | 0.5005 | 0.36212 | 0.2325
09h30 | 71.48 | 60.15 | 30.83 | 16.27 | 0.32 | 09h30 | 0.8935 | 0.75187 | 0.38538 | 0.20338 | 0.004
10h30 | 68.56 | 57.86 | 30.83 | 16.27 | 0.32 | 10h30 | 0.857 | 0.72325 | 0.38538 | 0.20338 | 0.004
11h30 | 69.06 | 58.6 | 30.06 | 14.96 | 0 | 11h30 | 0.86325 | 0.7325 | 0.37575 | 0.187 | 0
12h30 | 68.59 | 58.67 | 30.54 | 16 | 0.25 | 12h30 | 0.85737 | 0.73337 | 0.38175 | 0.2 | 0.003125
13h30 | 60.85 | 51.58 | 26.22 | 11.92 | 0.25 | 13h30 | 0.76062 | 0.64475 | 0.32775 | 0.149 | 0.003125
14h30 | 57.25 | 48.6 | 25.74 | 10.88 | 0 | 14h30 | 0.71562 | 0.6075 | 0.32175 | 0.136 | 0
15h30 | 57.58 | 49.51 | 25.93 | 11.49 | 0 | 15h30 | 0.71975 | 0.61887 | 0.32412 | 0.14363 | 0
16h30 | 58.17 | 50.54 | 27.43 | 13.04 | 0.55 | 16h30 | 0.72713 | 0.63175 | 0.34287 | 0.163 | 0.006875
17h30 | 63.47 | 55.89 | 31.51 | 17.4 | 5 | 17h30 | 0.79338 | 0.69863 | 0.39387 | 0.2175 | 0.0625
18h30 | 65.57 | 57.68 | 33.17 | 19.54 | 7.5 | 18h30 | 0.81963 | 0.721 | 0.41463 | 0.24425 | 0.09375
19h30 | 56.84 | 48.48 | 27.85 | 14.8 | 4.12 | 19h30 | 0.7105 | 0.606 | 0.34813 | 0.185 | 0.0515
20h30 | 50.51 | 39.13 | 24.68 | 11.1 | 1.07 | 20h30 | 0.63138 | 0.48912 | 0.3085 | 0.13875 | 0.013375
21h30 | 2.14 | 0 | 0 | 0 | 0 | 21h30 | 0.02675 | 0 | 0 | 0 | 0
22h30 | 8.86 | 0 | 0 | 0 | 0 | 22h30 | 0.11075 | 0 | 0 | 0 | 0
23h30 | 8.17 | 0 | 0 | 0 | 0 | 23h30 | 0.10212 | 0 | 0 | 0 | 0
00h30 | 1.45 | 0 | 0 | 0 | 0 | 00h30 | 0.018125 | 0 | 0 | 0 | 0
01h30 | 24.54 | 14.32 | 4.62 | 0 | 0 | 01h30 | 0.30675 | 0.179 | 0.05775 | 0 | 0
02h30 | 45.63 | 37.1 | 20.6 | 3.3 | 0 | 02h30 | 0.57037 | 0.46375 | 0.2575 | 0.04125 | 0
03h30 | 58.99 | 49.08 | 26.97 | 10.89 | 0 | 03h30 | 0.73738 | 0.6135 | 0.33713 | 0.13612 | 0
04h30 | 66.63 | 56.18 | 31.81 | 15.35 | 1.67 | 04h30 | 0.83288 | 0.70225 | 0.39763 | 0.19187 | 0.020875
05h30 | 71.84 | 60.87 | 35.18 | 19.46 | 5.57 | 05h30 | 0.898 | 0.76087 | 0.43975 | 0.24325 | 0.069625
06h30 | 64.43 | 52.85 | 30.87 | 15.56 | 3.9 | 06h30 | 0.80537 | 0.66063 | 0.38588 | 0.1945 | 0.04875
07h30 | 62.72 | 49.12 | 33.91 | 20.88 | 11.68 | 07h30 | 0.784 | 0.614 | 0.42388 | 0.261 | 0.146
08h30 | 49.11 | 32.59 | 20.12 | 17.02 | 11.68 | 08h30 | 0.61387 | 0.40737 | 0.2515 | 0.21275 | 0.146
09h30 | 32.99 | 15.92 | 9.42 | 0 | 0 | 09h30 | 0.41237 | 0.199 | 0.11775 | 0 | 0
10h30 | 25.28 | 10.6 | 6.71 | 0 | 0 | 10h30 | 0.316 | 0.1325 | 0.083875 | 0 | 0
11h30 | 27.73 | 9.45 | 4.05 | 0 | 0 | 11h30 | 0.34663 | 0.11812 | 0.050625 | 0 | 0
12h30 | 54.48 | 39.75 | 22.28 | 7.69 | 0 | 12h30 | 0.681 | 0.49688 | 0.2785 | 0.096125 | 0
13h30 | 68.03 | 54.54 | 30.91 | 18.8 | 8.3 | 13h30 | 0.85037 | 0.68175 | 0.38638 | 0.235 | 0.10375
14h30 | 68.81 | 55.49 | 31.59 | 18.34 | 8.3 | 14h30 | 0.86013 | 0.69363 | 0.39487 | 0.22925 | 0.10375
15h30 | 37.76 | 31.25 | 18.91 | 7.23 | 0 | 15h30 | 0.472 | 0.39062 | 0.23638 | 0.090375 | 0
16h30 | 13.01 | 0 | 0 | 0 | 0 | 16h30 | 0.16262 | 0 | 0 | 0 | 0
17h30 | 13.24 | 0 | 0 | 0 | 0 | 17h30 | 0.1655 | 0 | 0 | 0 | 0
18h30 | 11.4 | 0 | 0 | 0 | 0 | 18h30 | 0.1425 | 0 | 0 | 0 | 0
19h30 | 10.09 | 0 | 0 | 0 | 0 | 19h30 | 0.12612 | 0 | 0 | 0 | 0
20h30 | 9.7 | 0 | 0 | 0 | 0 | 20h30 | 0.12125 | 0 | 0 | 0 | 0
21h30 | 9.61 | 0 | 0 | 0 | 0 | 21h30 | 0.12012 | 0 | 0 | 0 | 0
22h30 | 9.77 | 0 | 0 | 0 | 0 | 22h30 | 0.12212 | 0 | 0 | 0 | 0
23h30 | 9.61 | 0 | 0 | 0 | 0 | 23h30 | 0.12012 | 0 | 0 | 0 | 0
00h30 | 8.89 | 0 | 0 | 0 | 0 | 00h30 | 0.11113 | 0 | 0 | 0 | 0
01h30 | 0 | 0 | 0 | 0 | 0 | 01h30 | 0 | 0 | 0 | 0 | 0
02h30 | 0.1 | 0 | 0 | 0 | 0 | 02h30 | 0.00125 | 0 | 0 | 0 | 0
03h30 | 35.74 | 21.87 | 8.04 | 0 | 0 | 03h30 | 0.44675 | 0.27337 | 0.1005 | 0 | 0
04h30 | 69.81 | 60.51 | 33.17 | 19.29 | 0 | 04h30 | 0.87262 | 0.75638 | 0.41463 | 0.24113 | 0
05h30 | 73.38 | 63.64 | 35.14 | 19.29 | 0 | 05h30 | 0.91725 | 0.7955 | 0.43925 | 0.24113 | 0
06h30 | 81.11 | 71.6 | 40.58 | 23.97 | 2.08 | 06h30 | 1.0139 | 0.895 | 0.50725 | 0.29962 | 0.026
07h30 | 139.19 | 129.01 | 80.85 | 65.79 | 42.8 | 07h30 | 1.7399 | 1.6126 | 1.0106 | 0.82237 | 0.535
08h30 | 180.22 | 168.05 | 100.81 | 87.08 | 63.1 | 08h30 | 2.2527 | 2.1006 | 1.2601 | 1.0885 | 0.78875
09h30 | 182.93 | 176.8 | 105.56 | 91.24 | 68.25 | 09h30 | 2.2866 | 2.21 | 1.3195 | 1.1405 | 0.85313
10h30 | 191.37 | 182.19 | 108.48 | 93.51 | 71.42 | 10h30 | 2.3921 | 2.2774 | 1.356 | 1.1689 | 0.89275
11h30 | 179.91 | 169.01 | 100.18 | 85.85 | 65.03 | 11h30 | 2.2489 | 2.1126 | 1.2523 | 1.0731 | 0.81288
12h30 | 141.21 | 130.85 | 76.24 | 63.39 | 44.18 | 12h30 | 1.7651 | 1.6356 | 0.953 | 0.79238 | 0.55225
13h30 | 116.3 | 107.3 | 61.16 | 48.48 | 31.2 | 13h30 | 1.4538 | 1.3413 | 0.7645 | 0.606 | 0.39
14h30 | 120.53 | 112.3 | 63.73 | 50.01 | 32.72 | 14h30 | 1.5066 | 1.4038 | 0.79663 | 0.62513 | 0.409
15h30 | 113.9 | 105.82 | 59.79 | 45.67 | 28.51 | 15h30 | 1.4238 | 1.3228 | 0.74738 | 0.57088 | 0.35637
16h30 | 105.62 | 97.64 | 55.62 | 41.67 | 25.52 | 16h30 | 1.3202 | 1.2205 | 0.69525 | 0.52087 | 0.319
17h30 | 120.85 | 112.39 | 65.9 | 51.89 | 36.3 | 17h30 | 1.5106 | 1.4049 | 0.82375 | 0.64863 | 0.45375
18h30 | 129.82 | 120.31 | 71.65 | 58.01 | 43.23 | 18h30 | 1.6227 | 1.5039 | 0.89563 | 0.72513 | 0.54038
19h30 | 131.25 | 121.11 | 72.45 | 59.44 | 44.83 | 19h30 | 1.6406 | 1.5139 | 0.90563 | 0.743 | 0.56037
20h30 | 146.41 | 135.98 | 81.69 | 68.61 | 53.41 | 20h30 | 1.8301 | 1.6998 | 1.0211 | 0.85762 | 0.66763
21h30 | 155.99 | 145.08 | 87.41 | 74.36 | 59.01 | 21h30 | 1.9499 | 1.8135 | 1.0926 | 0.9295 | 0.73762
22h30 | 148.2 | 136.73 | 82.58 | 69.74 | 55.54 | 22h30 | 1.8525 | 1.7091 | 1.0322 | 0.87175 | 0.69425
23h30 | 138.44 | 126.34 | 76.75 | 63.53 | 50.63 | 23h30 | 1.7305 | 1.5793 | 0.95937 | 0.79412 | 0.63287
00h30 | 109.31 | 98.26 | 54.92 | 41.68 | 35.35 | 00h30 | 1.3664 | 1.2283 | 0.6865 | 0.521 | 0.44188
01h30 | 99.72 | 90.3 | 53.82 | 38.75 | 26.86 | 01h30 | 1.2465 | 1.1287 | 0.67275 | 0.48438 | 0.33575
02h30 | 98.99 | 89.23 | 53.74 | 36.97 | 26.86 | 02h30 | 1.2374 | 1.1154 | 0.67175 | 0.46213 | 0.33575
03h30 | 110.74 | 99.82 | 60.65 | 44.69 | 32.92 | 03h30 | 1.3842 | 1.2477 | 0.75813 | 0.55863 | 0.4115
04h30 | 108.75 | 96.65 | 59.04 | 43.87 | 32.92 | 04h30 | 1.3594 | 1.2081 | 0.738 | 0.54837 | 0.4115
05h30 | 96.03 | 82.72 | 50.87 | 36.43 | 26.46 | 05h30 | 1.2004 | 1.034 | 0.63587 | 0.45537 | 0.33075
06h30 | 91.16 | 76.62 | 47.38 | 33.44 | 26.46 | 06h30 | 1.1395 | 0.95775 | 0.59225 | 0.418 | 0.33075
07h30 | 109.58 | 91.99 | 60.19 | 48.77 | 39.08 | 07h30 | 1.3698 | 1.1499 | 0.75238 | 0.60962 | 0.4885
08h30 | 102.3 | 84.23 | 49.13 | 42.92 | 39.08 | 08h30 | 1.2788 | 1.0529 | 0.61413 | 0.5365 | 0.4885
09h30 | 101.62 | 86.98 | 48.15 | 37.62 | 25.78 | 09h30 | 1.2703 | 1.0873 | 0.60188 | 0.47025 | 0.32225
10h30 | 94.96 | 81.52 | 48.15 | 37.62 | 25.78 | 10h30 | 1.187 | 1.019 | 0.60188 | 0.47025 | 0.32225
11h30 | 76.75 | 62.98 | 34.02 | 21.39 | 11.36 | 11h30 | 0.95937 | 0.78725 | 0.42525 | 0.26737 | 0.142
12h30 | 62.43 | 50.48 | 34.02 | 21.39 | 11.36 | 12h30 | 0.78038 | 0.631 | 0.42525 | 0.26737 | 0.142
13h30 | 45.77 | 33.26 | 14.39 | 4.13 | 0 | 13h30 | 0.57212 | 0.41575 | 0.17988 | 0.051625 | 0
14h30 | 45.77 | 33.26 | 14.39 | 4.13 | 0 | 14h30 | 0.57212 | 0.41575 | 0.17988 | 0.051625 | 0
15h30 | 21.09 | 10.98 | 0.39 | 0 | 0 | 15h30 | 0.26362 | 0.13725 | 0.004875 | 0 | 0
16h30 | 21.09 | 10.98 | 0.39 | 0 | 0 | 16h30 | 0.26362 | 0.13725 | 0.004875 | 0 | 0
17h30 | 9.14 | 0 | 0 | 0 | 0 | 17h30 | 0.11425 | 0 | 0 | 0 | 0
18h30 | 25.11 | 14 | 6.92 | 0 | 0 | 18h30 | 0.31388 | 0.175 | 0.0865 | 0 | 0
19h30 | 36.54 | 26.25 | 15.46 | 0.41 | 0 | 19h30 | 0.45675 | 0.32812 | 0.19325 | 0.005125 | 0
20h30 | 46.26 | 35.28 | 21.3 | 8.49 | 1.28 | 20h30 | 0.57825 | 0.441 | 0.26625 | 0.10612 | 0.016
21h30 | 49.23 | 37.64 | 22.79 | 9.6 | 2.48 | 21h30 | 0.61538 | 0.4705 | 0.28487 | 0.12 | 0.031
22h30 | 50.06 | 37.94 | 22.99 | 10.64 | 3.22 | 22h30 | 0.62575 | 0.47425 | 0.28737 | 0.133 | 0.04025
23h30 | 54.82 | 42.05 | 25.55 | 13.47 | 6.07 | 23h30 | 0.68525 | 0.52563 | 0.31938 | 0.16837 | 0.075875
00h30 | 48.26 | 36.89 | 17.39 | 5.02 | 4.04 | 00h30 | 0.60325 | 0.46113 | 0.21738 | 0.06275 | 0.0505
01h30 | 65.9 | 56.01 | 32.64 | 17.95 | 7.26 | 01h30 | 0.82375 | 0.70012 | 0.408 | 0.22437 | 0.09075
02h30 | 68.12 | 57.47 | 34 | 17.94 | 8.16 | 02h30 | 0.8515 | 0.71837 | 0.425 | 0.22425 | 0.102
03h30 | 58.94 | 47.31 | 28.34 | 13.29 | 3.72 | 03h30 | 0.73675 | 0.59137 | 0.35425 | 0.16612 | 0.0465
04h30 | 61.78 | 49.23 | 29.77 | 15.28 | 5.91 | 04h30 | 0.77225 | 0.61538 | 0.37212 | 0.191 | 0.073875
05h30 | 71.14 | 57.66 | 35.15 | 20.82 | 10.85 | 05h30 | 0.88925 | 0.72075 | 0.43938 | 0.26025 | 0.13562
06h30 | 75.54 | 61.08 | 37.44 | 23.47 | 13.21 | 06h30 | 0.94425 | 0.7635 | 0.468 | 0.29337 | 0.16512
07h30 | 63.15 | 44.62 | 32.18 | 21.03 | 14.01 | 07h30 | 0.78938 | 0.55775 | 0.40225 | 0.26288 | 0.17513
08h30 | 33.73 | 19.65 | 22.31 | 15.74 | 8.56 | 08h30 | 0.42163 | 0.24563 | 0.27887 | 0.19675 | 0.107
09h30 | 23.09 | 0.66 | 0.1 | 0 | 0 | 09h30 | 0.28863 | 0.00825 | 0.00125 | 0 | 0
10h30 | 23.09 | 1.38 | 1.38 | 0 | 0 | 10h30 | 0.28863 | 0.01725 | 0.01725 | 0 | 0
11h30 | 17.16 | 0.72 | 1.28 | 0 | 0 | 11h30 | 0.2145 | 0.009 | 0.016 | 0 | 0
12h30 | 17.16 | 0 | 0 | 0 | 0 | 12h30 | 0.2145 | 0 | 0 | 0 | 0
13h30 | 13.48 | 0 | 0 | 0 | 0 | 13h30 | 0.1685 | 0 | 0 | 0 | 0
14h30 | 13.48 | 0 | 0 | 0 | 0 | 14h30 | 0.1685 | 0 | 0 | 0 | 0
15h30 | 42.25 | 26.11 | 14.18 | 0 | 0 | 15h30 | 0.52812 | 0.32638 | 0.17725 | 0 | 0
16h30 | 73.12 | 57.98 | 33.86 | 19.67 | 8.66 | 16h30 | 0.914 | 0.72475 | 0.42325 | 0.24588 | 0.10825
17h30 | 74.24 | 58.99 | 35.11 | 21.69 | 11.37 | 17h30 | 0.928 | 0.73738 | 0.43888 | 0.27113 | 0.14213
18h30 | 45.07 | 30.01 | 18.34 | 4.66 | 2.71 | 18h30 | 0.56337 | 0.37512 | 0.22925 | 0.05825 | 0.033875
19h30 | 16.18 | 2.89 | 2.91 | 2.64 | 0 | 19h30 | 0.20225 | 0.036125 | 0.036375 | 0.033 | 0
20h30 | 16.79 | 1.87 | 1.82 | 0 | 0 | 20h30 | 0.20988 | 0.023375 | 0.02275 | 0 | 0
21h30 | 17.86 | 3.45 | 3.43 | 0 | 0 | 21h30 | 0.22325 | 0.043125 | 0.042875 | 0 | 0
22h30 | 18.1 | 3.49 | 3.46 | 0 | 0 | 22h30 | 0.22625 | 0.043625 | 0.04325 | 0 | 0
23h30 | 18.26 | 3.61 | 3.58 | 0 | 0 | 23h30 | 0.22825 | 0.045125 | 0.04475 | 0 | 0
00h30 | 15.7 | 1.7 | 1.72 | 0 | 0 | 00h30 | 0.19625 | 0.02125 | 0.0215 | 0 | 0
01h30 | 28.7 | 17.54 | 8.67 | 0 | 0 | 01h30 | 0.35875 | 0.21925 | 0.10837 | 0 | 0
02h30 | 31.65 | 21.21 | 12.22 | 0 | 0 | 02h30 | 0.39563 | 0.26512 | 0.15275 | 0 | 0
03h30 | 33.67 | 22.55 | 12.75 | 0 | 0 | 03h30 | 0.42087 | 0.28187 | 0.15937 | 0 | 0
04h30 | 40.17 | 28.32 | 16.32 | 0.64 | 0 | 04h30 | 0.50213 | 0.354 | 0.204 | 0.008 | 0
05h30 | 38.8 | 26.25 | 15.19 | 0.68 | 0 | 05h30 | 0.485 | 0.32812 | 0.18987 | 0.0085 | 0
06h30 | 29.36 | 16.8 | 8.08 | 0.03 | 0 | 06h30 | 0.367 | 0.21 | 0.101 | 0.000375 | 0
07h30 | 25.11 | 7.07 | 8.7 | 0 | 0 | 07h30 | 0.31388 | 0.088375 | 0.10875 | 0 | 0
08h30 | 25.11 | 7.07 | 8.7 | 0 | 0 | 08h30 | 0.31388 | 0.088375 | 0.10875 | 0 | 0
09h30 | 13.01 | 0 | 0 | 0 | 0 | 09h30 | 0.16262 | 0 | 0 | 0 | 0
10h30 | 13.01 | 0 | 0 | 0 | 0 | 10h30 | 0.16262 | 0 | 0 | 0 | 0
11h30 | 6.21 | 0 | 0 | 0 | 0 | 11h30 | 0.077625 | 0 | 0 | 0 | 0
12h30 | 6.21 | 0 | 0 | 0 | 0 | 12h30 | 0.077625 | 0 | 0 | 0 | 0
13h30 | 0.38 | 0 | 0 | 0 | 0 | 13h30 | 0.00475 | 0 | 0 | 0 | 0
14h30 | 0.38 | 0 | 0 | 0 | 0 | 14h30 | 0.00475 | 0 | 0 | 0 | 0
15h30 | 16.03 | 1.71 | 0 | 0 | 0 | 15h30 | 0.20037 | 0.021375 | 0 | 0 | 0
16h30 | 18.44 | 8.54 | 1.59 | 0 | 0 | 16h30 | 0.2305 | 0.10675 | 0.019875 | 0 | 0
17h30 | 3.43 | 6.84 | 1.59 | 0 | 0 | 17h30 | 0.042875 | 0.0855 | 0.019875 | 0 | 0
18h30 | 17.72 | 1.28 | 0 | 0 | 0 | 18h30 | 0.2215 | 0.016 | 0 | 0 | 0
19h30 | 18.05 | 9.09 | 3.26 | 0 | 0 | 19h30 | 0.22562 | 0.11363 | 0.04075 | 0 | 0
20h30 | 4.62 | 7.8 | 3.26 | 0 | 0 | 20h30 | 0.05775 | 0.0975 | 0.04075 | 0 | 0
21h30 | 14.04 | 0 | 0 | 0 | 0 | 21h30 | 0.1755 | 0 | 0 | 0 | 0
22h30 | 33.16 | 24.17 | 12.8 | 0 | 0 | 22h30 | 0.4145 | 0.30212 | 0.16 | 0 | 0
23h30 | 39.61 | 30.02 | 16.79 | 2.51 | 0 | 23h30 | 0.49512 | 0.37525 | 0.20988 | 0.031375 | 0
00h30 | 17.2 | 5.94 | 3.99 | 2.51 | 0 | 00h30 | 0.215 | 0.07425 | 0.049875 | 0.031375 | 0
01h30 | 12.72 | 6.18 | 0 | 0 | 0 | 01h30 | 0.159 | 0.07725 | 0 | 0 | 0
02h30 | 12.72 | 6.09 | 0 | 0 | 0 | 02h30 | 0.159 | 0.076125 | 0 | 0 | 0
03h30 | 0 | 0 | 0 | 0 | 0 | 03h30 | 0 | 0 | 0 | 0 | 0
04h30 | 11.54 | 1.1 | 0 | 0 | 0 | 04h30 | 0.14425 | 0.01375 | 0 | 0 | 0
05h30 | 24.56 | 16.95 | 7.92 | 0 | 0 | 05h30 | 0.307 | 0.21188 | 0.099 | 0 | 0
06h30 | 22.21 | 15.85 | 7.92 | 0 | 0 | 06h30 | 0.27763 | 0.19812 | 0.099 | 0 | 0
07h30 | 26.63 | 15.27 | 12.61 | 0 | 0 | 07h30 | 0.33287 | 0.19087 | 0.15762 | 0 | 0
08h30 | 17.44 | 15.27 | 12.61 | 0 | 0 | 08h30 | 0.218 | 0.19087 | 0.15762 | 0 | 0
09h30 | 9.88 | 0 | 0 | 0 | 0 | 09h30 | 0.1235 | 0 | 0 | 0 | 0
10h30 | 10.91 | 0 | 0 | 0 | 0 | 10h30 | 0.13637 | 0 | 0 | 0 | 0
11h30 | 19 | 6.28 | 0.15 | 0 | 0 | 11h30 | 0.2375 | 0.0785 | 0.001875 | 0 | 0
12h30 | 23.47 | 12.25 | 4.45 | 0 | 0 | 12h30 | 0.29337 | 0.15313 | 0.055625 | 0 | 0
13h30 | 22.64 | 12.08 | 4.3 | 0 | 0 | 13h30 | 0.283 | 0.151 | 0.05375 | 0 | 0
14h30 | 17.13 | 6.11 | 0 | 0 | 0 | 14h30 | 0.21413 | 0.076375 | 0 | 0 | 0
15h30 | 3.74 | 0 | 0 | 0 | 0 | 15h30 | 0.04675 | 0 | 0 | 0 | 0
16h30 | 20.58 | 6.82 | 0.73 | 0 | 0 | 16h30 | 0.25725 | 0.08525 | 0.009125 | 0 | 0
17h30 | 37.99 | 27.23 | 15.28 | 0 | 0 | 17h30 | 0.47487 | 0.34037 | 0.191 | 0 | 0
18h30 | 40.88 | 29.63 | 17.03 | 1.87 | 0 | 18h30 | 0.511 | 0.37038 | 0.21288 | 0.023375 | 0
19h30 | 37.7 | 26.49 | 15.33 | 1.87 | 0 | 19h30 | 0.47125 | 0.33113 | 0.19162 | 0.023375 | 0
20h30 | 42.73 | 31.43 | 18.37 | 3.86 | 0 | 20h30 | 0.53412 | 0.39287 | 0.22962 | 0.04825 | 0
21h30 | 53.7 | 42.21 | 25.05 | 10.98 | 0 | 21h30 | 0.67125 | 0.52763 | 0.31312 | 0.13725 | 0
22h30 | 47.14 | 35.37 | 21.02 | 7.31 | 0 | 22h30 | 0.58925 | 0.44212 | 0.26275 | 0.091375 | 0
23h30 | 32.17 | 20.07 | 11.73 | 0.19 | 0 | 23h30 | 0.40213 | 0.25088 | 0.14663 | 0.002375 | 0
00h30 | 13.97 | 12.74 | 10.24 | 0 | 0 | 00h30 | 0.17463 | 0.15925 | 0.128 | 0 | 0
01h30 | 24.46 | 13.89 | 3.26 | 0 | 0 | 01h30 | 0.30575 | 0.17363 | 0.04075 | 0 | 0
02h30 | 28.92 | 20.4 | 10.09 | 0 | 0 | 02h30 | 0.3615 | 0.255 | 0.12612 | 0 | 0
03h30 | 29.72 | 19.53 | 10.39 | 0 | 0 | 03h30 | 0.3715 | 0.24413 | 0.12987 | 0 | 0
04h30 | 34.87 | 24.11 | 13.78 | 0 | 0 | 04h30 | 0.43588 | 0.30138 | 0.17225 | 0 | 0
05h30 | 39.7 | 28.29 | 16.95 | 1.01 | 0 | 05h30 | 0.49625 | 0.35363 | 0.21188 | 0.012625 | 0
06h30 | 51.45 | 39.22 | 24.13 | 8.28 | 0 | 06h30 | 0.64312 | 0.49025 | 0.30162 | 0.1035 | 0
07h30 | 63.69 | 48.64 | 33.54 | 20.84 | 8.53 | 07h30 | 0.79612 | 0.608 | 0.41925 | 0.2605 | 0.10662
08h30 | 42.33 | 26.62 | 16.16 | 13.56 | 8.53 | 08h30 | 0.52912 | 0.33275 | 0.202 | 0.1695 | 0.10662
09h30 | 9.07 | 0 | 0 | 0 | 0 | 09h30 | 0.11338 | 0 | 0 | 0 | 0
10h30 | 9.07 | 0 | 0 | 0 | 0 | 10h30 | 0.11338 | 0 | 0 | 0 | 0
11h30 | 5.84 | 0 | 0 | 0 | 0 | 11h30 | 0.073 | 0 | 0 | 0 | 0
12h30 | 21.79 | 10.37 | 0 | 0 | 0 | 12h30 | 0.27237 | 0.12962 | 0 | 0 | 0
13h30 | 24.48 | 14.66 | 3.25 | 0 | 0 | 13h30 | 0.306 | 0.18325 | 0.040625 | 0 | 0
14h30 | 20.64 | 10.37 | 3.25 | 0 | 0 | 14h30 | 0.258 | 0.12962 | 0.040625 | 0 | 0
15h30 | 19.59 | 10.07 | 0 | 0 | 0 | 15h30 | 0.24488 | 0.12587 | 0 | 0 | 0
16h30 | 26.08 | 18.03 | 5.91 | 0 | 0 | 16h30 | 0.326 | 0.22537 | 0.073875 | 0 | 0
17h30 | 28.25 | 21.21 | 9.38 | 0 | 0 | 17h30 | 0.35313 | 0.26512 | 0.11725 | 0 | 0
18h30 | 20.79 | 13.95 | 5.69 | 0 | 0 | 18h30 | 0.25988 | 0.17438 | 0.071125 | 0 | 0
19h30 | 11.13 | 6.78 | 2.23 | 0 | 0 | 19h30 | 0.13912 | 0.08475 | 0.027875 | 0 | 0
20h30 | 3.27 | 0 | 0 | 0 | 0 | 20h30 | 0.040875 | 0 | 0 | 0 | 0
21h30 | 6.1 | 0 | 0 | 0 | 0 | 21h30 | 0.07625 | 0 | 0 | 0 | 0
22h30 | 7.04 | 0 | 0 | 0 | 0 | 22h30 | 0.088 | 0 | 0 | 0 | 0
23h30 | 8.04 | 0 | 0 | 0 | 0 | 23h30 | 0.1005 | 0 | 0 | 0 | 0
00h30 | 3.83 | 0 | 0 | 0 | 0 | 00h30 | 0.047875 | 0 | 0 | 0 | 0
01h30 | 2.12 | 0 | 0 | 0 | 0 | 01h30 | 0.0265 | 0 | 0 | 0 | 0
02h30 | 5.44 | 0 | 0 | 0 | 0 | 02h30 | 0.068 | 0 | 0 | 0 | 0
03h30 | 6.75 | 0 | 0 | 0 | 0 | 03h30 | 0.084375 | 0 | 0 | 0 | 0
04h30 | 8.63 | 0 | 0 | 0 | 0 | 04h30 | 0.10787 | 0 | 0 | 0 | 0
05h30 | 10.81 | 0 | 0 | 0 | 0 | 05h30 | 0.13512 | 0 | 0 | 0 | 0
06h30 | 13.4 | 0.44 | 0.27 | 0 | 0 | 06h30 | 0.1675 | 0.0055 | 0.003375 | 0 | 0
07h30 | 29.18 | 13.89 | 13.82 | 0 | 0 | 07h30 | 0.36475 | 0.17363 | 0.17275 | 0 | 0
08h30 | 21.38 | 13.44 | 13.55 | 0 | 0 | 08h30 | 0.26725 | 0.168 | 0.16937 | 0 | 0
09h30 | 13.13 | 0 | 0 | 0 | 0 | 09h30 | 0.16412 | 0 | 0 | 0 | 0
10h30 | 13.13 | 0 | 0 | 0 | 0 | 10h30 | 0.16412 | 0 | 0 | 0 | 0
11h30 | 31.86 | 13.66 | 3.22 | 0 | 0 | 11h30 | 0.39825 | 0.17075 | 0.04025 | 0 | 0
12h30 | 56.94 | 41.79 | 21.65 | 2.61 | 0 | 12h30 | 0.71175 | 0.52238 | 0.27063 | 0.032625 | 0
13h30 | 52.79 | 38.95 | 19.37 | 2.61 | 0 | 13h30 | 0.65987 | 0.48688 | 0.24213 | 0.032625 | 0
14h30 | 48.91 | 36.02 | 17.07 | 0 | 0 | 14h30 | 0.61138 | 0.45025 | 0.21338 | 0 | 0
15h30 | 48.76 | 36.55 | 17.62 | 0 | 0 | 15h30 | 0.6095 | 0.45687 | 0.22025 | 0 | 0
16h30 | 56.25 | 44.36 | 23.62 | 5.28 | 0 | 16h30 | 0.70312 | 0.5545 | 0.29525 | 0.066 | 0
17h30 | 54.45 | 42.39 | 23.66 | 5.99 | 0 | 17h30 | 0.68063 | 0.52987 | 0.29575 | 0.074875 | 0
18h30 | 28.44 | 16.1 | 8.3 | 0.71 | 0 | 18h30 | 0.3555 | 0.20125 | 0.10375 | 0.008875 | 0
19h30 | 10.08 | 6.71 | 6.78 | 0 | 0 | 19h30 | 0.126 | 0.083875 | 0.08475 | 0 | 0
20h30 | 11.69 | 0 | 0 | 0 | 0 | 20h30 | 0.14613 | 0 | 0 | 0 | 0
21h30 | 41.85 | 28.57 | 16.89 | 0 | 0 | 21h30 | 0.52312 | 0.35713 | 0.21113 | 0 | 0
22h30 | 70.81 | 57.99 | 34.86 | 17.35 | 2.36 | 22h30 | 0.88513 | 0.72488 | 0.43575 | 0.21688 | 0.0295
23h30 | 66.72 | 53.34 | 31.92 | 17.35 | 2.36 | 23h30 | 0.834 | 0.66675 | 0.399 | 0.21688 | 0.0295
00h30 | 41.33 | 29.73 | 13.94 | 0 | 0 | 00h30 | 0.51663 | 0.37162 | 0.17425 | 0 | 0
01h30 | 41.35 | 31.57 | 16.81 | 0 | 0 | 01h30 | 0.51687 | 0.39463 | 0.21013 | 0 | 0
02h30 | 41.09 | 30.93 | 16.84 | 0 | 0 | 02h30 | 0.51362 | 0.38662 | 0.2105 | 0 | 0
03h30 | 38.87 | 28.11 | 15.47 | 0 | 0 | 03h30 | 0.48588 | 0.35137 | 0.19337 | 0 | 0
04h30 | 35.78 | 24.42 | 15.44 | 0 | 0 | 04h30 | 0.44725 | 0.30525 | 0.193 | 0 | 0
05h30 | 38.82 | 26.85 | 14.99 | 0 | 0 | 05h30 | 0.48525 | 0.33563 | 0.18738 | 0 | 0
06h30 | 45.02 | 32.42 | 19.3 | 3.36 | 0 | 06h30 | 0.56275 | 0.40525 | 0.24125 | 0.042 | 0
07h30 | 66.15 | 50.48 | 35.14 | 21.97 | 7.82 | 07h30 | 0.82688 | 0.631 | 0.43925 | 0.27463 | 0.09775
08h30 | 68.45 | 50.1 | 31.23 | 19.26 | 7.82 | 08h30 | 0.85562 | 0.62625 | 0.39038 | 0.24075 | 0.09775
09h30 | 68.81 | 51.11 | 31.24 | 18.6 | 5.38 | 09h30 | 0.86013 | 0.63887 | 0.3905 | 0.2325 | 0.06725
10h30 | 67.59 | 50.92 | 30.84 | 18.25 | 5.38 | 10h30 | 0.84488 | 0.6365 | 0.3855 | 0.22812 | 0.06725
11h30 | 71.13 | 55.24 | 31.82 | 20.44 | 5.74 | 11h30 | 0.88913 | 0.6905 | 0.39775 | 0.2555 | 0.07175
12h30 | 64.43 | 49.37 | 31.82 | 20.14 | 5.74 | 12h30 | 0.80537 | 0.61713 | 0.39775 | 0.25175 | 0.07175
13h30 | 56.88 | 43.19 | 22.37 | 12.32 | 0 | 13h30 | 0.711 | 0.53987 | 0.27963 | 0.154 | 0
14h30 | 54.03 | 42.59 | 22.37 | 12.32 | 0 | 14h30 | 0.67537 | 0.53238 | 0.27963 | 0.154 | 0
15h30 | 54.79 | 42.42 | 22.96 | 10.82 | 0 | 15h30 | 0.68488 | 0.53025 | 0.287 | 0.13525 | 0
16h30 | 52.55 | 42.42 | 22.96 | 10.82 | 0 | 16h30 | 0.65687 | 0.53025 | 0.287 | 0.13525 | 0
17h30 | 41.84 | 27.77 | 16.15 | 4.91 | 0 | 17h30 | 0.523 | 0.34713 | 0.20187 | 0.061375 | 0
18h30 | 41.84 | 27.77 | 16.15 | 4.91 | 0 | 18h30 | 0.523 | 0.34713 | 0.20187 | 0.061375 | 0
19h30 | 10.86 | 0 | 0 | 0 | 0 | 19h30 | 0.13575 | 0 | 0 | 0 | 0
20h30 | 30.7 | 17.54 | 10.95 | 0 | 0 | 20h30 | 0.38375 | 0.21925 | 0.13687 | 0 | 0
21h30 | 51.65 | 39.53 | 24.39 | 10.68 | 0.21 | 21h30 | 0.64563 | 0.49412 | 0.30488 | 0.1335 | 0.002625
22h30 | 36.22 | 23.46 | 15.14 | 10.68 | 0.21 | 22h30 | 0.45275 | 0.29325 | 0.18925 | 0.1335 | 0.002625
23h30 | 16.09 | 3.05 | 3.18 | 0 | 0 | 23h30 | 0.20112 | 0.038125 | 0.03975 | 0 | 0
00h30 | 11.68 | 1.58 | 1.48 | 0 | 0 | 00h30 | 0.146 | 0.01975 | 0.0185 | 0 | 0
01h30 | 6.89 | 0 | 0 | 0 | 0 | 01h30 | 0.086125 | 0 | 0 | 0 | 0
02h30 | 9.03 | 0 | 0 | 0 | 0 | 02h30 | 0.11288 | 0 | 0 | 0 | 0
03h30 | 26.13 | 15.16 | 8.71 | 0 | 0 | 03h30 | 0.32662 | 0.1895 | 0.10887 | 0 | 0
04h30 | 42.82 | 31.62 | 19.08 | 1.9 | 0 | 04h30 | 0.53525 | 0.39525 | 0.2385 | 0.02375 | 0
05h30 | 27.76 | 16.46 | 10.37 | 1.9 | 0 | 05h30 | 0.347 | 0.20575 | 0.12962 | 0.02375 | 0
06h30 | 13.66 | 0.11 | 0.18 | 0 | 0 | 06h30 | 0.17075 | 0.001375 | 0.00225 | 0 | 0
07h30 | 28.53 | 11.47 | 11.54 | 0 | 0 | 07h30 | 0.35663 | 0.14338 | 0.14425 | 0 | 0
08h30 | 23.8 | 11.36 | 11.36 | 0 | 0 | 08h30 | 0.2975 | 0.142 | 0.142 | 0 | 0
09h30 | 19.17 | 0.34 | 0.44 | 0 | 0 | 09h30 | 0.23963 | 0.00425 | 0.0055 | 0 | 0
10h30 | 19.17 | 0.34 | 0.44 | 0 | 0 | 10h30 | 0.23963 | 0.00425 | 0.0055 | 0 | 0
11h30 | 13.85 | 0 | 0 | 0 | 0 | 11h30 | 0.17313 | 0 | 0 | 0 | 0
12h30 | 13.85 | 0 | 0 | 0 | 0 | 12h30 | 0.17313 | 0 | 0 | 0 | 0
13h30 | 10.14 | 0 | 0 | 0 | 0 | 13h30 | 0.12675 | 0 | 0 | 0 | 0
14h30 | 10.14 | 0 | 0 | 0 | 0 | 14h30 | 0.12675 | 0 | 0 | 0 | 0
15h30 | 9.54 | 0 | 0 | 0 | 0 | 15h30 | 0.11925 | 0 | 0 | 0 | 0
16h30 | 11.36 | 0 | 0 | 0 | 0 | 16h30 | 0.142 | 0 | 0 | 0 | 0
17h30 | 12.26 | 0 | 0 | 0 | 0 | 17h30 | 0.15325 | 0 | 0 | 0 | 0
18h30 | 12.39 | 0 | 0 | 0 | 0 | 18h30 | 0.15488 | 0 | 0 | 0 | 0
19h30 | 12.43 | 0 | 0 | 0 | 0 | 19h30 | 0.15538 | 0 | 0 | 0 | 0
20h30 | 12.5 | 0.17 | 0.21 | 0 | 0 | 20h30 | 0.15625 | 0.002125 | 0.002625 | 0 | 0
21h30 | 12.75 | 0.58 | 0.61 | 0 | 0 | 21h30 | 0.15937 | 0.00725 | 0.007625 | 0 | 0
22h30 | 44.75 | 32.66 | 20.05 | 0 | 0 | 22h30 | 0.55937 | 0.40825 | 0.25062 | 0 | 0
23h30 | 78.69 | 66.63 | 40.76 | 22.15 | 7.46 | 23h30 | 0.98362 | 0.83288 | 0.5095 | 0.27687 | 0.09325
00h30 | 44.66 | 34.38 | 21.11 | 22.15 | 7.46 | 00h30 | 0.55825 | 0.42975 | 0.26388 | 0.27687 | 0.09325
01h30 | 42.36 | 31.89 | 16.8 | 0 | 0 | 01h30 | 0.5295 | 0.39863 | 0.21 | 0 | 0
02h30 | 82.01 | 73.51 | 43.68 | 24.35 | 7.88 | 02h30 | 1.0251 | 0.91887 | 0.546 | 0.30438 | 0.0985
03h30 | 82.31 | 73.81 | 44.17 | 24.35 | 7.88 | 03h30 | 1.0289 | 0.92263 | 0.55212 | 0.30438 | 0.0985
04h30 | 85.61 | 76.3 | 46.09 | 26.21 | 8.81 | 04h30 | 1.0701 | 0.95375 | 0.57612 | 0.32762 | 0.11013
05h30 | 86.87 | 76.7 | 46.67 | 27.85 | 11.34 | 05h30 | 1.0859 | 0.95875 | 0.58337 | 0.34813 | 0.14175
06h30 | 86.72 | 75.71 | 46.24 | 28.43 | 12.53 | 06h30 | 1.084 | 0.94637 | 0.578 | 0.35537 | 0.15662
07h30 | 62.3 | 49 | 34.28 | 26.8 | 10.01 | 07h30 | 0.77875 | 0.6125 | 0.4285 | 0.335 | 0.12512
08h30 | 63.22 | 49.2 | 29.03 | 13.32 | 4.2 | 08h30 | 0.79025 | 0.615 | 0.36288 | 0.1665 | 0.0525
09h30 | 109.07 | 97.13 | 56.61 | 41.17 | 24.46 | 09h30 | 1.3634 | 1.2141 | 0.70762 | 0.51462 | 0.30575
10h30 | 128.82 | 118.4 | 68.7 | 52.61 | 31.58 | 10h30 | 1.6102 | 1.48 | 0.85875 | 0.65763 | 0.39475
11h30 | 135.76 | 125.87 | 73.06 | 57.63 | 34.71 | 11h30 | 1.697 | 1.5734 | 0.91325 | 0.72037 | 0.43388
12h30 | 123.47 | 113.57 | 65.81 | 51.11 | 29.63 | 12h30 | 1.5434 | 1.4196 | 0.82263 | 0.63887 | 0.37038
13h30 | 130.35 | 120.7 | 70.27 | 55.94 | 33.65 | 13h30 | 1.6294 | 1.5088 | 0.87838 | 0.69925 | 0.42063
14h30 | 114.3 | 104.98 | 60.96 | 47.09 | 27.42 | 14h30 | 1.4287 | 1.3122 | 0.762 | 0.58862 | 0.34275
15h30 | 90.1 | 80.81 | 46.8 | 33.25 | 17.06 | 15h30 | 1.1262 | 1.0101 | 0.585 | 0.41563 | 0.21325
16h30 | 87.34 | 77.85 | 45.67 | 32.22 | 17.67 | 16h30 | 1.0917 | 0.97313 | 0.57088 | 0.40275 | 0.22087
17h30 | 93.57 | 83.92 | 50.06 | 36.49 | 22.37 | 17h30 | 1.1696 | 1.049 | 0.62575 | 0.45613 | 0.27963
18h30 | 96.76 | 87.01 | 52.58 | 38.61 | 25.16 | 18h30 | 1.2095 | 1.0876 | 0.65725 | 0.48263 | 0.3145
19h30 | 97.3 | 87.4 | 53.3 | 39.01 | 26.19 | 19h30 | 1.2163 | 1.0925 | 0.66625 | 0.48762 | 0.32738
20h30 | 97.29 | 87.16 | 53.49 | 39.02 | 26.64 | 20h30 | 1.2161 | 1.0895 | 0.66863 | 0.48775 | 0.333
21h30 | 91.56 | 81.08 | 50.08 | 35.55 | 24.09 | 21h30 | 1.1445 | 1.0135 | 0.626 | 0.44438 | 0.30112
22h30 | 85.01 | 74.1 | 46.15 | 31.49 | 21.12 | 22h30 | 1.0626 | 0.92625 | 0.57688 | 0.39363 | 0.264
23h30 | 49.22 | 37.81 | 24.67 | 9.82 | 2.91 | 23h30 | 0.61525 | 0.47263 | 0.30838 | 0.12275 | 0.036375
00h30 | 20.2 | 8.35 | 8.37 | 3.39 | 2.02 | 00h30 | 0.2525 | 0.10437 | 0.10462 | 0.042375 | 0.02525
01h30 | 6.42 | 0 | 0 | 0 | 0 | 01h30 | 0.08025 | 0 | 0 | 0 | 0
02h30 | 11.4 | 0.85 | 0.84 | 0 | 0 | 02h30 | 0.1425 | 0.010625 | 0.0105 | 0 | 0
03h30 | 28.12 | 18.86 | 12.73 | 0 | 0 | 03h30 | 0.3515 | 0.23575 | 0.15912 | 0 | 0
04h30 | 44.73 | 33.61 | 21.36 | 3.44 | 0 | 04h30 | 0.55912 | 0.42013 | 0.267 | 0.043 | 0
05h30 | 53.44 | 41.06 | 25.9 | 9.87 | 1.5 | 05h30 | 0.668 | 0.51325 | 0.32375 | 0.12337 | 0.01875
06h30 | 60.84 | 47.28 | 29.89 | 13.54 | 4.58 | 06h30 | 0.7605 | 0.591 | 0.37362 | 0.16925 | 0.05725
07h30 | 79.96 | 62.82 | 43.91 | 30.98 | 22.06 | 07h30 | 0.9995 | 0.78525 | 0.54888 | 0.38725 | 0.27575
08h30 | 90.55 | 71.27 | 45.55 | 32.22 | 23.07 | 08h30 | 1.1319 | 0.89087 | 0.56937 | 0.40275 | 0.28837
09h30 | 97.79 | 79.76 | 50.62 | 34.79 | 24.72 | 09h30 | 1.2224 | 0.997 | 0.63275 | 0.43488 | 0.309
10h30 | 93.71 | 76.28 | 47.35 | 32.9 | 21.36 | 10h30 | 1.1714 | 0.9535 | 0.59188 | 0.41125 | 0.267
11h30 | 57.26 | 40.3 | 25.33 | 11 | 2.64 | 11h30 | 0.71575 | 0.50375 | 0.31662 | 0.1375 | 0.033
12h30 | 55.72 | 39.2 | 24.51 | 9.94 | 1.96 | 12h30 | 0.6965 | 0.49 | 0.30638 | 0.12425 | 0.0245
13h30 | 94.62 | 78.73 | 47.29 | 34.08 | 21.48 | 13h30 | 1.1827 | 0.98413 | 0.59113 | 0.426 | 0.2685
14h30 | 125.29 | 110.32 | 65.45 | 52.87 | 36.38 | 14h30 | 1.5661 | 1.379 | 0.81812 | 0.66087 | 0.45475
15h30 | 139.06 | 124.59 | 74.32 | 61.02 | 43.62 | 15h30 | 1.7383 | 1.5574 | 0.929 | 0.76275 | 0.54525
16h30 | 74.43 | 67.3 | 45.16 | 36.83 | 28.68 | 16h30 | 0.93037 | 0.84125 | 0.5645 | 0.46037 | 0.3585
17h30 | 18.38 | 1.12 | 1.12 | 0 | 0 | 17h30 | 0.22975 | 0.014 | 0.014 | 0 | 0
18h30 | 20.12 | 6.16 | 6.16 | 0 | 0 | 18h30 | 0.2515 | 0.077 | 0.077 | 0 | 0
19h30 | 81.77 | 67.47 | 42.75 | 21.81 | 10.15 | 19h30 | 1.0221 | 0.84337 | 0.53438 | 0.27263 | 0.12687
20h30 | 142.33 | 128.23 | 79.4 | 62.93 | 47.46 | 20h30 | 1.7791 | 1.6029 | 0.9925 | 0.78663 | 0.59325
21h30 | 141.76 | 127.74 | 79.37 | 63.15 | 47.99 | 21h30 | 1.772 | 1.5967 | 0.99213 | 0.78938 | 0.59988
22h30 | 154.09 | 140.09 | 86.85 | 70.85 | 54.5 | 22h30 | 1.9261 | 1.7511 | 1.0856 | 0.88562 | 0.68125
23h30 | 174.63 | 178.14 | 118.39 | 102.07 | 81.47 | 23h30 | 2.1829 | 2.2268 | 1.4799 | 1.2759 | 1.0184
00h30 | 197 | 192.31 | 115.81 | 102.06 | 77.25 | 00h30 | 2.4625 | 2.4039 | 1.4476 | 1.2757 | 0.96562
01h30 | 192.03 | 181.86 | 109.57 | 95.53 | 70.87 | 01h30 | 2.4004 | 2.2732 | 1.3696 | 1.1941 | 0.88587
02h30 | 183.81 | 172.45 | 104.36 | 87.87 | 65.63 | 02h30 | 2.2976 | 2.1556 | 1.3045 | 1.0984 | 0.82037
03h30 | 166.54 | 154.19 | 93.69 | 78.25 | 58.85 | 03h30 | 2.0817 | 1.9274 | 1.1711 | 0.97813 | 0.73562
04h30 | 131.65 | 118.59 | 72.67 | 57.67 | 42.49 | 04h30 | 1.6456 | 1.4824 | 0.90838 | 0.72088 | 0.53112
05h30 | 103.61 | 89.95 | 55.89 | 41.04 | 29.18 | 05h30 | 1.2951 | 1.1244 | 0.69863 | 0.513 | 0.36475
06h30 | 96.17 | 81.98 | 51.45 | 36.76 | 26 | 06h30 | 1.2021 | 1.0248 | 0.64312 | 0.4595 | 0.325
07h30 | 113.06 | 96.8 | 65.34 | 51.34 | 41.51 | 07h30 | 1.4132 | 1.21 | 0.81675 | 0.64175 | 0.51887
08h30 | 68.21 | 57.47 | 49.42 | 35.06 | 26.7 | 08h30 | 0.85262 | 0.71837 | 0.61775 | 0.43825 | 0.33375
09h30 | 21.54 | 4.33 | 2.34 | 0 | 0 | 09h30 | 0.26925 | 0.054125 | 0.02925 | 0 | 0
10h30 | 19.95 | 4.33 | 2.71 | 0 | 0 | 10h30 | 0.24938 | 0.054125 | 0.033875 | 0 | 0
11h30 | 18.95 | 3.39 | 3.25 | 0 | 0 | 11h30 | 0.23688 | 0.042375 | 0.040625 | 0 | 0
12h30 | 41.98 | 26.99 | 17.31 | 0 | 0 | 12h30 | 0.52475 | 0.33737 | 0.21638 | 0 | 0
13h30 | 40.55 | 26.05 | 16.55 | 0.42 | 0 | 13h30 | 0.50687 | 0.32562 | 0.20688 | 0.00525 | 0
14h30 | 76.21 | 62.05 | 38.65 | 23.28 | 13.41 | 14h30 | 0.95263 | 0.77563 | 0.48313 | 0.291 | 0.16762
15h30 | 142.57 | 128.39 | 78.77 | 63.73 | 50.76 | 15h30 | 1.7821 | 1.6049 | 0.98462 | 0.79663 | 0.6345
16h30 | 130.63 | 116.27 | 71.68 | 57.42 | 45.51 | 16h30 | 1.6329 | 1.4534 | 0.896 | 0.71775 | 0.56888
17h30 | 103.47 | 89.06 | 55.89 | 41.35 | 32.02 | 17h30 | 1.2934 | 1.1133 | 0.69863 | 0.51687 | 0.40025
18h30 | 111.96 | 97.5 | 61.48 | 46.28 | 36.57 | 18h30 | 1.3995 | 1.2188 | 0.7685 | 0.5785 | 0.45713
19h30 | 132.4 | 117.79 | 73.9 | 58.4 | 47.22 | 19h30 | 1.655 | 1.4724 | 0.92375 | 0.73 | 0.59025
20h30 | 139.48 | 124.6 | 78.19 | 62.32 | 50.86 | 20h30 | 1.7435 | 1.5575 | 0.97737 | 0.779 | 0.63575
21h30 | 140.42 | 125.16 | 78.77 | 62.5 | 51.17 | 21h30 | 1.7552 | 1.5645 | 0.98462 | 0.78125 | 0.63962
22h30 | 138.77 | 123.11 | 77.62 | 61.39 | 50.13 | 22h30 | 1.7346 | 1.5389 | 0.97025 | 0.76738 | 0.62662
23h30 | 134.11 | 118.02 | 74.65 | 58.4 | 47.56 | 23h30 | 1.6764 | 1.4752 | 0.93312 | 0.73 | 0.5945
00h30 | 102.7 | 87.51 | 50.61 | 36.68 | 32.25 | 00h30 | 1.2837 | 1.0939 | 0.63262 | 0.4585 | 0.40313
01h30 | 100.61 | 87.19 | 53.48 | 40.23 | 28.4 | 01h30 | 1.2576 | 1.0899 | 0.6685 | 0.50287 | 0.355
02h30 | 108.42 | 94.78 | 58.37 | 43.79 | 31.6 | 02h30 | 1.3553 | 1.1847 | 0.72962 | 0.54737 | 0.395
03h30 | 114.55 | 99.54 | 61.63 | 47.56 | 35.07 | 03h30 | 1.4319 | 1.2443 | 0.77038 | 0.5945 | 0.43838
04h30 | 111.24 | 95.37 | 59.52 | 45.63 | 34.05 | 04h30 | 1.3905 | 1.1921 | 0.744 | 0.57037 | 0.42562
05h30 | 98.59 | 82.01 | 51.75 | 38.16 | 27.91 | 05h30 | 1.2324 | 1.0251 | 0.64687 | 0.477 | 0.34887
06h30 | 85.72 | 68.55 | 43.87 | 33.97 | 25.74 | 06h30 | 1.0715 | 0.85688 | 0.54837 | 0.42462 | 0.32175
07h30 | 89.28 | 70.05 | 49.69 | 35.3 | 28.48 | 07h30 | 1.116 | 0.87562 | 0.62113 | 0.44125 | 0.356
08h30 | 81.94 | 61.76 | 40.68 | 35.3 | 28.48 | 08h30 | 1.0243 | 0.772 | 0.5085 | 0.44125 | 0.356
09h30 | 88.63 | 70.23 | 42.91 | 27.87 | 19.06 | 09h30 | 1.1079 | 0.87787 | 0.53638 | 0.34837 | 0.23825
10h30 | 96.57 | 79.56 | 46.97 | 34.94 | 24.74 | 10h30 | 1.2071 | 0.9945 | 0.58713 | 0.43675 | 0.30925
11h30 | 100.08 | 83.6 | 49.26 | 37.67 | 26.39 | 11h30 | 1.251 | 1.045 | 0.61575 | 0.47087 | 0.32987
12h30 | 90.98 | 74.94 | 45.2 | 32.78 | 22.01 | 12h30 | 1.1373 | 0.93675 | 0.565 | 0.40975 | 0.27513
13h30 | 80.13 | 64.88 | 38.32 | 26.9 | 17.05 | 13h30 | 1.0016 | 0.811 | 0.479 | 0.33625 | 0.21313
14h30 | 75.19 | 60.63 | 38.32 | 24.72 | 15.74 | 14h30 | 0.93988 | 0.75787 | 0.479 | 0.309 | 0.19675
15h30 | 73.39 | 59.22 | 35.88 | 23.73 | 15.24 | 15h30 | 0.91738 | 0.74025 | 0.4485 | 0.29663 | 0.1905
16h30 | 65.93 | 50.96 | 35.88 | 23.73 | 15.24 | 16h30 | 0.82412 | 0.637 | 0.4485 | 0.29663 | 0.1905
17h30 | 44.93 | 30.29 | 18.38 | 5.08 | 1.54 | 17h30 | 0.56163 | 0.37862 | 0.22975 | 0.0635 | 0.01925
18h30 | 53.5 | 40.13 | 26.28 | 12.99 | 7.97 | 18h30 | 0.66875 | 0.50162 | 0.3285 | 0.16237 | 0.099625
19h30 | 57.67 | 44.54 | 29.02 | 15.76 | 10.55 | 19h30 | 0.72088 | 0.55675 | 0.36275 | 0.197 | 0.13187
20h30 | 65 | 51.65 | 33.61 | 20.06 | 14.64 | 20h30 | 0.8125 | 0.64563 | 0.42013 | 0.25075 | 0.183
21h30 | 70.76 | 57.11 | 37.26 | 23.5 | 17.71 | 21h30 | 0.8845 | 0.71388 | 0.46575 | 0.29375 | 0.22137
22h30 | 70.66 | 56.62 | 37.32 | 23.1 | 17.38 | 22h30 | 0.88325 | 0.70775 | 0.4665 | 0.28875 | 0.21725
23h30 | 47.99 | 33.48 | 24.04 | 11.82 | 10.18 | 23h30 | 0.59988 | 0.4185 | 0.3005 | 0.14775 | 0.12725
00h30 | 32.2 | 17.03 | 11.49 | 0 | 0 | 00h30 | 0.4025 | 0.21288 | 0.14363 | 0 | 0
01h30 | 51.07 | 38.4 | 24.52 | 9.61 | 3.14 | 01h30 | 0.63838 | 0.48 | 0.3065 | 0.12012 | 0.03925
02h30 | 51.19 | 38.4 | 25.21 | 11.56 | 5.8 | 02h30 | 0.63987 | 0.48 | 0.31512 | 0.1445 | 0.0725
03h30 | 54.29 | 39.84 | 26.57 | 12.52 | 5.91 | 03h30 | 0.67863 | 0.498 | 0.33213 | 0.1565 | 0.073875
04h30 | 54.16 | 39.84 | 26.21 | 12.46 | 6.41 | 04h30 | 0.677 | 0.498 | 0.32762 | 0.15575 | 0.080125
05h30 | 53.61 | 36.92 | 25.74 | 12.08 | 6.44 | 05h30 | 0.67012 | 0.4615 | 0.32175 | 0.151 | 0.0805
06h30 | 57.94 | 40.52 | 28.14 | 14.32 | 8.54 | 06h30 | 0.72425 | 0.5065 | 0.35175 | 0.179 | 0.10675
07h30 | 80.55 | 60.27 | 45.58 | 30.93 | 25.6 | 07h30 | 1.0069 | 0.75338 | 0.56975 | 0.38662 | 0.32
08h30 | 76.22 | 56.66 | 42.85 | 26.79 | 20.34 | 08h30 | 0.95275 | 0.70825 | 0.53563 | 0.33487 | 0.25425
09h30 | 59.12 | 37.08 | 26.44 | 10.17 | 4.8 | 09h30 | 0.739 | 0.4635 | 0.3305 | 0.12712 | 0.06
10h30 | 62.57 | 41.87 | 27.57 | 13.97 | 8.22 | 10h30 | 0.78212 | 0.52338 | 0.34463 | 0.17463 | 0.10275
11h30 | 70.4 | 50.23 | 31.33 | 18.89 | 12.3 | 11h30 | 0.88 | 0.62787 | 0.39163 | 0.23613 | 0.15375
12h30 | 68.25 | 48.6 | 30.2 | 18.09 | 11.21 | 12h30 | 0.85313 | 0.6075 | 0.3775 | 0.22612 | 0.14012
13h30 | 63.57 | 44.63 | 26.89 | 15.98 | 9.13 | 13h30 | 0.79463 | 0.55788 | 0.33613 | 0.19975 | 0.11413
14h30 | 64.01 | 45.85 | 27.51 | 16.91 | 9.66 | 14h30 | 0.80012 | 0.57312 | 0.34387 | 0.21138 | 0.12075
15h30 | 70.91 | 53.44 | 32.32 | 21.47 | 13.63 | 15h30 | 0.88638 | 0.668 | 0.404 | 0.26837 | 0.17037
16h30 | 69.17 | 49.08 | 31.71 | 17.54 | 10.77 | 16h30 | 0.86462 | 0.6135 | 0.39637 | 0.21925 | 0.13462
17h30 | 21.17 | 2.44 | 4.09 | 0 | 0 | 17h30 | 0.26462 | 0.0305 | 0.051125 | 0 | 0
18h30 | 23.98 | 7.86 | 7.8 | 0 | 0 | 18h30 | 0.29975 | 0.09825 | 0.0975 | 0 | 0
19h30 | 23.01 | 7.8 | 8.02 | 0 | 0 | 19h30 | 0.28763 | 0.0975 | 0.10025 | 0 | 0
20h30 | 24.52 | 9.39 | 9.53 | 0 | 0 | 20h30 | 0.3065 | 0.11737 | 0.11912 | 0 | 0
21h30 | 46.42 | 31.29 | 22.77 | 5.09 | 0 | 21h30 | 0.58025 | 0.39113 | 0.28463 | 0.063625 | 0
22h30 | 82.79 | 67.54 | 44.44 | 29.39 | 21.43 | 22h30 | 1.0349 | 0.84425 | 0.5555 | 0.36738 | 0.26787
23h30 | 103.82 | 88.41 | 57.11 | 41.9 | 33.05 | 23h30 | 1.2977 | 1.1051 | 0.71388 | 0.52375 | 0.41313
00h30 | 88.9 | 74.53 | 43.07 | 29.69 | 22.06 | 00h30 | 1.1113 | 0.93163 | 0.53838 | 0.37112 | 0.27575
01h30 | 89.45 | 76.8 | 47.32 | 35.14 | 26.59 | 01h30 | 1.1181 | 0.96 | 0.5915 | 0.43925 | 0.33237
02h30 | 97.58 | 84.79 | 52.26 | 39.76 | 28.12 | 02h30 | 1.2197 | 1.0599 | 0.65325 | 0.497 | 0.3515
03h30 | 112.85 | 98.91 | 61.01 | 49.02 | 36.49 | 03h30 | 1.4106 | 1.2364 | 0.76262 | 0.61275 | 0.45613
04h30 | 102.76 | 88.12 | 54.9 | 42.77 | 31.21 | 04h30 | 1.2845 | 1.1015 | 0.68625 | 0.53463 | 0.39012
05h30 | 53.45 | 38.2 | 25.17 | 13.06 | 6.69 | 05h30 | 0.66812 | 0.4775 | 0.31462 | 0.16325 | 0.083625
06h30 | 34.04 | 18.2 | 13.5 | 2.58 | 0 | 06h30 | 0.4255 | 0.2275 | 0.16875 | 0.03225 | 0
07h30 | 66.7 | 48.48 | 36.76 | 24.23 | 18.3 | 07h30 | 0.83375 | 0.606 | 0.4595 | 0.30288 | 0.22875
08h30 | 68.82 | 49.07 | 36.76 | 24.23 | 18.3 | 08h30 | 0.86025 | 0.61338 | 0.4595 | 0.30288 | 0.22875
09h30 | 88.37 | 69.64 | 46.34 | 30.79 | 21.97 | 09h30 | 1.1046 | 0.8705 | 0.57925 | 0.38488 | 0.27463
10h30 | 105.29 | 87.27 | 55.75 | 41.47 | 31.55 | 10h30 | 1.3161 | 1.0909 | 0.69688 | 0.51838 | 0.39437
11h30 | 110.17 | 92.66 | 57.97 | 44.46 | 34.33 | 11h30 | 1.3771 | 1.1583 | 0.72462 | 0.55575 | 0.42912
12h30 | 116.46 | 99.39 | 61.56 | 48.77 | 38.46 | 12h30 | 1.4558 | 1.2424 | 0.7695 | 0.60962 | 0.48075
13h30 | 109.59 | 93 | 57.49 | 45.04 | 35.38 | 13h30 | 1.3699 | 1.1625 | 0.71862 | 0.563 | 0.44225
14h30 | 109 | 92.86 | 57.54 | 44.96 | 35.15 | 14h30 | 1.3625 | 1.1607 | 0.71925 | 0.562 | 0.43938
15h30 | 124.18 | 108.33 | 67.47 | 54.18 | 43.09 | 15h30 | 1.5522 | 1.3541 | 0.84337 | 0.67725 | 0.53863
16h30 | 148.25 | 132.57 | 82.86 | 68.78 | 55.52 | 16h30 | 1.8531 | 1.6571 | 1.0357 | 0.85975 | 0.694
17h30 | 153.19 | 155.63 | 99.67 | 85.33 | 69.62 | 17h30 | 1.9149 | 1.9454 | 1.2459 | 1.0666 | 0.87025
18h30 | 174.77 | 164.81 | 103.64 | 89.28 | 73.02 | 18h30 | 2.1846 | 2.0601 | 1.2955 | 1.116 | 0.91275
19h30 | 174.77 | 163.15 | 102.08 | 87.76 | 71.73 | 19h30 | 2.1846 | 2.0394 | 1.276 | 1.097 | 0.89663
20h30 | 170.51 | 154.61 | 96.6 | 82.78 | 67.46 | 20h30 | 2.1314 | 1.9326 | 1.2075 | 1.0348 | 0.84325
21h30 | 152.06 | 135.96 | 85.24 | 72 | 58.37 | 21h30 | 1.9007 | 1.6995 | 1.0655 | 0.9 | 0.72962
22h30 | 145.55 | 129.08 | 81.2 | 67.94 | 55.27 | 22h30 | 1.8194 | 1.6135 | 1.015 | 0.84925 | 0.69088
23h30 | 150.83 | 134.33 | 84.63 | 71.02 | 58.32 | 23h30 | 1.8854 | 1.6791 | 1.0579 | 0.88775 | 0.729
00h30 | 127.82 | 112.39 | 65.8 | 53.3 | 41.94 | 00h30 | 1.5978 | 1.4049 | 0.8225 | 0.66625 | 0.52425
01h30 | 114.73 | 100.78 | 61.93 | 50.74 | 40.25 | 01h30 | 1.4341 | 1.2597 | 0.77412 | 0.63425 | 0.50313
02h30 | 99.11 | 84.98 | 57.86 | 44.02 | 34.67 | 02h30 | 1.2389 | 1.0622 | 0.72325 | 0.55025 | 0.43338
03h30 | 92.4 | 77.35 | 48.4 | 37.08 | 28.16 | 03h30 | 1.155 | 0.96688 | 0.605 | 0.4635 | 0.352
04h30 | 89.59 | 73.79 | 48.4 | 37.08 | 28.16 | 04h30 | 1.1199 | 0.92237 | 0.605 | 0.4635 | 0.352
05h30 | 75.59 | 59.06 | 38.82 | 26.03 | 19.31 | 05h30 | 0.94488 | 0.73825 | 0.48525 | 0.32538 | 0.24138
06h30 | 53.03 | 50.98 | 38.82 | 26.03 | 19.31 | 06h30 | 0.66287 | 0.63725 | 0.48525 | 0.32538 | 0.24138
07h30 | 44.61 | 21.35 | 22.16 | 4.33 | 2.75 | 07h30 | 0.55763 | 0.26687 | 0.277 | 0.054125 | 0.034375
08h30 | 55.19 | 35.23 | 29.12 | 12.16 | 7.01 | 08h30 | 0.68988 | 0.44038 | 0.364 | 0.152 | 0.087625
09h30 | 83.35 | 61.64 | 43.99 | 27.65 | 21.13 | 09h30 | 1.0419 | 0.7705 | 0.54988 | 0.34563 | 0.26412
10h30 | 104.07 | 83.03 | 55.9 | 39.96 | 31.8 | 10h30 | 1.3009 | 1.0379 | 0.69875 | 0.4995 | 0.3975
11h30 | 116.08 | 95.34 | 62.48 | 47.14 | 37.82 | 11h30 | 1.451 | 1.1918 | 0.781 | 0.58925 | 0.47275
12h30 | 135.4 | 114.89 | 73.52 | 58.88 | 48.12 | 12h30 | 1.6925 | 1.4361 | 0.919 | 0.736 | 0.6015
13h30 | 150.62 | 137.22 | 86.78 | 72.05 | 59.49 | 13h30 | 1.8827 | 1.7152 | 1.0848 | 0.90063 | 0.74362
14h30 | 161.73 | 143.69 | 90.94 | 75.7 | 62.4 | 14h30 | 2.0216 | 1.7961 | 1.1367 | 0.94625 | 0.78
15h30 | 141.71 | 122.05 | 78.23 | 62.91 | 51.13 | 15h30 | 1.7714 | 1.5256 | 0.97788 | 0.78638 | 0.63913
16h30 | 79.98 | 60.76 | 44.16 | 27.39 | 23 | 16h30 | 0.99975 | 0.7595 | 0.552 | 0.34237 | 0.2875
17h30 | 72.75 | 52.59 | 36.22 | 21.43 | 13.39 | 17h30 | 0.90938 | 0.65738 | 0.45275 | 0.26787 | 0.16737
18h30 | 130.23 | 110.78 | 71.72 | 56.66 | 44.74 | 18h30 | 1.6279 | 1.3847 | 0.8965 | 0.70825 | 0.55925
19h30 | 132.31 | 113 | 73.02 | 57.87 | 45.97 | 19h30 | 1.6539 | 1.4125 | 0.91275 | 0.72337 | 0.57463
20h30 | 116.68 | 97.56 | 64.27 | 48.38 | 38.43 | 20h30 | 1.4585 | 1.2195 | 0.80337 | 0.60475 | 0.48037
21h30 | 75.56 | 56.58 | 40.26 | 25.74 | 23.81 | 21h30 | 0.9445 | 0.70725 | 0.50325 | 0.32175 | 0.29762
22h30 | 36.37 | 17.55 | 17.5 | 0 | 0 | 22h30 | 0.45463 | 0.21937 | 0.21875 | 0 | 0
23h30 | 37.39 | 18.71 | 18.66 | 0.24 | 0 | 23h30 | 0.46737 | 0.23387 | 0.23325 | 0.003 | 0
00h30 | 54.79 | 37.27 | 23.44 | 7.11 | 0 | 00h30 | 0.68488 | 0.46587 | 0.293 | 0.088875 | 0
01h30 | 93.9 | 77.91 | 50.11 | 36.44 | 27.33 | 01h30 | 1.1738 | 0.97388 | 0.62638 | 0.4555 | 0.34163
02h30 | 97.48 | 81.44 | 52.31 | 39.45 | 29.83 | 02h30 | 1.2185 | 1.018 | 0.65387 | 0.49312 | 0.37288
03h30 | 103.68 | 86.96 | 55.85 | 42.93 | 32.76 | 03h30 | 1.296 | 1.087 | 0.69812 | 0.53663 | 0.4095
04h30 | 104.87 | 87.65 | 56.55 | 43.25 | 33.24 | 04h30 | 1.3109 | 1.0956 | 0.70688 | 0.54063 | 0.4155
05h30 | 109.43 | 91.79 | 59.33 | 45.64 | 35.49 | 05h30 | 1.3679 | 1.1474 | 0.74162 | 0.5705 | 0.44362
06h30 | 123.4 | 105.42 | 67.92 | 53.55 | 42.66 | 06h30 | 1.5425 | 1.3177 | 0.849 | 0.66938 | 0.53325
07h30 | 138.79 | 126.75 | 86.56 | 68.83 | 59.22 | 07h30 | 1.7349 | 1.5844 | 1.082 | 0.86038 | 0.74025
08h30 | 100 | 86.6 | 66.3 | 50.72 | 49.07 | 08h30 | 1.25 | 1.0825 | 0.82875 | 0.634 | 0.61338
09h30 | 82.34 | 60.91 | 42.77 | 23.77 | 13.51 | 09h30 | 1.0292 | 0.76138 | 0.53463 | 0.29712 | 0.16887
10h30 | 82.34 | 60.91 | 42.77 | 24.84 | 17.13 | 10h30 | 1.0292 | 0.76138 | 0.53463 | 0.3105 | 0.21413
11h30 | 68.55 | 49.76 | 34.15 | 18.68 | 11.64 | 11h30 | 0.85688 | 0.622 | 0.42688 | 0.2335 | 0.1455
12h30 | 102.45 | 84.21 | 54.08 | 39.76 | 29.72 | 12h30 | 1.2806 | 1.0526 | 0.676 | 0.497 | 0.3715
13h30 | 62.48 | 45.01 | 30.48 | 22.16 | 21.7 | 13h30 | 0.781 | 0.56263 | 0.381 | 0.277 | 0.27125
14h30 | 83.33 | 66.34 | 43.96 | 26.8 | 15.45 | 14h30 | 1.0416 | 0.82925 | 0.5495 | 0.335 | 0.19312
15h30 | 154.75 | 149.9 | 94.82 | 79.24 | 64.53 | 15h30 | 1.9344 | 1.8738 | 1.1852 | 0.9905 | 0.80663
16h30 | 178.14 | 165.19 | 104.54 | 88.3 | 72.75 | 16h30 | 2.2268 | 2.0649 | 1.3068 | 1.1038 | 0.90938
17h30 | 151.8 | 135.54 | 86.92 | 71.1 | 58.25 | 17h30 | 1.8975 | 1.6943 | 1.0865 | 0.88875 | 0.72813
18h30 | 126.07 | 109.77 | 71.54 | 55.98 | 45.37 | 18h30 | 1.5759 | 1.3721 | 0.89425 | 0.69975 | 0.56712
19h30 | 120.26 | 104.31 | 68.42 | 52.74 | 42.58 | 19h30 | 1.5032 | 1.3039 | 0.85525 | 0.65925 | 0.53225
20h30 | 124.42 | 108.55 | 70.99 | 55.38 | 44.8 | 20h30 | 1.5553 | 1.3569 | 0.88738 | 0.69225 | 0.56
21h30 | 130.3 | 114.38 | 74.56 | 58.83 | 47.83 | 21h30 | 1.6287 | 1.4298 | 0.932 | 0.73538 | 0.59788
22h30 | 121.05 | 105 | 69.11 | 53.06 | 42.8 | 22h30 | 1.5131 | 1.3125 | 0.86387 | 0.66325 | 0.535
23h30 | 108.35 | 92.12 | 61.51 | 45.29 | 36.03 | 23h30 | 1.3544 | 1.1515 | 0.76887 | 0.56612 | 0.45038
00h30 | 89.23 | 73.86 | 44.6 | 29.48 | 28.06 | 00h30 | 1.1154 | 0.92325 | 0.5575 | 0.3685 | 0.35075
01h30 | 103.6 | 89.47 | 56.58 | 43.55 | 33.24 | 01h30 | 1.295 | 1.1184 | 0.70725 | 0.54438 | 0.4155
02h30 | 121.33 | 106.99 | 67.16 | 55.11 | 43.5 | 02h30 | 1.5166 | 1.3374 | 0.8395 | 0.68888 | 0.54375
03h30 | 133.98 | 118.83 | 74.56 | 62.42 | 49.21 | 03h30 | 1.6747 | 1.4854 | 0.932 | 0.78025 | 0.61513
04h30 | 141.29 | 125.58 | 78.78 | 66.55 | 52.77 | 04h30 | 1.7661 | 1.5697 | 0.98475 | 0.83188 | 0.65963
05h30 | 139.47 | 123.29 | 77.52 | 65.22 | 51.62 | 05h30 | 1.7434 | 1.5411 | 0.969 | 0.81525 | 0.64525
06h30 | 135.87 | 119.28 | 75.31 | 62.73 | 49.71 | 06h30 | 1.6984 | 1.491 | 0.94137 | 0.78412 | 0.62138
07h30 | 149.65 | 142.16 | 95.29 | 79.04 | 67.97 | 07h30 | 1.8706 | 1.777 | 1.1911 | 0.988 | 0.84962
08h30 | 165.06 | 148.07 | 96.27 | 78.35 | 65.88 | 08h30 | 2.0633 | 1.8509 | 1.2034 | 0.97937 | 0.8235
09h30 | 165.06 | 147.47 | 95.64 | 79.93 | 64.52 | 09h30 | 2.0633 | 1.8434 | 1.1955 | 0.99913 | 0.8065
10h30 | 165.26 | 146.61 | 93.71 | 78.6 | 62.99 | 10h30 | 2.0657 | 1.8326 | 1.1714 | 0.9825 | 0.78738
11h30 | 165.26 | 147.21 | 94.78 | 79.99 | 63.96 | 11h30 | 2.0657 | 1.8401 | 1.1847 | 0.99987 | 0.7995
12h30 | 163.36 | 145.82 | 92.08 | 77.8 | 61.79 | 12h30 | 2.042 | 1.8228 | 1.151 | 0.9725 | 0.77238
13h30 | 158.49 | 141.52 | 88.36 | 74.63 | 58.78 | 13h30 | 1.9811 | 1.769 | 1.1045 | 0.93288 | 0.73475
14h30 | 155.95 | 139.53 | 86.86 | 73.16 | 57.84 | 14h30 | 1.9494 | 1.7441 | 1.0857 | 0.9145 | 0.723
15h30 | 132.83 | 116.78 | 73.76 | 59.49 | 46.88 | 15h30 | 1.6604 | 1.4598 | 0.922 | 0.74362 | 0.586
16h30 | 105.57 | 89.71 | 58.46 | 50.16 | 41.68 | 16h30 | 1.3196 | 1.1214 | 0.73075 | 0.627 | 0.521
17h30 | 64.85 | 49.25 | 35 | 18.8 | 11.82 | 17h30 | 0.81063 | 0.61562 | 0.4375 | 0.235 | 0.14775
18h30 | 47.45 | 32.49 | 34.9 | 18.8 | 11.82 | 18h30 | 0.59313 | 0.40613 | 0.43625 | 0.235 | 0.14775
19h30 | 64.89 | 49.64 | 34.39 | 18.43 | 12.39 | 19h30 | 0.81112 | 0.6205 | 0.42988 | 0.23037 | 0.15488
20h30 | 67 | 51.78 | 36.54 | 21.75 | 15.69 | 20h30 | 0.8375 | 0.64725 | 0.45675 | 0.27187 | 0.19612
21h30 | 71.14 | 55.82 | 38.47 | 23.79 | 17.58 | 21h30 | 0.88925 | 0.69775 | 0.48087 | 0.29738 | 0.21975
22h30 | 62.29 | 53.69 | 36.32 | 20.46 | 14.28 | 22h30 | 0.77863 | 0.67112 | 0.454 | 0.25575 | 0.1785
23h30 | 40.33 | 24.09 | 19.42 | 5.47 | 1.45 | 23h30 | 0.50413 | 0.30112 | 0.24275 | 0.068375 | 0.018125
00h30 | 30.92 | 24.09 | 19.42 | 5.47 | 1.45 | 00h30 | 0.3865 | 0.30112 | 0.24275 | 0.068375 | 0.018125
01h30 | 30.34 | 14.1 | 8.66 | 0 | 0 | 01h30 | 0.37925 | 0.17625 | 0.10825 | 0 | 0
02h30 | 32.6 | 18.16 | 12.43 | 1.75 | 0 | 02h30 | 0.4075 | 0.227 | 0.15538 | 0.021875 | 0
03h30 | 43.54 | 28.48 | 18.97 | 9.37 | 4.01 | 03h30 | 0.54425 | 0.356 | 0.23713 | 0.11713 | 0.050125
04h30 | 57.28 | 41.51 | 27.28 | 17.06 | 11.3 | 04h30 | 0.716 | 0.51887 | 0.341 | 0.21325 | 0.14125
05h30 | 66.21 | 49.82 | 32.63 | 22.09 | 15.62 | 05h30 | 0.82763 | 0.62275 | 0.40787 | 0.27613 | 0.19525
06h30 | 69.02 | 52.13 | 34.55 | 23.14 | 16.78 | 06h30 | 0.86275 | 0.65163 | 0.43188 | 0.28925 | 0.20975
07h30 | 92.4 | 73.3 | 53.39 | 38.29 | 33.39 | 07h30 | 1.155 | 0.91625 | 0.66738 | 0.47863 | 0.41737
08h30 | 95.88 | 75.18 | 52.38 | 35.27 | 29.22 | 08h30 | 1.1985 | 0.93975 | 0.65475 | 0.44088 | 0.36525
09h30 | 102.91 | 82.86 | 57.24 | 41.16 | 32.43 | 09h30 | 1.2864 | 1.0357 | 0.7155 | 0.5145 | 0.40537
10h30 | 111.59 | 91.99 | 61.94 | 45.71 | 36.56 | 10h30 | 1.3949 | 1.1499 | 0.77425 | 0.57137 | 0.457
11h30 | 111.05 | 91.76 | 61.24 | 45.14 | 36 | 11h30 | 1.3881 | 1.147 | 0.7655 | 0.56425 | 0.45
12h30 | 102.32 | 83.32 | 55.6 | 40.02 | 31.41 | 12h30 | 1.279 | 1.0415 | 0.695 | 0.50025 | 0.39263
13h30 | 90.86 | 72.14 | 48.44 | 33.36 | 25.53 | 13h30 | 1.1358 | 0.90175 | 0.6055 | 0.417 | 0.31912
14h30 | 68.62 | 50.16 | 36.39 | 26.47 | 21.71 | 14h30 | 0.85775 | 0.627 | 0.45487 | 0.33087 | 0.27137
15h30 | 46.41 | 27.04 | 20.47 | 4.85 | 0 | 15h30 | 0.58013 | 0.338 | 0.25588 | 0.060625 | 0
16h30 | 60.17 | 42.1 | 29.75 | 16.61 | 10.46 | 16h30 | 0.75213 | 0.52625 | 0.37188 | 0.20763 | 0.13075
17h30 | 46.92 | 29.19 | 21.84 | 11.76 | 10.46 | 17h30 | 0.5865 | 0.36488 | 0.273 | 0.147 | 0.13075
18h30 | 38.79 | 21.14 | 16.8 | 4.22 | 0 | 18h30 | 0.48488 | 0.26425 | 0.21 | 0.05275 | 0
19h30 | 32.81 | 15.28 | 13.22 | 4.22 | 0 | 19h30 | 0.41013 | 0.191 | 0.16525 | 0.05275 | 0
20h30 | 43.23 | 25.88 | 19.96 | 6.45 | 1.82 | 20h30 | 0.54038 | 0.3235 | 0.2495 | 0.080625 | 0.02275
21h30 | 72.14 | 54.92 | 37.68 | 24.52 | 17.56 | 21h30 | 0.90175 | 0.6865 | 0.471 | 0.3065 | 0.2195
22h30 | 82.77 | 65.6 | 44.28 | 30.66 | 23.06 | 22h30 | 1.0346 | 0.82 | 0.5535 | 0.38325 | 0.28825
23h30 | 83.05 | 65.91 | 44.58 | 30.92 | 23.32 | 23h30 | 1.0381 | 0.82388 | 0.55725 | 0.3865 | 0.2915
00h30 | 73.03 | 57.03 | 33.16 | 20.91 | 16 | 00h30 | 0.91287 | 0.71288 | 0.4145 | 0.26138 | 0.2
01h30 | 83.19 | 68.73 | 42.82 | 32.59 | 24.13 | 01h30 | 1.0399 | 0.85913 | 0.53525 | 0.40737 | 0.30162
02h30 | 89.97 | 75.47 | 47.29 | 37.35 | 28.53 | 02h30 | 1.1246 | 0.94337 | 0.59113 | 0.46687 | 0.35663
03h30 | 100.94 | 85.69 | 54.04 | 43.55 | 34.23 | 03h30 | 1.2617 | 1.0711 | 0.6755 | 0.54438 | 0.42788
04h30 | 105.52 | 89.71 | 56.92 | 45.98 | 36.85 | 04h30 | 1.319 | 1.1214 | 0.7115 | 0.57475 | 0.46063
05h30 | 104.24 | 87.93 | 56.19 | 44.95 | 36.33 | 05h30 | 1.303 | 1.0991 | 0.70237 | 0.56188 | 0.45413
06h30 | 100.63 | 83.84 | 53.88 | 42.62 | 34.56 | 06h30 | 1.2579 | 1.048 | 0.6735 | 0.53275 | 0.432
07h30 | 117.85 | 98.98 | 68.86 | 54.61 | 47.99 | 07h30 | 1.4731 | 1.2372 | 0.86075 | 0.68263 | 0.59988
08h30 | 121.28 | 100.9 | 67.97 | 51.85 | 44.08 | 08h30 | 1.516 | 1.2612 | 0.84962 | 0.64812 | 0.551
09h30 | 126.64 | 106.85 | 71.75 | 56.84 | 46.93 | 09h30 | 1.583 | 1.3356 | 0.89687 | 0.7105 | 0.58662
10h30 | 132.83 | 113.42 | 74.72 | 59.89 | 49.58 | 10h30 | 1.6604 | 1.4178 | 0.934 | 0.74862 | 0.61975
11h30 | 134.03 | 122.91 | 79.75 | 65.04 | 53.91 | 11h30 | 1.6754 | 1.5364 | 0.99687 | 0.813 | 0.67388
12h30 | 150.18 | 132.96 | 85.33 | 70.77 | 58.83 | 12h30 | 1.8773 | 1.662 | 1.0666 | 0.88462 | 0.73538
13h30 | 150.18 | 138.95 | 88.77 | 74.15 | 61.81 | 13h30 | 1.8773 | 1.7369 | 1.1096 | 0.92688 | 0.77263
14h30 | 161.45 | 143.84 | 91.8 | 77.1 | 64.58 | 14h30 | 2.0181 | 1.798 | 1.1475 | 0.96375 | 0.80725
15h30 | 161.45 | 149.52 | 98.33 | 83.44 | 70.38 | 15h30 | 2.0181 | 1.869 | 1.2291 | 1.043 | 0.87975
16h30 | 170.63 | 153.76 | 99.36 | 83.98 | 71.09 | 16h30 | 2.1329 | 1.922 | 1.242 | 1.0497 | 0.88862
17h30 | 165.34 | 146.24 | 94.84 | 78.86 | 66.92 | 17h30 | 2.0667 | 1.828 | 1.1855 | 0.98575 | 0.8365
18h30 | 160.08 | 140.53 | 91.17 | 75.62 | 64.1 | 18h30 | 2.001 | 1.7566 | 1.1396 | 0.94525 | 0.80125
19h30 | 165.36 | 147.23 | 94.69 | 80.39 | 68.06 | 19h30 | 2.067 | 1.8404 | 1.1836 | 1.0049 | 0.85075
20h30 | 179.41 | 160.39 | 102.33 | 88.4 | 75.02 | 20h30 | 2.2426 | 2.0049 | 1.2791 | 1.105 | 0.93775
21h30 | 179.41 | 161.21 | 104.9 | 90.78 | 77.13 | 21h30 | 2.2426 | 2.0151 | 1.3113 | 1.1347 | 0.96413
22h30 | 189.85 | 170.68 | 109.15 | 94.96 | 81.04 | 22h30 | 2.3731 | 2.1335 | 1.3644 | 1.187 | 1.013
23h30 | 189.85 | 170.68 | 111.06 | 96.77 | 82.86 | 23h30 | 2.3731 | 2.1335 | 1.3882 | 1.2096 | 1.0357
00h30 | 164.35 | 145.98 | 88.26 | 74.79 | 62.43 | 00h30 | 2.0544 | 1.8248 | 1.1033 | 0.93488 | 0.78038
01h30 | 162.95 | 145.77 | 90.54 | 78.48 | 65.71 | 01h30 | 2.0369 | 1.8221 | 1.1318 | 0.981 | 0.82137
02h30 | 171.67 | 154.24 | 96.12 | 84.11 | 70.53 | 02h30 | 2.1459 | 1.928 | 1.2015 | 1.0514 | 0.88162
03h30 | 173.06 | 154.44 | 104.88 | 92.06 | 77.74 | 03h30 | 2.1633 | 1.9305 | 1.311 | 1.1507 | 0.97175
04h30 | 182.5 | 164.67 | 105.12 | 91.96 | 77.65 | 04h30 | 2.2812 | 2.0584 | 1.314 | 1.1495 | 0.97062
05h30 | 175.26 | 156.35 | 98.46 | 85.21 | 71.45 | 05h30 | 2.1907 | 1.9544 | 1.2308 | 1.0651 | 0.89312
06h30 | 172.18 | 152.62 | 96.01 | 82.57 | 68.91 | 06h30 | 2.1522 | 1.9078 | 1.2001 | 1.0321 | 0.86138
07h30 | 179.42 | 160.94 | 111.73 | 101.11 | 86.1 | 07h30 | 2.2428 | 2.0118 | 1.3966 | 1.2639 | 1.0762
08h30 | 196.85 | 175.64 | 115.59 | 99.12 | 83.9 | 08h30 | 2.4606 | 2.1955 | 1.4449 | 1.239 | 1.0488
09h30 | 190.78 | 168.65 | 109.68 | 93.58 | 79.6 | 09h30 | 2.3847 | 2.1081 | 1.371 | 1.1698 | 0.995
10h30 | 177.28 | 155.7 | 100.34 | 88.77 | 79.6 | 10h30 | 2.216 | 1.9463 | 1.2543 | 1.1096 | 0.995
11h30 | 167.05 | 146.16 | 93.87 | 78.62 | 65.32 | 11h30 | 2.0881 | 1.827 | 1.1734 | 0.98275 | 0.8165
12h30 | 160.06 | 139.71 | 89.42 | 78.62 | 65.32 | 12h30 | 2.0008 | 1.7464 | 1.1178 | 0.98275 | 0.8165
13h30 | 158.78 | 138.94 | 88.71 | 73.78 | 60.22 | 13h30 | 1.9848 | 1.7368 | 1.1089 | 0.92225 | 0.75275
14h30 | 158.51 | 139.13 | 88.94 | 73.78 | 60.39 | 14h30 | 1.9814 | 1.7391 | 1.1118 | 0.92225 | 0.75487
15h30 | 158.23 | 139.2 | 89.37 | 73.78 | 60.71 | 15h30 | 1.9779 | 1.74 | 1.1171 | 0.92225 | 0.75887
16h30 | 152.79 | 134.07 | 87.34 | 73.78 | 60.55 | 16h30 | 1.9099 | 1.6759 | 1.0917 | 0.92225 | 0.75687
17h30 | 145.83 | 127.43 | 83.14 | 67.39 | 55.65 | 17h30 | 1.8229 | 1.5929 | 1.0393 | 0.84237 | 0.69563
18h30 | 132.66 | 114.57 | 83.14 | 67.39 | 55.65 | 18h30 | 1.6583 | 1.4321 | 1.0393 | 0.84237 | 0.69563
19h30 | 118.43 | 100.53 | 67.78 | 50.45 | 41.26 | 19h30 | 1.4804 | 1.2566 | 0.84725 | 0.63062 | 0.51575
20h30 | 109.72 | 91.91 | 67.78 | 50.45 | 41.26 | 20h30 | 1.3715 | 1.1489 | 0.84725 | 0.63062 | 0.51575
21h30 | 101.32 | 83.5 | 57.28 | 39.93 | 32.55 | 21h30 | 1.2665 | 1.0437 | 0.716 | 0.49912 | 0.40687
22h30 | 95.09 | 77.18 | 57.28 | 39.93 | 32.55 | 22h30 | 1.1886 | 0.96475 | 0.716 | 0.49912 | 0.40687
23h30 | 93.68 | 75.64 | 52.78 | 35.34 | 28.83 | 23h30 | 1.171 | 0.9455 | 0.65975 | 0.44175 | 0.36038
00h30 | 51.29 | 52.16 | 52.78 | 35.34 | 28.83 | 00h30 | 0.64112 | 0.652 | 0.65975 | 0.44175 | 0.36038
01h30 | 28.54 | 9.62 | 6.32 | 0 | 0 | 01h30 | 0.35675 | 0.12025 | 0.079 | 0 | 0
02h30 | 29.4 | 13.02 | 12.08 | 0 | 0 | 02h30 | 0.3675 | 0.16275 | 0.151 | 0 | 0
03h30 | 34.54 | 16.22 | 13.35 | 0 | 0 | 03h30 | 0.43175 | 0.20275 | 0.16687 | 0 | 0
04h30 | 37.93 | 19.12 | 15.2 | 2.38 | 0 | 04h30 | 0.47413 | 0.239 | 0.19 | 0.02975 | 0
05h30 | 42.69 | 23.31 | 18.24 | 5.09 | 1.67 | 05h30 | 0.53363 | 0.29137 | 0.228 | 0.063625 | 0.020875
06h30 | 45.81 | 25.84 | 20.28 | 6.53 | 3.73 | 06h30 | 0.57263 | 0.323 | 0.2535 | 0.081625 | 0.046625
07h30 | 55.03 | 32.92 | 30.38 | 14.72 | 11.72 | 07h30 | 0.68788 | 0.4115 | 0.37975 | 0.184 | 0.1465
08h30 | 50.15 | 26.44 | 23.75 | 10.89 | 9.65 | 08h30 | 0.62687 | 0.3305 | 0.29688 | 0.13612 | 0.12062
09h30 | 66.3 | 43.18 | 33.36 | 18.03 | 12.32 | 09h30 | 0.82875 | 0.53975 | 0.417 | 0.22537 | 0.154
10h30 | 93.04 | 70.5 | 48.56 | 33.59 | 26.25 | 10h30 | 1.163 | 0.88125 | 0.607 | 0.41987 | 0.32812
11h30 | 106.82 | 84.69 | 56.03 | 41.29 | 32.12 | 11h30 | 1.3353 | 1.0586 | 0.70037 | 0.51612 | 0.4015
12h30 | 106.83 | 85.07 | 55.4 | 41.54 | 31.81 | 12h30 | 1.3354 | 1.0634 | 0.6925 | 0.51925 | 0.39763
13h30 | 98.37 | 77.01 | 50.31 | 36.61 | 27.64 | 13h30 | 1.2296 | 0.96262 | 0.62887 | 0.45763 | 0.3455
14h30 | 85.16 | 64.2 | 42.75 | 28.95 | 21.04 | 14h30 | 1.0645 | 0.8025 | 0.53438 | 0.36188 | 0.263
15h30 | 90.77 | 70.19 | 46.7 | 32.87 | 24.57 | 15h30 | 1.1346 | 0.87738 | 0.58375 | 0.41087 | 0.30712
16h30 | 101.36 | 81.12 | 53.83 | 39.81 | 31.24 | 16h30 | 1.267 | 1.014 | 0.67288 | 0.49762 | 0.3905
17h30 | 98.49 | 78.67 | 52.77 | 38.74 | 30.79 | 17h30 | 1.2311 | 0.98337 | 0.65963 | 0.48425 | 0.38488
18h30 | 92.65 | 73.27 | 49.57 | 35.96 | 28.59 | 18h30 | 1.1581 | 0.91587 | 0.61962 | 0.4495 | 0.35737
19h30 | 95.48 | 76.47 | 51.48 | 38.13 | 30.71 | 19h30 | 1.1935 | 0.95588 | 0.6435 | 0.47663 | 0.38388
20h30 | 105.02 | 86.27 | 57.55 | 43.94 | 35.99 | 20h30 | 1.3128 | 1.0784 | 0.71937 | 0.54925 | 0.44988
21h30 | 112.4 | 93.8 | 62.53 | 48.15 | 39.98 | 21h30 | 1.405 | 1.1725 | 0.78163 | 0.60188 | 0.49975
22h30 | 103.14 | 84.56 | 57.66 | 42.25 | 35.04 | 22h30 | 1.2893 | 1.057 | 0.72075 | 0.52812 | 0.438
23h30 | 88.05 | 69.37 | 48.93 | 33.24 | 27.1 | 23h30 | 1.1006 | 0.86713 | 0.61162 | 0.4155 | 0.33875
00h30 | 66.84 | 46.04 | 33.78 | 21.03 | 15.27 | 00h30 | 0.8355 | 0.5755 | 0.42225 | 0.26288 | 0.19087
01h30 | 62.41 | 45.78 | 30.54 | 17.52 | 13.06 | 01h30 | 0.78012 | 0.57225 | 0.38175 | 0.219 | 0.16325
02h30 | 64.01 | 47.23 | 32.24 | 20.16 | 15.84 | 02h30 | 0.80012 | 0.59037 | 0.403 | 0.252 | 0.198
03h30 | 76.23 | 58.76 | 39.61 | 26.71 | 21.51 | 03h30 | 0.95288 | 0.7345 | 0.49512 | 0.33387 | 0.26887
04h30 | 79.46 | 61.11 | 41.96 | 27.77 | 22.92 | 04h30 | 0.99325 | 0.76387 | 0.5245 | 0.34713 | 0.2865
05h30 | 68.56 | 49.46 | 35.32 | 21.14 | 16.96 | 05h30 | 0.857 | 0.61825 | 0.4415 | 0.26425 | 0.212
06h30 | 63.73 | 45.65 | 31.27 | 17.44 | 12.98 | 06h30 | 0.79663 | 0.57063 | 0.39087 | 0.218 | 0.16225
07h30 | 71.06 | 49.03 | 40.94 | 25.55 | 20.53 | 07h30 | 0.88825 | 0.61287 | 0.51175 | 0.31938 | 0.25662
08h30 | 71.06 | 49.03 | 40.94 | 25.55 | 20.32 | 08h30 | 0.88825 | 0.61287 | 0.51175 | 0.31938 | 0.254
09h30 | 62.95 | 39.5 | 30.2 | 15.86 | 10.87 | 09h30 | 0.78687 | 0.49375 | 0.3775 | 0.19825 | 0.13587
10h30 | 62.95 | 39.5 | 30.2 | 15.86 | 10.87 | 10h30 | 0.78687 | 0.49375 | 0.3775 | 0.19825 | 0.13587
11h30 | 27.13 | 4.42 | 5.11 | 0 | 0 | 11h30 | 0.33913 | 0.05525 | 0.063875 | 0 | 0
12h30 | 37.97 | 17.1 | 12.34 | 0.69 | 0 | 12h30 | 0.47463 | 0.21375 | 0.15425 | 0.008625 | 0
13h30 | 63.93 | 44.36 | 27.6 | 18.29 | 10.73 | 13h30 | 0.79912 | 0.5545 | 0.345 | 0.22862 | 0.13412
14h30 | 92.45 | 73.82 | 44.8 | 35.12 | 25.49 | 14h30 | 1.1556 | 0.92275 | 0.56 | 0.439 | 0.31862
15h30 | 107.97 | 89.92 | 55.2 | 44.47 | 34.06 | 15h30 | 1.3496 | 1.124 | 0.69 | 0.55588 | 0.42575
16h30 | 105.79 | 88.03 | 55.7 | 43.52 | 34.29 | 16h30 | 1.3224 | 1.1004 | 0.69625 | 0.544 | 0.42862
17h30 | 97.67 | 80.51 | 52.2 | 39.82 | 31.47 | 17h30 | 1.2209 | 1.0064 | 0.6525 | 0.49775 | 0.39337
18h30 | 80.81 | 64.39 | 42.78 | 30.64 | 23.67 | 18h30 | 1.0101 | 0.80488 | 0.53475 | 0.383 | 0.29587
19h30 | 53.11 | 37.23 | 26.71 | 14.36 | 9.53 | 19h30 | 0.66387 | 0.46537 | 0.33387 | 0.1795 | 0.11912
20h30 | 36.73 | 21.16 | 17.26 | 6.98 | 2.35 | 20h30 | 0.45913 | 0.2645 | 0.21575 | 0.08725 | 0.029375
21h30 | 30.1 | 14.66 | 13.46 | 0.77 | 0 | 21h30 | 0.37625 | 0.18325 | 0.16825 | 0.009625 | 0
22h30 | 27 | 11.55 | 11.55 | 0.77 | 0 | 22h30 | 0.3375 | 0.14438 | 0.14438 | 0.009625 | 0
23h30 | 27.17 | 11.59 | 11.59 | 0 | 0 | 23h30 | 0.33963 | 0.14488 | 0.14488 | 0 | 0
00h30 | 26.34 | 6.63 | 7.43 | 0 | 0 | 00h30 | 0.32925 | 0.082875 | 0.092875 | 0 | 0
01h30 | 23.83 | 10.49 | 7.21 | 0 | 0 | 01h30 | 0.29788 | 0.13112 | 0.090125 | 0 | 0
02h30 | 23.83 | 10.49 | 7.87 | 0 | 0 | 02h30 | 0.29788 | 0.13112 | 0.098375 | 0 | 0
03h30 | 28.7 | 14.15 | 10.86 | 0 | 0 | 03h30 | 0.35875 | 0.17688 | 0.13575 | 0 | 0
04h30 | 30.91 | 15.65 | 11.96 | 2.16 | 0 | 04h30 | 0.38638 | 0.19562 | 0.1495 | 0.027 | 0
05h30 | 35.32 | 19.26 | 14.64 | 4.07 | 0 | 05h30 | 0.4415 | 0.24075 | 0.183 | 0.050875 | 0
06h30 | 36.18 | 19.39 | 15.01 | 4.2 | 0.61 | 06h30 | 0.45225 | 0.24238 | 0.18762 | 0.0525 | 0.007625
07h30 | 46.15 | 27 | 25.33 | 11.8 | 10.15 | 07h30 | 0.57688 | 0.3375 | 0.31662 | 0.1475 | 0.12687
08h30 | 43.07 | 25.37 | 23.2 | 9.51 | 9.54 | 08h30 | 0.53838 | 0.31712 | 0.29 | 0.11887 | 0.11925
09h30 | 43.67 | 22.37 | 19.74 | 6.67 | 0.88 | 09h30 | 0.54587 | 0.27963 | 0.24675 | 0.083375 | 0.011
10h30 | 52.52 | 32.43 | 24.99 | 12.32 | 7.01 | 10h30 | 0.6565 | 0.40537 | 0.31238 | 0.154 | 0.087625
11h30 | 59.18 | 39.2 | 28.53 | 15.42 | 9.66 | 11h30 | 0.73975 | 0.49 | 0.35663 | 0.19275 | 0.12075
12h30 | 75.44 | 55.67 | 38.2 | 24.94 | 18.11 | 12h30 | 0.943 | 0.69588 | 0.4775 | 0.31175 | 0.22637
13h30 | 98.23 | 78.66 | 51.87 | 38.63 | 30.1 | 13h30 | 1.2279 | 0.98325 | 0.64838 | 0.48287 | 0.37625
14h30 | 116.7 | 97.33 | 63.19 | 49.79 | 39.72 | 14h30 | 1.4587 | 1.2166 | 0.78987 | 0.62238 | 0.4965
15h30 | 113.54 | 94.31 | 61.6 | 48.19 | 38.29 | 15h30 | 1.4192 | 1.1789 | 0.77 | 0.60237 | 0.47863
16h30 | 89.19 | 70.06 | 47.19 | 34.1 | 26.2 | 16h30 | 1.1149 | 0.87575 | 0.58988 | 0.42625 | 0.3275
17h30 | 72.45 | 53.47 | 37.3 | 24.5 | 18.04 | 17h30 | 0.90563 | 0.66838 | 0.46625 | 0.30625 | 0.2255
18h30 | 67.44 | 48.64 | 34.4 | 21.82 | 15.79 | 18h30 | 0.843 | 0.608 | 0.43 | 0.27275 | 0.19737
19h30 | 61.93 | 43.29 | 31.16 | 18.73 | 13.15 | 19h30 | 0.77412 | 0.54112 | 0.3895 | 0.23412 | 0.16437
20h30 | 64.55 | 46 | 32.8 | 20.39 | 14.66 | 20h30 | 0.80688 | 0.575 | 0.41 | 0.25488 | 0.18325
21h30 | 83.27 | 64.79 | 44.29 | 31.47 | 24.57 | 21h30 | 1.0409 | 0.80988 | 0.55363 | 0.39337 | 0.30712
22h30 | 99.68 | 81.21 | 54.57 | 40.99 | 33.18 | 22h30 | 1.246 | 1.0151 | 0.68212 | 0.51238 | 0.41475
23h30 | 105.36 | 86.84 | 58.38 | 44.15 | 36.19 | 23h30 | 1.317 | 1.0855 | 0.72975 | 0.55188 | 0.45238
00h30 | 76.95 | 59.5 | 37.52 | 23.43 | 16.2 | 00h30 | 0.96188 | 0.74375 | 0.469 | 0.29287 | 0.2025
01h30 | 58.72 | 42.67 | 28.42 | 17.11 | 12.09 | 01h30 | 0.734 | 0.53338 | 0.35525 | 0.21388 | 0.15113
02h30 | 53.89 | 36.52 | 28.42 | 17.11 | 12.09 | 02h30 | 0.67363 | 0.4565 | 0.35525 | 0.21388 | 0.15113
03h30 | 52.71 | 35.68 | 24.03 | 13.06 | 9.08 | 03h30 | 0.65887 | 0.446 | 0.30038 | 0.16325 | 0.1135
04h30 | 52.71 | 33.91 | 24.03 | 13.06 | 9.08 | 04h30 | 0.65887 | 0.42388 | 0.30038 | 0.16325 | 0.1135
05h30 | 39.08 | 20.78 | 16.22 | 3.98 | 1.31 | 05h30 | 0.4885 | 0.25975 | 0.20275 | 0.04975 | 0.016375
06h30 | 39.08 | 20.78 | 16.22 | 3.98 | 1.31 | 06h30 | 0.4885 | 0.25975 | 0.20275 | 0.04975 | 0.016375
07h30 | 60.16 | 38.92 | 33.73 | 19.06 | 14.94 | 07h30 | 0.752 | 0.4865 | 0.42163 | 0.23825 | 0.18675
08h30 | 60.16 | 38.92 | 33.73 | 19.06 | 14.94 | 08h30 | 0.752 | 0.4865 | 0.42163 | 0.23825 | 0.18675
09h30 | 53.55 | 31.97 | 26.53 | 12.37 | 7.48 | 09h30 | 0.66938 | 0.39963 | 0.33163 | 0.15463 | 0.0935
10h30 | 66.4 | 45.64 | 33.83 | 20.26 | 14.73 | 10h30 | 0.83 | 0.5705 | 0.42288 | 0.25325 | 0.18413
11h30 | 48.51 | 28.23 | 21.84 | 9.4 | 7.25 | 11h30 | 0.60637 | 0.35287 | 0.273 | 0.1175 | 0.090625
12h30 | 35.66 | 15.31 | 14.55 | 1.63 | 0 | 12h30 | 0.44575 | 0.19137 | 0.18188 | 0.020375 | 0
13h30 | 33.42 | 14.05 | 11.47 | 0.57 | 0 | 13h30 | 0.41775 | 0.17563 | 0.14338 | 0.007125 | 0
14h30 | 47.4 | 28.42 | 20.53 | 8.88 | 3.08 | 14h30 | 0.5925 | 0.35525 | 0.25662 | 0.111 | 0.0385
15h30 | 72.82 | 54.19 | 36.56 | 24.24 | 17.37 | 15h30 | 0.91025 | 0.67737 | 0.457 | 0.303 | 0.21713
16h30 | 58.83 | 39.06 | 27.5 | 15.81 | 14.29 | 16h30 | 0.73538 | 0.48825 | 0.34375 | 0.19762 | 0.17863
17h30 | 31.77 | 13.69 | 13.92 | 0 | 0 | 17h30 | 0.39713 | 0.17112 | 0.174 | 0 | 0
18h30 | 32.98 | 15.45 | 15.34 | 0.69 | 0 | 18h30 | 0.41225 | 0.19312 | 0.19175 | 0.008625 | 0
19h30 | 32.8 | 15.74 | 15.82 | 0.75 | 0 | 19h30 | 0.41 | 0.19675 | 0.19775 | 0.009375 | 0
20h30 | 32.19 | 15.25 | 15.29 | 0.75 | 0 | 20h30 | 0.40237 | 0.19062 | 0.19112 | 0.009375 | 0
21h30 | 31.28 | 14.46 | 14.49 | 0.68 | 0 | 21h30 | 0.391 | 0.18075 | 0.18113 | 0.0085 | 0
22h30 | 31.28 | 14.57 | 14.59 | 0.29 | 0 | 22h30 | 0.391 | 0.18213 | 0.18238 | 0.003625 | 0
23h30 | 77.86 | 61.22 | 42.78 | 28.04 | 19.09 | 23h30 | 0.97325 | 0.76525 | 0.53475 | 0.3505 | 0.23863
00h30 | 102.39 | 86.86 | 52.05 | 38.43 | 27.31 | 00h30 | 1.2799 | 1.0857 | 0.65063 | 0.48037 | 0.34137
01h30 | 99.57 | 85.55 | 53.6 | 42.33 | 30.97 | 01h30 | 1.2446 | 1.0694 | 0.67 | 0.52912 | 0.38712
02h30 | 96.43 | 82.5 | 51.59 | 41.59 | 29.64 | 02h30 | 1.2054 | 1.0312 | 0.64487 | 0.51987 | 0.3705
03h30 | 93.51 | 79.08 | 49.65 | 39.64 | 28.13 | 03h30 | 1.1689 | 0.9885 | 0.62062 | 0.4955 | 0.35163
04h30 | 86.44 | 71.72 | 45.3 | 35.3 | 24.61 | 04h30 | 1.0805 | 0.8965 | 0.56625 | 0.44125 | 0.30762
05h30 | 79.39 | 64.48 | 40.95 | 31.08 | 21.19 | 05h30 | 0.99238 | 0.806 | 0.51187 | 0.3885 | 0.26488
06h30 | 84.18 | 69.18 | 43.78 | 33.93 | 23.43 | 06h30 | 1.0522 | 0.86475 | 0.54725 | 0.42412 | 0.29287
07h30 | 114.62 | 98 | 66.65 | 54.39 | 43.91 | 07h30 | 1.4327 | 1.225 | 0.83313 | 0.67988 | 0.54888
08h30 | 112.52 | 94.88 | 62.14 | 48.9 | 38.3 | 08h30 | 1.4065 | 1.186 | 0.77675 | 0.61125 | 0.47875
09h30 | 104.01 | 87.43 | 57.31 | 46.03 | 32.97 | 09h30 | 1.3001 | 1.0929 | 0.71637 | 0.57537 | 0.41213
10h30 | 98.54 | 82.92 | 55.09 | 43.07 | 32.97 | 10h30 | 1.2317 | 1.0365 | 0.68863 | 0.53838 | 0.41213
11h30 | 83.56 | 68.87 | 43.5 | 33.4 | 21.39 | 11h30 | 1.0445 | 0.86087 | 0.54375 | 0.4175 | 0.26737
12h30 | 71.42 | 55.18 | 43.5 | 33.4 | 21.39 | 12h30 | 0.89275 | 0.68975 | 0.54375 | 0.4175 | 0.26737
13h30 | 75.88 | 62.56 | 37.39 | 28.04 | 15.08 | 13h30 | 0.9485 | 0.782 | 0.46737 | 0.3505 | 0.1885
14h30 | 86.12 | 74.25 | 44.1 | 35.85 | 21.22 | 14h30 | 1.0765 | 0.92812 | 0.55125 | 0.44812 | 0.26525
15h30 | 93.02 | 81.87 | 48.82 | 40.12 | 25.85 | 15h30 | 1.1627 | 1.0234 | 0.61025 | 0.5015 | 0.32312
16h30 | 97.72 | 86.89 | 53.09 | 43.43 | 29.84 | 16h30 | 1.2215 | 1.0861 | 0.66363 | 0.54287 | 0.373
17h30 | 94.08 | 83.79 | 51.87 | 42.02 | 29.13 | 17h30 | 1.176 | 1.0474 | 0.64838 | 0.52525 | 0.36412
18h30 | 93.89 | 84.15 | 52.26 | 42.38 | 29.47 | 18h30 | 1.1736 | 1.0519 | 0.65325 | 0.52975 | 0.36838
19h30 | 96.14 | 86.77 | 53.97 | 43.85 | 30.95 | 19h30 | 1.2018 | 1.0846 | 0.67463 | 0.54812 | 0.38688
20h30 | 90.76 | 81.57 | 50.97 | 40.72 | 28.76 | 20h30 | 1.1345 | 1.0196 | 0.63713 | 0.509 | 0.3595
21h30 | 80.89 | 71.75 | 45.12 | 34.91 | 24.26 | 21h30 | 1.0111 | 0.89687 | 0.564 | 0.43638 | 0.30325
22h30 | 73.66 | 64.46 | 40.84 | 30.55 | 21.07 | 22h30 | 0.92075 | 0.80575 | 0.5105 | 0.38188 | 0.26338
23h30 | 69.14 | 59.81 | 38.26 | 27.69 | 19.18 | 23h30 | 0.86425 | 0.74762 | 0.47825 | 0.34613 | 0.23975
00h30 | 66.99 | 55.22 | 34.17 | 23.7 | 14.09 | 00h30 | 0.83737 | 0.69025 | 0.42712 | 0.29625 | 0.17613
01h30 | 45.63 | 36.74 | 20.7 | 11.18 | 6.36 | 01h30 | 0.57037 | 0.45925 | 0.25875 | 0.13975 | 0.0795
02h30 | 53.42 | 45.5 | 27.64 | 19.16 | 12.88 | 02h30 | 0.66775 | 0.56875 | 0.3455 | 0.2395 | 0.161
03h30 | 57.2 | 49.18 | 30.15 | 21.58 | 13.62 | 03h30 | 0.715 | 0.61475 | 0.37688 | 0.26975 | 0.17025
04h30 | 51.31 | 42.44 | 26.5 | 17.88 | 10.94 | 04h30 | 0.64138 | 0.5305 | 0.33125 | 0.2235 | 0.13675
05h30 | 40.28 | 30.62 | 19.76 | 10.92 | 5.3 | 05h30 | 0.5035 | 0.38275 | 0.247 | 0.1365 | 0.06625
06h30 | 38.37 | 28.6 | 16.47 | 6.74 | 2 | 06h30 | 0.47963 | 0.3575 | 0.20588 | 0.08425 | 0.025
07h30 | 50.27 | 37.24 | 29.72 | 19.47 | 15.84 | 07h30 | 0.62838 | 0.4655 | 0.3715 | 0.24338 | 0.198
08h30 | 50.27 | 37.24 | 29.72 | 19.38 | 15.3 | 08h30 | 0.62838 | 0.4655 | 0.3715 | 0.24225 | 0.19125
09h30 | 46.24 | 31.83 | 23.22 | 10.42 | 4.76 | 09h30 | 0.578 | 0.39787 | 0.29025 | 0.13025 | 0.0595
10h30 | 56.17 | 42.27 | 28.65 | 16.74 | 10.75 | 10h30 | 0.70212 | 0.52838 | 0.35813 | 0.20925 | 0.13437
11h30 | 66.57 | 52.69 | 33.86 | 22.6 | 15.76 | 11h30 | 0.83213 | 0.65863 | 0.42325 | 0.2825 | 0.197
12h30 | 64.49 | 50.68 | 31.75 | 21.76 | 14.9 | 12h30 | 0.80612 | 0.6335 | 0.39687 | 0.272 | 0.18625
13h30 | 51.79 | 38.28 | 23.32 | 14.38 | 8.65 | 13h30 | 0.64738 | 0.4785 | 0.2915 | 0.17975 | 0.10812
14h30 | 43.93 | 30.13 | 20.01 | 9.14 | 4.4 | 14h30 | 0.54912 | 0.37662 | 0.25012 | 0.11425 | 0.055
15h30 | 43.43 | 30.04 | 18.85 | 8.93 | 4.43 | 15h30 | 0.54287 | 0.3755 | 0.23563 | 0.11163 | 0.055375
16h30 | 43.43 | 29.76 | 18.85 | 8.69 | 3.55 | 16h30 | 0.54287 | 0.372 | 0.23563 | 0.10862 | 0.044375
17h30 | 30.44 | 16.42 | 12.75 | 1.41 | 0 | 17h30 | 0.3805 | 0.20525 | 0.15937 | 0.017625 | 0
18h30 | 30.44 | 16.42 | 12.75 | 1.41 | 0 | 18h30 | 0.3805 | 0.20525 | 0.15937 | 0.017625 | 0
19h30 | 20.85 | 7.33 | 7.86 | 0 | 0 | 19h30 | 0.26062 | 0.091625 | 0.09825 | 0 | 0
20h30 | 29.67 | 16.2 | 13.31 | 0.59 | 0 | 20h30 | 0.37088 | 0.2025 | 0.16637 | 0.007375 | 0
21h30 | 37.79 | 24.1 | 18.38 | 6.24 | 1.05 | 21h30 | 0.47237 | 0.30125 | 0.22975 | 0.078 | 0.013125
22h30 | 31.86 | 17.71 | 14.9 | 5.65 | 1.05 | 22h30 | 0.39825 | 0.22137 | 0.18625 | 0.070625 | 0.013125
23h30 | 25.87 | 11.23 | 11.35 | 0 | 0 | 23h30 | 0.32338 | 0.14037 | 0.14188 | 0 | 0
00h30 | 22.98 | 8.74 | 9.38 | 0 | 0 | 00h30 | 0.28725 | 0.10925 | 0.11725 | 0 | 0
01h30 | 16.11 | 2.04 | 1.98 | 0 | 0 | 01h30 | 0.20137 | 0.0255 | 0.02475 | 0 | 0
02h30 | 22.78 | 9.41 | 7.83 | 0 | 0 | 02h30 | 0.28475 | 0.11762 | 0.097875 | 0 | 0
03h30 | 26.75 | 12.62 | 9.47 | 0 | 0 | 03h30 | 0.33437 | 0.15775 | 0.11837 | 0 | 0
04h30 | 27.83 | 12.58 | 9.55 | 0 | 0 | 04h30 | 0.34787 | 0.15725 | 0.11937 | 0 | 0
05h30 | 29.12 | 12.93 | 10 | 0 | 0 | 05h30 | 0.364 | 0.16162 | 0.125 | 0 | 0
06h30 | 26.7 | 9.72 | 8.3 | 0 | 0 | 06h30 | 0.33375 | 0.1215 | 0.10375 | 0 | 0
07h30 | 40.49 | 20.85 | 20.9 | 6.47 | 1.87 | 07h30 | 0.50613 | 0.26062 | 0.26125 | 0.080875 | 0.023375
08h30 | 36.68 | 16.73 | 16.68 | 6.47 | 1.87 | 08h30 | 0.4585 | 0.20913 | 0.2085 | 0.080875 | 0.023375
09h30 | 35.94 | 14.85 | 14.91 | 0 | 0 | 09h30 | 0.44925 | 0.18563 | 0.18638 | 0 | 0
10h30 | 34.41 | 14.85 | 14.91 | 0 | 0 | 10h30 | 0.43012 | 0.18563 | 0.18638 | 0 | 0
11h30 | 29.81 | 9.38 | 9.42 | 0 | 0 | 11h30 | 0.37262 | 0.11725 | 0.11775 | 0 | 0
12h30 | 29.81 | 9.38 | 9.42 | 0 | 0 | 12h30 | 0.37262 | 0.11725 | 0.11775 | 0 | 0
13h30 | 26.88 | 7.67 | 7.7 | 0 | 0 | 13h30 | 0.336 | 0.095875 | 0.09625 | 0 | 0
14h30 | 26.88 | 8.02 | 8.05 | 0 | 0 | 14h30 | 0.336 | 0.10025 | 0.10063 | 0 | 0
15h30 | 26.54 | 8.26 | 8.28 | 0 | 0 | 15h30 | 0.33175 | 0.10325 | 0.1035 | 0 | 0
16h30 | 46.98 | 29.08 | 21.01 | 6.6 | 0 | 16h30 | 0.58725 | 0.3635 | 0.26262 | 0.0825 | 0
17h30 | 70.57 | 53.14 | 35.71 | 22.34 | 13.58 | 17h30 | 0.88213 | 0.66425 | 0.44638 | 0.27925 | 0.16975
18h30 | 50.42 | 33.46 | 24.12 | 15.74 | 13.58 | 18h30 | 0.63025 | 0.41825 | 0.3015 | 0.19675 | 0.16975
19h30 | 26.84 | 10.25 | 10.27 | 0 | 0 | 19h30 | 0.3355 | 0.12812 | 0.12837 | 0 | 0
20h30 | 26.54 | 10.1 | 10.11 | 0 | 0 | 20h30 | 0.33175 | 0.12625 | 0.12637 | 0 | 0
21h30 | 26.11 | 10.06 | 10.08 | 0 | 0 | 21h30 | 0.32638 | 0.12575 | 0.126 | 0 | 0
22h30 | 26.11 | 10.14 | 10.15 | 0 | 0 | 22h30 | 0.32638 | 0.12675 | 0.12687 | 0 | 0
23h30 | 25.81 | 10.09 | 10.1 | 0 | 0 | 23h30 | 0.32262 | 0.12612 | 0.12625 | 0 | 0
00h30 | 25.81 | 8.67 | 8.69 | 0 | 0 | 00h30 | 0.32262 | 0.10837 | 0.10862 | 0 | 0
01h30 | 13.25 | 0 | 0 | 0 | 0 | 01h30 | 0.16562 | 0 | 0 | 0 | 0
02h30 | 15.63 | 2.82 | 2.82 | 0 | 0 | 02h30 | 0.19537 | 0.03525 | 0.03525 | 0 | 0
03h30 | 16.55 | 3.9 | 3.9 | 0 | 0 | 03h30 | 0.20688 | 0.04875 | 0.04875 | 0 | 0
04h30 | 18.16 | 4.85 | 4.85 | 0 | 0 | 04h30 | 0.227 | 0.060625 | 0.060625 | 0 | 0
05h30 | 18.8 | 5.07 | 5.07 | 0 | 0 | 05h30 | 0.235 | 0.063375 | 0.063375 | 0 | 0
06h30 | 19.18 | 5.12 | 5.12 | 0 | 0 | 06h30 | 0.23975 | 0.064 | 0.064 | 0 | 0
07h30 | 35 | 18.93 | 18.94 | 2.56 | 0 | 07h30 | 0.4375 | 0.23663 | 0.23675 | 0.032 | 0
08h30 | 52.77 | 35.33 | 26.35 | 11.59 | 3.09 | 08h30 | 0.65963 | 0.44162 | 0.32937 | 0.14488 | 0.038625
09h30 | 76.71 | 60.04 | 41.45 | 25.44 | 16.21 | 09h30 | 0.95888 | 0.7505 | 0.51812 | 0.318 | 0.20262
10h30 | 63.85 | 47.69 | 33.14 | 18.09 | 13.12 | 10h30 | 0.79812 | 0.59613 | 0.41425 | 0.22612 | 0.164
11h30 | 49.86 | 34.09 | 24.22 | 9.9 | 2.17 | 11h30 | 0.62325 | 0.42612 | 0.30275 | 0.12375 | 0.027125
12h30 | 51.76 | 36.35 | 25.12 | 11.28 | 4.63 | 12h30 | 0.647 | 0.45437 | 0.314 | 0.141 | 0.057875
13h30 | 59.05 | 43.96 | 29.57 | 15.85 | 8.47 | 13h30 | 0.73813 | 0.5495 | 0.36962 | 0.19812 | 0.10587
14h30 | 64.62 | 49.79 | 33.1 | 19.49 | 11.54 | 14h30 | 0.80775 | 0.62238 | 0.41375 | 0.24363 | 0.14425
15h30 | 67.05 | 52.39 | 34.98 | 21.13 | 13.09 | 15h30 | 0.83813 | 0.65487 | 0.43725 | 0.26412 | 0.16362
16h30 | 68.6 | 54.03 | 36.59 | 22.13 | 14.24 | 16h30 | 0.8575 | 0.67537 | 0.45737 | 0.27663 | 0.178
17h30 | 69.57 | 55.07 | 37.8 | 22.86 | 15.18 | 17h30 | 0.86962 | 0.68837 | 0.4725 | 0.28575 | 0.18975
18h30 | 79.24 | 64.81 | 43.95 | 28.87 | 20.63 | 18h30 | 0.9905 | 0.81012 | 0.54937 | 0.36088 | 0.25788
19h30 | 84.92 | 70.49 | 47.41 | 32.52 | 23.9 | 19h30 | 1.0615 | 0.88113 | 0.59262 | 0.4065 | 0.29875
20h30 | 74.49 | 59.98 | 41.18 | 26.28 | 18.57 | 20h30 | 0.93112 | 0.74975 | 0.51475 | 0.3285 | 0.23212
21h30 | 72.14 | 57.47 | 39.94 | 24.63 | 17.24 | 21h30 | 0.90175 | 0.71837 | 0.49925 | 0.30788 | 0.2155
22h30 | 73.56 | 58.66 | 40.89 | 25.31 | 17.95 | 22h30 | 0.9195 | 0.73325 | 0.51113 | 0.31638 | 0.22437
23h30 | 64.49 | 49.28 | 35.36 | 19.84 | 13.3 | 23h30 | 0.80612 | 0.616 | 0.442 | 0.248 | 0.16625
00h30 | 45.52 | 31.27 | 25.53 | 11.65 | 5.78 | 00h30 | 0.569 | 0.39087 | 0.31912 | 0.14563 | 0.07225
01h30 | 18.66 | 3.58 | 3.57 | 0 | 0 | 01h30 | 0.23325 | 0.04475 | 0.044625 | 0 | 0
02h30 | 35.51 | 21.58 | 16.09 | 0 | 0 | 02h30 | 0.44388 | 0.26975 | 0.20112 | 0 | 0
03h30 | 48.26 | 33.88 | 23.64 | 11.16 | 4.62 | 03h30 | 0.60325 | 0.4235 | 0.2955 | 0.1395 | 0.05775
04h30 | 36.47 | 21.11 | 16.35 | 11.16 | 4.62 | 04h30 | 0.45587 | 0.26388 | 0.20438 | 0.1395 | 0.05775
05h30 | 26.26 | 10.09 | 10.08 | 0 | 0 | 05h30 | 0.32825 | 0.12612 | 0.126 | 0 | 0
06h30 | 27.88 | 10.94 | 10.93 | 0 | 0 | 06h30 | 0.3485 | 0.13675 | 0.13662 | 0 | 0
07h30 | 44.88 | 25.55 | 25.54 | 8.86 | 3.94 | 07h30 | 0.561 | 0.31938 | 0.31925 | 0.11075 | 0.04925
08h30 | 38.85 | 19.47 | 19.46 | 8.86 | 3.94 | 08h30 | 0.48562 | 0.24338 | 0.24325 | 0.11075 | 0.04925
09h30 | 47.44 | 27.06 | 21.94 | 5.19 | 0 | 09h30 | 0.593 | 0.33825 | 0.27425 | 0.064875 | 0
10h30 | 67.95 | 48.45 | 33.08 | 18.32 | 11.98 | 10h30 | 0.84937 | 0.60562 | 0.4135 | 0.229 | 0.14975
11h30 | 88.72 | 69.36 | 45.01 | 30.45 | 22.62 | 11h30 | 1.109 | 0.867 | 0.56263 | 0.38062 | 0.28275
12h30 | 106.05 | 86.85 | 55.48 | 41.27 | 31.68 | 12h30 | 1.3256 | 1.0856 | 0.6935 | 0.51587 | 0.396
13h30 | 120.89 | 102.18 | 64.38 | 50.67 | 39.6 | 13h30 | 1.5111 | 1.2772 | 0.80475 | 0.63338 | 0.495
14h30 | 129.59 | 111.58 | 69.7 | 56.15 | 44.58 | 14h30 | 1.6199 | 1.3947 | 0.87125 | 0.70188 | 0.55725
15h30 | 125.27 | 107.59 | 67.97 | 53.58 | 42.71 | 15h30 | 1.5659 | 1.3449 | 0.84962 | 0.66975 | 0.53387
16h30 | 112.2 | 94.63 | 61.28 | 46.21 | 36.58 | 16h30 | 1.4025 | 1.1829 | 0.766 | 0.57763 | 0.45725
17h30 | 94.62 | 77.33 | 51.53 | 36.33 | 28.09 | 17h30 | 1.1827 | 0.96662 | 0.64412 | 0.45413 | 0.35113
18h30 | 92.43 | 75.45 | 50.97 | 35.04 | 27.22 | 18h30 | 1.1554 | 0.94312 | 0.63713 | 0.438 | 0.34025
19h30 | 110.95 | 94.12 | 63.02 | 45.71 | 37.03 | 19h30 | 1.3869 | 1.1765 | 0.78775 | 0.57137 | 0.46287
20h30 | 79.02 | 61.41 | 44.08 | 25.89 | 19.41 | 20h30 | 0.98775 | 0.76763 | 0.551 | 0.32362 | 0.24263
21h30 | 35.83 | 18.9 | 18.89 | 0.95 | 1.4 | 21h30 | 0.44788 | 0.23625 | 0.23613 | 0.011875 | 0.0175
22h30 | 76.25 | 59.43 | 43.29 | 24.87 | 17.16 | 22h30 | 0.95312 | 0.74287 | 0.54112 | 0.31088 | 0.2145
23h30 | 107.6 | 90.62 | 61.83 | 44.01 | 35.87 | 23h30 | 1.345 | 1.1327 | 0.77287 | 0.55012 | 0.44838
00h30 | 71.8 | 55.13 | 36.7 | 19.13 | 18.72 | 00h30 | 0.8975 | 0.68912 | 0.45875 | 0.23913 | 0.234
01h30 | 62.58 | 47 | 31.26 | 18.22 | 11.43 | 01h30 | 0.78225 | 0.5875 | 0.39075 | 0.22775 | 0.14288
02h30 | 59.21 | 43.24 | 31.26 | 18.22 | 11.55 | 02h30 | 0.74013 | 0.5405 | 0.39075 | 0.22775 | 0.14438
03h30 | 65.24 | 48.25 | 31.65 | 20.57 | 14.28 | 03h30 | 0.8155 | 0.60313 | 0.39563 | 0.25712 | 0.1785
04h30 | 78.96 | 61.27 | 40.12 | 28.72 | 21.53 | 04h30 | 0.987 | 0.76587 | 0.5015 | 0.359 | 0.26913
05h30 | 96.73 | 78.46 | 51 | 38.39 | 30.28 | 05h30 | 1.2091 | 0.98075 | 0.6375 | 0.47987 | 0.3785
06h30 | 106.16 | 87.35 | 57 | 43.34 | 34.97 | 06h30 | 1.327 | 1.0919 | 0.7125 | 0.54175 | 0.43712
07h30 | 121.65 | 100.66 | 70.95 | 54.4 | 47.59 | 07h30 | 1.5206 | 1.2583 | 0.88687 | 0.68 | 0.59488
08h30 | 117.95 | 95.39 | 65.46 | 47.85 | 39.97 | 08h30 | 1.4744 | 1.1924 | 0.81825 | 0.59813 | 0.49962
09h30 | 116.6 | 94.72 | 65.2 | 48.88 | 39.08 | 09h30 | 1.4575 | 1.184 | 0.815 | 0.611 | 0.4885
10h30 | 121.16 | 99.83 | 67.57 | 50.73 | 40.67 | 10h30 | 1.5145 | 1.2479 | 0.84462 | 0.63413 | 0.50838
11h30 | 83.78 | 62.88 | 44.88 | 27.87 | 20.58 | 11h30 | 1.0473 | 0.786 | 0.561 | 0.34837 | 0.25725
12h30 | 58.51 | 39.1 | 33.54 | 19.48 | 14.55 | 12h30 | 0.73137 | 0.48875 | 0.41925 | 0.2435 | 0.18188
13h30 | 32.96 | 10.99 | 11.92 | 0 | 0 | 13h30 | 0.412 | 0.13737 | 0.149 | 0 | 0
14h30 | 32.96 | 11.85 | 11.92 | 0 | 0 | 14h30 | 0.412 | 0.14813 | 0.149 | 0 | 0
15h30 | 28.18 | 10.21 | 10.39 | 0 | 0 | 15h30 | 0.35225 | 0.12762 | 0.12987 | 0 | 0
16h30 | 73.11 | 54.69 | 38.67 | 19.21 | 11.69 | 16h30 | 0.91387 | 0.68363 | 0.48337 | 0.24013 | 0.14613
17h30 | 112.73 | 94.51 | 63.83 | 45.73 | 37.09 | 17h30 | 1.4091 | 1.1814 | 0.79788 | 0.57163 | 0.46363
18h30 | 102.49 | 84.46 | 58.17 | 39.79 | 31.91 | 18h30 | 1.2811 | 1.0557 | 0.72713 | 0.49738 | 0.39887
19h30 | 66.45 | 48.56 | 36.89 | 18.51 | 12.94 | 19h30 | 0.83062 | 0.607 | 0.46113 | 0.23137 | 0.16175
20h30 | 38.01 | 20.09 | 20.16 | 5.24 | 6.43 | 20h30 | 0.47513 | 0.25112 | 0.252 | 0.0655 | 0.080375
21h30 | 38.98 | 20.89 | 20.94 | 1.25 | 0 | 21h30 | 0.48725 | 0.26112 | 0.26175 | 0.015625 | 0
22h30 | 56.33 | 37.92 | 31.14 | 12.84 | 7.27 | 22h30 | 0.70413 | 0.474 | 0.38925 | 0.1605 | 0.090875
23h30 | 72.44 | 53.61 | 40.22 | 22.56 | 16.82 | 23h30 | 0.9055 | 0.67012 | 0.50275 | 0.282 | 0.21025
00h30 | 48.84 | 29.75 | 24.14 | 10.96 | 9.55 | 00h30 | 0.6105 | 0.37188 | 0.30175 | 0.137 | 0.11937
01h30 | 36.65 | 19.48 | 15.6 | 0.15 | 0 | 01h30 | 0.45813 | 0.2435 | 0.195 | 0.001875 | 0
02h30 | 36.65 | 19.48 | 15.6 | 1.4 | 0 | 02h30 | 0.45813 | 0.2435 | 0.195 | 0.0175 | 0
03h30 | 41.63 | 22.48 | 18.38 | 5.21 | 0.49 | 03h30 | 0.52038 | 0.281 | 0.22975 | 0.065125 | 0.006125
04h30 | 45.91 | 26.23 | 20.67 | 7.19 | 3.67 | 04h30 | 0.57388 | 0.32788 | 0.25838 | 0.089875 | 0.045875
05h30 | 46.65 | 26.13 | 20.93 | 7.23 | 3.71 | 05h30 | 0.58313 | 0.32662 | 0.26162 | 0.090375 | 0.046375
06h30 | 42.37 | 22.37 | 18.63 | 4.01 | 0.53 | 06h30 | 0.52963 | 0.27963 | 0.23287 | 0.050125 | 0.006625
07h30 | 63.01 | 39.12 | 35.45 | 18.62 | 14.29 | 07h30 | 0.78763 | 0.489 | 0.44312 | 0.23275 | 0.17863
08h30 | 63.01 | 39.12 | 35.45 | 18.62 | 14.29 | 08h30 | 0.78763 | 0.489 | 0.44312 | 0.23275 | 0.17863
09h30 | 57.71 | 33.48 | 25.7 | 9.27 | 3.68 | 09h30 | 0.72137 | 0.4185 | 0.32125 | 0.11588 | 0.046
10h30 | 73.05 | 50.8 | 33.97 | 18.76 | 13.05 | 10h30 | 0.91312 | 0.635 | 0.42462 | 0.2345 | 0.16312
11h30 | 80.12 | 58.31 | 38.19 | 23.19 | 16.99 | 11h30 | 1.0015 | 0.72888 | 0.47737 | 0.28987 | 0.21238
12h30 | 79.5 | 57.93 | 37.86 | 23.85 | 17.14 | 12h30 | 0.99375 | 0.72413 | 0.47325 | 0.29812 | 0.21425
13h30 | 73.37 | 52.85 | 33.94 | 21.3 | 14.84 | 13h30 | 0.91712 | 0.66063 | 0.42425 | 0.26625 | 0.1855
14h30 | 82.41 | 62.9 | 40.04 | 26.93 | 19.89 | 14h30 | 1.0301 | 0.78625 | 0.5005 | 0.33663 | 0.24863
15h30 | 93.86 | 74.93 | 48.71 | 33.93 | 26.21 | 15h30 | 1.1732 | 0.93663 | 0.60888 | 0.42412 | 0.32762
16h30 | 94.13 | 75.81 | 50.66 | 35 | 27.39 | 16h30 | 1.1766 | 0.94763 | 0.63325 | 0.4375 | 0.34237
17h30 | 97.02 | 79.48 | 53.84 | 37.54 | 29.98 | 17h30 | 1.2127 | 0.9935 | 0.673 | 0.46925 | 0.37475
18h30 | 102.03 | 85.15 | 58.03 | 40.76 | 33.16 | 18h30 | 1.2754 | 1.0644 | 0.72537 | 0.5095 | 0.4145
19h30 | 87.2 | 70.69 | 49.61 | 32.43 | 25.75 | 19h30 | 1.09 | 0.88362 | 0.62013 | 0.40537 | 0.32188
20h30 | 58.19 | 37.15 | 29.41 | 12.77 | 8.04 | 20h30 | 0.72737 | 0.46437 | 0.36762 | 0.15962 | 0.1005
21h30 | 35.35 | 19.21 | 19.21 | 1.48 | 1.21 | 21h30 | 0.44188 | 0.24013 | 0.24013 | 0.0185 | 0.015125
22h30 | 37.97 | 21.17 | 21.17 | 2.14 | 0 | 22h30 | 0.47463 | 0.26462 | 0.26462 | 0.02675 | 0
23h30 | 70.5 | 53.75 | 40.74 | 22.16 | 16.24 | 23h30 | 0.88125 | 0.67188 | 0.50925 | 0.277 | 0.203
00h30 | 67.88 | 51.79 | 38.78 | 21.08 | 16.24 | 00h30 | 0.8485 | 0.64738 | 0.48475 | 0.2635 | 0.203
01h30 | 25.78 | 9.06 | 9.06 | 0 | 0 | 01h30 | 0.32225 | 0.11325 | 0.11325 | 0 | 0
02h30 | 28.2 | 12.09 | 12.09 | 0 | 0 | 02h30 | 0.3525 | 0.15113 | 0.15113 | 0 | 0
03h30 | 30 | 13.08 | 13.07 | 0 | 0 | 03h30 | 0.375 | 0.1635 | 0.16337 | 0 | 0
04h30 | 31.55 | 13.49 | 13.48 | 0 | 0 | 04h30 | 0.39437 | 0.16862 | 0.1685 | 0 | 0
05h30 | 32.71 | 13.69 | 13.68 | 0 | 0 | 05h30 | 0.40887 | 0.17112 | 0.171 | 0 | 0
06h30 | 34.58 | 14.73 | 14.72 | 0 | 0 | 06h30 | 0.43225 | 0.18413 | 0.184 | 0 | 0
07h30 | 52.8 | 30.56 | 30.55 | 12.53 | 7.77 | 07h30 | 0.66 | 0.382 | 0.38188 | 0.15662 | 0.097125
08h30 | 57.22 | 33.46 | 28.89 | 12.53 | 7.77 | 08h30 | 0.71525 | 0.41825 | 0.36112 | 0.15662 | 0.097125
09h30 | 48.4 | 25.95 | 21.38 | 5.67 | 0.74 | 09h30 | 0.605 | 0.32438 | 0.26725 | 0.070875 | 0.00925
10h30 | 48.35 | 27.11 | 19.35 | 5.67 | 0.74 | 10h30 | 0.60437 | 0.33887 | 0.24188 | 0.070875 | 0.00925
11h30 | 65.11 | 44.11 | 28.97 | 15.16 | 9.71 | 11h30 | 0.81388 | 0.55137 | 0.36212 | 0.1895 | 0.12137
12h30 | 54.88 | 35.57 | 28.17 | 15.16 | 9.71 | 12h30 | 0.686 | 0.44462 | 0.35213 | 0.1895 | 0.12137
13h30 | 51.52 | 30.81 | 17.66 | 6.4 | 0.21 | 13h30 | 0.644 | 0.38512 | 0.22075 | 0.08 | 0.002625
14h30 | 88.5 | 70.98 | 42.22 | 31.91 | 23.39 | 14h30 | 1.1062 | 0.88725 | 0.52775 | 0.39887 | 0.29237
15h30 | 111.34 | 94.76 | 57.51 | 45.64 | 36.4 | 15h30 | 1.3918 | 1.1845 | 0.71888 | 0.5705 | 0.455
16h30 | 105.04 | 88.33 | 56.06 | 41.47 | 33.87 | 16h30 | 1.313 | 1.1041 | 0.70075 | 0.51838 | 0.42338
17h30 | 91.33 | 75.16 | 49.76 | 34.39 | 27.5 | 17h30 | 1.1416 | 0.9395 | 0.622 | 0.42988 | 0.34375
18h30 | 96.42 | 81.06 | 54.19 | 38.1 | 30.7 | 18h30 | 1.2052 | 1.0132 | 0.67737 | 0.47625 | 0.38375
19h30 | 105.21 | 90.35 | 60.59 | 43.29 | 35.49 | 19h30 | 1.3151 | 1.1294 | 0.75738 | 0.54112 | 0.44362
20h30 | 101.41 | 86.69 | 58.76 | 41.33 | 33.77 | 20h30 | 1.2676 | 1.0836 | 0.7345 | 0.51663 | 0.42212
21h30 | 89.27 | 74.4 | 51.51 | 34.27 | 27.5 | 21h30 | 1.1159 | 0.93 | 0.64387 | 0.42838 | 0.34375
22h30 | 83.47 | 68.25 | 47.92 | 30.77 | 24.45 | 22h30 | 1.0434 | 0.85313 | 0.599 | 0.38462 | 0.30562
23h30 | 73.63 | 57.92 | 41.59 | 24.94 | 19.15 | 23h30 | 0.92038 | 0.724 | 0.51987 | 0.31175 | 0.23938
00h30 | 47.44 | 31.65 | 19.52 | 5.36 | 0.05 | 00h30 | 0.593 | 0.39563 | 0.244 | 0.067 | 0.000625
01h30 | 62.94 | 48.59 | 32.51 | 19.12 | 13.81 | 01h30 | 0.78675 | 0.60737 | 0.40637 | 0.239 | 0.17263
02h30 | 75.64 | 60.67 | 40.44 | 26.98 | 20.32 | 02h30 | 0.9455 | 0.75838 | 0.5055 | 0.33725 | 0.254
03h30 | 76.38 | 60.2 | 40.61 | 27 | 20.6 | 03h30 | 0.95475 | 0.7525 | 0.50762 | 0.3375 | 0.2575
04h30 | 84.11 | 66.9 | 45.02 | 30.95 | 24.43 | 04h30 | 1.0514 | 0.83625 | 0.56275 | 0.38688 | 0.30538
05h30 | 87.62 | 69.47 | 47.16 | 32.16 | 25.83 | 05h30 | 1.0953 | 0.86838 | 0.5895 | 0.402 | 0.32288
06h30 | 81.01 | 61.98 | 43.05 | 27.66 | 22.13 | 06h30 | 1.0126 | 0.77475 | 0.53812 | 0.34575 | 0.27663
07h30 | 98.05 | 76.57 | 58.02 | 39.63 | 34.76 | 07h30 | 1.2256 | 0.95713 | 0.72525 | 0.49538 | 0.4345
08h30 | 96.76 | 73.47 | 54.05 | 34.07 | 28.29 | 08h30 | 1.2095 | 0.91838 | 0.67563 | 0.42588 | 0.35363
09h30 | 112.21 | 89.35 | 63.23 | 45.05 | 37.06 | 09h30 | 1.4026 | 1.1169 | 0.79038 | 0.56312 | 0.46325
10h30 | 145.22 | 122.59 | 81.74 | 64.67 | 54.06 | 10h30 | 1.8153 | 1.5324 | 1.0217 | 0.80837 | 0.67575
11h30 | 145.54 | 143.97 | 93.52 | 77.48 | 64.86 | 11h30 | 1.8193 | 1.7996 | 1.169 | 0.9685 | 0.81075
12h30 | 155.89 | 139.11 | 89.97 | 74.31 | 61.75 | 12h30 | 1.9486 | 1.7389 | 1.1246 | 0.92888 | 0.77187
13h30 | 155.89 | 136.39 | 88.13 | 72.48 | 59.96 | 13h30 | 1.9486 | 1.7049 | 1.1016 | 0.906 | 0.7495
14h30 | 165.92 | 142.2 | 91.67 | 76.02 | 63.08 | 14h30 | 2.074 | 1.7775 | 1.1459 | 0.95025 | 0.7885
15h30 | 165.92 | 145.95 | 94.53 | 78.69 | 65.47 | 15h30 | 2.074 | 1.8244 | 1.1816 | 0.98362 | 0.81837
16h30 | 175.17 | 152.75 | 98.72 | 82.75 | 69.08 | 16h30 | 2.1896 | 1.9094 | 1.234 | 1.0344 | 0.8635
17h30 | 173.51 | 151.1 | 97.69 | 81.94 | 68.27 | 17h30 | 2.1689 | 1.8887 | 1.2211 | 1.0243 | 0.85337
18h30 | 174.16 | 152.34 | 98.32 | 82.74 | 68.83 | 18h30 | 2.177 | 1.9042 | 1.229 | 1.0342 | 0.86038
19h30 | 173.1 | 151.79 | 97.95 | 82.37 | 68.31 | 19h30 | 2.1637 | 1.8974 | 1.2244 | 1.0296 | 0.85388
20h30 | 157.94 | 136.99 | 88.85 | 73.68 | 60.59 | 20h30 | 1.9743 | 1.7124 | 1.1106 | 0.921 | 0.75738
21h30 | 151.23 | 130.59 | 84.74 | 70.06 | 57.47 | 21h30 | 1.8904 | 1.6324 | 1.0593 | 0.87575 | 0.71837
22h30 | 147.17 | 126.82 | 82.34 | 67.9 | 55.62 | 22h30 | 1.8396 | 1.5853 | 1.0292 | 0.84875 | 0.69525
23h30 | 135.57 | 115.52 | 75.48 | 61.18 | 49.82 | 23h30 | 1.6946 | 1.444 | 0.9435 | 0.76475 | 0.62275
00h30 | 107.27 | 88.69 | 59.35 | 45.43 | 38.07 | 00h30 | 1.3409 | 1.1086 | 0.74187 | 0.56788 | 0.47587
01h30 | 103.01 | 86.22 | 54.62 | 42.83 | 33.03 | 01h30 | 1.2876 | 1.0777 | 0.68275 | 0.53538 | 0.41287
02h30 | 102.82 | 86.17 | 54.62 | 43.84 | 34.45 | 02h30 | 1.2853 | 1.0771 | 0.68275 | 0.548 | 0.43062
03h30 | 109.19 | 92.07 | 58.2 | 47.12 | 37.07 | 03h30 | 1.3649 | 1.1509 | 0.7275 | 0.589 | 0.46337
04h30 | 118.01 | 100.69 | 63.86 | 52.14 | 41.65 | 04h30 | 1.4751 | 1.2586 | 0.79825 | 0.65175 | 0.52063
05h30 | 118.92 | 101.44 | 64.63 | 52.49 | 42.12 | 05h30 | 1.4865 | 1.268 | 0.80788 | 0.65612 | 0.5265
06h30 | 103.91 | 86.29 | 58.98 | 46.46 | 36.12 | 06h30 | 1.2989 | 1.0786 | 0.73725 | 0.58075 | 0.4515
07h30 | 112.31 | 93 | 65.95 | 51.73 | 42.17 | 07h30 | 1.4039 | 1.1625 | 0.82437 | 0.64663 | 0.52712
08h30 | 101.01 | 91 | 65.95 | 51.73 | 42.17 | 08h30 | 1.2626 | 1.1375 | 0.82437 | 0.64663 | 0.52712
09h30 | 104.31 | 85.24 | 58.33 | 42.98 | 34 | 09h30 | 1.3039 | 1.0655 | 0.72913 | 0.53725 | 0.425
10h30 | 110.11 | 91.13 | 61.28 | 46.95 | 37.46 | 10h30 | 1.3764 | 1.1391 | 0.766 | 0.58688 | 0.46825
11h30 | 100.98 | 81.84 | 54.65 | 40.92 | 32.03 | 11h30 | 1.2623 | 1.023 | 0.68312 | 0.5115 | 0.40037
12h30 | 87.48 | 75.95 | 51.7 | 36.95 | 28.57 | 12h30 | 1.0935 | 0.94937 | 0.64625 | 0.46187 | 0.35713
13h30 | 75.32 | 57.55 | 38.98 | 25.37 | 18.32 | 13h30 | 0.9415 | 0.71937 | 0.48725 | 0.31712 | 0.229
14h30 | 74.87 | 57.55 | 39.12 | 25.89 | 18.79 | 14h30 | 0.93588 | 0.71937 | 0.489 | 0.32362 | 0.23488
15h30 | 78.81 | 61.24 | 41.67 | 28.2 | 21.01 | 15h30 | 0.98513 | 0.7655 | 0.52087 | 0.3525 | 0.26262
16h30 | 83.88 | 66.66 | 45.75 | 31.4 | 24.24 | 16h30 | 1.0485 | 0.83325 | 0.57188 | 0.3925 | 0.303
17h30 | 84.92 | 67.97 | 47.22 | 32.21 | 25.3 | 17h30 | 1.0615 | 0.84962 | 0.59025 | 0.40263 | 0.31625
18h30 | 86.18 | 69.48 | 48.42 | 33.23 | 26.32 | 18h30 | 1.0773 | 0.8685 | 0.60525 | 0.41537 | 0.329
19h30 | 97.67 | 81.13 | 55.7 | 40.04 | 32.46 | 19h30 | 1.2209 | 1.0141 | 0.69625 | 0.5005 | 0.40575
20h30 | 124.11 | 107.6 | 71.98 | 55.63 | 46.51 | 20h30 | 1.5514 | 1.345 | 0.89975 | 0.69537 | 0.58137
21h30 | 119.38 | 102.76 | 69.27 | 52.77 | 43.98 | 21h30 | 1.4923 | 1.2845 | 0.86587 | 0.65963 | 0.54975
22h30 | 84.12 | 69.36 | 47.57 | 32.46 | 25.21 | 22h30 | 1.0515 | 0.867 | 0.59462 | 0.40575 | 0.31512
23h30 | 35.84 | 17.22 | 18.7 | 0.62 | 0 | 23h30 | 0.448 | 0.21525 | 0.23375 | 0.00775 | 0
00h30 | 35.84 | 17.22 | 18.7 | 0.62 | 0 | 00h30 | 0.448 | 0.21525 | 0.23375 | 0.00775 | 0
01h30 | 25.34 | 9.6 | 9.74 | 0 | 0 | 01h30 | 0.31675 | 0.12 | 0.12175 | 0 | 0
02h30 | 27.63 | 12.08 | 12.32 | 0 | 0 | 02h30 | 0.34537 | 0.151 | 0.154 | 0 | 0
03h30 | 29.35 | 13.27 | 13.42 | 0 | 0 | 03h30 | 0.36688 | 0.16587 | 0.16775 | 0 | 0
04h30 | 33.26 | 16.25 | 16.4 | 0 | 0 | 04h30 | 0.41575 | 0.20312 | 0.205 | 0 | 0
05h30 | 34.71 | 16.83 | 16.98 | 0 | 0 | 05h30 | 0.43388 | 0.21038 | 0.21225 | 0 | 0
06h30 | 33.95 | 15.31 | 15.44 | 0 | 0 | 06h30 | 0.42438 | 0.19137 | 0.193 | 0 | 0
07h30 | 50.55 | 29.83 | 29.98 | 12.57 | 8.23 | 07h30 | 0.63187 | 0.37288 | 0.37475 | 0.15712 | 0.10287
08h30 | 47.78 | 25.89 | 25.95 | 12.57 | 8.23 | 08h30 | 0.59725 | 0.32362 | 0.32438 | 0.15712 | 0.10287
09h30 | 82.61 | 60.58 | 46.52 | 27.09 | 19.85 | 09h30 | 1.0326 | 0.75725 | 0.5815 | 0.33863 | 0.24813
10h30 | 108.37 | 86.68 | 60.62 | 43.59 | 34.65 | 10h30 | 1.3546 | 1.0835 | 0.75775 | 0.54487 | 0.43312
11h30 | 108.76 | 87.28 | 60.14 | 43.11 | 34.15 | 11h30 | 1.3595 | 1.091 | 0.75175 | 0.53887 | 0.42688
12h30 | 80.34 | 61.19 | 46.04 | 26.61 | 19.36 | 12h30 | 1.0043 | 0.76487 | 0.5755 | 0.33263 | 0.242
13h30 | 34.83 | 13.75 | 13.83 | 0 | 0 | 13h30 | 0.43538 | 0.17188 | 0.17288 | 0 | 0
14h30 | 34.83 | 13.75 | 13.83 | 0 | 0 | 14h30 | 0.43538 | 0.17188 | 0.17288 | 0 | 0
15h30 | 28.75 | 9.35 | 9.41 | 0 | 0 | 15h30 | 0.35938 | 0.11688 | 0.11762 | 0 | 0
16h30 | 32.54 | 13.42 | 13.48 | 0 | 0 | 16h30 | 0.40675 | 0.16775 | 0.1685 | 0 | 0
17h30 | 34.43 | 15.69 | 15.74 | 0 | 0 | 17h30 | 0.43038 | 0.19612 | 0.19675 | 0 | 0
18h30 | 58.89 | 40.61 | 31 | 15.04 | 8.34 | 18h30 | 0.73613 | 0.50762 | 0.3875 | 0.188 | 0.10425
19h30 | 93.84 | 76.02 | 52.63 | 36.03 | 28.19 | 19h30 | 1.173 | 0.95025 | 0.65787 | 0.45038 | 0.35237
20h30 | 114.19 | 96.67 | 65.63 | 48.13 | 38.97 | 20h30 | 1.4274 | 1.2084 | 0.82037 | 0.60162 | 0.48712
21h30 | 116 | 98.61 | 67.18 | 49.3 | 40.27 | 21h30 | 1.45 | 1.2326 | 0.83975 | 0.61625 | 0.50338
22h30 | 101.2 | 83.78 | 58.25 | 40.73 | 32.75 | 22h30 | 1.265 | 1.0473 | 0.72813 | 0.50913 | 0.40937
23h30 | 92.22 | 74.66 | 52.71 | 35.49 | 28.21 | 23h30 | 1.1527 | 0.93325 | 0.65887 | 0.44362 | 0.35263
00h30 | 69.03 | 52.33 | 33.16 | 17.16 | 16.6 | 00h30 | 0.86287 | 0.65412 | 0.4145 | 0.2145 | 0.2075
01h30 | 68.86 | 53.27 | 36.21 | 22.36 | 15.59 | 01h30 | 0.86075 | 0.66587 | 0.45262 | 0.2795 | 0.19487
02h30 | 58.25 | 40.8 | 32.36 | 22.13 | 15.59 | 02h30 | 0.72813 | 0.51 | 0.4045 | 0.27663 | 0.19487
03h30 | 27.39 | 9.58 | 9.6 | 0 | 0 | 03h30 | 0.34237 | 0.11975 | 0.12 | 0 | 0
04h30 | 29.15 | 11.7 | 11.72 | 0 | 0 | 04h30 | 0.36438 | 0.14625 | 0.1465 | 0 | 0
05h30 | 27.66 | 9.92 | 9.94 | 0 | 0 | 05h30 | 0.34575 | 0.124 | 0.12425 | 0 | 0
06h30 | 27.53 | 9.16 | 9.18 | 0 | 0 | 06h30 | 0.34413 | 0.1145 | 0.11475 | 0 | 0
07h30 | 46.1 | 25.61 | 24.67 | 11.11 | 6.24 | 07h30 | 0.57625 | 0.32012 | 0.30838 | 0.13887 | 0.078
08h30 | 44.47 | 24.25 | 23.31 | 11.11 | 6.24 | 08h30 | 0.55588 | 0.30312 | 0.29137 | 0.13887 | 0.078
09h30 | 41.47 | 19.78 | 18.71 | 4.68 | 0 | 09h30 | 0.51838 | 0.24725 | 0.23387 | 0.0585 | 0
10h30 | 61.1 | 40.14 | 30.13 | 16.95 | 10.83 | 10h30 | 0.76375 | 0.50175 | 0.37662 | 0.21188 | 0.13537
11h30 | 110.74 | 90.1 | 59.58 | 45.94 | 35.84 | 11h30 | 1.3842 | 1.1262 | 0.74475 | 0.57425 | 0.448
12h30 | 132.6 | 112.42 | 72.66 | 59.16 | 47.15 | 12h30 | 1.6575 | 1.4053 | 0.90825 | 0.7395 | 0.58937
13h30 | 125.4 | 105.67 | 68.56 | 54.9 | 43.64 | 13h30 | 1.5675 | 1.3209 | 0.857 | 0.68625 | 0.5455
14h30 | 122.05 | 102.71 | 67.1 | 52.95 | 42.14 | 14h30 | 1.5256 | 1.2839 | 0.83875 | 0.66187 | 0.52675
15h30 | 120.28 | 101.27 | 66.51 | 52.38 | 41.73 | 15h30 | 1.5035 | 1.2659 | 0.83137 | 0.65475 | 0.52163
16h30 | 107.49 | 88.81 | 59.17 | 45.27 | 35.76 | 16h30 | 1.3436 | 1.1101 | 0.73962 | 0.56588 | 0.447
17h30 | 94.26 | 75.91 | 51.44 | 37.8 | 29.46 | 17h30 | 1.1783 | 0.94888 | 0.643 | 0.4725 | 0.36825
18h30 | 103.24 | 85.2 | 57.03 | 43.42 | 34.42 | 18h30 | 1.2905 | 1.065 | 0.71288 | 0.54275 | 0.43025
19h30 | 122.68 | 104.9 | 68.92 | 55.17 | 44.69 | 19h30 | 1.5335 | 1.3113 | 0.8615 | 0.68963 | 0.55863
20h30 | 120.56 | 102.95 | 67.61 | 54.18 | 43.86 | 20h30 | 1.507 | 1.2869 | 0.84513 | 0.67725 | 0.54825
21h30 | 107.71 | 90.19 | 59.68 | 46.8 | 37.47 | 21h30 | 1.3464 | 1.1274 | 0.746 | 0.585 | 0.46837
22h30 | 109.11 | 91.65 | 60.38 | 47.81 | 38.39 | 22h30 | 1.3639 | 1.1456 | 0.75475 | 0.59762 | 0.47987
23h30 | 104.18 | 86.76 | 57.33 | 44.95 | 35.93 | 23h30 | 1.3022 | 1.0845 | 0.71662 | 0.56188 | 0.44912
00h30 | 74.56 | 58.26 | 36.63 | 22.89 | 16.22 | 00h30 | 0.932 | 0.72825 | 0.45787 | 0.28613 | 0.20275
01h30 | 82.22 | 67.4 | 42.15 | 32.6 | 24.45 | 01h30 | 1.0277 | 0.8425 | 0.52687 | 0.4075 | 0.30562
02h30 | 86.41 | 71.54 | 45.03 | 35.88 | 27.63 | 02h30 | 1.0801 | 0.89425 | 0.56288 | 0.4485 | 0.34537
03h30 | 77.95 | 62.41 | 39.78 | 30.45 | 23.28 | 03h30 | 0.97437 | 0.78012 | 0.49725 | 0.38062 | 0.291
04h30 | 69.77 | 50.71 | 36.91 | 27.17 | 20.1 | 04h30 | 0.87213 | 0.63387 | 0.46137 | 0.33963 | 0.25125
05h30 | 64.79 | 48.21 | 31.29 | 19.68 | 15.27 | 05h30 | 0.80988 | 0.60262 | 0.39113 | 0.246 | 0.19087
06h30 | 76.12 | 59.43 | 39.25 | 28.32 | 22.03 | 06h30 | 0.9515 | 0.74287 | 0.49062 | 0.354 | 0.27537
07h30 | 99.44 | 81.12 | 58.02 | 44.82 | 37.88 | 07h30 | 1.243 | 1.014 | 0.72525 | 0.56025 | 0.4735
08h30 | 96.52 | 76.68 | 53.24 | 38.98 | 31.34 | 08h30 | 1.2065 | 0.9585 | 0.6655 | 0.48725 | 0.39175
09h30 | 92.57 | 73.29 | 51.28 | 38.39 | 30.77 | 09h30 | 1.1571 | 0.91612 | 0.641 | 0.47987 | 0.38462
10h30 | 96.6 | 77.71 | 52.8 | 40.38 | 32.41 | 10h30 | 1.2075 | 0.97137 | 0.66 | 0.50475 | 0.40513
11h30 | 101.04 | 82.42 | 54.84 | 42.75 | 34.35 | 11h30 | 1.263 | 1.0303 | 0.6855 | 0.53438 | 0.42938
12h30 | 98.05 | 79.67 | 52.68 | 40.84 | 32.56 | 12h30 | 1.2256 | 0.99587 | 0.6585 | 0.5105 | 0.407
13h30 | 91.95 | 73.78 | 48.94 | 37.14 | 29.31 | 13h30 | 1.1494 | 0.92225 | 0.61175 | 0.46425 | 0.36638
14h30 | 87.92 | 69.89 | 46.66 | 34.86 | 29.25 | 14h30 | 1.099 | 0.87362 | 0.58325 | 0.43575 | 0.36562
15h30 | 88.57 | 70.64 | 47.4 | 35.48 | 27.74 | 15h30 | 1.1071 | 0.883 | 0.5925 | 0.4435 | 0.34675
16h30 | 86.68 | 68.89 | 47.14 | 34.87 | 27.74 | 16h30 | 1.0835 | 0.86113 | 0.58925 | 0.43588 | 0.34675
17h30 | 79.19 | 61.55 | 42.52 | 30.05 | 23.08 | 17h30 | 0.98987 | 0.76938 | 0.5315 | 0.37562 | 0.2885
18h30 | 75.66 | 58.73 | 42.52 | 30.05 | 23.08 | 18h30 | 0.94575 | 0.73413 | 0.5315 | 0.37562 | 0.2885
19h30 | 64.29 | 46.26 | 32.67 | 20.41 | 14.75 | 19h30 | 0.80363 | 0.57825 | 0.40837 | 0.25512 | 0.18438
20h30 | 64.29 | 46.26 | 32.67 | 20.41 | 14.75 | 20h30 | 0.80363 | 0.57825 | 0.40837 | 0.25512 | 0.18438
21h30 | 54.61 | 36.98 | 27.62 | 15.43 | 10.79 | 21h30 | 0.68263 | 0.46225 | 0.34525 | 0.19287 | 0.13487
22h30 | 54.61 | 36.98 | 27.62 | 15.43 | 10.79 | 22h30 | 0.68263 | 0.46225 | 0.34525 | 0.19287 | 0.13487
23h30 | 45.29 | 27.26 | 22 | 9.38 | 5.34 | 23h30 | 0.56612 | 0.34075 | 0.275 | 0.11725 | 0.06675
00h30 | 45.29 | 27.26 | 22 | 9.38 | 5.34 | 00h30 | 0.56612 | 0.34075 | 0.275 | 0.11725 | 0.06675
01h30 | 62 | 46.65 | 29.88 | 18.83 | 13.65 | 01h30 | 0.775 | 0.58313 | 0.3735 | 0.23538 | 0.17062
02h30 | 72.13 | 56.78 | 36.77 | 26.92 | 21.1 | 02h30 | 0.90163 | 0.70975 | 0.45963 | 0.3365 | 0.26375
03h30 | 80.34 | 64.28 | 41.23 | 31.51 | 24.64 | 03h30 | 1.0043 | 0.8035 | 0.51538 | 0.39387 | 0.308
04h30 | 87.55 | 70.82 | 45.53 | 35.32 | 28.21 | 04h30 | 1.0944 | 0.88525 | 0.56912 | 0.4415 | 0.35263
05h30 | 94.63 | 77.36 | 49.74 | 39.15 | 31.7 | 05h30 | 1.1829 | 0.967 | 0.62175 | 0.48938 | 0.39625
06h30 | 90.88 | 73.14 | 47.39 | 36.74 | 29.62 | 06h30 | 1.136 | 0.91425 | 0.59237 | 0.45925 | 0.37025
07h30 | 96.02 | 76.18 | 54.99 | 42.55 | 35.57 | 07h30 | 1.2003 | 0.95225 | 0.68737 | 0.53187 | 0.44462
08h30 | 92.89 | 71.52 | 49.96 | 36.51 | 28.99 | 08h30 | 1.1611 | 0.894 | 0.6245 | 0.45637 | 0.36238
09h30 | 96.88 | 76.13 | 52.9 | 40.4 | 32.91 | 09h30 | 1.211 | 0.95163 | 0.66125 | 0.505 | 0.41137
10h30 | 93.99 | 73.7 | 50.47 | 38.19 | 30.86 | 10h30 | 1.1749 | 0.92125 | 0.63087 | 0.47737 | 0.38575
11h30 | 87.1 | 67.14 | 45.83 | 33.82 | 26.88 | 11h30 | 1.0888 | 0.83925 | 0.57288 | 0.42275 | 0.336
12h30 | 79.6 | 61.79 | 44.46 | 32.6 | 26.57 | 12h30 | 0.995 | 0.77238 | 0.55575 | 0.4075 | 0.33213
13h30 | 78.65 | 59.27 | 40.32 | 28.22 | 21.67 | 13h30 | 0.98313 | 0.74087 | 0.504 | 0.35275 | 0.27087
14h30 | 78.58 | 59.27 | 40.32 | 28.22 | 21.67 | 14h30 | 0.98225 | 0.74087 | 0.504 | 0.35275 | 0.27087
15h30 | 73.68 | 54.22 | 37.95 | 25.44 | 19.62 | 15h30 | 0.921 | 0.67775 | 0.47437 | 0.318 | 0.24525
16h30 | 73.82 | 54.71 | 38.99 | 25.65 | 19.88 | 16h30 | 0.92275 | 0.68388 | 0.48738 | 0.32062 | 0.2485
17h30 | 78.34 | 59.62 | 42.42 | 28.54 | 22.51 | 17h30 | 0.97925 | 0.74525 | 0.53025 | 0.35675 | 0.28137
18h30 | 78.19 | 59.13 | 41.38 | 28.33 | 22.24 | 18h30 | 0.97737 | 0.73913 | 0.51725 | 0.35413 | 0.278
19h30 | 73.42 | 54.49 | 39.2 | 25.85 | 20.29 | 19h30 | 0.91775 | 0.68112 | 0.49 | 0.32312 | 0.25362
20h30 | 82.54 | 63.7 | 45.09 | 31.11 | 25.11 | 20h30 | 1.0317 | 0.79625 | 0.56363 | 0.38888 | 0.31388
21h30 | 77.78 | 58.98 | 42.63 | 28.04 | 22.51 | 21h30 | 0.97225 | 0.73725 | 0.53287 | 0.3505 | 0.28137
22h30 | 68.67 | 49.77 | 36.74 | 22.78 | 17.68 | 22h30 | 0.85837 | 0.62213 | 0.45925 | 0.28475 | 0.221
23h30 | 36.3 | 15.86 | 17.03 | 1.47 | 0 | 23h30 | 0.45375 | 0.19825 | 0.21288 | 0.018375 | 0
00h30 | 36.3 | 17.92 | 17.03 | 1.47 | 0 | 00h30 | 0.45375 | 0.224 | 0.21288 | 0.018375 | 0
01h30 | 45.42 | 28.79 | 20.43 | 8.54 | 4.48 | 01h30 | 0.56775 | 0.35988 | 0.25538 | 0.10675 | 0.056
02h30 | 45.42 | 26.73 | 20.43 | 8.54 | 4.48 | 02h30 | 0.56775 | 0.33413 | 0.25538 | 0.10675 | 0.056
03h30 | 33.22 | 14.12 | 11.48 | 0.74 | 0 | 03h30 | 0.41525 | 0.1765 | 0.1435 | 0.00925 | 0
04h30 | 33.22 | 14.12 | 11.97 | 0.89 | 0 | 04h30 | 0.41525 | 0.1765 | 0.14963 | 0.011125 | 0
05h30 | 35.43 | 16.51 | 13.94 | 3.12 | 0 | 05h30 | 0.44288 | 0.20638 | 0.17425 | 0.039 | 0
06h30 | 49.6 | 30.04 | 22.5 | 10.84 | 7.23 | 06h30 | 0.62 | 0.3755 | 0.28125 | 0.1355 | 0.090375
07h30 | 79.26 | 57.59 | 45.61 | 31.03 | 24.89 | 07h30 | 0.99075 | 0.71988 | 0.57012 | 0.38788 | 0.31112
08h30 | 65.1 | 44.06 | 36.57 | 23.15 | 17.66 | 08h30 | 0.81375 | 0.55075 | 0.45713 | 0.28937 | 0.22075
09h30 | 46.84 | 23.81 | 23.95 | 7.49 | 3.84 | 09h30 | 0.5855 | 0.29762 | 0.29938 | 0.093625 | 0.048
10h30 | 46.84 | 23.81 | 23.95 | 7.49 | 3.84 | 10h30 | 0.5855 | 0.29762 | 0.29938 | 0.093625 | 0.048
11h30 | 63.47 | 41.1 | 32.45 | 17.01 | 12.3 | 11h30 | 0.79338 | 0.51375 | 0.40563 | 0.21263 | 0.15375
12h30 | 102.61 | 80.68 | 55.83 | 40.67 | 33.28 | 12h30 | 1.2826 | 1.0085 | 0.69788 | 0.50838 | 0.416
13h30 | 116.42 | 94.8 | 64.01 | 48.96 | 40.59 | 13h30 | 1.4552 | 1.185 | 0.80012 | 0.612 | 0.50738
14h30 | 101.89 | 80.42 | 55.23 | 40.6 | 33.11 | 14h30 | 1.2736 | 1.0052 | 0.69037 | 0.5075 | 0.41387
15h30 | 92.33 | 70.98 | 49.5 | 35.41 | 28.55 | 15h30 | 1.1541 | 0.88725 | 0.61875 | 0.44262 | 0.35687
16h30 | 98.66 | 77.45 | 53.39 | 39.68 | 32.47 | 16h30 | 1.2332 | 0.96813 | 0.66738 | 0.496 | 0.40587
17h30 | 109.34 | 88.32 | 59.89 | 46.41 | 38.5 | 17h30 | 1.3667 | 1.104 | 0.74862 | 0.58013 | 0.48125
18h30 | 115.01 | 94.22 | 63.6 | 49.74 | 41.46 | 18h30 | 1.4376 | 1.1778 | 0.795 | 0.62175 | 0.51825
19h30 | 112.47 | 91.85 | 62.33 | 48.16 | 40.06 | 19h30 | 1.4059 | 1.1481 | 0.77912 | 0.602 | 0.50075
20h30 | 116.43 | 95.92 | 64.74 | 50.63 | 42.27 | 20h30 | 1.4554 | 1.199 | 0.80925 | 0.63287 | 0.52838
21h30 | 129.92 | 109.48 | 73.07 | 58.52 | 49.39 | 21h30 | 1.624 | 1.3685 | 0.91338 | 0.7315 | 0.61738
22h30 | 130.28 | 109.89 | 73.58 | 58.54 | 49.52 | 22h30 | 1.6285 | 1.3736 | 0.91975 | 0.73175 | 0.619
23h30 | 121.34 | 100.94 | 68.16 | 53.35 | 44.92 | 23h30 | 1.5168 | 1.2617 | 0.852 | 0.66687 | 0.5615
00h30 | 101.29 | 82.03 | 50.46 | 36.9 | 28.69 | 00h30 | 1.2661 | 1.0254 | 0.63075 | 0.46125 | 0.35863
01h30 | 108.2 | 90.37 | 57.94 | 45.99 | 38.02 | 01h30 | 1.3525 | 1.1296 | 0.72425 | 0.57488 | 0.47525
02h30 | 107.84 | 89.83 | 57.88 | 46.29 | 38.89 | 02h30 | 1.348 | 1.1229 | 0.7235 | 0.57862 | 0.48612
03h30 | 106.7 | 87.96 | 57.2 | 45.23 | 38.25 | 03h30 | 1.3337 | 1.0995 | 0.715 | 0.56537 | 0.47813
04h30 | 99.29 | 80.03 | 52.89 | 40.54 | 34.16 | 04h30 | 1.2411 | 1.0004 | 0.66112 | 0.50675 | 0.427
05h30 | 74.13 | 54.4 | 38.05 | 25.16 | 20.34 | 05h30 | 0.92663 | 0.68 | 0.47563 | 0.3145 | 0.25425
06h30 | 61.01 | 39.74 | 34.99 | 20.63 | 17.06 | 06h30 | 0.76262 | 0.49675 | 0.43738 | 0.25788 | 0.21325
07h30 | 82.81 | 60.49 | 48.38 | 32.72 | 27.54 | 07h30 | 1.0351 | 0.75613 | 0.60475 | 0.409 | 0.34425
08h30 | 92.39 | 68.95 | 51.7 | 34.98 | 29.15 | 08h30 | 1.1549 | 0.86187 | 0.64625 | 0.43725 | 0.36438
09h30 | 100.46 | 78.52 | 54.25 | 38.76 | 32.25 | 09h30 | 1.2557 | 0.9815 | 0.67812 | 0.4845 | 0.40313
10h30 | 90.87 | 70.06 | 50.92 | 36.49 | 30.63 | 10h30 | 1.1359 | 0.87575 | 0.6365 | 0.45613 | 0.38288
11h30 | 69.02 | 47.96 | 31.2 | 18.07 | 12.57 | 11h30 | 0.86275 | 0.5995 | 0.39 | 0.22587 | 0.15712
12h30 | 70.19 | 49.92 | 33.14 | 20.93 | 15.58 | 12h30 | 0.87738 | 0.624 | 0.41425 | 0.26162 | 0.19475
13h30 | 79 | 59.6 | 38.15 | 26.95 | 21 | 13h30 | 0.9875 | 0.745 | 0.47687 | 0.33687 | 0.2625
14h30 | 91.63 | 72.98 | 46.44 | 34.87 | 28.15 | 14h30 | 1.1454 | 0.91225 | 0.5805 | 0.43588 | 0.35187
15h30 | 92.62 | 74.4 | 48.77 | 35.64 | 29.07 | 15h30 | 1.1578 | 0.93 | 0.60962 | 0.4455 | 0.36338
16h30 | 84.27 | 66.54 | 45.2 | 31.8 | 25.8 | 16h30 | 1.0534 | 0.83175 | 0.565 | 0.3975 | 0.3225
17h30 | 81.27 | 64.12 | 44.08 | 31.17 | 25.35 | 17h30 | 1.0159 | 0.8015 | 0.551 | 0.38962 | 0.31688
18h30 | 80.99 | 64.28 | 44.43 | 31.28 | 25.6 | 18h30 | 1.0124 | 0.8035 | 0.55537 | 0.391 | 0.32
19h30 | 69.61 | 53.05 | 38.13 | 24.35 | 19.41 | 19h30 | 0.87013 | 0.66312 | 0.47663 | 0.30438 | 0.24263
20h30 | 64.43 | 45.41 | 32.96 | 18.72 | 14.31 | 20h30 | 0.80537 | 0.56763 | 0.412 | 0.234 | 0.17888
21h30 | 60.88 | 43.92 | 33.35 | 18.98 | 14.56 | 21h30 | 0.761 | 0.549 | 0.41687 | 0.23725 | 0.182
22h30 | 60.88 | 43.92 | 31.49 | 17.56 | 12.51 | 22h30 | 0.761 | 0.549 | 0.39363 | 0.2195 | 0.15637
23h30 | 60.49 | 42.6 | 32.95 | 18.3 | 14.08 | 23h30 | 0.75613 | 0.5325 | 0.41187 | 0.22875 | 0.176
00h30 | 60.49 | 42.6 | 32.95 | 18.3 | 14.08 | 00h30 | 0.75613 | 0.5325 | 0.41187 | 0.22875 | 0.176
01h30 | 65.69 | 49.35 | 33.72 | 19.3 | 14.81 | 01h30 | 0.82112 | 0.61687 | 0.4215 | 0.24125 | 0.18513
02h30 | 65.69 | 49.35 | 33.72 | 19.3 | 14.81 | 02h30 | 0.82112 | 0.61687 | 0.4215 | 0.24125 | 0.18513
03h30 | 28.66 | 7.82 | 10.06 | 0 | 0 | 03h30 | 0.35825 | 0.09775 | 0.12575 | 0 | 0
04h30 | 33.47 | 14.52 | 14.45 | 0 | 0 | 04h30 | 0.41837 | 0.1815 | 0.18063 | 0 | 0
05h30 | 53.92 | 34.49 | 26.95 | 11.91 | 7.26 | 05h30 | 0.674 | 0.43112 | 0.33687 | 0.14888 | 0.09075
06h30 | 78.95 | 58.49 | 41.82 | 26.34 | 21.62 | 06h30 | 0.98687 | 0.73113 | 0.52275 | 0.32925 | 0.27025
07h30 | 92.52 | 69.61 | 54.59 | 37.2 | 31.37 | 07h30 | 1.1565 | 0.87013 | 0.68237 | 0.465 | 0.39213
08h30 | 65.87 | 40.99 | 35.33 | 22.76 | 17.02 | 08h30 | 0.82337 | 0.51238 | 0.44162 | 0.2845 | 0.21275
09h30 | 55.27 | 30.57 | 28.39 | 11.84 | 8.13 | 09h30 | 0.69088 | 0.38212 | 0.35487 | 0.148 | 0.10162
10h30 | 52.95 | 28.49 | 28.39 | 11.84 | 8.13 | 10h30 | 0.66187 | 0.35613 | 0.35487 | 0.148 | 0.10162
11h30 | 71.62 | 46.99 | 37.21 | 19.92 | 15.26 | 11h30 | 0.89525 | 0.58737 | 0.46513 | 0.249 | 0.19075
12h30 | 100.27 | 75.75 | 54.53 | 37.22 | 30.8 | 12h30 | 1.2534 | 0.94688 | 0.68163 | 0.46525 | 0.385
13h30 | 101.03 | 76.85 | 54.47 | 37.68 | 31.14 | 13h30 | 1.2629 | 0.96062 | 0.68088 | 0.471 | 0.38925
14h30 | 96.94 | 72.84 | 51.98 | 35.45 | 29.05 | 14h30 | 1.2118 | 0.9105 | 0.64975 | 0.44312 | 0.36312
15h30 | 95.44 | 71.41 | 51.21 | 34.87 | 28.46 | 15h30 | 1.193 | 0.89263 | 0.64013 | 0.43588 | 0.35575
16h30 | 70.06 | 46.67 | 36.39 | 19.91 | 15.1 | 16h30 | 0.87575 | 0.58337 | 0.45487 | 0.24888 | 0.18875
17h30 | 64.22 | 40.47 | 32.74 | 16.7 | 12.3 | 17h30 | 0.80275 | 0.50587 | 0.40925 | 0.20875 | 0.15375
18h30 | 82.71 | 59.16 | 43.69 | 28.16 | 22.58 | 18h30 | 1.0339 | 0.7395 | 0.54612 | 0.352 | 0.28225
19h30 | 62.78 | 39.4 | 31.72 | 16.31 | 11.96 | 19h30 | 0.78475 | 0.4925 | 0.3965 | 0.20388 | 0.1495
20h30 | 69.85 | 46.82 | 36.12 | 20.56 | 15.51 | 20h30 | 0.87313 | 0.58525 | 0.4515 | 0.257 | 0.19387
21h30 | 103.26 | 80.48 | 56.32 | 40.6 | 33.12 | 21h30 | 1.2908 | 1.006 | 0.704 | 0.5075 | 0.414
22h30 | 77.65 | 54.38 | 40.97 | 24.8 | 19.21 | 22h30 | 0.97062 | 0.67975 | 0.51213 | 0.31 | 0.24013
23h30 | 41.84 | 19.51 | 19.51 | 3.96 | 0.81 | 23h30 | 0.523 | 0.24388 | 0.24388 | 0.0495 | 0.010125
00h30 | 41.84 | 19.51 | 19.51 | 3.96 | 0.81 | 00h30 | 0.523 | 0.24388 | 0.24388 | 0.0495 | 0.010125
01h30 | 27.16 | 6.83 | 6.83 | 0 | 0 | 01h30 | 0.3395 | 0.085375 | 0.085375 | 0 | 0
02h30 | 28.07 | 9.26 | 9.26 | 0 | 0 | 02h30 | 0.35087 | 0.11575 | 0.11575 | 0 | 0
03h30 | 27.51 | 8.88 | 8.87 | 0 | 0 | 03h30 | 0.34387 | 0.111 | 0.11088 | 0 | 0
04h30 | 54.77 | 35.85 | 25.35 | 11.72 | 5.35 | 04h30 | 0.68463 | 0.44812 | 0.31688 | 0.1465 | 0.066875
05h30 | 88.76 | 69.76 | 45.83 | 33.66 | 25.32 | 05h30 | 1.1095 | 0.872 | 0.57288 | 0.42075 | 0.3165
06h30 | 97.67 | 78.69 | 51.16 | 39.2 | 29.95 | 06h30 | 1.2209 | 0.98362 | 0.6395 | 0.49 | 0.37438
07h30 | 121.56 | 101.09 | 70.5 | 56.72 | 45.48 | 07h30 | 1.5195 | 1.2636 | 0.88125 | 0.709 | 0.5685
08h30 | 112.23 | 90.8 | 62.28 | 47.17 | 36.22 | 08h30 | 1.4029 | 1.135 | 0.7785 | 0.58962 | 0.45275
09h30 | 103.89 | 83.54 | 58.14 | 43.76 | 34.6 | 09h30 | 1.2986 | 1.0442 | 0.72675 | 0.547 | 0.4325
10h30 | 105.55 | 86.1 | 58.77 | 44.48 | 34.95 | 10h30 | 1.3194 | 1.0762 | 0.73462 | 0.556 | 0.43688
11h30 | 104.67 | 85.96 | 58.04 | 43.91 | 34.32 | 11h30 | 1.3084 | 1.0745 | 0.7255 | 0.54888 | 0.429
12h30 | 117.26 | 99.21 | 65.51 | 51.68 | 40.85 | 12h30 | 1.4658 | 1.2401 | 0.81888 | 0.646 | 0.51062
13h30 | 124.8 | 107.47 | 69.64 | 56.62 | 44.76 | 13h30 | 1.56 | 1.3434 | 0.8705 | 0.70775 | 0.5595
14h30 | 115.34 | 98.73 | 63.38 | 51.49 | 39.72 | 14h30 | 1.4418 | 1.2341 | 0.79225 | 0.64363 | 0.4965
15h30 | 118.88 | 102.72 | 65.73 | 53.98 | 41.83 | 15h30 | 1.486 | 1.284 | 0.82163 | 0.67475 | 0.52287
16h30 | 126.6 | 110.79 | 71.24 | 58.94 | 46.52 | 16h30 | 1.5825 | 1.3849 | 0.8905 | 0.73675 | 0.5815
17h30 | 133.12 | 117.76 | 75.88 | 63.23 | 50.46 | 17h30 | 1.664 | 1.472 | 0.9485 | 0.79038 | 0.63075
18h30 | 140.68 | 125.75 | 80.87 | 67.99 | 54.94 | 18h30 | 1.7585 | 1.5719 | 1.0109 | 0.84988 | 0.68675
19h30 | 134.41 | 119.8 | 77.33 | 64.46 | 52.14 | 19h30 | 1.6801 | 1.4975 | 0.96662 | 0.80575 | 0.65175
20h30 | 123.37 | 109.01 | 70.85 | 58 | 46.64 | 20h30 | 1.5421 | 1.3626 | 0.88562 | 0.725 | 0.583
21h30 | 124.44 | 110.23 | 71.71 | 58.56 | 47.45 | 21h30 | 1.5555 | 1.3779 | 0.89638 | 0.732 | 0.59313
22h30 | 134.41 | 120.24 | 77.96 | 64.4 | 53.01 | 22h30 | 1.6801 | 1.503 | 0.9745 | 0.805 | 0.66263
23h30 | 146.1 | 131.92 | 85.21 | 71.33 | 59.23 | 23h30 | 1.8262 | 1.649 | 1.0651 | 0.89163 | 0.74038
00h30 | 130.61 | 117.31 | 70.46 | 57.4 | 47.43 | 00h30 | 1.6326 | 1.4664 | 0.88075 | 0.7175 | 0.59288
01h30 | 127.29 | 115.16 | 71.77 | 60.46 | 48.66 | 01h30 | 1.5911 | 1.4395 | 0.89712 | 0.75575 | 0.60825
02h30 | 119.44 | 107.13 | 67.25 | 56.44 | 48.66 | 02h30 | 1.493 | 1.3391 | 0.84062 | 0.7055 | 0.60825
03h30 | 112.79 | 99.74 | 63.22 | 52.08 | 42.12 | 03h30 | 1.4099 | 1.2468 | 0.79025 | 0.651 | 0.5265
04h30 | 101.95 | 88.34 | 56.49 | 49.87 | 42.12 | 04h30 | 1.2744 | 1.1042 | 0.70613 | 0.62338 | 0.5265
05h30 | 97.37 | 83.26 | 53.48 | 41.25 | 32.83 | 05h30 | 1.2171 | 1.0408 | 0.6685 | 0.51562 | 0.41037
06h30 | 106.84 | 92.26 | 59.03 | 47.92 | 38.54 | 06h30 | 1.3355 | 1.1533 | 0.73787 | 0.599 | 0.48175
07h30 | 122.02 | 120.91 | 82.19 | 68.62 | 58.21 | 07h30 | 1.5252 | 1.5114 | 1.0274 | 0.85775 | 0.72762
08h30 | 136 | 121.54 | 80.47 | 65.57 | 54.55 | 08h30 | 1.7 | 1.5192 | 1.0059 | 0.81963 | 0.68188
09h30 | 133.47 | 116.93 | 77.68 | 63.94 | 53.17 | 09h30 | 1.6684 | 1.4616 | 0.971 | 0.79925 | 0.66463
10h30 | 139.41 | 121.3 | 78.68 | 65.96 | 54.32 | 10h30 | 1.7426 | 1.5163 | 0.9835 | 0.8245 | 0.679
11h30 | 141.94 | 130.33 | 87.57 | 75.57 | 62.23 | 11h30 | 1.7743 | 1.6291 | 1.0946 | 0.94463 | 0.77787
12h30 | 162.11 | 146.96 | 93.42 | 81.41 | 67.02 | 12h30 | 2.0264 | 1.837 | 1.1678 | 1.0176 | 0.83775
13h30 | 162.11 | 146.96 | 93.77 | 81.94 | 67.23 | 13h30 | 2.0264 | 1.837 | 1.1721 | 1.0243 | 0.84037
14h30 | 156.96 | 140.86 | 87.81 | 76.32 | 62.34 | 14h30 | 1.962 | 1.7608 | 1.0976 | 0.954 | 0.77925
15h30 | 143.49 | 127.4 | 79.45 | 67.99 | 55.65 | 15h30 | 1.7936 | 1.5925 | 0.99313 | 0.84988 | 0.69563
16h30 | 122.14 | 106.08 | 72.64 | 62.14 | 52.56 | 16h30 | 1.5268 | 1.326 | 0.908 | 0.77675 | 0.657
17h30 | 101.38 | 85.62 | 55.55 | 43.36 | 34.63 | 17h30 | 1.2672 | 1.0702 | 0.69437 | 0.542 | 0.43288
18h30 | 92.82 | 77.41 | 55.55 | 43.36 | 34.63 | 18h30 | 1.1603 | 0.96762 | 0.69437 | 0.542 | 0.43288
19h30 | 85.14 | 69.93 | 46.6 | 33.53 | 26.72 | 19h30 | 1.0642 | 0.87413 | 0.5825 | 0.41913 | 0.334
20h30 | 76.16 | 60.98 | 46.6 | 33.53 | 26.72 | 20h30 | 0.952 | 0.76225 | 0.5825 | 0.41913 | 0.334
21h30 | 79.73 | 64.49 | 43.89 | 30.16 | 23.94 | 21h30 | 0.99662 | 0.80612 | 0.54863 | 0.377 | 0.29925
22h30 | 77.52 | 62.12 | 43.89 | 30.16 | 23.94 | 22h30 | 0.969 | 0.7765 | 0.54863 | 0.377 | 0.29925
23h30 | 49.13 | 33.48 | 25.65 | 11.5 | 7.4 | 23h30 | 0.61413 | 0.4185 | 0.32062 | 0.14375 | 0.0925
00h30 | 33.26 | 33.45 | 25.65 | 11.5 | 7.4 | 00h30 | 0.41575 | 0.41813 | 0.32062 | 0.14375 | 0.0925
01h30 | 32.27 | 16.36 | 10.55 | 0 | 0 | 01h30 | 0.40337 | 0.2045 | 0.13187 | 0 | 0
02h30 | 32.27 | 16.36 | 10.55 | 0 | 0 | 02h30 | 0.40337 | 0.2045 | 0.13187 | 0 | 0
03h30 | 24.43 | 7.08 | 7.12 | 0 | 0 | 03h30 | 0.30538 | 0.0885 | 0.089 | 0 | 0
04h30 | 31.26 | 15.11 | 11.48 | 0.62 | 0 | 04h30 | 0.39075 | 0.18887 | 0.1435 | 0.00775 | 0
05h30 | 31.94 | 15.49 | 12.01 | 2.32 | 0 | 05h30 | 0.39925 | 0.19362 | 0.15013 | 0.029 | 0
06h30 | 30 | 12.84 | 10.94 | 1.7 | 0 | 06h30 | 0.375 | 0.1605 | 0.13675 | 0.02125 | 0
07h30 | 47.82 | 28.34 | 26.21 | 12.73 | 8.58 | 07h30 | 0.59775 | 0.35425 | 0.32762 | 0.15912 | 0.10725
08h30 | 47.89 | 26.69 | 22.92 | 12.73 | 8.58 | 08h30 | 0.59862 | 0.33363 | 0.2865 | 0.15912 | 0.10725
09h30 | 48.1 | 27.47 | 22.85 | 10.03 | 5.37 | 09h30 | 0.60125 | 0.34337 | 0.28563 | 0.12537 | 0.067125
10h30 | 43.14 | 23.74 | 22.85 | 10.03 | 5.37 | 10h30 | 0.53925 | 0.29675 | 0.28563 | 0.12537 | 0.067125
11h30 | 30.26 | 10.21 | 9.75 | 0 | 0 | 11h30 | 0.37825 | 0.12762 | 0.12187 | 0 | 0
12h30 | 30.26 | 10.4 | 10.31 | 0 | 0 | 12h30 | 0.37825 | 0.13 | 0.12887 | 0 | 0
13h30 | 27.45 | 8.68 | 8.46 | 0 | 0 | 13h30 | 0.34313 | 0.1085 | 0.10575 | 0 | 0
14h30 | 27.45 | 8.49 | 8.24 | 0 | 0 | 14h30 | 0.34313 | 0.10612 | 0.103 | 0 | 0
15h30 | 45.04 | 26.87 | 19.87 | 6.33 | 0.29 | 15h30 | 0.563 | 0.33587 | 0.24838 | 0.079125 | 0.003625
16h30 | 59.12 | 41.19 | 28.84 | 16.41 | 10.3 | 16h30 | 0.739 | 0.51487 | 0.3605 | 0.20513 | 0.12875
17h30 | 52.76 | 35.29 | 25.33 | 13.03 | 10.01 | 17h30 | 0.6595 | 0.44112 | 0.31662 | 0.16287 | 0.12512
18h30 | 48.49 | 31.43 | 22.98 | 10.97 | 5.11 | 18h30 | 0.60613 | 0.39287 | 0.28725 | 0.13712 | 0.063875
19h30 | 46.55 | 29.81 | 21.96 | 10.11 | 5.13 | 19h30 | 0.58188 | 0.37262 | 0.2745 | 0.12637 | 0.064125
20h30 | 45.67 | 29.19 | 21.51 | 9.85 | 4.71 | 20h30 | 0.57088 | 0.36488 | 0.26887 | 0.12312 | 0.058875
21h30 | 46.12 | 29.84 | 21.8 | 10.33 | 5.15 | 21h30 | 0.5765 | 0.373 | 0.2725 | 0.12912 | 0.064375
22h30 | 47.95 | 31.81 | 23.01 | 11.42 | 6.19 | 22h30 | 0.59937 | 0.39763 | 0.28763 | 0.14275 | 0.077375
23h30 | 37.82 | 21.77 | 17.21 | 8.85 | 5.72 | 23h30 | 0.47275 | 0.27213 | 0.21513 | 0.11063 | 0.0715
00h30 | 27.05 | 9.95 | 9.5 | 0 | 0 | 00h30 | 0.33813 | 0.12437 | 0.11875 | 0 | 0
01h30 | 29.25 | 14.96 | 9.12 | 0 | 0 | 01h30 | 0.36562 | 0.187 | 0.114 | 0 | 0
02h30 | 45.94 | 32.76 | 20.98 | 10.78 | 4.36 | 02h30 | 0.57425 | 0.4095 | 0.26225 | 0.13475 | 0.0545
03h30 | 45.05 | 31.78 | 20.47 | 11.57 | 6.22 | 03h30 | 0.56312 | 0.39725 | 0.25588 | 0.14463 | 0.07775
04h30 | 39.8 | 25.91 | 17.15 | 8.15 | 2.79 | 04h30 | 0.4975 | 0.32388 | 0.21438 | 0.10187 | 0.034875
05h30 | 34.07 | 19.75 | 13.48 | 7.37 | 0.93 | 05h30 | 0.42588 | 0.24688 | 0.1685 | 0.092125 | 0.011625
06h30 | 31.45 | 16.79 | 11.79 | 2.1 | 0 | 06h30 | 0.39313 | 0.20988 | 0.14738 | 0.02625 | 0
07h30 | 47.56 | 30.9 | 25.9 | 14.91 | 11.82 | 07h30 | 0.5945 | 0.38625 | 0.32375 | 0.18638 | 0.14775
08h30 | 46.53 | 28.46 | 22.01 | 12.82 | 11.82 | 08h30 | 0.58162 | 0.35575 | 0.27513 | 0.16025 | 0.14775
09h30 | 38.62 | 21.27 | 17.7 | 6.36 | 0.94 | 09h30 | 0.48275 | 0.26587 | 0.22125 | 0.0795 | 0.01175
10h30 | 30.82 | 14.74 | 14.75 | 6.36 | 0.94 | 10h30 | 0.38525 | 0.18425 | 0.18438 | 0.0795 | 0.01175
11h30 | 23.92 | 7.02 | 6.96 | 0 | 0 | 11h30 | 0.299 | 0.08775 | 0.087 | 0 | 0
12h30 | 23.92 | 7.02 | 6.96 | 0 | 0 | 12h30 | 0.299 | 0.08775 | 0.087 | 0 | 0
13h30 | 20.98 | 5.4 | 5.36 | 0 | 0 | 13h30 | 0.26225 | 0.0675 | 0.067 | 0 | 0
14h30 | 20.98 | 5.4 | 5.36 | 0 | 0 | 14h30 | 0.26225 | 0.0675 | 0.067 | 0 | 0
15h30 | 21.16 | 6.14 | 6.11 | 0 | 0 | 15h30 | 0.2645 | 0.07675 | 0.076375 | 0 | 0
16h30 | 22.18 | 7.42 | 7.38 | 0 | 0 | 16h30 | 0.27725 | 0.09275 | 0.09225 | 0 | 0
17h30 | 39.94 | 25.5 | 18.65 | 6.2 | 0 | 17h30 | 0.49925 | 0.31875 | 0.23312 | 0.0775 | 0
18h30 | 55.11 | 40.91 | 28.01 | 16.29 | 9.35 | 18h30 | 0.68888 | 0.51138 | 0.35013 | 0.20363 | 0.11688
19h30 | 55.69 | 41.67 | 28.49 | 16.56 | 9.71 | 19h30 | 0.69612 | 0.52087 | 0.35613 | 0.207 | 0.12137
20h30 | 60.91 | 47.02 | 31.93 | 19.73 | 12.65 | 20h30 | 0.76138 | 0.58775 | 0.39913 | 0.24663 | 0.15812
21h30 | 63.55 | 49.73 | 33.78 | 21.34 | 14.2 | 21h30 | 0.79438 | 0.62162 | 0.42225 | 0.26675 | 0.1775
22h30 | 63.63 | 49.85 | 33.9 | 21.51 | 14.4 | 22h30 | 0.79538 | 0.62313 | 0.42375 | 0.26887 | 0.18
23h30 | 63.63 | 49.85 | 33.9 | 21.54 | 14.48 | 23h30 | 0.79538 | 0.62313 | 0.42375 | 0.26925 | 0.181
00h30 | 46.61 | 33.84 | 19.7 | 8.11 | 1.99 | 00h30 | 0.58262 | 0.423 | 0.24625 | 0.10138 | 0.024875
01h30 | 56.12 | 44.79 | 27.59 | 18.04 | 10.72 | 01h30 | 0.7015 | 0.55988 | 0.34487 | 0.2255 | 0.134
02h30 | 63 | 51.66 | 31.97 | 23.2 | 14.87 | 02h30 | 0.7875 | 0.64575 | 0.39963 | 0.29 | 0.18588
03h30 | 65.88 | 53.84 | 33.53 | 24.68 | 16.51 | 03h30 | 0.8235 | 0.673 | 0.41913 | 0.3085 | 0.20638
04h30 | 61.57 | 49.03 | 30.92 | 21.98 | 14.39 | 04h30 | 0.76963 | 0.61287 | 0.3865 | 0.27475 | 0.17988
05h30 | 45.89 | 32.94 | 21.29 | 12.59 | 6.66 | 05h30 | 0.57363 | 0.41175 | 0.26613 | 0.15737 | 0.08325
06h30 | 38.84 | 24.73 | 19.51 | 10.13 | 4.63 | 06h30 | 0.4855 | 0.30912 | 0.24388 | 0.12662 | 0.057875
07h30 | 33.45 | 17.24 | 17.5 | 5.14 | 2.82 | 07h30 | 0.41813 | 0.2155 | 0.21875 | 0.06425 | 0.03525
08h30 | 33.45 | 17.24 | 17.5 | 5.14 | 2.82 | 08h30 | 0.41813 | 0.2155 | 0.21875 | 0.06425 | 0.03525
09h30 | 35.18 | 19.03 | 16.17 | 4.4 | 0 | 09h30 | 0.43975 | 0.23788 | 0.20212 | 0.055 | 0
10h30 | 38.73 | 23.12 | 17.99 | 6.75 | 2.16 | 10h30 | 0.48413 | 0.289 | 0.22487 | 0.084375 | 0.027
11h30 | 29.26 | 13.94 | 11.62 | 2.35 | 2.16 | 11h30 | 0.36575 | 0.17425 | 0.14525 | 0.029375 | 0.027
12h30 | 25.72 | 9.86 | 9.8 | 0 | 0 | 12h30 | 0.3215 | 0.12325 | 0.1225 | 0 | 0
13h30 | 20.18 | 5.09 | 5.08 | 0 | 0 | 13h30 | 0.25225 | 0.063625 | 0.0635 | 0 | 0
14h30 | 20.62 | 5.89 | 5.88 | 0 | 0 | 14h30 | 0.25775 | 0.073625 | 0.0735 | 0 | 0
15h30 | 22.78 | 8.27 | 7.44 | 0 | 0 | 15h30 | 0.28475 | 0.10337 | 0.093 | 0 | 0
16h30 | 29.23 | 14.83 | 11.73 | 0.82 | 0 | 16h30 | 0.36538 | 0.18538 | 0.14663 | 0.01025 | 0
17h30 | 34.92 | 20.68 | 15.55 | 4.74 | 0 | 17h30 | 0.4365 | 0.2585 | 0.19437 | 0.05925 | 0
18h30 | 35.06 | 20.93 | 15.8 | 4.79 | 0 | 18h30 | 0.43825 | 0.26162 | 0.1975 | 0.059875 | 0
19h30 | 27.7 | 13.6 | 11.31 | 0.87 | 0 | 19h30 | 0.34625 | 0.17 | 0.14138 | 0.010875 | 0
20h30 | 21.7 | 7.59 | 7.58 | 0 | 0 | 20h30 | 0.27125 | 0.094875 | 0.09475 | 0 | 0
21h30 | 26.87 | 12.72 | 10.61 | 0 | 0 | 21h30 | 0.33587 | 0.159 | 0.13262 | 0 | 0
22h30 | 36.33 | 22.13 | 16.33 | 5.96 | 0 | 22h30 | 0.45413 | 0.27663 | 0.20413 | 0.0745 | 0
23h30 | 34.44 | 20.14 | 15.12 | 5.96 | 0 | 23h30 | 0.4305 | 0.25175 | 0.189 | 0.0745 | 0
00h30 | 23.94 | 9.14 | 7.81 | 0 | 0 | 00h30 | 0.29925 | 0.11425 | 0.097625 | 0 | 0
01h30 | 9.43 | 0 | 0 | 0 | 0 | 01h30 | 0.11787 | 0 | 0 | 0 | 0
02h30 | 16.59 | 3.95 | 2.12 | 0 | 0 | 02h30 | 0.20738 | 0.049375 | 0.0265 | 0 | 0
03h30 | 36.11 | 24.14 | 14.91 | 3.8 | 0 | 03h30 | 0.45138 | 0.30175 | 0.18638 | 0.0475 | 0
04h30 | 57.19 | 44.21 | 27.25 | 19.09 | 10.92 | 04h30 | 0.71488 | 0.55263 | 0.34063 | 0.23863 | 0.1365
05h30 | 63.64 | 50.2 | 31.13 | 22.77 | 14.55 | 05h30 | 0.7955 | 0.6275 | 0.38912 | 0.28463 | 0.18188
06h30 | 69.82 | 55.91 | 34.78 | 26.5 | 17.81 | 06h30 | 0.87275 | 0.69888 | 0.43475 | 0.33125 | 0.22262
07h30 | 86.44 | 70.2 | 48.97 | 39.31 | 32.34 | 07h30 | 1.0805 | 0.8775 | 0.61213 | 0.49138 | 0.40425
08h30 | 64.73 | 46.88 | 32.79 | 21.04 | 18.16 | 08h30 | 0.80912 | 0.586 | 0.40987 | 0.263 | 0.227
09h30 | 56.3 | 39.23 | 28.73 | 16.42 | 9.18 | 09h30 | 0.70375 | 0.49038 | 0.35913 | 0.20525 | 0.11475
10h30 | 61.57 | 44.92 | 31.16 | 19.44 | 12.29 | 10h30 | 0.76963 | 0.5615 | 0.3895 | 0.243 | 0.15363
11h30 | 66 | 49.64 | 33 | 22.2 | 14.45 | 11h30 | 0.825 | 0.6205 | 0.4125 | 0.2775 | 0.18063
12h30 | 76.74 | 60.64 | 38.94 | 28.73 | 19.98 | 12h30 | 0.95925 | 0.758 | 0.48675 | 0.35913 | 0.24975
13h30 | 99.48 | 83.66 | 52.8 | 42.15 | 31.32 | 13h30 | 1.2435 | 1.0457 | 0.66 | 0.52687 | 0.3915
14h30 | 116.06 | 100.5 | 63.44 | 51.84 | 39.74 | 14h30 | 1.4507 | 1.2563 | 0.793 | 0.648 | 0.49675
15h30 | 108.01 | 92.62 | 59.25 | 47.12 | 36.35 | 15h30 | 1.3501 | 1.1578 | 0.74062 | 0.589 | 0.45437
16h30 | 94.94 | 79.65 | 51.79 | 39.68 | 30.58 | 16h30 | 1.1867 | 0.99562 | 0.64738 | 0.496 | 0.38225
17h30 | 95.02 | 79.86 | 52.05 | 40.14 | 31.38 | 17h30 | 1.1878 | 0.99825 | 0.65063 | 0.50175 | 0.39225
18h30 | 97.26 | 82.22 | 53.56 | 41.7 | 33.09 | 18h30 | 1.2158 | 1.0277 | 0.6695 | 0.52125 | 0.41363
19h30 | 90.35 | 75.35 | 49.5 | 37.68 | 29.68 | 19h30 | 1.1294 | 0.94188 | 0.61875 | 0.471 | 0.371
20h30 | 84.73 | 69.69 | 46.14 | 34.36 | 26.87 | 20h30 | 1.0591 | 0.87113 | 0.57675 | 0.4295 | 0.33587
21h30 | 87.85 | 72.68 | 48.08 | 36.08 | 28.51 | 21h30 | 1.0981 | 0.9085 | 0.601 | 0.451 | 0.35637
22h30 | 87.18 | 71.83 | 47.75 | 35.5 | 28.04 | 22h30 | 1.0897 | 0.89787 | 0.59688 | 0.44375 | 0.3505
23h30 | 86.14 | 70.54 | 47.12 | 34.69 | 27.42 | 23h30 | 1.0768 | 0.88175 | 0.589 | 0.43362 | 0.34275
00h30 | 68.36 | 53.58 | 35.82 | 24.5 | 17.7 | 00h30 | 0.8545 | 0.66975 | 0.44775 | 0.30625 | 0.22125
01h30 | 70.81 | 57.29 | 35.81 | 25.62 | 18.95 | 01h30 | 0.88513 | 0.71613 | 0.44762 | 0.32025 | 0.23688
02h30 | 70.77 | 56.98 | 36.56 | 26.93 | 20.14 | 02h30 | 0.88462 | 0.71225 | 0.457 | 0.33663 | 0.25175
03h30 | 71.89 | 57.12 | 37.07 | 26.76 | 20.16 | 03h30 | 0.89863 | 0.714 | 0.46337 | 0.3345 | 0.252
04h30 | 74.67 | 59.13 | 38.59 | 27.92 | 21.47 | 04h30 | 0.93337 | 0.73913 | 0.48237 | 0.349 | 0.26837
05h30 | 72.71 | 56.48 | 37.2 | 26.2 | 20.17 | 05h30 | 0.90887 | 0.706 | 0.465 | 0.3275 | 0.25212
06h30 | 63.87 | 48.93 | 34.92 | 23.73 | 17.67 | 06h30 | 0.79837 | 0.61162 | 0.4365 | 0.29663 | 0.22087
07h30 | 79.65 | 60.6 | 45.95 | 31.2 | 25.25 | 07h30 | 0.99562 | 0.7575 | 0.57437 | 0.39 | 0.31562
08h30 | 77.79 | 60.6 | 45.95 | 31.2 | 25.25 | 08h30 | 0.97237 | 0.7575 | 0.57437 | 0.39 | 0.31562
09h30 | 78.73 | 58.37 | 42.07 | 26.95 | 20.6 | 09h30 | 0.98413 | 0.72962 | 0.52587 | 0.33687 | 0.2575
10h30 | 83.67 | 63.95 | 44.2 | 29.8 | 23.13 | 10h30 | 1.0459 | 0.79937 | 0.5525 | 0.3725 | 0.28913
11h30 | 84.13 | 64.56 | 43.45 | 29.59 | 22.4 | 11h30 | 1.0516 | 0.807 | 0.54312 | 0.36988 | 0.28
12h30 | 83.07 | 63.95 | 42.37 | 29.4 | 21.69 | 12h30 | 1.0384 | 0.79937 | 0.52963 | 0.3675 | 0.27113
13h30 | 100.27 | 81.58 | 52.37 | 40.02 | 30.41 | 13h30 | 1.2534 | 1.0197 | 0.65463 | 0.50025 | 0.38012
14h30 | 115.09 | 96.75 | 61.6 | 48.92 | 38.28 | 14h30 | 1.4386 | 1.2094 | 0.77 | 0.6115 | 0.4785
15h30 | 101.29 | 83.17 | 54.26 | 40.79 | 31.85 | 15h30 | 1.2661 | 1.0396 | 0.67825 | 0.50987 | 0.39813
16h30 | 91.3 | 73.48 | 49.37 | 35.11 | 27.42 | 16h30 | 1.1413 | 0.9185 | 0.61713 | 0.43888 | 0.34275
17h30 | 97.15 | 79.72 | 53.74 | 38.84 | 30.93 | 17h30 | 1.2144 | 0.9965 | 0.67175 | 0.4855 | 0.38662
18h30 | 101.11 | 84.01 | 56.63 | 41.39 | 33.28 | 18h30 | 1.2639 | 1.0501 | 0.70788 | 0.51738 | 0.416
19h30 | 98.78 | 81.88 | 55.46 | 40.17 | 32.23 | 19h30 | 1.2348 | 1.0235 | 0.69325 | 0.50213 | 0.40287
20h30 | 97.5 | 80.67 | 54.79 | 39.48 | 31.73 | 20h30 | 1.2188 | 1.0084 | 0.68488 | 0.4935 | 0.39663
21h30 | 113.84 | 100.69 | 66.94 | 51.48 | 42.56 | 21h30 | 1.423 | 1.2586 | 0.83675 | 0.6435 | 0.532
22h30 | 140.37 | 124.02 | 81.13 | 65.52 | 55.41 | 22h30 | 1.7546 | 1.5502 | 1.0141 | 0.819 | 0.69263
23h30 | 139.73 | 122.56 | 80.48 | 64.66 | 54.81 | 23h30 | 1.7466 | 1.532 | 1.006 | 0.80825 | 0.68512
00h30 | 101.8 | 85.69 | 58.69 | 42.9 | 34.85 | 00h30 | 1.2725 | 1.0711 | 0.73362 | 0.53625 | 0.43562
01h30 | 80.16 | 65.04 | 41.67 | 30.06 | 22.64 | 01h30 | 1.002 | 0.813 | 0.52087 | 0.37575 | 0.283
02h30 | 77.72 | 65.04 | 41.67 | 30.06 | 22.64 | 02h30 | 0.9715 | 0.813 | 0.52087 | 0.37575 | 0.283
03h30 | 94.61 | 77.55 | 48.97 | 38.33 | 30.15 | 03h30 | 1.1826 | 0.96937 | 0.61213 | 0.47913 | 0.37688
04h30 | 111.42 | 94.33 | 59.78 | 48.46 | 39.09 | 04h30 | 1.3927 | 1.1791 | 0.74725 | 0.60575 | 0.48862
05h30 | 104.28 | 86.94 | 55.48 | 44.25 | 35.37 | 05h30 | 1.3035 | 1.0868 | 0.6935 | 0.55312 | 0.44212
06h30 | 103.33 | 85.6 | 54.69 | 43.56 | 34.66 | 06h30 | 1.2916 | 1.07 | 0.68363 | 0.5445 | 0.43325
07h30 | 115.87 | 114.74 | 77.98 | 64.36 | 54.91 | 07h30 | 1.4484 | 1.4343 | 0.97475 | 0.8045 | 0.68637
08h30 | 126.81 | 109.29 | 72.56 | 57.4 | 47.39 | 08h30 | 1.5851 | 1.3661 | 0.907 | 0.7175 | 0.59237
09h30 | 126.19 | 106.41 | 70.75 | 56.86 | 45.69 | 09h30 | 1.5774 | 1.3301 | 0.88438 | 0.71075 | 0.57112
10h30 | 135.73 | 115.07 | 74.36 | 61.14 | 48.72 | 10h30 | 1.6966 | 1.4384 | 0.9295 | 0.76425 | 0.609
11h30 | 136.35 | 118.66 | 78.3 | 65.79 | 52.15 | 11h30 | 1.7044 | 1.4832 | 0.97875 | 0.82237 | 0.65187
12h30 | 136.66 | 118.29 | 75.36 | 63.48 | 49.7 | 12h30 | 1.7083 | 1.4786 | 0.942 | 0.7935 | 0.62125
13h30 | 132.44 | 113.82 | 71.78 | 60.35 | 46.82 | 13h30 | 1.6555 | 1.4227 | 0.89725 | 0.75438 | 0.58525
14h30 | 135.27 | 117.1 | 73.67 | 62.1 | 48.58 | 14h30 | 1.6909 | 1.4638 | 0.92087 | 0.77625 | 0.60725
15h30 | 139.5 | 121.57 | 78.01 | 65.97 | 52.41 | 15h30 | 1.7437 | 1.5196 | 0.97513 | 0.82463 | 0.65512
16h30 | 143.05 | 125.96 | 80.25 | 67.87 | 54.53 | 16h30 | 1.7881 | 1.5745 | 1.0031 | 0.84837 | 0.68163
17h30 | 137.36 | 120.76 | 77.16 | 64.62 | 52 | 17h30 | 1.717 | 1.5095 | 0.9645 | 0.80775 | 0.65
18h30 | 128.61 | 112.45 | 72.11 | 59.66 | 47.78 | 18h30 | 1.6076 | 1.4056 | 0.90138 | 0.74575 | 0.59725
19h30 | 126.02 | 110.2 | 70.67 | 58.41 | 46.56 | 19h30 | 1.5753 | 1.3775 | 0.88338 | 0.73013 | 0.582
20h30 | 134.38 | 118.82 | 75.88 | 63.46 | 50.88 | 20h30 | 1.6798 | 1.4852 | 0.9485 | 0.79325 | 0.636
21h30 | 142.1 | 126.27 | 80.83 | 67.92 | 54.86 | 21h30 | 1.7763 | 1.5784 | 1.0104 | 0.849 | 0.68575
22h30 | 136.38 | 120.98 | 77.54 | 64.53 | 51.99 | 22h30 | 1.7047 | 1.5123 | 0.96925 | 0.80663 | 0.64987
23h30 | 130.25 | 114.98 | 73.78 | 61.03 | 49.01 | 23h30 | 1.6281 | 1.4372 | 0.92225 | 0.76287 | 0.61262
00h30 | 114.46 | 100.32 | 67.51 | 56.21 | 46.61 | 00h30 | 1.4307 | 1.254 | 0.84388 | 0.70263 | 0.58262
01h30 | 119.85 | 106.32 | 66.35 | 55.46 | 43.21 | 01h30 | 1.4981 | 1.329 | 0.82937 | 0.69325 | 0.54012
02h30 | 119.83 | 107.02 | 66.35 | 55.86 | 43.31 | 02h30 | 1.4979 | 1.3377 | 0.82937 | 0.69825 | 0.54138
03h30 | 118.96 | 105.64 | 64.72 | 55.01 | 42.02 | 03h30 | 1.487 | 1.3205 | 0.809 | 0.68763 | 0.52525
04h30 | 129.89 | 116.19 | 72.17 | 61.42 | 49.04 | 04h30 | 1.6236 | 1.4524 | 0.90212 | 0.76775 | 0.613
05h30 | 132.07 | 117.57 | 82.83 | 70.67 | 58.67 | 05h30 | 1.6509 | 1.4696 | 1.0354 | 0.88338 | 0.73337
06h30 | 146.44 | 131.51 | 84.99 | 72.78 | 61.01 | 06h30 | 1.8305 | 1.6439 | 1.0624 | 0.90975 | 0.76262
07h30 | 146.44 | 131.51 | 95.02 | 80.93 | 70.81 | 07h30 | 1.8305 | 1.6439 | 1.1878 | 1.0116 | 0.88513
08h30 | 144.53 | 127.78 | 85.41 | 72 | 61.35 | 08h30 | 1.8066 | 1.5973 | 1.0676 | 0.9 | 0.76687
09h30 | 137.08 | 119.67 | 79.2 | 65.16 | 54.4 | 09h30 | 1.7135 | 1.4959 | 0.99 | 0.8145 | 0.68
10h30 | 125.93 | 108.42 | 79.2 | 65.16 | 54.4 | 10h30 | 1.5741 | 1.3553 | 0.99 | 0.8145 | 0.68
11h30 | 122.23 | 104.86 | 68.08 | 54.52 | 44.94 | 11h30 | 1.5279 | 1.3108 | 0.851 | 0.6815 | 0.56175
12h30 | 130.21 | 112.98 | 72.64 | 59.43 | 49.47 | 12h30 | 1.6276 | 1.4123 | 0.908 | 0.74287 | 0.61838
13h30 | 132.28 | 115.32 | 72.85 | 60.12 | 50.06 | 13h30 | 1.6535 | 1.4415 | 0.91063 | 0.7515 | 0.62575
14h30 | 123.56 | 106.7 | 68.29 | 55.21 | 45.71 | 14h30 | 1.5445 | 1.3337 | 0.85362 | 0.69012 | 0.57137
15h30 | 122.61 | 105.62 | 67.47 | 54.64 | 45.65 | 15h30 | 1.5326 | 1.3202 | 0.84337 | 0.683 | 0.57063
16h30 | 121.36 | 104.25 | 67.5 | 54.64 | 45.48 | 16h30 | 1.517 | 1.3031 | 0.84375 | 0.683 | 0.5685
17h30 | 116.73 | 99.65 | 65.12 | 51.75 | 43.55 | 17h30 | 1.4591 | 1.2456 | 0.814 | 0.64687 | 0.54438
18h30 | 127.9 | 110.79 | 72.53 | 58.07 | 49.67 | 18h30 | 1.5987 | 1.3849 | 0.90663 | 0.72588 | 0.62087
19h30 | 142.55 | 125.81 | 85.65 | 70.33 | 60.99 | 19h30 | 1.7819 | 1.5726 | 1.0706 | 0.87913 | 0.76238
20h30 | 167.99 | 150.81 | 98.34 | 82.13 | 71.74 | 20h30 | 2.0999 | 1.8851 | 1.2292 | 1.0266 | 0.89675
21h30 | 167.99 | 150.81 | 113.06 | 95.22 | 83.61 | 21h30 | 2.0999 | 1.8851 | 1.4132 | 1.1903 | 1.0451
22h30 | 200 | 183.99 | 122.42 | 103.76 | 91.49 | 22h30 | 2.5 | 2.2999 | 1.5303 | 1.297 | 1.1436
23h30 | 200 | 183.99 | 124.43 | 106 | 93.68 | 23h30 | 2.5 | 2.2999 | 1.5554 | 1.325 | 1.171
00h30 | 186.69 | 169.2 | 103.88 | 87.43 | 75.47 | 00h30 | 2.3336 | 2.115 | 1.2985 | 1.0929 | 0.94337
01h30 | 186.69 | 169.2 | 108.94 | 98.29 | 86 | 01h30 | 2.3336 | 2.115 | 1.3618 | 1.2286 | 1.075
02h30 | 200 | 199.04 | 124.94 | 111.65 | 98.29 | 02h30 | 2.5 | 2.488 | 1.5617 | 1.3956 | 1.2286
03h30 | 200 | 199.04 | 124.94 | 112.37 | 99.22 | 03h30 | 2.5 | 2.488 | 1.5617 | 1.4046 | 1.2403
04h30 | 186.74 | 170.59 | 108.08 | 92.91 | 81.76 | 04h30 | 2.3342 | 2.1324 | 1.351 | 1.1614 | 1.022
05h30 | 157.95 | 136.17 | 87.08 | 72.49 | 63.29 | 05h30 | 1.9744 | 1.7021 | 1.0885 | 0.90612 | 0.79112
06h30 | 150.45 | 127.05 | 81.64 | 70.5 | 61.92 | 06h30 | 1.8806 | 1.5881 | 1.0205 | 0.88125 | 0.774
07h30 | 179.23 | 155.02 | 102.64 | 88.45 | 78.2 | 07h30 | 2.2404 | 1.9378 | 1.283 | 1.1056 | 0.9775
08h30 | 194.58 | 168.3 | 109.76 | 93.28 | 82.16 | 08h30 | 2.4322 | 2.1037 | 1.372 | 1.166 | 1.027
09h30 | 194.58 | 174.75 | 109.76 | 100.73 | 88.85 | 09h30 | 2.4322 | 2.1844 | 1.372 | 1.2591 | 1.1106
10h30 | 200 | 200 | 129.51 | 113.48 | 100.31 | 10h30 | 2.5 | 2.5 | 1.6189 | 1.4185 | 1.2539
11h30 | 200 | 200 | 129.51 | 117.58 | 115.42 | 11h30 | 2.5 | 2.5 | 1.6189 | 1.4697 | 1.4427
12h30 | 200 | 200 | 160.62 | 143.83 | 130 | 12h30 | 2.5 | 2.5 | 2.0078 | 1.7979 | 1.625
13h30 | 200 | 200 | 160.62 | 143.83 | 130 | 13h30 | 2.5 | 2.5 | 2.0078 | 1.7979 | 1.625
14h30 | 200 | 200 | 156.56 | 138.68 | 122.62 | 14h30 | 2.5 | 2.5 | 1.957 | 1.7335 | 1.5328
15h30 | 200 | 200 | 145.71 | 127.72 | 113.05 | 15h30 | 2.5 | 2.5 | 1.8214 | 1.5965 | 1.4131
16h30 | 200 | 200 | 134.26 | 116.76 | 103.31 | 16h30 | 2.5 | 2.5 | 1.6783 | 1.4595 | 1.2914
17h30 | 200 | 178.62 | 114.31 | 97.49 | 85.96 | 17h30 | 2.5 | 2.2327 | 1.4289 | 1.2186 | 1.0745
18h30 | 191.43 | 163.65 | 104.26 | 87.46 | 76.97 | 18h30 | 2.3929 | 2.0456 | 1.3033 | 1.0933 | 0.96213
19h30 | 186.77 | 158.05 | 101.34 | 84.54 | 74.35 | 19h30 | 2.3346 | 1.9756 | 1.2668 | 1.0568 | 0.92937
20h30 | 180.39 | 152.96 | 98.63 | 81.96 | 72.11 | 20h30 | 2.2549 | 1.912 | 1.2329 | 1.0245 | 0.90138
21h30 | 182.65 | 155.92 | 100.78 | 83.89 | 74.09 | 21h30 | 2.2831 | 1.949 | 1.2597 | 1.0486 | 0.92612
22h30 | 179.89 | 153.38 | 99.68 | 82.44 | 72.81 | 22h30 | 2.2486 | 1.9172 | 1.246 | 1.0305 | 0.91012
23h30 | 182.28 | 162.69 | 105.68 | 88.06 | 78 | 23h30 | 2.2785 | 2.0336 | 1.321 | 1.1007 | 0.975
00h30 | 173.06 | 149.19 | 91.69 | 74.91 | 77.64 | 00h30 | 2.1633 | 1.8649 | 1.1461 | 0.93637 | 0.9705
01h30 | 154.99 | 131.18 | 83.64 | 68.26 | 58.96 | 01h30 | 1.9374 | 1.6398 | 1.0455 | 0.85325 | 0.737
02h30 | 131.91 | 107.58 | 70.16 | 67.74 | 58.96 | 02h30 | 1.6489 | 1.3447 | 0.877 | 0.84675 | 0.737
03h30 | 106.35 | 81.48 | 55.3 | 34.97 | 29.45 | 03h30 | 1.3294 | 1.0185 | 0.69125 | 0.43712 | 0.36812
04h30 | 94.07 | 68.7 | 51.52 | 34.97 | 29.45 | 04h30 | 1.1759 | 0.85875 | 0.644 | 0.43712 | 0.36812
05h30 | 95.38 | 69.57 | 48.44 | 30.93 | 25.08 | 05h30 | 1.1923 | 0.86962 | 0.6055 | 0.38662 | 0.3135
06h30 | 79.21 | 52.96 | 48.44 | 30.93 | 25.08 | 06h30 | 0.99013 | 0.662 | 0.6055 | 0.38662 | 0.3135
07h30 | 72.82 | 44.62 | 38.42 | 21.7 | 17.49 | 07h30 | 0.91025 | 0.55775 | 0.48025 | 0.27125 | 0.21863
08h30 | 64.45 | 34.79 | 38.42 | 21.7 | 17.49 | 08h30 | 0.80563 | 0.43488 | 0.48025 | 0.27125 | 0.21863
09h30 | 113.14 | 91.39 | 63.96 | 46.04 | 39.29 | 09h30 | 1.4143 | 1.1424 | 0.7995 | 0.5755 | 0.49112
10h30 | 112.57 | 90.3 | 63.96 | 46.04 | 39.29 | 10h30 | 1.4071 | 1.1287 | 0.7995 | 0.5755 | 0.49112
11h30 | 57.15 | 29.24 | 27.34 | 5.44 | 1.96 | 11h30 | 0.71437 | 0.3655 | 0.34175 | 0.068 | 0.0245
12h30 | 55.18 | 29.24 | 27.34 | 5.74 | 2.32 | 12h30 | 0.68975 | 0.3655 | 0.34175 | 0.07175 | 0.029
13h30 | 79.74 | 52.13 | 39.53 | 20.99 | 16.28 | 13h30 | 0.99675 | 0.65163 | 0.49412 | 0.26238 | 0.2035
14h30 | 106.37 | 79.65 | 55.8 | 37.43 | 31.31 | 14h30 | 1.3296 | 0.99562 | 0.6975 | 0.46787 | 0.39137
15h30 | 115.1 | 88.58 | 62 | 43.08 | 36.59 | 15h30 | 1.4387 | 1.1073 | 0.775 | 0.5385 | 0.45737
16h30 | 121.58 | 95.47 | 67.32 | 47.65 | 40.9 | 16h30 | 1.5197 | 1.1934 | 0.8415 | 0.59562 | 0.51125
17h30 | 118.83 | 93.19 | 66.09 | 47 | 40.42 | 17h30 | 1.4854 | 1.1649 | 0.82612 | 0.5875 | 0.50525
18h30 | 117.61 | 92.33 | 65.3 | 47.08 | 40.58 | 18h30 | 1.4701 | 1.1541 | 0.81625 | 0.5885 | 0.50725
19h30 | 119.29 | 94.25 | 66.39 | 48.43 | 41.91 | 19h30 | 1.4911 | 1.1781 | 0.82988 | 0.60537 | 0.52387
20h30 | 112.42 | 87.46 | 62.31 | 44.6 | 38.48 | 20h30 | 1.4053 | 1.0933 | 0.77887 | 0.5575 | 0.481
21h30 | 97.7 | 72.69 | 53.35 | 36.13 | 30.77 | 21h30 | 1.2212 | 0.90863 | 0.66687 | 0.45162 | 0.38462
22h30 | 97.82 | 72.72 | 53.46 | 36.21 | 30.9 | 22h30 | 1.2228 | 0.909 | 0.66825 | 0.45262 | 0.38625
23h30 | 109.72 | 84.47 | 60.66 | 43.29 | 37.46 | 23h30 | 1.3715 | 1.0559 | 0.75825 | 0.54112 | 0.46825
00h30 | 92.55 | 68.27 | 44.83 | 28.19 | 22.64 | 00h30 | 1.1569 | 0.85337 | 0.56037 | 0.35237 | 0.283
01h30 | 84.48 | 61.36 | 43.4 | 27.4 | 23.15 | 01h30 | 1.056 | 0.767 | 0.5425 | 0.3425 | 0.28937
02h30 | 70.14 | 50.76 | 42.39 | 24.88 | 21.42 | 02h30 | 0.87675 | 0.6345 | 0.52987 | 0.311 | 0.26775
03h30 | 52.85 | 27.71 | 22.6 | 7.41 | 3.87 | 03h30 | 0.66063 | 0.34637 | 0.2825 | 0.092625 | 0.048375
04h30 | 48.63 | 27.71 | 22.6 | 7.41 | 3.87 | 04h30 | 0.60788 | 0.34637 | 0.2825 | 0.092625 | 0.048375
05h30 | 54.44 | 27 | 23.48 | 8.57 | 5.63 | 05h30 | 0.6805 | 0.3375 | 0.2935 | 0.10712 | 0.070375
06h30 | 66.02 | 39.59 | 31.38 | 16.21 | 12.52 | 06h30 | 0.82525 | 0.49488 | 0.39225 | 0.20262 | 0.1565
07h30 | 80.81 | 52.05 | 45.34 | 28.59 | 24.55 | 07h30 | 1.0101 | 0.65063 | 0.56675 | 0.35737 | 0.30688
08h30 | 74.05 | 43.7 | 38.22 | 20.95 | 17.66 | 08h30 | 0.92563 | 0.54625 | 0.47775 | 0.26188 | 0.22075
09h30 | 71.29 | 41.55 | 36.39 | 20.38 | 16.37 | 09h30 | 0.89112 | 0.51938 | 0.45487 | 0.25475 | 0.20463
10h30 | 66.48 | 37.31 | 35.61 | 20.38 | 16.37 | 10h30 | 0.831 | 0.46637 | 0.44512 | 0.25475 | 0.20463
11h30 | 71.72 | 42.88 | 34.37 | 19.13 | 14.95 | 11h30 | 0.8965 | 0.536 | 0.42962 | 0.23913 | 0.18688
12h30 | 96.46 | 68.08 | 49.87 | 34.25 | 28.81 | 12h30 | 1.2058 | 0.851 | 0.62338 | 0.42812 | 0.36012
13h30 | 124.74 | 102.92 | 71.24 | 54.22 | 47.1 | 13h30 | 1.5593 | 1.2865 | 0.8905 | 0.67775 | 0.58875
14h30 | 157.09 | 130.39 | 88.74 | 70.47 | 61.94 | 14h30 | 1.9636 | 1.6299 | 1.1093 | 0.88087 | 0.77425
15h30 | 149.86 | 122.56 | 84.12 | 66.52 | 58.29 | 15h30 | 1.8733 | 1.532 | 1.0515 | 0.8315 | 0.72862
16h30 | 106.77 | 79.24 | 57.4 | 41.66 | 35.66 | 16h30 | 1.3346 | 0.9905 | 0.7175 | 0.52075 | 0.44575
17h30 | 78.55 | 51.61 | 40.45 | 25.3 | 20.8 | 17h30 | 0.98188 | 0.64512 | 0.50562 | 0.31625 | 0.26
18h30 | 98.65 | 72.08 | 53.41 | 36.66 | 31.14 | 18h30 | 1.2331 | 0.901 | 0.66763 | 0.45825 | 0.38925
19h30 | 134.1 | 119.64 | 83.24 | 63.91 | 55.97 | 19h30 | 1.6763 | 1.4955 | 1.0405 | 0.79888 | 0.69963
20h30 | 181.38 | 157.72 | 107.07 | 85.99 | 76.06 | 20h30 | 2.2673 | 1.9715 | 1.3384 | 1.0749 | 0.95075
21h30 | 126.79 | 101.14 | 73.51 | 51.77 | 44.85 | 21h30 | 1.5849 | 1.2643 | 0.91887 | 0.64712 | 0.56063
22h30 | 60.15 | 33.45 | 33.19 | 11.82 | 8.34 | 22h30 | 0.75187 | 0.41813 | 0.41487 | 0.14775 | 0.10425
23h30 | 60.44 | 34.11 | 33.86 | 10.99 | 7.74 | 23h30 | 0.7555 | 0.42638 | 0.42325 | 0.13737 | 0.09675
00h30 | 45.7 | 33.89 | 31.13 | 10.99 | 7.74 | 00h30 | 0.57125 | 0.42362 | 0.38912 | 0.13737 | 0.09675
01h30 | 46.13 | 20.87 | 20.98 | 0 | 0 | 01h30 | 0.57663 | 0.26088 | 0.26225 | 0 | 0
02h30 | 109.29 | 85.4 | 60.56 | 40.29 | 34.01 | 02h30 | 1.3661 | 1.0675 | 0.757 | 0.50362 | 0.42512
03h30 | 163.08 | 137.72 | 92.4 | 72.05 | 63.68 | 03h30 | 2.0385 | 1.7215 | 1.155 | 0.90063 | 0.796
04h30 | 140.74 | 115.44 | 79.3 | 59.38 | 51.65 | 04h30 | 1.7592 | 1.443 | 0.99125 | 0.74225 | 0.64563
05h30 | 117.08 | 91.53 | 64.7 | 45.92 | 39.3 | 05h30 | 1.4635 | 1.1441 | 0.80875 | 0.574 | 0.49125
06h30 | 113.74 | 88.01 | 62.37 | 44.31 | 37.67 | 06h30 | 1.4218 | 1.1001 | 0.77963 | 0.55388 | 0.47087
07h30 | 137.48 | 121.63 | 89.04 | 69.01 | 61.09 | 07h30 | 1.7185 | 1.5204 | 1.113 | 0.86262 | 0.76362
08h30 | 109 | 82.89 | 64.9 | 43.01 | 40.74 | 08h30 | 1.3625 | 1.0361 | 0.81125 | 0.53763 | 0.50925
09h30 | 64.82 | 37.09 | 36.96 | 15.16 | 11.05 | 09h30 | 0.81025 | 0.46363 | 0.462 | 0.1895 | 0.13812
10h30 | 110.88 | 82.72 | 63.47 | 41.74 | 35.75 | 10h30 | 1.386 | 1.034 | 0.79338 | 0.52175 | 0.44688
11h30 | 152.56 | 125.14 | 88.02 | 66.88 | 58.22 | 11h30 | 1.907 | 1.5642 | 1.1002 | 0.836 | 0.72775
12h30 | 102.36 | 79.51 | 61.5 | 40.31 | 33.53 | 12h30 | 1.2795 | 0.99387 | 0.76875 | 0.50387 | 0.41913
13h30 | 56.84 | 30.22 | 30.11 | 9.12 | 5.79 | 13h30 | 0.7105 | 0.37775 | 0.37638 | 0.114 | 0.072375
14h30 | 57.63 | 31.88 | 31.77 | 10.03 | 6.59 | 14h30 | 0.72037 | 0.3985 | 0.39713 | 0.12537 | 0.082375
15h30 | 103.78 | 77.94 | 59.62 | 37.93 | 32.37 | 15h30 | 1.2973 | 0.97425 | 0.74525 | 0.47413 | 0.40463
16h30 | 156.1 | 130.66 | 91.03 | 70.42 | 61.92 | 16h30 | 1.9512 | 1.6333 | 1.1379 | 0.88025 | 0.774
17h30 | 157.96 | 135.2 | 93.32 | 73.69 | 64.68 | 17h30 | 1.9745 | 1.69 | 1.1665 | 0.92112 | 0.8085
18h30 | 160.2 | 135.94 | 93.61 | 74.17 | 65.22 | 18h30 | 2.0025 | 1.6992 | 1.1701 | 0.92712 | 0.81525
19h30 | 160.2 | 139.29 | 95.68 | 76.07 | 66.97 | 19h30 | 2.0025 | 1.7411 | 1.196 | 0.95088 | 0.83713
20h30 | 159.85 | 136.09 | 93.76 | 74.14 | 65.23 | 20h30 | 1.9981 | 1.7011 | 1.172 | 0.92675 | 0.81537
21h30 | 143.41 | 119.17 | 83.41 | 64.18 | 56.17 | 21h30 | 1.7926 | 1.4896 | 1.0426 | 0.80225 | 0.70212
22h30 | 116.36 | 91.62 | 66.43 | 48.08 | 41.53 | 22h30 | 1.4545 | 1.1453 | 0.83037 | 0.601 | 0.51912
23h30 | 98.85 | 74.2 | 55.5 | 38.03 | 32.41 | 23h30 | 1.2356 | 0.9275 | 0.69375 | 0.47537 | 0.40513
00h30 | 78.64 | 55.1 | 41.05 | 22.18 | 17.9 | 00h30 | 0.983 | 0.68875 | 0.51313 | 0.27725 | 0.22375
01h30 | 85.49 | 63.25 | 44.16 | 29.58 | 24.27 | 01h30 | 1.0686 | 0.79063 | 0.552 | 0.36975 | 0.30338
02h30 | 86.16 | 63.72 | 44.79 | 30.45 | 25.35 | 02h30 | 1.077 | 0.7965 | 0.55988 | 0.38062 | 0.31688
03h30 | 84.69 | 61.61 | 43.83 | 29.48 | 24.47 | 03h30 | 1.0586 | 0.77012 | 0.54788 | 0.3685 | 0.30588
04h30 | 93.12 | 69.61 | 49.25 | 34.3 | 28.87 | 04h30 | 1.164 | 0.87013 | 0.61562 | 0.42875 | 0.36088
05h30 | 106.99 | 83.14 | 58.17 | 42.15 | 35.97 | 05h30 | 1.3374 | 1.0393 | 0.72713 | 0.52687 | 0.44962
06h30 | 93.8 | 69.62 | 52.11 | 36.46 | 30.49 | 06h30 | 1.1725 | 0.87025 | 0.65138 | 0.45575 | 0.38112
07h30 | 87.82 | 61.84 | 51.79 | 34.94 | 30.4 | 07h30 | 1.0978 | 0.773 | 0.64738 | 0.43675 | 0.38
08h30 | 79.32 | 61.63 | 51.79 | 34.94 | 30.4 | 08h30 | 0.9915 | 0.77038 | 0.64738 | 0.43675 | 0.38
09h30 | 83.58 | 56.21 | 45.41 | 28.64 | 24 | 09h30 | 1.0448 | 0.70263 | 0.56763 | 0.358 | 0.3
10h30 | 100.96 | 74.72 | 55.76 | 39.22 | 33.62 | 10h30 | 1.262 | 0.934 | 0.697 | 0.49025 | 0.42025
11h30 | 117.38 | 94.17 | 67.08 | 49.9 | 43.2 | 11h30 | 1.4672 | 1.1771 | 0.8385 | 0.62375 | 0.54
12h30 | 120.47 | 94.83 | 67.76 | 49.82 | 43.05 | 12h30 | 1.5059 | 1.1854 | 0.847 | 0.62275 | 0.53812
13h30 | 112.58 | 86.88 | 63.07 | 44.91 | 38.54 | 13h30 | 1.4072 | 1.086 | 0.78838 | 0.56137 | 0.48175
14h30 | 112.78 | 87.05 | 63.24 | 45.08 | 38.71 | 14h30 | 1.4098 | 1.0881 | 0.7905 | 0.5635 | 0.48387
15h30 | 112.97 | 87.55 | 63.74 | 45.54 | 39.16 | 15h30 | 1.4121 | 1.0944 | 0.79675 | 0.56925 | 0.4895
16h30 | 113.18 | 88 | 64.2 | 45.94 | 39.55 | 16h30 | 1.4147 | 1.1 | 0.8025 | 0.57425 | 0.49438
17h30 | 118.68 | 94.11 | 68.03 | 49.51 | 42.81 | 17h30 | 1.4835 | 1.1764 | 0.85037 | 0.61887 | 0.53512
18h30 | 135.11 | 110.78 | 78.37 | 59.11 | 51.59 | 18h30 | 1.6889 | 1.3847 | 0.97962 | 0.73887 | 0.64487
19h30 | 137.31 | 126.51 | 88.17 | 68.17 | 59.82 | 19h30 | 1.7164 | 1.5814 | 1.1021 | 0.85213 | 0.74775
20h30 | 153.35 | 131.36 | 91.15 | 71.03 | 62.35 | 20h30 | 1.9169 | 1.642 | 1.1394 | 0.88787 | 0.77938
21h30 | 151.91 | 127.67 | 88.83 | 68.85 | 60.37 | 21h30 | 1.8989 | 1.5959 | 1.1104 | 0.86062 | 0.75462
22h30 | 148.11 | 122.63 | 85.64 | 65.88 | 57.59 | 22h30 | 1.8514 | 1.5329 | 1.0705 | 0.8235 | 0.71988
23h30 | 143.55 | 118.51 | 82.97 | 63.5 | 55.35 | 23h30 | 1.7944 | 1.4814 | 1.0371 | 0.79375 | 0.69188
00h30 | 116.44 | 92.68 | 61.19 | 42.94 | 36.77 | 00h30 | 1.4555 | 1.1585 | 0.76487 | 0.53675 | 0.45963
01h30 | 113.49 | 91.12 | 61.9 | 45.32 | 38.16 | 01h30 | 1.4186 | 1.139 | 0.77375 | 0.5665 | 0.477
02h30 | 98.02 | 80.69 | 61.9 | 45.32 | 38.16 | 02h30 | 1.2252 | 1.0086 | 0.77375 | 0.5665 | 0.477
03h30 | 79.5 | 56.29 | 39.77 | 24.45 | 19.22 | 03h30 | 0.99375 | 0.70362 | 0.49712 | 0.30562 | 0.24025
04h30 | 76.41 | 56.29 | 39.77 | 24.93 | 19.99 | 04h30 | 0.95513 | 0.70362 | 0.49712 | 0.31162 | 0.24988
05h30 | 71.93 | 47.78 | 35.06 | 22.02 | 17.39 | 05h30 | 0.89912 | 0.59725 | 0.43825 | 0.27525 | 0.21738
06h30 | 68.04 | 47.78 | 35.06 | 21.54 | 16.62 | 06h30 | 0.8505 | 0.59725 | 0.43825 | 0.26925 | 0.20775
07h30 | 70.73 | 44.34 | 38.96 | 25.06 | 21.14 | 07h30 | 0.88413 | 0.55425 | 0.487 | 0.31325 | 0.26425
08h30 | 70.73 | 44.34 | 38.96 | 25.06 | 21.14 | 08h30 | 0.88413 | 0.55425 | 0.487 | 0.31325 | 0.26425
09h30 | 69.58 | 43.38 | 36.06 | 22.29 | 17.88 | 09h30 | 0.86975 | 0.54225 | 0.45075 | 0.27863 | 0.2235
10h30 | 72.95 | 47.81 | 37.82 | 24.47 | 19.75 | 10h30 | 0.91187 | 0.59762 | 0.47275 | 0.30588 | 0.24688
11h30 | 75.23 | 50.79 | 38.62 | 25.53 | 20.42 | 11h30 | 0.94037 | 0.63487 | 0.48275 | 0.31912 | 0.25525
12h30 | 81.62 | 57.77 | 42.35 | 29.35 | 23.66 | 12h30 | 1.0203 | 0.72213 | 0.52938 | 0.36688 | 0.29575
13h30 | 89.65 | 66.38 | 47.42 | 34.14 | 27.81 | 13h30 | 1.1206 | 0.82975 | 0.59275 | 0.42675 | 0.34763
14h30 | 95.38 | 72.62 | 51.3 | 37.78 | 31 | 14h30 | 1.1923 | 0.90775 | 0.64125 | 0.47225 | 0.3875
15h30 | 99.25 | 76.98 | 54.03 | 40.57 | 33.33 | 15h30 | 1.2406 | 0.96225 | 0.67537 | 0.50713 | 0.41663
16h30 | 102.6 | 80.87 | 56.36 | 42.99 | 35.3 | 16h30 | 1.2825 | 1.0109 | 0.7045 | 0.53738 | 0.44125
17h30 | 94.34 | 73.13 | 51.82 | 38.08 | 31.05 | 17h30 | 1.1792 | 0.91412 | 0.64775 | 0.476 | 0.38812
18h30 | 81.52 | 60.76 | 44.49 | 30.47 | 24.46 | 18h30 | 1.019 | 0.7595 | 0.55612 | 0.38088 | 0.30575
19h30 | 92.38 | 72 | 51.25 | 37.18 | 30.49 | 19h30 | 1.1547 | 0.9 | 0.64062 | 0.46475 | 0.38112
20h30 | 103.25 | 83.19 | 58.07 | 43.79 | 36.52 | 20h30 | 1.2906 | 1.0399 | 0.72588 | 0.54737 | 0.4565
21h30 | 94.72 | 74.92 | 53.17 | 38.87 | 32.31 | 21h30 | 1.184 | 0.9365 | 0.66463 | 0.48588 | 0.40387
22h30 | 78.94 | 59.37 | 43.84 | 29.6 | 24.12 | 22h30 | 0.98675 | 0.74213 | 0.548 | 0.37 | 0.3015
23h30 | 67.57 | 48.17 | 36.96 | 23.05 | 18.28 | 23h30 | 0.84462 | 0.60213 | 0.462 | 0.28813 | 0.2285
00h30 | 66.45 | 43.35 | 35.09 | 21.25 | 16.77 | 00h30 | 0.83062 | 0.54187 | 0.43862 | 0.26562 | 0.20963
01h30 | 30.17 | 11.81 | 9.43 | 0 | 0 | 01h30 | 0.37712 | 0.14763 | 0.11787 | 0 | 0
02h30 | 36.26 | 19.37 | 15.44 | 3.86 | 0.32 | 02h30 | 0.45325 | 0.24213 | 0.193 | 0.04825 | 0.004
03h30 | 38.93 | 22.24 | 17.32 | 6.55 | 3.69 | 03h30 | 0.48662 | 0.278 | 0.2165 | 0.081875 | 0.046125
04h30 | 41.09 | 23.65 | 18.58 | 7.44 | 4.36 | 04h30 | 0.51362 | 0.29563 | 0.23225 | 0.093 | 0.0545
05h30 | 42.56 | 24.66 | 19.44 | 8.25 | 5.02 | 05h30 | 0.532 | 0.30825 | 0.243 | 0.10312 | 0.06275
06h30 | 39.72 | 21.4 | 17.75 | 6.43 | 4.04 | 06h30 | 0.4965 | 0.2675 | 0.22187 | 0.080375 | 0.0505
07h30 | 50.3 | 30.12 | 29.08 | 16.36 | 13 | 07h30 | 0.62875 | 0.3765 | 0.3635 | 0.2045 | 0.1625
08h30 | 44.9 | 24.4 | 23.51 | 13.44 | 13 | 08h30 | 0.56125 | 0.305 | 0.29387 | 0.168 | 0.1625
09h30 | 48.39 | 26.97 | 25.77 | 11.76 | 7.74 | 09h30 | 0.60488 | 0.33713 | 0.32212 | 0.147 | 0.09675
10h30 | 57.97 | 37.06 | 31.04 | 17.43 | 13.42 | 10h30 | 0.72462 | 0.46325 | 0.388 | 0.21788 | 0.16775
11h30 | 62.82 | 42.11 | 33.12 | 19.6 | 14.99 | 11h30 | 0.78525 | 0.52638 | 0.414 | 0.245 | 0.18738
12h30 | 54.26 | 33.81 | 27.85 | 14.52 | 10.32 | 12h30 | 0.67825 | 0.42262 | 0.34813 | 0.1815 | 0.129
13h30 | 48.48 | 28.18 | 22.98 | 11.04 | 7.15 | 13h30 | 0.606 | 0.35225 | 0.28725 | 0.138 | 0.089375
14h30 | 48.99 | 28.73 | 23.48 | 11.38 | 7.48 | 14h30 | 0.61238 | 0.35913 | 0.2935 | 0.14225 | 0.0935
15h30 | 54.5 | 34.31 | 27.03 | 14.94 | 10.72 | 15h30 | 0.68125 | 0.42888 | 0.33787 | 0.18675 | 0.134
16h30 | 60.44 | 40.39 | 31.06 | 18.69 | 14.16 | 16h30 | 0.7555 | 0.50487 | 0.38825 | 0.23362 | 0.177
17h30 | 56.66 | 36.76 | 29.09 | 16.57 | 12.35 | 17h30 | 0.70825 | 0.4595 | 0.36362 | 0.20713 | 0.15438
18h30 | 52.28 | 32.51 | 26.52 | 14.15 | 10.24 | 18h30 | 0.6535 | 0.40637 | 0.3315 | 0.17688 | 0.128
19h30 | 52.04 | 32.36 | 26.33 | 14.14 | 10.24 | 19h30 | 0.6505 | 0.4045 | 0.32913 | 0.17675 | 0.128
20h30 | 51.49 | 31.85 | 25.95 | 13.78 | 9.92 | 20h30 | 0.64363 | 0.39813 | 0.32438 | 0.17225 | 0.124
21h30 | 51.48 | 31.81 | 25.96 | 13.64 | 9.81 | 21h30 | 0.6435 | 0.39763 | 0.3245 | 0.1705 | 0.12262
22h30 | 51.26 | 31.53 | 25.76 | 13.48 | 9.66 | 22h30 | 0.64075 | 0.39413 | 0.322 | 0.1685 | 0.12075
23h30 | 51.17 | 31.36 | 25.53 | 13.43 | 9.6 | 23h30 | 0.63962 | 0.392 | 0.31912 | 0.16787 | 0.12
00h30 | 48.84 | 27.97 | 24.15 | 11.68 | 7.4 | 00h30 | 0.6105 | 0.34963 | 0.30188 | 0.146 | 0.0925
01h30 | 33.63 | 15.26 | 10.83 | 0 | 0 | 01h30 | 0.42037 | 0.19075 | 0.13537 | 0 | 0
02h30 | 34.1 | 16.58 | 12.87 | 3.02 | 0 | 02h30 | 0.42625 | 0.20725 | 0.16087 | 0.03775 | 0
03h30 | 50.79 | 32.98 | 22.94 | 13.03 | 9.34 | 03h30 | 0.63487 | 0.41225 | 0.28675 | 0.16287 | 0.11675
04h30 | 65.07 | 46.6 | 31.64 | 21.29 | 16.4 | 04h30 | 0.81337 | 0.5825 | 0.3955 | 0.26613 | 0.205
05h30 | 59.55 | 40.65 | 28.49 | 17.73 | 13.18 | 05h30 | 0.74438 | 0.50813 | 0.35613 | 0.22162 | 0.16475
06h30 | 53.23 | 33.94 | 24.87 | 13.72 | 9.69 | 06h30 | 0.66538 | 0.42425 | 0.31088 | 0.1715 | 0.12112
07h30 | 70.95 | 49.74 | 40.44 | 27.84 | 22.98 | 07h30 | 0.88687 | 0.62175 | 0.5055 | 0.348 | 0.28725
08h30 | 68.11 | 45.46 | 35.8 | 22.5 | 19.42 | 08h30 | 0.85137 | 0.56825 | 0.4475 | 0.28125 | 0.24275
09h30 | 61.84 | 39.79 | 32.44 | 20.13 | 15.43 | 09h30 | 0.773 | 0.49738 | 0.4055 | 0.25162 | 0.19287
10h30 | 56.25 | 35.84 | 29.97 | 18.2 | 15.43 | 10h30 | 0.70312 | 0.448 | 0.37462 | 0.2275 | 0.19287
11h30 | 53.27 | 31.8 | 25.31 | 13.88 | 9.19 | 11h30 | 0.66587 | 0.3975 | 0.31638 | 0.1735 | 0.11488
12h30 | 60.01 | 39.19 | 29.41 | 18.13 | 13.19 | 12h30 | 0.75013 | 0.48988 | 0.36762 | 0.22662 | 0.16487
13h30 | 64.42 | 43.83 | 32.03 | 20.43 | 15.06 | 13h30 | 0.80525 | 0.54788 | 0.40037 | 0.25538 | 0.18825
14h30 | 61.37 | 41.02 | 30.33 | 18.9 | 13.78 | 14h30 | 0.76712 | 0.51275 | 0.37912 | 0.23625 | 0.17225
15h30 | 63.26 | 43.13 | 31.64 | 20.47 | 15.27 | 15h30 | 0.79075 | 0.53912 | 0.3955 | 0.25588 | 0.19087
16h30 | 70.88 | 51.03 | 36.59 | 25.24 | 19.53 | 16h30 | 0.886 | 0.63787 | 0.45737 | 0.3155 | 0.24413
17h30 | 73.35 | 53.8 | 38.33 | 26.93 | 21.04 | 17h30 | 0.91687 | 0.6725 | 0.47913 | 0.33663 | 0.263
18h30 | 77.8 | 58.51 | 41.13 | 29.75 | 23.59 | 18h30 | 0.9725 | 0.73137 | 0.51413 | 0.37188 | 0.29487
19h30 | 82.49 | 63.41 | 44.12 | 32.57 | 26.14 | 19h30 | 1.0311 | 0.79263 | 0.5515 | 0.40713 | 0.32675
20h30 | 81.18 | 62.26 | 43.44 | 31.86 | 25.53 | 20h30 | 1.0148 | 0.77825 | 0.543 | 0.39825 | 0.31912
21h30 | 87.35 | 68.55 | 47.25 | 35.56 | 28.86 | 21h30 | 1.0919 | 0.85688 | 0.59062 | 0.4445 | 0.36075
22h30 | 103.35 | 84.63 | 57 | 45.05 | 37.3 | 22h30 | 1.2919 | 1.0579 | 0.7125 | 0.56312 | 0.46625
23h30 | 107.55 | 88.88 | 59.66 | 47.48 | 39.45 | 23h30 | 1.3444 | 1.111 | 0.74575 | 0.5935 | 0.49312
00h30 | 77.1 | 56.75 | 40.43 | 28.38 | 22.07 | 00h30 | 0.96375 | 0.70937 | 0.50538 | 0.35475 | 0.27587
01h30 | 65.15 | 48.82 | 31.5 | 21.11 | 15.1 | 01h30 | 0.81437 | 0.61025 | 0.39375 | 0.26388 | 0.18875
02h30 | 65.15 | 48.82 | 31.5 | 21.11 | 15.1 | 02h30 | 0.81437 | 0.61025 | 0.39375 | 0.26388 | 0.18875
03h30 | 63.35 | 46.4 | 30.96 | 20.08 | 15.47 | 03h30 | 0.79187 | 0.58 | 0.387 | 0.251 | 0.19337
04h30 | 84.92 | 67.97 | 44.69 | 33.15 | 26.44 | 04h30 | 1.0615 | 0.84962 | 0.55863 | 0.41437 | 0.3305
05h30 | 102.3 | 85.06 | 55.36 | 43.61 | 35.33 | 05h30 | 1.2788 | 1.0633 | 0.692 | 0.54512 | 0.44162
06h30 | 101.38 | 83.83 | 54.71 | 43.11 | 34.64 | 06h30 | 1.2672 | 1.0479 | 0.68388 | 0.53887 | 0.433
07h30 | 120.65 | 102.17 | 71.55 | 58.55 | 48.99 | 07h30 | 1.5081 | 1.2771 | 0.89438 | 0.73188 | 0.61238
08h30 | 130.18 | 109.73 | 74.06 | 59.86 | 49.15 | 08h30 | 1.6273 | 1.3716 | 0.92575 | 0.74825 | 0.61438
09h30 | 130.18 | 112.8 | 76.28 | 62.4 | 52.05 | 09h30 | 1.6273 | 1.41 | 0.9535 | 0.78 | 0.65063
10h30 | 129.66 | 110.71 | 74.21 | 60.35 | 50.09 | 10h30 | 1.6207 | 1.3839 | 0.92763 | 0.75438 | 0.62613
11h30 | 129.66 | 120.33 | 79.47 | 65.5 | 54.44 | 11h30 | 1.6207 | 1.5041 | 0.99338 | 0.81875 | 0.6805
12h30 | 148.27 | 131.69 | 85.93 | 71.96 | 59.81 | 12h30 | 1.8534 | 1.6461 | 1.0741 | 0.8995 | 0.74762
13h30 | 148.27 | 135.34 | 87.74 | 74.12 | 61.3 | 13h30 | 1.8534 | 1.6918 | 1.0967 | 0.9265 | 0.76625
14h30 | 153.22 | 136.06 | 88.02 | 74.57 | 61.51 | 14h30 | 1.9152 | 1.7007 | 1.1002 | 0.93212 | 0.76887
15h30 | 151.5 | 133.47 | 86.65 | 72.99 | 60.17 | 15h30 | 1.8938 | 1.6684 | 1.0831 | 0.91238 | 0.75213
16h30 | 143.12 | 124.94 | 81.57 | 68.03 | 55.73 | 16h30 | 1.789 | 1.5617 | 1.0196 | 0.85037 | 0.69663
17h30 | 139.06 | 121.33 | 79.28 | 65.96 | 53.94 | 17h30 | 1.7383 | 1.5166 | 0.991 | 0.8245 | 0.67425
18h30 | 135.85 | 118.43 | 77.46 | 64.18 | 52.61 | 18h30 | 1.6981 | 1.4804 | 0.96825 | 0.80225 | 0.65763
19h30 | 122.5 | 105.32 | 69.41 | 56.49 | 45.99 | 19h30 | 1.5312 | 1.3165 | 0.86762 | 0.70613 | 0.57488
20h30 | 118.14 | 101.18 | 66.85 | 53.98 | 43.96 | 20h30 | 1.4768 | 1.2648 | 0.83562 | 0.67475 | 0.5495
21h30 | 128.85 | 112.12 | 73.58 | 60.24 | 49.34 | 21h30 | 1.6106 | 1.4015 | 0.91975 | 0.753 | 0.61675
22h30 | 133.18 | 116.64 | 76.26 | 62.9 | 51.31 | 22h30 | 1.6647 | 1.458 | 0.95325 | 0.78625 | 0.64138
23h30 | 132.13 | 115.74 | 75.49 | 62.41 | 50.66 | 23h30 | 1.6516 | 1.4467 | 0.94363 | 0.78012 | 0.63325
00h30 | 109.74 | 94.48 | 62.01 | 50.26 | 42.46 | 00h30 | 1.3718 | 1.181 | 0.77512 | 0.62825 | 0.53075
01h30 | 112.18 | 98.34 | 61.69 | 50.9 | 39.38 | 01h30 | 1.4022 | 1.2292 | 0.77112 | 0.63625 | 0.49225
02h30 | 127.6 | 113.78 | 70.89 | 60.84 | 48.57 | 02h30 | 1.595 | 1.4223 | 0.88613 | 0.7605 | 0.60713
03h30 | 134.62 | 121.01 | 79.32 | 68.83 | 55.86 | 03h30 | 1.6827 | 1.5126 | 0.9915 | 0.86038 | 0.69825
04h30 | 146.44 | 132.22 | 83.28 | 72.67 | 59.6 | 04h30 | 1.8305 | 1.6527 | 1.041 | 0.90838 | 0.745
05h30 | 140.39 | 125.33 | 78.63 | 68.04 | 55.86 | 05h30 | 1.7549 | 1.5666 | 0.98288 | 0.8505 | 0.69825
06h30 | 118.41 | 103.12 | 65.54 | 54.26 | 44.07 | 06h30 | 1.4801 | 1.289 | 0.81925 | 0.67825 | 0.55088
07h30 | 116.82 | 99.93 | 69.81 | 56.22 | 46.44 | 07h30 | 1.4603 | 1.2491 | 0.87262 | 0.70275 | 0.5805
08h30 | 98.67 | 89.92 | 69.73 | 56.22 | 45.31 | 08h30 | 1.2334 | 1.124 | 0.87162 | 0.70275 | 0.56637
09h30 | 100.92 | 83.63 | 56.5 | 43.25 | 35.71 | 09h30 | 1.2615 | 1.0454 | 0.70625 | 0.54063 | 0.44638
10h30 | 120.21 | 103.43 | 67.34 | 54.59 | 45.62 | 10h30 | 1.5026 | 1.2929 | 0.84175 | 0.68237 | 0.57025
11h30 | 125.59 | 114.11 | 72.88 | 58.85 | 49.28 | 11h30 | 1.5699 | 1.4264 | 0.911 | 0.73562 | 0.616
12h30 | 127.05 | 111.66 | 71.55 | 57.16 | 47.35 | 12h30 | 1.5881 | 1.3958 | 0.89438 | 0.7145 | 0.59188
13h30 | 125.9 | 110.12 | 69.7 | 56.61 | 46.43 | 13h30 | 1.5737 | 1.3765 | 0.87125 | 0.70762 | 0.58037
14h30 | 125.08 | 109.56 | 68.91 | 55.84 | 45.94 | 14h30 | 1.5635 | 1.3695 | 0.86138 | 0.698 | 0.57425
15h30 | 114.74 | 99.7 | 64.19 | 49.78 | 41.15 | 15h30 | 1.4343 | 1.2463 | 0.80237 | 0.62225 | 0.51438
16h30 | 97.78 | 82.9 | 55.47 | 40.9 | 33.66 | 16h30 | 1.2223 | 1.0362 | 0.69337 | 0.51125 | 0.42075
17h30 | 89.79 | 75.28 | 51.24 | 37.07 | 30.51 | 17h30 | 1.1224 | 0.941 | 0.6405 | 0.46337 | 0.38138
18h30 | 89.69 | 75.44 | 51.85 | 37.07 | 30.59 | 18h30 | 1.1211 | 0.943 | 0.64812 | 0.46337 | 0.38238
19h30 | 84.36 | 70.1 | 49.3 | 33.44 | 27.56 | 19h30 | 1.0545 | 0.87625 | 0.61625 | 0.418 | 0.3445
20h30 | 87.7 | 73.2 | 51.82 | 35.07 | 29.1 | 20h30 | 1.0962 | 0.915 | 0.64775 | 0.43838 | 0.36375
21h30 | 93.09 | 78.16 | 55.39 | 37.76 | 31.64 | 21h30 | 1.1636 | 0.977 | 0.69237 | 0.472 | 0.3955
22h30 | 89.19 | 74.89 | 52.95 | 36.13 | 30.02 | 22h30 | 1.1149 | 0.93612 | 0.66187 | 0.45162 | 0.37525
23h30 | 90.17 | 73.94 | 53.2 | 35.35 | 29.54 | 23h30 | 1.1271 | 0.92425 | 0.665 | 0.44188 | 0.36925
00h30 | 81.68 | 73.94 | 52.51 | 35.35 | 29.54 | 00h30 | 1.021 | 0.92425 | 0.65638 | 0.44188 | 0.36925
01h30 | 75.25 | 59.96 | 40.48 | 24.97 | 19.84 | 01h30 | 0.94063 | 0.7495 | 0.506 | 0.31212 | 0.248
02h30 | 75.13 | 59.96 | 40.48 | 24.97 | 19.84 | 02h30 | 0.93912 | 0.7495 | 0.506 | 0.31212 | 0.248
03h30 | 66.49 | 46 | 32.37 | 18.23 | 14.92 | 03h30 | 0.83113 | 0.575 | 0.40463 | 0.22787 | 0.1865
04h30 | 84.59 | 65.63 | 45.37 | 30.57 | 25.57 | 04h30 | 1.0574 | 0.82037 | 0.56712 | 0.38212 | 0.31962
05h30 | 84.03 | 64.39 | 45.15 | 30 | 25.28 | 05h30 | 1.0504 | 0.80488 | 0.56437 | 0.375 | 0.316
06h30 | 75.69 | 54.87 | 39.73 | 24.57 | 20.24 | 06h30 | 0.94612 | 0.68588 | 0.49662 | 0.30712 | 0.253
07h30 | 90.06 | 66.65 | 52.84 | 36.13 | 30.56 | 07h30 | 1.1258 | 0.83313 | 0.6605 | 0.45162 | 0.382
08h30 | 84.22 | 58.77 | 46.11 | 29.22 | 24.96 | 08h30 | 1.0528 | 0.73462 | 0.57637 | 0.36525 | 0.312
09h30 | 73.59 | 48.38 | 39.17 | 22.97 | 18.33 | 09h30 | 0.91987 | 0.60475 | 0.48962 | 0.28713 | 0.22912
10h30 | 69.67 | 46.14 | 38.31 | 22.97 | 18.33 | 10h30 | 0.87087 | 0.57675 | 0.47887 | 0.28713 | 0.22912
11h30 | 75.7 | 50.65 | 36.98 | 21.73 | 16.76 | 11h30 | 0.94625 | 0.63313 | 0.46225 | 0.27163 | 0.2095
12h30 | 85.65 | 60.94 | 43.6 | 27.96 | 22.46 | 12h30 | 1.0706 | 0.76175 | 0.545 | 0.3495 | 0.28075
13h30 | 98.53 | 73.93 | 50.73 | 35.85 | 29.56 | 13h30 | 1.2316 | 0.92412 | 0.63413 | 0.44812 | 0.3695
14h30 | 121.17 | 96.9 | 64.54 | 49.62 | 42.05 | 14h30 | 1.5146 | 1.2112 | 0.80675 | 0.62025 | 0.52563
15h30 | 124.63 | 100.48 | 67.51 | 51.9 | 44.36 | 15h30 | 1.5579 | 1.256 | 0.84388 | 0.64875 | 0.5545
16h30 | 95.67 | 71.69 | 51.03 | 35.15 | 29.34 | 16h30 | 1.1959 | 0.89612 | 0.63787 | 0.43938 | 0.36675
17h30 | 59.96 | 36.3 | 30.19 | 14.24 | 10.35 | 17h30 | 0.7495 | 0.45375 | 0.37738 | 0.178 | 0.12937
18h30 | 66.2 | 42.83 | 34.36 | 18.09 | 13.89 | 18h30 | 0.8275 | 0.53538 | 0.4295 | 0.22612 | 0.17363
19h30 | 93.78 | 70.58 | 51.38 | 34.45 | 28.8 | 19h30 | 1.1723 | 0.88225 | 0.64225 | 0.43062 | 0.36
20h30 | 100.35 | 77.19 | 55.67 | 38.21 | 32.23 | 20h30 | 1.2544 | 0.96488 | 0.69588 | 0.47763 | 0.40287
21h30 | 116.45 | 97.38 | 67.94 | 50.31 | 43.26 | 21h30 | 1.4556 | 1.2172 | 0.84925 | 0.62887 | 0.54075
22h30 | 139.81 | 117.39 | 80.04 | 62.32 | 54.21 | 22h30 | 1.7476 | 1.4674 | 1.0005 | 0.779 | 0.67763
23h30 | 139.81 | 117.56 | 80.2 | 62.42 | 54.32 | 23h30 | 1.7476 | 1.4695 | 1.0025 | 0.78025 | 0.679
00h30 | 116.97 | 94.29 | 59.99 | 43.24 | 35.64 | 00h30 | 1.4621 | 1.1786 | 0.74987 | 0.5405 | 0.4455
01h30 | 110.09 | 88.69 | 58.63 | 44.35 | 37.85 | 01h30 | 1.3761 | 1.1086 | 0.73288 | 0.55437 | 0.47313
02h30 | 93.12 | 74.33 | 54.34 | 40.64 | 35.43 | 02h30 | 1.164 | 0.92912 | 0.67925 | 0.508 | 0.44288
03h30 | 62.44 | 39.55 | 28.34 | 14.38 | 10.54 | 03h30 | 0.7805 | 0.49438 | 0.35425 | 0.17975 | 0.13175
04h30 | 62.44 | 39.55 | 28.34 | 14.38 | 10.54 | 04h30 | 0.7805 | 0.49438 | 0.35425 | 0.17975 | 0.13175
05h30 | 54.92 | 29.23 | 23.77 | 9.01 | 5.28 | 05h30 | 0.6865 | 0.36538 | 0.29712 | 0.11263 | 0.066
06h30 | 76.75 | 52.81 | 38.61 | 23.63 | 19.12 | 06h30 | 0.95937 | 0.66012 | 0.48263 | 0.29537 | 0.239
07h30 | 114.05 | 88.34 | 66.43 | 49.58 | 43.43 | 07h30 | 1.4256 | 1.1042 | 0.83037 | 0.61975 | 0.54287
08h30 | 118.75 | 91.35 | 66.49 | 48.43 | 41.57 | 08h30 | 1.4844 | 1.1419 | 0.83113 | 0.60537 | 0.51963
09h30 | 95.2 | 68.69 | 51.79 | 35.23 | 29.8 | 09h30 | 1.19 | 0.85862 | 0.64738 | 0.44038 | 0.3725
10h30 | 68.66 | 42.1 | 36.89 | 21.77 | 17.81 | 10h30 | 0.85825 | 0.52625 | 0.46113 | 0.27213 | 0.22262
11h30 | 43.42 | 17.65 | 15.69 | 0.7 | 0 | 11h30 | 0.54275 | 0.22062 | 0.19612 | 0.00875 | 0
12h30 | 48.61 | 24.33 | 20.23 | 6.08 | 2.29 | 12h30 | 0.60762 | 0.30412 | 0.25288 | 0.076 | 0.028625
13h30 | 45.62 | 22.49 | 17.78 | 5.38 | 2.29 | 13h30 | 0.57025 | 0.28113 | 0.22225 | 0.06725 | 0.028625
14h30 | 46.42 | 24.19 | 18.34 | 6.14 | 2.47 | 14h30 | 0.58025 | 0.30238 | 0.22925 | 0.07675 | 0.030875
15h30 | 42.82 | 21.05 | 17.98 | 6.14 | 2.47 | 15h30 | 0.53525 | 0.26312 | 0.22475 | 0.07675 | 0.030875
16h30 | 43.55 | 22.3 | 20.21 | 5.12 | 1.85 | 16h30 | 0.54438 | 0.27875 | 0.25262 | 0.064 | 0.023125
17h30 | 43.93 | 23.52 | 21.43 | 7.3 | 3.98 | 17h30 | 0.54912 | 0.294 | 0.26787 | 0.09125 | 0.04975
18h30 | 39.47 | 19.81 | 19.86 | 4.33 | 2.13 | 18h30 | 0.49338 | 0.24763 | 0.24825 | 0.054125 | 0.026625
19h30 | 70.2 | 51.02 | 39.36 | 22.39 | 17.42 | 19h30 | 0.8775 | 0.63775 | 0.492 | 0.27987 | 0.21775
20h30 | 109.64 | 90.64 | 63.46 | 46.06 | 38.99 | 20h30 | 1.3705 | 1.133 | 0.79325 | 0.57575 | 0.48738
21h30 | 125.31 | 106.27 | 73.19 | 55.15 | 47.2 | 21h30 | 1.5664 | 1.3284 | 0.91487 | 0.68937 | 0.59
22h30 | 87.46 | 68.27 | 50.71 | 32.09 | 26.39 | 22h30 | 1.0933 | 0.85337 | 0.63387 | 0.40113 | 0.32987
23h30 | 91.82 | 72.37 | 53.15 | 34.62 | 28.58 | 23h30 | 1.1478 | 0.90463 | 0.66438 | 0.43275 | 0.35725
00h30 | 123.61 | 104.9 | 66.52 | 48.74 | 39.83 | 00h30 | 1.5451 | 1.3113 | 0.8315 | 0.60925 | 0.49788
01h30 | 134.93 | 117.22 | 76.17 | 60.46 | 51.09 | 01h30 | 1.6866 | 1.4652 | 0.95212 | 0.75575 | 0.63862
02h30 | 141.51 | 123.35 | 79.65 | 65.15 | 55.65 | 02h30 | 1.7689 | 1.5419 | 0.99562 | 0.81437 | 0.69563
03h30 | 142.24 | 137.59 | 88.8 | 73.42 | 63.4 | 03h30 | 1.778 | 1.7199 | 1.11 | 0.91775 | 0.7925
04h30 | 164.79 | 148.35 | 95.89 | 79.83 | 69.07 | 04h30 | 2.0599 | 1.8544 | 1.1986 | 0.99787 | 0.86338
05h30 | 150.8 | 130.67 | 85.47 | 69.68 | 59.9 | 05h30 | 1.885 | 1.6334 | 1.0684 | 0.871 | 0.74875
06h30 | 90.1 | 73.71 | 54.15 | 41.71 | 37.65 | 06h30 | 1.1262 | 0.92138 | 0.67688 | 0.52138 | 0.47063
07h30 | 98.53 | 74.59 | 58.66 | 38.57 | 31.68 | 07h30 | 1.2316 | 0.93237 | 0.73325 | 0.48213 | 0.396
08h30 | 149.95 | 125.6 | 88.02 | 68.33 | 59.46 | 08h30 | 1.8744 | 1.57 | 1.1002 | 0.85413 | 0.74325
09h30 | 155.5 | 144.26 | 99.28 | 78.27 | 68.2 | 09h30 | 1.9438 | 1.8033 | 1.241 | 0.97837 | 0.8525
10h30 | 161.04 | 139.1 | 95.06 | 74.59 | 64.57 | 10h30 | 2.013 | 1.7388 | 1.1883 | 0.93237 | 0.80712
11h30 | 153.19 | 128.94 | 87.71 | 68.23 | 58.64 | 11h30 | 1.9149 | 1.6118 | 1.0964 | 0.85288 | 0.733
12h30 | 149.66 | 125.14 | 84.72 | 65.54 | 56.16 | 12h30 | 1.8707 | 1.5642 | 1.059 | 0.81925 | 0.702
13h30 | 146.71 | 122.91 | 82.9 | 64.05 | 54.59 | 13h30 | 1.8339 | 1.5364 | 1.0362 | 0.80063 | 0.68237
14h30 | 150.05 | 126.64 | 85.34 | 66.14 | 56.57 | 14h30 | 1.8756 | 1.583 | 1.0668 | 0.82675 | 0.70713
15h30 | 102.31 | 79.14 | 57.91 | 37.51 | 31.06 | 15h30 | 1.2789 | 0.98925 | 0.72388 | 0.46887 | 0.38825
16h30 | 51.24 | 33.35 | 33.31 | 12.03 | 7.42 | 16h30 | 0.6405 | 0.41687 | 0.41637 | 0.15038 | 0.09275
17h30 | 52.44 | 29.42 | 29.41 | 7.26 | 4.07 | 17h30 | 0.6555 | 0.36775 | 0.36762 | 0.09075 | 0.050875
18h30 | 53.77 | 31.67 | 31.66 | 8.75 | 5.39 | 18h30 | 0.67212 | 0.39587 | 0.39575 | 0.10938 | 0.067375
19h30 | 53.56 | 31.06 | 31.05 | 8.62 | 5.36 | 19h30 | 0.6695 | 0.38825 | 0.38812 | 0.10775 | 0.067
20h30 | 52.39 | 29.97 | 29.96 | 8.64 | 5.38 | 20h30 | 0.65487 | 0.37462 | 0.3745 | 0.108 | 0.06725
21h30 | 51.49 | 28.97 | 28.96 | 8.47 | 5.25 | 21h30 | 0.64363 | 0.36212 | 0.362 | 0.10587 | 0.065625
22h30 | 50.27 | 27.81 | 27.8 | 8.27 | 5.09 | 22h30 | 0.62838 | 0.34763 | 0.3475 | 0.10337 | 0.063625
23h30 | 58.65 | 35.65 | 31.85 | 13.71 | 10.08 | 23h30 | 0.73313 | 0.44562 | 0.39813 | 0.17137 | 0.126
00h30 | 49.94 | 35.65 | 31.85 | 12.39 | 8.9 | 00h30 | 0.62425 | 0.44562 | 0.39813 | 0.15488 | 0.11125
01h30 | 46.21 | 24.43 | 19.51 | 4.77 | 1.53 | 01h30 | 0.57763 | 0.30538 | 0.24388 | 0.059625 | 0.019125
02h30 | 46.21 | 24.43 | 19.51 | 4.77 | 1.53 | 02h30 | 0.57763 | 0.30538 | 0.24388 | 0.059625 | 0.019125
03h30 | 41.1 | 17.63 | 16.86 | 2.58 | 0.5 | 03h30 | 0.51375 | 0.22037 | 0.21075 | 0.03225 | 0.00625
04h30 | 47.04 | 23.94 | 21.01 | 6.56 | 3.77 | 04h30 | 0.588 | 0.29925 | 0.26262 | 0.082 | 0.047125
05h30 | 44.4 | 20.91 | 19.62 | 5.08 | 3.27 | 05h30 | 0.555 | 0.26138 | 0.24525 | 0.0635 | 0.040875
06h30 | 42.19 | 18.11 | 18.14 | 3.71 | 0.87 | 06h30 | 0.52738 | 0.22637 | 0.22675 | 0.046375 | 0.010875
07h30 | 59.82 | 33.68 | 33.7 | 17.95 | 14.8 | 07h30 | 0.74775 | 0.421 | 0.42125 | 0.22437 | 0.185
08h30 | 56.22 | 30.17 | 31.04 | 15.33 | 13.92 | 08h30 | 0.70275 | 0.37712 | 0.388 | 0.19162 | 0.174
09h30 | 52.26 | 25.13 | 25.04 | 9.91 | 6.3 | 09h30 | 0.65325 | 0.31412 | 0.313 | 0.12387 | 0.07875
10h30 | 52.14 | 25.13 | 25.04 | 9.91 | 6.3 | 10h30 | 0.65175 | 0.31412 | 0.313 | 0.12387 | 0.07875
11h30 | 49.76 | 23.5 | 20.18 | 5.88 | 2.48 | 11h30 | 0.622 | 0.29375 | 0.25225 | 0.0735 | 0.031
12h30 | 62.59 | 37.12 | 29.08 | 14.69 | 10.58 | 12h30 | 0.78238 | 0.464 | 0.3635 | 0.18363 | 0.13225
13h30 | 58.17 | 33.23 | 26.63 | 12.81 | 8.94 | 13h30 | 0.72713 | 0.41537 | 0.33287 | 0.16012 | 0.11175
14h30 | 46.89 | 22.27 | 20.38 | 6.7 | 3.49 | 14h30 | 0.58613 | 0.27837 | 0.25475 | 0.08375 | 0.043625
15h30 | 43.38 | 19.16 | 19.13 | 5.13 | 2.65 | 15h30 | 0.54225 | 0.2395 | 0.23913 | 0.064125 | 0.033125
16h30 | 44.16 | 20.39 | 20.37 | 6.15 | 3.1 | 16h30 | 0.552 | 0.25488 | 0.25462 | 0.076875 | 0.03875
17h30 | 62.65 | 39.31 | 32.05 | 17.57 | 13.65 | 17h30 | 0.78312 | 0.49138 | 0.40063 | 0.21962 | 0.17062
18h30 | 64.16 | 41.15 | 33.9 | 18 | 14.01 | 18h30 | 0.802 | 0.51438 | 0.42375 | 0.225 | 0.17513
19h30 | 81.7 | 58.89 | 45.6 | 27.66 | 22.83 | 19h30 | 1.0212 | 0.73613 | 0.57 | 0.34575 | 0.28537
20h30 | 113.24 | 90.45 | 65.02 | 46.41 | 39.9 | 20h30 | 1.4155 | 1.1306 | 0.81275 | 0.58013 | 0.49875
21h30 | 79.96 | 57.08 | 44.91 | 26.64 | 21.89 | 21h30 | 0.9995 | 0.7135 | 0.56137 | 0.333 | 0.27363
22h30 | 49.67 | 26.63 | 26.61 | 8.38 | 5.27 | 22h30 | 0.62087 | 0.33287 | 0.33263 | 0.10475 | 0.065875
23h30 | 50.06 | 26.81 | 26.79 | 8.42 | 5.31 | 23h30 | 0.62575 | 0.33513 | 0.33487 | 0.10525 | 0.066375
00h30 | 44.99 | 19.97 | 19.94 | 3.8 | 1.41 | 00h30 | 0.56237 | 0.24963 | 0.24925 | 0.0475 | 0.017625
01h30 | 38.69 | 17.01 | 16.99 | 0 | 0 | 01h30 | 0.48363 | 0.21263 | 0.21238 | 0 | 0
02h30 | 40.91 | 19.45 | 19.43 | 1.54 | 0 | 02h30 | 0.51138 | 0.24313 | 0.24288 | 0.01925 | 0
03h30 | 41.74 | 19.75 | 19.73 | 2.52 | 0 | 03h30 | 0.52175 | 0.24688 | 0.24663 | 0.0315 | 0
04h30 | 87.91 | 65.2 | 47.45 | 29.78 | 24.22 | 04h30 | 1.0989 | 0.815 | 0.59313 | 0.37225 | 0.30275
05h30 | 134.09 | 110.88 | 75.21 | 57.22 | 48.74 | 05h30 | 1.6761 | 1.386 | 0.94012 | 0.71525 | 0.60925
06h30 | 136.49 | 112.86 | 76.48 | 58.66 | 49.8 | 06h30 | 1.7061 | 1.4107 | 0.956 | 0.73325 | 0.6225
07h30 | 150.8 | 137.01 | 97.2 | 77.83 | 68.04 | 07h30 | 1.885 | 1.7126 | 1.215 | 0.97288 | 0.8505
08h30 | 164.75 | 140.57 | 97.67 | 76.84 | 66.56 | 08h30 | 2.0594 | 1.7571 | 1.2209 | 0.9605 | 0.832
09h30 | 163.53 | 137.88 | 96.33 | 75.91 | 66.04 | 09h30 | 2.0441 | 1.7235 | 1.2041 | 0.94888 | 0.8255
10h30 | 164.77 | 138.1 | 95.56 | 75.3 | 65.38 | 10h30 | 2.0596 | 1.7263 | 1.1945 | 0.94125 | 0.81725
11h30 | 165.99 | 151.73 | 103.26 | 82.74 | 71.98 | 11h30 | 2.0749 | 1.8966 | 1.2908 | 1.0342 | 0.89975
12h30 | 174.82 | 152.33 | 103.14 | 82.85 | 71.81 | 12h30 | 2.1852 | 1.9041 | 1.2893 | 1.0356 | 0.89763
13h30 | 152.22 | 127.66 | 87.66 | 68.31 | 58.55 | 13h30 | 1.9027 | 1.5958 | 1.0958 | 0.85388 | 0.73188
14h30 | 126.48 | 101.36 | 71.3 | 53.01 | 44.73 | 14h30 | 1.581 | 1.267 | 0.89125 | 0.66263 | 0.55912
15h30 | 122.59 | 98 | 69.02 | 51.36 | 43.11 | 15h30 | 1.5324 | 1.225 | 0.86275 | 0.642 | 0.53887
16h30 | 128.21 | 104.17 | 72.61 | 55.18 | 46.34 | 16h30 | 1.6026 | 1.3021 | 0.90763 | 0.68975 | 0.57925
17h30 | 124.65 | 101.11 | 70.49 | 53.49 | 44.64 | 17h30 | 1.5581 | 1.2639 | 0.88113 | 0.66863 | 0.558
18h30 | 122.89 | 99.83 | 69.35 | 52.82 | 43.82 | 18h30 | 1.5361 | 1.2479 | 0.86687 | 0.66025 | 0.54775
19h30 | 121.65 | 99.06 | 68.69 | 52.25 | 43.29 | 19h30 | 1.5206 | 1.2383 | 0.85862 | 0.65312 | 0.54112
20h30 | 110.34 | 88.15 | 61.95 | 45.75 | 37.62 | 20h30 | 1.3793 | 1.1019 | 0.77438 | 0.57188 | 0.47025
21h30 | 102.54 | 80.76 | 57.15 | 41.56 | 33.78 | 21h30 | 1.2817 | 1.0095 | 0.71437 | 0.5195 | 0.42225
22h30 | 102.78 | 81.45 | 57.22 | 42.03 | 33.96 | 22h30 | 1.2848 | 1.0181 | 0.71525 | 0.52538 | 0.4245
23h30 | 120.03 | 99.14 | 67.58 | 52.58 | 42.92 | 23h30 | 1.5004 | 1.2392 | 0.84475 | 0.65725 | 0.5365
00h30 | 127.87 | 108.45 | 66.84 | 52.65 | 40.65 | 00h30 | 1.5984 | 1.3556 | 0.8355 | 0.65812 | 0.50813
01h30 | 141.93 | 124.22 | 78.65 | 65.71 | 52.86 | 01h30 | 1.7741 | 1.5528 | 0.98313 | 0.82137 | 0.66075
02h30 | 142.78 | 125.32 | 79.37 | 66.96 | 53.94 | 02h30 | 1.7848 | 1.5665 | 0.99213 | 0.837 | 0.67425
03h30 | 139.61 | 121.97 | 77.73 | 65.15 | 52.14 | 03h30 | 1.7451 | 1.5246 | 0.97162 | 0.81437 | 0.65175
04h30 | 132.6 | 114.95 | 73.76 | 61.05 | 48.65 | 04h30 | 1.6575 | 1.4369 | 0.922 | 0.76313 | 0.60813
05h30 | 120.94 | 103.34 | 66.89 | 54.34 | 42.79 | 05h30 | 1.5117 | 1.2917 | 0.83613 | 0.67925 | 0.53487
06h30 | 107.18 | 89.68 | 60.45 | 46.55 | 41.4 | 06h30 | 1.3397 | 1.121 | 0.75562 | 0.58188 | 0.5175
07h30 | 109 | 90.24 | 65.17 | 51.36 | 42.33 | 07h30 | 1.3625 | 1.128 | 0.81463 | 0.642 | 0.52912
08h30 | 101.03 | 81.4 | 65.17 | 51.36 | 42.33 | 08h30 | 1.2629 | 1.0175 | 0.81463 | 0.642 | 0.52912
09h30 | 104.46 | 85.68 | 60.72 | 46.11 | 36.59 | 09h30 | 1.3057 | 1.071 | 0.759 | 0.57637 | 0.45737
10h30 | 101.19 | 83.16 | 60.72 | 46.11 | 36.59 | 10h30 | 1.2649 | 1.0395 | 0.759 | 0.57637 | 0.45737
11h30 | 98.47 | 81.09 | 55.29 | 42 | 32.18 | 11h30 | 1.2309 | 1.0136 | 0.69112 | 0.525 | 0.40225
12h30 | 94.62 | 80.11 | 55.29 | 42 | 32.18 | 12h30 | 1.1827 | 1.0014 | 0.69112 | 0.525 | 0.40225
13h30 | 95.6 | 79.65 | 52.96 | 40.57 | 30.21 | 13h30 | 1.195 | 0.99562 | 0.662 | 0.50713 | 0.37762
14h30 | 99.29 | 83.5 | 55.35 | 43.05 | 32.28 | 14h30 | 1.2411 | 1.0437 | 0.69188 | 0.53812 | 0.4035
15h30 | 97.39 | 81.89 | 54.38 | 42.15 | 31.54 | 15h30 | 1.2174 | 1.0236 | 0.67975 | 0.52687 | 0.39425
16h30 | 109.01 | 94.06 | 61.73 | 49.63 | 37.7 | 16h30 | 1.3626 | 1.1758 | 0.77163 | 0.62038 | 0.47125
17h30 | 119.64 | 105.17 | 68.26 | 56.4 | 43 | 17h30 | 1.4955 | 1.3146 | 0.85325 | 0.705 | 0.5375
18h30 | 102.22 | 89.15 | 58.52 | 46.44 | 34.78 | 18h30 | 1.2777 | 1.1144 | 0.7315 | 0.5805 | 0.43475
19h30 | 94.67 | 81.18 | 53.57 | 41.74 | 31.01 | 19h30 | 1.1834 | 1.0148 | 0.66963 | 0.52175 | 0.38762
20h30 | 110.18 | 96.92 | 63.2 | 50.97 | 38.7 | 20h30 | 1.3773 | 1.2115 | 0.79 | 0.63713 | 0.48375
21h30 | 118.21 | 105.17 | 68.26 | 55.76 | 42.86 | 21h30 | 1.4776 | 1.3146 | 0.85325 | 0.697 | 0.53575
22h30 | 115.06 | 102.28 | 66.5 | 53.98 | 41.4 | 22h30 | 1.4383 | 1.2785 | 0.83125 | 0.67475 | 0.5175
23h30 | 114.75 | 102.19 | 66.29 | 53.97 | 41.1 | 23h30 | 1.4344 | 1.2774 | 0.82862 | 0.67463 | 0.51375
00h30 | 89.82 | 89.35 | 58.42 | 46.51 | 34.87 | 00h30 | 1.1227 | 1.1169 | 0.73025 | 0.58137 | 0.43588
01h30 | 85.67 | 77.69 | 47.4 | 37.03 | 24.68 | 01h30 | 1.0709 | 0.97113 | 0.5925 | 0.46287 | 0.3085
02h30 | 91.64 | 81.74 | 50.4 | 41.3 | 28.62 | 02h30 | 1.1455 | 1.0217 | 0.63 | 0.51625 | 0.35775
03h30 | 89.74 | 79.02 | 48.79 | 40.12 | 27.37 | 03h30 | 1.1218 | 0.98775 | 0.60987 | 0.5015 | 0.34213
04h30 | 83.77 | 74.96 | 45.79 | 35.84 | 23.44 | 04h30 | 1.0471 | 0.937 | 0.57237 | 0.448 | 0.293
05h30 | 76.32 | 65.48 | 40.56 | 31.55 | 20.93 | 05h30 | 0.954 | 0.8185 | 0.507 | 0.39437 | 0.26162
06h30 | 76.32 | 65.48 | 40.56 | 31.55 | 20.93 | 06h30 | 0.954 | 0.8185 | 0.507 | 0.39437 | 0.26162
07h30 | 100 | 99.83 | 66.84 | 56 | 41.91 | 07h30 | 1.25 | 1.2479 | 0.8355 | 0.7 | 0.52387
08h30 | 128.13 | 118.69 | 76.2 | 64.39 | 46.9 | 08h30 | 1.6016 | 1.4836 | 0.9525 | 0.80488 | 0.58625
09h30 | 125.79 | 113.21 | 72.92 | 61.94 | 45.76 | 09h30 | 1.5724 | 1.4151 | 0.9115 | 0.77425 | 0.572
10h30 | 121.27 | 108.39 | 68.49 | 58.11 | 42.6 | 10h30 | 1.5159 | 1.3549 | 0.85613 | 0.72637 | 0.5325
11h30 | 121.02 | 109.55 | 68.17 | 58 | 42.18 | 11h30 | 1.5128 | 1.3694 | 0.85213 | 0.725 | 0.52725
12h30 | 116.77 | 105.78 | 65.34 | 55.38 | 40.35 | 12h30 | 1.4596 | 1.3222 | 0.81675 | 0.69225 | 0.50438
13h30 | 110.09 | 99.63 | 61.07 | 51.57 | 36.87 | 13h30 | 1.3761 | 1.2454 | 0.76338 | 0.64463 | 0.46087
14h30 | 107.66 | 97.85 | 59.95 | 50.46 | 36.87 | 14h30 | 1.3458 | 1.2231 | 0.74938 | 0.63075 | 0.46087
15h30 | 112.12 | 102.2 | 63.42 | 53.02 | 39.86 | 15h30 | 1.4015 | 1.2775 | 0.79275 | 0.66275 | 0.49825
16h30 | 108 | 98.38 | 62.45 | 52.18 | 39.86 | 16h30 | 1.35 | 1.2297 | 0.78063 | 0.65225 | 0.49825
17h30 | 104.84 | 95.55 | 61.13 | 48.97 | 37.81 | 17h30 | 1.3105 | 1.1944 | 0.76413 | 0.61213 | 0.47263
18h30 | 108.37 | 99.29 | 63.56 | 51.28 | 39.79 | 18h30 | 1.3546 | 1.2411 | 0.7945 | 0.641 | 0.49738
19h30 | 116.34 | 108.03 | 68.71 | 56.52 | 44.25 | 19h30 | 1.4543 | 1.3504 | 0.85888 | 0.7065 | 0.55312
20h30 | 130.21 | 121.2 | 76.52 | 64.55 | 51.27 | 20h30 | 1.6276 | 1.515 | 0.9565 | 0.80688 | 0.64087
21h30 | 130.21 | 121.59 | 78.29 | 66.18 | 52.91 | 21h30 | 1.6276 | 1.5199 | 0.97862 | 0.82725 | 0.66138
22h30 | 125.61 | 116.11 | 73.94 | 61.83 | 49.25 | 22h30 | 1.5701 | 1.4514 | 0.92425 | 0.77287 | 0.61562
23h30 | 121.2 | 111.12 | 70.72 | 58.52 | 46.81 | 23h30 | 1.515 | 1.389 | 0.884 | 0.7315 | 0.58513
00h30 | 102.98 | 95.01 | 64.83 | 52.53 | 41.47 | 00h30 | 1.2873 | 1.1876 | 0.81037 | 0.65663 | 0.51838
01h30 | 103.93 | 95.53 | 58.45 | 48.23 | 36.86 | 01h30 | 1.2991 | 1.1941 | 0.73062 | 0.60288 | 0.46075
02h30 | 107.6 | 98.69 | 60.5 | 51.25 | 39.41 | 02h30 | 1.345 | 1.2336 | 0.75625 | 0.64062 | 0.49262
03h30 | 111.07 | 103.16 | 64.62 | 54.75 | 42.23 | 03h30 | 1.3884 | 1.2895 | 0.80775 | 0.68437 | 0.52787
04h30 | 118.03 | 107.98 | 67.1 | 56.97 | 44.3 | 04h30 | 1.4754 | 1.3498 | 0.83875 | 0.71213 | 0.55375
05h30 | 103.63 | 92.47 | 57.86 | 47.46 | 36.46 | 05h30 | 1.2954 | 1.1559 | 0.72325 | 0.59325 | 0.45575
06h30 | 88.32 | 84.49 | 53.33 | 42.21 | 31.84 | 06h30 | 1.104 | 1.0561 | 0.66663 | 0.52763 | 0.398
07h30 | 102.72 | 98.78 | 67.46 | 53.66 | 44.51 | 07h30 | 1.284 | 1.2348 | 0.84325 | 0.67075 | 0.55637
08h30 | 114.35 | 101.11 | 67.46 | 53.66 | 44.51 | 08h30 | 1.4294 | 1.2639 | 0.84325 | 0.67075 | 0.55637
09h30 | 112.87 | 97.33 | 65.37 | 50.36 | 40.41 | 09h30 | 1.4109 | 1.2166 | 0.81712 | 0.6295 | 0.50513
10h30 | 109.81 | 95 | 65.37 | 50.36 | 40.41 | 10h30 | 1.3726 | 1.1875 | 0.81712 | 0.6295 | 0.50513
11h30 | 111.29 | 100 | 74.14 | 59.53 | 47.97 | 11h30 | 1.3911 | 1.25 | 0.92675 | 0.74413 | 0.59962
12h30 | 137.03 | 123.11 | 81.32 | 67.11 | 54.56 | 12h30 | 1.7129 | 1.5389 | 1.0165 | 0.83888 | 0.682
13h30 | 123.78 | 108.3 | 70.14 | 56.49 | 45.41 | 13h30 | 1.5473 | 1.3538 | 0.87675 | 0.70613 | 0.56763
14h30 | 105.2 | 89.33 | 62.95 | 48.92 | 38.83 | 14h30 | 1.315 | 1.1166 | 0.78687 | 0.6115 | 0.48538
15h30 | 88.02 | 72.3 | 47.69 | 34.36 | 26.57 | 15h30 | 1.1002 | 0.90375 | 0.59613 | 0.4295 | 0.33213
16h30 | 80.76 | 68.16 | 47.69 | 34.36 | 26.57 | 16h30 | 1.0095 | 0.852 | 0.59613 | 0.4295 | 0.33213
17h30 | 77.45 | 61.94 | 41.32 | 28.27 | 21.46 | 17h30 | 0.96813 | 0.77425 | 0.5165 | 0.35337 | 0.26825
18h30 | 66.27 | 61.94 | 41.32 | 28.27 | 21.46 | 18h30 | 0.82837 | 0.77425 | 0.5165 | 0.35337 | 0.26825
19h30 | 60.01 | 43.5 | 29.93 | 17.3 | 11.93 | 19h30 | 0.75013 | 0.54375 | 0.37412 | 0.21625 | 0.14913
20h30 | 63.09 | 47.46 | 32.82 | 20.38 | 14.86 | 20h30 | 0.78863 | 0.59325 | 0.41025 | 0.25475 | 0.18575
21h30 | 60.75 | 44.43 | 31.01 | 18.78 | 13.51 | 21h30 | 0.75938 | 0.55537 | 0.38762 | 0.23475 | 0.16887
22h30 | 64.14 | 47.88 | 33.06 | 20.95 | 15.39 | 22h30 | 0.80175 | 0.5985 | 0.41325 | 0.26188 | 0.19237
23h30 | 77.46 | 61.05 | 41.15 | 28.66 | 22.23 | 23h30 | 0.96825 | 0.76313 | 0.51438 | 0.35825 | 0.27787
00h30 | 71 | 53.63 | 36.2 | 23.42 | 17.41 | 00h30 | 0.8875 | 0.67038 | 0.4525 | 0.29275 | 0.21763
01h30 | 70.28 | 55.92 | 34.64 | 24.48 | 17.58 | 01h30 | 0.8785 | 0.699 | 0.433 | 0.306 | 0.21975
02h30 | 76.07 | 61.95 | 39.06 | 29.75 | 22.4 | 02h30 | 0.95088 | 0.77438 | 0.48825 | 0.37188 | 0.28
03h30 | 82.87 | 68.13 | 43.02 | 32.92 | 25.23 | 03h30 | 1.0359 | 0.85162 | 0.53775 | 0.4115 | 0.31538
04h30 | 93.24 | 77.85 | 49.34 | 38.75 | 30.45 | 04h30 | 1.1655 | 0.97313 | 0.61675 | 0.48438 | 0.38062
05h30 | 98.5 | 82.59 | 52.62 | 41.48 | 33.08 | 05h30 | 1.2312 | 1.0324 | 0.65775 | 0.5185 | 0.4135
06h30 | 96.63 | 80.26 | 51.53 | 40.03 | 32.01 | 06h30 | 1.2079 | 1.0032 | 0.64412 | 0.50038 | 0.40013
07h30 | 114.28 | 109.36 | 74.89 | 59.92 | 52.61 | 07h30 | 1.4285 | 1.367 | 0.93612 | 0.749 | 0.65763
08h30 | 120.5 | 102.87 | 69.12 | 52.19 | 44.43 | 08h30 | 1.5063 | 1.2859 | 0.864 | 0.65238 | 0.55537
09h30 | 113.76 | 94.77 | 64.81 | 49.53 | 40.4 | 09h30 | 1.422 | 1.1846 | 0.81012 | 0.61913 | 0.505
10h30 | 146.13 | 126.35 | 82.64 | 68.29 | 57 | 10h30 | 1.8266 | 1.5794 | 1.033 | 0.85362 | 0.7125
11h30 | 152.86 | 138.51 | 109.62 | 95.72 | 80.91 | 11h30 | 1.9107 | 1.7314 | 1.3702 | 1.1965 | 1.0114
12h30 | 200 | 184.36 | 124.13 | 109.42 | 92.69 | 12h30 | 2.5 | 2.3045 | 1.5516 | 1.3678 | 1.1586
13h30 | 200 | 184.36 | 120.47 | 105.52 | 89.26 | 13h30 | 2.5 | 2.3045 | 1.5059 | 1.319 | 1.1158
14h30 | 194.82 | 177.24 | 111.96 | 97.09 | 81.91 | 14h30 | 2.4352 | 2.2155 | 1.3995 | 1.2136 | 1.0239
15h30 | 194.82 | 177.24 | 120.33 | 104.53 | 88.72 | 15h30 | 2.4352 | 2.2155 | 1.5041 | 1.3066 | 1.109
16h30 | 190.03 | 171.94 | 112.77 | 95.99 | 81.42 | 16h30 | 2.3754 | 2.1492 | 1.4096 | 1.1999 | 1.0177
17h30 | 154.17 | 135.52 | 88.85 | 72.05 | 60.37 | 17h30 | 1.9271 | 1.694 | 1.1106 | 0.90063 | 0.75462
18h30 | 164.14 | 149.68 | 96.38 | 79.84 | 67.29 | 18h30 | 2.0518 | 1.871 | 1.2047 | 0.998 | 0.84113
19h30 | 191.23 | 174.06 | 111.23 | 94.57 | 80.43 | 19h30 | 2.3904 | 2.1757 | 1.3904 | 1.1821 | 1.0054
20h30 | 173.86 | 155.67 | 100.46 | 83.47 | 70.81 | 20h30 | 2.1732 | 1.9459 | 1.2557 | 1.0434 | 0.88513
21h30 | 160.28 | 141.85 | 92.42 | 75.1 | 63.43 | 21h30 | 2.0035 | 1.7731 | 1.1553 | 0.93875 | 0.79287
22h30 | 177.64 | 173.21 | 111.4 | 93.87 | 80.03 | 22h30 | 2.2205 | 2.1651 | 1.3925 | 1.1734 | 1.0004
23h30 | 200 | 187.58 | 120.02 | 102.63 | 87.8 | 23h30 | 2.5 | 2.3447 | 1.5003 | 1.2829 | 1.0975
00h30 | 171.93 | 155.52 | 94.65 | 78.43 | 64.68 | 00h30 | 2.1491 | 1.944 | 1.1831 | 0.98037 | 0.8085
01h30 | 165.36 | 148.62 | 93.02 | 78.94 | 65.81 | 01h30 | 2.067 | 1.8578 | 1.1627 | 0.98675 | 0.82263
02h30 | 153.82 | 137.15 | 86.16 | 73.14 | 60.79 | 02h30 | 1.9227 | 1.7144 | 1.077 | 0.91425 | 0.75987
03h30 | 144.4 | 127.19 | 80.46 | 67.12 | 55.86 | 03h30 | 1.805 | 1.5899 | 1.0057 | 0.839 | 0.69825
04h30 | 133.87 | 116.28 | 76.8 | 64.23 | 55.59 | 04h30 | 1.6734 | 1.4535 | 0.96 | 0.80288 | 0.69488
05h30 | 123.19 | 105.28 | 67.82 | 53.54 | 43.64 | 05h30 | 1.5399 | 1.316 | 0.84775 | 0.66925 | 0.5455
06h30 | 118.61 | 100.43 | 67.82 | 53.54 | 43.64 | 06h30 | 1.4826 | 1.2554 | 0.84775 | 0.66925 | 0.5455
07h30 | 141.23 | 121.35 | 83.78 | 67.86 | 56.81 | 07h30 | 1.7654 | 1.5169 | 1.0473 | 0.84825 | 0.71013
08h30 | 137.75 | 116.57 | 83.78 | 67.86 | 56.81 | 08h30 | 1.7219 | 1.4571 | 1.0473 | 0.84825 | 0.71013
09h30 | 121.44 | 100.9 | 69.37 | 53.07 | 43.86 | 09h30 | 1.518 | 1.2612 | 0.86713 | 0.66338 | 0.54825
10h30 | 113.69 | 93.75 | 69.37 | 53.07 | 43.86 | 10h30 | 1.4211 | 1.1719 | 0.86713 | 0.66338 | 0.54825
11h30 | 122.45 | 102.97 | 69.01 | 51.9 | 42.66 | 11h30 | 1.5306 | 1.2871 | 0.86262 | 0.64875 | 0.53325
12h30 | 132.64 | 113.59 | 75.12 | 58.23 | 48.31 | 12h30 | 1.658 | 1.4199 | 0.939 | 0.72788 | 0.60388
13h30 | 137.14 | 118.46 | 77.57 | 60.64 | 50.42 | 13h30 | 1.7143 | 1.4808 | 0.96962 | 0.758 | 0.63025
14h30 | 130.89 | 112.44 | 74.31 | 57.38 | 47.48 | 14h30 | 1.6361 | 1.4055 | 0.92888 | 0.71725 | 0.5935
15h30 | 115.56 | 97.31 | 65.46 | 48.91 | 40.1 | 15h30 | 1.4445 | 1.2164 | 0.81825 | 0.61138 | 0.50125
16h30 | 103.59 | 85.56 | 62.6 | 45.84 | 37.39 | 16h30 | 1.2949 | 1.0695 | 0.7825 | 0.573 | 0.46737
17h30 | 91.62 | 73.78 | 51 | 35.68 | 28.62 | 17h30 | 1.1453 | 0.92225 | 0.6375 | 0.446 | 0.35775
18h30 | 77.67 | 59.97 | 51 | 35.68 | 28.62 | 18h30 | 0.97088 | 0.74962 | 0.6375 | 0.446 | 0.35775
19h30 | 75.26 | 57.61 | 40.31 | 25.33 | 19.63 | 19h30 | 0.94075 | 0.72013 | 0.50387 | 0.31662 | 0.24538
20h30 | 71 | 53.31 | 40.31 | 25.33 | 19.63 | 20h30 | 0.8875 | 0.66638 | 0.50387 | 0.31662 | 0.24538
21h30 | 64.07 | 46.26 | 33.63 | 19.4 | 14.82 | 21h30 | 0.80088 | 0.57825 | 0.42037 | 0.2425 | 0.18525
22h30 | 66.53 | 48.56 | 35.51 | 21.28 | 16.62 | 22h30 | 0.83162 | 0.607 | 0.44388 | 0.266 | 0.20775
23h30 | 67.12 | 48.95 | 35.88 | 21.43 | 16.81 | 23h30 | 0.839 | 0.61187 | 0.4485 | 0.26787 | 0.21013
00h30 | 56.84 | 44.07 | 34 | 19.55 | 15.01 | 00h30 | 0.7105 | 0.55088 | 0.425 | 0.24438 | 0.18762
01h30 | 56.11 | 38.96 | 25.35 | 12.26 | 7.95 | 01h30 | 0.70137 | 0.487 | 0.31688 | 0.15325 | 0.099375
02h30 | 56.11 | 38.96 | 25.35 | 12.26 | 7.95 | 02h30 | 0.70137 | 0.487 | 0.31688 | 0.15325 | 0.099375
03h30 | 49.17 | 30.63 | 22.09 | 11.01 | 8.09 | 03h30 | 0.61462 | 0.38288 | 0.27613 | 0.13762 | 0.10113
04h30 | 63.12 | 44.83 | 31.23 | 18.5 | 14.64 | 04h30 | 0.789 | 0.56037 | 0.39038 | 0.23125 | 0.183
05h30 | 66.61 | 47.78 | 33.97 | 20.07 | 16.06 | 05h30 | 0.83262 | 0.59725 | 0.42462 | 0.25088 | 0.20075
06h30 | 52.66 | 33.58 | 24.83 | 12.58 | 9.51 | 06h30 | 0.65825 | 0.41975 | 0.31038 | 0.15725 | 0.11887
07h30 | 76.12 | 54.2 | 44.63 | 27.89 | 23.12 | 07h30 | 0.9515 | 0.6775 | 0.55788 | 0.34863 | 0.289
08h30 | 89.37 | 66.05 | 49.57 | 32.45 | 26.69 | 08h30 | 1.1171 | 0.82563 | 0.61962 | 0.40563 | 0.33363
09h30 | 79.08 | 55.8 | 43.69 | 27.09 | 22.09 | 09h30 | 0.9885 | 0.6975 | 0.54612 | 0.33863 | 0.27613
10h30 | 90.78 | 67.74 | 49.85 | 33.58 | 27.64 | 10h30 | 1.1347 | 0.84675 | 0.62313 | 0.41975 | 0.3455
11h30 | 118.43 | 95.62 | 66.25 | 49.3 | 41.31 | 11h30 | 1.4804 | 1.1952 | 0.82812 | 0.61625 | 0.51638
12h30 | 127.8 | 105.17 | 71.62 | 54.55 | 45.64 | 12h30 | 1.5975 | 1.3146 | 0.89525 | 0.68188 | 0.5705
13h30 | 126.56 | 104.07 | 70.54 | 53.86 | 44.77 | 13h30 | 1.582 | 1.3009 | 0.88175 | 0.67325 | 0.55963
14h30 | 127.32 | 104.99 | 70.92 | 54.46 | 45.09 | 14h30 | 1.5915 | 1.3124 | 0.8865 | 0.68075 | 0.56363
15h30 | 124.16 | 102.02 | 69.09 | 52.91 | 43.53 | 15h30 | 1.552 | 1.2752 | 0.86362 | 0.66138 | 0.54412
16h30 | 112.71 | 90.82 | 62.15 | 46.56 | 37.81 | 16h30 | 1.4089 | 1.1353 | 0.77687 | 0.582 | 0.47263
17h30 | 98.6 | 77.04 | 53.46 | 38.65 | 30.74 | 17h30 | 1.2325 | 0.963 | 0.66825 | 0.48313 | 0.38425
18h30 | 106.64 | 85.45 | 58.16 | 43.83 | 35.08 | 18h30 | 1.333 | 1.0681 | 0.727 | 0.54788 | 0.4385
19h30 | 123.25 | 102.46 | 68.18 | 54.02 | 43.68 | 19h30 | 1.5406 | 1.2808 | 0.85225 | 0.67525 | 0.546
20h30 | 125.71 | 105.33 | 69.66 | 55.82 | 44.89 | 20h30 | 1.5714 | 1.3166 | 0.87075 | 0.69775 | 0.56112
21h30 | 124.94 | 104.97 | 69.2 | 55.62 | 44.54 | 21h30 | 1.5617 | 1.3121 | 0.865 | 0.69525 | 0.55675
22h30 | 122.36 | 102.79 | 67.77 | 54.25 | 43.35 | 22h30 | 1.5295 | 1.2849 | 0.84713 | 0.67812 | 0.54187
23h30 | 115.14 | 95.97 | 63.53 | 50.22 | 39.93 | 23h30 | 1.4392 | 1.1996 | 0.79412 | 0.62775 | 0.49912
00h30 | 83.59 | 65.12 | 48.85 | 34.05 | 27.5 | 00h30 | 1.0449 | 0.814 | 0.61062 | 0.42562 | 0.34375
01h30 | 87.86 | 71.86 | 45.12 | 34.58 | 25.15 | 01h30 | 1.0982 | 0.89825 | 0.564 | 0.43225 | 0.31438
02h30 | 112.57 | 96.93 | 60.73 | 50.4 | 40.35 | 02h30 | 1.4071 | 1.2116 | 0.75913 | 0.63 | 0.50438
03h30 | 124.71 | 115.36 | 72.11 | 61.2 | 50.44 | 03h30 | 1.5589 | 1.442 | 0.90138 | 0.765 | 0.6305
04h30 | 126.94 | 112.3 | 70.89 | 59.46 | 49.16 | 04h30 | 1.5868 | 1.4038 | 0.88613 | 0.74325 | 0.6145
05h30 | 103.38 | 87.32 | 56.26 | 44.5 | 36.2 | 05h30 | 1.2922 | 1.0915 | 0.70325 | 0.55625 | 0.4525
06h30 | 88.41 | 71.66 | 46.86 | 35.52 | 28.4 | 06h30 | 1.1051 | 0.89575 | 0.58575 | 0.444 | 0.355
07h30 | 111.97 | 107.67 | 74.74 | 61.87 | 52.19 | 07h30 | 1.3996 | 1.3459 | 0.93425 | 0.77338 | 0.65238
08h30 | 142.29 | 125.32 | 83.06 | 68.64 | 57.49 | 08h30 | 1.7786 | 1.5665 | 1.0382 | 0.858 | 0.71862
09h30 | 142.29 | 125.32 | 83.88 | 70.32 | 60.01 | 09h30 | 1.7786 | 1.5665 | 1.0485 | 0.879 | 0.75013
10h30 | 151.29 | 132.81 | 85.46 | 72.61 | 61.44 | 10h30 | 1.8911 | 1.6601 | 1.0682 | 0.90763 | 0.768
11h30 | 151.29 | 132.81 | 97.22 | 84.47 | 71.41 | 11h30 | 1.8911 | 1.6601 | 1.2152 | 1.0559 | 0.89263
12h30 | 183.82 | 166.04 | 107.55 | 94.7 | 80.24 | 12h30 | 2.2978 | 2.0755 | 1.3444 | 1.1838 | 1.003
13h30 | 183.82 | 166.04 | 111.08 | 98.94 | 83.99 | 13h30 | 2.2978 | 2.0755 | 1.3885 | 1.2368 | 1.0499
14h30 | 188.71 | 172.14 | 108.3 | 96.5 | 82.04 | 14h30 | 2.3589 | 2.1517 | 1.3538 | 1.2063 | 1.0255
15h30 | 173.58 | 156.79 | 98.34 | 85.79 | 72.99 | 15h30 | 2.1698 | 1.9599 | 1.2292 | 1.0724 | 0.91238
16h30 | 152.84 | 136.32 | 86.34 | 73.6 | 62.46 | 16h30 | 1.9105 | 1.704 | 1.0793 | 0.92 | 0.78075
17h30 | 129.48 | 113.31 | 72.95 | 60.31 | 50.73 | 17h30 | 1.6185 | 1.4164 | 0.91187 | 0.75387 | 0.63413
18h30 | 122.37 | 106.4 | 69.33 | 55.86 | 46.99 | 18h30 | 1.5296 | 1.33 | 0.86662 | 0.69825 | 0.58737
19h30 | 131.02 | 115.09 | 75.15 | 60.7 | 51.52 | 19h30 | 1.6378 | 1.4386 | 0.93937 | 0.75875 | 0.644
20h30 | 124.2 | 108.14 | 71.38 | 56.5 | 47.86 | 20h30 | 1.5525 | 1.3518 | 0.89225 | 0.70625 | 0.59825
21h30 | 112.42 | 96.14 | 64.17 | 49.58 | 41.69 | 21h30 | 1.4053 | 1.2018 | 0.80212 | 0.61975 | 0.52112
22h30 | 120.55 | 103.95 | 68.51 | 54.77 | 46.36 | 22h30 | 1.5069 | 1.2994 | 0.85637 | 0.68463 | 0.5795
23h30 | 132.67 | 115.71 | 75.42 | 61.97 | 53.01 | 23h30 | 1.6584 | 1.4464 | 0.94275 | 0.77463 | 0.66263
00h30 | 120.47 | 104.19 | 68.03 | 55.67 | 46.52 | 00h30 | 1.5059 | 1.3024 | 0.85037 | 0.69588 | 0.5815
01h30 | 140.12 | 124.82 | 79 | 65.11 | 55.8 | 01h30 | 1.7515 | 1.5602 | 0.9875 | 0.81388 | 0.6975
02h30 | 151.75 | 135.99 | 86.5 | 72.55 | 62.76 | 02h30 | 1.8969 | 1.6999 | 1.0813 | 0.90687 | 0.7845
03h30 | 145.73 | 128.96 | 82.44 | 68.16 | 58.7 | 03h30 | 1.8216 | 1.612 | 1.0305 | 0.852 | 0.73375
04h30 | 142.02 | 124.44 | 80.15 | 65.32 | 56.42 | 04h30 | 1.7752 | 1.5555 | 1.0019 | 0.8165 | 0.70525
05h30 | 157.88 | 140.76 | 90.69 | 74.95 | 65.03 | 05h30 | 1.9735 | 1.7595 | 1.1336 | 0.93688 | 0.81288
06h30 | 161.62 | 142.92 | 92.59 | 75.89 | 65.58 | 06h30 | 2.0202 | 1.7865 | 1.1574 | 0.94863 | 0.81975
07h30 | 161.62 | 142.92 | 106.04 | 86.92 | 75.7 | 07h30 | 2.0202 | 1.7865 | 1.3255 | 1.0865 | 0.94625
08h30 | 189.48 | 167.77 | 113.38 | 92.41 | 79.78 | 08h30 | 2.3685 | 2.0971 | 1.4172 | 1.1551 | 0.99725
09h30 | 189.48 | 167.77 | 114.45 | 104.79 | 91.97 | 09h30 | 2.3685 | 2.0971 | 1.4306 | 1.3099 | 1.1496
10h30 | 200 | 191.7 | 127.66 | 107.99 | 94.91 | 10h30 | 2.5 | 2.3963 | 1.5958 | 1.3499 | 1.1864
11h30 | 200 | 188.36 | 123.56 | 102.89 | 89.98 | 11h30 | 2.5 | 2.3545 | 1.5445 | 1.2861 | 1.1247
12h30 | 200 | 183.72 | 120.58 | 99.17 | 86.3 | 12h30 | 2.5 | 2.2965 | 1.5072 | 1.2396 | 1.0788
13h30 | 200 | 183.92 | 120.43 | 99.46 | 86.37 | 13h30 | 2.5 | 2.299 | 1.5054 | 1.2432 | 1.0796
14h30 | 200 | 183.51 | 120.14 | 99.26 | 86.19 | 14h30 | 2.5 | 2.2939 | 1.5017 | 1.2408 | 1.0774
15h30 | 200 | 186.66 | 124.39 | 104.68 | 91.55 | 15h30 | 2.5 | 2.3333 | 1.5549 | 1.3085 | 1.1444
16h30 | 200 | 200 | 132.36 | 110.28 | 96.95 | 16h30 | 2.5 | 2.5 | 1.6545 | 1.3785 | 1.2119
17h30 | 200 | 193.81 | 128.05 | 105.78 | 92.93 | 17h30 | 2.5 | 2.4226 | 1.6006 | 1.3222 | 1.1616
18h30 | 197.89 | 177.52 | 117.89 | 95.81 | 83.94 | 18h30 | 2.4736 | 2.219 | 1.4736 | 1.1976 | 1.0493
19h30 | 193.05 | 168.68 | 112.66 | 90.57 | 79.53 | 19h30 | 2.4131 | 2.1085 | 1.4083 | 1.1321 | 0.99413
20h30 | 195.16 | 184.97 | 123.65 | 101.47 | 89.68 | 20h30 | 2.4395 | 2.3121 | 1.5456 | 1.2684 | 1.121
21h30 | 200 | 195.98 | 129.32 | 107.83 | 95.43 | 21h30 | 2.5 | 2.4497 | 1.6165 | 1.3479 | 1.1929
22h30 | 200 | 188.21 | 124.13 | 103.27 | 91.16 | 22h30 | 2.5 | 2.3526 | 1.5516 | 1.2909 | 1.1395
23h30 | 200 | 188.57 | 124.13 | 103.38 | 91.12 | 23h30 | 2.5 | 2.3571 | 1.5516 | 1.2922 | 1.139
00h30 | 177.15 | 155.08 | 97.63 | 91.1 | 80.43 | 00h30 | 2.2144 | 1.9385 | 1.2204 | 1.1387 | 1.0054
01h30 | 161.61 | 138.29 | 89.6 | 72.26 | 62.02 | 01h30 | 2.0201 | 1.7286 | 1.12 | 0.90325 | 0.77525
02h30 | 159.33 | 135.75 | 88.12 | 72.26 | 62.02 | 02h30 | 1.9916 | 1.6969 | 1.1015 | 0.90325 | 0.77525
03h30 | 155.56 | 131.72 | 86.17 | 68.78 | 59.83 | 03h30 | 1.9445 | 1.6465 | 1.0771 | 0.85975 | 0.74787
04h30 | 132.3 | 108.18 | 86.15 | 68.78 | 59.83 | 04h30 | 1.6538 | 1.3522 | 1.0769 | 0.85975 | 0.74787
05h30 | 107.32 | 83.01 | 55.86 | 38.68 | 31.3 | 05h30 | 1.3415 | 1.0376 | 0.69825 | 0.4835 | 0.39125
06h30 | 103.03 | 78.64 | 55.86 | 38.68 | 32.43 | 06h30 | 1.2879 | 0.983 | 0.69825 | 0.4835 | 0.40537
07h30 | 127.58 | 101.57 | 73.95 | 55.71 | 48.8 | 07h30 | 1.5947 | 1.2696 | 0.92437 | 0.69637 | 0.61
08h30 | 117.3 | 90.04 | 73.95 | 55.71 | 47.67 | 08h30 | 1.4663 | 1.1255 | 0.92437 | 0.69637 | 0.59588
09h30 | 108.01 | 81.42 | 60.63 | 41.22 | 35.11 | 09h30 | 1.3501 | 1.0177 | 0.75787 | 0.51525 | 0.43888
10h30 | 109.78 | 83.78 | 61.4 | 42.6 | 36.32 | 10h30 | 1.3722 | 1.0473 | 0.7675 | 0.5325 | 0.454
11h30 | 117.04 | 91.46 | 64.73 | 46.26 | 39.51 | 11h30 | 1.463 | 1.1433 | 0.80912 | 0.57825 | 0.49388
12h30 | 121.32 | 96.1 | 67.12 | 49.34 | 42.16 | 12h30 | 1.5165 | 1.2012 | 0.839 | 0.61675 | 0.527
13h30 | 121.58 | 96.76 | 66.93 | 49.71 | 42.33 | 13h30 | 1.5197 | 1.2095 | 0.83662 | 0.62138 | 0.52912
14h30 | 125.22 | 100.81 | 68.99 | 51.98 | 44.21 | 14h30 | 1.5653 | 1.2601 | 0.86238 | 0.64975 | 0.55263
15h30 | 137.1 | 112.95 | 76.66 | 59.16 | 50.75 | 15h30 | 1.7138 | 1.4119 | 0.95825 | 0.7395 | 0.63438
16h30 | 149.89 | 125.97 | 85.1 | 67.08 | 57.92 | 16h30 | 1.8736 | 1.5746 | 1.0637 | 0.8385 | 0.724
17h30 | 159.53 | 136.42 | 91.58 | 73.53 | 63.65 | 17h30 | 1.9941 | 1.7052 | 1.1447 | 0.91912 | 0.79563
18h30 | 169.75 | 146.59 | 97.61 | 79.72 | 68.96 | 18h30 | 2.1219 | 1.8324 | 1.2201 | 0.9965 | 0.862
19h30 | 167.99 | 144.99 | 96.17 | 79.15 | 68.22 | 19h30 | 2.0999 | 1.8124 | 1.2021 | 0.98938 | 0.85275
20h30 | 154.12 | 131.23 | 87.21 | 71.53 | 61.54 | 20h30 | 1.9265 | 1.6404 | 1.0901 | 0.89412 | 0.76925
21h30 | 146.43 | 123.68 | 82.29 | 67.31 | 58 | 21h30 | 1.8304 | 1.546 | 1.0286 | 0.84137 | 0.725
22h30 | 164.75 | 142.17 | 93.56 | 78.23 | 68.15 | 22h30 | 2.0594 | 1.7771 | 1.1695 | 0.97788 | 0.85188
23h30 | 174.2 | 155.73 | 110.46 | 94.42 | 82.97 | 23h30 | 2.1775 | 1.9466 | 1.3807 | 1.1803 | 1.0371
00h30 | 169.45 | 149.88 | 94.05 | 78.68 | 67.18 | 00h30 | 2.1181 | 1.8735 | 1.1756 | 0.9835 | 0.83975
01h30 | 150.67 | 130.93 | 83.37 | 69.62 | 60.2 | 01h30 | 1.8834 | 1.6366 | 1.0421 | 0.87025 | 0.7525
02h30 | 123.93 | 103.56 | 77.8 | 61.23 | 54.32 | 02h30 | 1.5491 | 1.2945 | 0.9725 | 0.76538 | 0.679
03h30 | 123.76 | 102.98 | 66.2 | 52.29 | 43.39 | 03h30 | 1.547 | 1.2873 | 0.8275 | 0.65363 | 0.54238
04h30 | 142.7 | 121.6 | 78.72 | 65.17 | 55.97 | 04h30 | 1.7837 | 1.52 | 0.984 | 0.81463 | 0.69963
05h30 | 148.08 | 126.71 | 81.8 | 67.52 | 58.06 | 05h30 | 1.851 | 1.5839 | 1.0225 | 0.844 | 0.72575
06h30 | 154.46 | 132.82 | 86.4 | 71 | 61.11 | 06h30 | 1.9307 | 1.6603 | 1.08 | 0.8875 | 0.76387
07h30 | 168.01 | 147.24 | 112.69 | 95.41 | 84.18 | 07h30 | 2.1001 | 1.8405 | 1.4086 | 1.1926 | 1.0522
08h30 | 200 | 178.92 | 120.76 | 102.51 | 90.06 | 08h30 | 2.5 | 2.2365 | 1.5095 | 1.2814 | 1.1258
09h30 | 200 | 178.92 | 125.18 | 113.82 | 100.53 | 09h30 | 2.5 | 2.2365 | 1.5648 | 1.4227 | 1.2566
10h30 | 200 | 195.98 | 128.63 | 114.14 | 100.49 | 10h30 | 2.5 | 2.4497 | 1.6079 | 1.4267 | 1.2561
11h30 | 200 | 195.98 | 128.63 | 116.36 | 102.35 | 11h30 | 2.5 | 2.4497 | 1.6079 | 1.4545 | 1.2794
12h30 | 200 | 200 | 141.51 | 124.83 | 109.89 | 12h30 | 2.5 | 2.5 | 1.7689 | 1.5604 | 1.3736
13h30 | 200 | 200 | 140.63 | 123.04 | 108.23 | 13h30 | 2.5 | 2.5 | 1.7579 | 1.538 | 1.3529
14h30 | 200 | 200 | 130.73 | 112.66 | 99.01 | 14h30 | 2.5 | 2.5 | 1.6341 | 1.4083 | 1.2376
15h30 | 200 | 197.18 | 126.77 | 108.09 | 95.22 | 15h30 | 2.5 | 2.4647 | 1.5846 | 1.3511 | 1.1903
16h30 | 200 | 191.9 | 123.85 | 104.93 | 92.71 | 16h30 | 2.5 | 2.3988 | 1.5481 | 1.3116 | 1.1589
17h30 | 188.64 | 166.55 | 108.94 | 90.74 | 79.93 | 17h30 | 2.358 | 2.0819 | 1.3618 | 1.1342 | 0.99913
18h30 | 155.44 | 130.16 | 86.57 | 72.04 | 62.65 | 18h30 | 1.943 | 1.627 | 1.0821 | 0.9005 | 0.78312
19h30 | 136.87 | 111.57 | 74.97 | 59.21 | 51.28 | 19h30 | 1.7109 | 1.3946 | 0.93712 | 0.74013 | 0.641
20h30 | 139.38 | 114.84 | 77 | 61.19 | 53.1 | 20h30 | 1.7423 | 1.4355 | 0.9625 | 0.76487 | 0.66375
21h30 | 132.67 | 108.52 | 73.11 | 57.53 | 49.75 | 21h30 | 1.6584 | 1.3565 | 0.91387 | 0.71913 | 0.62187
22h30 | 118.44 | 94.54 | 64.76 | 55.55 | 47.93 | 22h30 | 1.4805 | 1.1818 | 0.8095 | 0.69437 | 0.59913
23h30 | 120.93 | 97.2 | 66.45 | 50.3 | 42.97 | 23h30 | 1.5116 | 1.215 | 0.83062 | 0.62875 | 0.53712