## Biomass
Biomass Powered Data Centre
Biomass feedstocks analysis (5)
Energy & Availability Calculation | [6 empty] | Data used: |  |  |  |  | Biomass | Moisture | Volatile Matter | Fixed Carbon | Ash | Lower Heating Value
Input parameters | [6 empty] | Table of calorific values for solid biomass (2) | [5 empty] | (%) | (%) | (%) | (%) | (MJ/kg)
|  |  | Data centre requires: | 320 | kW electricity |  |  |  | MJ/kg |  |  | Wood | 20 | 82 | 17 | 1 | 18.6
|  |  | Demand profile: | constant |  |  |  | Green wood | 8 |  |  | Wheat straw | 16 | 59 | 21 | 4 | 17.3
|  |  | Tier 1 availability | 99.67% |  |  |  | Seasonal wood | 13 |  |  | Barley straw | 30 | 46 | 18 | 6 | 16.1
[8 empty] | Dried wood | 16 |  |  | Lignite | 34 | 29 | 31 | 6 | 26.8
Assumptions | [7 empty] | Dry vegetation | 15 |  |  | Bituminous coal | 11 | 35 | 45 | 9 | 34
|  |  | Efficiency of electricity conversion (2),(5): | 20% | Small CHP plant |  |  | Crop wastes | 12 to 15
|  |  | Average calorific value of fuel: | 13 | MJ/kg |  |  | Cow dung | 13 to 15
|  |  | Average bulk volume of wood: | 5.5 | m3/te | softwood chips
Bulk volume of wood products (5)
|  |  | Boiler type | expensive (3) | rugged (4) |  |  | Biomass | Bulk volume
|  |  | Typical maintenance interval, weeks | 13 | 4 |  |  |  | m3/te
|  |  | Typical maintenance period, days | 1 | 1.5 |  |  | Hardwood chips | 4.4
[8 empty] | Softwood chips | 5.2-5.6
Calculations | [7 empty] | Pellets | 1.6-1.8
Energy | [7 empty] | Sawdust | 6.2
|  | Combustion power incl waste heat |  | = requirement/efficiency | 1600 | kW |  | Planer shavings | 10.3
|  | Number of seconds in one day: |  | = 24x60x60 | 86400 | seconds
|  | Energy input to combustion per day |  | = combustion x sec/day | 138240000 | kJ/ day
|  | Amount of biofuel required per day: |  | = Energy / av calorific val | 10633.8462 | kg/ day
Availability
Availability = 1 - (maintenance period)/(maintenance interval)
|  |  | Availability |  | Days backup power required
| For expensive boiler |  | 98.9% |  | 4.011 | days
| For rugged boiler |  | 94.64% |  | 19.5536 | days
Conclusion
| Biomass furnace capcity |  |  |  | 1600 | kW
|  |  |  | Biomass could power the data centre but would require woodchips | 10.6338 | te/day
|  |  |  | = | 58.4862 | m3/day
But even the best boiler does not have the required availability
|  |  |  | Backup power always required | 4-20 days per year
Energy yields per ha (5)
Energy yield calculations | [7 empty] | Biomass | Crop yield | Higher H Val | Energy yield
[9 empty] | dmt/ha/yer | MJ/kg, dry | GJ/ha
Assumptions: | [7 empty] | Wheat | 14 | 12.3 | 123
| Softwood is slower growing so assume half the yield poplar or willow in terms of yield per hectare per year | [6 empty] | Poplar | 10-15 | 17.3 | 173-259 | 20 years to maturity (7)
|  | Dry matter energy yield | 18 | MJ/kg |  |  |  | Willow | 10-15 | 18.7 | 187-280
|  | Energy yield of seasonal wood | 13 | MJ/kg |  |  |  | Switchgrass | 8 | 17.4 | 139
|  | Crop yield | 6 | te dry matter / ha/ yr |  |  |  | Miscanthus | 12-30 | 18.5 | 222-555
|  | Proportion of finished wood for chippings | 50%
[8 empty] | Electricity from wood (6) |  |  | 110
Calculation:
|  | Factor for dry/seasonal weight: | 0.72222 | te dry matter per te delivered chips |  |  | "1 hectare (2.46 acres) broadleaved woodland should produce about 5 tonnes of fresh logs a year".
Conifers and cherries have a life of 40-60 years'
|  | Annual mass of woodchips: | 3881.3538 | te seasonal wood |  |  | Source (7)
|  | Annual dry mass in those chips: | 2803.2 | te dry matter (= mass x factor)
No of hectares = te dry matter /(proportion chips x yield per ha)
|  | = | 934.4 | ha required
About 950 ha of managed conifer forest required to fuel this plant
BUT 50% of the output is high-value finished wood,
only the offcuts are chipped
Waste Heat Calculation
If electrical conversion efficiency is only 20%, waste heat will be available at high temp (50-60 deg)
Assume unrecoverable losses incl heat for drying woodchip etc |  |  |  |  | 15%
Max Waste heat recovered = 1-losses - electricity prdn |  |  |  |  | 65%
Total energy available per quarter = data centre power x
| plant availability/electr efficiency x13 x7 x24 |  |  |  | 3456000 | kWh
Total for waste heat avaliable per quarter
| = Energy x recovery efficiency |  |  |  | 2246400 | kWh
Space heating energy required per person (8) |  |  |  |  | 24 | kWh/pp/day
Factor for for Northerly climate |  |  |  |  | 1.15
Assumed no of people per household |  |  |  |  | 3
Heating & hot water required for house per quarter |  |  |  |  | 180835.2 | kWh per q
No of households to be supplied |  |  |  |  | 12.4224
Note on E46: Kati Svehla: Assume half the yield of poplar pa from conifers as they are slower growing
Note on K41: Kati Svehla: dmt = dry matter te

## Data sources
Data Sources
Sources: | (1) | Twidell, J; Weir, T: Renewable Energy Resources, 2nd ed; Taylor & Francis, London, 2006
| (2) | Boyle, G; Everett, B;Ramage, R: Energy Systems and Sustainability, Oxford University Press, 2003
| (3) | Site visit to Queen Margaret University 1.5MW Biomass boiler, engineer from Buccleuch Environmental Services , 24 February 2010
| (4) | Site visit to Pentland Plants Biomass 2MW Biomass Boiler, engineer from Pentland Biomass
| (5) | McKendry, P: Energy production from biomass (part 1): overview of biomass, Bioresource Technology 83 pp37-46, 2002
| (6) | McKendry, P: Energy production from biomass (part 2): conversion technologies Bioresource Technology 83 pp47-54, 2002
| (7) | Royal Forestry Society: http://www.rfs.org.uk/learning/harvesting accessed 12 April 2010
| (8) | MacKay, D J C: Sustainable Energy - Without the Hot Air, Cambridge University Press, 2009 pg 53
Availability data - from convrsations with site engineers:
Source (3) | 1.5MW boiler, run at constant load
Runs only on well graded woodchip fuel
High degree of controls and waste heat reuse
Designed for low maintenance
2 yrs old, no breakdowns yet
Expensive, expected life 15-20 years
Preventative maintenance, shut down 1 day/quarter
Source (4) | 2MW boiler, load fluctuates from30-100%
Runs on any fuel from woodchip to chicken dung
Lower attention to contol & waste heat
Rugged construction, simple
3 years old, at least one major breakdown (backburn)
Engineer called out to fix something 1-2 times a month,
Typical down time = 1 day;
Min shutdown time is hours for cooldown & hours setting
of cement if new liner bricks have to be installed in boiler