## Charts
Data Centres Project
Cost Assessment - Charts | [7 empty] | Energy Costs |  |  |  | Potential Locations for various options | 3-year costs for data centre in Shetland
[13 empty] | Wind + biogas | Lerwick | total cost £3.7m
3-year costs for DC | Hydroelec tricity | Biomass CHP | Tidal + PS | Wind + H2 | Wind + H2 xs | Wind + biogas | Wave + H2 |  | Gross cost | Effective subsidy | Net cost
IT Equipment | 1250000 | 1250000 | 1250000 | 1250000 | 1250000 | 1250000 | 1250000 |  | p/kWh | p/kWh | p/kWh
Data centre infrastructure | 516826.288 | 516826.288 | 516826.288 | 516826.288 | 516826.288 | 516826.288 | 516826.288 | Hydroelectric | 13.1146 | -11 | 2.1146
Site | 347649.6792 | 347649.6792 | 347649.6792 | 347649.6792 | 347649.6792 | 347649.6792 | 347649.6792 | Biomass CHP | 16.3175 | 0 | 16.3175
Connectivity | 1468444.088 | 336088.8176 | 2600799.3583 | 336088.8176 | 336088.8176 | 336088.8176 | 5148598.7166 | Tidal current + pumped st | 44.5992 | -4.4082 | 40.191
Operating costs | 922095.7728 | 922095.7728 | 922095.7728 | 922095.7728 | 922095.7728 | 922095.7728 | 922095.7728 | Wind + hydrogen | 187.6548 | -4.5 | 183.1548
Net energy costs | 177830.6653 | 1372235.7646 | 3379903.0833 | 15402583.6027 | 7268397.6363 | 301612.9692 | 22987986.6045 | Wind + H2 excess prod | 90.9298 | -4.5 | 86.4298
Total | 4682846.4932 | 4744896.3221 | 9017274.1815 | 18775244.1602 | 10641058.1938 | 3674273.5267 | 31173157.0611 | Wind + biogas | 13.7275 | -10.141 | 3.5865
Net energy made up of: | [7 empty] | Wave + hydrogen | 273.3541 | 0 | 273.3541
Energy w/o FITs | 1102886.6653 | 1372235.7646 | 3750617.9678 | 15781015.6027 | 7646829.6363 | 1154429.9292 | 22987986.6045
Subsidies | -925056 | 0 | -370714.8845 | -378432 | -378432 | -852816.96 | 0
IT capex | 1250000 | 1250000 | 1250000 | 1250000 | 1250000 | 1250000 | 1250000
Data centre capex | 2332920.0551 | 1200564.7847 | 3465275.3255 | 1200564.7847 | 1200564.7847 | 1200564.7847 | 6013074.6838
Operating costs | 922095.7728 | 922095.7728 | 922095.7728 | 922095.7728 | 922095.7728 | 922095.7728 | 922095.7728
Net energy costs | 177830.6653 | 1372235.7646 | 3379903.0833 | 15402583.6027 | 7268397.6363 | 301612.9692 | 22987986.6045

## Energy costs
Energy Options - Costs
[6 empty] | Annual repayment = | C*r*(1+r)^n | C = | 100000 | unit
Power requirement | 320 | kW |  |  |  |  | (1+r)^n-1 | r = | 8% | cost of capital
Years operation | 20 | years | [5 empty] | n = | no of years
energy used kWh per year | 2803200 | kWh/yr
| Hydroelectric | Biomass CHP | Tidal current + pumped st | Wind + hydrogen | Wind + hydrogen (excess prodn) | Wind + biogas | Wave + hydrogen | n | Annual repayment
band (for FIT Quantitative Analysis) | 100-500 kW | to 500 kWe |  | 1.5-5MW | 1.5-5MW | 500kW-1.5MW |  | 4 | 30192.0804
Rating of primary energy kW | 320 | 320 | 1500 | 2300 | 4600 | 1500 | 2300 | 5 | 25045.6455
Rating of storage kW |  |  | 320 | 320 | 320 | 320 | 320 | 10 | 14902.9489
kWh used pa - primary | 2803200 | 2772480 | 4522695.144 | 2803200 | 2803200 | 1814080 |  | 15 | 11682.9545
kWh used pa - storage |  |  | 1123378.4378 |  |  | 989120 |  | 20 | 10185.2209
| (4) | (1) | (1) | (1) | (1) | (1) | (1) | 25 | 9367.8779
Primary energy capital cost per kW (1) | 4000 | 4700 | 3750 | 1500 | 1500 | 1500 | 7824 | 50 | 8174.2858
Primary energy capital cost total | 1280000 | 1504000 | 5625000 | 3450000 | 6900000 | 2250000 | 17995200
Life of facility (years) | 50 | 15 | 10 | 25 | 25 | 25 | 10
Annualised capital cost of primary energy | 104630.8584 | 175711.6356 | 838290.8739 | 323191.7877 | 646383.5755 | 210777.2529 | 2681815.455
|  |  | (4) | (8) | (8) | (5) | (8)
Storage capital cost per kW |  |  | 5100
Storage capital cost total |  |  | 1632000 | 32362027.8289 | 11300526.1206 | 1100000 | 32362027.8289
Life of facility (years) |  |  | 50 | 10 | 10 | 10 | 10
Annualised capital cost of storage |  |  | 152883.7674 | 4822896.4605 | 1684111.6298 | 163932.4376 | 4822896.4605
Transmission distance km | 14 | 0.5 | 5 | 0.5 | 0.5 | 0.5 | 0.5
Access rights cost per km (3) | 617.7635 | 617.7635 | 617.7635 | 617.7635 | 617.7635 | 617.7635 | 617.7635
Cost per km of buried cable (9) | 182000 | 118000 | 182000 | 118000 | 182000 | 118000 | 118000
Transformers (2) | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000
Total transmission costs | 2636648.6893 | 139308.8818 | 993088.8176 | 139308.8818 | 171308.8818 | 139308.8818 | 139308.8818
Lifetime years | 25 | 25 | 25 | 25 | 25 | 25 | 25
Annualised capital cost of transmission | 246998.03 | 13050.286 | 93031.3479 | 13050.286 | 16048.0069 | 13050.286 | 13050.286
Annual maintenance/opex per kW (1) | 50 | 235 | 100 | 44 | 44 | 44 | 63
Annual maintenance total | 16000 | 75200 | 150000 | 101200 | 202400 | 66000 | 144900
Storage maintenance per kW (1), |  |  | 50
Storage maintenance total |  |  | 16000 |  |  | 97000
Annual revenues total (5) | [5 empty] | 165950
Total annual opex less revenues | 16000 | 75200 | 166000 | 101200 | 202400 | -2950 | 144900
Fuel cost £/te (2) |  | 50
Fuel usage te/yr (calc) |  | 3869
Total annual fuel cost | 0 | 193450 | 0 | 0 | 0 | 0 | 0
Total annual cost | 367628.8884 | 457411.9215 | 1250205.9893 | 5260338.5342 | 2548943.2121 | 384809.9764 | 7662662.2015
Total cost per kWh consumed p/kWh | 13.1146 | 16.3175 | 44.5992 | 187.6548 | 90.9298 | 13.7275 | 273.3541
Cost of storage per kWh consumed | 0 | 0 | 5.4539 | 172.0497 | 60.0782 | 0 | 172.0497
FITs available primary: (6) | 11 |  |  | 4.5 | 4.5 | 9.4
FITs available storage: (6) |  |  | 11 |  |  | 11.5
Total annual subsidy | 308352 | 0 | 123571.6282 | 126144 | 126144 | 284272.32 | 0
Total subsidy per kWh consumed p/kWh | 11 | 0 | 4.4082 | 4.5 | 4.5 | 10.141 | 0
Net cost p/kWh | 2.1146 | 16.3175 | 40.191 | 183.1548 | 86.4298 | 3.5865 | 273.3541
cf PV at this level gets 29.3p subsidy
Source (1): DECC 2009 | Design of Feed-in Tariffs for Sub-5MW Electricity in Great Britain Quantitative analysis for DECC |  |  | Element Energy / Pyory for Dept of Energy & Climate Change | URN 09D/704, July 2009
Primary energy capital cost per kW (1) | 2750 | 4700 | 3750 | 1500 | 1500 | 7824
Annual maintenance/opex per kW (1) | 50 | 235 | 100 | 44 | 44 | 63
Source (2): see Biomass, high-reliability boiler; also, Balcas quotation for wood pellet delivery to Inverness area = £160/te
Source (3): Brian Willshire - Summers Inman
Transmission lines
| - access (land) | assume costs per km as for telecoms access |  | 617.7635 | per km
| - installation | Cost per m laid as for fibre optic cable - trenched |  | 55000 | per km
Soucre (4) - Small-scale Hydro project
BHA database of small hydroelectric schemes, 2010
| Average over 200-500kW range |  | average over 100-500kW range |  | say | 4000 | per kWh
| 3829.4396 |  | 4284.1329 | per kWh
|  |  | cf: FITs Quant analysis doc has |  |  | 3000 | pr kWh
Source (5): | National Non-Food Crop Centre Calculator
http://www.nnfcc.co.uk/metadot/index.pl?id=7197&isa=DBRow&field_name=file&op=download_file, accessed 17 April 2011
see Storage page for details
Source (6) DECC 2010 | Feed-in Tariffs: Government’s Response to the Summer 2009 Consultation
| Dept of Energy & Climate Change |  | 2010-02-01
Source (7) | Andres Pelamis approximation - check where from
| Cost Element Pelamis | Value (million £) | 750 | kW
| Onshore Transmission | 0.13
| Subsea cables | 5.6488
| Pelams Power Conversion Modules | 1.345
| Pelaimis Manufactured Steel Sections | 0.2
| Pelamis Mooring Instalation | 0.7
| Constrauction Mgmt & Commissioning | 0.415
| Total estimated cost for single unit (£m) | 8.4388 | 11251.6761 | £/kW
| cf: FITs Quant analysis doc has |  | 7824 | pr kWh | for shoreline / LIMPET
Source (8) | Tropical SA
http://www.tropical.gr/site-en/index.php?option=com_frontpage&Itemid=1
accessed 15 April 2010
see Storage page for details
Source (9) | Small hydro project - quote from supplier
11 kV cable, cost per km | 41000 | transmission losses = 4kW/km |  | 118000 | if short distance, use 11kV
33 kV cable, cost per kn | 105000 | transmission losses = 0.4kW/km |  | 182000 | if long distance use 33 kV
trenching costs per km | 57000 | £54-62k |  |  | must be buried for availability reasons
sand bedding costs per km | 20000
Note on B27: Kati Svehla: assumption, discussed with small hydro project
Note on E11: Kati Svehla: since hydrogen was produced by wind, all the electricity used is wind based
Note on E20: Kati Svehla: Note: assuming that storage can be had for £6-7m not £50+m
Note on F11: Kati Svehla: since hydrogen was produced by wind, all the electricity used is wind based
Note on F20: Kati Svehla: Note: assuming that storage can be had for £6-7m not £50+m
Note on H20: Kati Svehla: Note: assuming that storage can be had for £6-7m not £50+m

## Storage costs
Costs for Energy Storage
1) Pumped storage | 4000 | per kW | Soucre (8)
| 55% | civils | Source (1)
| 50% | increase for civil works with dam - assumptions
| 3300 | civils work adjusted
| 5100 | per kW total |  |  |  | cf quoted in Robertson
costs for 800m3 of compressed gas
[6 empty] | 23.8 | million
[6 empty] | 2.975 | per 100m3 tank |  | 26775000 | for compressed gas
2) Hydrogen
Balanced | Electroyser | 10 | 1200 l/min | 3448003.4166 |  | See quote |  | http://fuelcellhub.com/
| Compressed gas tanks | 9 | 100 m3 | 26775000 |  | 1 x 5000 Nm3 metal hydride tank |  |  |  |  | 44
| Fuel cells | 18 | 20kW | 2139024.4123 | kW | 16030 | sing$ | 0.474 | 7598.22
|  |  |  | 32362027.8289 |  | 721350 |  |  | 341919.9
Excess production | Electroyser | 5 | 1200 l/min | 1724001.7083
| Compressed gas tanks | 2.5 | 100 m3 | 7437500
| Fuel cells | 18 | 20kW | 2139024.4123
11300526.1206
http://www.tropical.gr
Electolyser | Euros | Pounds |  | 10 | Total cost (million £) | assuming disc. For large order 10%
30lt/m | 11000 | 9900 | 33 | a) | 3.8311 | 3.448
300lt/min | 28000 | 25200 | 84 | b) | 10.08 | 9.072
a) 1200lt/min | 425679.4341 | 383111.4907 | 319.2596
b) 1200lt/min | 1120000 | 1008000 | 840
TB-20KW Fuel Cells Power Generator | Euros | Pounds |  | 18 Items | Total cost (million £) | assuming disc. For large order 10%
1 KW | 8500 | 7650 | 7650 | a) | 2.3767 | 2.139 | 26.6667 | 680400
5KW | 27000 | 24300 | 4860 | b) | 8.748 | 7.8732
a) 20kW | 146709.4933 | 132038.544 | 6601.9272
b) 20kW | 540000 | 486000
use the cost/l for special fabrication
Hydrogent Metal Hybrid Tank | Euros | Pounds | £/lit | 220000000 | Total cost (million £) | assuming disc for large order 25%
60 ltr | 1200 | 1080 | 18 | a) | 1584 | 1188
750ltr | 40000 | 36000 | 48 | b) | 168.48 | 126.36
a) 15000 ltr | 54969.5006 | 49472.5505 | 3.2982
b) 15000 ltr | 120000 | 108000 | 7.2
Total cost | million £
Scenario a) | 1193.587
Scenario b) | 143.3052
3) Biogas
Source: National Non Food Crop Centre calculator
For an AD system of the size calculated in Wind+ Biogas v0.2:
Capital cost | £510,900-£1,038,800 |  | take upper limit | 1000000
Annual labour | 41000 |  | total | 97000 | pa
Annual overheads | 56000
Gate fee - for £40-48/te landfill tax | 35 | per te - assumption
| 14850 | te/year required, mixed slurry + food processing waste
| 20% | proportion of solids attrcting landfill tax
| 103950 | annual income
Income from fertiliser sales | 62000 | pa |  | 165950 | pa
Income from heat | 11000 | pa - don’t use as heat used in AD

## Summary Data Centre
Data Centres Project | [10 empty] | 1£ | 1.514 | $
Cost Assessment - Summary | [10 empty] | 1£ | 1.1082 | Euros |  |  | Comparisons
| Costs over 3 years: |  |  | Hydro | Biomass CHP | Tidal + PS | Wind + H2 | Wind+H2 xs | Wind + biogas | Wave + H2 |  | 1 acre | 4046.856 | m2 |  |  |  | Ours | Iceland small (UK version)
| TOTAL | 3674273.5267
| IT Equipment | 1250000 | 34.02% | [13 empty] | IT & Infrastruture | 66% | 44% |  | 322095.7728 | 3-yr services
| Data centre infrastructure | 516826.288 | 14.07% | [8 empty] | 1 kBTU | 0.29307 | kWh |  |  | Site | 9.462% | 28.18%
| Site | 347649.6792 | 9.462% | [13 empty] | Labour | 16.33% | 15.25% | BUT PwC included services under infrastructure
| Connectivity (note - ensure correct distances in ) | 336088.8176 | 9.147% | 1751532.9055 | 336088.8176 | 5261834.2437 | 336088.8176 | 336088.8176 | 336088.8176 | 5884629.6424 | [6 empty] | Energy | 8.209% | 12.57%
| Operating costs | 922095.7728 | 25.1%
| Net energy | 301612.9692 | 8.209% | 177830.6653 | 1372235.7646 | 3379903.0833 | 15402583.6027 | 7268397.6363 | 301612.9692 | 22987986.6045
| Energy |  |  | 1102886.6653 | 1372235.7646 | 3750617.9678 | 15781015.6027 | 7646829.6363 | 1154429.9292 | 22987986.6045 | [6 empty] | Cost per rack per year | 122475.7842 | 262794.261
| Subsidies |  |  | -925056 | 0 | -370714.8845 | -378432 | -378432 | -852816.96 | 0 | [6 empty] | Site cost or rent per m2 per month (office + IT) | 13.1836 | 380
Cost Element | Approach / Assumptions | [6 empty] | Total Cost | Costs rel to S of Scotland | Costs rel to California
IT equipment
- purchase | Estimate a typical cost per kW rated from a range of manufacturers' sites | 250 | kW |  | 5000 | per kW |  | 1250000 | Same | Same
- maintenance/replacement | lifetime: 3 years
Data Centre Infrastructure
Data centre container | HP 20 ft POD; 15m2 in footprint; delievred cost from press reports |  |  |  | 600000 | each, delivered |  | 396301.1889 | Same | Same
Fans |  | 5 | no | at | 2000 | each |  | 6605.0198 | Same | Same
Office | New build basic office building, laid out to hide POD and generator | 1400 | per m2 fitted out | 12.5 | m2 per person | 5 | persons | 87500
Backup generator | Need one 350 kW diesel generator as backup for each case | 40000 | delivered | each |  |  |  | 26420.0793
#VALUE!
Site | [11 empty] | Land + Gen Infrastructure |  | #VALUE! | #VALUE!
Land purchase | Undeveloped scrubland at edge of town - may have utilities/ brownfield | 10000 | per acre | 2.4711 | per m2 | 5625 | total m2 | 13899.6792 | Less | Much less |  | Services | 107365.2576 | 322095.7728
Security fence | 3m anti-climb, anti-cut fencing; requires 25 m security belt round buildings | 300 | per m |  |  | 300 | m | 90000
Base slab | Solid base needed for the work area, parking & access - 300mm depth concrete slab, drainage, services | 150 | per m2 |  |  | 1625 | m2 | 243750
Fibre optic link | Establish nearest access station (POP) and distance to data centre; requires 2 | [7 empty] | Same | More
Access (land) | 1m right of way, land cost 25% that for site; two independent routes | 5 | km | 5 | 000m2 | 617.7635 | cost per | 3088.8176
Connection | one-off cost, at each end of each of 2 connections | 4 | required |  |  | 5000 | each | 20000
Cable | Single- mode fibre is £1 per m approx | 5 | km |  |  | 1000 | per km | 5000
Trenching | 2m deep, assume mainly in field by side of road | 5 | km |  |  | 55000 | per km | 275000
Road crossings | Road crossings are expensive | 6 | no |  |  | 5500 | each | 33000
Annual Operating Costs | [8 empty] | Same | Less
Labour | Based on PwC small dc but manager/admin roles done by ops staff; 3% wage inflation | 4 | staff |  | 50000 | per year |  | 200000
Services | Based on PwC annual costs - % of data centre + comms connections capital cost | 20% |  |  | 536826.288 | capital cost |  | 107365.2576 | Same | Less
Annual Energy Costs | See page on Energy & Storage costs for details | 320 | kW data centre sues |  | 2803200 | kWh per year |  |  | Less | Less
- Hydroelectric | [5 empty] | 13.1146 | p per kWh | 367628.8884
- Biomass CHP | [5 empty] | 16.3175 |  | 457411.9215
- Tidal current + pumped st | [5 empty] | 44.5992 |  | 1250205.9893
- Wind + hydrogen | [5 empty] | 187.6548 |  | 5260338.5342
- Wind + Hydrogen xs | [5 empty] | 90.9298 |  | 2548943.2121
- Wind + biogas | [5 empty] | 13.7275 |  | 384809.9764
- Wave + hydrogen | [5 empty] | 273.3541 |  | 7662662.2015
Subsidies - effective FITs per data centre kWh
- Hydroelectric | (see Energy costs page) |  |  |  |  | 11 | p per kWh | 308352
- Biomass CHP | [5 empty] | 0 |  | 0
- Tidal current + pumped st | [5 empty] | 4.4082 |  | 123571.6282
- Wind + hydrogen | [5 empty] | 4.5 |  | 126144
- Wind + Hydrogen xs | [5 empty] | 4.5 |  | 126144
- Wind + biogas | [5 empty] | 10.141 |  | 284272.32
- Wave + hydrogen | [5 empty] | 0 |  | 0

## Operating costs
People & Services costs
Number of people:
Take PwC study numbers and assume that: 1) manager + admin roles are rolled into ops & analyst staff
2) less than 2 people per skills set is not robust on the long term
Total staff: | 2 | operations
| 2 | analysts
| 0 | management & admin
| 4 | total staff
Costs per head:
PwC study | Small | Med | Large
People | 7 | 14 | 15
Euros | 370101 | 701270 | 740483 | Euros
Cost/person | 52871.5714 | 50090.7143 | 49365.5333 | Euros | Can this be true?
| 47709.4129 | 45200.067 | 44545.6897
Wage inflation for IT
3%
starting point | 45000
2007 | 46350
2008 | 47740.5
2009 | 49172.715
2010 | 50647.8965
Use | 50000 | per year as average cost of IT staff
Assume that 3ops + 2 analysts are enough to run the POD between them
ie rel. to PwC study,
Services:
PwC study says 20% of infrastructure costs are an annual cost
covers: maintenance, services for electrical & mechanical parts as well as external telecomms; replacement parts etc
Use | 20% | of costs of: | data centre
fans
fibre optic cable connections

## Connectivity
Connectivity costs
Fibre optic link |  | Soucre (1) | Jim Mennie at Telecosse - unless otehrwise shown
|  | Soucre (2) | Brian Willshire - Summers Inman
|  | Soucre (3) | Marvin Smith at Shetland Council
Establish distance to nearest Point of Presence for Fibre Optic link
Two separate lines required - physically separate & organistionally as well if possible
In Shetland, Concil is building dual line from SHEFA to Lerwick (3)
access (land) | needs 1m right of way, assume land cost 25% that for site
LOCATION | NR LERWICK - wind+ biogas | line 1 | 2 | km | 2 | 000m2
|  | line 2 | 3 | km | 3 | 000m2
| Total |  | 5 | km | 5 | 000m2 | cost | 617.7635 | per m2
connection | one-off cost, at each end of each of 2 connections - £5000 is a generous estimate |  | 4 | required |  | 5000 | each | cost | 20000
cable | Single- mode fibre is £1 per m approx |  | 5 | km |  | 1000 | per km |  | 5000
cable trenching (2) | 2m deep, assume mainly in field by side of road - £50-60 per metre |  | 5 | km |  | 55000 | per km |  | 275000
road crossings | Road crossings are expensive - assume 10 x value of normal run, over 10m |  | 6 | no |  | 5500 | per crossing |  | 33000
Assumed locations: |  | links
Hydroelectric | on A970, say 15 km from Lerwick
Biomass CHP | 2-3 km from Lerwick | 2- 3
Tidal current + pumped st | Toft, nr Yell Sound: 46km from Lerwick | 46 -46
Wind + hydrogen | 2-3 km from Lerwick | 2- 3
Wind + H2 excess prod | 2-3 km from Lerwick | 2- 3
Wind + biogas | 2-3 km from Lerwick | 2- 3
Wave + hydrogen | Sandness, W coast of Mainland, 52km | 51+52

## Site costs
Office & Land Required
[10 empty] | Sources: | (1) PWC study
1) | HP 20 ft POD (4) |  | 2.4 | m wide | [6 empty] | (2) Brian Willshire - Summers Inman
|  |  | 6.1 | m long |  | 14.64 |  | 15 | m2 |  | (3) Elean Data Centre website, layout drawings of first building
(4) HP POD brochure
2) | Standby generator + fuel takes up that much space again | [6 empty] | 15 | m2 |  | (5) Betafence OOM estimate for anti-intruder fence (suppliers to Sullom Voe terminal & Faslane)
3) | Office building: | [8 empty] | Office space estimate
| Offices + visitor space + sorgae/ workroom + loos+ kitchen +corridor + security booth | [8 empty] | cf Eilean data centre - |  |  | 6 | m per cm | see Eilean website / brochure
| Use Iceland study estimate (1) |  |  | 12.5 | 4 | people |  | 50 | m2
[8 empty] | 6.2 x 10m |  | It build area |  | 5.4 | 11.4 | 61.56
| Cost per m2 office, fully fitted out (2) |  |  |  | 1400 |  | Total | 70000 |  | smaller office |  | 7.2 | 6 | 43.2
[10 empty] | kitchen/WC/shower |  | 3 | 10.2 | 30.6
[10 empty] | Security area |  | 7.8 | 3.6 | 28.08 | 163.44
4) | Total site area & perimeter
| Parking for 12 cars |  | 3 | m wide each | [5 empty] | Total of block |  | 12 | 15 | 180
|  |  | 5.5 | m long each
|  |  | 12 | cars |  | 16.5 | m2 per car
[6 empty] | 198 | m2 total
|  |  | Double for turning/access |  |  | 396 | m2 |  |  | cf rule of thumb for Iceland study |  |  | 12.5 | m2 per person overall
36m x 11m
| Turning area for trucks etc | [6 empty] | 18 m x 16m
| All this can be within an area |  |  |  | 25 | m | wide
[5 empty] | 25 | m | long
| Requires 20-30 yards around it for security fence |  |  |  |  | 75 | m | wide
| Access/ turning etc in the security belt at front |  |  |  |  | 75 |  | long
| Land |  | Cost (2): | 10000 | per acre | 5625 | m2 area required |  | estimate is for scubland at edge of town - utilities included
| Security fence |  | Cost (5) | 300 | per m | 300 | m long perimeter: |  | estimate is for anti-intruder, andti-cut high security fencing installed by supplier
5) | Base slab
| Paved area | Main block |  |  | 35 | m | wide
[5 empty] | 45 | m | long
|  | Access road |  |  | 5 | m | wide
[5 empty] | 10 | m | long
| 300mm concrete slab |  | Cost (2) | 150 | per m2 | 1625 | m2 required

## Infrastructure
Data Centre Infrastructure
Containerised Data Centre
| Use press quoted costs for HP 20 ft POD; 15m2 in footprint | [5 empty] | 600000 | each, delivered | 396301.1889
| Source: | Datacentreknowledge.com
Alternative: SUN MD20 Modular Data Centre, 25 kW/rack, 8 racks quoted cost is $559,000
Fans | 4 | fans at 1000cfm required
| 1 | spare
| 5 | total |  | 2000 | each |  | 6605.0198
Soucre | http://www.canadianblower.com/axialfan/index.html
Backup Generator
Web enquiry | Caterpillar 350kW |  | 39500
| Cummins 350kW |  | 32000
Use |  |  | 40000 |  |  | 26420.0793

## IT costs
IT costs estimate
Cost Element |  |  |  |  | Cost
IT equipment
- purchase | 250 | kW | 5000 | per kW | 1250000
assume replaced every 3 years
Data From:
PwC Iceland study 1997 - small DC
PwC Iceland study - 20 racks of mainly LD servers estimated at Euros 2.8m |  |  | 2.5266 | million for | 95 | servers
From EPA report 2007 - energy use per server
|  |  | normal | 2000 | 90% | 1800
|  |  | high end | 71500 | 10% | 7150
[6 empty] | 8950 | kWh per year for average server
[6 empty] | 1.0217 | kW is the 'smeared average' server
|  |  | Therefore, the Iceland study server nos are: |  |  |  | 95 | low | 190 | med
|  |  | Cost per server: |  |  |  | 26.539 | £k low |  |  | Seems very high
[7 empty] | 25.7411 | £k med
Maunfacturers
Look at range of server costs and power for manufacturers; estimate a typical cost per kW rated
Servers: | scale | Form fact | Watts rated | Costs £ | costs per kW
Dell Power Edge R710 | medium | 2U | 870 | 1049 | 1205.7471
Dell Power Edge R300 | low | 1U | 400 | 419 | 1047.5
Dell Blade M905 x8 | high | 8 sideways | 7080 | 60656 | 8567.2316 | here I have assumed a price of £5000 for a M1000e power unit which serves 8 M905 servers
HP Pro-Liant DL580 | high | 4U | 885 | 7000 | 7909.6045 | not given - assumed power same as 1 Dell blade
IBM x86 Enterprise server | high | 4U | 2000 | 10000 | 5000 | $10-$20k
Use an average of £5000 per kW for now
Sources | Dell website IBM website HP website

## Iceland study
Costs data
Source: PwC Iceland study 2007
Quotes:
Gartner Group study 2006/07: ratio of opex to capex costs for data centres
|  | 2006 | 145%
|  | 2009 | 579% | carrying on current trends
387%
|  |  | 204% | best case
APC study on TCO: |  |  | Euro 61,500-115,000 per rack
of which 20% is energy costs
Iceland study
Characteristics
| Single company, centre running 1-2 servers per client, basic apps | [6 empty] | Service to individual local companies as required
| Office hours support only | [6 empty] | Low value / backup service for intrenational clients
| Customer IT staff perform basic functions | [6 empty] | Support & ops mainly by data centre team
Low power requiremnets
Small Data centre | [7 empty] | Med data centre
| 150 | m2 | [5 empty] | 300 | m2
| 13 | racks low density servers | [5 empty] | 28 | racks low density servers
| 5 | racks routing/ pathcing equipment | [5 empty] | 9 | racks routing/ pathcing equipment
| 7 | racks high-density servers | [5 empty] | 13 | racks high-density servers
Average power / rack: |  | 7.45 | kW |  |  |  |  | 5.06 | kW
|  | 13000 | BTU/s |  | 3.8099 | = low density power |  | 13000 | BTU |  | 3.8099 | = low density power
| Max diss'n | 780 | kBTU | = twice actually needed = 4x IT? |  |  |  | 1742 | kBTU
|  | 325 | kBTU | average IT load |  | 95.2481 | kW | 650 | kBTU | average IT load |  | 190.4962 | kW
|  | 186.25 | kW | Total IT load |  |  |  | 253 | kW | Total IT load
|  | 400 | kVA genset |  |  |  |  | 800 | kVA genset
|  | 7 | persons to run the thing: |  |  |  |  | 14 | persons to run the thing:
|  |  | 3 ops, 2 back office, 1 mgr, 1 admin | [5 empty] | 5 ops, 5 back office, 2 mgrs, 2 admin
Infrastructure |  | 682000 | Euros | of which 20% pa recurring |  |  |  | 1247000 | Euros | of which 20% pa recurring
Newtork & servers |  | 2794000 | Euros | replaced after 3 yrs |  |  |  | 5420000 | Euros | replaced after 3 yrs
2521205.5586
Network & servers cost |  |  | 13.5367 | £k/kW |  |  |  |  | 19.3313 | £k/kW
Annual power cost |  | 112320 | Euros | Iceland
|  | 350010 |  | USA?
|  | 300010 |  | UK |  |  | 700020
Rent: |  | 400 | £ per rack per month, UK, cheap northern areas
|  | 120000 | £ per annum |  |  |  |  | 240000 | £ per annum
Free cooling savings: |  | 65.521 | Euros | pa
Non-IT space per 50% ratio |  |  |  | 75 | m2 |  |  |  | 150 | m2
Non-IT space per 2.5m2 per rack IT |  |  |  | 87.5 |  |  |  |  | 175 | m2
Space per person |  |  |  | 12.5 |  |  |  |  | 12.5
Small data centre
|  | Iceland | USA | UK | India
Annual network/infrastr |  | 1067788 | 1067788 | 1067788 | 1067788 |  | 44%
Annual rental (land) |  | 378000 | 592000 | 684000 | 648000 |  | 28.18%
Annual power cost |  | 112320 | 213174 | 305010 | 284400 |  | 12.57%
Annual labour cost |  | 451584 | 353251 | 370107 | 80689 |  | 15.25%
|  | 2009692 | 2226213 | 2426905 | 2080877
|  | 13397.9467 | 14841.42 | 16179.3667 | 13872.5133
Annual cost |  |  |  | 6569856.5241
Cost per rack per year |  |  |  | 262794.261
Land cost per m2 per m |  |  |  | 380