## Summary
Wind & Biogas Power Calculations
Summary
Lerwick
Summary outputs from various turbines
|  | 320 | kW Data centre demand
Turbine | Total | Supply / demand | % energy from wind | % energy from biogas | excess electricity/ total demand | Biogas req'd | Waste req'd - sorted & shredded | Waste req'd - mixed slurry & waste
| kWh |  |  |  |  | m3 | te/ month | te/ month
GE 1.5MW sle | 4874420 | 1.7389 | 64.71% | 35.29% | 62.78% | 474777.6 | 350 | 1250 | selected option
Vestas V52-850 | 2307730 | 0.82325 | 54.51% | 45.49% | 33.78% | 612024 | 453.3511 | 1619.805
Conclusions
- It would be possible to power the data centre with a combination of wind turbine + biogas from anaerobic digestion
- In this combination, excess wind energy is not stored; biogas acts as energy store to buffer low wind periods
- The feasibility is restricted by the amount of waste actually produced and collected in an area
- you would need a population of over 25,000 producing an average amount of organic waste to support this
- a substantial agricultural or food processing industry in the area would be a good enabler - eg, distillery, fish farming/processing
- A turbine up to 1.5MW attracts 9.4p/kWh in FITs vs 4.5p for bigger one
- AD attarcts FITs at 11.5p so may be be better economics than wind + hydrogen
- Excess electricity is produced, depending on size of turbine; could generate revenue eg from producing compressed air
[9 empty] | Turbine: | GE 1.5MW sle
Summary of energy sources
| Wind | Biogas
| kWh | kWh |  | Wind | Biogas
Jan | 188850 | 49230 |  | 0.79322 | 0.20678
Feb | 137147.5 | 77892.5 |  | 0.63778 | 0.36222
Mar | 164332.5 | 73747.5 |  | 0.69024 | 0.30976
Apr | 119110 | 111290 |  | 0.51697 | 0.48303
May | 102015 | 136065 |  | 0.42849 | 0.57151
Jun | 138132.5 | 92267.5 |  | 0.59953 | 0.40047
Jul | 140372.5 | 97707.5 |  | 0.5896 | 0.4104
Aug | 106155 | 131925 |  | 0.44588 | 0.55412
Sep | 163455 | 66945 |  | 0.70944 | 0.29056
Oct | 168560 | 69520 |  | 0.708 | 0.292
Nov | 194025 | 36375 |  | 0.84212 | 0.15788
Dec | 191925 | 46155 |  | 0.80614 | 0.19386
| 1814080 | 989120
Storage
Is the single year typical of the long term climate?
[10 empty] | Lerwick: | grid ref: | HU474414
[10 empty] | Average wind speed in 1978 (13) |  |  | 7.4151 | m/s | Assume at 10m height?
From (12):
[11 empty] | at 10m | 6.6 | m/s
[11 empty] | at 25m | 7.7 | m/s
[11 empty] | at 45m | 8.6 | m/s | BUT is 9.2 in next km to the W
Source
[10 empty] | (12) | DECC wind speed database for UK http://www.decc.gov.uk/en/windspeed/default.aspx
[10 empty] | (13) | MERIT: Time series wind speed data from University of Strathclyde energy supply/demand matching program
Conclusion: likely to produce more energy than calculated with a tall turbine
Also, possible to increase energy production by moving slightly to the West of the town
GE 1.5MW sle
Power production profiled in next worksheet: | [6 empty] | Data centre demand: | 320 | kW | Turbine: | GE 1.5MW sle

## Biogas production
Biogas Supply Calculations
Input parameters
| Upper bound production (dry, MSW, separated) (7) |  |  |  | 150 | m3/te | BUT Zorg Biogas is quoting 200m3/te for sorted waste
| Lower bound production (wet, mix of manure & MSW) (7) |  |  |  | 40 | m3/te | BUT Updated Guidebook on Biogas (FAO) SD dimensions says 45m3/te
| Safety margin |  |  |  | 20% |  | BUT you may not need to use biogas - there is heat off CHP as well
Do not need internal use of biogas - waste heat from CHP system
| Biogas required | Upper bound production | Lower bound production | Storage | 1301.3699 | m3 per day av production
| m3 | te | te | m3
|  |  |  | 58500 |  |  | Conclusion:
Jan | 23630.4 | 196.92 | 738.45 | 75212.0658
Feb | 37388.4 | 311.57 | 1168.3875 | 74262.0219 |  |  |  | 475000 | m3 biogas per year required to fill in for wind shortfalls, for 1.5MW turbine
Mar | 35398.8 | 294.99 | 1106.2125 | 79205.6877 |  |  |  | Storage required: |  |  |  | 58500 | m3 | biogas
Apr | 53419.2 | 445.16 | 1669.35 | 64827.5836 |  |  |  | This can be prodcued by anaerobic digestion systems using:
May | 65311.2 | 544.26 | 2040.975 | 39858.8493 |  |  |  | separated & shredded organic MSW |  |  |  | 3956.48 | te/year | 329.7067 | te/month
Jun | 44288.4 | 369.07 | 1384.0125 | 34611.5452 |  |  |  | mix of slurry household & industrial food waste |  |  |  | 14836.8 | te/year | 1236.4 | te/month
Jul | 46899.6 | 390.83 | 1465.6125 | 28054.411 |  |  |  | sewage from |  |  |  | 154852.4462 | people
Aug | 63324 | 527.7 | 1978.875 | 5072.8767
Sep | 32133.6 | 267.78 | 1004.175 | 11980.3726 |  |  |  | Average waste production per capita, UK (9) |  |  |  | 0.588 | te/yr
Oct | 33369.6 | 278.08 | 1042.8 | 18953.2384 |  |  |  | Assumed % of organic matter |  |  |  | 50%
Nov | 17460 | 145.5 | 545.625 | 40534.3342 |  |  | Size of population needed to support this facility |  |  |  |  | 50465.3061 | people | cf Shetland mainland has 17,750 |  | Source (6) | Haswell-Smith, H: The Scottish islands; Canongate, Edinburgh 2004
Dec | 22154.4 | 184.62 | 692.325 | 58722.4 |  |  | ie probably too large for NW remote locations
unless there is a large food processing or fish farming business that generates organic waste
Total biogas: | 474777.6 | 3956.48 | 14836.8 |  |  |  | Checking with the zero-carbon community project, we have used conservative assumptions about quantities
Sewage from 1000 animals produces (8): |  |  |  | No. of animals required
| kg/day each | l/kg | m3/year gas total
cows | 17 | 24 | 186150 | 2550.5109 |  |  |  |  | Soucre (7) | deMes, T Z D; Stams, A J M; Reith, J H; Zeeman, G
pigs | 2 | 20 | 14600 | 32519.0137 | [5 empty] | Methane production by anaerobic digestion of wastewater and solid wastes
humans | 0.3 | 28 | 3066 | 154852.4462 | [5 empty] | in: Bio-methane and bio-hydrogen, ed J H rieth, RH Wijffels & H Barten
Dutch Biological Hydrogen Foundation 2003
[10 empty] | Wet digestion (high liquid content) |  |  | Dry digestion (high solids content)
[9 empty] | Type | AVECON process | VAGRON process | Bigadan | Valorga | Dranco | Kompogas | Biocel
[9 empty] | temp range | mesophilic | thermophilic | mesophilic | mesophilic | thermophilic |  | mesophilic
[9 empty] | material | separated MSW & sewage sludge | separated MSW; Organic Waste Fraction washed out | shredded organic industrial & household waste, manure |  |  |  | separated MSW
[9 empty] | solids content | 10-15% |  |  | 30% |  | high
[9 empty] | gas m3/te input | 100-150 |  | 40-45 |  | 100-200
[9 empty] | gas m3/te organics |  | 125 |  | 220-250
[9 empty] | internal use | 20-30% |  | 10%
[9 empty] | Energy content of biogas: |  | 19-26 MJ/m3 (lower value) |  | 22-30 MJ/m3 (high value)
[9 empty] | Electrical energy conversion using gas engine |  |  | 35% | (Germany example) | 29-38% | (review article)
[9 empty] | Electricity exported as % of biogas energy |  |  | 21%
[9 empty] | Source (8) | Catherine's SE Asia small AD paper | [5 empty] | Source (10)
[9 empty] | Type of animal | Range of outputs | Range of energy content | Amount per animal | gas production | energy in gas |  | gas production
[10 empty] | kg/day | l/kg wet fuel | kg/ day | l/kg | kJ/day |  | l/kg
[13 empty] | =m3/te | 23.1 |  | =m3/te
kJ/l
[10 empty] | from your article - check that energy content is related to kg wet dung |  | use mid range | usemid range | =col D*col E* conversion factor F7 |  | usemid range
[9 empty] | cow (4) |  |  | 17 | 24 | 9424.8 |  | 0.023-0.04
[9 empty] | pig (4) |  |  | 2 | 20 | 924 |  | 0.040--.059
[9 empty] | human in SE Asia (4) |  |  | 0.3 | 28 | 194.04
[9 empty] | human in SE Asia (5) | 0.3-0.5 | [5 empty] | 0.02-0.028
[9 empty] | human in N Europe | 0.14-
[9 empty] | poultry | [6 empty] | 0.065 -0.116
[9 empty] | Source (9) | European Commission Eurostat
Waste Statistics, April 2009
http://epp.eurostat.ec.europa.eu/statistics_explained/index.php?title=File:Municipal_waste.PNG&filetimestamp=20090430100031
accessed 145 April 2010-04-15
[9 empty] | UK total waste per capita 2006 |  | 588 | kg
[9 empty] | Soource (10) | William's fao website

## Power production
Power Calculations
Time series calculations
Lerwick
Inputs | [14 empty] | Note: Paste turbine characteristics as values in column P
Data Centre Power Demand | [13 empty] | Wind speed | GE 1.5MW sle
| IT power |  | 250 | kW |  | Conclusion | [7 empty] | m/s | kW
| Fixed infrastructure |  | 0.25 | PUE |  | % of total energy from wind |  |  | 64.71% |  |  |  |  | 0 | 0
| Cooling |  | 0.03 | PUE |  | % from biogas |  |  | 35.29% |  |  |  |  | 0.5 | 0
| Total |  | 320 | kW |  | wasted electricity / total |  |  | 62.78% |  |  |  |  | 1 | 0
| Energy per time step |  | 320 | kWh | [9 empty] | 1.5 | 0
| Total demand in year |  | 2803200 | kWh |  | Turbine is operating: | [7 empty] | 2 | 0
[14 empty] | 2.5 | 0
Gas engine with biogas | [5 empty] | Exactly on demand |  | 0% | 0 | days on average |  |  |  | 3 | 0
| Electrical conversion efficiency (7) | 30% |  |  |  | Excess supply |  | 50.33% | 183.7083 | days on average |  |  |  | 3.5 | 25
| Energy content of biogagas (7) | 25 | MJ/m3 |  |  | Excess demand |  | 49.66% | 181.25 | days on average |  |  |  | 4 | 60
| Energy content of biogas | 6.9444 | kWh/m3 |  |  | Turbine cut out |  | 0.04566% | 0.16667 | days on average |  |  |  | 4.5 | 80
[6 empty] | Turbine not cut in |  | 19.01% | 69.375 | days on average |  |  |  | 5 | 110
| Turbine cut-in | 3.5 | m/s | [10 empty] | 5.5 | 150
| Turbine cut-out | 25 | m/s | [10 empty] | 6 | 220
[5 empty] | Totals | 4874420 | 3060340 | 989120 | kWh | 474777.6 | m3 biogas | 1814080 | kWh from wind | 6.5 | 300
[14 empty] | 7 | 400
Site | Date/time | Ambient | Wind | Wind | Power | Energy | Excess | Excess |  | Biogas | Biogas | Useful | Useful | 7.5 | 500
|  | temperature | speed | direction |  | in step | Supply | Demand |  | required | per month | wind energy | wind energy | 8 | 635
|  | C | m/s | deg from N | kW | kWh | kWh | kWh |  | m3 | m3 | kWh | kWh/ month | 8.5 | 770
[14 empty] | 9 | 900
Lerwick | 1978-01-01 00:30 | 2.4 | 13.9 | 195 | 1490 | 740 | 420 | 0 |  | 0 | 23630.4 | 320 | 188850 | 9.5 | 1025
Lerwick | 1978-01-01 01:30 | 7.6 | 15.2 | 240 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320 |  | 10 | 1150
Lerwick | 1978-01-01 02:30 | 7.9 | 16 | 240 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320 |  | 10.5 | 1270
Lerwick | 1978-01-01 03:30 | 8 | 15.8 | 240 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320 |  | 11 | 1340
Lerwick | 1978-01-01 04:30 | 8 | 16.2 | 240 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320 |  | 11.5 | 1400
Lerwick | 1978-01-01 05:30 | 8 | 17 | 242.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320 |  | 12 | 1450
Lerwick | 1978-01-01 06:30 | 8 | 17 | 247.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320 |  | 12.5 | 1470
Lerwick | 1978-01-01 07:30 | 7.8 | 16.4 | 250 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320 |  | 13 | 1480
Lerwick | 1978-01-01 08:30 | 7.3 | 16.7 | 250 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320 |  | 13.5 | 1490
Lerwick | 1978-01-01 09:30 | 7 | 18 | 250 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320 |  | 14 | 1500
Lerwick | 1978-01-01 10:30 | 6.7 | 19.4 | 250 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320 |  | 14.5 | 1500
Lerwick | 1978-01-01 11:30 | 6.2 | 20.6 | 252.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320 |  | 15 | 1500
Lerwick | 1978-01-01 12:30 | 6.1 | 20.8 | 257.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320 |  | 15.5 | 1500
Lerwick | 1978-01-01 13:30 | 5.6 | 19.9 | 262.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320 |  | 16 | 1500
Lerwick | 1978-01-01 14:30 | 5.4 | 18.9 | 267.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320 |  | 16.5 | 1500
Lerwick | 1978-01-01 15:30 | 5.9 | 18 | 272.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320 |  | 17 | 1500
Lerwick | 1978-01-01 16:30 | 6 | 16.6 | 277.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320 |  | 17.5 | 1500
Lerwick | 1978-01-01 17:30 | 5.5 | 14.5 | 280 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320 |  | 18 | 1500
Lerwick | 1978-01-01 18:30 | 4.7 | 12.2 | 280 | 1450 | 1475 | 1155 | 0 |  | 0 |  | 320 |  | 18.5 | 1500
Lerwick | 1978-01-01 19:30 | 4.6 | 10.6 | 280 | 1270 | 1360 | 1040 | 0 |  | 0 |  | 320 |  | 19 | 1500
Lerwick | 1978-01-01 20:30 | 4.5 | 10.6 | 275 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320 |  | 19.5 | 1500
Lerwick | 1978-01-01 21:30 | 4.6 | 10.9 | 262.5 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320 |  | 20 | 1500
Lerwick | 1978-01-01 22:30 | 4.5 | 10.4 | 255 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320 |  | 20.5 | 1500
Lerwick | 1978-01-01 23:30 | 4.4 | 10.4 | 255 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320 |  | 21 | 1500
Lerwick | 1978-01-02 00:30 | 4.6 | 10.9 | 252.5 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320 |  | 21.5 | 1500
Lerwick | 1978-01-02 01:30 | 4.1 | 10.7 | 247.5 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320 |  | 22 | 1500
Lerwick | 1978-01-02 02:30 | 4.1 | 9.7 | 255 | 1025 | 1147.5 | 827.5 | 0 |  | 0 |  | 320 |  | 22.5 | 1500
Lerwick | 1978-01-02 03:30 | 4.1 | 8.3 | 275 | 635 | 830 | 510 | 0 |  | 0 |  | 320 |  | 23 | 1500 | Wind speed characteristics
Lerwick | 1978-01-02 04:30 | 3.1 | 7.6 | 277.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320 |  | 23.5 | 1500 | occasions below | % exceeded | m/s
Lerwick | 1978-01-02 05:30 | 2.1 | 6.9 | 275 | 300 | 400 | 80 | 0 |  | 0 |  | 320 |  | 24 | 1500 | 8760 | 0% | 30
Lerwick | 1978-01-02 06:30 | 1.8 | 5.9 | 287.5 | 150 | 225 | 0 | 95 |  | 45.6 |  | 225 |  | 24.5 | 1500 | 8759 | 0.01142% | 29
Lerwick | 1978-01-02 07:30 | 1.1 | 4.9 | 295 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115 |  | 25 | 1500 | 8759 | 0.01142% | 28
Lerwick | 1978-01-02 08:30 | 0.7 | 3.7 | 302.5 | 25 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5 |  | 25.5 | 0 | 8758 | 0.02283% | 27
Lerwick | 1978-01-02 09:30 | 1 | 2.9 | 312.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5 |  | 26 | 0 | 8757 | 0.03425% | 26
Lerwick | 1978-01-02 10:30 | 0.8 | 3.3 | 322.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0 |  | 26.5 | 0 | 8756 | 0.04566% | 25
Lerwick | 1978-01-02 11:30 | 0.5 | 4.5 | 337.5 | 80 | 40 | 0 | 280 |  | 134.4 |  | 40 |  | 27 | 0 | 8754 | 0.06849% | 24
Lerwick | 1978-01-02 12:30 | 0.5 | 5 | 342.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95 |  | 27.5 | 0 | 8752 | 0.09132% | 23
Lerwick | 1978-01-02 13:30 | 0.5 | 4.7 | 337.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95 |  | 27.5 | 0 | 8744 | 0.1826% | 22
Lerwick | 1978-01-02 14:30 | 0.4 | 4 | 332.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70 |  |  |  | 8735 | 0.2854% | 21
Lerwick | 1978-01-02 15:30 | 0.3 | 3.6 | 327.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5 |  |  |  | 8722 | 0.4338% | 20
Lerwick | 1978-01-02 16:30 | 0.3 | 3.4 | 325 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5 |  |  |  | 8703 | 0.6507% | 19
Lerwick | 1978-01-02 17:30 | -0.1 | 3 | 327.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0 |  |  |  | 8686 | 0.8447% | 18
Lerwick | 1978-01-02 18:30 | -0.9 | 2.7 | 332.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0 |  |  |  | 8634 | 1.438% | 17
Lerwick | 1978-01-02 19:30 | -2 | 3 | 337.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0 |  |  |  | 8558 | 2.306% | 16
Lerwick | 1978-01-02 20:30 | -2.5 | 3.3 | 337.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0 |  |  |  | 8445 | 3.596% | 15
Lerwick | 1978-01-02 21:30 | -2.6 | 3.6 | 332.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5 |  |  |  | 8244 | 5.89% | 14
Lerwick | 1978-01-02 22:30 | -2.9 | 4.8 | 335 | 80 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5 |  |  |  | 7977 | 8.938% | 13
Lerwick | 1978-01-02 23:30 | -1.9 | 6.2 | 170 | 220 | 150 | 0 | 170 |  | 81.6 |  | 150 |  |  |  | 7634 | 12.85% | 12
Lerwick | 1978-01-03 00:30 | -1.1 | 6.7 | 5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260 |  |  |  | 7152 | 18.36% | 11
Lerwick | 1978-01-03 01:30 | -1 | 6.7 | 10 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300 |  |  |  | 6596 | 24.7% | 10
Lerwick | 1978-01-03 02:30 | -1 | 6.9 | 7.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300 |  |  |  | 5981 | 31.72% | 9
Lerwick | 1978-01-03 03:30 | -1.1 | 7.1 | 2.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320 |  |  |  | 5252 | 40.05% | 8
Lerwick | 1978-01-03 04:30 | -1.2 | 6.8 | 177.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320 |  |  |  | 4476 | 48.9% | 7
Lerwick | 1978-01-03 05:30 | -1.2 | 6.9 | 352.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300 |  |  |  | 3568 | 59.27% | 6
Lerwick | 1978-01-03 06:30 | -1.4 | 6.9 | 350 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300 |  |  |  | 2677 | 69.44% | 5
Lerwick | 1978-01-03 07:30 | -2 | 6.5 | 345 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300 |  |  |  | 1665 | 80.99% | 4
Lerwick | 1978-01-03 08:30 | -2.5 | 6.5 | 335 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300 |  |  |  | 838 | 90.43% | 3
Lerwick | 1978-01-03 09:30 | -2.4 | 6.8 | 327.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300 |  |  |  | 380 | 95.66% | 2
Lerwick | 1978-01-03 10:30 | -1.5 | 7.2 | 322.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320 |  |  |  | 83 | 99.05% | 1
Lerwick | 1978-01-03 11:30 | -0.5 | 8.2 | 322.5 | 635 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-03 12:30 | -0.4 | 9.9 | 325 | 1025 | 830 | 510 | 0 |  | 0 |  | 320
Lerwick | 1978-01-03 13:30 | -0.4 | 11.4 | 325 | 1340 | 1182.5 | 862.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-03 14:30 | -0.6 | 12.2 | 327.5 | 1450 | 1395 | 1075 | 0 |  | 0 |  | 320
Lerwick | 1978-01-03 15:30 | -0.6 | 12.2 | 330 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-01-03 16:30 | -0.1 | 11.9 | 332.5 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-01-03 17:30 | -0.1 | 11.5 | 335 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-01-03 18:30 | -0.3 | 11.3 | 330 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-01-03 19:30 | -1.4 | 11.4 | 322.5 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-01-03 20:30 | -2.1 | 11.1 | 322.5 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-01-03 21:30 | -1.6 | 10.5 | 325 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-01-03 22:30 | -1.4 | 10.1 | 322.5 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-01-03 23:30 | -1.3 | 10 | 322.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-01-04 00:30 | -1 | 9.9 | 327.5 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-04 01:30 | -0.4 | 9.4 | 330 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-04 02:30 | 0 | 8.7 | 330 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-01-04 03:30 | 0 | 8.3 | 327.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-04 04:30 | -0.1 | 8 | 325 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-01-04 05:30 | 0.3 | 7.8 | 327.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-04 06:30 | 0.7 | 7.2 | 332.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-01-04 07:30 | 0.5 | 5.8 | 335 | 150 | 275 | 0 | 45 |  | 21.6 |  | 275
Lerwick | 1978-01-04 08:30 | 0.4 | 4.4 | 332.5 | 60 | 105 | 0 | 215 |  | 103.2 |  | 105
Lerwick | 1978-01-04 09:30 | 0.3 | 3.6 | 327.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-01-04 10:30 | 0.1 | 3.2 | 317.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-01-04 11:30 | 0.5 | 3.2 | 295 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-04 12:30 | 1.1 | 3.4 | 267.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-04 13:30 | 1.3 | 3.4 | 245 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-04 14:30 | 0.9 | 3 | 222.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-04 15:30 | 0.2 | 3 | 205 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-04 16:30 | 0 | 4.3 | 200 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-01-04 17:30 | 0.4 | 6.5 | 197.5 | 300 | 180 | 0 | 140 |  | 67.2 |  | 180
Lerwick | 1978-01-04 18:30 | 1.8 | 8.7 | 192.5 | 770 | 535 | 215 | 0 |  | 0 |  | 320
Lerwick | 1978-01-04 19:30 | 2.8 | 10.6 | 190 | 1270 | 1020 | 700 | 0 |  | 0 |  | 320
Lerwick | 1978-01-04 20:30 | 3.1 | 12.4 | 190 | 1450 | 1360 | 1040 | 0 |  | 0 |  | 320
Lerwick | 1978-01-04 21:30 | 3.2 | 14.1 | 190 | 1500 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-01-04 22:30 | 3.5 | 15.9 | 187.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-04 23:30 | 2.9 | 18.1 | 182.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-05 00:30 | 2.4 | 19 | 182.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-05 01:30 | 2.4 | 17.9 | 190 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-05 02:30 | 2 | 16.6 | 202.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-05 03:30 | 3 | 15.3 | 217.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-05 04:30 | 4.7 | 12.9 | 232.5 | 1470 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-01-05 05:30 | 6.1 | 10.7 | 247.5 | 1270 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-01-05 06:30 | 7.1 | 9.9 | 257.5 | 1025 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-05 07:30 | 7.5 | 9.9 | 260 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-01-05 08:30 | 7.2 | 10.2 | 260 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-05 09:30 | 6.9 | 10.9 | 260 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-01-05 10:30 | 6.8 | 11.8 | 257.5 | 1400 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-01-05 11:30 | 7 | 12.2 | 252.5 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-01-05 12:30 | 7 | 11.5 | 247.5 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-01-05 13:30 | 7.2 | 10.7 | 242.5 | 1270 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-01-05 14:30 | 7.2 | 10 | 237.5 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-01-05 15:30 | 7.2 | 9.4 | 232.5 | 900 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-01-05 16:30 | 7.4 | 10.3 | 230 | 1150 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-01-05 17:30 | 7.4 | 12.1 | 230 | 1450 | 1300 | 980 | 0 |  | 0 |  | 320
Lerwick | 1978-01-05 18:30 | 7.6 | 13 | 230 | 1480 | 1465 | 1145 | 0 |  | 0 |  | 320
Lerwick | 1978-01-05 19:30 | 7.6 | 13.2 | 230 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-01-05 20:30 | 7.5 | 13.5 | 230 | 1490 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-01-05 21:30 | 7.5 | 13.9 | 230 | 1490 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-01-05 22:30 | 7.8 | 14.3 | 230 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-01-05 23:30 | 8 | 14.4 | 232.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-06 00:30 | 8 | 14.4 | 237.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-06 01:30 | 8.2 | 14.3 | 240 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-06 02:30 | 8.2 | 13.9 | 240 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-01-06 03:30 | 8.2 | 13.6 | 240 | 1490 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-01-06 04:30 | 8.3 | 13.9 | 240 | 1490 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-01-06 05:30 | 8.5 | 14.5 | 240 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-01-06 06:30 | 8.5 | 14.9 | 237.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-06 07:30 | 8.5 | 14.8 | 232.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-06 08:30 | 8.5 | 15 | 230 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-06 09:30 | 8.5 | 15.5 | 230 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-06 10:30 | 8.5 | 15.9 | 230 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-06 11:30 | 8.4 | 17.1 | 227.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-06 12:30 | 8.3 | 18.6 | 222.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-06 13:30 | 8.3 | 19 | 220 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-06 14:30 | 8.2 | 17.5 | 220 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-06 15:30 | 8 | 15.3 | 220 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-06 16:30 | 7.9 | 14.3 | 220 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-06 17:30 | 7.7 | 13.9 | 220 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-01-06 18:30 | 7.8 | 13.3 | 217.5 | 1480 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-01-06 19:30 | 7.7 | 13 | 212.5 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-01-06 20:30 | 7.6 | 13 | 210 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-01-06 21:30 | 7.7 | 13.3 | 210 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-01-06 22:30 | 7.6 | 13.6 | 210 | 1490 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-01-06 23:30 | 7.5 | 13.3 | 210 | 1480 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-01-07 00:30 | 7.5 | 13 | 212.5 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-01-07 01:30 | 7.7 | 12.9 | 215 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-01-07 02:30 | 7.8 | 12.7 | 212.5 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-01-07 03:30 | 7.7 | 12.7 | 210 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-01-07 04:30 | 7.7 | 13 | 212.5 | 1480 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-01-07 05:30 | 7.5 | 12.8 | 220 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-01-07 06:30 | 7.4 | 12.2 | 227.5 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-01-07 07:30 | 7.5 | 11.5 | 232.5 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-01-07 08:30 | 7.3 | 10.2 | 235 | 1150 | 1275 | 955 | 0 |  | 0 |  | 320
Lerwick | 1978-01-07 09:30 | 6.6 | 9.4 | 232.5 | 900 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-01-07 10:30 | 6.1 | 10.1 | 227.5 | 1150 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-01-07 11:30 | 6.3 | 11.9 | 225 | 1400 | 1275 | 955 | 0 |  | 0 |  | 320
Lerwick | 1978-01-07 12:30 | 6.8 | 13.2 | 225 | 1480 | 1440 | 1120 | 0 |  | 0 |  | 320
Lerwick | 1978-01-07 13:30 | 7 | 14.1 | 225 | 1500 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-01-07 14:30 | 6.9 | 15.2 | 230 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-07 15:30 | 6.1 | 15.8 | 237.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-07 16:30 | 5.2 | 16 | 240 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-07 17:30 | 5.3 | 15.7 | 240 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-07 18:30 | 5.8 | 15 | 240 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-07 19:30 | 5.9 | 14 | 240 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-07 20:30 | 5.8 | 12.9 | 237.5 | 1470 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-01-07 21:30 | 5.9 | 12.7 | 232.5 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-01-07 22:30 | 6.2 | 13.1 | 227.5 | 1480 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-01-07 23:30 | 6.3 | 13.5 | 220 | 1490 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-01-08 00:30 | 6.3 | 13.9 | 215 | 1490 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-01-08 01:30 | 5.9 | 14.7 | 215 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-01-08 02:30 | 5.9 | 15.2 | 212.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-08 03:30 | 6.4 | 15 | 212.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-08 04:30 | 6.5 | 15 | 217.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-08 05:30 | 6.4 | 15.2 | 220 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-08 06:30 | 6.5 | 15 | 220 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-08 07:30 | 6.8 | 14.5 | 220 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-08 08:30 | 6.8 | 13.8 | 220 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-01-08 09:30 | 6.7 | 13.1 | 217.5 | 1480 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-01-08 10:30 | 6.5 | 12.3 | 212.5 | 1450 | 1465 | 1145 | 0 |  | 0 |  | 320
Lerwick | 1978-01-08 11:30 | 6.4 | 11.5 | 207.5 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-01-08 12:30 | 6.5 | 11 | 200 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-01-08 13:30 | 6.3 | 10.8 | 195 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-01-08 14:30 | 6.1 | 11.1 | 197.5 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-01-08 15:30 | 6 | 11.9 | 200 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-01-08 16:30 | 6 | 12.6 | 200 | 1470 | 1435 | 1115 | 0 |  | 0 |  | 320
Lerwick | 1978-01-08 17:30 | 6.1 | 13 | 200 | 1480 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-01-08 18:30 | 6.4 | 13.3 | 200 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-01-08 19:30 | 6.6 | 13.9 | 200 | 1490 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-01-08 20:30 | 6.5 | 14.7 | 202.5 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-01-08 21:30 | 6.5 | 15.7 | 210 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-08 22:30 | 6.6 | 15.9 | 217.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-08 23:30 | 6.7 | 14.8 | 220 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-09 00:30 | 6.4 | 12.9 | 220 | 1470 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-01-09 01:30 | 5.7 | 11.5 | 222.5 | 1400 | 1435 | 1115 | 0 |  | 0 |  | 320
Lerwick | 1978-01-09 02:30 | 5.3 | 10.7 | 227.5 | 1270 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-01-09 03:30 | 5.1 | 10.4 | 230 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-01-09 04:30 | 4.8 | 10.3 | 230 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-01-09 05:30 | 4.6 | 10.1 | 227.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-01-09 06:30 | 3.9 | 10.1 | 222.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-01-09 07:30 | 3.7 | 10.8 | 217.5 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-01-09 08:30 | 3.8 | 11.1 | 215 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-01-09 09:30 | 3 | 10.5 | 220 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-01-09 10:30 | 2.7 | 10 | 230 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-01-09 11:30 | 3.3 | 10.1 | 240 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-01-09 12:30 | 3.8 | 10.4 | 247.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-01-09 13:30 | 3.9 | 10.7 | 250 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-01-09 14:30 | 3.9 | 11 | 252.5 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-01-09 15:30 | 3.7 | 10.7 | 257.5 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-01-09 16:30 | 3 | 10 | 262.5 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-01-09 17:30 | 2.5 | 8.7 | 262.5 | 770 | 960 | 640 | 0 |  | 0 |  | 320
Lerwick | 1978-01-09 18:30 | 1.9 | 7.7 | 250 | 500 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-01-09 19:30 | 1.8 | 7.3 | 235 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-01-09 20:30 | 2.2 | 7.6 | 232.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-01-09 21:30 | 2.1 | 8.3 | 230 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-09 22:30 | 1.8 | 8.5 | 220 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-09 23:30 | 1.9 | 9 | 217.5 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-01-10 00:30 | 2.4 | 8.6 | 222.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-01-10 01:30 | 1.2 | 6.9 | 225 | 300 | 535 | 215 | 0 |  | 0 |  | 320
Lerwick | 1978-01-10 02:30 | 0 | 6.9 | 227.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-01-10 03:30 | 0.6 | 8.3 | 237.5 | 635 | 467.5 | 147.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-10 04:30 | 0.7 | 8.1 | 247.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-01-10 05:30 | 0.6 | 7.2 | 250 | 400 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-10 06:30 | 1.1 | 7.6 | 255 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-01-10 07:30 | 1.4 | 8 | 262.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-10 08:30 | 1.7 | 8.8 | 260 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-10 09:30 | 1.7 | 9.9 | 247.5 | 1025 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-10 10:30 | 1.8 | 10.6 | 230 | 1270 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-10 11:30 | 1.6 | 10.4 | 215 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-01-10 12:30 | 0.9 | 8.7 | 212.5 | 770 | 960 | 640 | 0 |  | 0 |  | 320
Lerwick | 1978-01-10 13:30 | 0.7 | 7.2 | 220 | 400 | 585 | 265 | 0 |  | 0 |  | 320
Lerwick | 1978-01-10 14:30 | 0.9 | 6 | 230 | 220 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-01-10 15:30 | 0.9 | 4.9 | 262.5 | 80 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-01-10 16:30 | 0.9 | 4.6 | 305 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-01-10 17:30 | 0.5 | 4.4 | 297.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-01-10 18:30 | -0.1 | 3.6 | 262.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-01-10 19:30 | -0.6 | 3.9 | 252.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-01-10 20:30 | -1 | 4.4 | 255 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-01-10 21:30 | -0.8 | 3.8 | 257.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-01-10 22:30 | -0.3 | 3.3 | 267.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-01-10 23:30 | 0.1 | 4.1 | 270 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-01-11 00:30 | 0.6 | 5.8 | 255 | 150 | 105 | 0 | 215 |  | 103.2 |  | 105
Lerwick | 1978-01-11 01:30 | 0.8 | 7.4 | 245 | 400 | 275 | 0 | 45 |  | 21.6 |  | 275
Lerwick | 1978-01-11 02:30 | 0.5 | 8.5 | 260 | 770 | 585 | 265 | 0 |  | 0 |  | 320
Lerwick | 1978-01-11 03:30 | 0.3 | 10.5 | 302.5 | 1270 | 1020 | 700 | 0 |  | 0 |  | 320
Lerwick | 1978-01-11 04:30 | 0.6 | 14.3 | 167.5 | 1500 | 1385 | 1065 | 0 |  | 0 |  | 320
Lerwick | 1978-01-11 05:30 | 1.3 | 17.7 | 10 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-11 06:30 | 1.7 | 19.2 | 17.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-11 07:30 | 1.2 | 19.4 | 20 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-11 08:30 | 0.9 | 19.2 | 20 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-11 09:30 | 1.6 | 18.8 | 17.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-11 10:30 | 1.6 | 18 | 12.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-11 11:30 | 1.2 | 16.8 | 10 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-11 12:30 | 0.9 | 15.7 | 7.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-11 13:30 | 0.5 | 14.8 | 2.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-11 14:30 | 0.2 | 13.6 | 177.5 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-01-11 15:30 | -0.1 | 12.4 | 350 | 1450 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-01-11 16:30 | -0.6 | 12 | 342.5 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-01-11 17:30 | -1.6 | 11.9 | 340 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-01-11 18:30 | -2.3 | 11.8 | 340 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-01-11 19:30 | -2.8 | 11.8 | 340 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-01-11 20:30 | -2.6 | 11.5 | 340 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-01-11 21:30 | -2.8 | 11.3 | 340 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-01-11 22:30 | -2.8 | 11.6 | 340 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-01-11 23:30 | -2.2 | 11.9 | 340 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-01-12 00:30 | -2 | 11.8 | 340 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-01-12 01:30 | -2 | 11.9 | 340 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-01-12 02:30 | -2.2 | 11.5 | 340 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-01-12 03:30 | -2 | 10.2 | 340 | 1150 | 1275 | 955 | 0 |  | 0 |  | 320
Lerwick | 1978-01-12 04:30 | -1.7 | 8.8 | 340 | 770 | 960 | 640 | 0 |  | 0 |  | 320
Lerwick | 1978-01-12 05:30 | -2.3 | 7.6 | 340 | 500 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-01-12 06:30 | -2.7 | 6.8 | 340 | 300 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-01-12 07:30 | -2.3 | 6.1 | 340 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-01-12 08:30 | -2 | 5.1 | 337.5 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-01-12 09:30 | -1.8 | 3.8 | 330 | 25 | 67.5 | 0 | 252.5 |  | 121.2 |  | 67.5
Lerwick | 1978-01-12 10:30 | -1.5 | 3 | 317.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-01-12 11:30 | -1.2 | 2.4 | 302.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-12 12:30 | -0.9 | 1.9 | 287.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-12 13:30 | -0.9 | 1.9 | 265 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-12 14:30 | -1.2 | 3 | 240 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-12 15:30 | -0.9 | 5 | 227.5 | 110 | 55 | 0 | 265 |  | 127.2 |  | 55
Lerwick | 1978-01-12 16:30 | -0.2 | 7.3 | 222.5 | 400 | 255 | 0 | 65 |  | 31.2 |  | 255
Lerwick | 1978-01-12 17:30 | 0 | 9.6 | 217.5 | 1025 | 712.5 | 392.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-12 18:30 | 0.4 | 11.6 | 212.5 | 1400 | 1212.5 | 892.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-12 19:30 | 1.2 | 13.4 | 210 | 1480 | 1440 | 1120 | 0 |  | 0 |  | 320
Lerwick | 1978-01-12 20:30 | 1.5 | 15 | 210 | 1500 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-01-12 21:30 | 1.4 | 16.1 | 212.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-12 22:30 | 1.4 | 17 | 217.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-12 23:30 | 1.9 | 17.1 | 220 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-13 00:30 | 2.7 | 15.7 | 225 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-13 01:30 | 4.2 | 14.7 | 237.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-13 02:30 | 6.2 | 14.8 | 252.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-13 03:30 | 7.5 | 14.6 | 265 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-13 04:30 | 7.9 | 14.3 | 270 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-13 05:30 | 8 | 13.8 | 272.5 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-01-13 06:30 | 8 | 13.2 | 277.5 | 1480 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-01-13 07:30 | 8 | 13.2 | 280 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-01-13 08:30 | 8.1 | 13.1 | 280 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-01-13 09:30 | 8.1 | 12.2 | 280 | 1450 | 1465 | 1145 | 0 |  | 0 |  | 320
Lerwick | 1978-01-13 10:30 | 8.1 | 10.9 | 280 | 1270 | 1360 | 1040 | 0 |  | 0 |  | 320
Lerwick | 1978-01-13 11:30 | 8.1 | 10 | 280 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-01-13 12:30 | 8.1 | 9.6 | 280 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-13 13:30 | 8.1 | 9.1 | 280 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-13 14:30 | 8 | 8.4 | 280 | 635 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-13 15:30 | 8 | 8.3 | 280 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-01-13 16:30 | 8 | 8.9 | 280 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-13 17:30 | 7.9 | 9.3 | 280 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-01-13 18:30 | 7.7 | 9.1 | 280 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-01-13 19:30 | 7.8 | 9.1 | 277.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-01-13 20:30 | 8 | 9.5 | 272.5 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-13 21:30 | 7.8 | 10 | 270 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-13 22:30 | 7.6 | 10 | 267.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-01-13 23:30 | 7.5 | 10.1 | 265 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-01-14 00:30 | 7.6 | 11.2 | 267.5 | 1340 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-01-14 01:30 | 7.4 | 11.7 | 270 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-01-14 02:30 | 7.1 | 11.1 | 270 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-01-14 03:30 | 7 | 10.8 | 270 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-01-14 04:30 | 6.9 | 10.6 | 267.5 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-01-14 05:30 | 6.9 | 10.7 | 262.5 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-01-14 06:30 | 6.9 | 11 | 260 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-01-14 07:30 | 6.8 | 11 | 260 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-01-14 08:30 | 6.7 | 11.4 | 260 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-01-14 09:30 | 6.7 | 11.8 | 257.5 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-01-14 10:30 | 6.7 | 11.9 | 252.5 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-01-14 11:30 | 6.8 | 12 | 250 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-01-14 12:30 | 7 | 11.9 | 250 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-01-14 13:30 | 7.1 | 11.8 | 250 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-01-14 14:30 | 7 | 11.9 | 250 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-01-14 15:30 | 7 | 12 | 250 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-01-14 16:30 | 7.1 | 12 | 247.5 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-01-14 17:30 | 7.1 | 12.4 | 242.5 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-01-14 18:30 | 7 | 13.4 | 240 | 1480 | 1465 | 1145 | 0 |  | 0 |  | 320
Lerwick | 1978-01-14 19:30 | 6.9 | 14.4 | 240 | 1500 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-01-14 20:30 | 6.9 | 14.9 | 240 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-14 21:30 | 7 | 14.5 | 240 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-14 22:30 | 7 | 14 | 237.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-14 23:30 | 7 | 13.9 | 232.5 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-01-15 00:30 | 7 | 13.7 | 230 | 1490 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-01-15 01:30 | 7.1 | 13.5 | 230 | 1490 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-01-15 02:30 | 7.1 | 13.4 | 230 | 1480 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-01-15 03:30 | 7.1 | 13.2 | 227.5 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-01-15 04:30 | 7.1 | 12.8 | 222.5 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-01-15 05:30 | 6.9 | 12.5 | 217.5 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-01-15 06:30 | 6.4 | 12.5 | 215 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-01-15 07:30 | 6.2 | 12.2 | 217.5 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-01-15 08:30 | 6.3 | 11.7 | 220 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-01-15 09:30 | 6.6 | 11.2 | 217.5 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-01-15 10:30 | 6.8 | 10.4 | 207.5 | 1150 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-01-15 11:30 | 7.1 | 9.4 | 197.5 | 900 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-01-15 12:30 | 7 | 9.6 | 200 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-15 13:30 | 6.7 | 10.6 | 207.5 | 1270 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-15 14:30 | 6.9 | 10.5 | 207.5 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-01-15 15:30 | 6.7 | 9 | 200 | 900 | 1085 | 765 | 0 |  | 0 |  | 320
Lerwick | 1978-01-15 16:30 | 6.5 | 8.3 | 197.5 | 635 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-15 17:30 | 6.4 | 8.9 | 202.5 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-15 18:30 | 6.6 | 8.7 | 202.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-01-15 19:30 | 6.8 | 8.5 | 202.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-01-15 20:30 | 6.5 | 9.4 | 210 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-01-15 21:30 | 6.1 | 9.4 | 217.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-01-15 22:30 | 6 | 8.5 | 222.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-01-15 23:30 | 5.5 | 7.2 | 230 | 400 | 585 | 265 | 0 |  | 0 |  | 320
Lerwick | 1978-01-16 00:30 | 5.1 | 5.9 | 247.5 | 150 | 275 | 0 | 45 |  | 21.6 |  | 275
Lerwick | 1978-01-16 01:30 | 5.1 | 4.9 | 265 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-01-16 02:30 | 4.5 | 4 | 262.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-01-16 03:30 | 4 | 3.7 | 265 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-01-16 04:30 | 4.2 | 3.6 | 290 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-01-16 05:30 | 4.2 | 3.3 | 310 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-01-16 06:30 | 4 | 3.6 | 317.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-01-16 07:30 | 3.5 | 3.7 | 320 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-01-16 08:30 | 3 | 3.3 | 317.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-01-16 09:30 | 2.8 | 2.8 | 312.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-16 10:30 | 2.8 | 2.3 | 315 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-16 11:30 | 3 | 1.7 | 330 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-16 12:30 | 2.9 | 1.4 | 342.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-16 13:30 | 2.9 | 1.8 | 342.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-16 14:30 | 2.8 | 2.6 | 342.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-16 15:30 | 2.5 | 3.3 | 172.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-16 16:30 | 2.3 | 4 | 7.5 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-01-16 17:30 | 2.4 | 5.1 | 20 | 110 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-01-16 18:30 | 2.6 | 5.8 | 25 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-01-16 19:30 | 2.5 | 6.1 | 25 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-01-16 20:30 | 2 | 6.7 | 30 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-01-16 21:30 | 2 | 7.3 | 37.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-01-16 22:30 | 2.4 | 7.7 | 40 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-01-16 23:30 | 2.7 | 7.6 | 40 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-17 00:30 | 2.9 | 7.6 | 37.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-17 01:30 | 2.7 | 7.8 | 32.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-17 02:30 | 2.9 | 8.4 | 30 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-17 03:30 | 3.2 | 8.9 | 27.5 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-17 04:30 | 3.1 | 8.9 | 22.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-01-17 05:30 | 3.1 | 8.9 | 17.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-01-17 06:30 | 3.3 | 8.7 | 7.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-01-17 07:30 | 3.3 | 7.6 | 175 | 500 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-01-17 08:30 | 3 | 6.3 | 350 | 220 | 360 | 40 | 0 |  | 0 |  | 320
Lerwick | 1978-01-17 09:30 | 3.1 | 5.9 | 350 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-01-17 10:30 | 3.3 | 5.2 | 350 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-01-17 11:30 | 3 | 3.8 | 180 | 25 | 67.5 | 0 | 252.5 |  | 121.2 |  | 67.5
Lerwick | 1978-01-17 12:30 | 3.1 | 3.2 | 20 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-01-17 13:30 | 3.9 | 4.1 | 30 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-01-17 14:30 | 4.5 | 5.5 | 27.5 | 150 | 105 | 0 | 215 |  | 103.2 |  | 105
Lerwick | 1978-01-17 15:30 | 4.6 | 5.9 | 17.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-01-17 16:30 | 4 | 5.3 | 5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-01-17 17:30 | 3.6 | 5.2 | 0 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-01-17 18:30 | 3.4 | 4.9 | 0 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-01-17 19:30 | 3.3 | 4.7 | 5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-01-17 20:30 | 3.2 | 5.3 | 17.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-01-17 21:30 | 3.4 | 5.3 | 25 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-01-17 22:30 | 3.7 | 4.9 | 27.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-01-17 23:30 | 3.7 | 4.4 | 35 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-01-18 00:30 | 4 | 3.5 | 45 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-01-18 01:30 | 4 | 2.2 | 40 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-01-18 02:30 | 3.9 | 0.6 | 15 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-18 03:30 | 3.7 | 0 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-18 04:30 | 3.4 | 0 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-18 05:30 | 3.3 | 0 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-18 06:30 | 3.6 | 0 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-18 07:30 | 3.2 | 0 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-18 08:30 | 2.1 | 0 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-18 09:30 | 1.2 | 0.6 | 137.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-18 10:30 | 1.5 | 2.2 | 227.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-18 11:30 | 2.6 | 3.8 | 175 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-01-18 12:30 | 3.7 | 4.7 | 172.5 | 80 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-01-18 13:30 | 4.6 | 4.9 | 175 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-01-18 14:30 | 4.7 | 5.6 | 170 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-01-18 15:30 | 4 | 6.4 | 162.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-01-18 16:30 | 3.8 | 7.1 | 160 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-01-18 17:30 | 4.2 | 7.6 | 162.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-01-18 18:30 | 4.3 | 7.4 | 165 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-01-18 19:30 | 4.4 | 7.3 | 165 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-01-18 20:30 | 4.4 | 8.1 | 167.5 | 635 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-18 21:30 | 4.5 | 9 | 167.5 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-18 22:30 | 4.1 | 9.5 | 162.5 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-18 23:30 | 3.6 | 10 | 160 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-19 00:30 | 3.5 | 10.3 | 160 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-01-19 01:30 | 3.5 | 10 | 157.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-01-19 02:30 | 3.3 | 9.5 | 152.5 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-19 03:30 | 3.2 | 9.3 | 150 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-19 04:30 | 3.1 | 9.4 | 150 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-01-19 05:30 | 3.3 | 9.6 | 150 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-19 06:30 | 3.3 | 9.9 | 150 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-01-19 07:30 | 3.3 | 10.4 | 150 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-19 08:30 | 3.5 | 11 | 150 | 1340 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-01-19 09:30 | 3.3 | 11.3 | 150 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-01-19 10:30 | 3.3 | 10.8 | 147.5 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-01-19 11:30 | 3 | 10.3 | 145 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-01-19 12:30 | 3.1 | 10.6 | 145 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-01-19 13:30 | 3.6 | 11.2 | 145 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-01-19 14:30 | 3.5 | 11.9 | 147.5 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-01-19 15:30 | 3.3 | 12.4 | 150 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-01-19 16:30 | 3.3 | 12.2 | 147.5 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-01-19 17:30 | 3.5 | 11.4 | 145 | 1340 | 1395 | 1075 | 0 |  | 0 |  | 320
Lerwick | 1978-01-19 18:30 | 3.6 | 10.6 | 147.5 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-01-19 19:30 | 3.4 | 11 | 147.5 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-01-19 20:30 | 3.4 | 11.6 | 142.5 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-01-19 21:30 | 3.9 | 11.6 | 140 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-01-19 22:30 | 4.5 | 11.1 | 145 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-01-19 23:30 | 4.7 | 10.9 | 152.5 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-01-20 00:30 | 4.8 | 11.2 | 152.5 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-01-20 01:30 | 4.9 | 11.2 | 147.5 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-01-20 02:30 | 5.2 | 10.6 | 145 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-01-20 03:30 | 5.1 | 9.4 | 150 | 900 | 1085 | 765 | 0 |  | 0 |  | 320
Lerwick | 1978-01-20 04:30 | 4.4 | 9.1 | 152.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-01-20 05:30 | 4.4 | 10.9 | 145 | 1270 | 1085 | 765 | 0 |  | 0 |  | 320
Lerwick | 1978-01-20 06:30 | 5 | 11.7 | 140 | 1400 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-01-20 07:30 | 5 | 11.1 | 137.5 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-01-20 08:30 | 4.6 | 10.3 | 132.5 | 1150 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-01-20 09:30 | 4.5 | 9.4 | 135 | 900 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-01-20 10:30 | 4.4 | 9 | 145 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-01-20 11:30 | 4.2 | 9 | 147.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-01-20 12:30 | 4.6 | 8.7 | 142.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-01-20 13:30 | 4.8 | 8.3 | 137.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-20 14:30 | 4.6 | 8.1 | 132.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-01-20 15:30 | 4.4 | 8.3 | 130 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-01-20 16:30 | 4.3 | 8.5 | 130 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-20 17:30 | 4.4 | 8.5 | 130 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-01-20 18:30 | 4.5 | 8.3 | 130 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-20 19:30 | 4.2 | 7.4 | 130 | 400 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-20 20:30 | 4.2 | 6.4 | 132.5 | 220 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-01-20 21:30 | 4.2 | 6.6 | 137.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-01-20 22:30 | 4.2 | 7.3 | 142.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-01-20 23:30 | 4.7 | 8.2 | 147.5 | 635 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-21 00:30 | 4.9 | 9.1 | 150 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-21 01:30 | 5 | 9.6 | 150 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-21 02:30 | 5 | 9.9 | 150 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-01-21 03:30 | 5 | 10.2 | 150 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-21 04:30 | 4.7 | 10.9 | 147.5 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-01-21 05:30 | 4.5 | 11.4 | 142.5 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-01-21 06:30 | 4.7 | 11.2 | 140 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-01-21 07:30 | 4.9 | 10.9 | 142.5 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-01-21 08:30 | 5.2 | 10.9 | 147.5 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-01-21 09:30 | 5.2 | 11.2 | 145 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-01-21 10:30 | 5.3 | 11.9 | 137.5 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-01-21 11:30 | 5.2 | 12.4 | 137.5 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-01-21 12:30 | 5.2 | 12.4 | 140 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-01-21 13:30 | 5.4 | 12.2 | 140 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-01-21 14:30 | 5.3 | 11.7 | 140 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-01-21 15:30 | 5.3 | 11.5 | 140 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-01-21 16:30 | 5.2 | 11.6 | 140 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-01-21 17:30 | 5.1 | 11.9 | 140 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-01-21 18:30 | 5.3 | 12 | 140 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-01-21 19:30 | 5.3 | 11.9 | 142.5 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-01-21 20:30 | 5.2 | 11.6 | 147.5 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-01-21 21:30 | 4.9 | 11.6 | 147.5 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-01-21 22:30 | 4.9 | 11.9 | 142.5 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-01-21 23:30 | 5.1 | 12 | 140 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-01-22 00:30 | 5.4 | 12.4 | 140 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-01-22 01:30 | 5.2 | 13.1 | 140 | 1480 | 1465 | 1145 | 0 |  | 0 |  | 320
Lerwick | 1978-01-22 02:30 | 5.1 | 13.4 | 140 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-01-22 03:30 | 5 | 13.4 | 140 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-01-22 04:30 | 4.6 | 13.6 | 140 | 1490 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-01-22 05:30 | 4.3 | 14.4 | 140 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-01-22 06:30 | 4.3 | 15 | 140 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-22 07:30 | 4.1 | 14.9 | 140 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-22 08:30 | 4.2 | 14.4 | 140 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-22 09:30 | 4.6 | 14 | 140 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-22 10:30 | 4.9 | 13.7 | 140 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-01-22 11:30 | 5.1 | 13.3 | 140 | 1480 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-01-22 12:30 | 5.3 | 13 | 142.5 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-01-22 13:30 | 5.6 | 12.7 | 147.5 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-01-22 14:30 | 5.7 | 12.5 | 150 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-01-22 15:30 | 5.7 | 12.7 | 150 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-01-22 16:30 | 5.6 | 12.9 | 152.5 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-01-22 17:30 | 5.5 | 13 | 157.5 | 1480 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-01-22 18:30 | 5.6 | 12.8 | 160 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-01-22 19:30 | 5.4 | 11.6 | 157.5 | 1400 | 1435 | 1115 | 0 |  | 0 |  | 320
Lerwick | 1978-01-22 20:30 | 5.3 | 10 | 157.5 | 1150 | 1275 | 955 | 0 |  | 0 |  | 320
Lerwick | 1978-01-22 21:30 | 5.5 | 8.7 | 165 | 770 | 960 | 640 | 0 |  | 0 |  | 320
Lerwick | 1978-01-22 22:30 | 5.4 | 7.2 | 172.5 | 400 | 585 | 265 | 0 |  | 0 |  | 320
Lerwick | 1978-01-22 23:30 | 5.4 | 6.9 | 202.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-01-23 00:30 | 5.1 | 9.2 | 252.5 | 900 | 600 | 280 | 0 |  | 0 |  | 320
Lerwick | 1978-01-23 01:30 | 3.8 | 11.1 | 270 | 1340 | 1120 | 800 | 0 |  | 0 |  | 320
Lerwick | 1978-01-23 02:30 | 2.7 | 9.9 | 262.5 | 1025 | 1182.5 | 862.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-23 03:30 | 2.7 | 7.6 | 255 | 500 | 762.5 | 442.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-23 04:30 | 2.8 | 5.6 | 240 | 150 | 325 | 5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-23 05:30 | 2.4 | 3.8 | 227.5 | 25 | 87.5 | 0 | 232.5 |  | 111.6 |  | 87.5
Lerwick | 1978-01-23 06:30 | 1.7 | 2.6 | 217.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-01-23 07:30 | 1.7 | 2.2 | 202.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-23 08:30 | 1.9 | 2.7 | 197.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-23 09:30 | 1.7 | 3.3 | 200 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-23 10:30 | 1.7 | 3.9 | 195 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-01-23 11:30 | 2.3 | 5.3 | 182.5 | 110 | 67.5 | 0 | 252.5 |  | 121.2 |  | 67.5
Lerwick | 1978-01-23 12:30 | 3.2 | 6.3 | 175 | 220 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-01-23 13:30 | 3.5 | 6.4 | 175 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-01-23 14:30 | 3.4 | 6.4 | 172.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-01-23 15:30 | 3.7 | 5.9 | 172.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-01-23 16:30 | 3.4 | 4.9 | 167.5 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-01-23 17:30 | 2.5 | 4.9 | 145 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-01-23 18:30 | 3 | 6 | 122.5 | 220 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-01-23 19:30 | 3.8 | 6.8 | 115 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-01-23 20:30 | 3.9 | 7.5 | 122.5 | 500 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-01-23 21:30 | 4.2 | 9 | 135 | 900 | 700 | 380 | 0 |  | 0 |  | 320
Lerwick | 1978-01-23 22:30 | 4.3 | 10.4 | 137.5 | 1150 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-01-23 23:30 | 4.4 | 11 | 132.5 | 1340 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-01-24 00:30 | 4.3 | 11.4 | 127.5 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-01-24 01:30 | 4.3 | 11.5 | 125 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-01-24 02:30 | 4.4 | 11.6 | 127.5 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-01-24 03:30 | 4 | 11.5 | 130 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-01-24 04:30 | 3.8 | 11 | 127.5 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-01-24 05:30 | 3.6 | 11 | 122.5 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-01-24 06:30 | 3.5 | 11.4 | 120 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-01-24 07:30 | 3.6 | 11.1 | 120 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-01-24 08:30 | 3.3 | 10.6 | 120 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-01-24 09:30 | 3.2 | 10.9 | 117.5 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-01-24 10:30 | 3.3 | 11.5 | 110 | 1400 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-01-24 11:30 | 3.1 | 11.6 | 102.5 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-01-24 12:30 | 2.7 | 11.1 | 97.5 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-01-24 13:30 | 2.4 | 10.3 | 90 | 1150 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-01-24 14:30 | 2.5 | 9.3 | 82.5 | 900 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-01-24 15:30 | 2.5 | 8.4 | 82.5 | 635 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-24 16:30 | 2.1 | 7.7 | 82.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-24 17:30 | 2 | 6.8 | 75 | 300 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-01-24 18:30 | 1.8 | 6.2 | 67.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-01-24 19:30 | 2.1 | 6 | 62.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-01-24 20:30 | 2.3 | 4.7 | 57.5 | 80 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-01-24 21:30 | 2.1 | 3.1 | 35 | 0 | 40 | 0 | 280 |  | 134.4 |  | 40
Lerwick | 1978-01-24 22:30 | 2.5 | 3.1 | 177.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-24 23:30 | 2.6 | 4 | 335 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-01-25 00:30 | 2.3 | 4.7 | 322.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-01-25 01:30 | 2 | 5.3 | 312.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-01-25 02:30 | 2.2 | 6.2 | 312.5 | 220 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-01-25 03:30 | 2.5 | 7.1 | 320 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-01-25 04:30 | 2.3 | 7.3 | 327.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-01-25 05:30 | 2.4 | 6.9 | 330 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-01-25 06:30 | 2.5 | 6.5 | 330 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-01-25 07:30 | 2.3 | 6.1 | 327.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-01-25 08:30 | 2.1 | 5.4 | 327.5 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-01-25 09:30 | 2.3 | 4.4 | 332.5 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-01-25 10:30 | 2.4 | 4.2 | 327.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-01-25 11:30 | 2.7 | 4.4 | 317.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-01-25 12:30 | 3.6 | 4.2 | 320 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-01-25 13:30 | 3.5 | 3.6 | 320 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-01-25 14:30 | 3.2 | 3.6 | 312.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-01-25 15:30 | 3.4 | 4.2 | 322.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-01-25 16:30 | 3.1 | 4.4 | 335 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-01-25 17:30 | 2.1 | 4.4 | 327.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-01-25 18:30 | 1.7 | 4.2 | 312.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-01-25 19:30 | 2 | 4 | 297.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-01-25 20:30 | 1.8 | 4.2 | 287.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-01-25 21:30 | 1.7 | 4.9 | 285 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-01-25 22:30 | 1.8 | 5.5 | 285 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-01-25 23:30 | 2 | 5.5 | 280 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-01-26 00:30 | 1.7 | 5.4 | 272.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-01-26 01:30 | 1.5 | 5.5 | 270 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-01-26 02:30 | 1.7 | 5.8 | 270 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-01-26 03:30 | 1.9 | 5.9 | 272.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-01-26 04:30 | 2 | 5.9 | 277.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-01-26 05:30 | 2.2 | 6.1 | 277.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-01-26 06:30 | 2.2 | 6.5 | 275 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-01-26 07:30 | 2.3 | 6.7 | 275 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-01-26 08:30 | 2.3 | 7.1 | 272.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-01-26 09:30 | 1.8 | 7.7 | 270 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-01-26 10:30 | 1.7 | 8 | 270 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-26 11:30 | 1.7 | 8 | 267.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-01-26 12:30 | 1.6 | 7.5 | 270 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-26 13:30 | 1.8 | 6.6 | 290 | 300 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-01-26 14:30 | 2 | 6.4 | 310 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-01-26 15:30 | 2 | 7.2 | 312.5 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-01-26 16:30 | 2 | 8.1 | 317.5 | 635 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-26 17:30 | 1.7 | 8 | 332.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-01-26 18:30 | 1.2 | 6.9 | 337.5 | 300 | 467.5 | 147.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-26 19:30 | 1.1 | 6.7 | 330 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-01-26 20:30 | 1.2 | 7 | 322.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-01-26 21:30 | 1.1 | 6.7 | 322.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-01-26 22:30 | 1 | 6.4 | 327.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-01-26 23:30 | 0.7 | 6.4 | 327.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-01-27 00:30 | 0.1 | 6.4 | 322.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-01-27 01:30 | 0.2 | 6.3 | 317.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-01-27 02:30 | 0.2 | 5.9 | 317.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-01-27 03:30 | 0 | 5.1 | 317.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-01-27 04:30 | 0 | 4.2 | 312.5 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-01-27 05:30 | 0 | 3.9 | 320 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-01-27 06:30 | 0 | 4.2 | 337.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-01-27 07:30 | -0.1 | 4.4 | 172.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-01-27 08:30 | -0.1 | 4.4 | 5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-01-27 09:30 | 0.1 | 4.2 | 15 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-01-27 10:30 | 0.3 | 3.8 | 30 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-01-27 11:30 | 0.2 | 4.2 | 22.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-01-27 12:30 | 0.2 | 5.3 | 162.5 | 110 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-01-27 13:30 | 0.2 | 5.5 | 320 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-01-27 14:30 | 0.1 | 5.6 | 165 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-01-27 15:30 | 0.1 | 5.6 | 37.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-01-27 16:30 | 0.1 | 4.6 | 70 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-01-27 17:30 | 0 | 3.9 | 67.5 | 25 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-01-27 18:30 | 0 | 4.1 | 72.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-01-27 19:30 | 0 | 4.4 | 100 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-01-27 20:30 | 0 | 4.7 | 107.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-01-27 21:30 | 0 | 5.4 | 92.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-01-27 22:30 | 0 | 6.1 | 77.5 | 220 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-01-27 23:30 | 0 | 6.4 | 70 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-01-28 00:30 | 0 | 6.8 | 75 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-01-28 01:30 | 0 | 8 | 82.5 | 635 | 467.5 | 147.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-28 02:30 | 0.3 | 9.6 | 80 | 1025 | 830 | 510 | 0 |  | 0 |  | 320
Lerwick | 1978-01-28 03:30 | 0.9 | 11.7 | 72.5 | 1400 | 1212.5 | 892.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-28 04:30 | 1.2 | 13.5 | 67.5 | 1490 | 1445 | 1125 | 0 |  | 0 |  | 320
Lerwick | 1978-01-28 05:30 | 1.1 | 14.4 | 62.5 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-01-28 06:30 | 1 | 14.9 | 60 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-28 07:30 | 0.9 | 15.4 | 60 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-28 08:30 | 1.1 | 16.1 | 60 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-28 09:30 | 1.3 | 17.4 | 57.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-28 10:30 | 1.1 | 19 | 52.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-28 11:30 | 0.7 | 19.8 | 50 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-28 12:30 | 0.3 | 19.9 | 50 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-28 13:30 | 0 | 20.3 | 47.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-28 14:30 | -0.1 | 20.7 | 42.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-28 15:30 | 0 | 20.9 | 40 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-28 16:30 | 0 | 21.2 | 40 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-28 17:30 | 0 | 21.7 | 40 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-28 18:30 | 0 | 22.1 | 40 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-28 19:30 | 0 | 21.7 | 37.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-28 20:30 | 0 | 21.5 | 32.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-28 21:30 | 0 | 22.3 | 30 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-28 22:30 | 0 | 22.9 | 30 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-28 23:30 | 0 | 22.9 | 30 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-29 00:30 | 0 | 22.5 | 30 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-29 01:30 | 0 | 11.1 | 15 | 1340 | 1420 | 1100 | 0 |  | 0 |  | 320
Lerwick | 1978-01-29 02:30 | 0 | 0 | 0 | 0 | 670 | 350 | 0 |  | 0 |  | 320
Lerwick | 1978-01-29 03:30 | 0 | 0 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-29 04:30 | 0 | 10.9 | 12.5 | 1270 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-01-29 05:30 | 0 | 21.3 | 27.5 | 1500 | 1385 | 1065 | 0 |  | 0 |  | 320
Lerwick | 1978-01-29 06:30 | 0.1 | 20.4 | 27.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-29 07:30 | 0.2 | 19.8 | 22.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-29 08:30 | 0.3 | 19 | 20 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-29 09:30 | 0.3 | 18 | 20 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-29 10:30 | 0.4 | 17.1 | 20 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-29 11:30 | 0.7 | 16.4 | 20 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-29 12:30 | 1 | 16.2 | 17.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-29 13:30 | 0.9 | 16.3 | 12.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-29 14:30 | 0.4 | 16.3 | 7.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-29 15:30 | 0.2 | 16.2 | 2.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-29 16:30 | 0.4 | 15.9 | 2.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-29 17:30 | 0.2 | 15.5 | 5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-29 18:30 | 0.2 | 15.5 | 2.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-29 19:30 | 0.6 | 15.3 | 0 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-29 20:30 | 0.5 | 14.4 | 0 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-29 21:30 | 0.1 | 13.5 | 0 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-01-29 22:30 | 0 | 12.2 | 177.5 | 1450 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-01-29 23:30 | -0.2 | 10.6 | 355 | 1270 | 1360 | 1040 | 0 |  | 0 |  | 320
Lerwick | 1978-01-30 00:30 | -0.4 | 10.1 | 177.5 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-01-30 01:30 | -0.4 | 10.3 | 177.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-01-30 02:30 | -0.2 | 10.3 | 352.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-01-30 03:30 | -0.6 | 10.3 | 352.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-01-30 04:30 | -1.2 | 10.1 | 355 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-01-30 05:30 | -1 | 9.5 | 352.5 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-30 06:30 | -0.6 | 8.9 | 350 | 770 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-30 07:30 | -0.4 | 8.6 | 347.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-01-30 08:30 | -0.9 | 8 | 342.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-30 09:30 | -1.8 | 7.5 | 342.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-30 10:30 | -1.6 | 7.8 | 350 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-30 11:30 | -0.6 | 7.8 | 350 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-01-30 12:30 | -0.3 | 7.1 | 337.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-01-30 13:30 | -0.5 | 7.1 | 330 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-01-30 14:30 | -0.8 | 7.8 | 335 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-01-30 15:30 | -0.4 | 8.3 | 345 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-30 16:30 | -0.4 | 8.6 | 352.5 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-30 17:30 | -0.8 | 4.4 | 177.5 | 60 | 415 | 95 | 0 |  | 0 |  | 320
Lerwick | 1978-01-30 18:30 | -1 | 0 | 0 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-01-30 19:30 | -0.8 | 0 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-30 20:30 | -1.1 | 0 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-30 21:30 | -0.8 | 0 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-30 22:30 | -0.2 | 3.2 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-30 23:30 | -0.7 | 6.3 | 0 | 220 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-01-31 00:30 | -0.8 | 5.8 | 177.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-01-31 01:30 | -0.7 | 4.9 | 350 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-01-31 02:30 | -1.5 | 4 | 342.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-01-31 03:30 | -1.3 | 3.6 | 342.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-01-31 04:30 | -1.1 | 3.8 | 175 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-01-31 05:30 | -2.1 | 3.3 | 2.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-01-31 06:30 | -1.6 | 2.2 | 170 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-31 07:30 | -1.3 | 2.4 | 175 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-31 08:30 | -2.4 | 2.6 | 40 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-31 09:30 | -1.5 | 1.7 | 72.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-31 10:30 | 0 | 1.5 | 200 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-31 11:30 | 0 | 2.4 | 250 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-01-31 12:30 | 0.5 | 3.7 | 145 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-01-31 13:30 | 1.1 | 4.4 | 117.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-01-31 14:30 | 0.9 | 4.4 | 120 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-01-31 15:30 | 1.1 | 4.9 | 117.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-01-31 16:30 | 1.6 | 5.5 | 110 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-01-31 17:30 | 1 | 5.8 | 105 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-01-31 18:30 | 0.5 | 6.1 | 110 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-01-31 19:30 | 1.3 | 6.8 | 120 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-01-31 20:30 | 2.3 | 7.6 | 125 | 500 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-01-31 21:30 | 1.8 | 8.4 | 122.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-31 22:30 | 1.2 | 9 | 120 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-01-31 23:30 | 1.2 | 9.4 | 120 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-02-01 00:30 | 1.6 | 9.5 | 120 | 1025 | 962.5 | 642.5 | 0 |  | 0 | 37388.4 | 320 | 137147.5
Lerwick | 1978-02-01 01:30 | 2 | 9.6 | 122.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-02-01 02:30 | 2.1 | 10.3 | 127.5 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-01 03:30 | 2.6 | 11.1 | 132.5 | 1340 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-02-01 04:30 | 3.2 | 11.9 | 137.5 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-02-01 05:30 | 3.3 | 12.4 | 140 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-02-01 06:30 | 3.3 | 12.2 | 140 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-02-01 07:30 | 3 | 12.2 | 142.5 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-02-01 08:30 | 3.3 | 12.7 | 147.5 | 1470 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-02-01 09:30 | 3.8 | 13.5 | 150 | 1490 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-02-01 10:30 | 3.7 | 14.4 | 150 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-02-01 11:30 | 3.9 | 15.1 | 147.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-01 12:30 | 4 | 15.4 | 142.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-01 13:30 | 3.9 | 15.3 | 140 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-01 14:30 | 3.9 | 15.2 | 140 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-01 15:30 | 3.9 | 15 | 140 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-01 16:30 | 3.8 | 14.8 | 140 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-01 17:30 | 3.9 | 14.7 | 137.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-01 18:30 | 4 | 14.7 | 135 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-01 19:30 | 4 | 14.7 | 137.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-01 20:30 | 3.9 | 14.1 | 140 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-01 21:30 | 3.9 | 13.2 | 140 | 1480 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-02-01 22:30 | 3.7 | 12.7 | 140 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-02-01 23:30 | 3.6 | 12.1 | 142.5 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-02-02 00:30 | 3.4 | 11.5 | 147.5 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-02-02 01:30 | 3.4 | 11.1 | 150 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-02-02 02:30 | 3.6 | 10.7 | 147.5 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-02-02 03:30 | 3.3 | 10.2 | 142.5 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-02-02 04:30 | 2.9 | 10 | 142.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-02-02 05:30 | 2.9 | 10.1 | 147.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-02-02 06:30 | 3.3 | 10.3 | 150 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-02-02 07:30 | 3.5 | 10.4 | 150 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-02-02 08:30 | 3.4 | 10.6 | 150 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-02-02 09:30 | 3.3 | 10.6 | 150 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-02-02 10:30 | 3.2 | 10.4 | 150 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-02-02 11:30 | 3.2 | 10.3 | 150 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-02-02 12:30 | 3.4 | 10.3 | 150 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-02-02 13:30 | 3.1 | 10.3 | 150 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-02-02 14:30 | 2.5 | 10.3 | 147.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-02-02 15:30 | 2.5 | 10.1 | 145 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-02-02 16:30 | 2.9 | 9.7 | 150 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-02 17:30 | 3.2 | 9.6 | 157.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-02-02 18:30 | 3 | 10.1 | 160 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-02 19:30 | 3 | 10.9 | 162.5 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-02-02 20:30 | 3.6 | 11.8 | 167.5 | 1400 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-02-02 21:30 | 3.5 | 12.6 | 170 | 1470 | 1435 | 1115 | 0 |  | 0 |  | 320
Lerwick | 1978-02-02 22:30 | 2.9 | 13.1 | 170 | 1480 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-02-02 23:30 | 2.6 | 13.5 | 170 | 1490 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-02-03 00:30 | 2.4 | 13 | 170 | 1480 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-02-03 01:30 | 2.4 | 11.1 | 172.5 | 1340 | 1410 | 1090 | 0 |  | 0 |  | 320
Lerwick | 1978-02-03 02:30 | 2.7 | 8 | 185 | 635 | 987.5 | 667.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-03 03:30 | 2.8 | 5.8 | 207.5 | 150 | 392.5 | 72.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-03 04:30 | 3.2 | 5.4 | 225 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-02-03 05:30 | 3.2 | 4.9 | 230 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-02-03 06:30 | 2.7 | 4.2 | 227.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-02-03 07:30 | 2.5 | 4 | 220 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-02-03 08:30 | 2.4 | 3.9 | 210 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-02-03 09:30 | 2.2 | 3.9 | 202.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-02-03 10:30 | 2.3 | 4.4 | 197.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-02-03 11:30 | 3.2 | 5.4 | 190 | 110 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-02-03 12:30 | 4 | 6.7 | 182.5 | 300 | 205 | 0 | 115 |  | 55.2 |  | 205
Lerwick | 1978-02-03 13:30 | 4.3 | 8 | 180 | 635 | 467.5 | 147.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-03 14:30 | 4.5 | 8.9 | 177.5 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-03 15:30 | 4.4 | 9.5 | 172.5 | 1025 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-03 16:30 | 4.4 | 10.1 | 170 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-03 17:30 | 4.3 | 11 | 170 | 1340 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-02-03 18:30 | 4.4 | 11.9 | 170 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-02-03 19:30 | 4.6 | 12.9 | 170 | 1470 | 1435 | 1115 | 0 |  | 0 |  | 320
Lerwick | 1978-02-03 20:30 | 4.7 | 13.8 | 167.5 | 1490 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-02-03 21:30 | 4.7 | 14.3 | 162.5 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-02-03 22:30 | 4.7 | 14.5 | 160 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-03 23:30 | 4.7 | 14.9 | 160 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-04 00:30 | 4.6 | 15.6 | 160 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-04 01:30 | 4.4 | 16.2 | 162.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-04 02:30 | 4.2 | 16.3 | 165 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-04 03:30 | 3.9 | 16.3 | 165 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-04 04:30 | 3.9 | 16.7 | 167.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-04 05:30 | 4 | 16.8 | 167.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-04 06:30 | 3.7 | 16.8 | 162.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-04 07:30 | 3.6 | 17.2 | 160 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-04 08:30 | 3.7 | 17.4 | 162.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-04 09:30 | 3.7 | 17.3 | 167.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-04 10:30 | 3.8 | 17.3 | 170 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-04 11:30 | 3.8 | 17.1 | 170 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-04 12:30 | 3.7 | 17 | 170 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-04 13:30 | 3.5 | 17 | 170 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-04 14:30 | 3.4 | 16.8 | 167.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-04 15:30 | 3.5 | 16.7 | 162.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-04 16:30 | 3.5 | 16.7 | 160 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-04 17:30 | 3.6 | 16.7 | 160 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-04 18:30 | 3.7 | 16.7 | 160 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-04 19:30 | 3.7 | 16.6 | 160 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-04 20:30 | 3.6 | 16.3 | 160 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-04 21:30 | 3.5 | 15.9 | 160 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-04 22:30 | 3.5 | 15.4 | 160 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-04 23:30 | 3.5 | 15.3 | 160 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-05 00:30 | 3.4 | 15.5 | 160 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-05 01:30 | 3.5 | 15.4 | 160 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-05 02:30 | 3.8 | 14.8 | 160 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-05 03:30 | 4 | 14.1 | 160 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-05 04:30 | 4.1 | 13.9 | 157.5 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-02-05 05:30 | 4.1 | 13.7 | 152.5 | 1490 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-02-05 06:30 | 3.9 | 13.3 | 150 | 1480 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-02-05 07:30 | 3.9 | 13 | 150 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-02-05 08:30 | 3.9 | 12.7 | 150 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-02-05 09:30 | 3.9 | 12.4 | 150 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-02-05 10:30 | 4 | 12.1 | 150 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-02-05 11:30 | 4.1 | 11.6 | 150 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-02-05 12:30 | 4.1 | 11.7 | 150 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-02-05 13:30 | 3.9 | 12.2 | 147.5 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-02-05 14:30 | 3.9 | 12.7 | 142.5 | 1470 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-02-05 15:30 | 3.9 | 12.9 | 140 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-02-05 16:30 | 3.8 | 12.9 | 140 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-02-05 17:30 | 3.8 | 12.7 | 140 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-02-05 18:30 | 3.9 | 12.4 | 140 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-02-05 19:30 | 3.9 | 12.4 | 140 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-02-05 20:30 | 4 | 12.4 | 140 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-02-05 21:30 | 3.9 | 12.7 | 140 | 1470 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-02-05 22:30 | 3.7 | 12.9 | 140 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-02-05 23:30 | 3.6 | 12.7 | 137.5 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-02-06 00:30 | 3.7 | 12.2 | 132.5 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-02-06 01:30 | 3.7 | 11.9 | 132.5 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-02-06 02:30 | 3.5 | 11.8 | 137.5 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-02-06 03:30 | 3.4 | 11.8 | 140 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-02-06 04:30 | 3.2 | 11.8 | 140 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-02-06 05:30 | 3 | 11.6 | 140 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-02-06 06:30 | 3 | 11.1 | 140 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-02-06 07:30 | 2.7 | 10.5 | 140 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-02-06 08:30 | 2.6 | 10.5 | 140 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-02-06 09:30 | 3 | 11.1 | 140 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-02-06 10:30 | 2.9 | 11.6 | 140 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-02-06 11:30 | 2.6 | 11.6 | 140 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-02-06 12:30 | 2.6 | 11.4 | 140 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-02-06 13:30 | 2.5 | 11.1 | 140 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-02-06 14:30 | 2.5 | 10.6 | 140 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-02-06 15:30 | 2.8 | 10.1 | 140 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-02-06 16:30 | 3 | 10 | 137.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-02-06 17:30 | 2.8 | 9.9 | 132.5 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-06 18:30 | 2.7 | 9.6 | 130 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-02-06 19:30 | 2.7 | 9.4 | 127.5 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-06 20:30 | 2.5 | 9 | 125 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-02-06 21:30 | 2.4 | 8.4 | 130 | 635 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-06 22:30 | 2.9 | 8 | 137.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-02-06 23:30 | 2.7 | 8 | 142.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-02-07 00:30 | 2.2 | 8 | 150 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-02-07 01:30 | 2.6 | 8.1 | 155 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-02-07 02:30 | 3 | 8.1 | 152.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-02-07 03:30 | 3 | 8.3 | 150 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-02-07 04:30 | 2.8 | 8.5 | 152.5 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-07 05:30 | 2.6 | 8.3 | 157.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-07 06:30 | 2.7 | 8.1 | 160 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-02-07 07:30 | 2.7 | 8.1 | 157.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-02-07 08:30 | 2.8 | 7.9 | 152.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-07 09:30 | 3 | 7.4 | 147.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-02-07 10:30 | 3 | 7.2 | 142.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-02-07 11:30 | 3.1 | 6.9 | 140 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-02-07 12:30 | 3.4 | 6.2 | 142.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-02-07 13:30 | 3.7 | 5.3 | 147.5 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-02-07 14:30 | 3.6 | 4.7 | 150 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-02-07 15:30 | 3 | 4.7 | 150 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-02-07 16:30 | 2.5 | 4.9 | 147.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-02-07 17:30 | 2.1 | 4.9 | 142.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-02-07 18:30 | 1.9 | 4.9 | 140 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-02-07 19:30 | 1.9 | 4.9 | 140 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-02-07 20:30 | 2.1 | 4.9 | 142.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-02-07 21:30 | 2.4 | 5 | 145 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-02-07 22:30 | 2.6 | 4.9 | 142.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-02-07 23:30 | 2.6 | 4.7 | 140 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-02-08 00:30 | 2.4 | 4.5 | 145 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-02-08 01:30 | 2.4 | 4.4 | 155 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-02-08 02:30 | 2.6 | 4.2 | 160 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-02-08 03:30 | 2.6 | 4 | 160 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-02-08 04:30 | 2.4 | 4.2 | 157.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-02-08 05:30 | 2.3 | 4.6 | 157.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-02-08 06:30 | 2.5 | 5.1 | 165 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-02-08 07:30 | 2.3 | 5.5 | 170 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-02-08 08:30 | 2.4 | 5.3 | 175 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-02-08 09:30 | 2.6 | 4.7 | 190 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-02-08 10:30 | 2.3 | 4.7 | 202.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-02-08 11:30 | 2 | 5 | 202.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-02-08 12:30 | 1.9 | 4.4 | 197.5 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-02-08 13:30 | 2.1 | 3.9 | 190 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-02-08 14:30 | 2.4 | 3.9 | 180 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-02-08 15:30 | 2.6 | 3.9 | 180 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-02-08 16:30 | 2.5 | 3.7 | 205 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-02-08 17:30 | 2.3 | 3.6 | 232.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-02-08 18:30 | 2.1 | 3.6 | 235 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-02-08 19:30 | 2 | 3.6 | 232.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-02-08 20:30 | 1.9 | 3.6 | 240 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-02-08 21:30 | 1.9 | 3.6 | 247.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-02-08 22:30 | 2 | 3.4 | 250 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-02-08 23:30 | 2 | 3.6 | 252.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-02-09 00:30 | 2 | 4.1 | 257.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-02-09 01:30 | 2.2 | 4.4 | 260 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-02-09 02:30 | 2.4 | 4.7 | 262.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-02-09 03:30 | 2.3 | 4.9 | 267.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-02-09 04:30 | 2.3 | 4.9 | 267.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-02-09 05:30 | 2.6 | 5.1 | 262.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-02-09 06:30 | 2.8 | 5.2 | 262.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-02-09 07:30 | 2.7 | 4.7 | 270 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-02-09 08:30 | 2.6 | 4 | 277.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-02-09 09:30 | 2.6 | 3.1 | 312.5 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-02-09 10:30 | 2.8 | 2.6 | 205 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-09 11:30 | 3 | 3.3 | 77.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-09 12:30 | 2.8 | 4.4 | 97.5 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-02-09 13:30 | 2.7 | 4.9 | 110 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-02-09 14:30 | 2.4 | 5.1 | 115 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-02-09 15:30 | 2.1 | 5.8 | 110 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-02-09 16:30 | 2 | 6 | 100 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-02-09 17:30 | 1.8 | 5.8 | 90 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-02-09 18:30 | 1.6 | 5.8 | 82.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-02-09 19:30 | 1.5 | 5.9 | 80 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-02-09 20:30 | 1.3 | 5.8 | 80 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-02-09 21:30 | 1 | 5.9 | 77.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-02-09 22:30 | 1 | 6.4 | 70 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-02-09 23:30 | 1.2 | 6.5 | 60 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-02-10 00:30 | 1.1 | 6.4 | 52.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-02-10 01:30 | 1 | 6 | 52.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-02-10 02:30 | 1 | 5.3 | 70 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-02-10 03:30 | 1 | 5.7 | 97.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-02-10 04:30 | 1.4 | 6.7 | 112.5 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-02-10 05:30 | 1.8 | 7 | 120 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-02-10 06:30 | 1.7 | 7.1 | 125 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-02-10 07:30 | 1.6 | 7.2 | 120 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-02-10 08:30 | 1.6 | 7.2 | 115 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-02-10 09:30 | 1.4 | 6.9 | 117.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-02-10 10:30 | 1.3 | 6.5 | 120 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-02-10 11:30 | 1.3 | 6.4 | 120 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-02-10 12:30 | 1.2 | 6.1 | 120 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-02-10 13:30 | 1.2 | 5.8 | 120 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-02-10 14:30 | 1.3 | 5.5 | 117.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-02-10 15:30 | 0.8 | 5.2 | 115 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-02-10 16:30 | 0.1 | 5 | 115 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-02-10 17:30 | 0 | 5 | 115 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-02-10 18:30 | 0 | 5 | 115 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-02-10 19:30 | -0.1 | 4.7 | 115 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-02-10 20:30 | -0.2 | 4.2 | 115 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-02-10 21:30 | -0.4 | 4.2 | 117.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-02-10 22:30 | -0.3 | 4.4 | 125 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-02-10 23:30 | -0.1 | 4.2 | 130 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-02-11 00:30 | -0.2 | 3.6 | 130 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-02-11 01:30 | -0.2 | 3 | 127.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-02-11 02:30 | -0.2 | 2.7 | 125 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-11 03:30 | -0.2 | 2.6 | 125 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-11 04:30 | -0.4 | 2 | 112.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-11 05:30 | -0.3 | 1.4 | 82.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-11 06:30 | -0.3 | 1.4 | 37.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-11 07:30 | -0.7 | 1.4 | 180 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-11 08:30 | -1.3 | 1.3 | 197.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-11 09:30 | -1.5 | 1.5 | 72.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-11 10:30 | -0.4 | 1.9 | 115 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-11 11:30 | 0.7 | 2.3 | 135 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-11 12:30 | 1.1 | 2.8 | 150 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-11 13:30 | 1.4 | 2.9 | 180 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-11 14:30 | 0.8 | 2.6 | 210 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-11 15:30 | 0.2 | 2.4 | 230 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-11 16:30 | 0.3 | 1.8 | 262.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-11 17:30 | -0.1 | 1.2 | 297.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-11 18:30 | -1 | 0.7 | 322.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-11 19:30 | -2 | 1.3 | 177.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-11 20:30 | -2.5 | 2.7 | 20 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-11 21:30 | -1.9 | 2.9 | 185 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-11 22:30 | -2.6 | 2.6 | 340 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-11 23:30 | -4.2 | 2.9 | 327.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-12 00:30 | -4.4 | 3.3 | 330 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-12 01:30 | -3.6 | 3.6 | 337.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-02-12 02:30 | -3.2 | 3.6 | 335 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-02-12 03:30 | -3.4 | 3.6 | 330 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-02-12 04:30 | -2.5 | 3.7 | 335 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-02-12 05:30 | -2.7 | 3.7 | 340 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-02-12 06:30 | -2.6 | 3.6 | 170 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-02-12 07:30 | -1.6 | 4.2 | 15 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-02-12 08:30 | -1.5 | 5.4 | 35 | 110 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-02-12 09:30 | -0.6 | 5.9 | 40 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-02-12 10:30 | 0 | 5.6 | 42.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-02-12 11:30 | 0.1 | 5.5 | 45 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-02-12 12:30 | 0.6 | 6.4 | 42.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-02-12 13:30 | 1 | 7.8 | 40 | 500 | 360 | 40 | 0 |  | 0 |  | 320
Lerwick | 1978-02-12 14:30 | 1.3 | 9 | 40 | 900 | 700 | 380 | 0 |  | 0 |  | 320
Lerwick | 1978-02-12 15:30 | 1.5 | 9.4 | 40 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-02-12 16:30 | 1.5 | 8.9 | 40 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-02-12 17:30 | 1.6 | 9 | 40 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-02-12 18:30 | 1.9 | 9.7 | 40 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-12 19:30 | 1.9 | 10 | 40 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-12 20:30 | 1.7 | 10.1 | 42.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-02-12 21:30 | 1.4 | 10.1 | 47.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-02-12 22:30 | 0.9 | 9.5 | 50 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-12 23:30 | 0.7 | 8.7 | 47.5 | 770 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-13 00:30 | 1 | 8.3 | 42.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-13 01:30 | 1.3 | 8.4 | 42.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-02-13 02:30 | 1.5 | 8.9 | 50 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-13 03:30 | 1.6 | 9.7 | 50 | 1025 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-13 04:30 | 1.3 | 11.9 | 37.5 | 1400 | 1212.5 | 892.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-13 05:30 | 1.8 | 13.9 | 32.5 | 1490 | 1445 | 1125 | 0 |  | 0 |  | 320
Lerwick | 1978-02-13 06:30 | 2.7 | 14.5 | 37.5 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-02-13 07:30 | 2.7 | 14.3 | 40 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-13 08:30 | 2.7 | 13.5 | 40 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-02-13 09:30 | 2.8 | 12.5 | 35 | 1470 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-02-13 10:30 | 2.9 | 11.7 | 27.5 | 1400 | 1435 | 1115 | 0 |  | 0 |  | 320
Lerwick | 1978-02-13 11:30 | 2.4 | 11.7 | 27.5 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-02-13 12:30 | 2.4 | 12.2 | 32.5 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-02-13 13:30 | 2.7 | 11.9 | 35 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-02-13 14:30 | 2.7 | 11.4 | 35 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-02-13 15:30 | 2.6 | 11.5 | 37.5 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-02-13 16:30 | 2.3 | 11.8 | 37.5 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-02-13 17:30 | 2 | 11.9 | 35 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-02-13 18:30 | 1.8 | 12.4 | 37.5 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-02-13 19:30 | 1.9 | 13 | 40 | 1480 | 1465 | 1145 | 0 |  | 0 |  | 320
Lerwick | 1978-02-13 20:30 | 1.9 | 12.8 | 42.5 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-02-13 21:30 | 1.8 | 12.1 | 45 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-02-13 22:30 | 1.5 | 11.5 | 42.5 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-02-13 23:30 | 1.6 | 10.5 | 40 | 1270 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-02-14 00:30 | 1.7 | 8.9 | 40 | 770 | 1020 | 700 | 0 |  | 0 |  | 320
Lerwick | 1978-02-14 01:30 | 1.2 | 7.8 | 37.5 | 500 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-02-14 02:30 | 1.1 | 7.4 | 32.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-02-14 03:30 | 1.1 | 6.8 | 27.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-02-14 04:30 | 0.9 | 6.1 | 22.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-02-14 05:30 | 1 | 5.4 | 22.5 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-02-14 06:30 | 0.8 | 4.9 | 25 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-02-14 07:30 | 0.3 | 5.3 | 27.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-02-14 08:30 | 0.3 | 5.5 | 35 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-02-14 09:30 | 0.7 | 5.1 | 37.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-02-14 10:30 | 1.3 | 4.6 | 27.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-02-14 11:30 | 1.9 | 4.2 | 15 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-02-14 12:30 | 1.9 | 4 | 7.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-02-14 13:30 | 1.8 | 4 | 2.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-02-14 14:30 | 2 | 4 | 2.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-02-14 15:30 | 1.6 | 3.9 | 7.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-02-14 16:30 | 1 | 3.3 | 180 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-02-14 17:30 | 0.5 | 2.1 | 337.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-14 18:30 | -0.6 | 1.4 | 310 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-14 19:30 | -1.5 | 1.4 | 282.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-14 20:30 | -0.9 | 1.1 | 292.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-14 21:30 | -0.1 | 0.8 | 307.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-14 22:30 | -0.1 | 1.3 | 270 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-14 23:30 | 0 | 1.6 | 245 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-15 00:30 | 0.1 | 1 | 280 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-15 01:30 | 0 | 2 | 302.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-15 02:30 | -0.1 | 4.9 | 260 | 80 | 40 | 0 | 280 |  | 134.4 |  | 40
Lerwick | 1978-02-15 03:30 | 0.1 | 6.3 | 225 | 220 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-02-15 04:30 | 0 | 7 | 230 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-02-15 05:30 | -0.1 | 7.3 | 232.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-02-15 06:30 | 0 | 6 | 242.5 | 220 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-02-15 07:30 | 0 | 4.4 | 265 | 60 | 140 | 0 | 180 |  | 86.4 |  | 140
Lerwick | 1978-02-15 08:30 | -0.2 | 3.9 | 265 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-02-15 09:30 | -0.4 | 4.2 | 255 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-02-15 10:30 | -0.5 | 4.4 | 260 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-02-15 11:30 | -0.3 | 3.5 | 265 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-02-15 12:30 | -0.1 | 2.4 | 262.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-02-15 13:30 | -0.1 | 1.9 | 270 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-15 14:30 | 0 | 2.7 | 305 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-15 15:30 | -0.1 | 5.8 | 175 | 150 | 75 | 0 | 245 |  | 117.6 |  | 75
Lerwick | 1978-02-15 16:30 | -0.1 | 9.8 | 27.5 | 1025 | 587.5 | 267.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-15 17:30 | -0.1 | 11.7 | 37.5 | 1400 | 1212.5 | 892.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-15 18:30 | -0.4 | 11.4 | 45 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-02-15 19:30 | -0.3 | 10.5 | 50 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-02-15 20:30 | 0 | 9.8 | 47.5 | 1025 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-15 21:30 | 0 | 8.7 | 45 | 770 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-15 22:30 | 0.2 | 8.4 | 47.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-15 23:30 | 0.4 | 8.8 | 47.5 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-16 00:30 | 0.4 | 8.4 | 42.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-16 01:30 | 0.3 | 7.7 | 40 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-16 02:30 | 0 | 7.1 | 40 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-02-16 03:30 | -0.1 | 6.7 | 35 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-02-16 04:30 | 0 | 6.5 | 22.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-02-16 05:30 | -0.1 | 6 | 185 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-02-16 06:30 | -0.5 | 5.5 | 350 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-02-16 07:30 | -1.2 | 5.1 | 345 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-02-16 08:30 | -1.4 | 4.6 | 342.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-02-16 09:30 | -2.2 | 4.4 | 340 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-02-16 10:30 | -2.7 | 5 | 340 | 110 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-02-16 11:30 | -1.6 | 5.3 | 340 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-02-16 12:30 | -1.2 | 4.1 | 340 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-02-16 13:30 | -1.2 | 3.3 | 330 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-02-16 14:30 | -0.8 | 3 | 315 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-16 15:30 | -0.8 | 2.9 | 317.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-16 16:30 | -0.9 | 3.5 | 320 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-02-16 17:30 | -2.4 | 3.9 | 312.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-02-16 18:30 | -3 | 4.6 | 325 | 80 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-02-16 19:30 | -2.2 | 6.5 | 170 | 300 | 190 | 0 | 130 |  | 62.4 |  | 190
Lerwick | 1978-02-16 20:30 | -1.8 | 7.7 | 0 | 500 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-02-16 21:30 | -1.6 | 7 | 177.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-02-16 22:30 | -1.9 | 6.9 | 352.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-02-16 23:30 | -2.8 | 8.9 | 352.5 | 770 | 535 | 215 | 0 |  | 0 |  | 320
Lerwick | 1978-02-17 00:30 | -3 | 11.1 | 177.5 | 1340 | 1055 | 735 | 0 |  | 0 |  | 320
Lerwick | 1978-02-17 01:30 | -2.1 | 12.2 | 0 | 1450 | 1395 | 1075 | 0 |  | 0 |  | 320
Lerwick | 1978-02-17 02:30 | -2.3 | 11.7 | 2.5 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-02-17 03:30 | -2.8 | 10.6 | 5 | 1270 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-02-17 04:30 | -2.7 | 9.8 | 2.5 | 1025 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-17 05:30 | -3.1 | 8.7 | 177.5 | 770 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-17 06:30 | -3.5 | 8 | 352.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-17 07:30 | -3.8 | 8 | 350 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-02-17 08:30 | -3.9 | 8.4 | 352.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-02-17 09:30 | -4.2 | 8.9 | 355 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-17 10:30 | -3.6 | 8.5 | 350 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-02-17 11:30 | -3 | 7.5 | 345 | 500 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-02-17 12:30 | -3.5 | 7 | 347.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-02-17 13:30 | -3.3 | 7.3 | 350 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-02-17 14:30 | -3.3 | 7.8 | 347.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-02-17 15:30 | -3.3 | 7.8 | 345 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-17 16:30 | -3.6 | 7.6 | 345 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-17 17:30 | -4.2 | 7.3 | 342.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-02-17 18:30 | -4.1 | 7.2 | 342.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-02-17 19:30 | -3.9 | 6.9 | 347.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-02-17 20:30 | -4 | 6.7 | 350 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-02-17 21:30 | -4.3 | 6.7 | 347.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-02-17 22:30 | -4.5 | 6.5 | 342.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-02-17 23:30 | -5 | 6.5 | 340 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-02-18 00:30 | -5 | 6.8 | 340 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-02-18 01:30 | -4.4 | 7.1 | 337.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-02-18 02:30 | -4.5 | 6.7 | 335 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-02-18 03:30 | -4.4 | 6.2 | 335 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-02-18 04:30 | -4.7 | 6.6 | 332.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-02-18 05:30 | -4.9 | 7 | 335 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-02-18 06:30 | -4.4 | 7.2 | 345 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-02-18 07:30 | -4.4 | 7.3 | 347.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-02-18 08:30 | -4.6 | 6.9 | 340 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-02-18 09:30 | -4.3 | 6.4 | 335 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-02-18 10:30 | -3.8 | 5.8 | 337.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-02-18 11:30 | -3.6 | 4.9 | 342.5 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-02-18 12:30 | -3.5 | 4.4 | 345 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-02-18 13:30 | -3.2 | 4.2 | 340 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-02-18 14:30 | -3 | 3.8 | 335 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-02-18 15:30 | -3.2 | 3.4 | 335 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-02-18 16:30 | -3.7 | 3 | 332.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-18 17:30 | -4.5 | 2.4 | 327.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-18 18:30 | -4.9 | 2.2 | 322.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-18 19:30 | -4.6 | 2.4 | 317.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-18 20:30 | -3.9 | 3.1 | 317.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-18 21:30 | -3 | 3.4 | 322.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-18 22:30 | -2.7 | 3 | 315 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-18 23:30 | -2.7 | 2.9 | 295 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-19 00:30 | -2.3 | 3.1 | 280 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-19 01:30 | -2.1 | 3.1 | 272.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-19 02:30 | -2.1 | 2.9 | 270 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-19 03:30 | -2.1 | 2.6 | 285 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-19 04:30 | -2 | 2.6 | 310 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-19 05:30 | -2 | 2.7 | 317.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-19 06:30 | -1.9 | 2.6 | 317.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-19 07:30 | -2.9 | 2.4 | 320 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-19 08:30 | -4.1 | 2.1 | 322.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-19 09:30 | -4.4 | 2.1 | 327.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-19 10:30 | -4.6 | 2.4 | 330 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-19 11:30 | -3.8 | 2.6 | 327.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-19 12:30 | -3.2 | 2.4 | 322.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-19 13:30 | -2.7 | 2 | 312.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-19 14:30 | -2 | 2.2 | 295 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-19 15:30 | -1 | 3.2 | 280 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-19 16:30 | -0.1 | 4.1 | 275 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-02-19 17:30 | -0.2 | 4.6 | 277.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-02-19 18:30 | -0.2 | 5.3 | 277.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-02-19 19:30 | 0 | 5.9 | 272.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-02-19 20:30 | 0 | 6.3 | 270 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-02-19 21:30 | -0.1 | 6.8 | 267.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-02-19 22:30 | 0.2 | 7.2 | 267.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-02-19 23:30 | 0.7 | 6.8 | 275 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-02-20 00:30 | 1.1 | 6.4 | 280 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-02-20 01:30 | 1.5 | 6.8 | 280 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-02-20 02:30 | 1.9 | 7.6 | 280 | 500 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-02-20 03:30 | 2.2 | 8 | 280 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-20 04:30 | 2.4 | 7.7 | 280 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-20 05:30 | 2.3 | 7.6 | 277.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-20 06:30 | 2.4 | 7.6 | 272.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-20 07:30 | 2.7 | 7.5 | 270 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-20 08:30 | 2.6 | 7.7 | 270 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-20 09:30 | 2.7 | 8.2 | 270 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-20 10:30 | 3 | 8.5 | 270 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-20 11:30 | 3 | 8.3 | 270 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-20 12:30 | 3 | 8.1 | 270 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-02-20 13:30 | 3 | 8 | 270 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-02-20 14:30 | 2.9 | 7.3 | 270 | 400 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-20 15:30 | 2.6 | 6.2 | 270 | 220 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-02-20 16:30 | 2.5 | 5.3 | 267.5 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-02-20 17:30 | 2.3 | 4.7 | 260 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-02-20 18:30 | 1.8 | 4.5 | 252.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-02-20 19:30 | 1.4 | 4.4 | 247.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-02-20 20:30 | 1 | 4 | 245 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-02-20 21:30 | 0.9 | 2.9 | 245 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-02-20 22:30 | 0.6 | 1.7 | 242.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-20 23:30 | -0.3 | 1.1 | 230 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-21 00:30 | -0.8 | 1 | 212.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-21 01:30 | -1.1 | 1 | 207.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-21 02:30 | -1.8 | 0.7 | 247.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-21 03:30 | -1.9 | 0.2 | 142.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-21 04:30 | -2.4 | 0.2 | 45 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-21 05:30 | -3.5 | 0.9 | 135 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-21 06:30 | -3.6 | 1.9 | 177.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-21 07:30 | -2 | 3.1 | 170 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-21 08:30 | 0 | 3.6 | 162.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-02-21 09:30 | 1.2 | 3.6 | 157.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-02-21 10:30 | 1.7 | 3.7 | 150 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-02-21 11:30 | 2.2 | 3.9 | 140 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-02-21 12:30 | 2.6 | 4 | 135 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-02-21 13:30 | 2.6 | 4 | 142.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-02-21 14:30 | 2.7 | 4 | 152.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-02-21 15:30 | 2.3 | 4.2 | 152.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-02-21 16:30 | 1.8 | 4.4 | 145 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-02-21 17:30 | 1.3 | 4.5 | 135 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-02-21 18:30 | 1 | 4.5 | 130 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-02-21 19:30 | 1.1 | 4.5 | 125 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-02-21 20:30 | 1.2 | 4.4 | 112.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-02-21 21:30 | 1 | 4.2 | 102.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-02-21 22:30 | 1 | 3.9 | 97.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-02-21 23:30 | 1.2 | 3.9 | 80 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-02-22 00:30 | 1.3 | 4.2 | 55 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-02-22 01:30 | 1 | 5.3 | 50 | 110 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-02-22 02:30 | 0.8 | 6.7 | 57.5 | 300 | 205 | 0 | 115 |  | 55.2 |  | 205
Lerwick | 1978-02-22 03:30 | 0.7 | 7.6 | 60 | 500 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-02-22 04:30 | 0.8 | 8.5 | 62.5 | 770 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-02-22 05:30 | 1 | 9.1 | 67.5 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-02-22 06:30 | 1 | 9.4 | 70 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-02-22 07:30 | 1 | 9.7 | 72.5 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-22 08:30 | 1 | 10 | 77.5 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-22 09:30 | 0.8 | 10.1 | 80 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-02-22 10:30 | 0.7 | 10.4 | 80 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-02-22 11:30 | 1 | 10.2 | 82.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-02-22 12:30 | 0.6 | 9.9 | 87.5 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-22 13:30 | 0.5 | 9.8 | 90 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-02-22 14:30 | 1.1 | 9.9 | 90 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-02-22 15:30 | 1.1 | 10.1 | 90 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-22 16:30 | 1 | 10.3 | 87.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-02-22 17:30 | 0.8 | 10.3 | 82.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-02-22 18:30 | 0.4 | 10.3 | 82.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-02-22 19:30 | 0.4 | 10.3 | 87.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-02-22 20:30 | 0.5 | 10.3 | 90 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-02-22 21:30 | 0.5 | 10.3 | 90 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-02-22 22:30 | 0.4 | 10.1 | 92.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-02-22 23:30 | 0.5 | 10.1 | 100 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-02-23 00:30 | 0.9 | 11.3 | 110 | 1340 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-02-23 01:30 | 1.6 | 13.5 | 120 | 1490 | 1415 | 1095 | 0 |  | 0 |  | 320
Lerwick | 1978-02-23 02:30 | 2.2 | 15.2 | 127.5 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-02-23 03:30 | 2.2 | 16.2 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-23 04:30 | 1.6 | 17.1 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-23 05:30 | 1.1 | 17.5 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-23 06:30 | 1 | 17.6 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-23 07:30 | 1.1 | 17.9 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-23 08:30 | 1.2 | 17.9 | 132.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-23 09:30 | 1.3 | 17.8 | 137.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-23 10:30 | 1.5 | 17.9 | 140 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-23 11:30 | 1.8 | 18 | 140 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-23 12:30 | 2.1 | 17.9 | 140 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-23 13:30 | 2.2 | 17.5 | 140 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-23 14:30 | 2.3 | 17.3 | 140 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-23 15:30 | 2.5 | 17.1 | 140 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-23 16:30 | 2.7 | 16.6 | 140 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-23 17:30 | 2.7 | 15.9 | 140 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-23 18:30 | 2.8 | 15.7 | 140 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-23 19:30 | 2.8 | 15.8 | 140 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-23 20:30 | 2.7 | 16 | 140 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-23 21:30 | 2.7 | 15.7 | 140 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-23 22:30 | 2.7 | 15.1 | 140 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-23 23:30 | 2.9 | 14.5 | 140 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-24 00:30 | 2.8 | 13.5 | 140 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-02-24 01:30 | 2.7 | 12.4 | 140 | 1450 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-02-24 02:30 | 2.8 | 11.7 | 140 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-02-24 03:30 | 3 | 11.2 | 140 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-02-24 04:30 | 3.4 | 10.6 | 140 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-02-24 05:30 | 3.7 | 9.9 | 142.5 | 1025 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-24 06:30 | 3.9 | 9.4 | 147.5 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-24 07:30 | 4.2 | 9.4 | 150 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-02-24 08:30 | 4.7 | 9.4 | 152.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-02-24 09:30 | 4.9 | 8.7 | 157.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-02-24 10:30 | 5 | 7.6 | 160 | 500 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-02-24 11:30 | 5.1 | 6.8 | 165 | 300 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-02-24 12:30 | 5.3 | 6.1 | 180 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-02-24 13:30 | 5.5 | 6 | 197.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-02-24 14:30 | 5.4 | 6.4 | 207.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-02-24 15:30 | 5.5 | 6.5 | 205 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-02-24 16:30 | 5.8 | 5.7 | 195 | 150 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-02-24 17:30 | 5.4 | 5 | 190 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-02-24 18:30 | 4.7 | 5.6 | 190 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-02-24 19:30 | 4.6 | 5.9 | 190 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-02-24 20:30 | 4.9 | 5.5 | 192.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-02-24 21:30 | 5.1 | 6 | 200 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-02-24 22:30 | 5.2 | 7.1 | 210 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-02-24 23:30 | 5.6 | 7.7 | 217.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-02-25 00:30 | 5.7 | 7.8 | 215 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-25 01:30 | 5.8 | 7.6 | 210 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-25 02:30 | 5.8 | 8.1 | 217.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-25 03:30 | 5.7 | 8.4 | 227.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-02-25 04:30 | 6 | 6.5 | 217.5 | 300 | 467.5 | 147.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-25 05:30 | 5.8 | 4.7 | 195 | 80 | 190 | 0 | 130 |  | 62.4 |  | 190
Lerwick | 1978-02-25 06:30 | 5.4 | 4.7 | 185 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-02-25 07:30 | 4.8 | 4.7 | 180 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-02-25 08:30 | 4.5 | 4.5 | 172.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-02-25 09:30 | 4.8 | 5.2 | 172.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-02-25 10:30 | 5.4 | 6 | 175 | 220 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-02-25 11:30 | 5.9 | 5.8 | 170 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-02-25 12:30 | 6 | 4.9 | 162.5 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-02-25 13:30 | 6.1 | 4.5 | 157.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-02-25 14:30 | 6.1 | 4.9 | 152.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-02-25 15:30 | 6.1 | 5.5 | 150 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-02-25 16:30 | 5.9 | 5.7 | 147.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-02-25 17:30 | 5.9 | 5.9 | 140 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-02-25 18:30 | 5.8 | 6.4 | 132.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-02-25 19:30 | 5.6 | 6.9 | 127.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-02-25 20:30 | 5.5 | 7.2 | 125 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-02-25 21:30 | 5.3 | 6.9 | 127.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-02-25 22:30 | 5.2 | 6.7 | 132.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-02-25 23:30 | 5.3 | 6.4 | 140 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-02-26 00:30 | 5.5 | 5.8 | 145 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-02-26 01:30 | 5.5 | 5.4 | 142.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-02-26 02:30 | 5.5 | 5.6 | 140 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-02-26 03:30 | 5.5 | 5.9 | 140 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-02-26 04:30 | 5.5 | 5.9 | 140 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-02-26 05:30 | 5.5 | 5.9 | 137.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-02-26 06:30 | 5.6 | 5.9 | 132.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-02-26 07:30 | 5.7 | 6.1 | 127.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-02-26 08:30 | 5.7 | 7.2 | 122.5 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-02-26 09:30 | 5.8 | 8.7 | 122.5 | 770 | 585 | 265 | 0 |  | 0 |  | 320
Lerwick | 1978-02-26 10:30 | 5.8 | 9.2 | 130 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-02-26 11:30 | 5.7 | 8.5 | 140 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-02-26 12:30 | 5.7 | 8.1 | 150 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-26 13:30 | 5.8 | 8.3 | 157.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-02-26 14:30 | 5.9 | 8.7 | 160 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-26 15:30 | 5.9 | 9 | 157.5 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-02-26 16:30 | 5.8 | 9 | 145 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-02-26 17:30 | 5.5 | 9.4 | 127.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-02-26 18:30 | 5.5 | 9.9 | 117.5 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-26 19:30 | 5.7 | 9.6 | 112.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-02-26 20:30 | 5.6 | 8.6 | 112.5 | 770 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-26 21:30 | 5.5 | 7.5 | 122.5 | 500 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-02-26 22:30 | 5.5 | 7.2 | 140 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-02-26 23:30 | 5.6 | 7.7 | 157.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-02-27 00:30 | 5.7 | 7.8 | 167.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-27 01:30 | 5.6 | 7.8 | 170 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-27 02:30 | 5.5 | 7.8 | 170 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-27 03:30 | 5.3 | 7.8 | 170 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-27 04:30 | 5.2 | 8.4 | 170 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-27 05:30 | 5.2 | 8.6 | 170 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-27 06:30 | 5.2 | 8.1 | 172.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-27 07:30 | 5.2 | 7.2 | 177.5 | 400 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-02-27 08:30 | 5.3 | 6.3 | 180 | 220 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-02-27 09:30 | 5.3 | 6.1 | 185 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-02-27 10:30 | 5.3 | 7 | 200 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-02-27 11:30 | 5.8 | 7.8 | 212.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-02-27 12:30 | 6.8 | 7.7 | 210 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-02-27 13:30 | 7.3 | 7.2 | 202.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-02-27 14:30 | 7 | 6.8 | 202.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-02-27 15:30 | 6.9 | 6.2 | 202.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-02-27 16:30 | 6.9 | 4.8 | 192.5 | 80 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-02-27 17:30 | 6.6 | 3.8 | 180 | 25 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-02-27 18:30 | 6 | 3.7 | 180 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-02-27 19:30 | 5.8 | 4.1 | 192.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-02-27 20:30 | 5.9 | 4.2 | 200 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-02-27 21:30 | 5.8 | 3.6 | 200 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-02-27 22:30 | 5.3 | 3.3 | 202.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-02-27 23:30 | 4.8 | 3.6 | 210 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-02-28 00:30 | 4.6 | 3.9 | 212.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-02-28 01:30 | 4.5 | 3.6 | 200 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-02-28 02:30 | 3.9 | 3 | 190 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-02-28 03:30 | 3.5 | 2.4 | 190 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-28 04:30 | 3.3 | 2.1 | 180 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-28 05:30 | 2.8 | 2.1 | 162.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-28 06:30 | 3.7 | 2.1 | 152.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-28 07:30 | 4.6 | 2.3 | 147.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-28 08:30 | 4.8 | 2.8 | 140 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-28 09:30 | 5.2 | 3.1 | 127.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-28 10:30 | 4.8 | 2.6 | 112.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-28 11:30 | 4.4 | 1.8 | 90 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-28 12:30 | 4.4 | 2.1 | 77.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-28 13:30 | 4.8 | 3.3 | 95 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-28 14:30 | 4.8 | 3.9 | 110 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-02-28 15:30 | 4.5 | 3.6 | 100 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-02-28 16:30 | 4.4 | 3.3 | 80 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-02-28 17:30 | 4.5 | 3.2 | 80 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-28 18:30 | 4.8 | 3.1 | 107.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-28 19:30 | 5.1 | 3.3 | 135 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-02-28 20:30 | 5.2 | 4 | 150 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-02-28 21:30 | 5 | 4.6 | 157.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-02-28 22:30 | 4.7 | 4.4 | 157.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-02-28 23:30 | 4.5 | 3.8 | 155 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-03-01 00:30 | 4.7 | 3.3 | 155 | 0 | 12.5 | 0 | 307.5 |  | 147.6 | 35398.8 | 12.5 | 164332.5
Lerwick | 1978-03-01 01:30 | 4.9 | 2.4 | 155 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-01 02:30 | 4.9 | 2.2 | 157.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-01 03:30 | 4.6 | 3.3 | 160 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-01 04:30 | 4.1 | 4.7 | 160 | 80 | 40 | 0 | 280 |  | 134.4 |  | 40
Lerwick | 1978-03-01 05:30 | 4.7 | 6.3 | 160 | 220 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-03-01 06:30 | 5.2 | 7.3 | 157.5 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-03-01 07:30 | 4.9 | 6.8 | 150 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-03-01 08:30 | 4.9 | 6 | 142.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-03-01 09:30 | 5.1 | 6.5 | 140 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-03-01 10:30 | 5.1 | 7.6 | 137.5 | 500 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-03-01 11:30 | 4.9 | 8 | 132.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-01 12:30 | 5 | 8.1 | 130 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-03-01 13:30 | 5.2 | 8.3 | 130 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-03-01 14:30 | 5.3 | 8.7 | 130 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-01 15:30 | 5.4 | 9 | 130 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-03-01 16:30 | 5.6 | 9.1 | 127.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-03-01 17:30 | 5.7 | 9.6 | 122.5 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-01 18:30 | 5.6 | 10.2 | 120 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-01 19:30 | 5.5 | 10.9 | 120 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-03-01 20:30 | 5.3 | 11.5 | 120 | 1400 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-03-01 21:30 | 5.2 | 12.1 | 122.5 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-03-01 22:30 | 5.3 | 12.7 | 127.5 | 1470 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-03-01 23:30 | 5.3 | 13.2 | 130 | 1480 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-03-02 00:30 | 5.1 | 13.2 | 130 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-03-02 01:30 | 5.1 | 13.1 | 127.5 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-03-02 02:30 | 5.2 | 13.3 | 125 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-03-02 03:30 | 5.2 | 13.6 | 127.5 | 1490 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-03-02 04:30 | 5.1 | 13.3 | 130 | 1480 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-03-02 05:30 | 5.1 | 13 | 130 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-03-02 06:30 | 5.2 | 13 | 130 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-03-02 07:30 | 5.2 | 13.1 | 130 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-03-02 08:30 | 5.1 | 12.8 | 132.5 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-03-02 09:30 | 5.1 | 12.4 | 140 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-03-02 10:30 | 5.3 | 12.2 | 147.5 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-03-02 11:30 | 5.4 | 11.6 | 150 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-03-02 12:30 | 5.5 | 10.8 | 150 | 1270 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-03-02 13:30 | 5.5 | 9.9 | 150 | 1025 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-02 14:30 | 5.4 | 9.4 | 152.5 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-02 15:30 | 5.5 | 9.4 | 157.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-03-02 16:30 | 5.6 | 9.7 | 160 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-02 17:30 | 5.4 | 10.2 | 160 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-02 18:30 | 5.2 | 10.7 | 160 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-03-02 19:30 | 5 | 11 | 162.5 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-03-02 20:30 | 4.9 | 10.9 | 165 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-03-02 21:30 | 4.9 | 10.6 | 162.5 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-03-02 22:30 | 5 | 10.4 | 160 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-03-02 23:30 | 5 | 10.4 | 160 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-03-03 00:30 | 5.2 | 10.4 | 160 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-03-03 01:30 | 5.4 | 9.9 | 162.5 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-03 02:30 | 5.5 | 9.4 | 167.5 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-03 03:30 | 5.5 | 9.1 | 170 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-03-03 04:30 | 5.6 | 8.9 | 170 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-03-03 05:30 | 5.7 | 8.8 | 170 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-03-03 06:30 | 5.8 | 8.6 | 170 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-03-03 07:30 | 5.8 | 8.3 | 170 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-03 08:30 | 5.7 | 8 | 170 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-03-03 09:30 | 5.7 | 7.8 | 170 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-03 10:30 | 5.8 | 7.6 | 170 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-03-03 11:30 | 5.9 | 7.3 | 172.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-03-03 12:30 | 6 | 7.2 | 177.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-03-03 13:30 | 5.8 | 7.2 | 180 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-03-03 14:30 | 5.8 | 7.3 | 180 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-03-03 15:30 | 5.9 | 7.6 | 180 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-03-03 16:30 | 5.8 | 7.6 | 180 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-03-03 17:30 | 5.6 | 7.3 | 177.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-03-03 18:30 | 5.5 | 7.2 | 172.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-03-03 19:30 | 5.5 | 7.3 | 170 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-03-03 20:30 | 5.5 | 7.3 | 175 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-03-03 21:30 | 5.5 | 6.8 | 185 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-03-03 22:30 | 5.4 | 6.4 | 190 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-03-03 23:30 | 5.3 | 6.1 | 187.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-03-04 00:30 | 4.9 | 5.4 | 185 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-03-04 01:30 | 4.9 | 4.4 | 187.5 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-03-04 02:30 | 5.2 | 3.5 | 195 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-03-04 03:30 | 5.1 | 3.3 | 207.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-03-04 04:30 | 4.9 | 4 | 217.5 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-03-04 05:30 | 4.4 | 4.2 | 217.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-03-04 06:30 | 3.8 | 3.9 | 222.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-03-04 07:30 | 3.5 | 4.9 | 242.5 | 80 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-03-04 08:30 | 3.8 | 6.4 | 255 | 220 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-03-04 09:30 | 3.6 | 6.7 | 252.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-03-04 10:30 | 3.7 | 6.9 | 252.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-03-04 11:30 | 5 | 7.8 | 252.5 | 500 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-03-04 12:30 | 5.4 | 8.1 | 247.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-04 13:30 | 5.5 | 8.4 | 247.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-03-04 14:30 | 5 | 9.1 | 252.5 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-04 15:30 | 4.1 | 9.4 | 260 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-03-04 16:30 | 4 | 8.6 | 272.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-03-04 17:30 | 3.2 | 7.5 | 285 | 500 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-03-04 18:30 | 2.3 | 6.4 | 295 | 220 | 360 | 40 | 0 |  | 0 |  | 320
Lerwick | 1978-03-04 19:30 | 2.2 | 5.2 | 307.5 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-03-04 20:30 | 2.1 | 4.4 | 320 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-03-04 21:30 | 1.7 | 4.2 | 322.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-03-04 22:30 | 1.3 | 3.9 | 310 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-03-04 23:30 | 1.5 | 3.9 | 300 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-03-05 00:30 | 2 | 4 | 302.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-03-05 01:30 | 2 | 4 | 305 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-03-05 02:30 | 1.9 | 4.4 | 302.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-03-05 03:30 | 1.7 | 5.5 | 295 | 150 | 105 | 0 | 215 |  | 103.2 |  | 105
Lerwick | 1978-03-05 04:30 | 1.5 | 6.6 | 290 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-03-05 05:30 | 1.4 | 7.3 | 290 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-03-05 06:30 | 1 | 7.6 | 290 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-03-05 07:30 | 0.8 | 6.9 | 297.5 | 300 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-03-05 08:30 | 0.9 | 6.4 | 310 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-03-05 09:30 | 1.3 | 6.7 | 312.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-03-05 10:30 | 2.1 | 7.2 | 312.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-03-05 11:30 | 2.5 | 7.5 | 317.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-03-05 12:30 | 2.5 | 7.3 | 320 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-03-05 13:30 | 2.4 | 7.1 | 322.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-03-05 14:30 | 2.5 | 6.7 | 327.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-03-05 15:30 | 2.5 | 6.1 | 332.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-03-05 16:30 | 2.3 | 5.2 | 337.5 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-03-05 17:30 | 1.7 | 4 | 342.5 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-03-05 18:30 | 0.8 | 3.4 | 345 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-03-05 19:30 | -0.1 | 3 | 342.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-05 20:30 | -0.3 | 2.7 | 342.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-05 21:30 | -0.5 | 2.9 | 347.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-05 22:30 | -1.4 | 2.6 | 350 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-05 23:30 | -1.4 | 1.7 | 347.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-06 00:30 | -1 | 1.4 | 172.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-06 01:30 | -0.8 | 1.5 | 12.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-06 02:30 | -0.2 | 1 | 20 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-06 03:30 | -0.3 | 0.6 | 27.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-06 04:30 | -0.7 | 1.5 | 67.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-06 05:30 | -0.3 | 2.9 | 105 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-06 06:30 | 0.2 | 4.2 | 120 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-03-06 07:30 | 0.4 | 5.5 | 130 | 150 | 105 | 0 | 215 |  | 103.2 |  | 105
Lerwick | 1978-03-06 08:30 | 1 | 6.4 | 137.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-03-06 09:30 | 1.6 | 6.9 | 140 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-03-06 10:30 | 1.8 | 7.6 | 142.5 | 500 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-03-06 11:30 | 2.2 | 8 | 147.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-06 12:30 | 2 | 8.3 | 150 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-03-06 13:30 | 1.6 | 8.7 | 150 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-06 14:30 | 1.8 | 9.1 | 150 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-03-06 15:30 | 2.2 | 9 | 150 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-03-06 16:30 | 2.8 | 8.4 | 152.5 | 635 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-06 17:30 | 3.6 | 8.1 | 157.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-03-06 18:30 | 4 | 7.6 | 165 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-06 19:30 | 4.3 | 6.5 | 177.5 | 300 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-03-06 20:30 | 4.4 | 5.6 | 185 | 150 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-03-06 21:30 | 4.2 | 5.2 | 182.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-03-06 22:30 | 4.3 | 4.9 | 180 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-03-06 23:30 | 4.6 | 4.9 | 187.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-03-07 00:30 | 4.8 | 5.4 | 207.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-03-07 01:30 | 5.3 | 6 | 225 | 220 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-03-07 02:30 | 5.8 | 5.9 | 230 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-03-07 03:30 | 5.9 | 5.8 | 230 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-03-07 04:30 | 6.1 | 5.9 | 227.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-03-07 05:30 | 6.1 | 5.4 | 217.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-03-07 06:30 | 5.9 | 4.4 | 200 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-03-07 07:30 | 5.4 | 4.2 | 185 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-03-07 08:30 | 5.2 | 4.9 | 180 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-03-07 09:30 | 5.6 | 5.8 | 182.5 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-03-07 10:30 | 6.2 | 6.6 | 187.5 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-03-07 11:30 | 6.4 | 7 | 192.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-03-07 12:30 | 6.3 | 6.8 | 195 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-03-07 13:30 | 6.5 | 6.4 | 190 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-03-07 14:30 | 6.6 | 5.9 | 185 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-03-07 15:30 | 6.3 | 5.8 | 187.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-03-07 16:30 | 6.1 | 5.9 | 190 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-03-07 17:30 | 5.8 | 5.8 | 190 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-03-07 18:30 | 5.6 | 5.7 | 187.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-03-07 19:30 | 5.5 | 6 | 182.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-03-07 20:30 | 5.5 | 6.9 | 182.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-03-07 21:30 | 5.5 | 7.7 | 187.5 | 500 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-03-07 22:30 | 5.6 | 8.2 | 187.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-07 23:30 | 5.8 | 9 | 182.5 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-08 00:30 | 5.8 | 9.9 | 182.5 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-08 01:30 | 5.6 | 10.1 | 187.5 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-08 02:30 | 5.5 | 9.7 | 192.5 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-08 03:30 | 5.5 | 9.2 | 197.5 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-08 04:30 | 5.5 | 8.5 | 200 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-03-08 05:30 | 5.5 | 8.4 | 207.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-08 06:30 | 5.5 | 9.3 | 230 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-08 07:30 | 5.7 | 10.5 | 262.5 | 1270 | 1085 | 765 | 0 |  | 0 |  | 320
Lerwick | 1978-03-08 08:30 | 6.3 | 11.9 | 290 | 1400 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-03-08 09:30 | 6.5 | 12.8 | 297.5 | 1470 | 1435 | 1115 | 0 |  | 0 |  | 320
Lerwick | 1978-03-08 10:30 | 5.9 | 13.6 | 292.5 | 1490 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-03-08 11:30 | 5.7 | 14.4 | 290 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-03-08 12:30 | 5.9 | 14.7 | 287.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-03-08 13:30 | 6.5 | 14.1 | 282.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-03-08 14:30 | 6.5 | 13.2 | 280 | 1480 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-03-08 15:30 | 6.1 | 12.9 | 280 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-03-08 16:30 | 6.2 | 12.9 | 280 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-03-08 17:30 | 6.2 | 12.3 | 280 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-03-08 18:30 | 6.1 | 10.9 | 280 | 1270 | 1360 | 1040 | 0 |  | 0 |  | 320
Lerwick | 1978-03-08 19:30 | 6.2 | 9.5 | 280 | 1025 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-08 20:30 | 5.8 | 8.5 | 277.5 | 770 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-08 21:30 | 5.3 | 8 | 267.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-08 22:30 | 5.6 | 8.9 | 255 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-08 23:30 | 6.1 | 10.6 | 250 | 1270 | 1020 | 700 | 0 |  | 0 |  | 320
Lerwick | 1978-03-09 00:30 | 6.2 | 11.6 | 250 | 1400 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-03-09 01:30 | 6.3 | 11.4 | 250 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-03-09 02:30 | 6.5 | 10.5 | 252.5 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-03-09 03:30 | 6.5 | 9.6 | 255 | 1025 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-09 04:30 | 6.5 | 9.4 | 252.5 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-09 05:30 | 6.5 | 9.7 | 247.5 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-09 06:30 | 6.5 | 10.2 | 245 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-09 07:30 | 6.5 | 10.7 | 247.5 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-03-09 08:30 | 6.5 | 11.2 | 250 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-03-09 09:30 | 6.5 | 11.2 | 250 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-03-09 10:30 | 6.6 | 10.2 | 250 | 1150 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-03-09 11:30 | 6.8 | 8.8 | 250 | 770 | 960 | 640 | 0 |  | 0 |  | 320
Lerwick | 1978-03-09 12:30 | 6.7 | 8 | 247.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-09 13:30 | 6.6 | 7.8 | 242.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-09 14:30 | 6.6 | 6.9 | 237.5 | 300 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-03-09 15:30 | 6.5 | 5.9 | 232.5 | 150 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-03-09 16:30 | 6.5 | 5.5 | 222.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-03-09 17:30 | 6.2 | 4.7 | 205 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-03-09 18:30 | 5.7 | 4.2 | 192.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-03-09 19:30 | 5.4 | 4.9 | 192.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-03-09 20:30 | 5.2 | 5.6 | 197.5 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-03-09 21:30 | 5 | 6 | 200 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-03-09 22:30 | 5 | 6.2 | 200 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-03-09 23:30 | 5.1 | 6.3 | 200 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-03-10 00:30 | 5.3 | 6.8 | 200 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-03-10 01:30 | 5.6 | 8.5 | 205 | 770 | 535 | 215 | 0 |  | 0 |  | 320
Lerwick | 1978-03-10 02:30 | 6.1 | 10.9 | 217.5 | 1270 | 1020 | 700 | 0 |  | 0 |  | 320
Lerwick | 1978-03-10 03:30 | 6.8 | 12.2 | 227.5 | 1450 | 1360 | 1040 | 0 |  | 0 |  | 320
Lerwick | 1978-03-10 04:30 | 7 | 12.7 | 232.5 | 1470 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-03-10 05:30 | 7.1 | 12.7 | 240 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-03-10 06:30 | 7.2 | 12.4 | 250 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-03-10 07:30 | 7.2 | 12.2 | 262.5 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-03-10 08:30 | 7.3 | 11.9 | 272.5 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-03-10 09:30 | 7.5 | 11.8 | 272.5 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-03-10 10:30 | 7.7 | 11.8 | 272.5 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-03-10 11:30 | 8.2 | 11.8 | 280 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-03-10 12:30 | 8.5 | 11.8 | 285 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-03-10 13:30 | 8.6 | 11.8 | 280 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-03-10 14:30 | 8.8 | 11.5 | 275 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-03-10 15:30 | 8.5 | 10.5 | 277.5 | 1270 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-03-10 16:30 | 8.1 | 8.7 | 280 | 770 | 1020 | 700 | 0 |  | 0 |  | 320
Lerwick | 1978-03-10 17:30 | 7.6 | 7 | 280 | 400 | 585 | 265 | 0 |  | 0 |  | 320
Lerwick | 1978-03-10 18:30 | 6.8 | 6.1 | 277.5 | 220 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-03-10 19:30 | 6.3 | 5.8 | 272.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-03-10 20:30 | 5.9 | 5.5 | 267.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-03-10 21:30 | 5.7 | 4.9 | 262.5 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-03-10 22:30 | 5.3 | 3.7 | 252.5 | 25 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-03-10 23:30 | 5.3 | 2.8 | 252.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-03-11 00:30 | 5.7 | 2.2 | 130 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-11 01:30 | 5 | 1.8 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-11 02:30 | 3.7 | 2.2 | 65 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-11 03:30 | 3.4 | 2.6 | 150 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-11 04:30 | 4.1 | 2.6 | 165 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-11 05:30 | 4.4 | 3.3 | 152.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-11 06:30 | 4.6 | 4.6 | 147.5 | 80 | 40 | 0 | 280 |  | 134.4 |  | 40
Lerwick | 1978-03-11 07:30 | 5 | 5.9 | 155 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-03-11 08:30 | 5.2 | 6.7 | 160 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-03-11 09:30 | 5.3 | 7 | 160 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-03-11 10:30 | 5.6 | 6.8 | 160 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-03-11 11:30 | 5.6 | 7.3 | 162.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-03-11 12:30 | 5.6 | 8.6 | 167.5 | 770 | 585 | 265 | 0 |  | 0 |  | 320
Lerwick | 1978-03-11 13:30 | 5.9 | 9.1 | 172.5 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-03-11 14:30 | 6.1 | 8.5 | 177.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-03-11 15:30 | 6 | 7.8 | 177.5 | 500 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-03-11 16:30 | 6.1 | 6.9 | 175 | 300 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-03-11 17:30 | 6.2 | 6 | 177.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-03-11 18:30 | 6.1 | 5.5 | 182.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-03-11 19:30 | 6 | 5.1 | 182.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-03-11 20:30 | 6 | 4.6 | 177.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-03-11 21:30 | 5.8 | 4.4 | 180 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-03-11 22:30 | 5.8 | 4.4 | 192.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-03-11 23:30 | 5.8 | 3.3 | 200 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-03-12 00:30 | 5.7 | 1.6 | 192.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-12 01:30 | 5.6 | 1.1 | 185 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-12 02:30 | 5.5 | 1.3 | 190 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-12 03:30 | 5.5 | 1.1 | 200 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-12 04:30 | 5.6 | 1 | 207.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-12 05:30 | 5.7 | 1 | 217.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-12 06:30 | 5.8 | 1 | 227.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-12 07:30 | 6.1 | 1.4 | 225 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-12 08:30 | 6.1 | 2.2 | 225 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-12 09:30 | 6.2 | 2.6 | 230 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-12 10:30 | 6.6 | 2.6 | 215 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-12 11:30 | 6.7 | 2.8 | 190 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-12 12:30 | 6.5 | 3.1 | 182.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-12 13:30 | 6.2 | 3.1 | 182.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-12 14:30 | 5.9 | 3.2 | 172.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-12 15:30 | 5.7 | 3.3 | 165 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-12 16:30 | 5.6 | 3.6 | 170 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-03-12 17:30 | 5.6 | 4.2 | 177.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-03-12 18:30 | 5.4 | 4.1 | 182.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-03-12 19:30 | 5.4 | 4.4 | 197.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-03-12 20:30 | 5.4 | 6.1 | 220 | 220 | 140 | 0 | 180 |  | 86.4 |  | 140
Lerwick | 1978-03-12 21:30 | 5 | 7.6 | 232.5 | 500 | 360 | 40 | 0 |  | 0 |  | 320
Lerwick | 1978-03-12 22:30 | 4.2 | 8.4 | 242.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-12 23:30 | 4 | 9.3 | 260 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-13 00:30 | 4.1 | 10.5 | 275 | 1270 | 1085 | 765 | 0 |  | 0 |  | 320
Lerwick | 1978-03-13 01:30 | 4.5 | 11.5 | 280 | 1400 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-03-13 02:30 | 4.6 | 11.8 | 280 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-03-13 03:30 | 4.6 | 12.3 | 280 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-03-13 04:30 | 4.8 | 13 | 280 | 1480 | 1465 | 1145 | 0 |  | 0 |  | 320
Lerwick | 1978-03-13 05:30 | 4.8 | 12.2 | 282.5 | 1450 | 1465 | 1145 | 0 |  | 0 |  | 320
Lerwick | 1978-03-13 06:30 | 4.9 | 10.5 | 285 | 1270 | 1360 | 1040 | 0 |  | 0 |  | 320
Lerwick | 1978-03-13 07:30 | 4.8 | 9.6 | 282.5 | 1025 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-13 08:30 | 4.8 | 9.9 | 277.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-03-13 09:30 | 4.9 | 10.4 | 272.5 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-13 10:30 | 5.6 | 10.1 | 270 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-03-13 11:30 | 6.3 | 9.4 | 267.5 | 900 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-03-13 12:30 | 6.6 | 8.9 | 262.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-03-13 13:30 | 6.7 | 8.4 | 257.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-13 14:30 | 6.4 | 7.9 | 255 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-13 15:30 | 6.2 | 7.3 | 252.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-03-13 16:30 | 6.2 | 6.2 | 245 | 220 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-03-13 17:30 | 5.7 | 4.9 | 240 | 80 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-03-13 18:30 | 4.7 | 4 | 232.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-03-13 19:30 | 3.3 | 2.9 | 220 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-03-13 20:30 | 2.3 | 1.7 | 212.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-13 21:30 | 1.8 | 0.9 | 245 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-13 22:30 | 1.2 | 0.2 | 140 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-13 23:30 | 0.5 | 0.4 | 27.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-14 00:30 | 0.4 | 1.7 | 82.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-14 01:30 | 1.3 | 3.5 | 110 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-03-14 02:30 | 2.7 | 4.7 | 107.5 | 80 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-03-14 03:30 | 3.3 | 5.4 | 100 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-03-14 04:30 | 3.1 | 6.7 | 92.5 | 300 | 205 | 0 | 115 |  | 55.2 |  | 205
Lerwick | 1978-03-14 05:30 | 3.1 | 8.1 | 90 | 635 | 467.5 | 147.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-14 06:30 | 3.2 | 9.3 | 90 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-14 07:30 | 3.4 | 10.1 | 90 | 1150 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-03-14 08:30 | 3.8 | 10.9 | 90 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-03-14 09:30 | 4.1 | 11.8 | 90 | 1400 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-03-14 10:30 | 4.4 | 12.7 | 87.5 | 1470 | 1435 | 1115 | 0 |  | 0 |  | 320
Lerwick | 1978-03-14 11:30 | 4.5 | 13.5 | 80 | 1490 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-03-14 12:30 | 4.4 | 14.1 | 72.5 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-03-14 13:30 | 4.3 | 14.4 | 70 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-03-14 14:30 | 4 | 14.4 | 70 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-03-14 15:30 | 3.7 | 14.4 | 70 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-03-14 16:30 | 3.5 | 14.5 | 70 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-03-14 17:30 | 3.4 | 14.5 | 70 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-03-14 18:30 | 3.3 | 14.3 | 67.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-03-14 19:30 | 3.4 | 14.3 | 62.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-03-14 20:30 | 3.6 | 14.3 | 60 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-03-14 21:30 | 3.6 | 14 | 60 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-03-14 22:30 | 3.5 | 13.7 | 60 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-03-14 23:30 | 3.3 | 13.3 | 57.5 | 1480 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-03-15 00:30 | 3.2 | 13.2 | 52.5 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-03-15 01:30 | 2.8 | 13.6 | 50 | 1490 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-03-15 02:30 | 2.5 | 13.6 | 50 | 1490 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-03-15 03:30 | 2.3 | 13.1 | 50 | 1480 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-03-15 04:30 | 2.1 | 12.9 | 50 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-03-15 05:30 | 2 | 12.9 | 50 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-03-15 06:30 | 2 | 12.7 | 50 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-03-15 07:30 | 2 | 12.4 | 50 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-03-15 08:30 | 2.1 | 12.4 | 50 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-03-15 09:30 | 2.3 | 12.4 | 50 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-03-15 10:30 | 2.6 | 12.4 | 50 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-03-15 11:30 | 2.7 | 12.4 | 50 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-03-15 12:30 | 3.1 | 12.2 | 50 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-03-15 13:30 | 3.4 | 11.9 | 50 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-03-15 14:30 | 3.1 | 11.6 | 50 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-03-15 15:30 | 2.8 | 11.2 | 50 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-03-15 16:30 | 2.7 | 10.7 | 50 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-03-15 17:30 | 2.5 | 10.5 | 50 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-03-15 18:30 | 2.2 | 10.6 | 50 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-03-15 19:30 | 1.8 | 10.8 | 50 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-03-15 20:30 | 1.5 | 10.8 | 50 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-03-15 21:30 | 1.1 | 10.9 | 50 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-03-15 22:30 | 1.3 | 11.2 | 50 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-03-15 23:30 | 1.6 | 11.5 | 47.5 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-03-16 00:30 | 1.6 | 11.2 | 42.5 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-03-16 01:30 | 1.5 | 11.2 | 40 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-03-16 02:30 | 1.5 | 11.7 | 40 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-03-16 03:30 | 1.5 | 12 | 37.5 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-03-16 04:30 | 1.4 | 12.7 | 35 | 1470 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-03-16 05:30 | 1.2 | 13.6 | 35 | 1490 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-03-16 06:30 | 1.2 | 13.4 | 32.5 | 1480 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-03-16 07:30 | 1 | 12.3 | 32.5 | 1450 | 1465 | 1145 | 0 |  | 0 |  | 320
Lerwick | 1978-03-16 08:30 | 0.9 | 11.8 | 35 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-03-16 09:30 | 1 | 12.1 | 32.5 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-03-16 10:30 | 1 | 12.4 | 30 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-03-16 11:30 | 1.1 | 12.8 | 30 | 1470 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-03-16 12:30 | 1.3 | 13.1 | 30 | 1480 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-03-16 13:30 | 1.2 | 13 | 30 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-03-16 14:30 | 1.4 | 12.7 | 27.5 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-03-16 15:30 | 1.7 | 12.4 | 22.5 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-03-16 16:30 | 1.5 | 12.4 | 20 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-03-16 17:30 | 0.9 | 12.6 | 20 | 1470 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-03-16 18:30 | 0.8 | 13.1 | 17.5 | 1480 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-03-16 19:30 | 0.7 | 13.1 | 12.5 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-03-16 20:30 | 0.7 | 12.7 | 12.5 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-03-16 21:30 | 0.9 | 12.5 | 15 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-03-16 22:30 | 0.6 | 12 | 12.5 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-03-16 23:30 | 0.7 | 10.9 | 7.5 | 1270 | 1360 | 1040 | 0 |  | 0 |  | 320
Lerwick | 1978-03-17 00:30 | 0.8 | 9.6 | 180 | 1025 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-17 01:30 | 0.6 | 8.5 | 355 | 770 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-17 02:30 | 0.1 | 7.6 | 355 | 500 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-03-17 03:30 | -0.2 | 6.9 | 350 | 300 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-03-17 04:30 | -0.5 | 6.2 | 342.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-03-17 05:30 | -0.9 | 5.3 | 335 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-03-17 06:30 | -1.6 | 5.4 | 325 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-03-17 07:30 | -1.2 | 6 | 322.5 | 220 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-03-17 08:30 | 0 | 6.3 | 325 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-03-17 09:30 | 0.4 | 6.9 | 322.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-03-17 10:30 | 1.3 | 8.2 | 322.5 | 635 | 467.5 | 147.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-17 11:30 | 2.2 | 9.4 | 327.5 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-17 12:30 | 2.4 | 9.4 | 327.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-03-17 13:30 | 2.3 | 8.5 | 322.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-03-17 14:30 | 2.3 | 8 | 320 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-17 15:30 | 2.1 | 8.1 | 325 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-03-17 16:30 | 2.2 | 7.2 | 335 | 400 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-17 17:30 | 1.7 | 5.7 | 337.5 | 150 | 275 | 0 | 45 |  | 21.6 |  | 275
Lerwick | 1978-03-17 18:30 | 1 | 4.7 | 325 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-03-17 19:30 | 0.7 | 4.2 | 307.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-03-17 20:30 | 0.5 | 3.7 | 295 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-03-17 21:30 | 0.2 | 3.6 | 282.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-03-17 22:30 | 0.4 | 3.6 | 270 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-03-17 23:30 | 1 | 3.3 | 260 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-03-18 00:30 | 1 | 3.2 | 250 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-18 01:30 | 1 | 3.6 | 257.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-03-18 02:30 | 1.8 | 3.6 | 280 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-03-18 03:30 | 1.9 | 3.4 | 287.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-03-18 04:30 | 1.6 | 3.6 | 287.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-03-18 05:30 | 2 | 3.3 | 287.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-03-18 06:30 | 2.1 | 2.9 | 270 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-18 07:30 | 1.9 | 3 | 250 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-18 08:30 | 2.3 | 4.1 | 255 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-03-18 09:30 | 3.8 | 5.6 | 265 | 150 | 105 | 0 | 215 |  | 103.2 |  | 105
Lerwick | 1978-03-18 10:30 | 5.3 | 6.9 | 262.5 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-03-18 11:30 | 5.9 | 7.8 | 260 | 500 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-03-18 12:30 | 6.2 | 8.1 | 260 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-18 13:30 | 5.9 | 8 | 260 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-03-18 14:30 | 6.3 | 7.2 | 270 | 400 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-18 15:30 | 6.5 | 5.4 | 282.5 | 110 | 255 | 0 | 65 |  | 31.2 |  | 255
Lerwick | 1978-03-18 16:30 | 5.7 | 4.7 | 272.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-03-18 17:30 | 5.4 | 5.4 | 255 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-03-18 18:30 | 5.7 | 5.6 | 247.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-03-18 19:30 | 5.5 | 5.2 | 242.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-03-18 20:30 | 5.3 | 5 | 240 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-03-18 21:30 | 5.1 | 5 | 235 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-03-18 22:30 | 5 | 4.7 | 217.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-03-18 23:30 | 4.9 | 4.4 | 195 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-03-19 00:30 | 4.6 | 4.7 | 182.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-03-19 01:30 | 4.5 | 5.6 | 177.5 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-03-19 02:30 | 4.6 | 6.8 | 172.5 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-03-19 03:30 | 4.7 | 8.4 | 170 | 635 | 467.5 | 147.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-19 04:30 | 4.6 | 10.3 | 167.5 | 1150 | 892.5 | 572.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-19 05:30 | 4.4 | 12.6 | 162.5 | 1470 | 1310 | 990 | 0 |  | 0 |  | 320
Lerwick | 1978-03-19 06:30 | 4.4 | 14.8 | 160 | 1500 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-03-19 07:30 | 4.5 | 15.9 | 160 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-03-19 08:30 | 4.7 | 16.8 | 160 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-03-19 09:30 | 5.1 | 18.3 | 160 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-03-19 10:30 | 5.1 | 19.6 | 160 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-03-19 11:30 | 4.7 | 20.7 | 160 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-03-19 12:30 | 4.6 | 21.8 | 160 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-03-19 13:30 | 4.5 | 21.9 | 162.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-03-19 14:30 | 4 | 20.6 | 170 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-03-19 15:30 | 3.9 | 18.7 | 177.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-03-19 16:30 | 3.7 | 16.2 | 180 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-03-19 17:30 | 3.4 | 13 | 185 | 1480 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-03-19 18:30 | 3.6 | 10.4 | 197.5 | 1150 | 1315 | 995 | 0 |  | 0 |  | 320
Lerwick | 1978-03-19 19:30 | 4.2 | 9 | 207.5 | 900 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-03-19 20:30 | 4.3 | 8.5 | 210 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-03-19 21:30 | 4 | 8.6 | 212.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-03-19 22:30 | 3.9 | 8.8 | 215 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-03-19 23:30 | 3.9 | 8.4 | 215 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-20 00:30 | 3.9 | 7.7 | 217.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-20 01:30 | 4 | 7.7 | 222.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-03-20 02:30 | 3.6 | 8.2 | 225 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-20 03:30 | 3 | 8.6 | 225 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-20 04:30 | 3 | 8.4 | 225 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-20 05:30 | 3 | 8 | 222.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-03-20 06:30 | 2.9 | 8 | 225 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-03-20 07:30 | 3.1 | 8 | 235 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-03-20 08:30 | 3.2 | 8.2 | 235 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-03-20 09:30 | 3.4 | 9 | 225 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-20 10:30 | 4.1 | 9.2 | 225 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-03-20 11:30 | 5 | 8.5 | 232.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-03-20 12:30 | 4.8 | 8.1 | 232.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-20 13:30 | 5.2 | 7.9 | 230 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-20 14:30 | 5.2 | 7.3 | 230 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-03-20 15:30 | 5 | 6.7 | 237.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-03-20 16:30 | 4.4 | 5.9 | 245 | 150 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-03-20 17:30 | 3.2 | 4.9 | 237.5 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-03-20 18:30 | 2.6 | 4.1 | 235 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-03-20 19:30 | 2 | 3.2 | 237.5 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-03-20 20:30 | 1.5 | 2 | 220 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-20 21:30 | 1.4 | 1.4 | 202.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-20 22:30 | 1.4 | 1.4 | 207.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-20 23:30 | 1.2 | 1.5 | 197.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-21 00:30 | 0.9 | 1.2 | 90 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-21 01:30 | 0.8 | 0.7 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-21 02:30 | 0.8 | 0.2 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-21 03:30 | 0.3 | 0 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-21 04:30 | 0 | 0.9 | 170 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-21 05:30 | -0.2 | 2 | 170 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-21 06:30 | -0.1 | 1.3 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-21 07:30 | 0.1 | 0.5 | 152.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-21 08:30 | 0.2 | 0.9 | 270 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-21 09:30 | 1.2 | 2 | 235 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-21 10:30 | 2.4 | 3.6 | 245 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-03-21 11:30 | 3.9 | 5.1 | 257.5 | 110 | 67.5 | 0 | 252.5 |  | 121.2 |  | 67.5
Lerwick | 1978-03-21 12:30 | 5.3 | 6.3 | 260 | 220 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-03-21 13:30 | 5.5 | 7.2 | 257.5 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-03-21 14:30 | 5.7 | 7.3 | 257.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-03-21 15:30 | 5.9 | 6.8 | 267.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-03-21 16:30 | 5.5 | 5.4 | 272.5 | 110 | 205 | 0 | 115 |  | 55.2 |  | 205
Lerwick | 1978-03-21 17:30 | 5.2 | 4.2 | 262.5 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-03-21 18:30 | 4 | 4.1 | 250 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-03-21 19:30 | 2.5 | 5.1 | 245 | 110 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-03-21 20:30 | 2.3 | 5.9 | 242.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-03-21 21:30 | 2.4 | 5.8 | 237.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-03-21 22:30 | 2.5 | 5.8 | 242.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-03-21 23:30 | 2.8 | 5.6 | 250 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-03-22 00:30 | 2.7 | 5.5 | 245 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-03-22 01:30 | 2.6 | 5.7 | 237.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-03-22 02:30 | 2.6 | 5.8 | 232.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-03-22 03:30 | 2.6 | 5.9 | 225 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-03-22 04:30 | 2.5 | 5.9 | 215 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-03-22 05:30 | 2.7 | 6.3 | 207.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-03-22 06:30 | 3.3 | 7.4 | 200 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-03-22 07:30 | 3.9 | 8.9 | 190 | 770 | 585 | 265 | 0 |  | 0 |  | 320
Lerwick | 1978-03-22 08:30 | 4.3 | 10 | 182.5 | 1150 | 960 | 640 | 0 |  | 0 |  | 320
Lerwick | 1978-03-22 09:30 | 4.6 | 10.6 | 177.5 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-03-22 10:30 | 5 | 11.7 | 175 | 1400 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-03-22 11:30 | 5.5 | 12.7 | 177.5 | 1470 | 1435 | 1115 | 0 |  | 0 |  | 320
Lerwick | 1978-03-22 12:30 | 5.3 | 13.5 | 180 | 1490 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-03-22 13:30 | 4.8 | 14 | 180 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-03-22 14:30 | 4.3 | 13.8 | 180 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-03-22 15:30 | 3.8 | 12.1 | 185 | 1450 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-03-22 16:30 | 3.6 | 9.9 | 202.5 | 1025 | 1237.5 | 917.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-22 17:30 | 4.1 | 8.5 | 225 | 770 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-22 18:30 | 4 | 7.3 | 240 | 400 | 585 | 265 | 0 |  | 0 |  | 320
Lerwick | 1978-03-22 19:30 | 3.7 | 6 | 257.5 | 220 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-03-22 20:30 | 3.5 | 4 | 262.5 | 60 | 140 | 0 | 180 |  | 86.4 |  | 140
Lerwick | 1978-03-22 21:30 | 3.3 | 2 | 240 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-03-22 22:30 | 2.8 | 1.1 | 227.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-22 23:30 | 1.8 | 1 | 235 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-23 00:30 | 1.1 | 1 | 255 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-23 01:30 | 0.6 | 1.5 | 282.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-23 02:30 | 0.8 | 2.7 | 300 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-23 03:30 | 2.2 | 3.4 | 310 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-23 04:30 | 2.9 | 3.6 | 320 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-03-23 05:30 | 2.1 | 3.4 | 330 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-03-23 06:30 | 2.1 | 3.3 | 337.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-23 07:30 | 1.7 | 3.6 | 337.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-03-23 08:30 | 2 | 3.9 | 330 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-03-23 09:30 | 3.9 | 4 | 322.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-03-23 10:30 | 4.8 | 4.2 | 317.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-03-23 11:30 | 5.7 | 4.9 | 315 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-03-23 12:30 | 6.2 | 5.4 | 317.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-03-23 13:30 | 6.6 | 5.4 | 325 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-03-23 14:30 | 6.5 | 5.4 | 335 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-03-23 15:30 | 6.4 | 5.1 | 340 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-03-23 16:30 | 6.3 | 4.4 | 335 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-03-23 17:30 | 5.9 | 3.8 | 327.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-03-23 18:30 | 5.3 | 3.4 | 327.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-03-23 19:30 | 4.4 | 3 | 330 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-23 20:30 | 3.3 | 2.7 | 327.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-23 21:30 | 3 | 2.9 | 320 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-23 22:30 | 3.2 | 3.1 | 312.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-23 23:30 | 3.1 | 3.1 | 310 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-24 00:30 | 3 | 3.1 | 310 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-24 01:30 | 3.1 | 3.3 | 312.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-24 02:30 | 3.1 | 3.8 | 315 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-03-24 03:30 | 3 | 4 | 315 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-03-24 04:30 | 3.2 | 4 | 315 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-03-24 05:30 | 3.2 | 4.2 | 312.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-03-24 06:30 | 2.8 | 4.7 | 307.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-03-24 07:30 | 2.9 | 5.3 | 302.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-03-24 08:30 | 3.9 | 5.9 | 297.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-03-24 09:30 | 5.1 | 6.6 | 290 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-03-24 10:30 | 6.1 | 7 | 280 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-03-24 11:30 | 6.6 | 6.8 | 270 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-03-24 12:30 | 6.8 | 6.8 | 262.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-03-24 13:30 | 7 | 7 | 260 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-03-24 14:30 | 6.9 | 7.1 | 257.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-03-24 15:30 | 7.1 | 7.2 | 250 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-03-24 16:30 | 7 | 6.5 | 240 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-03-24 17:30 | 6.3 | 5.4 | 230 | 110 | 205 | 0 | 115 |  | 55.2 |  | 205
Lerwick | 1978-03-24 18:30 | 5.4 | 4.4 | 217.5 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-03-24 19:30 | 4.4 | 4.5 | 200 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-03-24 20:30 | 3.9 | 6.5 | 182.5 | 300 | 190 | 0 | 130 |  | 62.4 |  | 190
Lerwick | 1978-03-24 21:30 | 4.4 | 9.3 | 172.5 | 900 | 600 | 280 | 0 |  | 0 |  | 320
Lerwick | 1978-03-24 22:30 | 4.9 | 11.4 | 175 | 1340 | 1120 | 800 | 0 |  | 0 |  | 320
Lerwick | 1978-03-24 23:30 | 4.9 | 12.1 | 185 | 1450 | 1395 | 1075 | 0 |  | 0 |  | 320
Lerwick | 1978-03-25 00:30 | 4 | 10.4 | 200 | 1150 | 1300 | 980 | 0 |  | 0 |  | 320
Lerwick | 1978-03-25 01:30 | 3.2 | 8.7 | 225 | 770 | 960 | 640 | 0 |  | 0 |  | 320
Lerwick | 1978-03-25 02:30 | 4.1 | 9 | 245 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-03-25 03:30 | 4.9 | 9.5 | 252.5 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-25 04:30 | 5 | 9.4 | 257.5 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-25 05:30 | 5 | 9.3 | 260 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-03-25 06:30 | 4.7 | 9.1 | 260 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-03-25 07:30 | 4.6 | 9.6 | 260 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-25 08:30 | 4.8 | 11 | 260 | 1340 | 1182.5 | 862.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-25 09:30 | 5.1 | 11.9 | 265 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-03-25 10:30 | 5.7 | 11.7 | 270 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-03-25 11:30 | 5.7 | 11.1 | 262.5 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-03-25 12:30 | 5.3 | 10.5 | 257.5 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-03-25 13:30 | 5.7 | 10.1 | 262.5 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-03-25 14:30 | 6.3 | 10 | 265 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-03-25 15:30 | 6.7 | 9.6 | 265 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-25 16:30 | 6.3 | 9 | 260 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-25 17:30 | 5.9 | 8.2 | 252.5 | 635 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-25 18:30 | 5.1 | 7 | 252.5 | 400 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-25 19:30 | 3.9 | 5.9 | 255 | 150 | 275 | 0 | 45 |  | 21.6 |  | 275
Lerwick | 1978-03-25 20:30 | 3.2 | 4.9 | 255 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-03-25 21:30 | 2.9 | 4.5 | 257.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-03-25 22:30 | 2.6 | 4.4 | 257.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-03-25 23:30 | 2.1 | 4.2 | 252.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-03-26 00:30 | 1.9 | 4 | 250 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-03-26 01:30 | 1.9 | 4 | 250 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-03-26 02:30 | 1.8 | 4.2 | 250 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-03-26 03:30 | 1.7 | 4.7 | 252.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-03-26 04:30 | 1.8 | 5 | 257.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-03-26 05:30 | 1.8 | 4.7 | 260 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-03-26 06:30 | 1.8 | 4.2 | 252.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-03-26 07:30 | 2.2 | 3.9 | 230 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-03-26 08:30 | 3.3 | 3.7 | 212.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-03-26 09:30 | 4.3 | 3.6 | 215 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-03-26 10:30 | 4.9 | 4 | 217.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-03-26 11:30 | 5.7 | 4.7 | 210 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-03-26 12:30 | 5.7 | 5.2 | 200 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-03-26 13:30 | 5.3 | 5.5 | 192.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-03-26 14:30 | 6 | 5.3 | 187.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-03-26 15:30 | 6.2 | 4.7 | 180 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-03-26 16:30 | 5.3 | 4.5 | 172.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-03-26 17:30 | 5.3 | 4.2 | 170 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-03-26 18:30 | 4.7 | 3.8 | 167.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-03-26 19:30 | 3.3 | 3.7 | 162.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-03-26 20:30 | 3 | 4.1 | 160 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-03-26 21:30 | 3.2 | 4.6 | 160 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-03-26 22:30 | 3.3 | 4.9 | 160 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-03-26 23:30 | 3.6 | 4.9 | 160 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-03-27 00:30 | 3.7 | 5.1 | 160 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-03-27 01:30 | 3.6 | 5.6 | 160 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-03-27 02:30 | 3.6 | 6.3 | 160 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-03-27 03:30 | 3.9 | 7.1 | 160 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-03-27 04:30 | 4.1 | 8 | 160 | 635 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-27 05:30 | 4.2 | 9.2 | 160 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-27 06:30 | 4.1 | 10.4 | 160 | 1150 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-03-27 07:30 | 4.2 | 10.8 | 162.5 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-03-27 08:30 | 4.7 | 10.6 | 167.5 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-03-27 09:30 | 4.9 | 10.6 | 172.5 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-03-27 10:30 | 4.4 | 10.8 | 177.5 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-03-27 11:30 | 3.5 | 10 | 180 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-03-27 12:30 | 2.7 | 8.4 | 187.5 | 635 | 892.5 | 572.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-27 13:30 | 2.9 | 7.7 | 212.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-27 14:30 | 4.4 | 8.6 | 240 | 770 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-03-27 15:30 | 6.4 | 9.3 | 250 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-03-27 16:30 | 7.1 | 9 | 250 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-03-27 17:30 | 6.4 | 8.4 | 247.5 | 635 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-27 18:30 | 5.8 | 8 | 240 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-03-27 19:30 | 5.6 | 8.2 | 232.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-03-27 20:30 | 5.5 | 9 | 230 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-27 21:30 | 5.5 | 9.5 | 230 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-27 22:30 | 5.5 | 9.4 | 232.5 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-27 23:30 | 5.5 | 9.5 | 235 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-28 00:30 | 5.4 | 9.4 | 232.5 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-28 01:30 | 4.9 | 9 | 230 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-03-28 02:30 | 4.5 | 8.9 | 227.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-03-28 03:30 | 4.2 | 8 | 220 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-28 04:30 | 4.1 | 7.2 | 215 | 400 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-28 05:30 | 4.2 | 7.1 | 217.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-03-28 06:30 | 4.1 | 6.7 | 217.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-03-28 07:30 | 4.2 | 6.8 | 210 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-03-28 08:30 | 4.9 | 7.6 | 200 | 500 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-03-28 09:30 | 5.7 | 8.2 | 192.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-28 10:30 | 6.4 | 8.9 | 190 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-28 11:30 | 6.9 | 9.5 | 190 | 1025 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-28 12:30 | 6.9 | 9.6 | 187.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-03-28 13:30 | 6.9 | 9.5 | 180 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-03-28 14:30 | 7.2 | 9.6 | 170 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-03-28 15:30 | 6.9 | 9.8 | 162.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-03-28 16:30 | 6.3 | 9.9 | 160 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-03-28 17:30 | 6.1 | 10.7 | 157.5 | 1270 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-28 18:30 | 5.7 | 12.5 | 157.5 | 1470 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-03-28 19:30 | 5.7 | 14.6 | 170 | 1500 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-03-28 20:30 | 6.3 | 17.7 | 195 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-03-28 21:30 | 5.9 | 20.2 | 220 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-03-28 22:30 | 4.3 | 18.8 | 230 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-03-28 23:30 | 4 | 15.7 | 227.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-03-29 00:30 | 4.5 | 12.8 | 220 | 1470 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-03-29 01:30 | 4.7 | 10.1 | 212.5 | 1150 | 1310 | 990 | 0 |  | 0 |  | 320
Lerwick | 1978-03-29 02:30 | 5 | 8.9 | 210 | 770 | 960 | 640 | 0 |  | 0 |  | 320
Lerwick | 1978-03-29 03:30 | 5.1 | 8.4 | 210 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-29 04:30 | 5.1 | 8 | 210 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-03-29 05:30 | 4.7 | 8.4 | 207.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-03-29 06:30 | 4.6 | 9 | 202.5 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-29 07:30 | 5 | 9.6 | 200 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-29 08:30 | 5.4 | 10 | 200 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-03-29 09:30 | 5.8 | 10.4 | 200 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-03-29 10:30 | 6.5 | 11.1 | 200 | 1340 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-03-29 11:30 | 6.9 | 11.2 | 202.5 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-03-29 12:30 | 6.8 | 10.7 | 207.5 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-03-29 13:30 | 6.7 | 10.2 | 210 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-03-29 14:30 | 6.9 | 9.4 | 212.5 | 900 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-03-29 15:30 | 7.4 | 8.6 | 217.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-03-29 16:30 | 7 | 9.1 | 220 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-03-29 17:30 | 5.8 | 10.1 | 222.5 | 1150 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-03-29 18:30 | 5.4 | 10.7 | 225 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-03-29 19:30 | 5.5 | 11.5 | 222.5 | 1400 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-03-29 20:30 | 5.4 | 12.8 | 220 | 1470 | 1435 | 1115 | 0 |  | 0 |  | 320
Lerwick | 1978-03-29 21:30 | 5.5 | 13.6 | 222.5 | 1490 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-03-29 22:30 | 5.6 | 12.5 | 227.5 | 1470 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-03-29 23:30 | 5.3 | 11 | 227.5 | 1340 | 1405 | 1085 | 0 |  | 0 |  | 320
Lerwick | 1978-03-30 00:30 | 5.2 | 10.9 | 222.5 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-03-30 01:30 | 5.2 | 11.6 | 220 | 1400 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-03-30 02:30 | 5.3 | 12 | 220 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-03-30 03:30 | 5.5 | 11.7 | 220 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-03-30 04:30 | 5.5 | 11.5 | 220 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-03-30 05:30 | 5.5 | 11.4 | 220 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-03-30 06:30 | 5.4 | 11.3 | 220 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-03-30 07:30 | 5.4 | 11.5 | 220 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-03-30 08:30 | 5.7 | 11.8 | 220 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-03-30 09:30 | 6.2 | 11.5 | 220 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-03-30 10:30 | 6.2 | 11.1 | 220 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-03-30 11:30 | 6.3 | 11.1 | 220 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-03-30 12:30 | 6.8 | 11.1 | 220 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-03-30 13:30 | 7.4 | 10.7 | 220 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-03-30 14:30 | 7.8 | 10 | 222.5 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-03-30 15:30 | 7.1 | 8.8 | 227.5 | 770 | 960 | 640 | 0 |  | 0 |  | 320
Lerwick | 1978-03-30 16:30 | 6.4 | 7.2 | 225 | 400 | 585 | 265 | 0 |  | 0 |  | 320
Lerwick | 1978-03-30 17:30 | 6.4 | 5.6 | 212.5 | 150 | 275 | 0 | 45 |  | 21.6 |  | 275
Lerwick | 1978-03-30 18:30 | 6 | 4.9 | 205 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-03-30 19:30 | 5.6 | 4.6 | 207.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-03-30 20:30 | 5.1 | 4.4 | 212.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-03-30 21:30 | 4.8 | 4.4 | 220 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-03-30 22:30 | 4.7 | 4 | 235 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-03-30 23:30 | 4.6 | 3.3 | 252.5 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-03-31 00:30 | 4.4 | 2.8 | 257.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-31 01:30 | 4.4 | 2.6 | 250 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-31 02:30 | 4 | 3.1 | 242.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-31 03:30 | 4 | 3.8 | 240 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-03-31 04:30 | 4.2 | 4.2 | 237.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-03-31 05:30 | 4 | 4.5 | 237.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-03-31 06:30 | 4 | 4.5 | 240 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-03-31 07:30 | 4.5 | 5.1 | 232.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-03-31 08:30 | 5.4 | 6 | 222.5 | 220 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-03-31 09:30 | 6.2 | 6.5 | 220 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-03-31 10:30 | 6.8 | 6.5 | 215 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-03-31 11:30 | 7 | 6.4 | 200 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-03-31 12:30 | 7.2 | 6.5 | 185 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-03-31 13:30 | 7.2 | 6.5 | 177.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-03-31 14:30 | 7.5 | 6.3 | 172.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-03-31 15:30 | 7.9 | 6 | 170 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-03-31 16:30 | 7.3 | 5.4 | 170 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-03-31 17:30 | 6.6 | 4.4 | 165 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-03-31 18:30 | 6 | 3.5 | 152.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-03-31 19:30 | 5 | 3.1 | 140 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-03-31 20:30 | 4.5 | 3.1 | 137.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-31 21:30 | 4.6 | 2.6 | 145 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-31 22:30 | 5.1 | 2.2 | 147.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-03-31 23:30 | 5.5 | 3 | 140 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-01 00:30 | 5.4 | 4.4 | 132.5 | 60 | 30 | 0 | 290 |  | 139.2 | 53419.2 | 30 | 119110
Lerwick | 1978-04-01 01:30 | 5.2 | 4.9 | 127.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-04-01 02:30 | 5 | 5.2 | 125 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-04-01 03:30 | 5 | 5.5 | 125 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-04-01 04:30 | 5 | 5.7 | 122.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-04-01 05:30 | 5 | 5.9 | 117.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-04-01 06:30 | 5.2 | 6.7 | 110 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-04-01 07:30 | 5.4 | 7.6 | 102.5 | 500 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-04-01 08:30 | 5.8 | 8.2 | 97.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-01 09:30 | 6.3 | 9 | 95 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-01 10:30 | 6.6 | 10 | 97.5 | 1150 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-04-01 11:30 | 6.9 | 10.6 | 97.5 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-04-01 12:30 | 7 | 10.8 | 92.5 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-04-01 13:30 | 7 | 10.8 | 90 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-04-01 14:30 | 7 | 10.8 | 87.5 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-04-01 15:30 | 7.1 | 10.9 | 82.5 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-04-01 16:30 | 6.8 | 11 | 80 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-04-01 17:30 | 6.4 | 10.7 | 80 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-04-01 18:30 | 6.1 | 10.2 | 80 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-04-01 19:30 | 6 | 10 | 77.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-04-01 20:30 | 6 | 10.1 | 72.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-04-01 21:30 | 6 | 9.8 | 72.5 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-01 22:30 | 6 | 8.2 | 80 | 635 | 830 | 510 | 0 |  | 0 |  | 320
Lerwick | 1978-04-01 23:30 | 5.7 | 6.1 | 92.5 | 220 | 427.5 | 107.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-02 00:30 | 5.3 | 4.3 | 115 | 60 | 140 | 0 | 180 |  | 86.4 |  | 140
Lerwick | 1978-04-02 01:30 | 5.2 | 3.1 | 135 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-04-02 02:30 | 5 | 2.4 | 120 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-02 03:30 | 4.8 | 2.1 | 85 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-02 04:30 | 4.6 | 2.3 | 72.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-02 05:30 | 4.4 | 3.2 | 75 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-02 06:30 | 4.8 | 4.6 | 75 | 80 | 40 | 0 | 280 |  | 134.4 |  | 40
Lerwick | 1978-04-02 07:30 | 5.3 | 5.9 | 80 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-04-02 08:30 | 5.6 | 6.3 | 90 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-04-02 09:30 | 5.7 | 6.2 | 100 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-04-02 10:30 | 5.8 | 6.3 | 107.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-04-02 11:30 | 6 | 6.7 | 110 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-04-02 12:30 | 6 | 7.3 | 112.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-04-02 13:30 | 6 | 7.7 | 117.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-04-02 14:30 | 5.8 | 7.6 | 120 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-04-02 15:30 | 5.7 | 7.2 | 120 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-04-02 16:30 | 5.6 | 6.7 | 120 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-04-02 17:30 | 5.9 | 6.4 | 120 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-04-02 18:30 | 5.9 | 6.1 | 120 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-04-02 19:30 | 5.3 | 5.4 | 122.5 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-04-02 20:30 | 5.2 | 5.3 | 127.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-04-02 21:30 | 5.3 | 5.8 | 130 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-04-02 22:30 | 5.3 | 5.6 | 132.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-04-02 23:30 | 5.1 | 4.9 | 140 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-04-03 00:30 | 5 | 4.4 | 142.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-04-03 01:30 | 5 | 4.1 | 130 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-04-03 02:30 | 5 | 3.6 | 105 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-04-03 03:30 | 4.9 | 3.6 | 80 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-04-03 04:30 | 4.8 | 4.2 | 75 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-04-03 05:30 | 4.8 | 4.9 | 87.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-04-03 06:30 | 4.8 | 5.5 | 107.5 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-04-03 07:30 | 4.7 | 5.5 | 130 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-04-03 08:30 | 4.6 | 4.9 | 140 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-04-03 09:30 | 4.8 | 4 | 137.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-04-03 10:30 | 5 | 3.3 | 130 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-04-03 11:30 | 5.3 | 3.2 | 110 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-03 12:30 | 5.7 | 3.6 | 77.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-04-03 13:30 | 6 | 4.2 | 57.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-04-03 14:30 | 6.1 | 4.5 | 57.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-04-03 15:30 | 6 | 4.5 | 60 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-04-03 16:30 | 5.8 | 4.4 | 57.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-04-03 17:30 | 5.7 | 4.2 | 52.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-04-03 18:30 | 5.6 | 4.2 | 50 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-04-03 19:30 | 5.5 | 4.4 | 52.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-04-03 20:30 | 5.6 | 4.2 | 55 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-04-03 21:30 | 5.8 | 3.6 | 52.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-04-03 22:30 | 5.9 | 3.2 | 47.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-04-03 23:30 | 5.9 | 3.1 | 42.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-04 00:30 | 5.8 | 2.9 | 42.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-04 01:30 | 5.7 | 2.4 | 45 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-04 02:30 | 5.7 | 1.7 | 40 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-04 03:30 | 5.6 | 1.7 | 32.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-04 04:30 | 5.5 | 2.4 | 30 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-04 05:30 | 5.5 | 2.7 | 30 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-04 06:30 | 5.2 | 2.7 | 30 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-04 07:30 | 5.3 | 2.9 | 30 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-04 08:30 | 5.8 | 3.5 | 30 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-04-04 09:30 | 6.1 | 4.1 | 35 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-04-04 10:30 | 6.4 | 4.2 | 42.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-04-04 11:30 | 6.8 | 3.9 | 42.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-04-04 12:30 | 6.9 | 3.9 | 47.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-04-04 13:30 | 7 | 3.6 | 67.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-04-04 14:30 | 7.5 | 3.2 | 72.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-04-04 15:30 | 7.5 | 3.2 | 50 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-04 16:30 | 7 | 3 | 30 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-04 17:30 | 6.5 | 2.1 | 25 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-04 18:30 | 6.1 | 1.2 | 190 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-04 19:30 | 5.5 | 1.6 | 342.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-04 20:30 | 4.6 | 2.7 | 335 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-04 21:30 | 3.7 | 3.2 | 342.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-04 22:30 | 3.2 | 3.1 | 345 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-04 23:30 | 2.8 | 3.1 | 340 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-05 00:30 | 2.5 | 3.1 | 332.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-05 01:30 | 2.1 | 3.1 | 332.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-05 02:30 | 2.1 | 3.1 | 337.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-05 03:30 | 3.1 | 3.1 | 340 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-05 04:30 | 3.8 | 3.2 | 342.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-05 05:30 | 4.1 | 3.4 | 347.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-05 06:30 | 4.5 | 3.6 | 350 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-04-05 07:30 | 4.8 | 3.4 | 352.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-04-05 08:30 | 5.3 | 3 | 185 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-05 09:30 | 5.9 | 2.4 | 25 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-05 10:30 | 6.4 | 1.7 | 42.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-05 11:30 | 6.8 | 1.3 | 47.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-05 12:30 | 7 | 1.5 | 187.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-05 13:30 | 7.2 | 2.2 | 295 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-05 14:30 | 7.2 | 3.3 | 255 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-05 15:30 | 7 | 3.7 | 252.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-04-05 16:30 | 6.8 | 3.3 | 267.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-04-05 17:30 | 6.8 | 2.9 | 290 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-05 18:30 | 7.1 | 2.6 | 300 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-05 19:30 | 7.1 | 2.4 | 292.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-05 20:30 | 6.8 | 2.2 | 277.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-05 21:30 | 6.4 | 2.4 | 265 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-05 22:30 | 6.1 | 2.9 | 257.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-05 23:30 | 5.9 | 3.1 | 257.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-06 00:30 | 5.9 | 3.1 | 262.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-06 01:30 | 5.9 | 3.1 | 270 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-06 02:30 | 5.9 | 3.2 | 277.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-06 03:30 | 5.9 | 3.4 | 277.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-06 04:30 | 5.9 | 3.7 | 272.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-04-06 05:30 | 6 | 3.9 | 270 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-04-06 06:30 | 6 | 4.2 | 270 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-04-06 07:30 | 6 | 4.7 | 270 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-04-06 08:30 | 6 | 4.7 | 272.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-04-06 09:30 | 6 | 4.5 | 275 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-04-06 10:30 | 6 | 4.7 | 270 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-04-06 11:30 | 6.2 | 4.9 | 262.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-04-06 12:30 | 6.6 | 4.9 | 260 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-04-06 13:30 | 7 | 5.3 | 257.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-04-06 14:30 | 7.3 | 5.8 | 252.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-04-06 15:30 | 7.6 | 5.9 | 247.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-04-06 16:30 | 7.4 | 5.6 | 242.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-04-06 17:30 | 6.8 | 4.9 | 240 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-04-06 18:30 | 6.1 | 3.7 | 237.5 | 25 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-04-06 19:30 | 4.7 | 2.9 | 235 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-04-06 20:30 | 4.2 | 3 | 235 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-06 21:30 | 4.7 | 3.3 | 240 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-06 22:30 | 5.1 | 3.4 | 255 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-06 23:30 | 5.3 | 4 | 270 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-04-07 00:30 | 5.6 | 4.2 | 277.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-04-07 01:30 | 5.6 | 3.9 | 280 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-04-07 02:30 | 5.6 | 3.9 | 280 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-04-07 03:30 | 5.7 | 3.6 | 277.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-04-07 04:30 | 5.8 | 3 | 270 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-04-07 05:30 | 6 | 2.9 | 260 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-07 06:30 | 6.1 | 3.5 | 252.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-04-07 07:30 | 6.1 | 4.4 | 250 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-04-07 08:30 | 6.1 | 5.1 | 250 | 110 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-04-07 09:30 | 6.3 | 5.2 | 260 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-04-07 10:30 | 6.5 | 4.7 | 275 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-04-07 11:30 | 7.3 | 4.4 | 272.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-04-07 12:30 | 7.8 | 4.9 | 262.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-04-07 13:30 | 7.8 | 5.5 | 260 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-04-07 14:30 | 7.6 | 5.8 | 260 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-04-07 15:30 | 7.3 | 6.1 | 260 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-04-07 16:30 | 7.2 | 6.8 | 260 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-04-07 17:30 | 6.9 | 7.4 | 260 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-04-07 18:30 | 6.8 | 7.8 | 260 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-04-07 19:30 | 6.4 | 7.6 | 260 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-04-07 20:30 | 6 | 6.4 | 257.5 | 220 | 360 | 40 | 0 |  | 0 |  | 320
Lerwick | 1978-04-07 21:30 | 6.2 | 5.8 | 255 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-04-07 22:30 | 6.5 | 5.8 | 262.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-04-07 23:30 | 6.6 | 4.8 | 275 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-04-08 00:30 | 6.5 | 3.3 | 272.5 | 0 | 40 | 0 | 280 |  | 134.4 |  | 40
Lerwick | 1978-04-08 01:30 | 6.4 | 2.6 | 252.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-08 02:30 | 5.9 | 2.8 | 235 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-08 03:30 | 5.5 | 3.5 | 227.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-04-08 04:30 | 5.3 | 4.7 | 225 | 80 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-04-08 05:30 | 5.3 | 5.5 | 227.5 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-04-08 06:30 | 5.5 | 5.7 | 232.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-04-08 07:30 | 5.9 | 6 | 237.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-04-08 08:30 | 6 | 6.8 | 237.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-04-08 09:30 | 6.3 | 8.1 | 232.5 | 635 | 467.5 | 147.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-08 10:30 | 7.2 | 9.7 | 230 | 1025 | 830 | 510 | 0 |  | 0 |  | 320
Lerwick | 1978-04-08 11:30 | 7.6 | 10.5 | 232.5 | 1270 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-08 12:30 | 7.6 | 10.5 | 235 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-04-08 13:30 | 8.1 | 10.6 | 235 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-04-08 14:30 | 8.4 | 10.9 | 235 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-04-08 15:30 | 8.1 | 11 | 232.5 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-04-08 16:30 | 7.6 | 10.9 | 230 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-04-08 17:30 | 6.9 | 10.8 | 230 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-04-08 18:30 | 6.1 | 10.8 | 230 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-04-08 19:30 | 5.7 | 10.4 | 230 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-04-08 20:30 | 5.5 | 9.6 | 232.5 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-08 21:30 | 5.1 | 9 | 240 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-08 22:30 | 4.6 | 8.2 | 250 | 635 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-08 23:30 | 3.8 | 6.9 | 255 | 300 | 467.5 | 147.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-09 00:30 | 3.3 | 6 | 257.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-04-09 01:30 | 3.5 | 6.4 | 265 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-04-09 02:30 | 3.6 | 6.7 | 277.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-04-09 03:30 | 3.6 | 6 | 302.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-04-09 04:30 | 3.2 | 5.7 | 330 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-04-09 05:30 | 2.5 | 5.3 | 342.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-04-09 06:30 | 2 | 5 | 347.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-04-09 07:30 | 1.9 | 5.6 | 352.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-04-09 08:30 | 1.9 | 6.3 | 352.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-04-09 09:30 | 2.4 | 6.3 | 347.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-04-09 10:30 | 2.6 | 6 | 342.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-04-09 11:30 | 3.1 | 6.3 | 332.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-04-09 12:30 | 3.6 | 7.3 | 325 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-04-09 13:30 | 2.7 | 8 | 327.5 | 635 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-09 14:30 | 2.1 | 8 | 335 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-04-09 15:30 | 2.2 | 8.8 | 347.5 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-09 16:30 | 1.6 | 9.9 | 177.5 | 1025 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-09 17:30 | 0.8 | 10.4 | 175 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-09 18:30 | -0.3 | 10.6 | 345 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-04-09 19:30 | -1.4 | 10.6 | 340 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-04-09 20:30 | -1.6 | 10.1 | 340 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-04-09 21:30 | -1.5 | 9.4 | 340 | 900 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-04-09 22:30 | -1.4 | 8.5 | 340 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-04-09 23:30 | -1.7 | 8 | 342.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-10 00:30 | -2.1 | 7.8 | 347.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-10 01:30 | -2.4 | 7.3 | 347.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-04-10 02:30 | -2.6 | 6.7 | 342.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-04-10 03:30 | -2.6 | 6.5 | 345 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-04-10 04:30 | -2.9 | 7.4 | 175 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-04-10 05:30 | -3 | 8.3 | 0 | 635 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-10 06:30 | -2.6 | 8.2 | 177.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-04-10 07:30 | -2.1 | 8.4 | 352.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-04-10 08:30 | -1.6 | 8.6 | 350 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-10 09:30 | -2 | 8.2 | 345 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-10 10:30 | -2.1 | 8.4 | 335 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-04-10 11:30 | -0.8 | 8.6 | 330 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-10 12:30 | 0 | 8.6 | 335 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-04-10 13:30 | 0 | 9.1 | 340 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-04-10 14:30 | -0.1 | 9.4 | 335 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-04-10 15:30 | 0 | 9.4 | 330 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-04-10 16:30 | 0.2 | 9.7 | 332.5 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-10 17:30 | 0.6 | 10.1 | 337.5 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-10 18:30 | 0.7 | 9.9 | 340 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-10 19:30 | 0.3 | 9.6 | 337.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-04-10 20:30 | 0 | 9.9 | 335 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-04-10 21:30 | 0 | 9.5 | 337.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-04-10 22:30 | 0 | 8.5 | 340 | 770 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-10 23:30 | 0 | 7.6 | 340 | 500 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-04-11 00:30 | 0 | 6.7 | 340 | 300 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-04-11 01:30 | 0.1 | 5.9 | 337.5 | 150 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-04-11 02:30 | 0 | 5.7 | 335 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-04-11 03:30 | -0.4 | 5.7 | 332.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-04-11 04:30 | -0.9 | 5.7 | 330 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-04-11 05:30 | -0.5 | 5.8 | 332.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-04-11 06:30 | -0.1 | 6.1 | 335 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-04-11 07:30 | -0.2 | 6.7 | 337.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-04-11 08:30 | -0.2 | 7.5 | 340 | 500 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-04-11 09:30 | 0.8 | 8.9 | 345 | 770 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-04-11 10:30 | 2.1 | 9.9 | 175 | 1025 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-11 11:30 | 2.5 | 9.5 | 177.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-04-11 12:30 | 3.2 | 8.3 | 350 | 635 | 830 | 510 | 0 |  | 0 |  | 320
Lerwick | 1978-04-11 13:30 | 3.7 | 7.4 | 337.5 | 400 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-11 14:30 | 3.4 | 7.1 | 320 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-04-11 15:30 | 3.3 | 7 | 302.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-04-11 16:30 | 3.2 | 7 | 292.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-04-11 17:30 | 2.5 | 7 | 287.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-04-11 18:30 | 2.4 | 7.3 | 287.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-04-11 19:30 | 2.3 | 7.3 | 305 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-04-11 20:30 | 1 | 6.3 | 327.5 | 220 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-04-11 21:30 | -0.3 | 5.7 | 332.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-04-11 22:30 | -0.3 | 5.7 | 327.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-04-11 23:30 | -0.1 | 5.5 | 322.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-04-12 00:30 | -0.1 | 5.1 | 315 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-04-12 01:30 | -0.2 | 4.7 | 307.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-04-12 02:30 | -0.5 | 4.5 | 305 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-04-12 03:30 | -0.8 | 4.7 | 305 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-04-12 04:30 | -0.6 | 5.5 | 310 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-04-12 05:30 | -0.4 | 6.8 | 317.5 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-04-12 06:30 | -0.2 | 7.5 | 325 | 500 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-04-12 07:30 | 0.1 | 7.6 | 332.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-04-12 08:30 | 0.1 | 8.2 | 332.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-12 09:30 | 0.5 | 9 | 330 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-12 10:30 | 1.5 | 9.3 | 327.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-04-12 11:30 | 2.2 | 9.1 | 322.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-04-12 12:30 | 2.4 | 9 | 317.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-04-12 13:30 | 2.6 | 9.2 | 312.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-04-12 14:30 | 3 | 9.5 | 310 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-12 15:30 | 3.2 | 9.4 | 312.5 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-12 16:30 | 2.5 | 8.9 | 317.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-04-12 17:30 | 1.8 | 8.1 | 317.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-12 18:30 | 1.8 | 7.6 | 312.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-12 19:30 | 1.6 | 7.3 | 310 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-04-12 20:30 | 1.1 | 7.1 | 307.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-04-12 21:30 | 1.1 | 6.7 | 302.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-04-12 22:30 | 0.9 | 6.1 | 300 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-04-12 23:30 | 0.3 | 5.9 | 297.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-04-13 00:30 | 0 | 5.8 | 297.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-04-13 01:30 | 0.1 | 5.3 | 305 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-04-13 02:30 | 0.3 | 5.2 | 310 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-04-13 03:30 | 0.1 | 5.4 | 310 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-04-13 04:30 | 0 | 5.1 | 307.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-04-13 05:30 | -0.1 | 4.9 | 307.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-04-13 06:30 | -0.1 | 5.3 | 312.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-04-13 07:30 | 0 | 6.2 | 312.5 | 220 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-04-13 08:30 | 0.4 | 6.8 | 312.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-04-13 09:30 | 1.1 | 7 | 317.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-04-13 10:30 | 1.7 | 7.2 | 315 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-04-13 11:30 | 2.4 | 7.5 | 307.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-04-13 12:30 | 2.8 | 7.1 | 307.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-04-13 13:30 | 3 | 6.5 | 312.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-04-13 14:30 | 2.8 | 6.3 | 317.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-04-13 15:30 | 2.9 | 5.6 | 315 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-04-13 16:30 | 3.2 | 5 | 297.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-04-13 17:30 | 2.9 | 4.5 | 267.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-04-13 18:30 | 1.4 | 3.3 | 257.5 | 0 | 40 | 0 | 280 |  | 134.4 |  | 40
Lerwick | 1978-04-13 19:30 | 0 | 2.4 | 282.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-13 20:30 | 0.3 | 2 | 307.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-13 21:30 | 0.7 | 1.6 | 312.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-13 22:30 | 0.7 | 2 | 307.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-13 23:30 | 0.7 | 3.2 | 315 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-14 00:30 | 0.6 | 3.9 | 330 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-04-14 01:30 | 0 | 4.4 | 337.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-04-14 02:30 | -0.3 | 5.3 | 340 | 110 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-04-14 03:30 | 0 | 5.5 | 342.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-04-14 04:30 | -0.3 | 4.9 | 345 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-04-14 05:30 | -0.7 | 4.2 | 342.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-04-14 06:30 | -0.5 | 4 | 340 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-04-14 07:30 | 0.7 | 4.2 | 337.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-04-14 08:30 | 2.1 | 5.2 | 335 | 110 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-04-14 09:30 | 3.5 | 6.5 | 345 | 300 | 205 | 0 | 115 |  | 55.2 |  | 205
Lerwick | 1978-04-14 10:30 | 4.2 | 7.6 | 182.5 | 500 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-04-14 11:30 | 4.6 | 8.4 | 7.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-14 12:30 | 5.2 | 8.4 | 5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-04-14 13:30 | 5.7 | 7.8 | 177.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-14 14:30 | 5.5 | 7.9 | 337.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-04-14 15:30 | 4.6 | 8 | 330 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-14 16:30 | 3.9 | 7.7 | 342.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-14 17:30 | 3.9 | 6.9 | 347.5 | 300 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-04-14 18:30 | 4 | 5.6 | 342.5 | 150 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-04-14 19:30 | 3.1 | 4.4 | 342.5 | 60 | 105 | 0 | 215 |  | 103.2 |  | 105
Lerwick | 1978-04-14 20:30 | 2.2 | 3.9 | 340 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-04-14 21:30 | 2.1 | 3.7 | 327.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-04-14 22:30 | 2 | 3.4 | 320 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-04-14 23:30 | 2 | 3.2 | 325 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-15 00:30 | 2.1 | 3.2 | 335 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-15 01:30 | 2 | 3.6 | 340 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-04-15 02:30 | 1.9 | 4.2 | 342.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-04-15 03:30 | 2.1 | 4.2 | 345 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-04-15 04:30 | 1.2 | 3.5 | 345 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-04-15 05:30 | 0.4 | 2.8 | 342.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-04-15 06:30 | 0.7 | 2.6 | 335 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-15 07:30 | 1.7 | 2.8 | 335 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-15 08:30 | 3.1 | 2.9 | 175 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-15 09:30 | 3.6 | 2.6 | 47.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-15 10:30 | 4.1 | 2.6 | 110 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-15 11:30 | 5 | 2.9 | 132.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-15 12:30 | 5.2 | 3.1 | 132.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-15 13:30 | 5 | 2.9 | 140 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-15 14:30 | 4.9 | 2.7 | 147.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-15 15:30 | 4.8 | 2.9 | 157.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-15 16:30 | 4.9 | 3.2 | 190 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-15 17:30 | 5.3 | 3.3 | 235 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-15 18:30 | 5.3 | 3 | 260 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-15 19:30 | 4.4 | 2.2 | 255 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-15 20:30 | 3.5 | 1.4 | 227.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-15 21:30 | 2.6 | 1 | 205 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-15 22:30 | 1.7 | 1 | 202.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-15 23:30 | 1.7 | 1.5 | 205 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-16 00:30 | 2.1 | 2.4 | 205 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-16 01:30 | 2.3 | 2.7 | 205 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-16 02:30 | 2.3 | 3 | 202.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-16 03:30 | 2.3 | 3.6 | 200 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-04-16 04:30 | 2.5 | 4.1 | 200 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-04-16 05:30 | 2.6 | 4.9 | 200 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-04-16 06:30 | 3.3 | 6.2 | 200 | 220 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-04-16 07:30 | 4.2 | 7.3 | 200 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-04-16 08:30 | 5 | 7.8 | 202.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-04-16 09:30 | 5.2 | 8.5 | 207.5 | 770 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-04-16 10:30 | 5 | 9.7 | 212.5 | 1025 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-16 11:30 | 5.1 | 10.7 | 220 | 1270 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-16 12:30 | 5.1 | 10.6 | 230 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-04-16 13:30 | 5.2 | 9.9 | 240 | 1025 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-16 14:30 | 5.9 | 9.2 | 250 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-16 15:30 | 6.6 | 8.9 | 257.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-04-16 16:30 | 6.9 | 8.8 | 260 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-04-16 17:30 | 7 | 9 | 262.5 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-04-16 18:30 | 7 | 9.3 | 267.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-04-16 19:30 | 6.8 | 9.1 | 267.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-04-16 20:30 | 6.4 | 8.7 | 262.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-04-16 21:30 | 6.2 | 8 | 260 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-16 22:30 | 6.3 | 7.3 | 262.5 | 400 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-16 23:30 | 6.4 | 7.1 | 270 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-04-17 00:30 | 6.4 | 6.7 | 282.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-04-17 01:30 | 6.5 | 6.1 | 312.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-04-17 02:30 | 6.3 | 5.8 | 182.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-04-17 03:30 | 5.6 | 5.7 | 40 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-04-17 04:30 | 4.8 | 5.8 | 50 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-04-17 05:30 | 4.4 | 6.1 | 50 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-04-17 06:30 | 4.2 | 6.5 | 50 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-04-17 07:30 | 4.1 | 6.7 | 50 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-04-17 08:30 | 4.5 | 6.9 | 50 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-04-17 09:30 | 4.8 | 7.6 | 50 | 500 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-04-17 10:30 | 4.8 | 8.4 | 50 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-17 11:30 | 5.1 | 8.6 | 50 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-17 12:30 | 5.3 | 8.2 | 50 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-17 13:30 | 5.2 | 7.8 | 50 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-17 14:30 | 5 | 7.8 | 50 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-04-17 15:30 | 4.9 | 8 | 50 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-17 16:30 | 4.9 | 7.6 | 52.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-17 17:30 | 4.7 | 6.9 | 57.5 | 300 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-04-17 18:30 | 4.4 | 6.4 | 60 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-04-17 19:30 | 3.8 | 5.8 | 57.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-04-17 20:30 | 3.3 | 5.2 | 52.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-04-17 21:30 | 3.1 | 5 | 50 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-04-17 22:30 | 2.7 | 5 | 47.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-04-17 23:30 | 2.5 | 5.2 | 45 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-04-18 00:30 | 2.7 | 5.4 | 47.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-04-18 01:30 | 2.4 | 5.1 | 47.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-04-18 02:30 | 2.3 | 4.7 | 42.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-04-18 03:30 | 2.3 | 4.4 | 40 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-04-18 04:30 | 2.2 | 4.2 | 37.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-04-18 05:30 | 2.2 | 4.2 | 32.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-04-18 06:30 | 2.7 | 4.7 | 32.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-04-18 07:30 | 3.5 | 4.7 | 37.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-04-18 08:30 | 4.1 | 4.7 | 37.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-04-18 09:30 | 4.5 | 4.9 | 32.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-04-18 10:30 | 4.8 | 5 | 32.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-04-18 11:30 | 5.3 | 4.9 | 42.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-04-18 12:30 | 5.4 | 4.4 | 57.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-04-18 13:30 | 6 | 3.8 | 67.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-04-18 14:30 | 6.6 | 3.4 | 70 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-04-18 15:30 | 6.3 | 3 | 77.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-18 16:30 | 6.1 | 2.4 | 102.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-18 17:30 | 5.8 | 2 | 132.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-18 18:30 | 5.4 | 1.5 | 140 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-18 19:30 | 4.7 | 0.9 | 97.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-18 20:30 | 3.6 | 0.2 | 30 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-18 21:30 | 2.2 | 0.2 | 22.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-18 22:30 | 1.1 | 0.7 | 72.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-18 23:30 | 1.6 | 1.6 | 107.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-19 00:30 | 2.5 | 3 | 122.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-19 01:30 | 2.7 | 4.1 | 132.5 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-04-19 02:30 | 3.3 | 4.2 | 127.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-04-19 03:30 | 3.6 | 3.8 | 115 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-04-19 04:30 | 3.7 | 3.6 | 117.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-04-19 05:30 | 4.2 | 3.8 | 137.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-04-19 06:30 | 4.9 | 4.5 | 155 | 80 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-04-19 07:30 | 5.6 | 5.3 | 157.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-04-19 08:30 | 5.9 | 5.8 | 152.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-04-19 09:30 | 6.4 | 5.8 | 150 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-04-19 10:30 | 6.8 | 5.5 | 152.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-04-19 11:30 | 6.8 | 5.5 | 155 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-04-19 12:30 | 6.7 | 5.5 | 152.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-04-19 13:30 | 6.9 | 5.2 | 150 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-04-19 14:30 | 6.7 | 5.2 | 150 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-04-19 15:30 | 6.2 | 5.5 | 150 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-04-19 16:30 | 6 | 5.8 | 152.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-04-19 17:30 | 6 | 6.1 | 157.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-04-19 18:30 | 6 | 6.5 | 160 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-04-19 19:30 | 5.9 | 6.7 | 160 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-04-19 20:30 | 5.9 | 6.5 | 162.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-04-19 21:30 | 5.8 | 6.3 | 167.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-04-19 22:30 | 5.7 | 6.6 | 167.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-04-19 23:30 | 5.7 | 7.1 | 162.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-04-20 00:30 | 5.6 | 7.3 | 162.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-04-20 01:30 | 5.5 | 7.7 | 165 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-04-20 02:30 | 5.5 | 8 | 162.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-20 03:30 | 5.2 | 8 | 157.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-04-20 04:30 | 5.2 | 8 | 155 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-04-20 05:30 | 5.2 | 8 | 155 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-04-20 06:30 | 5.2 | 7.7 | 152.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-20 07:30 | 6.2 | 7.2 | 147.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-04-20 08:30 | 6.9 | 6.8 | 145 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-04-20 09:30 | 7.2 | 6.7 | 147.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-04-20 10:30 | 7.2 | 6.7 | 147.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-04-20 11:30 | 7.3 | 7.1 | 145 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-04-20 12:30 | 7 | 7.8 | 147.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-04-20 13:30 | 6.1 | 8.1 | 150 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-20 14:30 | 5.8 | 8 | 150 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-04-20 15:30 | 5.7 | 8 | 150 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-04-20 16:30 | 5.5 | 8.2 | 150 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-04-20 17:30 | 5.5 | 8.5 | 150 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-20 18:30 | 5.4 | 8.5 | 150 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-04-20 19:30 | 5.1 | 8.6 | 150 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-04-20 20:30 | 4.8 | 8.8 | 150 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-04-20 21:30 | 4.9 | 8.6 | 150 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-04-20 22:30 | 4.9 | 8.2 | 147.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-20 23:30 | 4.8 | 7.8 | 145 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-21 00:30 | 4.8 | 7.8 | 147.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-04-21 01:30 | 4.8 | 8 | 150 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-21 02:30 | 4.8 | 7.6 | 150 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-21 03:30 | 5 | 6.9 | 150 | 300 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-04-21 04:30 | 5 | 6.7 | 150 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-04-21 05:30 | 5 | 6.9 | 150 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-04-21 06:30 | 5.1 | 7.4 | 150 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-04-21 07:30 | 5.1 | 7.6 | 150 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-04-21 08:30 | 5.2 | 7.3 | 150 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-04-21 09:30 | 5.6 | 7.1 | 150 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-04-21 10:30 | 5.6 | 6.7 | 150 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-04-21 11:30 | 6 | 6.3 | 150 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-04-21 12:30 | 6.2 | 6.2 | 150 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-04-21 13:30 | 5.9 | 6.2 | 152.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-04-21 14:30 | 5.8 | 6 | 157.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-04-21 15:30 | 5.7 | 5.8 | 160 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-04-21 16:30 | 5.7 | 5.7 | 160 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-04-21 17:30 | 5.7 | 5.5 | 160 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-04-21 18:30 | 5.7 | 5.4 | 157.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-04-21 19:30 | 5.7 | 5.4 | 152.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-04-21 20:30 | 5.8 | 5.4 | 155 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-04-21 21:30 | 5.8 | 5.6 | 165 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-04-21 22:30 | 5.6 | 6.1 | 170 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-04-21 23:30 | 5.5 | 6.9 | 172.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-04-22 00:30 | 5.5 | 7.7 | 177.5 | 500 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-04-22 01:30 | 5.3 | 8 | 180 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-22 02:30 | 5.1 | 8 | 180 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-04-22 03:30 | 4.9 | 8.3 | 177.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-04-22 04:30 | 4.5 | 8.6 | 175 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-22 05:30 | 4.3 | 8.8 | 177.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-04-22 06:30 | 4.5 | 8.8 | 180 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-04-22 07:30 | 4.9 | 8.4 | 182.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-22 08:30 | 5 | 7.8 | 187.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-22 09:30 | 5.1 | 7.5 | 187.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-04-22 10:30 | 5.3 | 7.5 | 182.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-04-22 11:30 | 5.8 | 7.2 | 177.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-04-22 12:30 | 6.2 | 6.8 | 175 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-04-22 13:30 | 6.2 | 6.8 | 180 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-04-22 14:30 | 6.4 | 7.2 | 187.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-04-22 15:30 | 6.7 | 7.3 | 192.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-04-22 16:30 | 6.6 | 6.9 | 200 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-04-22 17:30 | 6.8 | 6.7 | 207.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-04-22 18:30 | 6.7 | 6.7 | 210 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-04-22 19:30 | 6.3 | 6.3 | 212.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-04-22 20:30 | 6.1 | 4.9 | 227.5 | 80 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-04-22 21:30 | 6 | 3 | 250 | 0 | 40 | 0 | 280 |  | 134.4 |  | 40
Lerwick | 1978-04-22 22:30 | 6 | 2.4 | 265 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-22 23:30 | 6 | 3 | 265 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-23 00:30 | 5.7 | 2.9 | 247.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-23 01:30 | 5.6 | 2.2 | 247.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-23 02:30 | 5.7 | 1.8 | 297.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-23 03:30 | 5.7 | 1.6 | 172.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-23 04:30 | 5.4 | 1.2 | 7.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-23 05:30 | 5.2 | 1 | 12.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-23 06:30 | 5.2 | 1.1 | 12.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-23 07:30 | 5.3 | 1.5 | 172.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-23 08:30 | 5.6 | 2 | 340 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-23 09:30 | 5.8 | 2.4 | 330 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-23 10:30 | 6.3 | 3 | 315 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-23 11:30 | 7 | 3.6 | 315 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-04-23 12:30 | 7.7 | 3.9 | 320 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-04-23 13:30 | 8.3 | 4 | 320 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-04-23 14:30 | 8.3 | 4.2 | 317.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-04-23 15:30 | 7.9 | 4.7 | 312.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-04-23 16:30 | 7.3 | 4.9 | 312.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-04-23 17:30 | 6.8 | 4.9 | 320 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-04-23 18:30 | 6.2 | 5.1 | 330 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-04-23 19:30 | 5.4 | 5.6 | 337.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-04-23 20:30 | 4.8 | 5.8 | 340 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-04-23 21:30 | 4.9 | 5.3 | 337.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-04-23 22:30 | 4.9 | 5.3 | 332.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-04-23 23:30 | 4.9 | 6.3 | 332.5 | 220 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-04-24 00:30 | 4.8 | 7 | 337.5 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-04-24 01:30 | 4.6 | 6.6 | 342.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-04-24 02:30 | 4.6 | 6.4 | 350 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-04-24 03:30 | 4.7 | 6.7 | 177.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-04-24 04:30 | 4.5 | 6.3 | 177.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-04-24 05:30 | 4.3 | 6.1 | 355 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-04-24 06:30 | 4.4 | 7 | 355 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-04-24 07:30 | 4.7 | 7.9 | 355 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-04-24 08:30 | 5.9 | 8.4 | 180 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-24 09:30 | 7.4 | 9.1 | 10 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-24 10:30 | 7.7 | 9.7 | 20 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-24 11:30 | 7.7 | 9.7 | 25 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-04-24 12:30 | 7.9 | 9.1 | 22.5 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-24 13:30 | 8 | 9 | 20 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-04-24 14:30 | 8 | 9.3 | 20 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-04-24 15:30 | 7.6 | 9 | 20 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-04-24 16:30 | 7.4 | 8.8 | 17.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-04-24 17:30 | 7.1 | 8.4 | 12.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-24 18:30 | 6.1 | 8 | 10 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-04-24 19:30 | 5.2 | 8 | 10 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-04-24 20:30 | 4.7 | 7.7 | 7.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-24 21:30 | 4.3 | 7.3 | 2.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-04-24 22:30 | 4 | 6.9 | 177.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-04-24 23:30 | 3.8 | 6.5 | 352.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-04-25 00:30 | 3.8 | 6.7 | 350 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-04-25 01:30 | 3.4 | 7.1 | 350 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-04-25 02:30 | 2.9 | 7.1 | 350 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-04-25 03:30 | 2 | 6.8 | 350 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-04-25 04:30 | 1.6 | 6.9 | 350 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-04-25 05:30 | 2.1 | 7.6 | 352.5 | 500 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-04-25 06:30 | 2.5 | 8.1 | 177.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-25 07:30 | 1.6 | 7.8 | 7.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-25 08:30 | 1 | 7.2 | 20 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-04-25 09:30 | 1.2 | 7.3 | 22.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-04-25 10:30 | 2.1 | 8.2 | 25 | 635 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-25 11:30 | 2.1 | 8.8 | 35 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-25 12:30 | 1.8 | 8.6 | 40 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-04-25 13:30 | 3 | 8.1 | 37.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-25 14:30 | 3.3 | 7.2 | 32.5 | 400 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-25 15:30 | 3.4 | 6.4 | 27.5 | 220 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-04-25 16:30 | 3.1 | 5.9 | 15 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-04-25 17:30 | 2.3 | 5.3 | 170 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-04-25 18:30 | 1.4 | 4.7 | 325 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-04-25 19:30 | 0.9 | 4.4 | 305 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-04-25 20:30 | 0.5 | 4.4 | 287.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-04-25 21:30 | 0 | 4.1 | 277.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-04-25 22:30 | 0 | 3.9 | 272.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-04-25 23:30 | 0.1 | 3 | 292.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-04-26 00:30 | 0.1 | 1.7 | 195 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-26 01:30 | -0.5 | 1.7 | 130 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-26 02:30 | -0.9 | 2.1 | 197.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-26 03:30 | -0.4 | 2.1 | 202.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-26 04:30 | -0.3 | 2.6 | 182.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-26 05:30 | 0.1 | 3.5 | 160 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-04-26 06:30 | 1.2 | 4.1 | 145 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-04-26 07:30 | 2.3 | 4.4 | 135 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-04-26 08:30 | 3.6 | 4.5 | 127.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-04-26 09:30 | 4.1 | 4.5 | 122.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-04-26 10:30 | 4.6 | 4.7 | 115 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-04-26 11:30 | 5 | 5.1 | 102.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-04-26 12:30 | 4.8 | 5.6 | 92.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-04-26 13:30 | 5.1 | 6.1 | 87.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-04-26 14:30 | 5.7 | 6.5 | 80 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-04-26 15:30 | 5.7 | 6.3 | 77.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-04-26 16:30 | 5.2 | 5.6 | 87.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-04-26 17:30 | 4.9 | 5.5 | 97.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-04-26 18:30 | 4.6 | 5.7 | 100 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-04-26 19:30 | 4.1 | 5.5 | 100 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-04-26 20:30 | 3.8 | 5.2 | 100 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-04-26 21:30 | 3.4 | 4.7 | 97.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-04-26 22:30 | 2.7 | 4.7 | 90 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-04-26 23:30 | 2.6 | 5.3 | 80 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-04-27 00:30 | 2.8 | 5.3 | 70 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-04-27 01:30 | 2.6 | 4.9 | 62.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-04-27 02:30 | 2.7 | 5.1 | 55 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-04-27 03:30 | 2.9 | 5.6 | 45 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-04-27 04:30 | 2.9 | 5.9 | 42.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-04-27 05:30 | 2.4 | 5.8 | 50 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-04-27 06:30 | 2.8 | 5.9 | 57.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-04-27 07:30 | 3.8 | 6.3 | 60 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-04-27 08:30 | 4.3 | 6.5 | 55 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-04-27 09:30 | 4.5 | 6.5 | 45 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-04-27 10:30 | 3.9 | 6.3 | 40 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-04-27 11:30 | 4.1 | 6.4 | 42.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-04-27 12:30 | 4.9 | 6.9 | 47.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-04-27 13:30 | 5 | 7.1 | 52.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-04-27 14:30 | 5.3 | 6.4 | 60 | 220 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-04-27 15:30 | 5.5 | 5.4 | 72.5 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-04-27 16:30 | 5.4 | 4.5 | 85 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-04-27 17:30 | 5.1 | 3.8 | 92.5 | 25 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-04-27 18:30 | 4.6 | 3.4 | 97.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-04-27 19:30 | 3.9 | 2.7 | 85 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-27 20:30 | 3 | 1.9 | 67.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-27 21:30 | 2.3 | 2.4 | 77.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-27 22:30 | 2.4 | 3.5 | 90 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-04-27 23:30 | 2.4 | 3.9 | 87.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-04-28 00:30 | 2.3 | 3.9 | 82.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-04-28 01:30 | 2.3 | 3.9 | 80 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-04-28 02:30 | 2.2 | 4.2 | 80 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-04-28 03:30 | 2.4 | 4.5 | 80 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-04-28 04:30 | 2.7 | 4.7 | 80 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-04-28 05:30 | 3 | 5.3 | 77.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-04-28 06:30 | 3.6 | 6.2 | 72.5 | 220 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-04-28 07:30 | 4.4 | 7.1 | 70 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-04-28 08:30 | 5.3 | 7.8 | 67.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-04-28 09:30 | 5.8 | 8.3 | 62.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-28 10:30 | 5.7 | 8.2 | 60 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-04-28 11:30 | 5.3 | 7.7 | 62.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-04-28 12:30 | 5.6 | 7.3 | 67.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-04-28 13:30 | 6.6 | 6.8 | 82.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-04-28 14:30 | 6.4 | 5.9 | 110 | 150 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-04-28 15:30 | 6.2 | 5.1 | 122.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-04-28 16:30 | 6.6 | 4.7 | 115 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-04-28 17:30 | 6.2 | 4.5 | 110 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-04-28 18:30 | 5.5 | 4.4 | 107.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-04-28 19:30 | 4.7 | 4.1 | 102.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-04-28 20:30 | 3.9 | 3.7 | 100 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-04-28 21:30 | 3.5 | 3.4 | 100 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-04-28 22:30 | 3.4 | 2.7 | 100 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-28 23:30 | 3.1 | 1.5 | 75 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-29 00:30 | 2.8 | 0.4 | 25 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-29 01:30 | 2.4 | 0 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-29 02:30 | 2.3 | 0 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-29 03:30 | 1.9 | 0 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-29 04:30 | 1.1 | 0 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-29 05:30 | 0.5 | 0.4 | 10 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-29 06:30 | 2 | 1.7 | 30 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-29 07:30 | 4.1 | 3.5 | 42.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-04-29 08:30 | 5 | 4.9 | 50 | 80 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-04-29 09:30 | 5.7 | 5.1 | 57.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-04-29 10:30 | 5.8 | 4.6 | 62.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-04-29 11:30 | 5.8 | 4.2 | 67.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-04-29 12:30 | 6 | 3.9 | 70 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-04-29 13:30 | 6.5 | 3.7 | 72.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-04-29 14:30 | 6.9 | 3.4 | 75 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-04-29 15:30 | 6.8 | 3 | 72.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-29 16:30 | 6.3 | 2.6 | 80 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-29 17:30 | 5.9 | 2.6 | 100 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-29 18:30 | 5.7 | 2.4 | 107.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-29 19:30 | 5 | 2 | 95 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-29 20:30 | 3.8 | 1.5 | 42.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-29 21:30 | 2.9 | 1.4 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-29 22:30 | 2.6 | 1.5 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-29 23:30 | 2.5 | 1.8 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-30 00:30 | 2.7 | 2.1 | 22.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-30 01:30 | 2.4 | 1.7 | 27.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-30 02:30 | 2.1 | 1.1 | 7.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-30 03:30 | 2.2 | 1 | 12.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-30 04:30 | 2 | 1 | 30 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-30 05:30 | 2 | 1.8 | 45 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-04-30 06:30 | 2.7 | 3.7 | 55 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-04-30 07:30 | 4.4 | 5.4 | 57.5 | 110 | 67.5 | 0 | 252.5 |  | 121.2 |  | 67.5
Lerwick | 1978-04-30 08:30 | 5.9 | 6.1 | 50 | 220 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-04-30 09:30 | 6.6 | 6.7 | 45 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-04-30 10:30 | 6.9 | 7 | 45 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-04-30 11:30 | 7.2 | 7 | 45 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-04-30 12:30 | 7.8 | 7.1 | 50 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-04-30 13:30 | 7.8 | 7.2 | 57.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-04-30 14:30 | 7.5 | 7.2 | 62.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-04-30 15:30 | 7.4 | 6.9 | 67.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-04-30 16:30 | 7.3 | 6 | 70 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-04-30 17:30 | 6.6 | 5.1 | 67.5 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-04-30 18:30 | 6.2 | 4.9 | 62.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-04-30 19:30 | 5.8 | 5 | 60 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-04-30 20:30 | 5 | 5.2 | 60 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-04-30 21:30 | 4.5 | 5.2 | 60 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-04-30 22:30 | 4.2 | 4.7 | 57.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-04-30 23:30 | 3.9 | 4 | 50 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-01 00:30 | 3.5 | 3.4 | 42.5 | 0 | 30 | 0 | 290 |  | 139.2 | 65311.2 | 30 | 102015
Lerwick | 1978-05-01 01:30 | 3.2 | 3.6 | 40 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-05-01 02:30 | 3.4 | 4.4 | 40 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-01 03:30 | 3.5 | 5.1 | 40 | 110 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-05-01 04:30 | 3.6 | 5.6 | 42.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-05-01 05:30 | 4 | 6.1 | 47.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-05-01 06:30 | 4.2 | 6.7 | 50 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-05-01 07:30 | 5.1 | 7.1 | 50 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-05-01 08:30 | 5.8 | 7.2 | 50 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-05-01 09:30 | 6.3 | 7.2 | 50 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-05-01 10:30 | 6.6 | 7.2 | 50 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-05-01 11:30 | 6.7 | 7.1 | 52.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-05-01 12:30 | 7 | 6.6 | 55 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-05-01 13:30 | 7.1 | 5.9 | 50 | 150 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-05-01 14:30 | 6.7 | 5.5 | 42.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-05-01 15:30 | 6.7 | 5.2 | 42.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-05-01 16:30 | 6.4 | 5 | 45 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-05-01 17:30 | 5.8 | 5.2 | 35 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-05-01 18:30 | 5.3 | 5.4 | 20 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-05-01 19:30 | 4.9 | 4.9 | 10 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-05-01 20:30 | 4.2 | 4.7 | 180 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-05-01 21:30 | 3.4 | 5.1 | 355 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-05-01 22:30 | 2.6 | 5.5 | 352.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-05-01 23:30 | 1.7 | 5.3 | 352.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-05-02 00:30 | 1.4 | 4.4 | 182.5 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-05-02 01:30 | 2.2 | 3.9 | 10 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-02 02:30 | 2.9 | 3.9 | 182.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-05-02 03:30 | 2.7 | 4.1 | 355 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-02 04:30 | 2.6 | 4.4 | 355 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-02 05:30 | 2.4 | 4.2 | 180 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-02 06:30 | 2.4 | 4 | 15 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-02 07:30 | 3.3 | 4.2 | 25 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-02 08:30 | 4.6 | 4.7 | 27.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-02 09:30 | 4.8 | 5.2 | 35 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-05-02 10:30 | 5.3 | 5.5 | 40 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-05-02 11:30 | 6.4 | 5.5 | 42.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-05-02 12:30 | 6.3 | 5.4 | 50 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-05-02 13:30 | 6.4 | 5.1 | 52.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-05-02 14:30 | 6.5 | 4.6 | 45 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-05-02 15:30 | 6.3 | 4.4 | 45 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-02 16:30 | 6.1 | 4.4 | 55 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-02 17:30 | 5.6 | 4 | 60 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-02 18:30 | 5.3 | 3.3 | 57.5 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-05-02 19:30 | 5 | 2.9 | 55 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-02 20:30 | 4.7 | 2.4 | 50 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-02 21:30 | 4.2 | 1.8 | 22.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-02 22:30 | 4.1 | 1.2 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-02 23:30 | 4.1 | 0.7 | 25 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-03 00:30 | 3.9 | 0.2 | 25 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-03 01:30 | 3.9 | 0.2 | 170 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-03 02:30 | 3.6 | 0.7 | 327.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-03 03:30 | 3.3 | 0.7 | 325 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-03 04:30 | 3.5 | 0.7 | 207.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-03 05:30 | 3.6 | 1.6 | 120 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-03 06:30 | 3.9 | 2.6 | 160 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-03 07:30 | 4.5 | 3.5 | 157.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-05-03 08:30 | 5 | 4.1 | 152.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-03 09:30 | 5.6 | 4.6 | 152.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-03 10:30 | 6.3 | 5.1 | 157.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-05-03 11:30 | 6.7 | 5.4 | 160 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-05-03 12:30 | 6.3 | 5.1 | 157.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-05-03 13:30 | 6.3 | 4.9 | 152.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-05-03 14:30 | 6.6 | 4.9 | 155 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-05-03 15:30 | 6.3 | 4.9 | 162.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-05-03 16:30 | 5.7 | 4.7 | 162.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-05-03 17:30 | 5.7 | 4.4 | 157.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-03 18:30 | 5.7 | 4.1 | 150 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-03 19:30 | 5 | 3.9 | 140 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-03 20:30 | 4.1 | 3.9 | 127.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-05-03 21:30 | 3.8 | 4.2 | 117.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-03 22:30 | 3.9 | 4.7 | 115 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-03 23:30 | 4.1 | 4.9 | 115 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-05-04 00:30 | 4.4 | 5.3 | 115 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-05-04 01:30 | 4.6 | 5.7 | 115 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-05-04 02:30 | 4.8 | 5.7 | 117.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-05-04 03:30 | 4.8 | 5.7 | 117.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-05-04 04:30 | 4.7 | 5.5 | 112.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-05-04 05:30 | 4.6 | 5.4 | 112.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-05-04 06:30 | 4.5 | 5.5 | 115 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-05-04 07:30 | 4.4 | 5.8 | 107.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-05-04 08:30 | 4.6 | 6.5 | 95 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-05-04 09:30 | 4.8 | 7.8 | 90 | 500 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-05-04 10:30 | 5.5 | 8.9 | 90 | 770 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-05-04 11:30 | 6.5 | 9.6 | 95 | 1025 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-04 12:30 | 6.8 | 9.9 | 105 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-05-04 13:30 | 6.6 | 9.5 | 105 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-05-04 14:30 | 6.2 | 9.1 | 95 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-04 15:30 | 5.4 | 8.9 | 90 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-05-04 16:30 | 4.7 | 8.6 | 90 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-05-04 17:30 | 4.7 | 8.6 | 87.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-05-04 18:30 | 4.8 | 8.9 | 85 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-05-04 19:30 | 5 | 8.9 | 87.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-05-04 20:30 | 5.2 | 8.4 | 90 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-04 21:30 | 5.5 | 7.8 | 90 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-04 22:30 | 5.6 | 7.3 | 87.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-05-04 23:30 | 5.5 | 7.3 | 80 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-05-05 00:30 | 5.5 | 7.1 | 75 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-05-05 01:30 | 5.5 | 6.3 | 75 | 220 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-05-05 02:30 | 5.5 | 6.1 | 70 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-05-05 03:30 | 5.5 | 6.7 | 62.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-05-05 04:30 | 5.4 | 7.1 | 60 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-05-05 05:30 | 5.4 | 7.3 | 60 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-05-05 06:30 | 5.7 | 7.6 | 60 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-05-05 07:30 | 6 | 7.7 | 60 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-05-05 08:30 | 6.2 | 7.9 | 57.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-05-05 09:30 | 6.4 | 8.5 | 52.5 | 770 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-05-05 10:30 | 6.6 | 9.2 | 50 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-05-05 11:30 | 7.1 | 9.7 | 50 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-05 12:30 | 7.4 | 10.1 | 50 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-05 13:30 | 7.5 | 10.1 | 50 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-05-05 14:30 | 7.3 | 9.9 | 50 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-05 15:30 | 6.8 | 9.4 | 50 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-05 16:30 | 6.7 | 8.3 | 50 | 635 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-05 17:30 | 6.5 | 7.3 | 52.5 | 400 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-05 18:30 | 6.5 | 6.8 | 60 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-05-05 19:30 | 6.5 | 6.8 | 67.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-05-05 20:30 | 6.4 | 7.1 | 67.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-05-05 21:30 | 6.2 | 7.1 | 60 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-05-05 22:30 | 6 | 6.7 | 55 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-05-05 23:30 | 5.9 | 6.5 | 57.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-05-06 00:30 | 5.8 | 6.7 | 60 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-05-06 01:30 | 5.6 | 6.5 | 57.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-05-06 02:30 | 5.6 | 6.5 | 55 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-05-06 03:30 | 5.7 | 6.8 | 57.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-05-06 04:30 | 5.6 | 7.1 | 60 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-05-06 05:30 | 5.5 | 7.1 | 60 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-05-06 06:30 | 5.6 | 6.7 | 60 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-05-06 07:30 | 6.1 | 6 | 55 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-05-06 08:30 | 6.5 | 5.5 | 47.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-05-06 09:30 | 7 | 5.6 | 50 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-05-06 10:30 | 8.2 | 6.4 | 57.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-05-06 11:30 | 8.8 | 7.2 | 62.5 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-05-06 12:30 | 8.9 | 7.2 | 67.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-05-06 13:30 | 9.3 | 7 | 70 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-05-06 14:30 | 9.5 | 7 | 72.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-05-06 15:30 | 9.3 | 6.8 | 80 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-05-06 16:30 | 8.8 | 6.2 | 85 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-05-06 17:30 | 8.5 | 4.8 | 75 | 80 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-05-06 18:30 | 8.1 | 3.9 | 55 | 25 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-05-06 19:30 | 7.5 | 4.2 | 52.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-06 20:30 | 7.3 | 4.2 | 47.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-06 21:30 | 7.5 | 3 | 195 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-05-06 22:30 | 6.5 | 2.4 | 352.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-06 23:30 | 5.2 | 2.9 | 192.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-07 00:30 | 5.3 | 3.3 | 42.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-07 01:30 | 6.2 | 3.4 | 32.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-07 02:30 | 5.8 | 3.8 | 20 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-05-07 03:30 | 5.3 | 4 | 27.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-07 04:30 | 5.6 | 3.5 | 30 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-07 05:30 | 5.7 | 2.9 | 35 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-05-07 06:30 | 6.4 | 3.3 | 45 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-07 07:30 | 7.6 | 3.9 | 50 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-05-07 08:30 | 8.8 | 4.2 | 55 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-07 09:30 | 9.7 | 4.7 | 67.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-07 10:30 | 11 | 4.7 | 90 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-05-07 11:30 | 11.6 | 4.4 | 120 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-07 12:30 | 11.2 | 4.4 | 140 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-07 13:30 | 11 | 4.5 | 147.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-07 14:30 | 11 | 4.4 | 150 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-07 15:30 | 10.7 | 4.1 | 150 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-07 16:30 | 10.7 | 3.6 | 150 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-07 17:30 | 10.6 | 3 | 145 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-05-07 18:30 | 9.9 | 2.4 | 132.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-07 19:30 | 9.5 | 1.7 | 107.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-07 20:30 | 8.9 | 1.1 | 92.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-07 21:30 | 8 | 1.6 | 112.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-07 22:30 | 7 | 2.7 | 130 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-07 23:30 | 7 | 3.3 | 130 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-08 00:30 | 7.1 | 3.6 | 132.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-05-08 01:30 | 7.3 | 3.3 | 140 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-05-08 02:30 | 7.4 | 2 | 187.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-08 03:30 | 6.3 | 1.1 | 275 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-08 04:30 | 5.3 | 1 | 335 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-08 05:30 | 5.2 | 1 | 182.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-08 06:30 | 7 | 1.8 | 22.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-08 07:30 | 9.2 | 3.3 | 35 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-08 08:30 | 9.6 | 4.5 | 37.5 | 80 | 40 | 0 | 280 |  | 134.4 |  | 40
Lerwick | 1978-05-08 09:30 | 10.1 | 5.8 | 32.5 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-05-08 10:30 | 11.7 | 7.1 | 30 | 400 | 275 | 0 | 45 |  | 21.6 |  | 275
Lerwick | 1978-05-08 11:30 | 11.7 | 7.5 | 30 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-05-08 12:30 | 10.7 | 7.2 | 30 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-05-08 13:30 | 11 | 6.7 | 30 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-05-08 14:30 | 10.9 | 6.3 | 30 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-05-08 15:30 | 10 | 6.3 | 30 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-05-08 16:30 | 9.1 | 6.5 | 30 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-05-08 17:30 | 8.3 | 6.5 | 27.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-05-08 18:30 | 8.1 | 6.3 | 22.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-05-08 19:30 | 7.8 | 6.2 | 20 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-05-08 20:30 | 7 | 6.2 | 17.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-05-08 21:30 | 6.1 | 6.3 | 12.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-05-08 22:30 | 5.5 | 6.5 | 7.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-05-08 23:30 | 5.2 | 6.8 | 2.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-05-09 00:30 | 4.5 | 7.2 | 0 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-05-09 01:30 | 4 | 7.7 | 0 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-05-09 02:30 | 4.2 | 8 | 2.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-09 03:30 | 5.2 | 8.1 | 7.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-05-09 04:30 | 6.2 | 8.3 | 10 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-05-09 05:30 | 6.6 | 8.6 | 12.5 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-09 06:30 | 7.4 | 8.9 | 17.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-05-09 07:30 | 8.5 | 9.1 | 20 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-05-09 08:30 | 9.6 | 9 | 22.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-05-09 09:30 | 10.5 | 8.6 | 27.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-05-09 10:30 | 11 | 8.6 | 30 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-05-09 11:30 | 11.4 | 8.4 | 30 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-09 12:30 | 11.9 | 7.9 | 30 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-09 13:30 | 12 | 7.6 | 30 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-05-09 14:30 | 12.6 | 7.2 | 27.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-05-09 15:30 | 12.7 | 6.8 | 25 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-05-09 16:30 | 11.5 | 6.8 | 27.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-05-09 17:30 | 10.3 | 7 | 30 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-05-09 18:30 | 8.8 | 6.8 | 30 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-05-09 19:30 | 7.5 | 6.8 | 30 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-05-09 20:30 | 6.7 | 7.2 | 27.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-05-09 21:30 | 6.4 | 7.3 | 22.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-05-09 22:30 | 6.4 | 6.9 | 20 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-05-09 23:30 | 6.3 | 6.4 | 22.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-05-10 00:30 | 6.1 | 5.8 | 22.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-05-10 01:30 | 5.8 | 5.1 | 15 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-05-10 02:30 | 5.3 | 4.4 | 7.5 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-05-10 03:30 | 5 | 3.8 | 7.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-10 04:30 | 5.4 | 3.7 | 17.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-05-10 05:30 | 5.8 | 3.9 | 30 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-05-10 06:30 | 6 | 3.9 | 37.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-05-10 07:30 | 6.6 | 3.6 | 47.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-05-10 08:30 | 7.3 | 3.3 | 70 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-05-10 09:30 | 7.9 | 3.6 | 102.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-05-10 10:30 | 8.4 | 4.4 | 135 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-10 11:30 | 8.6 | 5.3 | 157.5 | 110 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-05-10 12:30 | 8.4 | 6.2 | 167.5 | 220 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-05-10 13:30 | 9.1 | 7.1 | 170 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-05-10 14:30 | 9.5 | 7.6 | 172.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-05-10 15:30 | 9.1 | 7.7 | 177.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-05-10 16:30 | 8.4 | 7.7 | 182.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-05-10 17:30 | 7.8 | 7.8 | 185 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-05-10 18:30 | 7.5 | 8 | 182.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-10 19:30 | 7.4 | 7.8 | 177.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-10 20:30 | 7.2 | 7.8 | 172.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-05-10 21:30 | 7.2 | 8.2 | 170 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-10 22:30 | 7.2 | 8.5 | 172.5 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-10 23:30 | 7.1 | 8.6 | 177.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-05-11 00:30 | 6.9 | 9.3 | 180 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-05-11 01:30 | 6.8 | 10.3 | 180 | 1150 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-05-11 02:30 | 6.7 | 11.1 | 180 | 1340 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-05-11 03:30 | 6.6 | 11.9 | 180 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-05-11 04:30 | 6.5 | 12.6 | 180 | 1470 | 1435 | 1115 | 0 |  | 0 |  | 320
Lerwick | 1978-05-11 05:30 | 6.4 | 12.7 | 180 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-05-11 06:30 | 6.4 | 12.4 | 180 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-05-11 07:30 | 6.3 | 12.2 | 180 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-05-11 08:30 | 6.5 | 11.2 | 182.5 | 1340 | 1395 | 1075 | 0 |  | 0 |  | 320
Lerwick | 1978-05-11 09:30 | 6.8 | 9.5 | 192.5 | 1025 | 1182.5 | 862.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-11 10:30 | 6.9 | 7.8 | 205 | 500 | 762.5 | 442.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-11 11:30 | 7.1 | 7.1 | 217.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-05-11 12:30 | 7.2 | 7 | 232.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-05-11 13:30 | 7.1 | 7 | 235 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-05-11 14:30 | 7.2 | 7.5 | 225 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-05-11 15:30 | 7.6 | 8.4 | 222.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-11 16:30 | 7.9 | 8.8 | 227.5 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-11 17:30 | 8.1 | 8.4 | 232.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-11 18:30 | 8 | 7.5 | 237.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-11 19:30 | 7.5 | 6.6 | 240 | 300 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-05-11 20:30 | 7.1 | 6.2 | 240 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-05-11 21:30 | 6.9 | 6.2 | 240 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-05-11 22:30 | 6.8 | 5.9 | 240 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-05-11 23:30 | 6.8 | 5.3 | 242.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-05-12 00:30 | 6.5 | 4.9 | 245 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-05-12 01:30 | 6 | 4.9 | 240 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-05-12 02:30 | 5.8 | 4.4 | 235 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-12 03:30 | 5.4 | 3.9 | 235 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-12 04:30 | 5.3 | 4.1 | 230 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-12 05:30 | 5.5 | 5 | 222.5 | 110 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-05-12 06:30 | 5.9 | 5.8 | 220 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-05-12 07:30 | 6.4 | 5.8 | 220 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-05-12 08:30 | 6.9 | 5.7 | 217.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-05-12 09:30 | 7.2 | 5.5 | 212.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-05-12 10:30 | 7.5 | 5.2 | 197.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-05-12 11:30 | 8 | 4.9 | 167.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-05-12 12:30 | 7.6 | 4.7 | 150 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-05-12 13:30 | 6.7 | 4.4 | 152.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-12 14:30 | 7 | 4 | 150 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-12 15:30 | 7.4 | 3.4 | 142.5 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-05-12 16:30 | 7.4 | 3.3 | 137.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-12 17:30 | 7.4 | 3 | 130 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-12 18:30 | 7.3 | 2.4 | 120 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-12 19:30 | 7.1 | 2 | 105 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-12 20:30 | 6.7 | 1.5 | 77.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-12 21:30 | 6 | 1.1 | 40 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-12 22:30 | 5.2 | 0.7 | 10 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-12 23:30 | 5 | 0.2 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-13 00:30 | 4.9 | 0 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-13 01:30 | 4.8 | 0 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-13 02:30 | 5.1 | 0 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-13 03:30 | 5.3 | 0.2 | 155 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-13 04:30 | 5.3 | 0.9 | 287.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-13 05:30 | 5.6 | 1.7 | 237.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-13 06:30 | 6.1 | 2.3 | 177.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-13 07:30 | 6.5 | 2.6 | 142.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-13 08:30 | 7.2 | 2.8 | 145 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-13 09:30 | 7.9 | 3.5 | 152.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-05-13 10:30 | 8.7 | 4.1 | 155 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-13 11:30 | 9.2 | 4.4 | 155 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-13 12:30 | 9.2 | 4.7 | 152.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-13 13:30 | 9.3 | 4.9 | 155 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-05-13 14:30 | 9.2 | 5.2 | 165 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-05-13 15:30 | 8.9 | 5.4 | 170 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-05-13 16:30 | 8.1 | 5.1 | 167.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-05-13 17:30 | 7.3 | 4.6 | 157.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-05-13 18:30 | 6.9 | 4.2 | 150 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-13 19:30 | 6.5 | 4.2 | 160 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-13 20:30 | 6.5 | 4.7 | 175 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-13 21:30 | 6.3 | 4.9 | 177.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-05-13 22:30 | 6.3 | 5.4 | 172.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-05-13 23:30 | 6.4 | 6.3 | 170 | 220 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-05-14 00:30 | 6.3 | 6.9 | 170 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-05-14 01:30 | 6.1 | 7.3 | 167.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-05-14 02:30 | 6 | 7.6 | 165 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-05-14 03:30 | 6.1 | 7.7 | 167.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-05-14 04:30 | 6 | 7.6 | 170 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-05-14 05:30 | 5.9 | 7.2 | 172.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-05-14 06:30 | 6 | 6.7 | 177.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-05-14 07:30 | 6.1 | 6.4 | 177.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-05-14 08:30 | 6.2 | 6.4 | 172.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-05-14 09:30 | 6.4 | 6.4 | 167.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-05-14 10:30 | 7.3 | 6.5 | 162.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-05-14 11:30 | 8.5 | 6.5 | 157.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-05-14 12:30 | 7.9 | 6.3 | 152.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-05-14 13:30 | 7.6 | 6.2 | 150 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-05-14 14:30 | 8.6 | 6.2 | 150 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-05-14 15:30 | 8.4 | 6.2 | 150 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-05-14 16:30 | 7.9 | 6.2 | 152.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-05-14 17:30 | 8.1 | 6 | 155 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-05-14 18:30 | 7.9 | 5.4 | 152.5 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-05-14 19:30 | 7.3 | 4.7 | 150 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-05-14 20:30 | 6.7 | 4.5 | 150 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-05-14 21:30 | 5.9 | 4.5 | 150 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-05-14 22:30 | 5.4 | 4.7 | 150 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-05-14 23:30 | 5.6 | 4.9 | 147.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-05-15 00:30 | 5.5 | 4.6 | 145 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-05-15 01:30 | 5.4 | 4.2 | 147.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-15 02:30 | 5.2 | 4 | 150 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-15 03:30 | 5 | 4 | 150 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-15 04:30 | 5.1 | 4 | 152.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-15 05:30 | 5.6 | 4.2 | 155 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-15 06:30 | 6.1 | 4.6 | 152.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-15 07:30 | 6.6 | 4.9 | 150 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-05-15 08:30 | 7.7 | 5 | 150 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-05-15 09:30 | 8.7 | 5 | 147.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-05-15 10:30 | 9 | 5 | 142.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-05-15 11:30 | 9.2 | 5.2 | 142.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-05-15 12:30 | 9.4 | 5.4 | 147.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-05-15 13:30 | 9.4 | 5.2 | 150 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-05-15 14:30 | 9 | 4.9 | 150 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-05-15 15:30 | 8.8 | 4.7 | 150 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-05-15 16:30 | 8.8 | 4.4 | 150 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-15 17:30 | 8.5 | 4.4 | 150 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-15 18:30 | 8 | 4.4 | 150 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-15 19:30 | 7.1 | 4.7 | 150 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-15 20:30 | 6.5 | 4.9 | 150 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-05-15 21:30 | 6.3 | 5.2 | 152.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-05-15 22:30 | 6.1 | 5.5 | 157.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-05-15 23:30 | 5.9 | 5.5 | 160 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-05-16 00:30 | 5.7 | 5.2 | 160 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-05-16 01:30 | 5.3 | 5.2 | 160 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-05-16 02:30 | 5.4 | 5.5 | 160 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-05-16 03:30 | 5.6 | 5.7 | 160 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-05-16 04:30 | 5.7 | 5.8 | 160 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-05-16 05:30 | 6.2 | 6.1 | 160 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-05-16 06:30 | 6.6 | 6.5 | 160 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-05-16 07:30 | 7 | 6.8 | 160 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-05-16 08:30 | 7.1 | 7.3 | 160 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-05-16 09:30 | 7.3 | 7.8 | 162.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-05-16 10:30 | 7.8 | 8 | 170 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-16 11:30 | 8 | 8.2 | 175 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-05-16 12:30 | 8.6 | 8.5 | 175 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-16 13:30 | 9 | 8.2 | 175 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-16 14:30 | 8.7 | 7.8 | 172.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-16 15:30 | 8.9 | 7.4 | 170 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-05-16 16:30 | 9.4 | 6.5 | 170 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-05-16 17:30 | 9.2 | 5.4 | 170 | 110 | 205 | 0 | 115 |  | 55.2 |  | 205
Lerwick | 1978-05-16 18:30 | 8.6 | 4.9 | 170 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-05-16 19:30 | 8 | 4.6 | 170 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-05-16 20:30 | 7.5 | 4.1 | 167.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-16 21:30 | 7.3 | 3.6 | 165 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-16 22:30 | 7.3 | 3 | 165 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-05-16 23:30 | 7.4 | 2.7 | 165 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-17 00:30 | 7.3 | 2.7 | 165 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-17 01:30 | 7.3 | 2.6 | 165 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-17 02:30 | 7.6 | 3.1 | 182.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-17 03:30 | 7.9 | 3.7 | 210 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-05-17 04:30 | 8.1 | 3.5 | 212.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-05-17 05:30 | 8.4 | 2.9 | 195 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-05-17 06:30 | 8.7 | 3 | 192.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-17 07:30 | 8.8 | 3.6 | 215 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-05-17 08:30 | 8.9 | 4.4 | 235 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-17 09:30 | 9.3 | 5.5 | 245 | 150 | 105 | 0 | 215 |  | 103.2 |  | 105
Lerwick | 1978-05-17 10:30 | 9.7 | 5.9 | 250 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-05-17 11:30 | 10.7 | 5 | 225 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-05-17 12:30 | 12 | 3.8 | 172.5 | 25 | 67.5 | 0 | 252.5 |  | 121.2 |  | 67.5
Lerwick | 1978-05-17 13:30 | 12.1 | 3.4 | 145 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-05-17 14:30 | 11.6 | 3.8 | 147.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-05-17 15:30 | 12.1 | 3.9 | 152.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-05-17 16:30 | 11.8 | 3.6 | 155 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-05-17 17:30 | 11.2 | 3 | 162.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-05-17 18:30 | 11.1 | 2.4 | 170 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-17 19:30 | 10.4 | 2.1 | 160 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-17 20:30 | 9.6 | 2.4 | 155 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-17 21:30 | 7.9 | 3 | 162.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-17 22:30 | 6.9 | 3.4 | 162.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-17 23:30 | 6.9 | 3.7 | 160 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-05-18 00:30 | 6.6 | 3.9 | 160 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-05-18 01:30 | 6.5 | 3.6 | 157.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-05-18 02:30 | 6.4 | 3.2 | 152.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-05-18 03:30 | 6.2 | 3.1 | 147.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-18 04:30 | 5.8 | 3.1 | 142.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-18 05:30 | 5.8 | 2.9 | 135 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-18 06:30 | 5.8 | 2.6 | 125 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-18 07:30 | 5.8 | 2.6 | 120 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-18 08:30 | 6 | 2.8 | 120 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-18 09:30 | 6.3 | 3.2 | 122.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-18 10:30 | 6.5 | 3 | 132.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-18 11:30 | 6.9 | 2.7 | 145 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-18 12:30 | 7.3 | 2.9 | 147.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-18 13:30 | 7.3 | 3.1 | 135 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-18 14:30 | 7.2 | 3.1 | 120 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-18 15:30 | 7.3 | 2.9 | 110 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-18 16:30 | 7.5 | 2.7 | 100 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-18 17:30 | 7.5 | 3 | 95 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-18 18:30 | 7.3 | 3.4 | 90 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-18 19:30 | 7 | 3.6 | 77.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-05-18 20:30 | 6.8 | 3.6 | 67.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-05-18 21:30 | 6.5 | 3.4 | 70 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-05-18 22:30 | 6.2 | 3.3 | 80 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-18 23:30 | 6.1 | 3.2 | 87.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-19 00:30 | 6.3 | 2.9 | 85 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-19 01:30 | 6.4 | 3.1 | 72.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-19 02:30 | 6.4 | 3.8 | 60 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-05-19 03:30 | 6.5 | 4 | 55 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-19 04:30 | 6.7 | 4 | 62.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-19 05:30 | 6.9 | 4.2 | 75 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-19 06:30 | 6.9 | 4.6 | 77.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-19 07:30 | 6.8 | 4.7 | 75 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-05-19 08:30 | 6.6 | 4.4 | 80 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-19 09:30 | 6.6 | 4.4 | 90 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-19 10:30 | 6.7 | 4.5 | 100 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-19 11:30 | 6.8 | 4.4 | 110 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-19 12:30 | 7 | 4.1 | 115 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-19 13:30 | 7.7 | 3.7 | 110 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-19 14:30 | 8.4 | 3.8 | 107.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-05-19 15:30 | 8.5 | 4.2 | 120 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-19 16:30 | 8.3 | 4.1 | 137.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-19 17:30 | 8.4 | 3.7 | 140 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-19 18:30 | 8.6 | 3.8 | 127.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-05-19 19:30 | 8.3 | 4 | 117.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-19 20:30 | 8 | 3.6 | 110 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-19 21:30 | 7.6 | 3.2 | 102.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-05-19 22:30 | 7.5 | 3.5 | 102.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-05-19 23:30 | 7.5 | 4.5 | 107.5 | 80 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-05-20 00:30 | 7.4 | 4.7 | 110 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-05-20 01:30 | 7.2 | 4 | 110 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-20 02:30 | 7 | 3.7 | 110 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-20 03:30 | 6.9 | 3.9 | 110 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-05-20 04:30 | 7.1 | 3.7 | 107.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-05-20 05:30 | 7.3 | 3.7 | 107.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-05-20 06:30 | 7.5 | 3.9 | 117.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-05-20 07:30 | 7.8 | 3.7 | 127.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-05-20 08:30 | 7.9 | 3.6 | 130 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-05-20 09:30 | 8.1 | 3.6 | 130 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-05-20 10:30 | 8.4 | 3.6 | 130 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-05-20 11:30 | 9 | 3.6 | 130 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-05-20 12:30 | 9.4 | 3.6 | 130 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-05-20 13:30 | 9.6 | 3.7 | 132.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-05-20 14:30 | 9.7 | 3.9 | 137.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-05-20 15:30 | 9.5 | 3.7 | 140 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-05-20 16:30 | 9.4 | 3.4 | 137.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-05-20 17:30 | 9.2 | 3.2 | 125 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-20 18:30 | 8.7 | 3.2 | 107.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-20 19:30 | 7.8 | 3.4 | 105 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-20 20:30 | 7.1 | 3.4 | 117.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-20 21:30 | 7 | 3 | 127.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-20 22:30 | 6.8 | 2.6 | 130 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-20 23:30 | 6.5 | 2.3 | 127.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-21 00:30 | 6.3 | 1.9 | 125 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-21 01:30 | 6.1 | 1.8 | 122.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-21 02:30 | 5.9 | 1.6 | 117.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-21 03:30 | 5.8 | 1.5 | 110 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-21 04:30 | 5.6 | 1.5 | 97.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-21 05:30 | 5.5 | 1.6 | 85 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-21 06:30 | 5.7 | 1.8 | 72.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-21 07:30 | 6.2 | 1.9 | 57.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-21 08:30 | 6.4 | 2.4 | 45 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-21 09:30 | 6.5 | 3 | 45 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-21 10:30 | 6.6 | 3.6 | 47.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-05-21 11:30 | 6.9 | 3.9 | 37.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-05-21 12:30 | 7.1 | 4 | 30 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-21 13:30 | 7.3 | 4 | 35 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-21 14:30 | 7.5 | 4.2 | 42.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-21 15:30 | 7.3 | 4.9 | 42.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-21 16:30 | 7.2 | 5.5 | 37.5 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-05-21 17:30 | 7.1 | 5.7 | 32.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-05-21 18:30 | 6.7 | 5.8 | 32.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-05-21 19:30 | 6.6 | 5.9 | 37.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-05-21 20:30 | 6.4 | 5.6 | 40 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-05-21 21:30 | 6.3 | 5.2 | 40 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-05-21 22:30 | 6.5 | 5 | 40 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-05-21 23:30 | 6.4 | 5.2 | 37.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-05-22 00:30 | 6.3 | 5.1 | 35 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-05-22 01:30 | 6.1 | 4.7 | 35 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-05-22 02:30 | 6 | 4.9 | 30 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-05-22 03:30 | 5.8 | 5.8 | 27.5 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-05-22 04:30 | 5.7 | 6.3 | 32.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-05-22 05:30 | 5.8 | 6.3 | 35 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-05-22 06:30 | 6.1 | 6 | 35 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-05-22 07:30 | 6.2 | 6 | 30 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-05-22 08:30 | 6.3 | 6.4 | 27.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-05-22 09:30 | 6.5 | 6.5 | 32.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-05-22 10:30 | 6.9 | 6.1 | 32.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-05-22 11:30 | 7.3 | 5.8 | 30 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-05-22 12:30 | 7.6 | 5.7 | 32.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-05-22 13:30 | 7.9 | 5.7 | 35 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-05-22 14:30 | 8.2 | 5.7 | 35 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-05-22 15:30 | 8.1 | 5.5 | 35 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-05-22 16:30 | 7.7 | 4.9 | 35 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-05-22 17:30 | 7.5 | 4.2 | 32.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-22 18:30 | 7.2 | 4.2 | 27.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-22 19:30 | 7 | 4.4 | 27.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-22 20:30 | 6.7 | 4.4 | 30 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-22 21:30 | 6.4 | 4.4 | 30 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-22 22:30 | 6.3 | 4.4 | 30 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-22 23:30 | 6.1 | 4.5 | 30 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-23 00:30 | 6 | 4.5 | 27.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-05-23 01:30 | 6 | 4.5 | 22.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-05-23 02:30 | 6 | 4.7 | 20 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-05-23 03:30 | 6.1 | 4.7 | 17.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-05-23 04:30 | 6.2 | 4.2 | 15 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-23 05:30 | 6.3 | 4 | 17.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-23 06:30 | 6.5 | 4.2 | 20 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-23 07:30 | 6.7 | 4.4 | 20 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-23 08:30 | 6.8 | 4.2 | 20 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-23 09:30 | 7.1 | 4.2 | 22.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-23 10:30 | 8.5 | 4.4 | 27.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-23 11:30 | 10 | 4 | 30 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-23 12:30 | 9.8 | 3.7 | 30 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-23 13:30 | 9.2 | 3.9 | 30 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-05-23 14:30 | 9.9 | 3.9 | 27.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-05-23 15:30 | 9.3 | 3.7 | 25 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-05-23 16:30 | 8.5 | 3.3 | 27.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-05-23 17:30 | 8.5 | 2.6 | 30 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-23 18:30 | 8.6 | 2.1 | 30 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-23 19:30 | 8.6 | 2.4 | 15 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-23 20:30 | 8.1 | 3.5 | 162.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-05-23 21:30 | 7.9 | 4.7 | 322.5 | 80 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-05-23 22:30 | 7.8 | 5.6 | 320 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-05-23 23:30 | 7.4 | 6.9 | 317.5 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-05-24 00:30 | 7.5 | 8.1 | 312.5 | 635 | 467.5 | 147.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-24 01:30 | 7.8 | 8.6 | 312.5 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-24 02:30 | 7.9 | 9 | 317.5 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-05-24 03:30 | 7.8 | 9.5 | 315 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-24 04:30 | 7.4 | 9.8 | 305 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-05-24 05:30 | 6.7 | 9.6 | 300 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-05-24 06:30 | 6.5 | 9.5 | 297.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-05-24 07:30 | 7 | 9.2 | 292.5 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-24 08:30 | 7.6 | 8.9 | 287.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-05-24 09:30 | 8.1 | 9.1 | 280 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-05-24 10:30 | 8.7 | 9.5 | 272.5 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-24 11:30 | 9.3 | 9.2 | 270 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-24 12:30 | 9.5 | 9 | 270 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-05-24 13:30 | 9.3 | 9 | 267.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-05-24 14:30 | 8.9 | 8.9 | 262.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-05-24 15:30 | 9.3 | 8.6 | 260 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-05-24 16:30 | 9.2 | 8.2 | 257.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-24 17:30 | 8.6 | 7.6 | 255 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-24 18:30 | 8.6 | 6.7 | 255 | 300 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-05-24 19:30 | 8.5 | 5.5 | 250 | 150 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-05-24 20:30 | 8 | 4.4 | 242.5 | 60 | 105 | 0 | 215 |  | 103.2 |  | 105
Lerwick | 1978-05-24 21:30 | 6.9 | 3.6 | 237.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-24 22:30 | 5.9 | 3.3 | 232.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-05-24 23:30 | 5.8 | 3.4 | 227.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-25 00:30 | 6 | 3.7 | 222.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-05-25 01:30 | 6.5 | 4.4 | 220 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-25 02:30 | 7.1 | 5.7 | 220 | 150 | 105 | 0 | 215 |  | 103.2 |  | 105
Lerwick | 1978-05-25 03:30 | 7.2 | 6.5 | 217.5 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-05-25 04:30 | 7.4 | 7.1 | 215 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-05-25 05:30 | 7.7 | 7.8 | 215 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-05-25 06:30 | 7.9 | 8.5 | 210 | 770 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-05-25 07:30 | 8.1 | 9.1 | 202.5 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-05-25 08:30 | 8.7 | 9 | 200 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-05-25 09:30 | 9 | 8.8 | 202.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-05-25 10:30 | 9.1 | 8.6 | 207.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-05-25 11:30 | 9 | 8.5 | 210 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-05-25 12:30 | 9 | 8.9 | 212.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-05-25 13:30 | 9.5 | 9.8 | 217.5 | 1025 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-25 14:30 | 10.6 | 10.6 | 220 | 1270 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-25 15:30 | 11.3 | 10.9 | 217.5 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-05-25 16:30 | 11 | 10.5 | 215 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-05-25 17:30 | 10.2 | 10.1 | 217.5 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-05-25 18:30 | 9.5 | 9.5 | 220 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-25 19:30 | 9.1 | 8.3 | 220 | 635 | 830 | 510 | 0 |  | 0 |  | 320
Lerwick | 1978-05-25 20:30 | 9.1 | 7.4 | 220 | 400 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-25 21:30 | 9.1 | 7.6 | 222.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-05-25 22:30 | 8.9 | 8.5 | 230 | 770 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-05-25 23:30 | 8.8 | 8.5 | 237.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-05-26 00:30 | 8.7 | 7.5 | 240 | 500 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-05-26 01:30 | 8.7 | 6.7 | 240 | 300 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-05-26 02:30 | 8.8 | 6.4 | 237.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-05-26 03:30 | 9.1 | 6.1 | 232.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-05-26 04:30 | 9.3 | 6 | 230 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-05-26 05:30 | 9.1 | 6.8 | 230 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-05-26 06:30 | 9.1 | 8 | 230 | 635 | 467.5 | 147.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-26 07:30 | 9.6 | 8.6 | 225 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-26 08:30 | 10.3 | 8.8 | 212.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-05-26 09:30 | 10.5 | 8.1 | 200 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-26 10:30 | 11 | 6.6 | 192.5 | 300 | 467.5 | 147.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-26 11:30 | 11 | 5.5 | 187.5 | 150 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-05-26 12:30 | 10.7 | 5.8 | 190 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-05-26 13:30 | 11.5 | 6.8 | 205 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-05-26 14:30 | 11.5 | 7.8 | 217.5 | 500 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-05-26 15:30 | 10.9 | 8.1 | 222.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-26 16:30 | 10.7 | 7.6 | 227.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-26 17:30 | 10.5 | 6.3 | 230 | 220 | 360 | 40 | 0 |  | 0 |  | 320
Lerwick | 1978-05-26 18:30 | 10.2 | 4.9 | 222.5 | 80 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-05-26 19:30 | 9.6 | 4.4 | 212.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-26 20:30 | 9.3 | 4.7 | 217.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-26 21:30 | 9.2 | 4.4 | 225 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-26 22:30 | 8.9 | 3.7 | 220 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-26 23:30 | 8.9 | 4.5 | 217.5 | 80 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-05-27 00:30 | 9 | 6.3 | 222.5 | 220 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-05-27 01:30 | 9.1 | 7.4 | 222.5 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-05-27 02:30 | 9.2 | 7.6 | 222.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-05-27 03:30 | 9.1 | 7.5 | 227.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-05-27 04:30 | 9 | 7.6 | 227.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-05-27 05:30 | 9 | 7.8 | 225 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-05-27 06:30 | 9.3 | 8 | 225 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-27 07:30 | 9.6 | 8 | 225 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-05-27 08:30 | 9.8 | 7.6 | 225 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-05-27 09:30 | 10 | 7.2 | 225 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-05-27 10:30 | 10.2 | 7.4 | 225 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-05-27 11:30 | 10.6 | 7.8 | 227.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-05-27 12:30 | 10.9 | 7.8 | 230 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-05-27 13:30 | 11.5 | 7.3 | 225 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-05-27 14:30 | 11.7 | 7 | 222.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-05-27 15:30 | 11.4 | 6.8 | 227.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-05-27 16:30 | 11.2 | 6.2 | 227.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-05-27 17:30 | 11 | 5.3 | 222.5 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-05-27 18:30 | 11 | 4.7 | 217.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-05-27 19:30 | 10 | 4.5 | 215 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-05-27 20:30 | 8.7 | 4.5 | 217.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-05-27 21:30 | 8.5 | 4.4 | 217.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-27 22:30 | 8.9 | 4.4 | 215 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-27 23:30 | 9 | 4.4 | 217.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-28 00:30 | 8.9 | 4 | 220 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-28 01:30 | 9 | 3.4 | 215 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-05-28 02:30 | 9.1 | 3.3 | 210 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-28 03:30 | 9.3 | 2.7 | 202.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-28 04:30 | 9.7 | 1.8 | 182.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-28 05:30 | 9.8 | 1.6 | 165 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-28 06:30 | 9.7 | 2 | 157.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-28 07:30 | 9.5 | 2.4 | 152.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-28 08:30 | 10.2 | 3.1 | 147.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-28 09:30 | 11.2 | 4 | 150 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-05-28 10:30 | 11.2 | 4.6 | 160 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-28 11:30 | 10.7 | 5.1 | 167.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-05-28 12:30 | 10.1 | 5.6 | 165 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-05-28 13:30 | 10.1 | 5.4 | 157.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-05-28 14:30 | 11 | 4 | 170 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-05-28 15:30 | 11.7 | 2.8 | 197.5 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-05-28 16:30 | 12.5 | 2.4 | 205 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-28 17:30 | 13.4 | 2.1 | 200 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-28 18:30 | 13.3 | 1.9 | 195 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-28 19:30 | 12.3 | 1.6 | 182.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-28 20:30 | 11.9 | 1.5 | 177.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-28 21:30 | 11.7 | 1.5 | 180 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-28 22:30 | 11.7 | 1.5 | 190 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-28 23:30 | 11.9 | 1.8 | 215 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-29 00:30 | 12.1 | 2.1 | 232.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-29 01:30 | 12 | 1.7 | 222.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-29 02:30 | 11.6 | 1.1 | 205 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-29 03:30 | 10.7 | 1 | 210 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-29 04:30 | 10.3 | 1.1 | 220 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-29 05:30 | 10.8 | 1.7 | 212.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-29 06:30 | 11.3 | 2.4 | 210 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-29 07:30 | 12.1 | 3.1 | 222.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-29 08:30 | 13.7 | 4 | 232.5 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-05-29 09:30 | 14.8 | 4.2 | 225 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-29 10:30 | 15.2 | 3.5 | 192.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-29 11:30 | 15.4 | 3.3 | 162.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-05-29 12:30 | 15.5 | 4 | 157.5 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-05-29 13:30 | 15.1 | 4.5 | 160 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-29 14:30 | 15.6 | 4.2 | 162.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-29 15:30 | 16.3 | 4 | 170 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-29 16:30 | 15.5 | 4 | 175 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-29 17:30 | 14.6 | 4 | 172.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-29 18:30 | 13.8 | 4 | 172.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-29 19:30 | 12.9 | 3.8 | 177.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-29 20:30 | 12.1 | 3.6 | 177.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-05-29 21:30 | 11.4 | 3.7 | 175 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-05-29 22:30 | 10.7 | 3.2 | 180 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-05-29 23:30 | 10.4 | 1.9 | 185 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-30 00:30 | 9.9 | 1.3 | 190 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-30 01:30 | 9.3 | 1.7 | 212.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-30 02:30 | 9.5 | 2.3 | 250 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-30 03:30 | 11.1 | 2.6 | 282.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-30 04:30 | 12.1 | 2.3 | 297.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-30 05:30 | 12.8 | 1.7 | 155 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-30 06:30 | 14.5 | 1.3 | 47.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-30 07:30 | 16 | 1.4 | 87.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-30 08:30 | 16 | 1.8 | 105 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-30 09:30 | 15.5 | 2.6 | 135 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-30 10:30 | 15.4 | 3.2 | 150 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-30 11:30 | 15.2 | 3.2 | 152.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-30 12:30 | 16.1 | 3.3 | 155 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-30 13:30 | 16.2 | 4 | 155 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-05-30 14:30 | 14.9 | 4.4 | 160 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-30 15:30 | 14.3 | 4.4 | 167.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-30 16:30 | 14.3 | 4.7 | 170 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-30 17:30 | 14.3 | 4.9 | 172.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-05-30 18:30 | 13.8 | 4.7 | 172.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-05-30 19:30 | 12.8 | 4.5 | 167.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-05-30 20:30 | 11.7 | 4.2 | 167.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-30 21:30 | 10.5 | 3.9 | 170 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-30 22:30 | 10 | 4.2 | 170 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-30 23:30 | 10.1 | 4.4 | 170 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-31 00:30 | 10.2 | 4.4 | 172.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-31 01:30 | 10 | 4.1 | 175 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-05-31 02:30 | 9.7 | 3.9 | 172.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-31 03:30 | 9.5 | 4.2 | 175 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-05-31 04:30 | 9.6 | 4.9 | 180 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-05-31 05:30 | 10 | 5.8 | 170 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-05-31 06:30 | 10.4 | 6 | 155 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-05-31 07:30 | 10.9 | 5.4 | 145 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-05-31 08:30 | 11.5 | 4.9 | 135 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-05-31 09:30 | 12 | 5.1 | 135 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-05-31 10:30 | 12.7 | 5.6 | 152.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-05-31 11:30 | 13 | 6.1 | 170 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-05-31 12:30 | 13.2 | 6.7 | 172.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-05-31 13:30 | 13.7 | 7.2 | 170 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-05-31 14:30 | 13.9 | 7.5 | 170 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-05-31 15:30 | 13.9 | 7.2 | 170 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-05-31 16:30 | 13.8 | 6.4 | 167.5 | 220 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-05-31 17:30 | 13.5 | 5.1 | 162.5 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-05-31 18:30 | 13 | 3.7 | 160 | 25 | 67.5 | 0 | 252.5 |  | 121.2 |  | 67.5
Lerwick | 1978-05-31 19:30 | 12.3 | 2.8 | 162.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-05-31 20:30 | 11.5 | 2.6 | 167.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-31 21:30 | 10.6 | 2.4 | 175 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-31 22:30 | 9.9 | 2.1 | 185 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-05-31 23:30 | 9.7 | 2.3 | 190 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-01 00:30 | 9.8 | 2.6 | 187.5 | 0 | 0 | 0 | 320 |  | 153.6 | 44288.4 | 0 | 138132.5
Lerwick | 1978-06-01 01:30 | 9.7 | 2.4 | 182.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-01 02:30 | 9.8 | 2.2 | 177.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-01 03:30 | 9.9 | 2.6 | 172.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-01 04:30 | 9.5 | 3.5 | 167.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-06-01 05:30 | 9.9 | 4.4 | 162.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-06-01 06:30 | 11 | 4.9 | 160 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-06-01 07:30 | 11.8 | 5.2 | 162.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-06-01 08:30 | 12.8 | 5.5 | 165 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-06-01 09:30 | 13.6 | 5.7 | 162.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-06-01 10:30 | 14.2 | 5.9 | 162.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-06-01 11:30 | 14.5 | 6.4 | 167.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-06-01 12:30 | 14.4 | 6.5 | 170 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-06-01 13:30 | 14.5 | 6.3 | 170 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-06-01 14:30 | 14.6 | 5.8 | 167.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-06-01 15:30 | 14.3 | 5.2 | 162.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-06-01 16:30 | 13.9 | 5 | 160 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-06-01 17:30 | 13.9 | 4.5 | 162.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-06-01 18:30 | 13.5 | 3.8 | 167.5 | 25 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-06-01 19:30 | 12.7 | 3.3 | 167.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-06-01 20:30 | 12 | 3.1 | 165 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-01 21:30 | 11 | 3.2 | 167.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-01 22:30 | 10.6 | 3.3 | 172.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-01 23:30 | 10.4 | 3.2 | 177.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-02 00:30 | 10 | 3.2 | 177.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-02 01:30 | 10.2 | 3.9 | 175 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-06-02 02:30 | 10.6 | 4.7 | 177.5 | 80 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-06-02 03:30 | 10.7 | 5 | 180 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-06-02 04:30 | 10.5 | 5 | 180 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-06-02 05:30 | 10.7 | 4.9 | 182.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-06-02 06:30 | 11.2 | 4.7 | 185 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-06-02 07:30 | 11.6 | 4.7 | 182.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-06-02 08:30 | 12.1 | 4.9 | 180 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-06-02 09:30 | 12.8 | 4.9 | 180 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-06-02 10:30 | 13.5 | 4.9 | 180 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-06-02 11:30 | 14.1 | 4.7 | 187.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-06-02 12:30 | 15.2 | 5.1 | 202.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-06-02 13:30 | 16.3 | 5.7 | 210 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-06-02 14:30 | 17.6 | 5 | 215 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-06-02 15:30 | 17.8 | 4.4 | 227.5 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-06-02 16:30 | 16.8 | 5 | 240 | 110 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-06-02 17:30 | 15.8 | 6.2 | 252.5 | 220 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-06-02 18:30 | 14.4 | 6.4 | 267.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-06-02 19:30 | 13.6 | 5.6 | 280 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-06-02 20:30 | 13.2 | 4.3 | 302.5 | 60 | 105 | 0 | 215 |  | 103.2 |  | 105
Lerwick | 1978-06-02 21:30 | 13.1 | 3.1 | 322.5 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-06-02 22:30 | 13.3 | 3 | 312.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-02 23:30 | 12.9 | 3.4 | 307.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-03 00:30 | 12.2 | 3.3 | 322.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-03 01:30 | 11.7 | 2.4 | 165 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-03 02:30 | 11.3 | 1.5 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-03 03:30 | 11.1 | 1.4 | 112.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-03 04:30 | 11 | 1.8 | 220 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-03 05:30 | 11 | 2.4 | 217.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-03 06:30 | 10.9 | 2.6 | 210 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-03 07:30 | 11.2 | 2.3 | 187.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-03 08:30 | 12.2 | 2.1 | 180 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-03 09:30 | 12.7 | 2.4 | 182.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-03 10:30 | 13.2 | 3 | 170 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-03 11:30 | 14.2 | 3.3 | 165 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-03 12:30 | 14.7 | 3.4 | 185 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-03 13:30 | 15.4 | 4 | 210 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-06-03 14:30 | 16 | 4.4 | 220 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-06-03 15:30 | 15.8 | 4.1 | 210 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-06-03 16:30 | 15.3 | 3.7 | 187.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-06-03 17:30 | 14.4 | 3.7 | 175 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-06-03 18:30 | 13.4 | 3.7 | 180 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-06-03 19:30 | 12.9 | 3.3 | 190 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-06-03 20:30 | 12.6 | 3.1 | 190 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-03 21:30 | 12.5 | 3.2 | 182.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-03 22:30 | 12.3 | 3.4 | 185 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-03 23:30 | 11.7 | 3.6 | 190 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-06-04 00:30 | 11.4 | 3.4 | 192.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-06-04 01:30 | 11.4 | 3.6 | 192.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-06-04 02:30 | 11.9 | 3.9 | 185 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-06-04 03:30 | 11.9 | 3.5 | 180 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-06-04 04:30 | 11.6 | 2.9 | 177.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-06-04 05:30 | 11.6 | 3 | 177.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-04 06:30 | 12 | 3.6 | 182.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-06-04 07:30 | 12.9 | 4.2 | 180 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-06-04 08:30 | 13.4 | 4.5 | 172.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-06-04 09:30 | 14.2 | 4.4 | 172.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-06-04 10:30 | 13.6 | 4.1 | 175 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-06-04 11:30 | 13.1 | 3.9 | 172.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-06-04 12:30 | 13.7 | 4.4 | 170 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-06-04 13:30 | 12.8 | 4.9 | 167.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-06-04 14:30 | 11.8 | 4.9 | 160 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-06-04 15:30 | 11.5 | 4.7 | 150 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-06-04 16:30 | 11.5 | 4.7 | 140 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-06-04 17:30 | 11.4 | 4.9 | 132.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-06-04 18:30 | 11.4 | 4.7 | 130 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-06-04 19:30 | 11.2 | 4.2 | 130 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-06-04 20:30 | 11.2 | 4 | 132.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-06-04 21:30 | 11.1 | 4.2 | 142.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-06-04 22:30 | 10.9 | 4.4 | 155 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-06-04 23:30 | 11.2 | 4.2 | 160 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-06-05 00:30 | 11.5 | 4.5 | 160 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-06-05 01:30 | 11.4 | 5.3 | 157.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-06-05 02:30 | 11.2 | 5.8 | 152.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-06-05 03:30 | 11.3 | 5.9 | 150 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-06-05 04:30 | 11.3 | 5.4 | 145 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-06-05 05:30 | 11 | 4.6 | 132.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-06-05 06:30 | 11 | 4.6 | 127.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-06-05 07:30 | 11 | 5.1 | 130 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-06-05 08:30 | 11.3 | 5.9 | 125 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-06-05 09:30 | 11.8 | 6.4 | 122.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-06-05 10:30 | 12.6 | 6 | 130 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-06-05 11:30 | 12.5 | 5.8 | 140 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-06-05 12:30 | 11.7 | 5.6 | 150 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-06-05 13:30 | 11.5 | 5.5 | 162.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-06-05 14:30 | 11.7 | 5.9 | 175 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-06-05 15:30 | 11.7 | 6 | 180 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-06-05 16:30 | 11.2 | 5.6 | 180 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-06-05 17:30 | 11.6 | 4.9 | 185 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-06-05 18:30 | 12.3 | 4.5 | 192.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-06-05 19:30 | 12 | 4.2 | 190 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-06-05 20:30 | 11.5 | 3.6 | 180 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-06-05 21:30 | 10.7 | 3.3 | 182.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-06-05 22:30 | 9.7 | 3.3 | 197.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-05 23:30 | 9.4 | 3.4 | 200 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-06 00:30 | 9.6 | 3.1 | 192.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-06 01:30 | 9.7 | 2 | 187.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-06 02:30 | 9.7 | 1.8 | 185 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-06 03:30 | 9.3 | 2.3 | 182.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-06 04:30 | 9.1 | 2.6 | 172.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-06 05:30 | 10.1 | 3.1 | 162.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-06 06:30 | 11 | 3.8 | 162.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-06-06 07:30 | 11.3 | 3.9 | 162.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-06-06 08:30 | 11.5 | 4.1 | 160 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-06-06 09:30 | 11.5 | 4.7 | 165 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-06-06 10:30 | 11.4 | 5.4 | 172.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-06-06 11:30 | 11.6 | 6.5 | 175 | 300 | 205 | 0 | 115 |  | 55.2 |  | 205
Lerwick | 1978-06-06 12:30 | 12.6 | 7.4 | 172.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-06-06 13:30 | 13.2 | 7.6 | 170 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-06-06 14:30 | 13.2 | 7.2 | 170 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-06-06 15:30 | 13.3 | 6.8 | 170 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-06-06 16:30 | 12.8 | 6.5 | 167.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-06-06 17:30 | 12.1 | 5.6 | 157.5 | 150 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-06-06 18:30 | 11.7 | 4.9 | 157.5 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-06-06 19:30 | 11 | 6.3 | 185 | 220 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-06-06 20:30 | 11.1 | 8.7 | 212.5 | 770 | 495 | 175 | 0 |  | 0 |  | 320
Lerwick | 1978-06-06 21:30 | 11.2 | 10 | 220 | 1150 | 960 | 640 | 0 |  | 0 |  | 320
Lerwick | 1978-06-06 22:30 | 10.6 | 10.4 | 222.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-06-06 23:30 | 10.3 | 10.2 | 227.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-06-07 00:30 | 10.1 | 9.4 | 227.5 | 900 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-06-07 01:30 | 9.7 | 8.4 | 225 | 635 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-07 02:30 | 9.5 | 7.5 | 222.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-07 03:30 | 9.4 | 6.2 | 207.5 | 220 | 360 | 40 | 0 |  | 0 |  | 320
Lerwick | 1978-06-07 04:30 | 9.4 | 5.1 | 185 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-06-07 05:30 | 9.4 | 5.8 | 177.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-06-07 06:30 | 9.4 | 7.7 | 187.5 | 500 | 325 | 5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-07 07:30 | 9.6 | 9.5 | 200 | 1025 | 762.5 | 442.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-07 08:30 | 9.9 | 10.8 | 210 | 1270 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-07 09:30 | 10.2 | 11.3 | 222.5 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-06-07 10:30 | 10.7 | 11.3 | 235 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-06-07 11:30 | 11.1 | 11 | 240 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-06-07 12:30 | 10.9 | 10.6 | 240 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-06-07 13:30 | 10.9 | 10.6 | 240 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-06-07 14:30 | 11.4 | 10.8 | 237.5 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-06-07 15:30 | 11.5 | 10.8 | 235 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-06-07 16:30 | 11 | 10.8 | 237.5 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-06-07 17:30 | 10.3 | 10.6 | 237.5 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-06-07 18:30 | 9.9 | 10 | 232.5 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-06-07 19:30 | 9.5 | 9 | 230 | 900 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-06-07 20:30 | 8.8 | 8.3 | 227.5 | 635 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-07 21:30 | 8.8 | 8 | 222.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-06-07 22:30 | 8.8 | 8 | 220 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-06-07 23:30 | 8.3 | 8.4 | 220 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-06-08 00:30 | 8.1 | 9 | 220 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-08 01:30 | 8.2 | 9.3 | 220 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-06-08 02:30 | 8.4 | 9.1 | 222.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-06-08 03:30 | 8.5 | 8.7 | 227.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-06-08 04:30 | 8.5 | 8.5 | 232.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-06-08 05:30 | 8.7 | 8.6 | 235 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-06-08 06:30 | 8.5 | 8.6 | 232.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-06-08 07:30 | 8.4 | 8.7 | 230 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-06-08 08:30 | 9 | 9.5 | 227.5 | 1025 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-08 09:30 | 9.5 | 9.6 | 225 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-06-08 10:30 | 9.2 | 9 | 227.5 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-08 11:30 | 8.3 | 9 | 230 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-06-08 12:30 | 8.8 | 9.1 | 230 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-06-08 13:30 | 9.8 | 9.1 | 230 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-06-08 14:30 | 9.8 | 9.3 | 232.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-06-08 15:30 | 9.7 | 9.3 | 237.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-06-08 16:30 | 9.3 | 9.6 | 240 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-08 17:30 | 8.4 | 9.9 | 240 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-06-08 18:30 | 8.5 | 9.4 | 240 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-08 19:30 | 8.7 | 8.3 | 240 | 635 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-08 20:30 | 8.3 | 6.9 | 240 | 300 | 467.5 | 147.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-08 21:30 | 8.1 | 5.8 | 242.5 | 150 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-06-08 22:30 | 8 | 5.2 | 245 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-06-08 23:30 | 7.7 | 5.3 | 245 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-06-09 00:30 | 7.9 | 5.9 | 252.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-06-09 01:30 | 8.5 | 6 | 265 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-06-09 02:30 | 8.6 | 5.6 | 270 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-06-09 03:30 | 8.4 | 5.5 | 270 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-06-09 04:30 | 8.4 | 5.8 | 272.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-06-09 05:30 | 8.3 | 6.3 | 277.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-06-09 06:30 | 8.3 | 7.4 | 280 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-06-09 07:30 | 8.5 | 8.3 | 280 | 635 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-09 08:30 | 8.5 | 8.6 | 280 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-09 09:30 | 8.7 | 9 | 280 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-06-09 10:30 | 9.1 | 9 | 282.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-06-09 11:30 | 9.4 | 8.6 | 285 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-06-09 12:30 | 9.9 | 8.7 | 282.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-06-09 13:30 | 10.3 | 9.4 | 280 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-06-09 14:30 | 9.7 | 9.9 | 280 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-09 15:30 | 9.3 | 9.7 | 280 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-06-09 16:30 | 9.5 | 9.1 | 280 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-09 17:30 | 9.3 | 8.9 | 280 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-06-09 18:30 | 9.1 | 9.1 | 282.5 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-06-09 19:30 | 9 | 8.9 | 287.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-06-09 20:30 | 9 | 8.7 | 290 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-06-09 21:30 | 8.7 | 9.2 | 290 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-06-09 22:30 | 8.5 | 9.4 | 290 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-06-09 23:30 | 8.4 | 9.1 | 290 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-06-10 00:30 | 8.3 | 9 | 290 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-06-10 01:30 | 8.1 | 9.1 | 290 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-06-10 02:30 | 7.9 | 9.4 | 292.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-06-10 03:30 | 7.7 | 9.5 | 297.5 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-10 04:30 | 7.7 | 9.5 | 302.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-06-10 05:30 | 7.6 | 9.5 | 307.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-06-10 06:30 | 7.5 | 9.4 | 310 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-10 07:30 | 7.4 | 9.3 | 307.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-06-10 08:30 | 7.2 | 9.4 | 302.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-06-10 09:30 | 7.1 | 9.7 | 300 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-10 10:30 | 7.1 | 10.1 | 300 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-10 11:30 | 7.3 | 10.3 | 300 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-06-10 12:30 | 7.4 | 10.3 | 300 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-06-10 13:30 | 7.3 | 10.3 | 302.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-06-10 14:30 | 7.2 | 10.4 | 307.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-06-10 15:30 | 7.2 | 10.5 | 310 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-06-10 16:30 | 7.6 | 10.4 | 310 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-06-10 17:30 | 7.8 | 10 | 310 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-06-10 18:30 | 7.7 | 9.3 | 307.5 | 900 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-06-10 19:30 | 7.9 | 9 | 300 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-06-10 20:30 | 7.8 | 9.3 | 290 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-06-10 21:30 | 7.6 | 9 | 280 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-06-10 22:30 | 7.9 | 8.9 | 270 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-06-10 23:30 | 8.3 | 8.9 | 257.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-06-11 00:30 | 8.3 | 9.1 | 247.5 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-06-11 01:30 | 8.4 | 10.1 | 250 | 1150 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-06-11 02:30 | 8.9 | 11.6 | 260 | 1400 | 1275 | 955 | 0 |  | 0 |  | 320
Lerwick | 1978-06-11 03:30 | 9 | 12.7 | 267.5 | 1470 | 1435 | 1115 | 0 |  | 0 |  | 320
Lerwick | 1978-06-11 04:30 | 8.9 | 13.3 | 267.5 | 1480 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-06-11 05:30 | 8.7 | 14.1 | 265 | 1500 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-06-11 06:30 | 8.5 | 14.7 | 267.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-06-11 07:30 | 8.5 | 14.4 | 270 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-06-11 08:30 | 8.8 | 13.8 | 270 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-06-11 09:30 | 8.9 | 13.1 | 272.5 | 1480 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-06-11 10:30 | 9.2 | 12.9 | 280 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-06-11 11:30 | 9.4 | 12.7 | 290 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-06-11 12:30 | 9.1 | 12.1 | 295 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-06-11 13:30 | 9.1 | 11.6 | 292.5 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-06-11 14:30 | 9.8 | 11.7 | 292.5 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-06-11 15:30 | 9.8 | 12.2 | 297.5 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-06-11 16:30 | 9.4 | 12.8 | 300 | 1470 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-06-11 17:30 | 8.8 | 13.1 | 302.5 | 1480 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-06-11 18:30 | 7.7 | 12.7 | 307.5 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-06-11 19:30 | 6.9 | 11.9 | 310 | 1400 | 1435 | 1115 | 0 |  | 0 |  | 320
Lerwick | 1978-06-11 20:30 | 6.5 | 11.6 | 310 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-06-11 21:30 | 6.7 | 11.9 | 310 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-06-11 22:30 | 6.5 | 11.7 | 312.5 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-06-11 23:30 | 6.4 | 11.2 | 317.5 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-06-12 00:30 | 6 | 10.7 | 320 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-06-12 01:30 | 5.7 | 10.1 | 320 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-06-12 02:30 | 5.6 | 9.3 | 320 | 900 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-06-12 03:30 | 5.7 | 8.6 | 320 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-06-12 04:30 | 6.1 | 8.9 | 322.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-06-12 05:30 | 6.2 | 9.4 | 327.5 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-06-12 06:30 | 6.3 | 9.4 | 330 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-06-12 07:30 | 6.8 | 9.3 | 330 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-06-12 08:30 | 7.6 | 9.3 | 330 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-06-12 09:30 | 8 | 9.1 | 330 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-06-12 10:30 | 8.3 | 9 | 330 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-06-12 11:30 | 8.3 | 9 | 330 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-06-12 12:30 | 8.5 | 8.9 | 330 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-06-12 13:30 | 9 | 8.8 | 330 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-06-12 14:30 | 9 | 8.6 | 330 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-06-12 15:30 | 8.8 | 8.1 | 330 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-12 16:30 | 8.7 | 7.7 | 330 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-12 17:30 | 8.3 | 7.8 | 332.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-06-12 18:30 | 7.7 | 7.7 | 337.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-06-12 19:30 | 7.5 | 7.2 | 337.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-06-12 20:30 | 7.3 | 6.8 | 332.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-06-12 21:30 | 7.1 | 6.5 | 335 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-06-12 22:30 | 6.9 | 6.4 | 345 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-06-12 23:30 | 6.5 | 6.4 | 350 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-06-13 00:30 | 6.2 | 6.3 | 350 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-06-13 01:30 | 6.1 | 6 | 347.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-06-13 02:30 | 6 | 5.8 | 345 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-06-13 03:30 | 6 | 5.8 | 345 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-06-13 04:30 | 6.2 | 5.9 | 342.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-06-13 05:30 | 6.5 | 6.1 | 340 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-06-13 06:30 | 7 | 6.8 | 342.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-06-13 07:30 | 7.4 | 7.2 | 347.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-06-13 08:30 | 7.9 | 7.2 | 175 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-06-13 09:30 | 8.5 | 7.1 | 7.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-06-13 10:30 | 8.8 | 6.8 | 20 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-06-13 11:30 | 9.1 | 6.8 | 25 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-06-13 12:30 | 9.3 | 7.1 | 22.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-06-13 13:30 | 9.8 | 6.9 | 20 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-06-13 14:30 | 10.1 | 6.4 | 20 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-06-13 15:30 | 10.2 | 6.2 | 20 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-06-13 16:30 | 10.3 | 6.2 | 20 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-06-13 17:30 | 9.9 | 6.3 | 20 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-06-13 18:30 | 9.2 | 6.3 | 20 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-06-13 19:30 | 8.6 | 5.8 | 17.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-06-13 20:30 | 8.2 | 5.2 | 10 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-06-13 21:30 | 8 | 5 | 2.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-06-13 22:30 | 8 | 5.2 | 2.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-06-13 23:30 | 7.9 | 5.5 | 7.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-06-14 00:30 | 7.9 | 5.8 | 10 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-06-14 01:30 | 7.7 | 5.9 | 10 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-06-14 02:30 | 7.6 | 5.4 | 5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-06-14 03:30 | 7.7 | 4.4 | 172.5 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-06-14 04:30 | 7.5 | 4 | 345 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-06-14 05:30 | 7.3 | 4.2 | 177.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-06-14 06:30 | 7.8 | 4.4 | 17.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-06-14 07:30 | 8.6 | 4.1 | 22.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-06-14 08:30 | 8.9 | 3.7 | 20 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-06-14 09:30 | 9.1 | 3.4 | 20 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-06-14 10:30 | 9.3 | 2.7 | 42.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-14 11:30 | 9.6 | 2.2 | 95 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-14 12:30 | 10.1 | 2.7 | 130 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-14 13:30 | 10.3 | 3.6 | 140 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-06-14 14:30 | 10.3 | 4.1 | 155 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-06-14 15:30 | 10.2 | 4.4 | 175 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-06-14 16:30 | 9.8 | 4.4 | 185 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-06-14 17:30 | 9.6 | 4.7 | 175 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-06-14 18:30 | 9.4 | 4.6 | 162.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-06-14 19:30 | 9 | 4.2 | 157.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-06-14 20:30 | 8.4 | 4.4 | 152.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-06-14 21:30 | 8 | 5.3 | 150 | 110 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-06-14 22:30 | 8 | 5.8 | 147.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-06-14 23:30 | 7.8 | 6.1 | 142.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-06-15 00:30 | 7.8 | 6.5 | 140 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-06-15 01:30 | 7.9 | 6.7 | 140 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-06-15 02:30 | 7.9 | 6.7 | 140 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-06-15 03:30 | 8 | 6.7 | 140 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-06-15 04:30 | 8.1 | 6.8 | 140 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-06-15 05:30 | 8 | 6.8 | 137.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-06-15 06:30 | 8.3 | 6.5 | 132.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-06-15 07:30 | 8.8 | 6.5 | 127.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-06-15 08:30 | 9.5 | 6.7 | 120 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-06-15 09:30 | 10.3 | 6.7 | 112.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-06-15 10:30 | 10.4 | 6.5 | 110 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-06-15 11:30 | 10.6 | 6.1 | 112.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-06-15 12:30 | 11 | 5.8 | 117.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-06-15 13:30 | 11 | 5.5 | 117.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-06-15 14:30 | 11.3 | 5.4 | 107.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-06-15 15:30 | 11.3 | 5.6 | 90 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-06-15 16:30 | 11.1 | 6.3 | 72.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-06-15 17:30 | 11 | 6.8 | 60 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-06-15 18:30 | 10.8 | 6.7 | 50 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-06-15 19:30 | 10.3 | 6.3 | 40 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-06-15 20:30 | 9.8 | 6.4 | 32.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-06-15 21:30 | 9.4 | 6.9 | 32.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-06-15 22:30 | 9.2 | 7.2 | 37.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-06-15 23:30 | 9 | 7.2 | 40 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-06-16 00:30 | 8.7 | 7.1 | 37.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-06-16 01:30 | 8.2 | 6.8 | 32.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-06-16 02:30 | 8 | 6.8 | 27.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-06-16 03:30 | 8 | 7.1 | 25 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-06-16 04:30 | 8 | 7.4 | 25 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-06-16 05:30 | 8.2 | 8.1 | 22.5 | 635 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-16 06:30 | 8.3 | 8.5 | 20 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-16 07:30 | 8.3 | 8.2 | 17.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-16 08:30 | 8.7 | 8 | 12.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-06-16 09:30 | 9 | 8.5 | 10 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-16 10:30 | 9.4 | 9.4 | 12.5 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-06-16 11:30 | 9.8 | 10.1 | 15 | 1150 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-06-16 12:30 | 10.6 | 10.6 | 12.5 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-06-16 13:30 | 11.7 | 10.6 | 12.5 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-06-16 14:30 | 11.2 | 10.7 | 17.5 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-06-16 15:30 | 10.3 | 11.2 | 20 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-06-16 16:30 | 10.2 | 11.1 | 17.5 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-06-16 17:30 | 9.9 | 10.5 | 12.5 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-06-16 18:30 | 9.3 | 10.3 | 10 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-06-16 19:30 | 9.1 | 10.3 | 10 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-06-16 20:30 | 8.9 | 10.5 | 10 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-06-16 21:30 | 8.5 | 10.8 | 7.5 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-06-16 22:30 | 8.3 | 10.5 | 2.5 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-06-16 23:30 | 8 | 10.5 | 0 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-06-17 00:30 | 7.7 | 11.6 | 2.5 | 1400 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-06-17 01:30 | 7.7 | 12.4 | 7.5 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-06-17 02:30 | 7.7 | 11.7 | 7.5 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-06-17 03:30 | 7.7 | 10.9 | 5 | 1270 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-06-17 04:30 | 7.7 | 10.8 | 7.5 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-06-17 05:30 | 7.8 | 10.6 | 10 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-06-17 06:30 | 8.1 | 10.5 | 10 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-06-17 07:30 | 9.1 | 11 | 12.5 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-06-17 08:30 | 9.6 | 11.6 | 15 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-06-17 09:30 | 9.6 | 11.3 | 15 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-06-17 10:30 | 10.2 | 10.4 | 17.5 | 1150 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-06-17 11:30 | 10.7 | 9.9 | 20 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-17 12:30 | 11 | 9.5 | 20 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-06-17 13:30 | 11.3 | 8.6 | 20 | 770 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-17 14:30 | 11.6 | 7.8 | 20 | 500 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-06-17 15:30 | 11.6 | 7.9 | 20 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-06-17 16:30 | 11.4 | 8.1 | 17.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-17 17:30 | 10.9 | 8 | 12.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-06-17 18:30 | 10.2 | 7.6 | 10 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-17 19:30 | 9.5 | 6.9 | 10 | 300 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-06-17 20:30 | 8.8 | 6.5 | 10 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-06-17 21:30 | 8.3 | 6.1 | 10 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-06-17 22:30 | 7.7 | 5.6 | 10 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-06-17 23:30 | 7.5 | 5.1 | 7.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-06-18 00:30 | 7.4 | 4.6 | 2.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-06-18 01:30 | 7.3 | 4.1 | 175 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-06-18 02:30 | 7.1 | 3.6 | 342.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-06-18 03:30 | 6.8 | 3.2 | 335 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-06-18 04:30 | 6.6 | 2.6 | 345 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-18 05:30 | 6.7 | 1.8 | 345 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-18 06:30 | 7.1 | 1.6 | 317.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-18 07:30 | 7.5 | 2 | 290 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-18 08:30 | 7.8 | 2.7 | 270 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-18 09:30 | 8.3 | 3.8 | 257.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-06-18 10:30 | 8.8 | 4.7 | 252.5 | 80 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-06-18 11:30 | 9.2 | 5.3 | 250 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-06-18 12:30 | 9.4 | 5.5 | 250 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-06-18 13:30 | 9.4 | 5.2 | 250 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-06-18 14:30 | 9.2 | 5 | 250 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-06-18 15:30 | 8.8 | 5.2 | 250 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-06-18 16:30 | 8.5 | 5.6 | 247.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-06-18 17:30 | 8.8 | 6 | 242.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-06-18 18:30 | 8.8 | 6.3 | 240 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-06-18 19:30 | 8.4 | 6.7 | 242.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-06-18 20:30 | 8.1 | 6.8 | 242.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-06-18 21:30 | 8.1 | 6.4 | 232.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-06-18 22:30 | 8.2 | 6.2 | 220 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-06-18 23:30 | 8.3 | 6.2 | 212.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-06-19 00:30 | 8.5 | 6.4 | 210 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-06-19 01:30 | 8.6 | 7.3 | 210 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-06-19 02:30 | 8.6 | 8.7 | 210 | 770 | 585 | 265 | 0 |  | 0 |  | 320
Lerwick | 1978-06-19 03:30 | 8.7 | 10 | 210 | 1150 | 960 | 640 | 0 |  | 0 |  | 320
Lerwick | 1978-06-19 04:30 | 8.7 | 10.7 | 210 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-06-19 05:30 | 8.5 | 11.1 | 210 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-06-19 06:30 | 8.4 | 10.5 | 215 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-06-19 07:30 | 8.5 | 8.9 | 225 | 770 | 1020 | 700 | 0 |  | 0 |  | 320
Lerwick | 1978-06-19 08:30 | 8.7 | 8.3 | 232.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-19 09:30 | 9.1 | 9 | 237.5 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-19 10:30 | 10.5 | 9.9 | 240 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-19 11:30 | 11.5 | 10 | 240 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-19 12:30 | 11.3 | 9.5 | 240 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-19 13:30 | 10.3 | 9.6 | 240 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-06-19 14:30 | 10.5 | 10.2 | 240 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-19 15:30 | 11.5 | 10.4 | 240 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-06-19 16:30 | 11.2 | 10.3 | 237.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-06-19 17:30 | 11 | 10.1 | 232.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-06-19 18:30 | 10.7 | 9.6 | 230 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-19 19:30 | 10.2 | 9 | 230 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-19 20:30 | 9.5 | 8.6 | 227.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-06-19 21:30 | 8.9 | 8.2 | 222.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-19 22:30 | 8.8 | 7.8 | 217.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-19 23:30 | 8.6 | 7.8 | 212.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-06-20 00:30 | 8.5 | 8.2 | 205 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-20 01:30 | 8.8 | 8.9 | 195 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-20 02:30 | 9.2 | 10.1 | 195 | 1150 | 960 | 640 | 0 |  | 0 |  | 320
Lerwick | 1978-06-20 03:30 | 9.1 | 11.7 | 205 | 1400 | 1275 | 955 | 0 |  | 0 |  | 320
Lerwick | 1978-06-20 04:30 | 8.9 | 12.7 | 210 | 1470 | 1435 | 1115 | 0 |  | 0 |  | 320
Lerwick | 1978-06-20 05:30 | 9.2 | 12.7 | 210 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-06-20 06:30 | 9.3 | 12.2 | 210 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-06-20 07:30 | 9.5 | 11.9 | 210 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-06-20 08:30 | 10.7 | 11.4 | 207.5 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-06-20 09:30 | 11.4 | 10.2 | 195 | 1150 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-06-20 10:30 | 11.1 | 9.5 | 177.5 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-20 11:30 | 10.9 | 9.9 | 175 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-06-20 12:30 | 11.1 | 10.4 | 185 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-20 13:30 | 10.3 | 10.2 | 195 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-06-20 14:30 | 9.8 | 9.4 | 200 | 900 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-06-20 15:30 | 10 | 8.8 | 195 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-06-20 16:30 | 9.7 | 8.8 | 190 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-06-20 17:30 | 9.4 | 8.9 | 195 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-06-20 18:30 | 10.3 | 9 | 202.5 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-06-20 19:30 | 10.9 | 8.5 | 202.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-06-20 20:30 | 10.3 | 7.9 | 202.5 | 500 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-06-20 21:30 | 9.8 | 7.3 | 207.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-06-20 22:30 | 9.3 | 6.7 | 215 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-06-20 23:30 | 9.1 | 6 | 225 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-06-21 00:30 | 8.7 | 5 | 237.5 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-06-21 01:30 | 8.2 | 4 | 250 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-06-21 02:30 | 7.6 | 3.7 | 255 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-06-21 03:30 | 7.3 | 3.9 | 255 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-06-21 04:30 | 7.6 | 4 | 250 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-06-21 05:30 | 7.8 | 4.2 | 245 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-06-21 06:30 | 8.4 | 4.4 | 245 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-06-21 07:30 | 9.3 | 4.7 | 240 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-06-21 08:30 | 9.6 | 4.9 | 240 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-06-21 09:30 | 10.2 | 4.9 | 252.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-06-21 10:30 | 10.2 | 4.7 | 255 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-06-21 11:30 | 10.2 | 4.4 | 245 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-06-21 12:30 | 11.4 | 4.2 | 240 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-06-21 13:30 | 12.2 | 4 | 220 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-06-21 14:30 | 12.7 | 4.2 | 180 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-06-21 15:30 | 12.4 | 4.4 | 155 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-06-21 16:30 | 12.2 | 4 | 147.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-06-21 17:30 | 11.7 | 3.3 | 142.5 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-06-21 18:30 | 11 | 3.1 | 132.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-21 19:30 | 10.5 | 3.2 | 107.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-21 20:30 | 9.7 | 3.6 | 75 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-06-21 21:30 | 9.2 | 4.4 | 60 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-06-21 22:30 | 8.8 | 5.4 | 57.5 | 110 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-06-21 23:30 | 8.5 | 6 | 50 | 220 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-06-22 00:30 | 8.8 | 6.6 | 42.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-06-22 01:30 | 9.1 | 7.5 | 40 | 500 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-06-22 02:30 | 9.1 | 8.2 | 40 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-22 03:30 | 9 | 8.7 | 37.5 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-22 04:30 | 9 | 9.4 | 32.5 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-06-22 05:30 | 8.9 | 10.1 | 30 | 1150 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-06-22 06:30 | 8.9 | 10.9 | 27.5 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-06-22 07:30 | 9.1 | 11.3 | 25 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-06-22 08:30 | 9.1 | 10.3 | 30 | 1150 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-06-22 09:30 | 9.3 | 8.2 | 40 | 635 | 892.5 | 572.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-22 10:30 | 9.7 | 6.8 | 60 | 300 | 467.5 | 147.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-22 11:30 | 10.2 | 6.3 | 90 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-06-22 12:30 | 10.4 | 6.2 | 107.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-06-22 13:30 | 10.5 | 6.3 | 110 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-06-22 14:30 | 10.8 | 6.4 | 107.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-06-22 15:30 | 10.9 | 6.4 | 102.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-06-22 16:30 | 10.4 | 6.5 | 97.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-06-22 17:30 | 10.2 | 6.4 | 92.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-06-22 18:30 | 10.4 | 5.8 | 87.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-06-22 19:30 | 10.4 | 4.9 | 80 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-06-22 20:30 | 10.3 | 4 | 72.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-06-22 21:30 | 10.2 | 2.9 | 70 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-06-22 22:30 | 10.1 | 1.7 | 77.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-22 23:30 | 10.2 | 1.7 | 97.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-23 00:30 | 10.2 | 2.6 | 112.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-23 01:30 | 10 | 2.9 | 105 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-23 02:30 | 10 | 3 | 90 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-23 03:30 | 10 | 3.9 | 90 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-06-23 04:30 | 9.9 | 4.7 | 97.5 | 80 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-06-23 05:30 | 9.9 | 4.9 | 100 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-06-23 06:30 | 10 | 4.7 | 102.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-06-23 07:30 | 9.9 | 4.4 | 107.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-06-23 08:30 | 10.2 | 4.4 | 110 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-06-23 09:30 | 10.4 | 4.5 | 110 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-06-23 10:30 | 10.4 | 4.5 | 110 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-06-23 11:30 | 11 | 4.7 | 110 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-06-23 12:30 | 11.6 | 5.2 | 110 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-06-23 13:30 | 11.9 | 5.4 | 110 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-06-23 14:30 | 11.9 | 5.2 | 110 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-06-23 15:30 | 11.7 | 4.7 | 110 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-06-23 16:30 | 11.6 | 4.4 | 110 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-06-23 17:30 | 11.8 | 4.2 | 110 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-06-23 18:30 | 12.2 | 3.9 | 102.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-06-23 19:30 | 11.7 | 3.6 | 82.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-06-23 20:30 | 10.7 | 3.2 | 60 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-06-23 21:30 | 10.1 | 3.2 | 42.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-23 22:30 | 9.3 | 3.4 | 32.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-23 23:30 | 9.1 | 4 | 25 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-06-24 00:30 | 9.1 | 4.7 | 12.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-06-24 01:30 | 8.9 | 5.4 | 2.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-06-24 02:30 | 8.9 | 6.1 | 0 | 220 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-06-24 03:30 | 8.6 | 6.3 | 177.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-06-24 04:30 | 8.5 | 6.4 | 350 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-06-24 05:30 | 9 | 7.2 | 342.5 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-06-24 06:30 | 9.8 | 8.2 | 340 | 635 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-24 07:30 | 10.3 | 9.3 | 340 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-24 08:30 | 11.2 | 10.1 | 337.5 | 1150 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-06-24 09:30 | 12.5 | 10.5 | 332.5 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-06-24 10:30 | 12.8 | 10.2 | 330 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-06-24 11:30 | 12.7 | 10 | 332.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-06-24 12:30 | 12.9 | 10 | 337.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-06-24 13:30 | 12.7 | 9.9 | 342.5 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-24 14:30 | 12.5 | 9.1 | 350 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-24 15:30 | 12.8 | 8 | 177.5 | 635 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-24 16:30 | 12.8 | 7.5 | 177.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-24 17:30 | 11.8 | 7.6 | 177.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-06-24 18:30 | 11.4 | 8.2 | 5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-24 19:30 | 11.3 | 8.6 | 7.5 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-24 20:30 | 11 | 7.7 | 180 | 500 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-06-24 21:30 | 10.8 | 6.7 | 350 | 300 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-06-24 22:30 | 10.5 | 6.9 | 340 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-06-24 23:30 | 10.4 | 7.8 | 332.5 | 500 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-06-25 00:30 | 9.9 | 7.9 | 332.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-06-25 01:30 | 9.2 | 7.4 | 332.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-06-25 02:30 | 9.1 | 7.1 | 327.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-06-25 03:30 | 8.9 | 7.1 | 325 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-06-25 04:30 | 8.4 | 7.2 | 322.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-06-25 05:30 | 8 | 6.9 | 320 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-06-25 06:30 | 8 | 6.8 | 320 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-06-25 07:30 | 8 | 7.1 | 320 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-06-25 08:30 | 7.9 | 7.1 | 320 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-06-25 09:30 | 7.8 | 6.8 | 320 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-06-25 10:30 | 7.8 | 6.7 | 317.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-06-25 11:30 | 7.9 | 6.9 | 310 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-06-25 12:30 | 8.2 | 7.4 | 302.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-06-25 13:30 | 8.5 | 7.8 | 302.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-06-25 14:30 | 8.5 | 7.8 | 307.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-06-25 15:30 | 8.4 | 7.6 | 310 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-06-25 16:30 | 8.2 | 7.5 | 312.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-06-25 17:30 | 7.9 | 7.2 | 315 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-06-25 18:30 | 7.5 | 6.8 | 315 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-06-25 19:30 | 7.4 | 6.7 | 315 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-06-25 20:30 | 7.4 | 6.3 | 312.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-06-25 21:30 | 7.4 | 5.6 | 310 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-06-25 22:30 | 7.4 | 5.5 | 310 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-06-25 23:30 | 7.2 | 5.9 | 312.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-06-26 00:30 | 6.8 | 6.3 | 317.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-06-26 01:30 | 6.6 | 6.1 | 320 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-06-26 02:30 | 6.3 | 5.8 | 320 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-06-26 03:30 | 6.2 | 5.7 | 317.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-06-26 04:30 | 6.2 | 5.5 | 310 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-06-26 05:30 | 6.3 | 5.2 | 305 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-06-26 06:30 | 6.6 | 5 | 310 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-06-26 07:30 | 6.7 | 5.2 | 315 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-06-26 08:30 | 6.9 | 5.5 | 312.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-06-26 09:30 | 7.3 | 5.8 | 307.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-06-26 10:30 | 7.4 | 5.9 | 302.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-06-26 11:30 | 7.3 | 5.8 | 300 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-06-26 12:30 | 7.4 | 5.7 | 300 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-06-26 13:30 | 7.7 | 5.3 | 302.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-06-26 14:30 | 8 | 4.9 | 305 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-06-26 15:30 | 8.6 | 5.1 | 300 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-06-26 16:30 | 9.6 | 5.6 | 290 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-06-26 17:30 | 10 | 5.9 | 282.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-06-26 18:30 | 9.7 | 5.8 | 277.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-06-26 19:30 | 9.5 | 5.3 | 272.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-06-26 20:30 | 8.9 | 4.7 | 267.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-06-26 21:30 | 8.3 | 4.2 | 260 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-06-26 22:30 | 7.5 | 4.2 | 252.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-06-26 23:30 | 7.2 | 4.5 | 242.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-06-27 00:30 | 7.9 | 4.7 | 227.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-06-27 01:30 | 8.4 | 5.7 | 220 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-06-27 02:30 | 8.7 | 6.7 | 225 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-06-27 03:30 | 8.9 | 7.3 | 237.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-06-27 04:30 | 9.2 | 7.6 | 250 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-06-27 05:30 | 9.5 | 7.3 | 257.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-06-27 06:30 | 9.5 | 7.6 | 260 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-06-27 07:30 | 9.7 | 8 | 260 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-27 08:30 | 9.8 | 8 | 260 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-06-27 09:30 | 9.7 | 8.2 | 260 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-06-27 10:30 | 9.6 | 8.3 | 257.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-06-27 11:30 | 9.7 | 8 | 252.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-06-27 12:30 | 9.8 | 8 | 250 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-06-27 13:30 | 9.8 | 7.8 | 250 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-06-27 14:30 | 9.9 | 7.6 | 250 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-06-27 15:30 | 10 | 7.1 | 247.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-06-27 16:30 | 9.9 | 6.3 | 242.5 | 220 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-06-27 17:30 | 9.9 | 5.9 | 237.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-06-27 18:30 | 10 | 5.4 | 232.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-06-27 19:30 | 9.9 | 4.5 | 225 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-06-27 20:30 | 9.7 | 3.9 | 212.5 | 25 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-06-27 21:30 | 9.6 | 3.7 | 202.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-06-27 22:30 | 9.6 | 3.7 | 200 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-06-27 23:30 | 9.7 | 3.6 | 187.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-06-28 00:30 | 9.8 | 3 | 162.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-06-28 01:30 | 9.7 | 3.3 | 152.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-28 02:30 | 9.5 | 4.4 | 155 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-06-28 03:30 | 9.5 | 4.7 | 150 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-06-28 04:30 | 9.5 | 4.4 | 137.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-06-28 05:30 | 9.4 | 4.6 | 125 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-06-28 06:30 | 9.5 | 4.4 | 125 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-06-28 07:30 | 9.8 | 4 | 142.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-06-28 08:30 | 10.2 | 4.5 | 162.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-06-28 09:30 | 10.4 | 5.2 | 170 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-06-28 10:30 | 10.4 | 5.4 | 182.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-06-28 11:30 | 10.4 | 5.8 | 210 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-06-28 12:30 | 10.8 | 6.3 | 225 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-06-28 13:30 | 11.3 | 6.1 | 222.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-06-28 14:30 | 10.9 | 5.9 | 220 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-06-28 15:30 | 10.5 | 6 | 220 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-06-28 16:30 | 10.5 | 6.2 | 220 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-06-28 17:30 | 10.7 | 6.2 | 217.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-06-28 18:30 | 10.9 | 5.9 | 210 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-06-28 19:30 | 10.7 | 5.3 | 197.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-06-28 20:30 | 10.5 | 5 | 182.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-06-28 21:30 | 10.3 | 4.9 | 172.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-06-28 22:30 | 10 | 5.1 | 167.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-06-28 23:30 | 10 | 5.6 | 162.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-06-29 00:30 | 10 | 5.8 | 162.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-06-29 01:30 | 10 | 5.5 | 167.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-06-29 02:30 | 10 | 4.9 | 167.5 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-06-29 03:30 | 10 | 4 | 160 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-06-29 04:30 | 10 | 3.6 | 155 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-06-29 05:30 | 10 | 3.7 | 157.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-06-29 06:30 | 10.2 | 3.6 | 160 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-06-29 07:30 | 10.3 | 3.3 | 160 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-06-29 08:30 | 10.4 | 3.9 | 160 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-06-29 09:30 | 11 | 5.1 | 162.5 | 110 | 67.5 | 0 | 252.5 |  | 121.2 |  | 67.5
Lerwick | 1978-06-29 10:30 | 11.4 | 5.8 | 175 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-06-29 11:30 | 12 | 5.9 | 197.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-06-29 12:30 | 11.9 | 5.4 | 215 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-06-29 13:30 | 11.6 | 4.7 | 227.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-06-29 14:30 | 12 | 4.5 | 237.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-06-29 15:30 | 12.3 | 4.4 | 235 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-06-29 16:30 | 11.9 | 4 | 230 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-06-29 17:30 | 11.2 | 3.3 | 235 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-06-29 18:30 | 11 | 3.1 | 247.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-29 19:30 | 10.5 | 3.1 | 257.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-29 20:30 | 10.1 | 2.8 | 262.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-29 21:30 | 9.9 | 2.3 | 257.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-29 22:30 | 9.6 | 2.3 | 245 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-29 23:30 | 9.3 | 3.1 | 247.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-30 00:30 | 8.8 | 3.7 | 257.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-06-30 01:30 | 8.7 | 3.9 | 262.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-06-30 02:30 | 8.7 | 3.7 | 270 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-06-30 03:30 | 8.5 | 3.1 | 280 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-06-30 04:30 | 8.6 | 2.4 | 285 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-30 05:30 | 8.9 | 2.4 | 277.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-30 06:30 | 9.4 | 2.4 | 260 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-30 07:30 | 9.8 | 2 | 245 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-30 08:30 | 10.3 | 2.2 | 217.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-30 09:30 | 11 | 3.1 | 170 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-06-30 10:30 | 11.6 | 3.7 | 167.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-06-30 11:30 | 11.7 | 4.1 | 217.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-06-30 12:30 | 11.6 | 4.9 | 245 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-06-30 13:30 | 11.9 | 5.4 | 245 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-06-30 14:30 | 11.6 | 5.1 | 247.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-06-30 15:30 | 11.3 | 4.9 | 250 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-06-30 16:30 | 11.3 | 4.9 | 250 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-06-30 17:30 | 11.1 | 4.7 | 250 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-06-30 18:30 | 10.7 | 4.7 | 250 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-06-30 19:30 | 10.2 | 4.9 | 252.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-06-30 20:30 | 9.8 | 4.6 | 260 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-06-30 21:30 | 9.5 | 4.2 | 267.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-06-30 22:30 | 9.3 | 4 | 267.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-06-30 23:30 | 9.1 | 3.8 | 260 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-07-01 00:30 | 9.1 | 3.4 | 252.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 | 46899.6 | 12.5 | 140372.5
Lerwick | 1978-07-01 01:30 | 9 | 3.6 | 252.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-07-01 02:30 | 8.8 | 3.9 | 257.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-07-01 03:30 | 8.3 | 3.8 | 255 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-07-01 04:30 | 8.3 | 3.4 | 245 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-07-01 05:30 | 8.5 | 3.4 | 242.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-01 06:30 | 9 | 3.1 | 245 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-01 07:30 | 9.7 | 2.9 | 222.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-01 08:30 | 10.2 | 3.8 | 180 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-07-01 09:30 | 10.6 | 4.7 | 157.5 | 80 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-07-01 10:30 | 10.9 | 4.9 | 155 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-07-01 11:30 | 10.7 | 5.3 | 157.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-07-01 12:30 | 11.2 | 5.7 | 157.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-07-01 13:30 | 11.5 | 5.7 | 155 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-01 14:30 | 11.5 | 5.5 | 155 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-01 15:30 | 11.7 | 5.2 | 150 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-07-01 16:30 | 11.5 | 5.4 | 145 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-07-01 17:30 | 11.1 | 6.1 | 147.5 | 220 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-07-01 18:30 | 10.9 | 6.3 | 152.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-07-01 19:30 | 10.8 | 6 | 160 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-07-01 20:30 | 10.4 | 5.6 | 167.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-07-01 21:30 | 10.2 | 4.9 | 172.5 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-07-01 22:30 | 9.9 | 4.2 | 177.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-07-01 23:30 | 9.9 | 3.7 | 190 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-07-02 00:30 | 9.9 | 3.6 | 210 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-07-02 01:30 | 9.7 | 3.4 | 217.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-07-02 02:30 | 9.5 | 3 | 212.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-02 03:30 | 9.4 | 2.9 | 215 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-02 04:30 | 9.4 | 3.5 | 222.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-07-02 05:30 | 9.3 | 4.2 | 225 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-07-02 06:30 | 9.4 | 4.7 | 230 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-07-02 07:30 | 9.7 | 4.9 | 235 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-07-02 08:30 | 10.2 | 5.4 | 232.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-07-02 09:30 | 10.9 | 6.3 | 230 | 220 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-07-02 10:30 | 11.4 | 7.2 | 235 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-07-02 11:30 | 11.3 | 7.8 | 245 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-02 12:30 | 10.7 | 8 | 250 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-02 13:30 | 10.4 | 8 | 250 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-07-02 14:30 | 10.8 | 8 | 245 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-07-02 15:30 | 11.8 | 7.6 | 235 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-02 16:30 | 12.2 | 6.9 | 230 | 300 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-07-02 17:30 | 11.6 | 6.4 | 230 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-07-02 18:30 | 11 | 5.8 | 230 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-07-02 19:30 | 10.6 | 4.9 | 230 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-07-02 20:30 | 10.2 | 4 | 230 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-07-02 21:30 | 9.4 | 3.1 | 230 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-07-02 22:30 | 8.3 | 2.2 | 227.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-02 23:30 | 7.6 | 1.1 | 257.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-03 00:30 | 7.6 | 0.5 | 317.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-03 01:30 | 7.6 | 0.7 | 342.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-03 02:30 | 7.6 | 1.5 | 345 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-03 03:30 | 7 | 2.4 | 352.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-03 04:30 | 7.3 | 3 | 345 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-03 05:30 | 8.4 | 3.9 | 340 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-07-03 06:30 | 9.4 | 5.1 | 182.5 | 110 | 67.5 | 0 | 252.5 |  | 121.2 |  | 67.5
Lerwick | 1978-07-03 07:30 | 10.4 | 5.9 | 20 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-07-03 08:30 | 11 | 6.3 | 17.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-07-03 09:30 | 11.2 | 6.8 | 7.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-07-03 10:30 | 11.5 | 7.4 | 175 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-07-03 11:30 | 11.2 | 7.8 | 347.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-03 12:30 | 10.5 | 8.6 | 347.5 | 770 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-07-03 13:30 | 10.4 | 9.9 | 177.5 | 1025 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-03 14:30 | 10.6 | 10.7 | 7.5 | 1270 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-03 15:30 | 10.7 | 11.5 | 10 | 1400 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-07-03 16:30 | 10.4 | 11.9 | 10 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-07-03 17:30 | 10.4 | 11 | 10 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-07-03 18:30 | 10.2 | 9.9 | 7.5 | 1025 | 1182.5 | 862.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-03 19:30 | 10 | 9.4 | 5 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-03 20:30 | 9.9 | 9 | 5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-07-03 21:30 | 9.8 | 8.8 | 2.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-07-03 22:30 | 9.7 | 9.1 | 0 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-07-03 23:30 | 9.5 | 9.9 | 0 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-04 00:30 | 9.5 | 10.5 | 177.5 | 1270 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-04 01:30 | 9.4 | 10.6 | 352.5 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-07-04 02:30 | 9.4 | 10.6 | 352.5 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-07-04 03:30 | 9.7 | 11 | 177.5 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-07-04 04:30 | 10 | 11.3 | 0 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-07-04 05:30 | 9.9 | 11.3 | 0 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-07-04 06:30 | 9.7 | 11.4 | 0 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-07-04 07:30 | 9.6 | 11.7 | 0 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-07-04 08:30 | 9.8 | 12.2 | 0 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-07-04 09:30 | 10 | 12.4 | 0 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-04 10:30 | 10.2 | 12.1 | 0 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-04 11:30 | 10.7 | 11.9 | 0 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-07-04 12:30 | 10.8 | 12.2 | 0 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-07-04 13:30 | 10.8 | 12.4 | 0 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-04 14:30 | 10.7 | 12.4 | 0 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-04 15:30 | 10.5 | 12.4 | 0 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-04 16:30 | 10.4 | 12.4 | 0 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-04 17:30 | 10.1 | 12.7 | 0 | 1470 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-07-04 18:30 | 9.7 | 12.6 | 0 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-07-04 19:30 | 9.5 | 12.2 | 0 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-07-04 20:30 | 9.2 | 12 | 0 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-04 21:30 | 9 | 11.9 | 0 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-07-04 22:30 | 9 | 11.6 | 0 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-07-04 23:30 | 8.9 | 11.4 | 0 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-07-05 00:30 | 8.8 | 11.5 | 0 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-07-05 01:30 | 8.9 | 11.9 | 0 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-07-05 02:30 | 8.9 | 12 | 177.5 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-07-05 03:30 | 8.7 | 11.9 | 355 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-07-05 04:30 | 8.7 | 11.4 | 355 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-07-05 05:30 | 8.8 | 11 | 352.5 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-07-05 06:30 | 8.9 | 11 | 347.5 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-07-05 07:30 | 9.1 | 10.9 | 342.5 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-07-05 08:30 | 9.1 | 10.9 | 340 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-07-05 09:30 | 9.2 | 11.2 | 340 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-07-05 10:30 | 9.5 | 11.6 | 340 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-07-05 11:30 | 9.8 | 11.8 | 340 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-07-05 12:30 | 10 | 11.8 | 340 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-07-05 13:30 | 10.2 | 11.9 | 340 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-07-05 14:30 | 9.9 | 11.9 | 337.5 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-07-05 15:30 | 9.6 | 11.4 | 332.5 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-07-05 16:30 | 9.5 | 10.7 | 330 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-07-05 17:30 | 9.2 | 10.4 | 332.5 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-07-05 18:30 | 9.2 | 10.3 | 337.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-07-05 19:30 | 9.3 | 10.1 | 340 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-07-05 20:30 | 9.3 | 9.7 | 340 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-05 21:30 | 9.3 | 9.5 | 340 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-07-05 22:30 | 9.2 | 9.7 | 340 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-07-05 23:30 | 8.8 | 10.4 | 340 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-06 00:30 | 8.6 | 11 | 337.5 | 1340 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-07-06 01:30 | 8.6 | 10.8 | 330 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-07-06 02:30 | 8.5 | 9.9 | 322.5 | 1025 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-06 03:30 | 8.3 | 9.6 | 317.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-07-06 04:30 | 8.3 | 9.5 | 315 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-07-06 05:30 | 8.7 | 9.4 | 320 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-06 06:30 | 9.1 | 10.1 | 330 | 1150 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-07-06 07:30 | 9.5 | 11.3 | 337.5 | 1340 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-07-06 08:30 | 9.9 | 12.1 | 342.5 | 1450 | 1395 | 1075 | 0 |  | 0 |  | 320
Lerwick | 1978-07-06 09:30 | 9.9 | 11.9 | 347.5 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-07-06 10:30 | 9.9 | 11 | 352.5 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-07-06 11:30 | 9.9 | 10.4 | 355 | 1150 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-07-06 12:30 | 10.1 | 10.4 | 352.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-07-06 13:30 | 10.2 | 10.5 | 350 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-07-06 14:30 | 10.2 | 10.4 | 350 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-07-06 15:30 | 10.2 | 10.3 | 347.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-07-06 16:30 | 10 | 10 | 342.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-07-06 17:30 | 9.7 | 9.3 | 337.5 | 900 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-07-06 18:30 | 9.4 | 8.4 | 332.5 | 635 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-06 19:30 | 9.2 | 8 | 330 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-07-06 20:30 | 8.8 | 8 | 327.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-07-06 21:30 | 8.4 | 8.1 | 325 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-07-06 22:30 | 8.1 | 8.1 | 325 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-07-06 23:30 | 7.9 | 8.1 | 322.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-07-07 00:30 | 7.8 | 8.1 | 320 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-07-07 01:30 | 7.7 | 8.1 | 320 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-07-07 02:30 | 7.7 | 8.1 | 320 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-07-07 03:30 | 7.5 | 8.3 | 320 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-07-07 04:30 | 7.3 | 8.6 | 320 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-07 05:30 | 7.4 | 9 | 317.5 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-07-07 06:30 | 7.4 | 9.5 | 312.5 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-07 07:30 | 7.5 | 9.8 | 312.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-07-07 08:30 | 7.6 | 9.9 | 317.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-07-07 09:30 | 8 | 10.1 | 317.5 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-07 10:30 | 8 | 10.3 | 312.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-07-07 11:30 | 8 | 10.3 | 310 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-07-07 12:30 | 8.3 | 10.4 | 307.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-07-07 13:30 | 8.2 | 10.7 | 302.5 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-07-07 14:30 | 8.2 | 11.2 | 297.5 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-07-07 15:30 | 8.2 | 11.7 | 292.5 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-07-07 16:30 | 8.3 | 11.9 | 290 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-07-07 17:30 | 8.1 | 11.6 | 290 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-07-07 18:30 | 7.6 | 11.6 | 290 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-07-07 19:30 | 7.3 | 11.5 | 290 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-07-07 20:30 | 7.2 | 11.4 | 287.5 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-07-07 21:30 | 7 | 12 | 282.5 | 1450 | 1395 | 1075 | 0 |  | 0 |  | 320
Lerwick | 1978-07-07 22:30 | 6.9 | 12.8 | 280 | 1470 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-07-07 23:30 | 6.7 | 13.2 | 280 | 1480 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-07-08 00:30 | 6.7 | 13.2 | 280 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-07-08 01:30 | 6.7 | 12.8 | 280 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-07-08 02:30 | 6.6 | 12.1 | 282.5 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-07-08 03:30 | 6.6 | 11.3 | 285 | 1340 | 1395 | 1075 | 0 |  | 0 |  | 320
Lerwick | 1978-07-08 04:30 | 6.8 | 10.5 | 285 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-07-08 05:30 | 7 | 10.1 | 287.5 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-07-08 06:30 | 7.3 | 9.9 | 290 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-08 07:30 | 7.5 | 9.6 | 290 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-07-08 08:30 | 7.8 | 9.1 | 292.5 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-08 09:30 | 8 | 8.4 | 297.5 | 635 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-08 10:30 | 8.4 | 8 | 300 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-07-08 11:30 | 8.9 | 7.8 | 300 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-08 12:30 | 9.5 | 7.6 | 297.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-07-08 13:30 | 10.3 | 7.2 | 292.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-08 14:30 | 10.8 | 6.7 | 290 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-07-08 15:30 | 11.1 | 6.3 | 290 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-07-08 16:30 | 11.2 | 6.2 | 290 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-07-08 17:30 | 10.8 | 6.4 | 287.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-07-08 18:30 | 10.2 | 7.2 | 282.5 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-07-08 19:30 | 9.5 | 7.9 | 280 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-08 20:30 | 9.2 | 8.1 | 280 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-08 21:30 | 8.9 | 7.9 | 282.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-08 22:30 | 8.4 | 6.9 | 287.5 | 300 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-07-08 23:30 | 8.1 | 5.3 | 290 | 110 | 205 | 0 | 115 |  | 55.2 |  | 205
Lerwick | 1978-07-09 00:30 | 8.1 | 3.8 | 287.5 | 25 | 67.5 | 0 | 252.5 |  | 121.2 |  | 67.5
Lerwick | 1978-07-09 01:30 | 8.1 | 4.1 | 282.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-07-09 02:30 | 7.9 | 5.6 | 282.5 | 150 | 105 | 0 | 215 |  | 103.2 |  | 105
Lerwick | 1978-07-09 03:30 | 8.1 | 6.3 | 285 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-07-09 04:30 | 8.7 | 6 | 285 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-07-09 05:30 | 8.8 | 5.2 | 287.5 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-07-09 06:30 | 9.8 | 4 | 290 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-07-09 07:30 | 11.6 | 3.7 | 290 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-07-09 08:30 | 12.8 | 3.9 | 297.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-07-09 09:30 | 13.6 | 4.2 | 330 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-07-09 10:30 | 15.3 | 4.4 | 192.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-07-09 11:30 | 15.6 | 4.2 | 27.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-07-09 12:30 | 13.5 | 3.8 | 22.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-07-09 13:30 | 12.1 | 3.3 | 27.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-07-09 14:30 | 12 | 2.9 | 37.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-09 15:30 | 12.7 | 2.6 | 37.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-09 16:30 | 13.4 | 2.2 | 17.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-09 17:30 | 13 | 1.5 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-09 18:30 | 11.9 | 1.1 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-09 19:30 | 11.1 | 1.1 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-09 20:30 | 10.5 | 1.4 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-09 21:30 | 9.9 | 1.4 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-09 22:30 | 9.4 | 1.1 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-09 23:30 | 9 | 1.1 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-10 00:30 | 8.7 | 1.7 | 120 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-10 01:30 | 8.2 | 2.3 | 227.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-10 02:30 | 8 | 2.3 | 215 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-10 03:30 | 8 | 1.8 | 222.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-10 04:30 | 7.8 | 1.5 | 230 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-10 05:30 | 7.6 | 1.5 | 232.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-10 06:30 | 7.7 | 1.4 | 237.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-10 07:30 | 7.8 | 1.1 | 247.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-10 08:30 | 7.9 | 1 | 127.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-10 09:30 | 8.3 | 1.2 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-10 10:30 | 9.3 | 1.8 | 80 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-10 11:30 | 10 | 2.3 | 165 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-10 12:30 | 10.8 | 2.8 | 157.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-10 13:30 | 11.8 | 2.8 | 145 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-10 14:30 | 11.9 | 2.2 | 145 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-10 15:30 | 11.6 | 1.6 | 157.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-10 16:30 | 11.1 | 1.5 | 157.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-10 17:30 | 10.5 | 1.5 | 112.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-10 18:30 | 10 | 1.5 | 60 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-10 19:30 | 9.7 | 1.8 | 30 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-10 20:30 | 9.4 | 2.7 | 22.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-10 21:30 | 9.1 | 3.3 | 25 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-10 22:30 | 8.6 | 3.2 | 22.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-10 23:30 | 8.4 | 3.1 | 15 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-11 00:30 | 8.4 | 3.2 | 182.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-11 01:30 | 8.3 | 3.4 | 177.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-11 02:30 | 8.5 | 3.6 | 5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-07-11 03:30 | 8.8 | 3.6 | 10 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-07-11 04:30 | 9 | 3.7 | 10 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-07-11 05:30 | 9.1 | 4.2 | 10 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-07-11 06:30 | 9.4 | 4.9 | 12.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-07-11 07:30 | 9.4 | 5.5 | 17.5 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-07-11 08:30 | 9.6 | 5.7 | 22.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-11 09:30 | 9.8 | 5.7 | 27.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-11 10:30 | 10.5 | 5.8 | 30 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-11 11:30 | 11.1 | 5.9 | 30 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-11 12:30 | 11.2 | 5.9 | 30 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-11 13:30 | 11.7 | 6 | 30 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-07-11 14:30 | 11.8 | 6.2 | 30 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-07-11 15:30 | 11.8 | 6.2 | 30 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-07-11 16:30 | 11.7 | 6.3 | 27.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-07-11 17:30 | 11.4 | 6.4 | 22.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-07-11 18:30 | 10.9 | 6.1 | 20 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-07-11 19:30 | 10.3 | 5.8 | 17.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-07-11 20:30 | 9.7 | 5.7 | 10 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-11 21:30 | 9.3 | 5.3 | 180 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-07-11 22:30 | 9.1 | 4.7 | 352.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-07-11 23:30 | 8.9 | 4.2 | 347.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-07-12 00:30 | 8.7 | 3.9 | 340 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-07-12 01:30 | 8.7 | 4.1 | 337.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-07-12 02:30 | 9 | 4.7 | 347.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-07-12 03:30 | 8.7 | 5.2 | 177.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-07-12 04:30 | 8.4 | 5.5 | 2.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-07-12 05:30 | 8.4 | 5.7 | 7.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-12 06:30 | 8.6 | 5.7 | 10 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-12 07:30 | 8.9 | 5.5 | 7.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-12 08:30 | 9 | 5.1 | 5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-07-12 09:30 | 9.2 | 4.6 | 10 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-07-12 10:30 | 9.5 | 4.2 | 7.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-07-12 11:30 | 9.7 | 3.9 | 172.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-07-12 12:30 | 10 | 3.9 | 350 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-07-12 13:30 | 10.5 | 3.9 | 347.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-07-12 14:30 | 10.6 | 4 | 330 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-07-12 15:30 | 10.2 | 4 | 320 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-07-12 16:30 | 10.1 | 3.9 | 317.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-07-12 17:30 | 10.1 | 3.9 | 312.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-07-12 18:30 | 10 | 3.9 | 310 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-07-12 19:30 | 9.9 | 3.9 | 307.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-07-12 20:30 | 9.7 | 3.7 | 300 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-07-12 21:30 | 9.5 | 3.6 | 292.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-07-12 22:30 | 9.2 | 3.6 | 290 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-07-12 23:30 | 9 | 3.8 | 290 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-07-13 00:30 | 8.9 | 4.4 | 290 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-07-13 01:30 | 8.8 | 4.9 | 285 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-07-13 02:30 | 8.8 | 4.9 | 275 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-07-13 03:30 | 8.6 | 4.9 | 270 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-07-13 04:30 | 8.5 | 5.3 | 270 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-07-13 05:30 | 8.4 | 6.2 | 272.5 | 220 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-07-13 06:30 | 8.6 | 6.9 | 277.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-07-13 07:30 | 8.5 | 7.2 | 277.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-07-13 08:30 | 8.2 | 7.2 | 275 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-07-13 09:30 | 8.4 | 7.3 | 275 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-07-13 10:30 | 8.8 | 7.7 | 272.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-13 11:30 | 9.3 | 8.5 | 270 | 770 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-07-13 12:30 | 9.7 | 9.5 | 270 | 1025 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-13 13:30 | 10.2 | 9.9 | 272.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-07-13 14:30 | 10.8 | 9.3 | 280 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-13 15:30 | 11 | 8.2 | 287.5 | 635 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-13 16:30 | 10.8 | 7 | 292.5 | 400 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-13 17:30 | 10.6 | 6.1 | 297.5 | 220 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-07-13 18:30 | 10.4 | 6.4 | 297.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-07-13 19:30 | 10.1 | 7.3 | 295 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-07-13 20:30 | 9.4 | 7.8 | 300 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-13 21:30 | 9.1 | 8 | 310 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-13 22:30 | 8.8 | 7.5 | 317.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-13 23:30 | 8.2 | 6.7 | 320 | 300 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-07-14 00:30 | 8 | 6.5 | 320 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-07-14 01:30 | 8 | 6.8 | 320 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-07-14 02:30 | 7.7 | 7.2 | 320 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-07-14 03:30 | 7.3 | 7.5 | 320 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-14 04:30 | 7.1 | 7.5 | 320 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-07-14 05:30 | 7.1 | 7.6 | 322.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-07-14 06:30 | 7.2 | 7.7 | 325 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-07-14 07:30 | 7.5 | 7.7 | 322.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-07-14 08:30 | 7.8 | 7.8 | 320 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-07-14 09:30 | 8.5 | 8 | 320 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-14 10:30 | 8.7 | 7.8 | 320 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-14 11:30 | 8.6 | 7.7 | 317.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-07-14 12:30 | 8.7 | 7.6 | 312.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-07-14 13:30 | 8.7 | 7.3 | 310 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-14 14:30 | 8.5 | 7.3 | 310 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-07-14 15:30 | 8.6 | 7.5 | 310 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-14 16:30 | 8.7 | 7.2 | 312.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-14 17:30 | 8.4 | 6.8 | 315 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-07-14 18:30 | 8.2 | 6.7 | 312.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-07-14 19:30 | 7.9 | 6.5 | 310 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-07-14 20:30 | 7.8 | 6.4 | 305 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-07-14 21:30 | 7.7 | 6.4 | 292.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-07-14 22:30 | 7.5 | 6 | 282.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-07-14 23:30 | 7.5 | 5.3 | 280 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-07-15 00:30 | 7.6 | 4.9 | 280 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-07-15 01:30 | 7.8 | 5.3 | 277.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-07-15 02:30 | 7.9 | 5.7 | 270 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-07-15 03:30 | 7.9 | 5.7 | 262.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-15 04:30 | 7.9 | 5.8 | 257.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-15 05:30 | 8 | 5.8 | 252.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-15 06:30 | 8.2 | 5.5 | 250 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-15 07:30 | 8.1 | 5.5 | 247.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-15 08:30 | 8.4 | 5.8 | 247.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-15 09:30 | 8.8 | 6.1 | 257.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-07-15 10:30 | 9.1 | 6.5 | 267.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-07-15 11:30 | 9.7 | 6.7 | 270 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-07-15 12:30 | 9.9 | 6.7 | 272.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-07-15 13:30 | 10 | 6.7 | 280 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-07-15 14:30 | 10.2 | 6.9 | 290 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-07-15 15:30 | 10.4 | 7.1 | 297.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-07-15 16:30 | 10.5 | 7 | 302.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-07-15 17:30 | 10.4 | 7.3 | 310 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-07-15 18:30 | 9.7 | 7.8 | 317.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-15 19:30 | 9.2 | 7.8 | 317.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-07-15 20:30 | 8.8 | 7.3 | 312.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-15 21:30 | 7.8 | 6.6 | 312.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-07-15 22:30 | 7.1 | 5.6 | 317.5 | 150 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-07-15 23:30 | 6.9 | 4.9 | 320 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-07-16 00:30 | 6.6 | 5.1 | 320 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-07-16 01:30 | 6.5 | 5.6 | 320 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-07-16 02:30 | 6.7 | 6.1 | 320 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-07-16 03:30 | 6.9 | 6.1 | 317.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-07-16 04:30 | 6.9 | 5.8 | 312.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-07-16 05:30 | 6.9 | 5.9 | 312.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-16 06:30 | 7.3 | 6 | 317.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-07-16 07:30 | 8.1 | 5.8 | 317.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-07-16 08:30 | 8.7 | 5.7 | 310 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-16 09:30 | 9.2 | 5.8 | 302.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-16 10:30 | 9.2 | 5.9 | 302.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-16 11:30 | 9.1 | 5.8 | 307.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-16 12:30 | 9.3 | 5.7 | 307.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-16 13:30 | 9.8 | 5.5 | 302.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-16 14:30 | 10.6 | 5.9 | 290 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-16 15:30 | 11.1 | 6.8 | 272.5 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-07-16 16:30 | 10.4 | 6.7 | 267.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-07-16 17:30 | 9.5 | 5.6 | 275 | 150 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-07-16 18:30 | 8.9 | 4.5 | 282.5 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-07-16 19:30 | 8.5 | 3.8 | 282.5 | 25 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-07-16 20:30 | 8.3 | 3.4 | 277.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-07-16 21:30 | 8 | 3.3 | 270 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-16 22:30 | 7.9 | 3.2 | 257.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-16 23:30 | 7.8 | 2.6 | 245 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-17 00:30 | 7.7 | 2 | 235 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-17 01:30 | 7.6 | 2.2 | 225 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-17 02:30 | 7.7 | 3.2 | 217.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-17 03:30 | 8.1 | 4.1 | 212.5 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-07-17 04:30 | 8.3 | 4.7 | 207.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-07-17 05:30 | 8.4 | 5.4 | 202.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-07-17 06:30 | 8.8 | 6.3 | 202.5 | 220 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-07-17 07:30 | 9.2 | 6.9 | 207.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-07-17 08:30 | 9.3 | 7.2 | 210 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-07-17 09:30 | 9.4 | 7.2 | 210 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-07-17 10:30 | 9.4 | 7.4 | 212.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-07-17 11:30 | 9.7 | 7.7 | 215 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-17 12:30 | 10 | 7.4 | 210 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-17 13:30 | 10 | 6.9 | 200 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-07-17 14:30 | 10 | 6.4 | 192.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-07-17 15:30 | 10 | 6.2 | 187.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-07-17 16:30 | 10 | 6 | 182.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-07-17 17:30 | 10.2 | 5.6 | 180 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-07-17 18:30 | 10.5 | 4.9 | 177.5 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-07-17 19:30 | 10.2 | 4.1 | 175 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-07-17 20:30 | 9.7 | 3.9 | 175 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-07-17 21:30 | 9.4 | 3.7 | 170 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-07-17 22:30 | 9.5 | 3.6 | 162.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-07-17 23:30 | 9.5 | 3.1 | 157.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-07-18 00:30 | 9.5 | 2.1 | 160 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-18 01:30 | 9.5 | 1.2 | 207.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-18 02:30 | 9.6 | 1.2 | 287.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-18 03:30 | 9.6 | 1.8 | 330 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-18 04:30 | 9.6 | 2.4 | 337.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-18 05:30 | 9.6 | 2.9 | 342.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-18 06:30 | 9.7 | 2.9 | 345 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-18 07:30 | 9.9 | 2.9 | 340 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-18 08:30 | 10 | 3.3 | 330 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-18 09:30 | 10 | 3.4 | 322.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-18 10:30 | 10.2 | 2.9 | 327.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-18 11:30 | 10.5 | 2.6 | 327.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-18 12:30 | 10.5 | 3.2 | 300 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-18 13:30 | 10.9 | 4.4 | 277.5 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-07-18 14:30 | 11.4 | 5.1 | 277.5 | 110 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-07-18 15:30 | 11.5 | 5.4 | 282.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-07-18 16:30 | 11.2 | 5.4 | 285 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-07-18 17:30 | 11 | 5.5 | 280 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-07-18 18:30 | 10.7 | 5.7 | 272.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-18 19:30 | 9.9 | 5.3 | 270 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-07-18 20:30 | 8.9 | 4.4 | 267.5 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-07-18 21:30 | 8.5 | 3.9 | 262.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-07-18 22:30 | 8.1 | 3.9 | 260 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-07-18 23:30 | 7.8 | 3.9 | 260 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-07-19 00:30 | 8 | 3.9 | 257.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-07-19 01:30 | 8.1 | 3.6 | 252.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-07-19 02:30 | 8 | 3 | 252.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-07-19 03:30 | 7.9 | 2.6 | 260 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-19 04:30 | 7.9 | 2.3 | 270 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-19 05:30 | 8 | 1.8 | 280 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-19 06:30 | 8.1 | 1.6 | 285 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-19 07:30 | 8.3 | 2 | 280 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-19 08:30 | 9 | 2.4 | 137.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-19 09:30 | 9.4 | 2.2 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-19 10:30 | 9.6 | 1.5 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-19 11:30 | 9.6 | 1.4 | 32.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-19 12:30 | 9.4 | 1.4 | 32.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-19 13:30 | 9.2 | 1.1 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-19 14:30 | 9 | 1 | 57.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-19 15:30 | 9 | 1.1 | 95 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-19 16:30 | 9 | 1.9 | 57.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-19 17:30 | 9.2 | 3.7 | 37.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-07-19 18:30 | 9.2 | 5.8 | 40 | 150 | 87.5 | 0 | 232.5 |  | 111.6 |  | 87.5
Lerwick | 1978-07-19 19:30 | 9 | 6.9 | 45 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-07-19 20:30 | 9 | 7.3 | 40 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-07-19 21:30 | 9.2 | 7.5 | 30 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-19 22:30 | 9.3 | 7.2 | 22.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-19 23:30 | 9.1 | 6.8 | 15 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-07-20 00:30 | 8.8 | 6.3 | 182.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-07-20 01:30 | 8.3 | 5.6 | 352.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-07-20 02:30 | 8.1 | 5.8 | 347.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-20 03:30 | 8 | 6.4 | 345 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-07-20 04:30 | 7.9 | 6.9 | 342.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-07-20 05:30 | 8.2 | 7.4 | 335 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-07-20 06:30 | 8.7 | 7.9 | 330 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-20 07:30 | 9.5 | 8.3 | 327.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-20 08:30 | 9.8 | 8.5 | 322.5 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-20 09:30 | 9.6 | 8.6 | 320 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-07-20 10:30 | 9.4 | 8.6 | 320 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-07-20 11:30 | 9.4 | 8.3 | 320 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-20 12:30 | 9.4 | 8.3 | 322.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-07-20 13:30 | 9.4 | 8.6 | 327.5 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-20 14:30 | 9.6 | 8.9 | 330 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-07-20 15:30 | 9.8 | 9.1 | 330 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-07-20 16:30 | 10.1 | 9 | 330 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-07-20 17:30 | 10.1 | 8.4 | 330 | 635 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-20 18:30 | 9.7 | 8.3 | 327.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-07-20 19:30 | 9.3 | 8.5 | 322.5 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-20 20:30 | 8.8 | 8.5 | 317.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-07-20 21:30 | 8.4 | 8.6 | 315 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-07-20 22:30 | 8.2 | 8.4 | 315 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-20 23:30 | 8 | 8 | 315 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-07-21 00:30 | 7.8 | 8.4 | 315 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-07-21 01:30 | 7.5 | 8.8 | 310 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-21 02:30 | 7.1 | 8.8 | 302.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-07-21 03:30 | 7 | 8.9 | 300 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-07-21 04:30 | 7 | 8.7 | 300 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-07-21 05:30 | 7 | 8.2 | 297.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-21 06:30 | 7 | 8 | 292.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-07-21 07:30 | 7.1 | 8.7 | 290 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-21 08:30 | 7.4 | 9.3 | 290 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-07-21 09:30 | 7.6 | 9.1 | 287.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-07-21 10:30 | 7.8 | 9.1 | 282.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-07-21 11:30 | 7.9 | 9.1 | 280 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-07-21 12:30 | 8.4 | 8.7 | 280 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-07-21 13:30 | 8.9 | 8.3 | 277.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-21 14:30 | 8.9 | 8 | 272.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-07-21 15:30 | 8.7 | 8 | 267.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-07-21 16:30 | 8.7 | 8 | 262.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-07-21 17:30 | 8.7 | 7.5 | 262.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-21 18:30 | 8.5 | 6.3 | 262.5 | 220 | 360 | 40 | 0 |  | 0 |  | 320
Lerwick | 1978-07-21 19:30 | 8.5 | 4.8 | 250 | 80 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-21 20:30 | 8.3 | 3.6 | 230 | 25 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-07-21 21:30 | 8 | 3.3 | 212.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-07-21 22:30 | 8.2 | 3.4 | 202.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-21 23:30 | 7.9 | 3.7 | 200 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-07-22 00:30 | 7.7 | 3.9 | 197.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-07-22 01:30 | 8.2 | 4.2 | 190 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-07-22 02:30 | 8.5 | 4.9 | 180 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-07-22 03:30 | 8.8 | 5.9 | 170 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-07-22 04:30 | 9 | 6.9 | 160 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-07-22 05:30 | 9.2 | 7.6 | 152.5 | 500 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-07-22 06:30 | 9.7 | 7.7 | 150 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-07-22 07:30 | 9.7 | 7.8 | 150 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-07-22 08:30 | 9.8 | 8 | 150 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-22 09:30 | 10.3 | 7.7 | 150 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-22 10:30 | 11 | 7.3 | 150 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-22 11:30 | 12.3 | 7.3 | 150 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-07-22 12:30 | 12.8 | 7.6 | 152.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-22 13:30 | 11.9 | 7.8 | 157.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-07-22 14:30 | 11.4 | 8 | 160 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-22 15:30 | 11.3 | 8 | 160 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-07-22 16:30 | 11.4 | 8.5 | 160 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-22 17:30 | 11.4 | 9.4 | 160 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-07-22 18:30 | 11.4 | 9.6 | 160 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-22 19:30 | 11.3 | 8.8 | 160 | 770 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-22 20:30 | 11.1 | 7.9 | 160 | 500 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-07-22 21:30 | 11 | 7.6 | 160 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-07-22 22:30 | 11 | 7.1 | 160 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-22 23:30 | 11 | 6.3 | 162.5 | 220 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-07-23 00:30 | 11 | 5.4 | 167.5 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-07-23 01:30 | 11 | 4.7 | 170 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-07-23 02:30 | 11 | 4.7 | 170 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-07-23 03:30 | 10.9 | 4.7 | 167.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-07-23 04:30 | 10.7 | 4.5 | 165 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-07-23 05:30 | 10.7 | 4.7 | 165 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-07-23 06:30 | 10.9 | 5.3 | 162.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-07-23 07:30 | 11 | 5.7 | 160 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-07-23 08:30 | 11.1 | 5.5 | 162.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-23 09:30 | 11 | 4.9 | 165 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-07-23 10:30 | 11.1 | 4.4 | 165 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-07-23 11:30 | 11.3 | 4.7 | 167.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-07-23 12:30 | 11.3 | 5.6 | 167.5 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-07-23 13:30 | 12.4 | 6.3 | 162.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-07-23 14:30 | 13.8 | 6.3 | 162.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-07-23 15:30 | 14.3 | 6 | 165 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-07-23 16:30 | 13.8 | 5.8 | 162.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-07-23 17:30 | 13 | 5.8 | 162.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-23 18:30 | 12.4 | 5.8 | 165 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-23 19:30 | 11.8 | 5.1 | 157.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-07-23 20:30 | 11.4 | 4.4 | 150 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-07-23 21:30 | 10.9 | 4.2 | 157.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-07-23 22:30 | 10.5 | 3.8 | 177.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-07-23 23:30 | 10.5 | 3.3 | 202.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-07-24 00:30 | 10.7 | 2.4 | 107.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-24 01:30 | 11 | 1.1 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-24 02:30 | 10.9 | 0.2 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-24 03:30 | 10.4 | 0 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-24 04:30 | 9.8 | 0 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-24 05:30 | 9.8 | 1.1 | 145 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-24 06:30 | 11 | 3.8 | 262.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-07-24 07:30 | 11.5 | 5.9 | 240 | 150 | 87.5 | 0 | 232.5 |  | 111.6 |  | 87.5
Lerwick | 1978-07-24 08:30 | 11.7 | 6.4 | 235 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-07-24 09:30 | 12.5 | 6.4 | 205 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-07-24 10:30 | 12.8 | 6.7 | 175 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-07-24 11:30 | 13.6 | 7.2 | 167.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-07-24 12:30 | 13.7 | 7.7 | 172.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-24 13:30 | 13.6 | 7.7 | 177.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-07-24 14:30 | 14.1 | 6.9 | 180 | 300 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-07-24 15:30 | 13.4 | 6.1 | 177.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-07-24 16:30 | 12.2 | 5.9 | 175 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-07-24 17:30 | 11.7 | 5.9 | 177.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-24 18:30 | 11.9 | 6 | 182.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-07-24 19:30 | 12 | 6.7 | 192.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-07-24 20:30 | 11.4 | 7.1 | 200 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-07-24 21:30 | 11 | 7 | 195 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-07-24 22:30 | 11 | 7.3 | 190 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-07-24 23:30 | 10.5 | 7.9 | 192.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-25 00:30 | 10.1 | 8.5 | 195 | 770 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-07-25 01:30 | 9.9 | 9.1 | 195 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-07-25 02:30 | 9.7 | 9.8 | 200 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-25 03:30 | 9.8 | 10.8 | 207.5 | 1270 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-25 04:30 | 10 | 11.1 | 210 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-07-25 05:30 | 10.1 | 11.2 | 210 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-07-25 06:30 | 10.3 | 12 | 212.5 | 1450 | 1395 | 1075 | 0 |  | 0 |  | 320
Lerwick | 1978-07-25 07:30 | 10.3 | 12.5 | 217.5 | 1470 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-07-25 08:30 | 10.4 | 12.2 | 222.5 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-07-25 09:30 | 10.7 | 12 | 227.5 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-25 10:30 | 10.9 | 11.9 | 230 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-07-25 11:30 | 11.1 | 11.5 | 232.5 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-07-25 12:30 | 11.1 | 11.1 | 232.5 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-07-25 13:30 | 11.6 | 10.4 | 222.5 | 1150 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-07-25 14:30 | 12.2 | 8.9 | 212.5 | 770 | 960 | 640 | 0 |  | 0 |  | 320
Lerwick | 1978-07-25 15:30 | 11.7 | 7.2 | 202.5 | 400 | 585 | 265 | 0 |  | 0 |  | 320
Lerwick | 1978-07-25 16:30 | 11.9 | 6 | 185 | 220 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-07-25 17:30 | 12.4 | 5.1 | 172.5 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-07-25 18:30 | 12 | 4 | 170 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-07-25 19:30 | 11.1 | 3.7 | 165 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-07-25 20:30 | 10.7 | 4.4 | 157.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-07-25 21:30 | 10.4 | 5.3 | 157.5 | 110 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-07-25 22:30 | 10.3 | 5.3 | 157.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-07-25 23:30 | 10.3 | 4.7 | 150 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-07-26 00:30 | 10.3 | 4.9 | 145 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-07-26 01:30 | 10.5 | 5.8 | 147.5 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-07-26 02:30 | 10.7 | 6.6 | 150 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-07-26 03:30 | 10.8 | 7 | 150 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-07-26 04:30 | 10.7 | 7 | 147.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-07-26 05:30 | 10.5 | 7.2 | 142.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-07-26 06:30 | 10.7 | 7.6 | 140 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-26 07:30 | 11 | 7.7 | 142.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-07-26 08:30 | 11 | 7.6 | 147.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-07-26 09:30 | 11 | 7.5 | 150 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-07-26 10:30 | 11.2 | 7.7 | 150 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-07-26 11:30 | 11.7 | 8.2 | 152.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-26 12:30 | 11.9 | 8.6 | 157.5 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-26 13:30 | 11.6 | 8.2 | 157.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-26 14:30 | 11.6 | 7.3 | 152.5 | 400 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-26 15:30 | 11.6 | 7.2 | 147.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-07-26 16:30 | 11.4 | 7.6 | 142.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-26 17:30 | 11.4 | 7.4 | 140 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-26 18:30 | 11.3 | 6.7 | 140 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-07-26 19:30 | 11.2 | 5.8 | 142.5 | 150 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-07-26 20:30 | 11.1 | 5.1 | 147.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-07-26 21:30 | 11.1 | 4.6 | 150 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-07-26 22:30 | 11.1 | 4 | 150 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-07-26 23:30 | 11 | 3.1 | 157.5 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-07-27 00:30 | 11 | 2.4 | 177.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-27 01:30 | 11 | 2 | 190 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-27 02:30 | 11.2 | 1.6 | 182.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-27 03:30 | 11 | 1.5 | 172.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-27 04:30 | 10.9 | 1.5 | 175 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-27 05:30 | 10.9 | 1.8 | 182.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-27 06:30 | 10.9 | 3 | 182.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-27 07:30 | 11.1 | 4.4 | 180 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-07-27 08:30 | 11.3 | 5.3 | 177.5 | 110 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-07-27 09:30 | 11.2 | 5.7 | 172.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-07-27 10:30 | 10.7 | 5.3 | 165 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-07-27 11:30 | 10.7 | 4.7 | 157.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-07-27 12:30 | 11.2 | 4.9 | 160 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-07-27 13:30 | 11.9 | 6 | 165 | 220 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-27 14:30 | 12.4 | 7.2 | 162.5 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-07-27 15:30 | 12.4 | 8.1 | 160 | 635 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-27 16:30 | 12.4 | 8.6 | 160 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-27 17:30 | 12.2 | 8.8 | 160 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-07-27 18:30 | 11.8 | 8.4 | 162.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-27 19:30 | 11.5 | 8 | 167.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-07-27 20:30 | 11.5 | 7.8 | 170 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-27 21:30 | 11.5 | 7.2 | 172.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-27 22:30 | 11.5 | 6.2 | 177.5 | 220 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-07-27 23:30 | 11.5 | 5.3 | 180 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-07-28 00:30 | 11.5 | 5.3 | 177.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-07-28 01:30 | 11.5 | 5.9 | 172.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-07-28 02:30 | 11.7 | 6.6 | 170 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-07-28 03:30 | 11.7 | 7 | 172.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-07-28 04:30 | 11.5 | 6.6 | 177.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-07-28 05:30 | 11.5 | 6.2 | 177.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-07-28 06:30 | 11.5 | 5.5 | 172.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-07-28 07:30 | 11.5 | 4.4 | 170 | 60 | 105 | 0 | 215 |  | 103.2 |  | 105
Lerwick | 1978-07-28 08:30 | 11.5 | 4.8 | 170 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-07-28 09:30 | 11.7 | 6.4 | 167.5 | 220 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-28 10:30 | 12.8 | 7.4 | 165 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-07-28 11:30 | 13.8 | 8.3 | 175 | 635 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-28 12:30 | 13.4 | 9.7 | 202.5 | 1025 | 830 | 510 | 0 |  | 0 |  | 320
Lerwick | 1978-07-28 13:30 | 13 | 11 | 232.5 | 1340 | 1182.5 | 862.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-28 14:30 | 12.7 | 11.2 | 247.5 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-07-28 15:30 | 12.7 | 10.4 | 247.5 | 1150 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-07-28 16:30 | 13.5 | 9.4 | 240 | 900 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-07-28 17:30 | 14 | 9 | 230 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-07-28 18:30 | 13.7 | 8.5 | 220 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-07-28 19:30 | 13.1 | 7.1 | 205 | 400 | 585 | 265 | 0 |  | 0 |  | 320
Lerwick | 1978-07-28 20:30 | 12.6 | 5.3 | 190 | 110 | 255 | 0 | 65 |  | 31.2 |  | 255
Lerwick | 1978-07-28 21:30 | 11.7 | 4.1 | 182.5 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-07-28 22:30 | 11 | 3.9 | 175 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-07-28 23:30 | 11 | 3.7 | 172.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-07-29 00:30 | 10.7 | 3.6 | 175 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-07-29 01:30 | 10.4 | 3.6 | 172.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-07-29 02:30 | 10.4 | 3.4 | 165 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-07-29 03:30 | 10.4 | 3.3 | 155 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-29 04:30 | 10.4 | 3.3 | 152.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-29 05:30 | 10.7 | 3.4 | 157.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-29 06:30 | 11.5 | 4 | 160 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-07-29 07:30 | 11.8 | 4.4 | 162.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-07-29 08:30 | 12.2 | 4.4 | 162.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-07-29 09:30 | 13.1 | 4.4 | 157.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-07-29 10:30 | 13.5 | 4.4 | 157.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-07-29 11:30 | 13.9 | 4.9 | 160 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-07-29 12:30 | 14 | 5.8 | 160 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-07-29 13:30 | 14 | 5.9 | 157.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-07-29 14:30 | 14.3 | 5.3 | 155 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-07-29 15:30 | 14.7 | 5 | 157.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-07-29 16:30 | 14.5 | 4.7 | 157.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-07-29 17:30 | 14.1 | 4.2 | 155 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-07-29 18:30 | 13.3 | 3.8 | 160 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-07-29 19:30 | 12.6 | 2.9 | 165 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-07-29 20:30 | 12 | 1.8 | 177.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-29 21:30 | 10.9 | 1.5 | 95 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-29 22:30 | 10.3 | 1.4 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-29 23:30 | 9.8 | 1.1 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-30 00:30 | 9.5 | 1 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-30 01:30 | 9.3 | 1 | 77.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-30 02:30 | 9.4 | 1 | 157.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-30 03:30 | 9.6 | 1.1 | 157.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-30 04:30 | 9.6 | 1.3 | 147.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-30 05:30 | 9.9 | 1.4 | 142.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-30 06:30 | 10.7 | 1.8 | 150 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-30 07:30 | 11.4 | 2.4 | 152.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-30 08:30 | 12 | 2.6 | 152.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-30 09:30 | 12.3 | 2.4 | 165 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-30 10:30 | 12.5 | 2.1 | 172.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-30 11:30 | 13 | 2.3 | 160 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-30 12:30 | 13 | 2.6 | 150 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-30 13:30 | 12.6 | 2.6 | 152.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-30 14:30 | 12.7 | 2.3 | 152.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-30 15:30 | 13.1 | 2.1 | 125 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-30 16:30 | 13.3 | 2.1 | 67.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-30 17:30 | 13.1 | 2.1 | 25 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-30 18:30 | 12.6 | 2.9 | 20 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-07-30 19:30 | 12.1 | 4 | 25 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-07-30 20:30 | 11.6 | 4.7 | 22.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-07-30 21:30 | 11.2 | 5.2 | 17.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-07-30 22:30 | 11 | 5.8 | 10 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-07-30 23:30 | 11 | 6.8 | 2.5 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-07-31 00:30 | 11 | 8.1 | 0 | 635 | 467.5 | 147.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-31 01:30 | 10.7 | 9 | 0 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-31 02:30 | 10.5 | 9.3 | 0 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-07-31 03:30 | 10.5 | 9.4 | 0 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-07-31 04:30 | 10.7 | 9.5 | 0 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-31 05:30 | 10.8 | 9.4 | 0 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-31 06:30 | 10.8 | 9.3 | 177.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-07-31 07:30 | 10.9 | 9.1 | 352.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-07-31 08:30 | 11 | 8.7 | 350 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-07-31 09:30 | 11.3 | 8.5 | 350 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-07-31 10:30 | 11.5 | 8.6 | 352.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-07-31 11:30 | 11.9 | 9 | 177.5 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-07-31 12:30 | 12.7 | 9.5 | 2.5 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-31 13:30 | 13.5 | 9.6 | 5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-07-31 14:30 | 13.9 | 9.2 | 5 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-31 15:30 | 14.4 | 8.7 | 10 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-07-31 16:30 | 13.8 | 8.1 | 15 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-31 17:30 | 12.8 | 7.4 | 12.5 | 400 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-31 18:30 | 12.5 | 7.2 | 10 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-07-31 19:30 | 12.1 | 7.3 | 7.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-07-31 20:30 | 11.8 | 7.8 | 2.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-07-31 21:30 | 11.3 | 8.4 | 0 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-31 22:30 | 11 | 8.8 | 2.5 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-07-31 23:30 | 11 | 8.9 | 7.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-08-01 00:30 | 11 | 9.4 | 10 | 900 | 835 | 515 | 0 |  | 0 | 63324 | 320 | 106155
Lerwick | 1978-08-01 01:30 | 11 | 9.9 | 10 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-01 02:30 | 10.9 | 9.9 | 10 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-08-01 03:30 | 10.9 | 9.9 | 10 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-08-01 04:30 | 10.9 | 10.4 | 10 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-01 05:30 | 10.7 | 11 | 12.5 | 1340 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-08-01 06:30 | 10.5 | 11.3 | 17.5 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-08-01 07:30 | 10.5 | 11.4 | 20 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-08-01 08:30 | 10.7 | 11.7 | 20 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-08-01 09:30 | 10.7 | 12 | 20 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-08-01 10:30 | 10.7 | 11.7 | 20 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-08-01 11:30 | 10.9 | 11.4 | 20 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-08-01 12:30 | 11 | 11.3 | 20 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-08-01 13:30 | 11 | 11.3 | 20 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-08-01 14:30 | 11 | 11.3 | 20 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-08-01 15:30 | 11.1 | 11.1 | 22.5 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-08-01 16:30 | 11.3 | 10.7 | 25 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-08-01 17:30 | 11.4 | 10 | 25 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-08-01 18:30 | 11.2 | 9.2 | 27.5 | 900 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-08-01 19:30 | 11 | 9 | 30 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-08-01 20:30 | 10.9 | 8.5 | 30 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-08-01 21:30 | 10.6 | 7.5 | 30 | 500 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-08-01 22:30 | 10.5 | 6.4 | 30 | 220 | 360 | 40 | 0 |  | 0 |  | 320
Lerwick | 1978-08-01 23:30 | 10.5 | 5.6 | 30 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-08-02 00:30 | 10.5 | 5.5 | 30 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-08-02 01:30 | 10.6 | 5.9 | 27.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-08-02 02:30 | 10.9 | 6.3 | 22.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-08-02 03:30 | 10.7 | 6.3 | 17.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-02 04:30 | 10.5 | 6 | 15 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-02 05:30 | 10.5 | 5.4 | 20 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-08-02 06:30 | 11 | 4.4 | 30 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-08-02 07:30 | 11.5 | 3.6 | 57.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-08-02 08:30 | 12 | 3 | 105 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-02 09:30 | 12.6 | 2.4 | 137.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-02 10:30 | 13.2 | 2.6 | 150 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-02 11:30 | 13.4 | 2.9 | 177.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-02 12:30 | 13.1 | 2.4 | 200 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-02 13:30 | 13.3 | 2.4 | 175 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-02 14:30 | 13.7 | 2.6 | 150 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-02 15:30 | 13.1 | 2.6 | 155 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-02 16:30 | 12.4 | 2.4 | 165 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-02 17:30 | 12.1 | 2.1 | 137.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-02 18:30 | 12 | 2.4 | 67.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-02 19:30 | 11.9 | 3 | 27.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-02 20:30 | 11.3 | 3.6 | 25 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-02 21:30 | 10.7 | 3.9 | 25 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-08-02 22:30 | 10.4 | 4 | 22.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-08-02 23:30 | 10.3 | 4.2 | 20 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-08-03 00:30 | 10.2 | 4.4 | 17.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-08-03 01:30 | 10.1 | 4.5 | 10 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-08-03 02:30 | 10 | 4.5 | 5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-08-03 03:30 | 10.7 | 5.1 | 10 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-08-03 04:30 | 11.6 | 6.4 | 17.5 | 220 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-08-03 05:30 | 11.6 | 7.6 | 20 | 500 | 360 | 40 | 0 |  | 0 |  | 320
Lerwick | 1978-08-03 06:30 | 11.7 | 8.2 | 20 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-03 07:30 | 12.3 | 8.3 | 22.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-08-03 08:30 | 13.1 | 7.8 | 27.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-03 09:30 | 13.1 | 7.3 | 30 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-08-03 10:30 | 12.8 | 6.9 | 30 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-08-03 11:30 | 13.1 | 6.4 | 32.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-08-03 12:30 | 13.3 | 5.9 | 37.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-08-03 13:30 | 13.1 | 5.1 | 40 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-08-03 14:30 | 12.7 | 4.2 | 40 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-08-03 15:30 | 12.8 | 3.8 | 37.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-08-03 16:30 | 12.8 | 3.1 | 30 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-03 17:30 | 12.3 | 2.4 | 15 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-03 18:30 | 12.2 | 1.4 | 180 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-03 19:30 | 12.4 | 0.6 | 327.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-03 20:30 | 12.3 | 0.7 | 270 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-03 21:30 | 12 | 1.4 | 225 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-03 22:30 | 11.8 | 2.2 | 195 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-03 23:30 | 11.6 | 3 | 180 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-04 00:30 | 11.3 | 3.4 | 182.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-04 01:30 | 11.3 | 3.7 | 187.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-04 02:30 | 11.1 | 3.9 | 190 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-08-04 03:30 | 11 | 3.9 | 187.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-08-04 04:30 | 11 | 4.2 | 185 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-08-04 05:30 | 10.9 | 4 | 182.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-08-04 06:30 | 10.9 | 3.3 | 175 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-08-04 07:30 | 11 | 3.1 | 170 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-04 08:30 | 11.2 | 3.1 | 167.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-04 09:30 | 11.6 | 3.2 | 162.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-04 10:30 | 12 | 3.3 | 155 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-04 11:30 | 12.8 | 3.2 | 150 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-04 12:30 | 13.5 | 2.9 | 155 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-04 13:30 | 13.5 | 2.4 | 157.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-04 14:30 | 13.3 | 2 | 157.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-04 15:30 | 13 | 1.5 | 160 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-04 16:30 | 13.1 | 1.1 | 160 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-04 17:30 | 13.2 | 1 | 157.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-04 18:30 | 12.8 | 1 | 147.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-04 19:30 | 12.6 | 1.2 | 145 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-04 20:30 | 12.5 | 1.8 | 155 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-04 21:30 | 12.2 | 2.4 | 165 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-04 22:30 | 12 | 2.4 | 180 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-04 23:30 | 11.9 | 1.8 | 195 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-05 00:30 | 11.7 | 1.5 | 187.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-05 01:30 | 11.8 | 1.6 | 162.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-05 02:30 | 11.5 | 1.9 | 157.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-05 03:30 | 11.5 | 1.9 | 172.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-05 04:30 | 11.9 | 1.5 | 170 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-05 05:30 | 11.9 | 1.1 | 145 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-05 06:30 | 11.9 | 1 | 132.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-05 07:30 | 12 | 1 | 147.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-05 08:30 | 12.2 | 1.1 | 162.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-05 09:30 | 12.4 | 1.5 | 155 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-05 10:30 | 13.2 | 2.2 | 142.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-05 11:30 | 14.6 | 2.6 | 140 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-05 12:30 | 15.2 | 2.9 | 137.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-05 13:30 | 15.2 | 3.3 | 137.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-05 14:30 | 15.1 | 3.4 | 142.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-05 15:30 | 14.4 | 3 | 147.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-05 16:30 | 13.8 | 2.4 | 155 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-05 17:30 | 13.7 | 1.8 | 160 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-05 18:30 | 13.4 | 1.2 | 157.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-05 19:30 | 12.9 | 0.7 | 117.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-05 20:30 | 12.6 | 1.3 | 55 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-05 21:30 | 12.5 | 3 | 45 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-05 22:30 | 12.4 | 3.6 | 57.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-05 23:30 | 12 | 3.3 | 47.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-06 00:30 | 11.8 | 3.6 | 35 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-06 01:30 | 11.4 | 3.7 | 32.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-08-06 02:30 | 10.8 | 3.1 | 37.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-06 03:30 | 10.5 | 2.7 | 40 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-06 04:30 | 10.5 | 3 | 40 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-06 05:30 | 10.3 | 3.4 | 37.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-06 06:30 | 10.2 | 3.6 | 32.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-06 07:30 | 10.4 | 3.1 | 35 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-06 08:30 | 10.5 | 2.2 | 42.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-06 09:30 | 10.9 | 1.9 | 197.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-06 10:30 | 11.1 | 2.4 | 327.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-06 11:30 | 11.7 | 3 | 310 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-06 12:30 | 12.7 | 3.6 | 317.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-06 13:30 | 12.5 | 3.9 | 320 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-08-06 14:30 | 12.2 | 4 | 322.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-08-06 15:30 | 12.5 | 3.9 | 327.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-08-06 16:30 | 12.1 | 3.7 | 330 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-08-06 17:30 | 11.6 | 3.8 | 330 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-08-06 18:30 | 11.5 | 4 | 330 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-08-06 19:30 | 11.2 | 3.5 | 332.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-08-06 20:30 | 10.9 | 2.9 | 337.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-06 21:30 | 10.8 | 2.7 | 337.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-06 22:30 | 10.6 | 2.6 | 332.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-06 23:30 | 10.4 | 2.3 | 340 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-07 00:30 | 10.2 | 1.8 | 177.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-07 01:30 | 9.9 | 1.4 | 10 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-07 02:30 | 9.9 | 1.1 | 22.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-07 03:30 | 10 | 1.1 | 32.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-07 04:30 | 10.1 | 1.4 | 37.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-07 05:30 | 10.1 | 1.6 | 40 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-07 06:30 | 10.2 | 2.2 | 40 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-07 07:30 | 10.3 | 2.9 | 40 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-07 08:30 | 10.4 | 3.3 | 42.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-07 09:30 | 10.8 | 3.3 | 45 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-07 10:30 | 11.4 | 3.6 | 42.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-07 11:30 | 12.1 | 3.9 | 40 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-08-07 12:30 | 12.2 | 4.5 | 37.5 | 80 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-08-07 13:30 | 12.2 | 5.7 | 32.5 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-08-07 14:30 | 12.2 | 6.7 | 30 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-08-07 15:30 | 11.7 | 7.1 | 30 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-08-07 16:30 | 11.4 | 6.9 | 30 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-08-07 17:30 | 11.4 | 6.5 | 30 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-08-07 18:30 | 11.5 | 6.5 | 30 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-08-07 19:30 | 11.4 | 6.7 | 30 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-08-07 20:30 | 11.1 | 6.5 | 30 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-08-07 21:30 | 10.9 | 6.3 | 30 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-08-07 22:30 | 10.8 | 6 | 30 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-07 23:30 | 10.7 | 5.9 | 30 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-08-08 00:30 | 10.6 | 6.3 | 30 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-08-08 01:30 | 10.7 | 7.1 | 30 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-08-08 02:30 | 10.8 | 7.2 | 27.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-08-08 03:30 | 10.7 | 6.4 | 22.5 | 220 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-08-08 04:30 | 10.6 | 5.6 | 17.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-08-08 05:30 | 10.6 | 5.2 | 12.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-08-08 06:30 | 10.7 | 5 | 12.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-08-08 07:30 | 11.1 | 5.3 | 17.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-08-08 08:30 | 11.9 | 6 | 22.5 | 220 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-08-08 09:30 | 12.7 | 6.7 | 30 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-08-08 10:30 | 12.8 | 7.1 | 37.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-08-08 11:30 | 12.7 | 7.3 | 37.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-08-08 12:30 | 12.8 | 7.3 | 35 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-08-08 13:30 | 12.9 | 6.8 | 35 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-08-08 14:30 | 12.9 | 6.4 | 32.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-08-08 15:30 | 12.6 | 6.4 | 30 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-08 16:30 | 12.1 | 6.4 | 27.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-08 17:30 | 11.9 | 6.5 | 25 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-08-08 18:30 | 11.7 | 6.7 | 27.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-08-08 19:30 | 11.2 | 6.5 | 30 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-08-08 20:30 | 10.9 | 6.4 | 27.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-08-08 21:30 | 10.9 | 6.4 | 22.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-08 22:30 | 10.6 | 6.1 | 20 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-08 23:30 | 10.3 | 6 | 20 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-09 00:30 | 10.2 | 6.3 | 20 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-09 01:30 | 10 | 6.3 | 17.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-09 02:30 | 9.9 | 6.2 | 17.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-09 03:30 | 9.8 | 6.2 | 22.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-09 04:30 | 9.7 | 6.2 | 25 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-09 05:30 | 9.6 | 6 | 27.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-09 06:30 | 9.6 | 5.9 | 30 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-08-09 07:30 | 10 | 5.9 | 30 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-08-09 08:30 | 10.4 | 6.3 | 30 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-08-09 09:30 | 10.4 | 6.9 | 30 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-08-09 10:30 | 11 | 6.9 | 27.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-08-09 11:30 | 11.5 | 6.9 | 22.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-08-09 12:30 | 11.6 | 7.3 | 20 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-08-09 13:30 | 11.7 | 7.2 | 20 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-08-09 14:30 | 11.9 | 6.7 | 20 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-08-09 15:30 | 11.9 | 6.1 | 20 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-08-09 16:30 | 11.7 | 5.8 | 20 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-08-09 17:30 | 11.5 | 5.5 | 17.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-08-09 18:30 | 11.6 | 5.2 | 15 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-08-09 19:30 | 11.2 | 5 | 15 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-08-09 20:30 | 10.7 | 5 | 10 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-08-09 21:30 | 10.4 | 4.7 | 2.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-08-09 22:30 | 10.1 | 4 | 0 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-08-09 23:30 | 9.9 | 3.3 | 0 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-08-10 00:30 | 9.7 | 2.8 | 175 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-10 01:30 | 9.5 | 2.6 | 345 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-10 02:30 | 9.5 | 3.1 | 340 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-10 03:30 | 9.5 | 3.4 | 342.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-10 04:30 | 9.5 | 3.2 | 347.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-10 05:30 | 9.5 | 3.1 | 347.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-10 06:30 | 9.4 | 3.2 | 340 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-10 07:30 | 9.5 | 3.6 | 330 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-10 08:30 | 9.7 | 4.2 | 325 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-08-10 09:30 | 10 | 4.4 | 327.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-08-10 10:30 | 10.2 | 4.2 | 332.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-08-10 11:30 | 10.4 | 4 | 170 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-08-10 12:30 | 10.6 | 4 | 17.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-08-10 13:30 | 10.6 | 4 | 27.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-08-10 14:30 | 10.7 | 4 | 187.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-08-10 15:30 | 10.8 | 4.2 | 345 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-08-10 16:30 | 11.1 | 4.6 | 345 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-08-10 17:30 | 11.2 | 4.9 | 342.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-08-10 18:30 | 11.1 | 4.7 | 330 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-08-10 19:30 | 10.8 | 4 | 322.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-08-10 20:30 | 10.1 | 3.6 | 320 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-08-10 21:30 | 10 | 4 | 317.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-08-10 22:30 | 10 | 4.9 | 312.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-08-10 23:30 | 10 | 5.4 | 310 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-08-11 00:30 | 10.1 | 5.1 | 312.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-08-11 01:30 | 10.1 | 4.7 | 320 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-08-11 02:30 | 10.1 | 4.7 | 330 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-08-11 03:30 | 10.1 | 4.7 | 337.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-08-11 04:30 | 10.2 | 4.5 | 342.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-08-11 05:30 | 10.3 | 4.9 | 172.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-08-11 06:30 | 10.4 | 5.2 | 2.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-08-11 07:30 | 10.7 | 4.7 | 7.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-08-11 08:30 | 11.2 | 4.7 | 17.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-08-11 09:30 | 11.3 | 4.9 | 27.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-08-11 10:30 | 11.5 | 5 | 30 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-08-11 11:30 | 11.9 | 5 | 30 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-08-11 12:30 | 12.3 | 4.7 | 30 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-08-11 13:30 | 12.2 | 4.5 | 30 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-08-11 14:30 | 12.3 | 4.7 | 30 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-08-11 15:30 | 12.3 | 5.2 | 32.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-08-11 16:30 | 11.7 | 5.5 | 37.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-08-11 17:30 | 11.4 | 5.7 | 37.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-08-11 18:30 | 11 | 5.3 | 32.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-08-11 19:30 | 10.4 | 4.9 | 27.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-08-11 20:30 | 9.8 | 4.7 | 25 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-08-11 21:30 | 9.3 | 4.2 | 25 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-08-11 22:30 | 9.2 | 3.6 | 30 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-08-11 23:30 | 9.2 | 3 | 45 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-12 00:30 | 9.4 | 2.6 | 52.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-12 01:30 | 9.8 | 2.6 | 40 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-12 02:30 | 9.6 | 2.4 | 25 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-12 03:30 | 9.2 | 1.8 | 20 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-12 04:30 | 9.2 | 1.5 | 27.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-12 05:30 | 9.5 | 1.8 | 45 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-12 06:30 | 9.8 | 2.4 | 55 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-12 07:30 | 10.1 | 2.7 | 55 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-12 08:30 | 10.5 | 3 | 57.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-12 09:30 | 10.9 | 3.2 | 65 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-12 10:30 | 11.2 | 2.9 | 77.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-12 11:30 | 11.3 | 2.6 | 95 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-12 12:30 | 11.6 | 2 | 112.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-12 13:30 | 11.9 | 1.4 | 135 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-12 14:30 | 11.9 | 1.7 | 135 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-12 15:30 | 12 | 2.4 | 97.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-12 16:30 | 12.1 | 2.4 | 87.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-12 17:30 | 12 | 2.1 | 105 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-12 18:30 | 11.8 | 1.9 | 97.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-12 19:30 | 11.4 | 1.6 | 67.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-12 20:30 | 10.9 | 1.2 | 42.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-12 21:30 | 10.2 | 1 | 20 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-12 22:30 | 9.7 | 1 | 170 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-12 23:30 | 9.4 | 1 | 170 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-13 00:30 | 9.7 | 1 | 25 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-13 01:30 | 10 | 1 | 55 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-13 02:30 | 10 | 1 | 75 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-13 03:30 | 10.1 | 1.1 | 85 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-13 04:30 | 10.1 | 1.5 | 87.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-13 05:30 | 10.2 | 2 | 95 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-13 06:30 | 10.4 | 2.6 | 102.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-13 07:30 | 10.7 | 3.5 | 110 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-13 08:30 | 11.1 | 3.9 | 120 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-08-13 09:30 | 11.3 | 4 | 127.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-08-13 10:30 | 11.5 | 3.9 | 132.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-08-13 11:30 | 11.4 | 3.7 | 137.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-08-13 12:30 | 11.3 | 3.7 | 142.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-08-13 13:30 | 11.5 | 3.9 | 150 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-08-13 14:30 | 12 | 3.9 | 157.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-08-13 15:30 | 12.4 | 3.3 | 157.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-13 16:30 | 12.4 | 2.4 | 150 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-13 17:30 | 12.2 | 2.4 | 140 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-13 18:30 | 12.3 | 2.4 | 135 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-13 19:30 | 12.2 | 2 | 137.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-13 20:30 | 11.8 | 1.9 | 142.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-13 21:30 | 11.5 | 2.6 | 150 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-13 22:30 | 11.5 | 3.5 | 155 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-13 23:30 | 11.4 | 3.7 | 150 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-08-14 00:30 | 11.4 | 3.1 | 142.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-14 01:30 | 11.5 | 2.9 | 137.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-14 02:30 | 11.5 | 3.3 | 130 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-14 03:30 | 11.5 | 3.6 | 122.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-14 04:30 | 11.8 | 3.6 | 122.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-08-14 05:30 | 11.7 | 3.7 | 127.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-08-14 06:30 | 11.9 | 4.2 | 130 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-08-14 07:30 | 12.2 | 4.9 | 130 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-08-14 08:30 | 12.8 | 5.6 | 130 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-08-14 09:30 | 13.3 | 6 | 130 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-08-14 10:30 | 13.1 | 6.2 | 130 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-14 11:30 | 12.7 | 6.2 | 130 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-14 12:30 | 12.5 | 6.2 | 130 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-14 13:30 | 12.6 | 6.2 | 130 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-14 14:30 | 12.5 | 6.3 | 130 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-14 15:30 | 12.5 | 6.4 | 132.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-14 16:30 | 12.3 | 6.4 | 145 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-14 17:30 | 12.2 | 6.1 | 165 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-14 18:30 | 12.4 | 5.4 | 177.5 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-08-14 19:30 | 12.4 | 4.4 | 182.5 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-08-14 20:30 | 12.2 | 3.5 | 192.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-08-14 21:30 | 12.1 | 3.7 | 212.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-08-14 22:30 | 12 | 4.9 | 235 | 80 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-08-14 23:30 | 11.6 | 5.5 | 250 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-08-15 00:30 | 11.3 | 5.7 | 257.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-08-15 01:30 | 11 | 5 | 255 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-08-15 02:30 | 10.7 | 3.5 | 242.5 | 25 | 67.5 | 0 | 252.5 |  | 121.2 |  | 67.5
Lerwick | 1978-08-15 03:30 | 10.4 | 2.9 | 230 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-15 04:30 | 10.5 | 3.5 | 222.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-15 05:30 | 10.5 | 4.2 | 222.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-08-15 06:30 | 10.7 | 4.2 | 220 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-08-15 07:30 | 11 | 3.8 | 202.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-08-15 08:30 | 11.3 | 3.4 | 185 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-15 09:30 | 11.5 | 3.2 | 175 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-15 10:30 | 11.8 | 3.1 | 165 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-15 11:30 | 12.2 | 2.8 | 162.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-15 12:30 | 12.4 | 2.8 | 175 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-15 13:30 | 12.2 | 3.3 | 197.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-15 14:30 | 12.2 | 2.9 | 212.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-15 15:30 | 12.6 | 2.1 | 205 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-15 16:30 | 13 | 2.4 | 200 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-15 17:30 | 13.1 | 2.7 | 215 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-15 18:30 | 12.6 | 2.6 | 222.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-15 19:30 | 12.1 | 2.6 | 225 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-15 20:30 | 11.1 | 2.2 | 227.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-15 21:30 | 9.6 | 1.6 | 212.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-15 22:30 | 9.1 | 1.6 | 197.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-15 23:30 | 9.9 | 1.8 | 200 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-16 00:30 | 10.5 | 1.6 | 202.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-16 01:30 | 10.7 | 1.5 | 192.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-16 02:30 | 10.9 | 1.8 | 185 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-16 03:30 | 11 | 2.4 | 190 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-16 04:30 | 11 | 2.7 | 202.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-16 05:30 | 11 | 2.9 | 217.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-16 06:30 | 11.1 | 3.8 | 230 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-16 07:30 | 11.3 | 5.1 | 237.5 | 110 | 67.5 | 0 | 252.5 |  | 121.2 |  | 67.5
Lerwick | 1978-08-16 08:30 | 11.8 | 5.7 | 240 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-08-16 09:30 | 12.5 | 5.5 | 242.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-08-16 10:30 | 13 | 5.2 | 250 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-08-16 11:30 | 13.6 | 5.2 | 257.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-08-16 12:30 | 13.7 | 5.4 | 272.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-08-16 13:30 | 13.2 | 5.1 | 300 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-08-16 14:30 | 12.7 | 4.9 | 317.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-08-16 15:30 | 11.9 | 5.4 | 317.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-08-16 16:30 | 10.9 | 5.6 | 310 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-08-16 17:30 | 9.5 | 4.9 | 305 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-08-16 18:30 | 8.6 | 4.1 | 307.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-08-16 19:30 | 8.3 | 3.5 | 307.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-08-16 20:30 | 8.3 | 3.1 | 297.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-16 21:30 | 8.7 | 3.5 | 282.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-16 22:30 | 8.8 | 3.9 | 272.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-08-16 23:30 | 8.8 | 3.7 | 277.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-08-17 00:30 | 9 | 3.7 | 290 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-08-17 01:30 | 9.2 | 3.9 | 292.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-08-17 02:30 | 9.1 | 3.5 | 290 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-08-17 03:30 | 9 | 2.9 | 287.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-17 04:30 | 8.8 | 2.7 | 282.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-17 05:30 | 9 | 2.7 | 280 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-17 06:30 | 9.5 | 3.1 | 280 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-17 07:30 | 10.1 | 4 | 277.5 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-08-17 08:30 | 10.7 | 4.6 | 270 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-08-17 09:30 | 11.2 | 5.1 | 265 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-08-17 10:30 | 11.8 | 5.5 | 265 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-08-17 11:30 | 12.2 | 5.7 | 262.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-08-17 12:30 | 12.6 | 5.8 | 257.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-08-17 13:30 | 13.1 | 5.9 | 252.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-08-17 14:30 | 13.3 | 5.8 | 250 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-08-17 15:30 | 13.6 | 5.5 | 247.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-08-17 16:30 | 13.4 | 5.1 | 242.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-08-17 17:30 | 13.1 | 4.4 | 237.5 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-08-17 18:30 | 12.6 | 3.6 | 232.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-08-17 19:30 | 11.6 | 3.2 | 230 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-17 20:30 | 10.4 | 3.2 | 227.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-17 21:30 | 9.8 | 3.2 | 217.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-17 22:30 | 9.6 | 3.2 | 207.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-17 23:30 | 9.6 | 3.6 | 205 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-18 00:30 | 9.5 | 4.2 | 202.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-08-18 01:30 | 10 | 4.4 | 197.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-08-18 02:30 | 10.5 | 4.1 | 190 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-08-18 03:30 | 10.6 | 3.9 | 182.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-08-18 04:30 | 10.9 | 4.2 | 177.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-08-18 05:30 | 11 | 4.9 | 172.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-08-18 06:30 | 11.2 | 5.5 | 170 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-08-18 07:30 | 11.5 | 5.8 | 170 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-08-18 08:30 | 12 | 6 | 167.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-08-18 09:30 | 12.7 | 6 | 160 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-18 10:30 | 13.4 | 6 | 155 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-18 11:30 | 14.2 | 6.7 | 157.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-08-18 12:30 | 14.7 | 7.6 | 160 | 500 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-08-18 13:30 | 14.5 | 8 | 160 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-18 14:30 | 14.5 | 7.6 | 160 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-18 15:30 | 14.6 | 7.2 | 160 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-08-18 16:30 | 14.2 | 7.6 | 160 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-08-18 17:30 | 13.8 | 8.2 | 162.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-18 18:30 | 13.2 | 8.5 | 167.5 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-18 19:30 | 12.6 | 8.2 | 172.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-18 20:30 | 12.2 | 7.8 | 177.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-18 21:30 | 12.1 | 7.7 | 180 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-08-18 22:30 | 12.3 | 7.4 | 180 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-08-18 23:30 | 12.3 | 7.1 | 180 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-08-19 00:30 | 12.1 | 7 | 180 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-08-19 01:30 | 12 | 6.7 | 180 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-08-19 02:30 | 11.9 | 6.3 | 180 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-08-19 03:30 | 11.8 | 6.2 | 182.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-19 04:30 | 11.7 | 6.2 | 187.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-19 05:30 | 11.7 | 6 | 187.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-19 06:30 | 11.9 | 5.9 | 180 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-08-19 07:30 | 12.2 | 6 | 175 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-08-19 08:30 | 12.3 | 6 | 177.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-19 09:30 | 12.3 | 6.1 | 180 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-19 10:30 | 12.4 | 6.7 | 180 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-08-19 11:30 | 13.2 | 6.7 | 180 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-08-19 12:30 | 13.5 | 6.1 | 180 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-08-19 13:30 | 12.9 | 5.8 | 180 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-08-19 14:30 | 13 | 5.9 | 180 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-08-19 15:30 | 13.1 | 6.2 | 182.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-08-19 16:30 | 13.2 | 5.9 | 187.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-08-19 17:30 | 12.9 | 5.7 | 190 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-08-19 18:30 | 12.5 | 5.5 | 190 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-08-19 19:30 | 12.3 | 5.4 | 190 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-08-19 20:30 | 12.1 | 5.4 | 187.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-08-19 21:30 | 12 | 5.4 | 180 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-08-19 22:30 | 11.9 | 5.2 | 175 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-08-19 23:30 | 11.7 | 4.3 | 180 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-08-20 00:30 | 11.5 | 3.1 | 187.5 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-08-20 01:30 | 11.7 | 2.4 | 195 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-20 02:30 | 11.6 | 1.5 | 197.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-20 03:30 | 11.7 | 1 | 185 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-20 04:30 | 11.7 | 1.2 | 170 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-20 05:30 | 11.3 | 2 | 165 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-20 06:30 | 11 | 2.6 | 167.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-20 07:30 | 11.1 | 2.6 | 172.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-20 08:30 | 11.5 | 3.1 | 175 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-20 09:30 | 11.9 | 4 | 175 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-08-20 10:30 | 12 | 4.1 | 177.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-08-20 11:30 | 12 | 3.9 | 177.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-08-20 12:30 | 12.6 | 4.1 | 175 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-08-20 13:30 | 13.7 | 4.6 | 177.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-08-20 14:30 | 14.7 | 4.7 | 175 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-08-20 15:30 | 15.3 | 4.2 | 165 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-08-20 16:30 | 14.9 | 3.7 | 160 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-08-20 17:30 | 14 | 3.8 | 165 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-08-20 18:30 | 13.1 | 4.2 | 175 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-08-20 19:30 | 12.3 | 4.7 | 177.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-08-20 20:30 | 12.1 | 4.7 | 172.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-08-20 21:30 | 12 | 4.5 | 172.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-08-20 22:30 | 12 | 4.5 | 182.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-08-20 23:30 | 12 | 4.5 | 197.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-08-21 00:30 | 12 | 4.9 | 212.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-08-21 01:30 | 12 | 5.5 | 220 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-08-21 02:30 | 12 | 5.5 | 210 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-08-21 03:30 | 12 | 5.4 | 195 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-08-21 04:30 | 11.8 | 5.9 | 197.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-08-21 05:30 | 11.6 | 6.5 | 215 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-08-21 06:30 | 11.8 | 6.5 | 230 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-08-21 07:30 | 11.6 | 6.4 | 235 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-08-21 08:30 | 11.4 | 6.8 | 235 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-08-21 09:30 | 11.6 | 7.6 | 235 | 500 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-08-21 10:30 | 12.6 | 8 | 235 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-21 11:30 | 12.9 | 8.2 | 237.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-08-21 12:30 | 13.2 | 8.5 | 237.5 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-21 13:30 | 13.9 | 8.3 | 230 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-21 14:30 | 13.7 | 7.8 | 222.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-21 15:30 | 13.3 | 6.8 | 215 | 300 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-08-21 16:30 | 12.5 | 5.6 | 205 | 150 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-08-21 17:30 | 11.9 | 4.5 | 200 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-08-21 18:30 | 11.6 | 3.8 | 202.5 | 25 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-08-21 19:30 | 11.5 | 4 | 210 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-08-21 20:30 | 11.5 | 4.7 | 215 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-08-21 21:30 | 11.4 | 5 | 212.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-08-21 22:30 | 11.1 | 5.6 | 212.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-08-21 23:30 | 10.5 | 6.6 | 220 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-08-22 00:30 | 10.1 | 6.8 | 230 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-08-22 01:30 | 10.1 | 6.9 | 237.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-08-22 02:30 | 10.1 | 7.4 | 240 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-08-22 03:30 | 10.2 | 7.9 | 240 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-08-22 04:30 | 10.4 | 8.5 | 240 | 770 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-08-22 05:30 | 10.5 | 9.4 | 237.5 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-08-22 06:30 | 10.8 | 10.4 | 232.5 | 1150 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-08-22 07:30 | 11 | 11.2 | 230 | 1340 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-08-22 08:30 | 11.1 | 11.1 | 232.5 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-08-22 09:30 | 11.3 | 10.3 | 240 | 1150 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-08-22 10:30 | 11.4 | 9.3 | 247.5 | 900 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-08-22 11:30 | 11.7 | 8.4 | 250 | 635 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-22 12:30 | 11.9 | 7.7 | 250 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-22 13:30 | 11.7 | 7.6 | 250 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-08-22 14:30 | 11.5 | 7.9 | 255 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-08-22 15:30 | 11.5 | 8 | 267.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-22 16:30 | 11.2 | 7.6 | 280 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-22 17:30 | 11.2 | 7.3 | 285 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-08-22 18:30 | 11.4 | 8.1 | 282.5 | 635 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-22 19:30 | 11.1 | 8.9 | 280 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-22 20:30 | 10.8 | 8.5 | 280 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-08-22 21:30 | 10.7 | 8 | 277.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-22 22:30 | 10.5 | 8.2 | 272.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-08-22 23:30 | 10.5 | 8.6 | 270 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-23 00:30 | 10.4 | 8.9 | 270 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-08-23 01:30 | 10.4 | 9.1 | 270 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-08-23 02:30 | 10.4 | 9.1 | 270 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-08-23 03:30 | 10.2 | 8.9 | 270 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-08-23 04:30 | 10.2 | 8.6 | 270 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-08-23 05:30 | 10.3 | 8.5 | 270 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-08-23 06:30 | 10.2 | 8.9 | 272.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-08-23 07:30 | 10.2 | 9.8 | 275 | 1025 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-23 08:30 | 10.4 | 10.8 | 272.5 | 1270 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-23 09:30 | 10.6 | 11.5 | 270 | 1400 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-08-23 10:30 | 11.4 | 11.6 | 270 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-08-23 11:30 | 12.1 | 11.1 | 267.5 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-08-23 12:30 | 12.2 | 10.6 | 262.5 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-08-23 13:30 | 12.3 | 10.2 | 260 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-08-23 14:30 | 12.4 | 9.4 | 260 | 900 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-08-23 15:30 | 11.8 | 8.4 | 260 | 635 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-23 16:30 | 11.2 | 7.8 | 257.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-23 17:30 | 11.1 | 7.9 | 252.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-08-23 18:30 | 11.3 | 8.7 | 250 | 770 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-08-23 19:30 | 11 | 9.4 | 250 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-08-23 20:30 | 10.5 | 9.5 | 250 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-23 21:30 | 10.5 | 9.7 | 247.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-08-23 22:30 | 10.4 | 10.1 | 245 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-23 23:30 | 10.4 | 10 | 245 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-08-24 00:30 | 10.3 | 9.5 | 245 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-24 01:30 | 10 | 9.1 | 247.5 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-24 02:30 | 10 | 9.1 | 252.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-08-24 03:30 | 10.2 | 9.3 | 257.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-08-24 04:30 | 10.2 | 9.4 | 262.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-08-24 05:30 | 10 | 9.9 | 270 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-24 06:30 | 10 | 10.3 | 272.5 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-24 07:30 | 10.5 | 10.3 | 265 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-08-24 08:30 | 11.2 | 10.3 | 260 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-08-24 09:30 | 11.5 | 10.5 | 260 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-08-24 10:30 | 11.3 | 11 | 260 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-08-24 11:30 | 11.8 | 11.3 | 260 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-08-24 12:30 | 12.2 | 11.4 | 262.5 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-08-24 13:30 | 12 | 11.7 | 270 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-08-24 14:30 | 12 | 11.7 | 277.5 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-08-24 15:30 | 11.9 | 11.1 | 280 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-08-24 16:30 | 11.7 | 10.6 | 282.5 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-08-24 17:30 | 11.4 | 10.1 | 285 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-08-24 18:30 | 11.4 | 9.4 | 285 | 900 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-08-24 19:30 | 11.2 | 8.5 | 287.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-08-24 20:30 | 10.7 | 7.9 | 292.5 | 500 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-08-24 21:30 | 10.4 | 7.7 | 297.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-08-24 22:30 | 10.2 | 7.6 | 300 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-08-24 23:30 | 10 | 7.1 | 300 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-08-25 00:30 | 9.9 | 6.4 | 300 | 220 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-08-25 01:30 | 9.7 | 6.2 | 302.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-25 02:30 | 9.5 | 6.4 | 307.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-25 03:30 | 9.3 | 7.1 | 310 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-08-25 04:30 | 9.4 | 7.6 | 310 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-08-25 05:30 | 9.3 | 7.8 | 310 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-08-25 06:30 | 9 | 8 | 307.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-25 07:30 | 9 | 8.3 | 305 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-08-25 08:30 | 9.2 | 8.6 | 310 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-25 09:30 | 9.3 | 9 | 317.5 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-08-25 10:30 | 9.3 | 9.4 | 320 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-08-25 11:30 | 9.3 | 9.2 | 320 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-08-25 12:30 | 9.7 | 9 | 320 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-08-25 13:30 | 9.6 | 8.7 | 320 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-08-25 14:30 | 9.9 | 8.2 | 322.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-25 15:30 | 9.9 | 8 | 325 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-08-25 16:30 | 9.1 | 8 | 322.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-08-25 17:30 | 8.8 | 7.5 | 322.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-25 18:30 | 8.5 | 6 | 327.5 | 220 | 360 | 40 | 0 |  | 0 |  | 320
Lerwick | 1978-08-25 19:30 | 8 | 4.5 | 327.5 | 80 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-08-25 20:30 | 7.7 | 4.2 | 322.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-08-25 21:30 | 7.9 | 4.4 | 317.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-08-25 22:30 | 7.7 | 4.2 | 312.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-08-25 23:30 | 7.6 | 3.9 | 310 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-08-26 00:30 | 7.9 | 4.1 | 307.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-08-26 01:30 | 8.1 | 4.4 | 302.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-08-26 02:30 | 7.8 | 4.5 | 300 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-08-26 03:30 | 7.8 | 4.2 | 297.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-08-26 04:30 | 8.3 | 3.9 | 292.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-08-26 05:30 | 8.5 | 3.9 | 287.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-08-26 06:30 | 8.7 | 4.4 | 282.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-08-26 07:30 | 9.2 | 5.4 | 282.5 | 110 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-08-26 08:30 | 9.9 | 6.3 | 290 | 220 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-08-26 09:30 | 10.1 | 7.2 | 297.5 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-08-26 10:30 | 10.5 | 7.9 | 300 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-08-26 11:30 | 11.3 | 8 | 300 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-26 12:30 | 11.8 | 8 | 300 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-08-26 13:30 | 11.7 | 8.4 | 305 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-08-26 14:30 | 11.7 | 9 | 315 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-26 15:30 | 11.7 | 9.6 | 322.5 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-26 16:30 | 11.2 | 10 | 327.5 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-26 17:30 | 10.7 | 9.6 | 330 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-26 18:30 | 10 | 8.7 | 330 | 770 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-26 19:30 | 9.1 | 7.9 | 332.5 | 500 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-08-26 20:30 | 8.5 | 7.7 | 335 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-08-26 21:30 | 8.2 | 7.7 | 332.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-08-26 22:30 | 8.1 | 7.7 | 330 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-08-26 23:30 | 8 | 7.3 | 330 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-08-27 00:30 | 7.9 | 6.6 | 330 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-08-27 01:30 | 7.8 | 6.2 | 332.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-08-27 02:30 | 7.8 | 6.2 | 337.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-27 03:30 | 7.8 | 6.3 | 340 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-27 04:30 | 7.8 | 6.4 | 340 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-27 05:30 | 7.8 | 6.4 | 337.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-27 06:30 | 7.7 | 6.5 | 335 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-08-27 07:30 | 8.2 | 6.8 | 337.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-08-27 08:30 | 9 | 7.1 | 337.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-08-27 09:30 | 9.6 | 7.2 | 332.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-08-27 10:30 | 10 | 6.9 | 330 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-08-27 11:30 | 10.4 | 6.4 | 327.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-08-27 12:30 | 10.9 | 6.2 | 320 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-27 13:30 | 10.7 | 6 | 310 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-27 14:30 | 10.7 | 5.9 | 302.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-08-27 15:30 | 10.7 | 5.9 | 302.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-08-27 16:30 | 10.1 | 5.6 | 310 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-08-27 17:30 | 9.5 | 5.1 | 315 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-08-27 18:30 | 9.1 | 4.4 | 312.5 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-08-27 19:30 | 8.6 | 3.6 | 310 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-08-27 20:30 | 8.2 | 3 | 305 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-27 21:30 | 8 | 2.6 | 292.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-27 22:30 | 7.9 | 2.6 | 282.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-27 23:30 | 7.9 | 2.3 | 270 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-28 00:30 | 7.8 | 1.9 | 237.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-28 01:30 | 7.4 | 2.2 | 197.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-28 02:30 | 7.3 | 3.3 | 175 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-28 03:30 | 7.5 | 3.9 | 170 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-28 04:30 | 7.8 | 3.3 | 162.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-28 05:30 | 8.4 | 1.8 | 112.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-28 06:30 | 9.2 | 1.5 | 200 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-28 07:30 | 9.7 | 3.3 | 317.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-28 08:30 | 10.1 | 4.7 | 302.5 | 80 | 40 | 0 | 280 |  | 134.4 |  | 40
Lerwick | 1978-08-28 09:30 | 10.5 | 4.7 | 290 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-08-28 10:30 | 11 | 4.7 | 272.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-08-28 11:30 | 11.3 | 5.6 | 265 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-08-28 12:30 | 11.2 | 6.6 | 267.5 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-08-28 13:30 | 11.1 | 7 | 272.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-08-28 14:30 | 11 | 6.7 | 280 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-08-28 15:30 | 11 | 6.3 | 290 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-08-28 16:30 | 11 | 5.9 | 297.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-08-28 17:30 | 11.2 | 5.7 | 300 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-08-28 18:30 | 11.4 | 6 | 300 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-08-28 19:30 | 11.2 | 6.7 | 300 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-08-28 20:30 | 10.8 | 7 | 300 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-08-28 21:30 | 10 | 6.6 | 300 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-08-28 22:30 | 9.2 | 5.9 | 300 | 150 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-08-28 23:30 | 8.8 | 6 | 300 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-08-29 00:30 | 8.7 | 6.5 | 302.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-08-29 01:30 | 8.8 | 6.3 | 312.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-08-29 02:30 | 8.7 | 6.5 | 332.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-08-29 03:30 | 9 | 7.4 | 172.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-08-29 04:30 | 9.2 | 7 | 0 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-08-29 05:30 | 8.6 | 6 | 177.5 | 220 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-08-29 06:30 | 8.2 | 5.1 | 347.5 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-08-29 07:30 | 8.5 | 4.2 | 332.5 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-08-29 08:30 | 9.5 | 4.2 | 317.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-08-29 09:30 | 10.3 | 5.1 | 305 | 110 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-08-29 10:30 | 10.6 | 5.9 | 305 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-08-29 11:30 | 11 | 6.2 | 322.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-08-29 12:30 | 11 | 6.4 | 170 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-08-29 13:30 | 10.9 | 6.9 | 12.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-08-29 14:30 | 10.1 | 7.3 | 17.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-08-29 15:30 | 9.7 | 7.6 | 7.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-08-29 16:30 | 10.2 | 7.6 | 175 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-08-29 17:30 | 9.7 | 7.3 | 350 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-08-29 18:30 | 9.6 | 6.9 | 347.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-08-29 19:30 | 9.1 | 6.5 | 342.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-08-29 20:30 | 8 | 7 | 340 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-08-29 21:30 | 7.8 | 7.7 | 337.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-08-29 22:30 | 7.8 | 7.2 | 330 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-08-29 23:30 | 7.5 | 6.5 | 325 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-08-30 00:30 | 7.6 | 6.4 | 327.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-08-30 01:30 | 8 | 6.7 | 332.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-08-30 02:30 | 7.7 | 7 | 335 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-08-30 03:30 | 7.3 | 7 | 335 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-08-30 04:30 | 7.1 | 7 | 332.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-08-30 05:30 | 7.1 | 7 | 327.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-08-30 06:30 | 7.6 | 7.2 | 327.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-08-30 07:30 | 8 | 7.7 | 332.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-08-30 08:30 | 8 | 8 | 337.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-30 09:30 | 8.2 | 7.9 | 337.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-08-30 10:30 | 8.7 | 7.6 | 332.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-08-30 11:30 | 9.1 | 7.5 | 330 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-08-30 12:30 | 9.6 | 7.5 | 332.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-08-30 13:30 | 9.8 | 7.5 | 335 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-08-30 14:30 | 10 | 7.5 | 330 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-08-30 15:30 | 10.2 | 7.5 | 325 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-08-30 16:30 | 9.9 | 7.1 | 325 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-08-30 17:30 | 9.7 | 6.3 | 322.5 | 220 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-08-30 18:30 | 9.4 | 5.4 | 320 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-08-30 19:30 | 9.1 | 4.9 | 320 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-08-30 20:30 | 8.7 | 4.7 | 322.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-08-30 21:30 | 8.3 | 4.2 | 327.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-08-30 22:30 | 8.2 | 3.6 | 325 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-08-30 23:30 | 8 | 2.7 | 317.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-31 00:30 | 7.8 | 2.2 | 310 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-31 01:30 | 7.8 | 2.7 | 297.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-31 02:30 | 7.8 | 3 | 290 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-31 03:30 | 7.8 | 2.2 | 292.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-31 04:30 | 7.5 | 1.3 | 312.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-31 05:30 | 7.3 | 0.4 | 165 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-31 06:30 | 7.1 | 0.2 | 140 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-31 07:30 | 7.3 | 0.9 | 240 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-31 08:30 | 7.9 | 1.5 | 192.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-31 09:30 | 8.8 | 2 | 170 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-31 10:30 | 9.6 | 2.4 | 147.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-31 11:30 | 9.7 | 2.9 | 142.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-31 12:30 | 10.2 | 2.9 | 147.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-31 13:30 | 10.4 | 2.7 | 152.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-31 14:30 | 10 | 2.9 | 155 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-31 15:30 | 9.6 | 2.9 | 147.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-31 16:30 | 9.3 | 2.6 | 135 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-31 17:30 | 9 | 2.6 | 125 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-31 18:30 | 9 | 3 | 115 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-31 19:30 | 8.9 | 3.3 | 100 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-31 20:30 | 8.9 | 3.4 | 75 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-08-31 21:30 | 8.9 | 3.7 | 55 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-31 22:30 | 8.6 | 3.3 | 45 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-08-31 23:30 | 8.4 | 2.4 | 25 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-01 00:30 | 8.3 | 2.4 | 180 | 0 | 0 | 0 | 320 |  | 153.6 | 32133.6 | 0 | 163455
Lerwick | 1978-09-01 01:30 | 8.1 | 2.6 | 347.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-01 02:30 | 7.9 | 2.4 | 340 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-01 03:30 | 8 | 2.1 | 335 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-01 04:30 | 8.1 | 2.1 | 337.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-01 05:30 | 8 | 1.9 | 335 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-01 06:30 | 7.9 | 1.8 | 325 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-01 07:30 | 8.3 | 2 | 325 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-01 08:30 | 9 | 2.4 | 165 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-01 09:30 | 9.4 | 2.4 | 15 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-01 10:30 | 9.5 | 2.2 | 32.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-01 11:30 | 9.8 | 2.4 | 35 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-01 12:30 | 10.2 | 3.3 | 35 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-01 13:30 | 11 | 4.4 | 22.5 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-09-01 14:30 | 11.5 | 5.1 | 180 | 110 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-09-01 15:30 | 11.7 | 5.4 | 347.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-09-01 16:30 | 11.5 | 5.4 | 340 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-09-01 17:30 | 11 | 5.5 | 330 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-09-01 18:30 | 10.4 | 5.7 | 322.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-09-01 19:30 | 9.6 | 5.7 | 322.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-09-01 20:30 | 9.1 | 5.8 | 327.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-09-01 21:30 | 8.8 | 6.1 | 327.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-09-01 22:30 | 8.4 | 6.1 | 322.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-09-01 23:30 | 7.7 | 5.2 | 320 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-09-02 00:30 | 7.4 | 4.5 | 322.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-09-02 01:30 | 7.6 | 5.1 | 325 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-09-02 02:30 | 7.8 | 5.8 | 322.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-09-02 03:30 | 7.5 | 5.8 | 320 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-09-02 04:30 | 7.5 | 5.7 | 320 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-09-02 05:30 | 7.4 | 5.7 | 320 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-09-02 06:30 | 7.3 | 5.7 | 320 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-09-02 07:30 | 8.2 | 5.9 | 320 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-09-02 08:30 | 9 | 6.4 | 322.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-09-02 09:30 | 9.3 | 6.8 | 325 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-09-02 10:30 | 9.7 | 7 | 322.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-09-02 11:30 | 10.3 | 7 | 320 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-09-02 12:30 | 10.9 | 7.1 | 320 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-09-02 13:30 | 11 | 7.3 | 320 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-09-02 14:30 | 10.5 | 7.5 | 317.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-09-02 15:30 | 10.3 | 7.2 | 315 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-09-02 16:30 | 9.9 | 6.8 | 317.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-09-02 17:30 | 9.6 | 6.5 | 322.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-09-02 18:30 | 9.9 | 6.1 | 327.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-09-02 19:30 | 9.5 | 5.6 | 327.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-09-02 20:30 | 9.3 | 5.1 | 322.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-09-02 21:30 | 9.3 | 4.9 | 322.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-09-02 22:30 | 9.2 | 4.9 | 320 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-09-02 23:30 | 9.4 | 4.7 | 310 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-09-03 00:30 | 9.6 | 4.5 | 310 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-09-03 01:30 | 9.3 | 4.5 | 315 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-09-03 02:30 | 8.7 | 4.5 | 310 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-09-03 03:30 | 8.5 | 4.7 | 302.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-09-03 04:30 | 8.5 | 4.9 | 300 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-09-03 05:30 | 8.2 | 4.9 | 302.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-09-03 06:30 | 7.9 | 5.2 | 307.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-09-03 07:30 | 8.5 | 5.5 | 312.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-09-03 08:30 | 9 | 6 | 317.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-09-03 09:30 | 9.3 | 6.7 | 317.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-09-03 10:30 | 9.9 | 7 | 312.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-09-03 11:30 | 10.5 | 6.6 | 315 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-09-03 12:30 | 10.4 | 6 | 322.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-09-03 13:30 | 10 | 5.9 | 322.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-09-03 14:30 | 10 | 6 | 322.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-09-03 15:30 | 9.9 | 6.3 | 325 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-09-03 16:30 | 9.6 | 6.1 | 325 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-09-03 17:30 | 9.5 | 5.8 | 327.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-09-03 18:30 | 9.1 | 5.3 | 327.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-09-03 19:30 | 8.7 | 4.4 | 320 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-09-03 20:30 | 8.6 | 3.7 | 315 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-09-03 21:30 | 8.3 | 3.7 | 320 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-09-03 22:30 | 7.7 | 4.1 | 325 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-09-03 23:30 | 7.5 | 4.4 | 325 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-09-04 00:30 | 7.5 | 4.1 | 327.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-09-04 01:30 | 7.6 | 3.9 | 335 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-09-04 02:30 | 7.5 | 4 | 342.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-09-04 03:30 | 7.1 | 4 | 345 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-09-04 04:30 | 6.9 | 4.4 | 347.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-09-04 05:30 | 6.9 | 4.9 | 350 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-09-04 06:30 | 7 | 5.3 | 350 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-09-04 07:30 | 7.8 | 6.2 | 352.5 | 220 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-09-04 08:30 | 9.2 | 6.9 | 180 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-09-04 09:30 | 10 | 7.3 | 10 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-09-04 10:30 | 10.5 | 7.7 | 17.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-09-04 11:30 | 11 | 8.2 | 20 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-04 12:30 | 11.6 | 8.5 | 20 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-04 13:30 | 11.9 | 8.2 | 17.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-04 14:30 | 11.3 | 7.8 | 15 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-04 15:30 | 11 | 7.8 | 15 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-04 16:30 | 11 | 8 | 12.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-04 17:30 | 10.6 | 7.7 | 10 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-04 18:30 | 10.3 | 7.2 | 10 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-09-04 19:30 | 10 | 7 | 10 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-09-04 20:30 | 9.8 | 7 | 10 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-09-04 21:30 | 9.8 | 6.8 | 7.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-09-04 22:30 | 9.8 | 6.4 | 2.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-09-04 23:30 | 9.5 | 5.9 | 0 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-09-05 00:30 | 9.4 | 5.7 | 0 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-09-05 01:30 | 9.6 | 5.8 | 2.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-09-05 02:30 | 9.8 | 5.9 | 5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-09-05 03:30 | 10 | 5.4 | 2.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-09-05 04:30 | 10 | 4.9 | 2.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-09-05 05:30 | 10 | 4.9 | 10 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-09-05 06:30 | 10 | 4.9 | 20 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-09-05 07:30 | 10.3 | 4.4 | 27.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-09-05 08:30 | 10.7 | 3.9 | 37.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-09-05 09:30 | 11.1 | 3.9 | 60 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-09-05 10:30 | 11.9 | 3.9 | 82.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-09-05 11:30 | 12.5 | 3.9 | 95 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-09-05 12:30 | 12.9 | 3.7 | 107.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-09-05 13:30 | 12.7 | 3.6 | 115 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-09-05 14:30 | 12.4 | 3.4 | 112.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-09-05 15:30 | 12.4 | 3.3 | 112.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-05 16:30 | 12.2 | 3.3 | 115 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-05 17:30 | 11.9 | 3.4 | 112.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-05 18:30 | 11.8 | 4 | 112.5 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-09-05 19:30 | 11.4 | 4.6 | 115 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-09-05 20:30 | 11.2 | 5.1 | 112.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-09-05 21:30 | 11.3 | 5.5 | 110 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-09-05 22:30 | 11.3 | 5.8 | 110 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-09-05 23:30 | 11.3 | 5.9 | 110 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-09-06 00:30 | 11.2 | 5.8 | 112.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-09-06 01:30 | 11 | 5.7 | 112.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-09-06 02:30 | 10.7 | 5.7 | 105 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-09-06 03:30 | 10.7 | 5.9 | 100 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-09-06 04:30 | 11 | 6.3 | 100 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-09-06 05:30 | 11 | 6.3 | 100 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-09-06 06:30 | 11 | 6.3 | 102.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-09-06 07:30 | 11.4 | 6.7 | 107.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-09-06 08:30 | 12.1 | 7 | 110 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-09-06 09:30 | 12.7 | 6.8 | 110 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-09-06 10:30 | 13.3 | 6.7 | 110 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-09-06 11:30 | 13.8 | 6.8 | 107.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-09-06 12:30 | 13.8 | 6.8 | 105 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-09-06 13:30 | 13.8 | 6.7 | 107.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-09-06 14:30 | 13.4 | 6.8 | 110 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-09-06 15:30 | 12.6 | 6.7 | 110 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-09-06 16:30 | 12.3 | 6.3 | 110 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-09-06 17:30 | 12.1 | 6.2 | 110 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-09-06 18:30 | 11.7 | 6.2 | 110 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-09-06 19:30 | 11.4 | 6.4 | 110 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-09-06 20:30 | 11.2 | 6.8 | 110 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-09-06 21:30 | 11.3 | 7 | 110 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-09-06 22:30 | 11.4 | 7 | 110 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-09-06 23:30 | 11.3 | 6.7 | 110 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-09-07 00:30 | 11.3 | 6.3 | 110 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-09-07 01:30 | 11.3 | 6.4 | 110 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-09-07 02:30 | 11.3 | 7.2 | 110 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-09-07 03:30 | 11.4 | 7.9 | 110 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-09-07 04:30 | 11.5 | 8.1 | 110 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-07 05:30 | 11.2 | 8.3 | 110 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-09-07 06:30 | 11.2 | 8.3 | 110 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-09-07 07:30 | 11.5 | 7.8 | 110 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-07 08:30 | 11.5 | 7.2 | 115 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-09-07 09:30 | 11.5 | 6.8 | 125 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-09-07 10:30 | 11 | 6.9 | 130 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-09-07 11:30 | 10.9 | 7.6 | 127.5 | 500 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-09-07 12:30 | 11.1 | 8.3 | 122.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-07 13:30 | 11.2 | 8.5 | 120 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-07 14:30 | 11.6 | 8.5 | 122.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-09-07 15:30 | 11.5 | 8.5 | 127.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-09-07 16:30 | 11.3 | 9 | 125 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-09-07 17:30 | 11 | 9.4 | 125 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-09-07 18:30 | 11 | 8.4 | 145 | 635 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-07 19:30 | 11.2 | 6.7 | 165 | 300 | 467.5 | 147.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-07 20:30 | 11.3 | 5.4 | 172.5 | 110 | 205 | 0 | 115 |  | 55.2 |  | 205
Lerwick | 1978-09-07 21:30 | 11 | 4.7 | 180 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-09-07 22:30 | 11 | 5.1 | 190 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-09-07 23:30 | 11.1 | 6.3 | 197.5 | 220 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-09-08 00:30 | 11.3 | 6.7 | 200 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-09-08 01:30 | 11.2 | 6.5 | 202.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-09-08 02:30 | 11 | 7.2 | 212.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-09-08 03:30 | 10.9 | 7.7 | 225 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-09-08 04:30 | 10.9 | 7.4 | 225 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-09-08 05:30 | 10.7 | 7.3 | 215 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-09-08 06:30 | 10.6 | 7.5 | 210 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-09-08 07:30 | 10.9 | 7.5 | 210 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-08 08:30 | 11.1 | 7.3 | 202.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-09-08 09:30 | 11.5 | 6.9 | 187.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-09-08 10:30 | 11.8 | 6.7 | 177.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-09-08 11:30 | 11.6 | 6.5 | 172.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-09-08 12:30 | 11.6 | 6 | 167.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-09-08 13:30 | 11.9 | 6.3 | 162.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-09-08 14:30 | 12 | 8 | 162.5 | 635 | 427.5 | 107.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-08 15:30 | 11.7 | 9.2 | 165 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-08 16:30 | 11.4 | 9.5 | 165 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-08 17:30 | 11.2 | 9.2 | 167.5 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-08 18:30 | 11 | 8.5 | 172.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-09-08 19:30 | 11 | 8.4 | 180 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-08 20:30 | 11 | 9.8 | 192.5 | 1025 | 830 | 510 | 0 |  | 0 |  | 320
Lerwick | 1978-09-08 21:30 | 11.4 | 10.6 | 207.5 | 1270 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-08 22:30 | 11.4 | 9.6 | 215 | 1025 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-08 23:30 | 10.9 | 8.1 | 210 | 635 | 830 | 510 | 0 |  | 0 |  | 320
Lerwick | 1978-09-09 00:30 | 10.9 | 7.1 | 197.5 | 400 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-09 01:30 | 11 | 7.2 | 187.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-09-09 02:30 | 10.9 | 8.2 | 190 | 635 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-09 03:30 | 10.9 | 8.6 | 197.5 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-09 04:30 | 10.9 | 8.5 | 202.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-09-09 05:30 | 10.6 | 9 | 205 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-09-09 06:30 | 10.2 | 10.1 | 202.5 | 1150 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-09-09 07:30 | 10.3 | 11 | 202.5 | 1340 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-09-09 08:30 | 10.8 | 11.1 | 210 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-09-09 09:30 | 11 | 10.6 | 220 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-09-09 10:30 | 11.3 | 10 | 227.5 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-09-09 11:30 | 11.7 | 9.8 | 230 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-09 12:30 | 12.2 | 9.9 | 230 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-09-09 13:30 | 12.4 | 10.1 | 230 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-09 14:30 | 12.4 | 10.3 | 230 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-09-09 15:30 | 12.3 | 10.1 | 230 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-09-09 16:30 | 12.1 | 10 | 230 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-09-09 17:30 | 11.5 | 9.7 | 230 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-09 18:30 | 10.9 | 9.1 | 230 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-09 19:30 | 10.4 | 8.9 | 230 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-09-09 20:30 | 10.3 | 9 | 227.5 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-09-09 21:30 | 10.1 | 9.1 | 222.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-09-09 22:30 | 9.9 | 9.3 | 220 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-09-09 23:30 | 10 | 8.9 | 220 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-09-10 00:30 | 10.2 | 8.5 | 220 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-09-10 01:30 | 10.4 | 8.3 | 217.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-10 02:30 | 10.5 | 7.5 | 212.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-10 03:30 | 10.5 | 6.6 | 217.5 | 300 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-09-10 04:30 | 10.2 | 6 | 237.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-09-10 05:30 | 9.9 | 5.8 | 260 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-09-10 06:30 | 9.7 | 5.9 | 275 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-09-10 07:30 | 9.7 | 6.6 | 282.5 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-09-10 08:30 | 9.8 | 7.1 | 285 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-09-10 09:30 | 9.8 | 7.3 | 282.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-09-10 10:30 | 10.3 | 7.7 | 277.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-09-10 11:30 | 11.1 | 8 | 275 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-10 12:30 | 11.6 | 7.7 | 275 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-10 13:30 | 11.6 | 7.2 | 272.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-09-10 14:30 | 11.2 | 6.8 | 270 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-09-10 15:30 | 10.7 | 6.7 | 270 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-09-10 16:30 | 10.2 | 6.7 | 270 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-09-10 17:30 | 9.7 | 6.4 | 267.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-09-10 18:30 | 9.5 | 5.9 | 262.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-09-10 19:30 | 9.4 | 5.3 | 257.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-09-10 20:30 | 9.3 | 4.6 | 252.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-09-10 21:30 | 9.4 | 4 | 245 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-09-10 22:30 | 9.4 | 2.9 | 237.5 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-09-10 23:30 | 9 | 1.8 | 225 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-11 00:30 | 8.7 | 1.5 | 207.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-11 01:30 | 8.7 | 1.2 | 242.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-11 02:30 | 8.5 | 0.5 | 142.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-11 03:30 | 8.3 | 0 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-11 04:30 | 8.2 | 0.6 | 175 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-11 05:30 | 7.9 | 2.3 | 347.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-11 06:30 | 7.8 | 3.8 | 345 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-09-11 07:30 | 7.9 | 4.6 | 340 | 80 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-09-11 08:30 | 8.8 | 5.4 | 332.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-09-11 09:30 | 9.5 | 6.7 | 327.5 | 300 | 205 | 0 | 115 |  | 55.2 |  | 205
Lerwick | 1978-09-11 10:30 | 10 | 7.8 | 322.5 | 500 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-09-11 11:30 | 10.7 | 8.7 | 320 | 770 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-09-11 12:30 | 10.8 | 9.8 | 320 | 1025 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-11 13:30 | 10.6 | 10.3 | 320 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-11 14:30 | 10.9 | 10.3 | 320 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-09-11 15:30 | 11.1 | 10.3 | 320 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-09-11 16:30 | 10.7 | 10.5 | 320 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-09-11 17:30 | 10.1 | 11 | 320 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-09-11 18:30 | 9.9 | 11.1 | 320 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-09-11 19:30 | 9.7 | 10.7 | 320 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-09-11 20:30 | 9.3 | 10.4 | 320 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-09-11 21:30 | 9.2 | 10.3 | 320 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-09-11 22:30 | 9.4 | 9.9 | 320 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-11 23:30 | 9.3 | 9 | 317.5 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-12 00:30 | 9.1 | 8.3 | 312.5 | 635 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-12 01:30 | 8.8 | 8.3 | 312.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-09-12 02:30 | 8.3 | 8.5 | 317.5 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-12 03:30 | 8.1 | 8.5 | 320 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-09-12 04:30 | 8 | 8.5 | 320 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-09-12 05:30 | 7.9 | 8 | 320 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-12 06:30 | 7.6 | 6.9 | 320 | 300 | 467.5 | 147.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-12 07:30 | 7.8 | 6.4 | 320 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-09-12 08:30 | 8.5 | 6.5 | 317.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-09-12 09:30 | 9 | 6.4 | 312.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-09-12 10:30 | 9.3 | 5.9 | 305 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-09-12 11:30 | 9.3 | 5.5 | 292.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-09-12 12:30 | 9.3 | 5.4 | 277.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-09-12 13:30 | 9.5 | 5.1 | 265 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-09-12 14:30 | 9.7 | 4.4 | 257.5 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-09-12 15:30 | 9.4 | 3.5 | 247.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-09-12 16:30 | 9 | 2.6 | 225 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-09-12 17:30 | 8.5 | 2.3 | 192.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-12 18:30 | 8.3 | 3.3 | 165 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-12 19:30 | 8.1 | 4.8 | 155 | 80 | 40 | 0 | 280 |  | 134.4 |  | 40
Lerwick | 1978-09-12 20:30 | 8.2 | 6.3 | 160 | 220 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-09-12 21:30 | 8.8 | 7.5 | 165 | 500 | 360 | 40 | 0 |  | 0 |  | 320
Lerwick | 1978-09-12 22:30 | 8.4 | 8.4 | 162.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-12 23:30 | 7.9 | 8.9 | 157.5 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-13 00:30 | 8 | 8.9 | 157.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-09-13 01:30 | 8.4 | 8.1 | 175 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-13 02:30 | 9.4 | 7.2 | 205 | 400 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-13 03:30 | 10 | 7.1 | 227.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-09-13 04:30 | 10.3 | 7.3 | 237.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-09-13 05:30 | 10.5 | 7.5 | 237.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-09-13 06:30 | 10.4 | 7.7 | 232.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-13 07:30 | 10.7 | 8.5 | 230 | 770 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-09-13 08:30 | 10.9 | 9.2 | 227.5 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-09-13 09:30 | 11.2 | 9.9 | 222.5 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-13 10:30 | 11.8 | 10.6 | 220 | 1270 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-13 11:30 | 12.4 | 10.9 | 220 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-09-13 12:30 | 12.7 | 10.5 | 220 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-09-13 13:30 | 12.8 | 10.4 | 220 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-09-13 14:30 | 12.6 | 10.4 | 220 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-09-13 15:30 | 12.7 | 10.1 | 217.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-09-13 16:30 | 12.2 | 10.2 | 212.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-09-13 17:30 | 11.5 | 10.5 | 210 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-09-13 18:30 | 11.5 | 10.1 | 210 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-09-13 19:30 | 11.1 | 9.6 | 210 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-13 20:30 | 10.9 | 9.7 | 210 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-09-13 21:30 | 11 | 10.1 | 210 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-13 22:30 | 10.9 | 10.3 | 210 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-09-13 23:30 | 10.7 | 10.5 | 210 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-09-14 00:30 | 10.4 | 11.6 | 210 | 1400 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-09-14 01:30 | 10.2 | 12.7 | 210 | 1470 | 1435 | 1115 | 0 |  | 0 |  | 320
Lerwick | 1978-09-14 02:30 | 10.1 | 12.8 | 210 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-09-14 03:30 | 10 | 12.4 | 212.5 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-09-14 04:30 | 10 | 12.4 | 217.5 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-09-14 05:30 | 10.2 | 12.4 | 220 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-09-14 06:30 | 10.4 | 12.1 | 220 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-09-14 07:30 | 10.5 | 12.1 | 220 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-09-14 08:30 | 10.6 | 12.6 | 222.5 | 1470 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-09-14 09:30 | 10.9 | 13 | 227.5 | 1480 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-09-14 10:30 | 11.1 | 13.2 | 232.5 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-09-14 11:30 | 10.8 | 13.4 | 237.5 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-09-14 12:30 | 10.6 | 13.9 | 242.5 | 1490 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-09-14 13:30 | 10.6 | 14.6 | 247.5 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-09-14 14:30 | 10.3 | 14.5 | 250 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-14 15:30 | 10 | 14.3 | 250 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-14 16:30 | 10.1 | 14.6 | 250 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-14 17:30 | 10.3 | 14.8 | 252.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-14 18:30 | 10.4 | 14.3 | 257.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-14 19:30 | 10.1 | 13.5 | 260 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-09-14 20:30 | 9.7 | 12.7 | 257.5 | 1470 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-09-14 21:30 | 9.5 | 11.3 | 252.5 | 1340 | 1405 | 1085 | 0 |  | 0 |  | 320
Lerwick | 1978-09-14 22:30 | 9.3 | 8.9 | 247.5 | 770 | 1055 | 735 | 0 |  | 0 |  | 320
Lerwick | 1978-09-14 23:30 | 9.1 | 6.7 | 237.5 | 300 | 535 | 215 | 0 |  | 0 |  | 320
Lerwick | 1978-09-15 00:30 | 8.8 | 5.4 | 220 | 110 | 205 | 0 | 115 |  | 55.2 |  | 205
Lerwick | 1978-09-15 01:30 | 8.7 | 4.4 | 200 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-09-15 02:30 | 8.7 | 3.6 | 170 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-09-15 03:30 | 8.5 | 3 | 112.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-09-15 04:30 | 8.1 | 3.8 | 52.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-09-15 05:30 | 7.6 | 6.3 | 22.5 | 220 | 122.5 | 0 | 197.5 |  | 94.8 |  | 122.5
Lerwick | 1978-09-15 06:30 | 7.6 | 7.9 | 182.5 | 500 | 360 | 40 | 0 |  | 0 |  | 320
Lerwick | 1978-09-15 07:30 | 7.6 | 7.9 | 340 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-15 08:30 | 7.6 | 7.9 | 320 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-15 09:30 | 8.5 | 8.7 | 302.5 | 770 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-09-15 10:30 | 9.5 | 9.5 | 292.5 | 1025 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-15 11:30 | 10 | 9.8 | 290 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-09-15 12:30 | 10.4 | 9.8 | 290 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-09-15 13:30 | 10.8 | 9.8 | 287.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-09-15 14:30 | 10.7 | 10 | 280 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-15 15:30 | 10.6 | 9.9 | 275 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-15 16:30 | 10.7 | 8.5 | 272.5 | 770 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-15 17:30 | 10.5 | 7.2 | 262.5 | 400 | 585 | 265 | 0 |  | 0 |  | 320
Lerwick | 1978-09-15 18:30 | 10.2 | 7 | 255 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-09-15 19:30 | 9.8 | 6.7 | 252.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-09-15 20:30 | 9.6 | 6.3 | 242.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-09-15 21:30 | 9.4 | 6.2 | 232.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-09-15 22:30 | 9.2 | 6.3 | 227.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-09-15 23:30 | 9.2 | 7 | 220 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-09-16 00:30 | 9.4 | 7.9 | 207.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-09-16 01:30 | 9.2 | 8.1 | 192.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-16 02:30 | 9 | 9 | 180 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-16 03:30 | 8.9 | 10.7 | 175 | 1270 | 1085 | 765 | 0 |  | 0 |  | 320
Lerwick | 1978-09-16 04:30 | 9.2 | 11.7 | 182.5 | 1400 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-09-16 05:30 | 9.5 | 12.5 | 197.5 | 1470 | 1435 | 1115 | 0 |  | 0 |  | 320
Lerwick | 1978-09-16 06:30 | 10.3 | 13.2 | 210 | 1480 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-09-16 07:30 | 11.2 | 13.1 | 217.5 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-09-16 08:30 | 11.7 | 12.9 | 220 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-09-16 09:30 | 12 | 12.9 | 217.5 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-09-16 10:30 | 12 | 12.7 | 212.5 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-09-16 11:30 | 12.2 | 11.7 | 202.5 | 1400 | 1435 | 1115 | 0 |  | 0 |  | 320
Lerwick | 1978-09-16 12:30 | 12.7 | 10.5 | 187.5 | 1270 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-09-16 13:30 | 12.3 | 10.9 | 180 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-09-16 14:30 | 11.8 | 13.3 | 182.5 | 1480 | 1375 | 1055 | 0 |  | 0 |  | 320
Lerwick | 1978-09-16 15:30 | 12.2 | 16.3 | 190 | 1500 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-09-16 16:30 | 12.3 | 20.7 | 200 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-16 17:30 | 11.8 | 26.5 | 207.5 | 0 | 750 | 430 | 0 |  | 0 |  | 320
Lerwick | 1978-09-16 18:30 | 10.6 | 29.2 | 215 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-16 19:30 | 10.1 | 27.9 | 227.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-16 20:30 | 10.4 | 25.7 | 242.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-16 21:30 | 10.4 | 24.1 | 257.5 | 1500 | 750 | 430 | 0 |  | 0 |  | 320
Lerwick | 1978-09-16 22:30 | 9.8 | 23.3 | 267.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-16 23:30 | 9.3 | 22.3 | 270 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-17 00:30 | 9.4 | 20.8 | 270 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-17 01:30 | 9.3 | 19 | 272.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-17 02:30 | 8.6 | 17.3 | 277.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-17 03:30 | 8.2 | 16.4 | 280 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-17 04:30 | 8.2 | 15.7 | 280 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-17 05:30 | 8 | 15 | 280 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-17 06:30 | 8 | 14.1 | 280 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-17 07:30 | 7.4 | 12.9 | 280 | 1470 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-09-17 08:30 | 6.7 | 12.7 | 280 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-09-17 09:30 | 7.3 | 13.5 | 280 | 1490 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-09-17 10:30 | 8.4 | 14.3 | 280 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-09-17 11:30 | 9 | 14.8 | 277.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-17 12:30 | 9.3 | 14.9 | 272.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-17 13:30 | 9.6 | 14.8 | 270 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-17 14:30 | 10 | 14.5 | 270 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-17 15:30 | 10.4 | 14.3 | 270 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-17 16:30 | 10 | 13.8 | 270 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-09-17 17:30 | 9.4 | 13.1 | 270 | 1480 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-09-17 18:30 | 9.2 | 12.7 | 270 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-09-17 19:30 | 9 | 12.4 | 270 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-09-17 20:30 | 9 | 12.2 | 270 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-09-17 21:30 | 9.2 | 11.9 | 270 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-09-17 22:30 | 9.4 | 11.5 | 270 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-09-17 23:30 | 9.6 | 10.9 | 270 | 1270 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-09-18 00:30 | 9.6 | 10.5 | 270 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-09-18 01:30 | 9.5 | 10.9 | 270 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-09-18 02:30 | 9.4 | 11 | 267.5 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-09-18 03:30 | 9.4 | 10.8 | 262.5 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-09-18 04:30 | 9.6 | 11.4 | 260 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-09-18 05:30 | 9.6 | 11.7 | 260 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-09-18 06:30 | 9.3 | 11 | 260 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-09-18 07:30 | 9.3 | 10.4 | 260 | 1150 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-09-18 08:30 | 9.5 | 10.8 | 260 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-09-18 09:30 | 9.8 | 11.5 | 262.5 | 1400 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-09-18 10:30 | 9.9 | 10.4 | 272.5 | 1150 | 1275 | 955 | 0 |  | 0 |  | 320
Lerwick | 1978-09-18 11:30 | 9.9 | 7.6 | 292.5 | 500 | 825 | 505 | 0 |  | 0 |  | 320
Lerwick | 1978-09-18 12:30 | 9.9 | 6 | 315 | 220 | 360 | 40 | 0 |  | 0 |  | 320
Lerwick | 1978-09-18 13:30 | 9.5 | 5.9 | 327.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-09-18 14:30 | 9 | 5.9 | 325 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-09-18 15:30 | 8.8 | 5.9 | 315 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-09-18 16:30 | 8.7 | 5.4 | 310 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-09-18 17:30 | 8.3 | 4.7 | 310 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-09-18 18:30 | 7.9 | 4.7 | 307.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-09-18 19:30 | 7.1 | 6 | 305 | 220 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-09-18 20:30 | 6.6 | 7.1 | 310 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-09-18 21:30 | 6.7 | 6.5 | 315 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-09-18 22:30 | 6.4 | 5.8 | 312.5 | 150 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-09-18 23:30 | 6.3 | 5.8 | 312.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-09-19 00:30 | 6.8 | 6 | 317.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-09-19 01:30 | 7 | 5.9 | 320 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-09-19 02:30 | 6.5 | 4.8 | 317.5 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-09-19 03:30 | 6.2 | 3.8 | 312.5 | 25 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-09-19 04:30 | 6.2 | 3.4 | 315 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-09-19 05:30 | 6.1 | 3.2 | 325 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-19 06:30 | 5.8 | 3.1 | 330 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-19 07:30 | 6 | 3.2 | 325 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-19 08:30 | 6.9 | 3.6 | 320 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-09-19 09:30 | 7.9 | 3.9 | 327.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-09-19 10:30 | 8.7 | 4 | 335 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-09-19 11:30 | 8.9 | 4 | 330 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-09-19 12:30 | 8.8 | 4.2 | 320 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-09-19 13:30 | 9.2 | 4.4 | 312.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-09-19 14:30 | 9.2 | 4.4 | 307.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-09-19 15:30 | 8.1 | 4.1 | 300 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-09-19 16:30 | 7.5 | 3.7 | 297.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-09-19 17:30 | 7.6 | 3.4 | 300 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-09-19 18:30 | 7 | 3 | 290 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-19 19:30 | 6.3 | 2.7 | 270 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-19 20:30 | 5.8 | 3 | 250 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-19 21:30 | 5.3 | 3.6 | 232.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-09-19 22:30 | 5.7 | 4.7 | 225 | 80 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-09-19 23:30 | 7.1 | 6 | 225 | 220 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-09-20 00:30 | 8.4 | 6.9 | 225 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-09-20 01:30 | 9 | 7.2 | 227.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-09-20 02:30 | 9.4 | 7.6 | 230 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-09-20 03:30 | 9.7 | 9.4 | 227.5 | 900 | 700 | 380 | 0 |  | 0 |  | 320
Lerwick | 1978-09-20 04:30 | 9.8 | 11.6 | 225 | 1400 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-09-20 05:30 | 9.8 | 12.4 | 225 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-09-20 06:30 | 9.6 | 12.4 | 225 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-09-20 07:30 | 9.7 | 12.4 | 227.5 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-09-20 08:30 | 10.1 | 12.5 | 235 | 1470 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-09-20 09:30 | 10.7 | 12.7 | 250 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-09-20 10:30 | 11 | 12.7 | 267.5 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-09-20 11:30 | 10.8 | 11.7 | 280 | 1400 | 1435 | 1115 | 0 |  | 0 |  | 320
Lerwick | 1978-09-20 12:30 | 10.5 | 10.6 | 287.5 | 1270 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-09-20 13:30 | 10.5 | 10.3 | 287.5 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-09-20 14:30 | 10.4 | 10 | 282.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-09-20 15:30 | 10.3 | 9.6 | 280 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-20 16:30 | 10.4 | 9.4 | 282.5 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-20 17:30 | 10.3 | 9 | 287.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-09-20 18:30 | 9.8 | 8.8 | 290 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-09-20 19:30 | 9.6 | 8.6 | 287.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-09-20 20:30 | 9.6 | 8.3 | 285 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-20 21:30 | 9.7 | 8.4 | 290 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-09-20 22:30 | 9.6 | 8.6 | 297.5 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-20 23:30 | 9.2 | 7.8 | 300 | 500 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-09-21 00:30 | 9 | 6.8 | 300 | 300 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-09-21 01:30 | 8.8 | 5.9 | 300 | 150 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-09-21 02:30 | 8.2 | 4.9 | 302.5 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-09-21 03:30 | 7.8 | 4.2 | 310 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-09-21 04:30 | 7.7 | 3.5 | 315 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-09-21 05:30 | 7.7 | 2.9 | 307.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-09-21 06:30 | 7.7 | 2.4 | 297.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-21 07:30 | 7.8 | 1.4 | 312.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-21 08:30 | 8 | 0.6 | 202.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-21 09:30 | 8.2 | 1 | 115 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-21 10:30 | 8.4 | 2.1 | 157.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-21 11:30 | 8.5 | 3.5 | 162.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-09-21 12:30 | 8.5 | 4.9 | 172.5 | 80 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-09-21 13:30 | 8.8 | 6 | 192.5 | 220 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-09-21 14:30 | 9.8 | 7.4 | 215 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-09-21 15:30 | 11 | 8.4 | 227.5 | 635 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-21 16:30 | 11.4 | 8.9 | 227.5 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-21 17:30 | 11.4 | 9.2 | 220 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-09-21 18:30 | 11.4 | 9.7 | 212.5 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-21 19:30 | 11.4 | 10.4 | 210 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-21 20:30 | 11.7 | 11 | 212.5 | 1340 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-09-21 21:30 | 11.7 | 11.1 | 217.5 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-09-21 22:30 | 11.5 | 11.4 | 222.5 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-09-21 23:30 | 11.5 | 12.1 | 230 | 1450 | 1395 | 1075 | 0 |  | 0 |  | 320
Lerwick | 1978-09-22 00:30 | 11.7 | 12.5 | 237.5 | 1470 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-09-22 01:30 | 11.6 | 12.8 | 237.5 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-09-22 02:30 | 11.3 | 13.1 | 232.5 | 1480 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-09-22 03:30 | 11.1 | 12.7 | 230 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-09-22 04:30 | 11 | 12.2 | 232.5 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-09-22 05:30 | 11 | 12 | 237.5 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-09-22 06:30 | 11 | 11.7 | 240 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-09-22 07:30 | 10.8 | 11.2 | 242.5 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-09-22 08:30 | 10.7 | 10.5 | 250 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-09-22 09:30 | 10.9 | 9 | 265 | 900 | 1085 | 765 | 0 |  | 0 |  | 320
Lerwick | 1978-09-22 10:30 | 11 | 7.3 | 290 | 400 | 650 | 330 | 0 |  | 0 |  | 320
Lerwick | 1978-09-22 11:30 | 11.1 | 6.4 | 317.5 | 220 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-09-22 12:30 | 11.5 | 5.9 | 335 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-09-22 13:30 | 12 | 5.9 | 330 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-09-22 14:30 | 12.1 | 6.3 | 315 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-09-22 15:30 | 11.5 | 6.1 | 320 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-09-22 16:30 | 10.7 | 5.4 | 332.5 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-09-22 17:30 | 10.2 | 4.2 | 337.5 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-09-22 18:30 | 10 | 3.3 | 170 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-09-22 19:30 | 9.9 | 3.1 | 10 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-22 20:30 | 9.7 | 3.1 | 35 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-22 21:30 | 9.4 | 2.6 | 77.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-22 22:30 | 9.3 | 1.5 | 125 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-22 23:30 | 9.2 | 1.2 | 157.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-23 00:30 | 9.1 | 1.6 | 180 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-23 01:30 | 9 | 1.9 | 177.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-23 02:30 | 8.7 | 2.6 | 160 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-23 03:30 | 8.6 | 3.7 | 162.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-09-23 04:30 | 8.7 | 5 | 170 | 110 | 67.5 | 0 | 252.5 |  | 121.2 |  | 67.5
Lerwick | 1978-09-23 05:30 | 8.9 | 5.9 | 172.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-09-23 06:30 | 9.2 | 6.7 | 182.5 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-09-23 07:30 | 9.7 | 7.6 | 205 | 500 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-09-23 08:30 | 10.6 | 7.9 | 230 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-23 09:30 | 11.4 | 7.2 | 237.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-09-23 10:30 | 11.3 | 6.4 | 232.5 | 220 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-09-23 11:30 | 11.1 | 6.2 | 232.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-09-23 12:30 | 11 | 6 | 237.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-09-23 13:30 | 11 | 5.9 | 237.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-09-23 14:30 | 11 | 6.3 | 230 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-09-23 15:30 | 11 | 6.7 | 222.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-09-23 16:30 | 10.9 | 6.7 | 217.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-09-23 17:30 | 10.8 | 6.8 | 207.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-09-23 18:30 | 10.8 | 7 | 192.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-09-23 19:30 | 10.6 | 7.5 | 182.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-09-23 20:30 | 10.2 | 8.6 | 180 | 770 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-09-23 21:30 | 10 | 9.8 | 180 | 1025 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-23 22:30 | 10.2 | 10.8 | 182.5 | 1270 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-23 23:30 | 10.4 | 12.2 | 195 | 1450 | 1360 | 1040 | 0 |  | 0 |  | 320
Lerwick | 1978-09-24 00:30 | 10.6 | 13.2 | 215 | 1480 | 1465 | 1145 | 0 |  | 0 |  | 320
Lerwick | 1978-09-24 01:30 | 10.9 | 11.9 | 232.5 | 1400 | 1440 | 1120 | 0 |  | 0 |  | 320
Lerwick | 1978-09-24 02:30 | 10.9 | 9.6 | 242.5 | 1025 | 1212.5 | 892.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-24 03:30 | 10.4 | 8.9 | 245 | 770 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-24 04:30 | 10 | 9 | 245 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-09-24 05:30 | 9.7 | 8.9 | 245 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-09-24 06:30 | 9.2 | 8.8 | 247.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-09-24 07:30 | 9.4 | 9 | 247.5 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-09-24 08:30 | 10.1 | 9.5 | 242.5 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-24 09:30 | 10.6 | 9.8 | 240 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-09-24 10:30 | 11.4 | 10.1 | 240 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-24 11:30 | 12 | 10.7 | 237.5 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-09-24 12:30 | 12.1 | 10.6 | 232.5 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-09-24 13:30 | 11.9 | 10.3 | 232.5 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-09-24 14:30 | 11.3 | 10.3 | 237.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-09-24 15:30 | 11.2 | 9.8 | 240 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-24 16:30 | 11.2 | 8.9 | 237.5 | 770 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-24 17:30 | 10.6 | 8.2 | 232.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-24 18:30 | 10 | 8 | 232.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-09-24 19:30 | 9.5 | 8 | 235 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-09-24 20:30 | 9.1 | 8.1 | 235 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-09-24 21:30 | 9 | 8.4 | 237.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-09-24 22:30 | 9 | 9 | 240 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-24 23:30 | 8.8 | 8.9 | 237.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-09-25 00:30 | 8.7 | 8.2 | 235 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-25 01:30 | 8.5 | 7.8 | 237.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-25 02:30 | 8.6 | 7.4 | 240 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-09-25 03:30 | 8.4 | 7.4 | 240 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-09-25 04:30 | 8.3 | 7.8 | 237.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-09-25 05:30 | 8.6 | 7.8 | 235 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-25 06:30 | 8.4 | 7.8 | 237.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-25 07:30 | 8.3 | 8 | 237.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-25 08:30 | 8.8 | 8 | 235 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-09-25 09:30 | 9.8 | 8 | 235 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-09-25 10:30 | 9.3 | 7.8 | 230 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-25 11:30 | 8.1 | 7.9 | 232.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-25 12:30 | 7.9 | 8.8 | 245 | 770 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-09-25 13:30 | 7.3 | 10.1 | 247.5 | 1150 | 960 | 640 | 0 |  | 0 |  | 320
Lerwick | 1978-09-25 14:30 | 8.2 | 10.5 | 245 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-09-25 15:30 | 9.7 | 9.8 | 240 | 1025 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-25 16:30 | 9.3 | 9.4 | 232.5 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-25 17:30 | 8.6 | 9.4 | 230 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-09-25 18:30 | 8.3 | 9 | 230 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-09-25 19:30 | 8.4 | 8.9 | 235 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-09-25 20:30 | 8.4 | 8.9 | 242.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-09-25 21:30 | 8.3 | 8.9 | 245 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-09-25 22:30 | 8.2 | 9 | 247.5 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-09-25 23:30 | 7.9 | 8.7 | 250 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-09-26 00:30 | 7.7 | 7.8 | 247.5 | 500 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-09-26 01:30 | 8.1 | 6.8 | 242.5 | 300 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-09-26 02:30 | 8.6 | 6.8 | 240 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-09-26 03:30 | 8.7 | 6.8 | 237.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-09-26 04:30 | 8.4 | 5.7 | 230 | 150 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-09-26 05:30 | 8.2 | 5.2 | 222.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-09-26 06:30 | 8.2 | 5.1 | 222.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-09-26 07:30 | 7.5 | 4.6 | 235 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-09-26 08:30 | 7.3 | 4.6 | 245 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-09-26 09:30 | 7.7 | 5.1 | 237.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-09-26 10:30 | 8.6 | 5.6 | 232.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-09-26 11:30 | 10.2 | 6.3 | 235 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-09-26 12:30 | 10.8 | 6.9 | 230 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-09-26 13:30 | 10.6 | 7.1 | 220 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-09-26 14:30 | 10.5 | 6.7 | 212.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-09-26 15:30 | 10 | 5.7 | 210 | 150 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-09-26 16:30 | 9.5 | 4 | 210 | 60 | 105 | 0 | 215 |  | 103.2 |  | 105
Lerwick | 1978-09-26 17:30 | 9.2 | 2.6 | 217.5 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-09-26 18:30 | 8.4 | 2.7 | 240 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-26 19:30 | 8 | 3.6 | 265 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-09-26 20:30 | 8 | 3.7 | 275 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-09-26 21:30 | 8.1 | 3.4 | 270 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-09-26 22:30 | 8.1 | 3.2 | 260 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-26 23:30 | 7.5 | 3.2 | 252.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-27 00:30 | 7 | 3.6 | 250 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-09-27 01:30 | 7 | 3.9 | 252.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-09-27 02:30 | 7 | 3.7 | 260 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-09-27 03:30 | 7.3 | 3.3 | 265 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-09-27 04:30 | 7.4 | 2.6 | 262.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-27 05:30 | 6.7 | 1.9 | 262.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-27 06:30 | 6.5 | 2 | 267.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-27 07:30 | 7 | 2.6 | 275 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-27 08:30 | 7.6 | 3.7 | 290 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-09-27 09:30 | 8.5 | 4.7 | 305 | 80 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-09-27 10:30 | 9.2 | 5 | 307.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-09-27 11:30 | 9.3 | 5.2 | 302.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-09-27 12:30 | 9.3 | 5.8 | 302.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-09-27 13:30 | 9.6 | 6.6 | 305 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-09-27 14:30 | 9.9 | 7.1 | 302.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-09-27 15:30 | 9.6 | 7.4 | 300 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-09-27 16:30 | 8.9 | 7.8 | 302.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-09-27 17:30 | 8.4 | 7.8 | 302.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-27 18:30 | 7.8 | 7.4 | 295 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-09-27 19:30 | 7.6 | 6.9 | 290 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-09-27 20:30 | 7.5 | 6.5 | 290 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-09-27 21:30 | 7.3 | 5.9 | 290 | 150 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-09-27 22:30 | 7.3 | 4.9 | 290 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-09-27 23:30 | 6.7 | 4 | 290 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-09-28 00:30 | 6 | 3.3 | 290 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-09-28 01:30 | 6.1 | 3.1 | 290 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-28 02:30 | 6.1 | 3.1 | 290 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-28 03:30 | 5.7 | 3.1 | 290 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-28 04:30 | 6 | 3.1 | 292.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-28 05:30 | 6.2 | 2.6 | 300 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-28 06:30 | 6 | 1.5 | 320 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-28 07:30 | 5.6 | 0.6 | 200 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-28 08:30 | 6.2 | 1.3 | 100 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-28 09:30 | 8.2 | 2.8 | 140 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-28 10:30 | 9.1 | 4 | 147.5 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-09-28 11:30 | 9.1 | 5.1 | 147.5 | 110 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-09-28 12:30 | 9.4 | 6.2 | 142.5 | 220 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-09-28 13:30 | 9.5 | 7.2 | 140 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-09-28 14:30 | 9 | 8.1 | 140 | 635 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-28 15:30 | 8.7 | 8.9 | 142.5 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-28 16:30 | 8.5 | 9.6 | 145 | 1025 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-28 17:30 | 8.4 | 10.4 | 142.5 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-28 18:30 | 8.4 | 11 | 140 | 1340 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-09-28 19:30 | 8.5 | 11.4 | 140 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-09-28 20:30 | 8.5 | 11.7 | 137.5 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-09-28 21:30 | 8.4 | 12.2 | 132.5 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-09-28 22:30 | 8.2 | 12.7 | 130 | 1470 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-09-28 23:30 | 8.1 | 13 | 127.5 | 1480 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-09-29 00:30 | 8.1 | 13.5 | 125 | 1490 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-09-29 01:30 | 8.1 | 14.1 | 127.5 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-09-29 02:30 | 7.8 | 14.5 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-29 03:30 | 7.4 | 14.7 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-29 04:30 | 7.3 | 14.4 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-29 05:30 | 7.5 | 13.9 | 130 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-09-29 06:30 | 7.7 | 13.3 | 130 | 1480 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-09-29 07:30 | 7.9 | 13.2 | 130 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-09-29 08:30 | 8 | 13.8 | 130 | 1490 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-09-29 09:30 | 8.2 | 14.3 | 130 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-09-29 10:30 | 8.3 | 14.3 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-29 11:30 | 8.3 | 14.3 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-29 12:30 | 8.4 | 14.6 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-29 13:30 | 8.6 | 14.5 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-09-29 14:30 | 8.6 | 13.8 | 130 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-09-29 15:30 | 8.7 | 13.5 | 130 | 1490 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-09-29 16:30 | 8.9 | 12.8 | 130 | 1470 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-09-29 17:30 | 9.1 | 11.1 | 130 | 1340 | 1405 | 1085 | 0 |  | 0 |  | 320
Lerwick | 1978-09-29 18:30 | 9.4 | 10.4 | 130 | 1150 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-09-29 19:30 | 9.7 | 10.7 | 130 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-09-29 20:30 | 9.7 | 11.2 | 130 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-09-29 21:30 | 9.4 | 11.1 | 130 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-09-29 22:30 | 9.3 | 9.9 | 130 | 1025 | 1182.5 | 862.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-29 23:30 | 9.3 | 8.1 | 125 | 635 | 830 | 510 | 0 |  | 0 |  | 320
Lerwick | 1978-09-30 00:30 | 9.3 | 6.5 | 122.5 | 300 | 467.5 | 147.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-30 01:30 | 9.2 | 5.9 | 130 | 150 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-09-30 02:30 | 9.2 | 6.7 | 130 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-09-30 03:30 | 9.5 | 8.1 | 125 | 635 | 467.5 | 147.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-30 04:30 | 9.4 | 8.6 | 125 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-30 05:30 | 9.3 | 8.7 | 122.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-09-30 06:30 | 9.5 | 9.4 | 120 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-09-30 07:30 | 9.5 | 9.5 | 120 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-30 08:30 | 9.5 | 8.9 | 120 | 770 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-30 09:30 | 9.8 | 8.2 | 120 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-30 10:30 | 10 | 7.7 | 120 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-09-30 11:30 | 10.4 | 7.2 | 120 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-09-30 12:30 | 10.9 | 6.7 | 120 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-09-30 13:30 | 11.2 | 5.9 | 122.5 | 150 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-09-30 14:30 | 11.2 | 4.6 | 122.5 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-09-30 15:30 | 11 | 3 | 102.5 | 0 | 40 | 0 | 280 |  | 134.4 |  | 40
Lerwick | 1978-09-30 16:30 | 10.7 | 1.7 | 60 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-30 17:30 | 10 | 1.1 | 195 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-30 18:30 | 9.1 | 0.7 | 352.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-30 19:30 | 7.9 | 0.2 | 175 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-30 20:30 | 7.8 | 0 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-30 21:30 | 7 | 0 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-30 22:30 | 5.8 | 0 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-09-30 23:30 | 5.7 | 0 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-01 00:30 | 5.2 | 0.2 | 142.5 | 0 | 0 | 0 | 320 |  | 153.6 | 33369.6 | 0 | 168560
Lerwick | 1978-10-01 01:30 | 4.6 | 0.7 | 247.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-01 02:30 | 5 | 1 | 207.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-01 03:30 | 5.3 | 1 | 202.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-01 04:30 | 5.2 | 1.1 | 202.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-01 05:30 | 5.2 | 1.5 | 205 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-01 06:30 | 4.9 | 2.2 | 202.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-01 07:30 | 5.8 | 3.3 | 202.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-01 08:30 | 7.5 | 4.9 | 207.5 | 80 | 40 | 0 | 280 |  | 134.4 |  | 40
Lerwick | 1978-10-01 09:30 | 9.2 | 6.5 | 207.5 | 300 | 190 | 0 | 130 |  | 62.4 |  | 190
Lerwick | 1978-10-01 10:30 | 10.4 | 7.8 | 202.5 | 500 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-10-01 11:30 | 10.8 | 9.2 | 200 | 900 | 700 | 380 | 0 |  | 0 |  | 320
Lerwick | 1978-10-01 12:30 | 10.9 | 10.4 | 200 | 1150 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-10-01 13:30 | 11.1 | 10.8 | 200 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-10-01 14:30 | 10.9 | 10.8 | 200 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-10-01 15:30 | 10.2 | 10.8 | 200 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-10-01 16:30 | 9.9 | 11 | 197.5 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-10-01 17:30 | 9.7 | 11.9 | 192.5 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-10-01 18:30 | 9.6 | 13 | 192.5 | 1480 | 1440 | 1120 | 0 |  | 0 |  | 320
Lerwick | 1978-10-01 19:30 | 9.5 | 14.1 | 200 | 1500 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-10-01 20:30 | 9.5 | 15 | 207.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-01 21:30 | 9.4 | 15.1 | 210 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-01 22:30 | 9.4 | 14.5 | 212.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-01 23:30 | 9.7 | 13 | 227.5 | 1480 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-10-02 00:30 | 9.8 | 10.4 | 247.5 | 1150 | 1315 | 995 | 0 |  | 0 |  | 320
Lerwick | 1978-10-02 01:30 | 9.5 | 8.5 | 255 | 770 | 960 | 640 | 0 |  | 0 |  | 320
Lerwick | 1978-10-02 02:30 | 9.1 | 7.9 | 257.5 | 500 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-10-02 03:30 | 8.9 | 7.3 | 257.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-10-02 04:30 | 8.5 | 6.8 | 252.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-10-02 05:30 | 8.3 | 6.7 | 252.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-10-02 06:30 | 8.4 | 6.7 | 255 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-10-02 07:30 | 8.4 | 6.7 | 250 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-10-02 08:30 | 8.7 | 7.1 | 247.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-10-02 09:30 | 8.9 | 7.7 | 255 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-10-02 10:30 | 9.4 | 7.7 | 257.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-02 11:30 | 10 | 7.5 | 250 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-02 12:30 | 10.5 | 7.5 | 240 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-02 13:30 | 11.1 | 7.3 | 230 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-10-02 14:30 | 11 | 7.2 | 220 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-10-02 15:30 | 10.7 | 6.8 | 210 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-10-02 16:30 | 10.1 | 6 | 200 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-10-02 17:30 | 9.2 | 6 | 192.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-10-02 18:30 | 8.9 | 7.2 | 187.5 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-10-02 19:30 | 9 | 8.5 | 185 | 770 | 585 | 265 | 0 |  | 0 |  | 320
Lerwick | 1978-10-02 20:30 | 9.1 | 9.4 | 187.5 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-10-02 21:30 | 8.9 | 9.4 | 190 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-10-02 22:30 | 8.5 | 8.9 | 192.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-10-02 23:30 | 8.6 | 9.5 | 197.5 | 1025 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-03 00:30 | 8.8 | 10.6 | 200 | 1270 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-03 01:30 | 8.9 | 11.4 | 202.5 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-10-03 02:30 | 9.1 | 11.8 | 210 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-10-03 03:30 | 8.9 | 11.5 | 217.5 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-10-03 04:30 | 8.4 | 10.9 | 220 | 1270 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-10-03 05:30 | 7.8 | 10 | 222.5 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-10-03 06:30 | 7.5 | 9.6 | 227.5 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-03 07:30 | 7.3 | 10.6 | 227.5 | 1270 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-03 08:30 | 8 | 12 | 222.5 | 1450 | 1360 | 1040 | 0 |  | 0 |  | 320
Lerwick | 1978-10-03 09:30 | 8.9 | 12.7 | 220 | 1470 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-10-03 10:30 | 9 | 13.4 | 222.5 | 1480 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-10-03 11:30 | 9.6 | 13.6 | 227.5 | 1490 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-10-03 12:30 | 9.9 | 13.4 | 230 | 1480 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-10-03 13:30 | 9.2 | 13.4 | 230 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-10-03 14:30 | 8.5 | 12.6 | 227.5 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-10-03 15:30 | 8.4 | 11.8 | 225 | 1400 | 1435 | 1115 | 0 |  | 0 |  | 320
Lerwick | 1978-10-03 16:30 | 8.3 | 11.9 | 227.5 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-10-03 17:30 | 8.3 | 11.7 | 232.5 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-10-03 18:30 | 8 | 11.4 | 237.5 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-10-03 19:30 | 7.4 | 11.4 | 237.5 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-10-03 20:30 | 7.3 | 11.6 | 232.5 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-10-03 21:30 | 7.6 | 11.9 | 232.5 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-10-03 22:30 | 7.7 | 12.2 | 237.5 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-10-03 23:30 | 7.9 | 12.4 | 242.5 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-10-04 00:30 | 8 | 12.2 | 247.5 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-10-04 01:30 | 7.9 | 11.5 | 247.5 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-10-04 02:30 | 8.1 | 10.6 | 245 | 1270 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-10-04 03:30 | 7.4 | 10.4 | 247.5 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-10-04 04:30 | 7 | 10.7 | 250 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-10-04 05:30 | 7.1 | 11.1 | 250 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-10-04 06:30 | 7 | 11.4 | 250 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-10-04 07:30 | 7.5 | 11.7 | 250 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-10-04 08:30 | 8 | 12.2 | 252.5 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-10-04 09:30 | 8.2 | 12.8 | 257.5 | 1470 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-10-04 10:30 | 8.9 | 13.5 | 260 | 1490 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-10-04 11:30 | 9.1 | 14 | 260 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-10-04 12:30 | 9.1 | 13.9 | 262.5 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-10-04 13:30 | 9.4 | 13.2 | 265 | 1480 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-10-04 14:30 | 8.8 | 12.7 | 262.5 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-10-04 15:30 | 8.2 | 12.5 | 260 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-10-04 16:30 | 8.2 | 12.4 | 260 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-10-04 17:30 | 8.1 | 12.4 | 262.5 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-10-04 18:30 | 8 | 12.1 | 265 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-10-04 19:30 | 8 | 11.4 | 262.5 | 1340 | 1395 | 1075 | 0 |  | 0 |  | 320
Lerwick | 1978-10-04 20:30 | 8 | 10.7 | 260 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-10-04 21:30 | 8 | 10.1 | 260 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-10-04 22:30 | 8 | 9.1 | 260 | 900 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-10-04 23:30 | 7.9 | 7.7 | 257.5 | 500 | 700 | 380 | 0 |  | 0 |  | 320
Lerwick | 1978-10-05 00:30 | 7.9 | 6.3 | 252.5 | 220 | 360 | 40 | 0 |  | 0 |  | 320
Lerwick | 1978-10-05 01:30 | 7.6 | 4.5 | 247.5 | 80 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-10-05 02:30 | 7.1 | 2 | 272.5 | 0 | 40 | 0 | 280 |  | 134.4 |  | 40
Lerwick | 1978-10-05 03:30 | 6.6 | 1.3 | 162.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-05 04:30 | 6.3 | 2.8 | 47.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-05 05:30 | 6.1 | 4.4 | 77.5 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-10-05 06:30 | 6.2 | 5.5 | 82.5 | 150 | 105 | 0 | 215 |  | 103.2 |  | 105
Lerwick | 1978-10-05 07:30 | 6.6 | 6.3 | 80 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-10-05 08:30 | 6.7 | 6.1 | 82.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-10-05 09:30 | 6.9 | 5.6 | 87.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-10-05 10:30 | 7.1 | 5.2 | 92.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-10-05 11:30 | 7.3 | 4.9 | 100 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-10-05 12:30 | 7.7 | 4.7 | 107.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-10-05 13:30 | 8 | 4.4 | 110 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-10-05 14:30 | 8 | 4.2 | 110 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-10-05 15:30 | 8 | 4.2 | 107.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-10-05 16:30 | 8 | 4.9 | 102.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-10-05 17:30 | 7.9 | 5.2 | 105 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-10-05 18:30 | 7.8 | 4.7 | 117.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-10-05 19:30 | 7.9 | 4.1 | 130 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-10-05 20:30 | 8 | 3.3 | 137.5 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-10-05 21:30 | 8.3 | 3.3 | 170 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-05 22:30 | 8.5 | 5.4 | 230 | 110 | 55 | 0 | 265 |  | 127.2 |  | 55
Lerwick | 1978-10-05 23:30 | 9.3 | 7.7 | 262.5 | 500 | 305 | 0 | 15 |  | 7.2 |  | 305
Lerwick | 1978-10-06 00:30 | 10.2 | 8.7 | 267.5 | 770 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-10-06 01:30 | 10.4 | 9.4 | 270 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-10-06 02:30 | 10.1 | 10 | 270 | 1150 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-10-06 03:30 | 9.7 | 10.1 | 267.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-10-06 04:30 | 9.6 | 9.5 | 262.5 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-06 05:30 | 9.7 | 8.3 | 257.5 | 635 | 830 | 510 | 0 |  | 0 |  | 320
Lerwick | 1978-10-06 06:30 | 9.9 | 7.3 | 252.5 | 400 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-06 07:30 | 9.9 | 7.5 | 245 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-10-06 08:30 | 10.2 | 9.7 | 235 | 1025 | 762.5 | 442.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-06 09:30 | 10.8 | 12.7 | 230 | 1470 | 1247.5 | 927.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-06 10:30 | 11.2 | 14.4 | 230 | 1500 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-10-06 11:30 | 11.4 | 14.4 | 230 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-06 12:30 | 11.4 | 14.4 | 230 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-06 13:30 | 11.9 | 14.9 | 230 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-06 14:30 | 12.3 | 15 | 232.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-06 15:30 | 12.1 | 14.5 | 237.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-06 16:30 | 11.6 | 13.8 | 240 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-10-06 17:30 | 11.5 | 13.1 | 240 | 1480 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-10-06 18:30 | 11.5 | 12.9 | 237.5 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-10-06 19:30 | 11.4 | 13 | 232.5 | 1480 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-10-06 20:30 | 11.2 | 13.2 | 227.5 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-10-06 21:30 | 11.2 | 13.2 | 222.5 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-10-06 22:30 | 11.4 | 13.3 | 220 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-10-06 23:30 | 11.4 | 13.7 | 217.5 | 1490 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-10-07 00:30 | 11.5 | 13.2 | 212.5 | 1480 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-10-07 01:30 | 11.7 | 12 | 212.5 | 1450 | 1465 | 1145 | 0 |  | 0 |  | 320
Lerwick | 1978-10-07 02:30 | 11.9 | 11.2 | 217.5 | 1340 | 1395 | 1075 | 0 |  | 0 |  | 320
Lerwick | 1978-10-07 03:30 | 12 | 11.1 | 220 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-10-07 04:30 | 12 | 11.4 | 220 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-10-07 05:30 | 11.8 | 11.2 | 217.5 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-10-07 06:30 | 11.6 | 10.9 | 215 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-10-07 07:30 | 11.6 | 10.6 | 215 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-10-07 08:30 | 11.8 | 10 | 212.5 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-10-07 09:30 | 12 | 9 | 210 | 900 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-10-07 10:30 | 12.1 | 8.3 | 217.5 | 635 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-07 11:30 | 12.4 | 7.8 | 235 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-07 12:30 | 12.7 | 6.8 | 247.5 | 300 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-10-07 13:30 | 12.9 | 5.8 | 250 | 150 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-10-07 14:30 | 12.5 | 5.2 | 252.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-10-07 15:30 | 12.1 | 4.9 | 255 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-10-07 16:30 | 11.5 | 4.4 | 250 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-10-07 17:30 | 10.5 | 3.3 | 227.5 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-10-07 18:30 | 9.4 | 2.4 | 195 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-07 19:30 | 8.3 | 2.9 | 180 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-07 20:30 | 8 | 3.6 | 180 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-10-07 21:30 | 8.4 | 3.6 | 180 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-10-07 22:30 | 8.7 | 3.6 | 180 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-10-07 23:30 | 8.9 | 3.3 | 172.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-10-08 00:30 | 8.7 | 2.9 | 160 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-08 01:30 | 8.5 | 2.9 | 160 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-08 02:30 | 8.6 | 3.7 | 172.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-10-08 03:30 | 8.9 | 4.6 | 182.5 | 80 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-10-08 04:30 | 9 | 4.7 | 175 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-10-08 05:30 | 9.1 | 4.7 | 162.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-10-08 06:30 | 9.1 | 5.1 | 165 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-10-08 07:30 | 9.3 | 5.4 | 170 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-10-08 08:30 | 9.7 | 5.5 | 172.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-10-08 09:30 | 9.9 | 6 | 177.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-10-08 10:30 | 10.4 | 6.5 | 180 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-10-08 11:30 | 11.5 | 6.5 | 177.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-10-08 12:30 | 12.1 | 6.1 | 170 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-10-08 13:30 | 12.3 | 5.6 | 162.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-10-08 14:30 | 11.8 | 5.4 | 162.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-10-08 15:30 | 11.6 | 5.6 | 167.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-10-08 16:30 | 11.9 | 5.9 | 172.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-10-08 17:30 | 11 | 5.6 | 175 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-10-08 18:30 | 10.4 | 5.5 | 175 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-10-08 19:30 | 10.4 | 6.9 | 182.5 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-10-08 20:30 | 10.7 | 9.5 | 200 | 1025 | 662.5 | 342.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-08 21:30 | 11.8 | 11 | 215 | 1340 | 1182.5 | 862.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-08 22:30 | 12.3 | 10.4 | 222.5 | 1150 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-10-08 23:30 | 12 | 9.3 | 227.5 | 900 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-10-09 00:30 | 11.7 | 8.2 | 230 | 635 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-09 01:30 | 11.5 | 6.9 | 230 | 300 | 467.5 | 147.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-09 02:30 | 11.1 | 4.9 | 217.5 | 80 | 190 | 0 | 130 |  | 62.4 |  | 190
Lerwick | 1978-10-09 03:30 | 10.8 | 3.1 | 187.5 | 0 | 40 | 0 | 280 |  | 134.4 |  | 40
Lerwick | 1978-10-09 04:30 | 10.9 | 2.6 | 170 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-09 05:30 | 10.5 | 2.7 | 175 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-09 06:30 | 9.7 | 3 | 175 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-09 07:30 | 9.7 | 3 | 160 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-09 08:30 | 10.1 | 2.2 | 145 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-09 09:30 | 10.4 | 2.2 | 125 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-09 10:30 | 10.5 | 3.3 | 82.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-09 11:30 | 10 | 3.6 | 40 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-10-09 12:30 | 9.1 | 2.9 | 25 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-10-09 13:30 | 9.1 | 2.3 | 25 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-09 14:30 | 9.4 | 2.1 | 185 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-09 15:30 | 9.5 | 2.4 | 315 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-09 16:30 | 9.1 | 2.4 | 277.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-09 17:30 | 8.4 | 1.8 | 277.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-09 18:30 | 7.8 | 1.5 | 280 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-09 19:30 | 7.1 | 1.5 | 262.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-09 20:30 | 6.9 | 1.6 | 240 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-09 21:30 | 7 | 2.2 | 225 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-09 22:30 | 6.7 | 3.1 | 217.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-09 23:30 | 6.7 | 3.7 | 215 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-10-10 00:30 | 7.2 | 3.9 | 217.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-10-10 01:30 | 7.4 | 4.2 | 217.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-10-10 02:30 | 7.5 | 4.9 | 215 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-10-10 03:30 | 7.5 | 5.4 | 220 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-10-10 04:30 | 7.6 | 5.1 | 227.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-10-10 05:30 | 7.5 | 4.7 | 232.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-10-10 06:30 | 7.5 | 4.4 | 235 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-10-10 07:30 | 7.8 | 4.4 | 230 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-10-10 08:30 | 8.1 | 4.9 | 220 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-10-10 09:30 | 8.6 | 5.8 | 212.5 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-10-10 10:30 | 9 | 6.4 | 212.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-10-10 11:30 | 9.3 | 6.7 | 220 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-10-10 12:30 | 9.7 | 6.8 | 225 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-10-10 13:30 | 10 | 7.1 | 220 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-10-10 14:30 | 10 | 7.1 | 212.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-10-10 15:30 | 9.9 | 6.4 | 212.5 | 220 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-10-10 16:30 | 9.8 | 4.9 | 217.5 | 80 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-10-10 17:30 | 9.3 | 3.1 | 212.5 | 0 | 40 | 0 | 280 |  | 134.4 |  | 40
Lerwick | 1978-10-10 18:30 | 8.4 | 1.8 | 200 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-10 19:30 | 7.7 | 1.5 | 192.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-10 20:30 | 8 | 1.8 | 177.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-10 21:30 | 8.4 | 3 | 157.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-10 22:30 | 8.1 | 3.9 | 150 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-10-10 23:30 | 8.1 | 4.2 | 147.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-10-11 00:30 | 8.3 | 4.7 | 137.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-10-11 01:30 | 8.4 | 5 | 122.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-10-11 02:30 | 8.8 | 5 | 107.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-10-11 03:30 | 9 | 5.2 | 95 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-10-11 04:30 | 9 | 5.8 | 92.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-10-11 05:30 | 9.2 | 6.7 | 100 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-10-11 06:30 | 9.6 | 7.8 | 110 | 500 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-10-11 07:30 | 9.9 | 8.9 | 120 | 770 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-10-11 08:30 | 10.2 | 8.9 | 132.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-10-11 09:30 | 10.5 | 8 | 145 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-11 10:30 | 10.5 | 7.8 | 152.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-11 11:30 | 10.5 | 8.4 | 160 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-11 12:30 | 10.5 | 8.4 | 167.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-10-11 13:30 | 10.5 | 8.4 | 170 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-10-11 14:30 | 10.2 | 9 | 172.5 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-11 15:30 | 10 | 8.9 | 175 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-10-11 16:30 | 10 | 8.5 | 175 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-10-11 17:30 | 10.2 | 9.1 | 177.5 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-10-11 18:30 | 10.7 | 9.4 | 180 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-10-11 19:30 | 11.4 | 8.3 | 180 | 635 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-11 20:30 | 11.8 | 7.3 | 177.5 | 400 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-11 21:30 | 11.7 | 6.4 | 175 | 220 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-10-11 22:30 | 11.3 | 5.8 | 175 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-10-11 23:30 | 11 | 5.1 | 175 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-10-12 00:30 | 11 | 4 | 172.5 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-10-12 01:30 | 11.1 | 4 | 167.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-10-12 02:30 | 11.1 | 4.4 | 167.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-10-12 03:30 | 11 | 4.2 | 170 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-10-12 04:30 | 10.9 | 3.9 | 170 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-10-12 05:30 | 10.4 | 4.1 | 167.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-10-12 06:30 | 10 | 4.4 | 162.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-10-12 07:30 | 10.2 | 4.6 | 160 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-10-12 08:30 | 10.4 | 5.8 | 165 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-10-12 09:30 | 10.4 | 8.3 | 187.5 | 635 | 392.5 | 72.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-12 10:30 | 10.5 | 11.2 | 217.5 | 1340 | 987.5 | 667.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-12 11:30 | 11.2 | 13 | 230 | 1480 | 1410 | 1090 | 0 |  | 0 |  | 320
Lerwick | 1978-10-12 12:30 | 12.5 | 14.1 | 230 | 1500 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-10-12 13:30 | 12.7 | 14.5 | 230 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-12 14:30 | 12 | 13.9 | 232.5 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-10-12 15:30 | 11.3 | 13.5 | 235 | 1490 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-10-12 16:30 | 10.9 | 13.6 | 237.5 | 1490 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-10-12 17:30 | 10.3 | 12.7 | 245 | 1470 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-10-12 18:30 | 9.9 | 10.6 | 247.5 | 1270 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-10-12 19:30 | 10 | 8.7 | 242.5 | 770 | 1020 | 700 | 0 |  | 0 |  | 320
Lerwick | 1978-10-12 20:30 | 10 | 7.6 | 240 | 500 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-10-12 21:30 | 9.7 | 6.8 | 240 | 300 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-10-12 22:30 | 9.7 | 6.3 | 240 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-10-12 23:30 | 9.6 | 5.9 | 240 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-10-13 00:30 | 9 | 5.1 | 240 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-10-13 01:30 | 8.6 | 4.2 | 235 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-10-13 02:30 | 8.3 | 3.7 | 225 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-10-13 03:30 | 8 | 3.4 | 222.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-10-13 04:30 | 7.9 | 3.3 | 222.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-13 05:30 | 7.3 | 3.3 | 212.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-13 06:30 | 6.5 | 3 | 200 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-13 07:30 | 6.8 | 2.7 | 192.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-13 08:30 | 7.9 | 3 | 187.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-13 09:30 | 8.7 | 3.4 | 182.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-13 10:30 | 9.7 | 4 | 177.5 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-10-13 11:30 | 10.7 | 4.7 | 172.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-10-13 12:30 | 10.8 | 5 | 170 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-10-13 13:30 | 10.8 | 4.7 | 167.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-10-13 14:30 | 10.5 | 4.2 | 162.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-10-13 15:30 | 10.5 | 4 | 162.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-10-13 16:30 | 10.2 | 4.2 | 167.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-10-13 17:30 | 9.5 | 4.9 | 170 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-10-13 18:30 | 9.5 | 5.2 | 172.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-10-13 19:30 | 9.5 | 4.7 | 180 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-10-13 20:30 | 9.5 | 4.4 | 187.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-10-13 21:30 | 9.5 | 4.2 | 195 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-10-13 22:30 | 9.5 | 3.8 | 210 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-10-13 23:30 | 9.4 | 3.4 | 230 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-10-14 00:30 | 8.8 | 3.6 | 250 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-10-14 01:30 | 8.2 | 3.9 | 267.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-10-14 02:30 | 8.2 | 4 | 275 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-10-14 03:30 | 8.1 | 3.8 | 270 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-10-14 04:30 | 8.2 | 3.1 | 262.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-10-14 05:30 | 8.3 | 2.6 | 255 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-14 06:30 | 8 | 2.6 | 247.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-14 07:30 | 8.4 | 2.8 | 260 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-14 08:30 | 8.6 | 4 | 302.5 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-10-14 09:30 | 9 | 5.8 | 167.5 | 150 | 105 | 0 | 215 |  | 103.2 |  | 105
Lerwick | 1978-10-14 10:30 | 9.4 | 6.5 | 7.5 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-10-14 11:30 | 9.3 | 6.1 | 12.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-10-14 12:30 | 9.2 | 5.8 | 17.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-10-14 13:30 | 9.2 | 5.7 | 20 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-10-14 14:30 | 9.4 | 5.7 | 20 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-10-14 15:30 | 9.3 | 5.5 | 20 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-10-14 16:30 | 8.7 | 5.2 | 20 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-10-14 17:30 | 8.2 | 5.2 | 22.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-10-14 18:30 | 8 | 5.5 | 27.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-10-14 19:30 | 8 | 5.5 | 30 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-10-14 20:30 | 8 | 4.9 | 30 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-10-14 21:30 | 8 | 4.4 | 32.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-10-14 22:30 | 7.9 | 4.6 | 37.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-10-14 23:30 | 7.9 | 4.9 | 40 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-10-15 00:30 | 7.8 | 4.7 | 42.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-10-15 01:30 | 7.7 | 4.5 | 50 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-10-15 02:30 | 7.7 | 4.4 | 55 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-10-15 03:30 | 7.5 | 4.4 | 55 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-10-15 04:30 | 7.3 | 4.5 | 55 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-10-15 05:30 | 7.3 | 4.2 | 52.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-10-15 06:30 | 7.4 | 4 | 55 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-10-15 07:30 | 7.3 | 4 | 65 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-10-15 08:30 | 7.3 | 4 | 65 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-10-15 09:30 | 7.4 | 4 | 60 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-10-15 10:30 | 7.6 | 3.9 | 70 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-10-15 11:30 | 7.8 | 3.9 | 85 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-10-15 12:30 | 7.7 | 3.9 | 90 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-10-15 13:30 | 7.7 | 3.8 | 92.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-10-15 14:30 | 7.7 | 3.1 | 97.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-10-15 15:30 | 7.5 | 2.2 | 107.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-15 16:30 | 7.7 | 1.8 | 140 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-15 17:30 | 7.4 | 2.2 | 180 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-15 18:30 | 6.5 | 2.4 | 187.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-15 19:30 | 6 | 1.5 | 162.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-15 20:30 | 5.7 | 1.1 | 147.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-15 21:30 | 5.7 | 1.9 | 162.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-15 22:30 | 6.4 | 3.1 | 165 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-15 23:30 | 6.8 | 4.9 | 180 | 80 | 40 | 0 | 280 |  | 134.4 |  | 40
Lerwick | 1978-10-16 00:30 | 7.1 | 7.5 | 237.5 | 500 | 290 | 0 | 30 |  | 14.4 |  | 290
Lerwick | 1978-10-16 01:30 | 7.1 | 8.4 | 267.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-16 02:30 | 6.9 | 7.3 | 262.5 | 400 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-16 03:30 | 7 | 6.2 | 255 | 220 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-10-16 04:30 | 6.9 | 5.3 | 237.5 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-10-16 05:30 | 6.8 | 5 | 215 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-10-16 06:30 | 6.7 | 5.2 | 207.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-10-16 07:30 | 6.7 | 5.4 | 217.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-10-16 08:30 | 6.6 | 5.1 | 237.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-10-16 09:30 | 7.1 | 5.3 | 262.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-10-16 10:30 | 7.7 | 6.7 | 280 | 300 | 205 | 0 | 115 |  | 55.2 |  | 205
Lerwick | 1978-10-16 11:30 | 8.1 | 8.5 | 290 | 770 | 535 | 215 | 0 |  | 0 |  | 320
Lerwick | 1978-10-16 12:30 | 8.4 | 9.5 | 297.5 | 1025 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-16 13:30 | 8.1 | 9.5 | 300 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-10-16 14:30 | 7.4 | 8.6 | 300 | 770 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-16 15:30 | 7.2 | 7.5 | 297.5 | 500 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-10-16 16:30 | 7.3 | 6.8 | 292.5 | 300 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-10-16 17:30 | 6.9 | 6.5 | 290 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-10-16 18:30 | 6.6 | 6.1 | 287.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-10-16 19:30 | 6.2 | 5.6 | 282.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-10-16 20:30 | 5.9 | 5.1 | 280 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-10-16 21:30 | 5.8 | 4.6 | 277.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-10-16 22:30 | 5.3 | 4.1 | 277.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-10-16 23:30 | 5.1 | 3.5 | 287.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-10-17 00:30 | 5 | 3.3 | 300 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-10-17 01:30 | 4.6 | 4.2 | 315 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-10-17 02:30 | 4.6 | 5.3 | 330 | 110 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-10-17 03:30 | 4.1 | 6 | 335 | 220 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-10-17 04:30 | 3.9 | 6.7 | 335 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-10-17 05:30 | 4.3 | 6.8 | 332.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-10-17 06:30 | 4.6 | 6.7 | 330 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-10-17 07:30 | 5.1 | 7.2 | 330 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-10-17 08:30 | 5.6 | 7.9 | 330 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-10-17 09:30 | 6.2 | 8.1 | 330 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-17 10:30 | 6.8 | 8.1 | 327.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-10-17 11:30 | 7 | 8.1 | 322.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-10-17 12:30 | 7.2 | 8 | 320 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-10-17 13:30 | 7.7 | 7.7 | 317.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-17 14:30 | 6.9 | 6.8 | 310 | 300 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-10-17 15:30 | 6.1 | 5.8 | 300 | 150 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-10-17 16:30 | 5.9 | 5.2 | 292.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-10-17 17:30 | 5.4 | 5 | 287.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-10-17 18:30 | 5.1 | 5.4 | 280 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-10-17 19:30 | 5.4 | 5.8 | 265 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-10-17 20:30 | 6 | 6.2 | 247.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-10-17 21:30 | 6.6 | 7.7 | 240 | 500 | 360 | 40 | 0 |  | 0 |  | 320
Lerwick | 1978-10-17 22:30 | 7.3 | 9.3 | 240 | 900 | 700 | 380 | 0 |  | 0 |  | 320
Lerwick | 1978-10-17 23:30 | 7.8 | 9.8 | 240 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-18 00:30 | 7.8 | 10.1 | 242.5 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-18 01:30 | 7.9 | 11.5 | 247.5 | 1400 | 1275 | 955 | 0 |  | 0 |  | 320
Lerwick | 1978-10-18 02:30 | 8.4 | 12.5 | 250 | 1470 | 1435 | 1115 | 0 |  | 0 |  | 320
Lerwick | 1978-10-18 03:30 | 8.7 | 12.5 | 252.5 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-10-18 04:30 | 8.7 | 12.9 | 260 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-10-18 05:30 | 8.8 | 13.1 | 267.5 | 1480 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-10-18 06:30 | 8.9 | 12.9 | 267.5 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-10-18 07:30 | 8.9 | 13 | 262.5 | 1480 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-10-18 08:30 | 9.2 | 13.3 | 262.5 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-10-18 09:30 | 9.4 | 13.9 | 270 | 1490 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-10-18 10:30 | 9.5 | 14.2 | 275 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-10-18 11:30 | 9.8 | 14.3 | 272.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-18 12:30 | 10.1 | 14 | 272.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-18 13:30 | 10.3 | 13.2 | 275 | 1480 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-10-18 14:30 | 10.3 | 12.6 | 272.5 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-10-18 15:30 | 10.2 | 11.9 | 270 | 1400 | 1435 | 1115 | 0 |  | 0 |  | 320
Lerwick | 1978-10-18 16:30 | 10 | 11.4 | 270 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-10-18 17:30 | 10 | 11.1 | 270 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-10-18 18:30 | 10 | 10.6 | 267.5 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-10-18 19:30 | 10 | 9.8 | 262.5 | 1025 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-18 20:30 | 10 | 8.9 | 260 | 770 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-18 21:30 | 10 | 8.5 | 260 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-10-18 22:30 | 9.9 | 8.5 | 257.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-10-18 23:30 | 9.7 | 8.2 | 252.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-19 00:30 | 9.3 | 7.8 | 250 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-19 01:30 | 9.3 | 7.8 | 245 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-19 02:30 | 9.4 | 8.4 | 237.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-19 03:30 | 9.4 | 8.8 | 232.5 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-19 04:30 | 9 | 9 | 227.5 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-10-19 05:30 | 8.8 | 10 | 227.5 | 1150 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-10-19 06:30 | 9.2 | 10.8 | 230 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-10-19 07:30 | 9.3 | 10.8 | 230 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-10-19 08:30 | 9.4 | 11.1 | 227.5 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-10-19 09:30 | 9.5 | 12 | 222.5 | 1450 | 1395 | 1075 | 0 |  | 0 |  | 320
Lerwick | 1978-10-19 10:30 | 9.7 | 12.8 | 220 | 1470 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-10-19 11:30 | 9.9 | 13.6 | 220 | 1490 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-10-19 12:30 | 10 | 14.8 | 220 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-10-19 13:30 | 9.7 | 15.1 | 220 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-19 14:30 | 9.4 | 14.9 | 220 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-19 15:30 | 9.7 | 15.4 | 220 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-19 16:30 | 10 | 16.5 | 220 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-19 17:30 | 10.1 | 17.2 | 222.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-19 18:30 | 10.3 | 17 | 230 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-19 19:30 | 10.4 | 15.4 | 242.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-19 20:30 | 9.6 | 13.7 | 255 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-10-19 21:30 | 8.9 | 13.6 | 260 | 1490 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-10-19 22:30 | 8.8 | 14.8 | 260 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-10-19 23:30 | 8.3 | 15.8 | 260 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-20 00:30 | 8 | 16.6 | 260 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-20 01:30 | 7.7 | 17 | 262.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-20 02:30 | 7.4 | 16.6 | 265 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-20 03:30 | 7 | 15.7 | 265 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-20 04:30 | 6.9 | 13.8 | 275 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-10-20 05:30 | 6.4 | 11.5 | 297.5 | 1400 | 1445 | 1125 | 0 |  | 0 |  | 320
Lerwick | 1978-10-20 06:30 | 5.3 | 10.4 | 312.5 | 1150 | 1275 | 955 | 0 |  | 0 |  | 320
Lerwick | 1978-10-20 07:30 | 4.7 | 10 | 310 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-10-20 08:30 | 4.6 | 9.9 | 305 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-20 09:30 | 4.6 | 10.1 | 307.5 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-20 10:30 | 4.1 | 10 | 310 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-10-20 11:30 | 4.2 | 9.8 | 310 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-20 12:30 | 4.8 | 9.9 | 310 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-10-20 13:30 | 4.4 | 10 | 312.5 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-20 14:30 | 4.1 | 9.9 | 315 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-20 15:30 | 4 | 9.4 | 312.5 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-20 16:30 | 3.2 | 9 | 312.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-10-20 17:30 | 3 | 8.9 | 315 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-10-20 18:30 | 3.4 | 8 | 315 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-20 19:30 | 3.1 | 6.4 | 320 | 220 | 427.5 | 107.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-20 20:30 | 2.8 | 5.5 | 325 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-10-20 21:30 | 2.7 | 5.5 | 320 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-10-20 22:30 | 3.1 | 5.3 | 312.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-10-20 23:30 | 3.3 | 4.9 | 307.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-10-21 00:30 | 3 | 4.9 | 300 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-10-21 01:30 | 3.1 | 4.9 | 290 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-10-21 02:30 | 3.2 | 4.9 | 285 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-10-21 03:30 | 3.4 | 4.9 | 287.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-10-21 04:30 | 3.6 | 4.4 | 287.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-10-21 05:30 | 3.7 | 3.5 | 285 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-10-21 06:30 | 3.6 | 2.8 | 285 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-10-21 07:30 | 3.7 | 2.3 | 280 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-21 08:30 | 3.8 | 1.9 | 270 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-21 09:30 | 4.2 | 2.2 | 255 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-21 10:30 | 4.6 | 2.9 | 240 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-21 11:30 | 4.7 | 3.4 | 230 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-21 12:30 | 4.5 | 3.4 | 210 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-21 13:30 | 4.3 | 3.3 | 182.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-21 14:30 | 4.4 | 4.1 | 165 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-10-21 15:30 | 4.6 | 5.9 | 157.5 | 150 | 105 | 0 | 215 |  | 103.2 |  | 105
Lerwick | 1978-10-21 16:30 | 4.9 | 7.5 | 155 | 500 | 325 | 5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-21 17:30 | 5.4 | 8.2 | 155 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-21 18:30 | 5.6 | 8.9 | 155 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-21 19:30 | 5.8 | 9.3 | 157.5 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-10-21 20:30 | 6.2 | 8.7 | 162.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-10-21 21:30 | 6.1 | 8.3 | 192.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-21 22:30 | 6.9 | 9 | 247.5 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-21 23:30 | 8.3 | 9.5 | 277.5 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-22 00:30 | 8.1 | 9.9 | 280 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-10-22 01:30 | 7.7 | 10.5 | 280 | 1270 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-22 02:30 | 7.9 | 10.5 | 282.5 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-10-22 03:30 | 7.6 | 10.1 | 287.5 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-10-22 04:30 | 7.6 | 10 | 290 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-10-22 05:30 | 7.2 | 10 | 287.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-10-22 06:30 | 6.9 | 9.9 | 282.5 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-22 07:30 | 6.7 | 9.8 | 282.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-10-22 08:30 | 6.7 | 9.8 | 287.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-10-22 09:30 | 6.9 | 9.8 | 287.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-10-22 10:30 | 7.2 | 9.9 | 285 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-10-22 11:30 | 7.8 | 10 | 287.5 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-22 12:30 | 7.7 | 10.1 | 287.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-10-22 13:30 | 7.7 | 10.3 | 282.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-10-22 14:30 | 7.9 | 9.8 | 282.5 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-22 15:30 | 8 | 8.7 | 285 | 770 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-22 16:30 | 7.3 | 7.9 | 282.5 | 500 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-10-22 17:30 | 6.9 | 7.7 | 280 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-22 18:30 | 7.1 | 7.6 | 277.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-22 19:30 | 7.1 | 7.5 | 272.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-22 20:30 | 7.1 | 7.8 | 267.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-22 21:30 | 7.1 | 8.1 | 260 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-22 22:30 | 7.3 | 7.9 | 250 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-22 23:30 | 7.4 | 8.2 | 240 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-23 00:30 | 7.9 | 9.4 | 232.5 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-23 01:30 | 8.6 | 10.6 | 230 | 1270 | 1085 | 765 | 0 |  | 0 |  | 320
Lerwick | 1978-10-23 02:30 | 8.8 | 11.8 | 230 | 1400 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-10-23 03:30 | 9.1 | 12.4 | 230 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-10-23 04:30 | 9.5 | 12.8 | 230 | 1470 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-10-23 05:30 | 9.7 | 13 | 230 | 1480 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-10-23 06:30 | 9.9 | 12.2 | 230 | 1450 | 1465 | 1145 | 0 |  | 0 |  | 320
Lerwick | 1978-10-23 07:30 | 10 | 11.2 | 230 | 1340 | 1395 | 1075 | 0 |  | 0 |  | 320
Lerwick | 1978-10-23 08:30 | 10 | 11.2 | 230 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-10-23 09:30 | 10.1 | 11.5 | 230 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-10-23 10:30 | 10.3 | 11.4 | 230 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-10-23 11:30 | 10.2 | 11.5 | 227.5 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-10-23 12:30 | 9.6 | 11.5 | 225 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-10-23 13:30 | 9.3 | 10.8 | 230 | 1270 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-10-23 14:30 | 9.5 | 10.4 | 237.5 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-10-23 15:30 | 9.3 | 10.7 | 235 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-10-23 16:30 | 8.8 | 11.2 | 230 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-10-23 17:30 | 8.8 | 11.5 | 237.5 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-10-23 18:30 | 9.1 | 11.4 | 247.5 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-10-23 19:30 | 9.1 | 11.4 | 247.5 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-10-23 20:30 | 8.7 | 11.7 | 242.5 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-10-23 21:30 | 8.6 | 12 | 242.5 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-10-23 22:30 | 8.2 | 12 | 247.5 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-10-23 23:30 | 7.8 | 11.9 | 250 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-10-24 00:30 | 7.7 | 11.1 | 252.5 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-10-24 01:30 | 6.8 | 11 | 255 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-10-24 02:30 | 6.1 | 12.7 | 252.5 | 1470 | 1405 | 1085 | 0 |  | 0 |  | 320
Lerwick | 1978-10-24 03:30 | 5.8 | 14.1 | 250 | 1500 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-10-24 04:30 | 5.6 | 14.1 | 252.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-24 05:30 | 6.2 | 14.4 | 255 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-24 06:30 | 6.3 | 15.7 | 252.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-24 07:30 | 6.3 | 16.3 | 250 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-24 08:30 | 7.1 | 16.1 | 252.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-24 09:30 | 7.3 | 15.8 | 257.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-24 10:30 | 7.3 | 15.8 | 260 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-24 11:30 | 7.4 | 16.2 | 257.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-24 12:30 | 6.6 | 16.7 | 255 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-24 13:30 | 6.7 | 17.9 | 257.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-24 14:30 | 8 | 19.3 | 262.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-24 15:30 | 8.1 | 19 | 267.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-24 16:30 | 6.2 | 17.6 | 270 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-24 17:30 | 5.8 | 16.7 | 270 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-24 18:30 | 7.2 | 15.9 | 270 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-24 19:30 | 7.2 | 14.6 | 272.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-24 20:30 | 6.8 | 13.4 | 277.5 | 1480 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-10-24 21:30 | 6.9 | 12.9 | 280 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-10-24 22:30 | 6.9 | 12.9 | 280 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-10-24 23:30 | 6.8 | 13 | 280 | 1480 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-10-25 00:30 | 6.9 | 13.2 | 280 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-10-25 01:30 | 6.6 | 12.9 | 282.5 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-10-25 02:30 | 6.6 | 12 | 287.5 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-10-25 03:30 | 6.6 | 11.2 | 290 | 1340 | 1395 | 1075 | 0 |  | 0 |  | 320
Lerwick | 1978-10-25 04:30 | 6.5 | 10.6 | 290 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-10-25 05:30 | 6.2 | 10 | 290 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-10-25 06:30 | 5.5 | 9.6 | 290 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-25 07:30 | 5.4 | 9 | 292.5 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-25 08:30 | 5.4 | 8.1 | 295 | 635 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-25 09:30 | 5.5 | 8.2 | 292.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-10-25 10:30 | 6.3 | 9 | 290 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-25 11:30 | 6.6 | 8.5 | 290 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-10-25 12:30 | 6.5 | 7.2 | 290 | 400 | 585 | 265 | 0 |  | 0 |  | 320
Lerwick | 1978-10-25 13:30 | 6.6 | 6.7 | 290 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-10-25 14:30 | 6.7 | 6.4 | 292.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-10-25 15:30 | 6.7 | 5.6 | 300 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-10-25 16:30 | 6.5 | 4.4 | 307.5 | 60 | 105 | 0 | 215 |  | 103.2 |  | 105
Lerwick | 1978-10-25 17:30 | 6.2 | 3.3 | 305 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-10-25 18:30 | 5.8 | 2.4 | 295 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-25 19:30 | 5.8 | 2.2 | 290 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-25 20:30 | 5.7 | 2.4 | 290 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-25 21:30 | 5.5 | 2.6 | 290 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-25 22:30 | 5.5 | 2.6 | 290 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-25 23:30 | 5.2 | 2.6 | 290 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-26 00:30 | 5 | 2.7 | 292.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-26 01:30 | 4.9 | 2.4 | 297.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-26 02:30 | 4.3 | 2 | 295 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-26 03:30 | 4.7 | 1.5 | 270 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-26 04:30 | 5.2 | 1.1 | 230 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-26 05:30 | 4.1 | 1.2 | 202.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-26 06:30 | 3.2 | 1.6 | 192.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-26 07:30 | 3.1 | 1.9 | 190 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-26 08:30 | 4.2 | 3 | 187.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-26 09:30 | 5.7 | 5.1 | 182.5 | 110 | 55 | 0 | 265 |  | 127.2 |  | 55
Lerwick | 1978-10-26 10:30 | 6.9 | 7.4 | 180 | 400 | 255 | 0 | 65 |  | 31.2 |  | 255
Lerwick | 1978-10-26 11:30 | 7.9 | 8.9 | 180 | 770 | 585 | 265 | 0 |  | 0 |  | 320
Lerwick | 1978-10-26 12:30 | 8.1 | 9 | 182.5 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-10-26 13:30 | 8.1 | 8.8 | 195 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-10-26 14:30 | 8.4 | 9.1 | 217.5 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-10-26 15:30 | 9.3 | 9.7 | 237.5 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-26 16:30 | 9.9 | 10.4 | 247.5 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-26 17:30 | 10 | 10.9 | 250 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-10-26 18:30 | 10 | 10.7 | 252.5 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-10-26 19:30 | 10 | 10.4 | 255 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-10-26 20:30 | 9.9 | 10 | 255 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-10-26 21:30 | 9.9 | 9.4 | 250 | 900 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-10-26 22:30 | 10 | 9 | 240 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-10-26 23:30 | 10.1 | 9.4 | 237.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-10-27 00:30 | 10.2 | 10 | 240 | 1150 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-10-27 01:30 | 10.3 | 10.6 | 237.5 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-10-27 02:30 | 10.2 | 11.4 | 232.5 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-10-27 03:30 | 10.2 | 12.1 | 230 | 1450 | 1395 | 1075 | 0 |  | 0 |  | 320
Lerwick | 1978-10-27 04:30 | 10.4 | 13 | 230 | 1480 | 1465 | 1145 | 0 |  | 0 |  | 320
Lerwick | 1978-10-27 05:30 | 10.4 | 14 | 230 | 1500 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-10-27 06:30 | 10.5 | 14.6 | 230 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-27 07:30 | 10.6 | 14.9 | 230 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-27 08:30 | 10.8 | 14.8 | 230 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-27 09:30 | 10.6 | 14.5 | 230 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-27 10:30 | 10.5 | 14.1 | 230 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-27 11:30 | 10.7 | 13.4 | 230 | 1480 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-10-27 12:30 | 10.9 | 12.7 | 232.5 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-10-27 13:30 | 10.9 | 12.8 | 237.5 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-10-27 14:30 | 10.9 | 13.5 | 237.5 | 1490 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-10-27 15:30 | 10.9 | 14.1 | 232.5 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-10-27 16:30 | 10.9 | 14.5 | 230 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-27 17:30 | 10.9 | 14.5 | 232.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-27 18:30 | 10.9 | 14.5 | 237.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-27 19:30 | 11 | 15 | 240 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-27 20:30 | 11 | 15.1 | 242.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-27 21:30 | 10.9 | 14.5 | 247.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-27 22:30 | 10.8 | 13.5 | 250 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-10-27 23:30 | 10.6 | 11.9 | 252.5 | 1400 | 1445 | 1125 | 0 |  | 0 |  | 320
Lerwick | 1978-10-28 00:30 | 10.4 | 10.6 | 260 | 1270 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-10-28 01:30 | 10.3 | 9.9 | 270 | 1025 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-28 02:30 | 10.1 | 8.8 | 275 | 770 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-28 03:30 | 9.8 | 7.5 | 272.5 | 500 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-10-28 04:30 | 9.3 | 6 | 270 | 220 | 360 | 40 | 0 |  | 0 |  | 320
Lerwick | 1978-10-28 05:30 | 9 | 4.5 | 275 | 80 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-10-28 06:30 | 8.9 | 3.9 | 277.5 | 25 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-10-28 07:30 | 8.5 | 3.9 | 265 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-10-28 08:30 | 8.1 | 3.9 | 252.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-10-28 09:30 | 8.4 | 4.1 | 247.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-10-28 10:30 | 8.9 | 4.7 | 242.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-10-28 11:30 | 9.1 | 5.2 | 240 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-10-28 12:30 | 9.3 | 5.8 | 237.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-10-28 13:30 | 9.8 | 6.6 | 235 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-10-28 14:30 | 10.1 | 7.3 | 237.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-10-28 15:30 | 10.2 | 8.5 | 240 | 770 | 585 | 265 | 0 |  | 0 |  | 320
Lerwick | 1978-10-28 16:30 | 10.1 | 9.8 | 240 | 1025 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-28 17:30 | 10.2 | 10.6 | 240 | 1270 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-28 18:30 | 10.3 | 11.7 | 240 | 1400 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-10-28 19:30 | 10.3 | 12.9 | 242.5 | 1470 | 1435 | 1115 | 0 |  | 0 |  | 320
Lerwick | 1978-10-28 20:30 | 10.3 | 13.6 | 247.5 | 1490 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-10-28 21:30 | 10.4 | 14 | 250 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-10-28 22:30 | 10.5 | 13.9 | 250 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-10-28 23:30 | 10.3 | 13 | 250 | 1480 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-10-29 00:30 | 10.1 | 11.9 | 250 | 1400 | 1440 | 1120 | 0 |  | 0 |  | 320
Lerwick | 1978-10-29 01:30 | 10.2 | 10.9 | 250 | 1270 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-10-29 02:30 | 10.2 | 10.1 | 250 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-10-29 03:30 | 10.1 | 9.8 | 247.5 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-29 04:30 | 10.1 | 9.6 | 242.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-10-29 05:30 | 10.1 | 8.7 | 240 | 770 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-29 06:30 | 10.2 | 7.6 | 237.5 | 500 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-10-29 07:30 | 10.2 | 7.6 | 232.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-29 08:30 | 10.1 | 8.2 | 230 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-29 09:30 | 10.3 | 8.6 | 230 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-29 10:30 | 10.6 | 9.1 | 227.5 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-10-29 11:30 | 10.8 | 9.6 | 222.5 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-29 12:30 | 10.6 | 10 | 220 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-29 13:30 | 10.5 | 10.8 | 222.5 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-10-29 14:30 | 10.5 | 11.3 | 227.5 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-10-29 15:30 | 10.6 | 11 | 230 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-10-29 16:30 | 10.8 | 10.6 | 230 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-10-29 17:30 | 10.7 | 10.1 | 230 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-10-29 18:30 | 10.5 | 9.8 | 230 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-29 19:30 | 10.5 | 10.1 | 230 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-29 20:30 | 10.6 | 10.5 | 230 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-10-29 21:30 | 10.7 | 10.5 | 232.5 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-10-29 22:30 | 10.7 | 11 | 237.5 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-10-29 23:30 | 10.5 | 11.5 | 240 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-10-30 00:30 | 10.5 | 10.6 | 237.5 | 1270 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-10-30 01:30 | 10.5 | 9.6 | 232.5 | 1025 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-30 02:30 | 10.5 | 9.7 | 230 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-10-30 03:30 | 10.5 | 9.9 | 230 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-10-30 04:30 | 10.5 | 9.5 | 230 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-10-30 05:30 | 10.6 | 9 | 230 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-30 06:30 | 10.7 | 8.4 | 230 | 635 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-30 07:30 | 10.9 | 7.9 | 227.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-30 08:30 | 10.9 | 7.8 | 222.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-30 09:30 | 10.9 | 8 | 217.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-30 10:30 | 11.5 | 8 | 212.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-10-30 11:30 | 12 | 8.1 | 210 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-10-30 12:30 | 11.8 | 7.9 | 210 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-30 13:30 | 11.8 | 7.9 | 210 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-10-30 14:30 | 11.5 | 8.3 | 210 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-30 15:30 | 11 | 8.9 | 210 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-30 16:30 | 11.2 | 9.9 | 212.5 | 1025 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-30 17:30 | 11.2 | 10.4 | 217.5 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-30 18:30 | 11.2 | 9.8 | 220 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-30 19:30 | 11.3 | 8.7 | 220 | 770 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-30 20:30 | 11.3 | 7.8 | 220 | 500 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-10-30 21:30 | 11.3 | 7.1 | 220 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-10-30 22:30 | 11.1 | 6 | 217.5 | 220 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-10-30 23:30 | 10.9 | 4.7 | 212.5 | 80 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-10-31 00:30 | 10.8 | 3.5 | 205 | 25 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-10-31 01:30 | 10.6 | 2.9 | 190 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-10-31 02:30 | 10.3 | 3.1 | 175 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-10-31 03:30 | 10.1 | 4.9 | 175 | 80 | 40 | 0 | 280 |  | 134.4 |  | 40
Lerwick | 1978-10-31 04:30 | 10 | 7.3 | 192.5 | 400 | 240 | 0 | 80 |  | 38.4 |  | 240
Lerwick | 1978-10-31 05:30 | 10.5 | 8.2 | 232.5 | 635 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-31 06:30 | 10.4 | 6.8 | 280 | 300 | 467.5 | 147.5 | 0 |  | 0 |  | 320
Lerwick | 1978-10-31 07:30 | 8.6 | 5.1 | 292.5 | 110 | 205 | 0 | 115 |  | 55.2 |  | 205
Lerwick | 1978-10-31 08:30 | 7.5 | 4.7 | 272.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-10-31 09:30 | 7.6 | 5.4 | 252.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-10-31 10:30 | 7.8 | 6.5 | 242.5 | 300 | 205 | 0 | 115 |  | 55.2 |  | 205
Lerwick | 1978-10-31 11:30 | 8.3 | 7.4 | 237.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-10-31 12:30 | 9.2 | 7.6 | 232.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-10-31 13:30 | 9.9 | 7.3 | 230 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-10-31 14:30 | 9.8 | 7.1 | 230 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-10-31 15:30 | 9 | 6.8 | 230 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-10-31 16:30 | 8.4 | 6.7 | 232.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-10-31 17:30 | 8.4 | 6.5 | 235 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-10-31 18:30 | 7.7 | 6.7 | 235 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-10-31 19:30 | 7.3 | 7.9 | 235 | 500 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-10-31 20:30 | 7.6 | 9.3 | 232.5 | 900 | 700 | 380 | 0 |  | 0 |  | 320
Lerwick | 1978-10-31 21:30 | 7.7 | 10 | 230 | 1150 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-10-31 22:30 | 7.9 | 10.8 | 230 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-10-31 23:30 | 8.2 | 11.4 | 227.5 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-11-01 00:30 | 8.5 | 11.6 | 222.5 | 1400 | 1370 | 1050 | 0 |  | 0 | 17460 | 320 | 194025
Lerwick | 1978-11-01 01:30 | 8.7 | 12.1 | 220 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-11-01 02:30 | 8.8 | 12.2 | 222.5 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-11-01 03:30 | 8.7 | 11.7 | 225 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-11-01 04:30 | 8.7 | 11.2 | 222.5 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-11-01 05:30 | 8.9 | 10.1 | 215 | 1150 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-11-01 06:30 | 8.9 | 8.2 | 205 | 635 | 892.5 | 572.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-01 07:30 | 8.7 | 6.9 | 197.5 | 300 | 467.5 | 147.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-01 08:30 | 8.5 | 7.3 | 190 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-11-01 09:30 | 8.8 | 9.1 | 180 | 900 | 650 | 330 | 0 |  | 0 |  | 320
Lerwick | 1978-11-01 10:30 | 8.8 | 11.3 | 172.5 | 1340 | 1120 | 800 | 0 |  | 0 |  | 320
Lerwick | 1978-11-01 11:30 | 8.9 | 13 | 170 | 1480 | 1410 | 1090 | 0 |  | 0 |  | 320
Lerwick | 1978-11-01 12:30 | 9.4 | 14.1 | 170 | 1500 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-11-01 13:30 | 9.5 | 15 | 172.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-01 14:30 | 9.5 | 15.5 | 177.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-01 15:30 | 9.3 | 15.7 | 180 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-01 16:30 | 9.3 | 15.4 | 182.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-01 17:30 | 9.3 | 15.2 | 187.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-01 18:30 | 9.3 | 15.4 | 190 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-01 19:30 | 9.3 | 15.5 | 192.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-01 20:30 | 9.5 | 15.7 | 197.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-01 21:30 | 10 | 16.3 | 202.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-01 22:30 | 10.5 | 16.4 | 207.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-01 23:30 | 10.5 | 15.8 | 210 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-02 00:30 | 10.4 | 14.8 | 217.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-02 01:30 | 10.4 | 12.5 | 237.5 | 1470 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-11-02 02:30 | 9.5 | 9.4 | 257.5 | 900 | 1185 | 865 | 0 |  | 0 |  | 320
Lerwick | 1978-11-02 03:30 | 8.2 | 7.7 | 267.5 | 500 | 700 | 380 | 0 |  | 0 |  | 320
Lerwick | 1978-11-02 04:30 | 7.7 | 6.9 | 272.5 | 300 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-11-02 05:30 | 7.8 | 5.7 | 277.5 | 150 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-11-02 06:30 | 7.7 | 4.7 | 280 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-11-02 07:30 | 7.5 | 4.5 | 280 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-11-02 08:30 | 7.3 | 4.9 | 277.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-11-02 09:30 | 7.1 | 5.8 | 272.5 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-11-02 10:30 | 7.4 | 6 | 270 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-11-02 11:30 | 7.7 | 5.8 | 272.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-11-02 12:30 | 7.8 | 5.5 | 272.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-11-02 13:30 | 8.3 | 5.4 | 255 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-11-02 14:30 | 8.5 | 5.6 | 230 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-11-02 15:30 | 7.7 | 5.9 | 217.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-11-02 16:30 | 6.7 | 5.9 | 210 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-11-02 17:30 | 5.9 | 6.7 | 200 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-11-02 18:30 | 6 | 9 | 195 | 900 | 600 | 280 | 0 |  | 0 |  | 320
Lerwick | 1978-11-02 19:30 | 7.1 | 11.4 | 202.5 | 1340 | 1120 | 800 | 0 |  | 0 |  | 320
Lerwick | 1978-11-02 20:30 | 8 | 11.7 | 215 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-11-02 21:30 | 8.6 | 10.2 | 217.5 | 1150 | 1275 | 955 | 0 |  | 0 |  | 320
Lerwick | 1978-11-02 22:30 | 8.4 | 9.2 | 210 | 900 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-11-02 23:30 | 8.3 | 9.5 | 202.5 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-03 00:30 | 8.4 | 10.7 | 200 | 1270 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-03 01:30 | 8.5 | 11.4 | 197.5 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-11-03 02:30 | 8.5 | 11 | 192.5 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-11-03 03:30 | 8.5 | 10.9 | 190 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-11-03 04:30 | 8.7 | 11.1 | 192.5 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-11-03 05:30 | 8.8 | 11.1 | 200 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-11-03 06:30 | 8.6 | 9.9 | 225 | 1025 | 1182.5 | 862.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-03 07:30 | 7.7 | 6.9 | 275 | 300 | 662.5 | 342.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-03 08:30 | 6.2 | 5.6 | 295 | 150 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-11-03 09:30 | 5.3 | 8.2 | 257.5 | 635 | 392.5 | 72.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-03 10:30 | 6 | 11.3 | 220 | 1340 | 987.5 | 667.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-03 11:30 | 7.3 | 13.3 | 212.5 | 1480 | 1410 | 1090 | 0 |  | 0 |  | 320
Lerwick | 1978-11-03 12:30 | 8 | 15.1 | 225 | 1500 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-11-03 13:30 | 7.6 | 16.6 | 240 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-03 14:30 | 6.2 | 18 | 247.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-03 15:30 | 5.8 | 18.6 | 252.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-03 16:30 | 6.3 | 17.9 | 260 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-03 17:30 | 6.3 | 16.6 | 267.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-03 18:30 | 6.2 | 14.9 | 267.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-03 19:30 | 6.4 | 13.2 | 260 | 1480 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-11-03 20:30 | 6.8 | 12.5 | 250 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-11-03 21:30 | 7 | 12.5 | 242.5 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-11-03 22:30 | 7.2 | 12.8 | 240 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-11-03 23:30 | 7.6 | 13.2 | 237.5 | 1480 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-11-04 00:30 | 7.9 | 13.1 | 235 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-11-04 01:30 | 7.9 | 13 | 240 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-11-04 02:30 | 7.3 | 12.7 | 247.5 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-11-04 03:30 | 6.8 | 11.7 | 247.5 | 1400 | 1435 | 1115 | 0 |  | 0 |  | 320
Lerwick | 1978-11-04 04:30 | 6.6 | 10.7 | 242.5 | 1270 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-11-04 05:30 | 6.8 | 9.7 | 242.5 | 1025 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-04 06:30 | 7.3 | 7.8 | 252.5 | 500 | 762.5 | 442.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-04 07:30 | 7.3 | 5.6 | 262.5 | 150 | 325 | 5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-04 08:30 | 7.1 | 3.6 | 252.5 | 25 | 87.5 | 0 | 232.5 |  | 111.6 |  | 87.5
Lerwick | 1978-11-04 09:30 | 6.8 | 2.4 | 225 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-11-04 10:30 | 7.1 | 2.1 | 200 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-11-04 11:30 | 7.3 | 2.2 | 182.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-11-04 12:30 | 7.5 | 2.4 | 170 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-11-04 13:30 | 7.7 | 3.3 | 162.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-11-04 14:30 | 7.7 | 4.4 | 155 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-11-04 15:30 | 7 | 5.1 | 142.5 | 110 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-11-04 16:30 | 6.4 | 5.6 | 132.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-11-04 17:30 | 6.5 | 6.1 | 130 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-11-04 18:30 | 6.9 | 6.5 | 130 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-11-04 19:30 | 7.3 | 6.7 | 130 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-11-04 20:30 | 7.6 | 6.9 | 127.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-11-04 21:30 | 7.7 | 7.4 | 125 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-11-04 22:30 | 7.7 | 7.3 | 132.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-11-04 23:30 | 7.8 | 6.4 | 150 | 220 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-11-05 00:30 | 8.4 | 6.3 | 177.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-11-05 01:30 | 8.9 | 7.8 | 207.5 | 500 | 360 | 40 | 0 |  | 0 |  | 320
Lerwick | 1978-11-05 02:30 | 9.8 | 9.6 | 217.5 | 1025 | 762.5 | 442.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-05 03:30 | 10.6 | 10.1 | 210 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-05 04:30 | 10.6 | 10.6 | 205 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-11-05 05:30 | 10.7 | 12.8 | 207.5 | 1470 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-11-05 06:30 | 11.2 | 15.2 | 212.5 | 1500 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-11-05 07:30 | 11.5 | 16.1 | 220 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-05 08:30 | 11.6 | 16.4 | 225 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-05 09:30 | 11.7 | 16.7 | 225 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-05 10:30 | 11.6 | 16.8 | 227.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-05 11:30 | 11.8 | 17 | 227.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-05 12:30 | 12 | 16.6 | 222.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-05 13:30 | 11.7 | 15.9 | 222.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-05 14:30 | 11.6 | 15.4 | 227.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-05 15:30 | 11.6 | 15 | 230 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-05 16:30 | 11.5 | 14.5 | 230 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-05 17:30 | 11.5 | 13.5 | 230 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-11-05 18:30 | 11.4 | 12.3 | 230 | 1450 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-11-05 19:30 | 11.2 | 11.4 | 230 | 1340 | 1395 | 1075 | 0 |  | 0 |  | 320
Lerwick | 1978-11-05 20:30 | 11 | 10.9 | 230 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-11-05 21:30 | 11 | 10.8 | 230 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-11-05 22:30 | 10.9 | 10.6 | 230 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-11-05 23:30 | 10.9 | 10.4 | 232.5 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-11-06 00:30 | 10.9 | 10.1 | 237.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-11-06 01:30 | 10.6 | 9.7 | 237.5 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-06 02:30 | 10.7 | 9.4 | 232.5 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-06 03:30 | 11 | 9.3 | 227.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-11-06 04:30 | 11.4 | 8.9 | 222.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-11-06 05:30 | 11.9 | 7.7 | 220 | 500 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-11-06 06:30 | 12 | 6.4 | 215 | 220 | 360 | 40 | 0 |  | 0 |  | 320
Lerwick | 1978-11-06 07:30 | 11.6 | 5.9 | 205 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-11-06 08:30 | 10.4 | 6 | 200 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-11-06 09:30 | 9.5 | 6.2 | 200 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-11-06 10:30 | 9.8 | 6.3 | 197.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-11-06 11:30 | 10.3 | 6.5 | 192.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-11-06 12:30 | 10.3 | 6.5 | 187.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-11-06 13:30 | 10.4 | 6.3 | 182.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-11-06 14:30 | 10.6 | 5.9 | 182.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-11-06 15:30 | 10.2 | 5.7 | 185 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-11-06 16:30 | 10 | 5.9 | 185 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-11-06 17:30 | 9.5 | 5.6 | 187.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-11-06 18:30 | 9.2 | 4.9 | 192.5 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-11-06 19:30 | 9.2 | 5.4 | 197.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-11-06 20:30 | 9.3 | 6.5 | 200 | 300 | 205 | 0 | 115 |  | 55.2 |  | 205
Lerwick | 1978-11-06 21:30 | 9.9 | 8.2 | 197.5 | 635 | 467.5 | 147.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-06 22:30 | 10.1 | 9.8 | 192.5 | 1025 | 830 | 510 | 0 |  | 0 |  | 320
Lerwick | 1978-11-06 23:30 | 9.7 | 10.8 | 190 | 1270 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-07 00:30 | 9.4 | 11.8 | 190 | 1400 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-11-07 01:30 | 9.3 | 12.1 | 190 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-11-07 02:30 | 9.2 | 11.6 | 190 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-11-07 03:30 | 9 | 11.6 | 190 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-11-07 04:30 | 9 | 11.3 | 187.5 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-11-07 05:30 | 9.1 | 10.5 | 185 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-11-07 06:30 | 9.2 | 10.4 | 187.5 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-11-07 07:30 | 9.4 | 10.5 | 190 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-11-07 08:30 | 9.4 | 10.9 | 190 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-11-07 09:30 | 9.3 | 11.3 | 190 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-11-07 10:30 | 9.3 | 10.9 | 190 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-11-07 11:30 | 9.4 | 10.5 | 190 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-11-07 12:30 | 9.5 | 10.6 | 190 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-11-07 13:30 | 9.5 | 10.8 | 190 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-11-07 14:30 | 9.4 | 10.9 | 187.5 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-11-07 15:30 | 9.3 | 11.4 | 182.5 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-11-07 16:30 | 9.3 | 12.1 | 180 | 1450 | 1395 | 1075 | 0 |  | 0 |  | 320
Lerwick | 1978-11-07 17:30 | 9.3 | 12.8 | 180 | 1470 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-11-07 18:30 | 9.3 | 13.5 | 180 | 1490 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-11-07 19:30 | 9.4 | 14.1 | 180 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-11-07 20:30 | 9.6 | 14.4 | 180 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-07 21:30 | 9.7 | 14.4 | 180 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-07 22:30 | 9.8 | 14.1 | 180 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-07 23:30 | 9.8 | 13.6 | 180 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-11-08 00:30 | 9.8 | 13.4 | 180 | 1480 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-11-08 01:30 | 9.8 | 13.4 | 180 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-11-08 02:30 | 9.9 | 13.4 | 180 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-11-08 03:30 | 10 | 13.5 | 180 | 1490 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-11-08 04:30 | 10 | 14 | 182.5 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-11-08 05:30 | 10 | 14.8 | 190 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-08 06:30 | 10.3 | 15.4 | 207.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-08 07:30 | 10.7 | 15 | 237.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-08 08:30 | 9.7 | 13.4 | 260 | 1480 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-11-08 09:30 | 8 | 12.4 | 260 | 1450 | 1465 | 1145 | 0 |  | 0 |  | 320
Lerwick | 1978-11-08 10:30 | 7.9 | 12.4 | 250 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-11-08 11:30 | 8.5 | 12.8 | 242.5 | 1470 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-11-08 12:30 | 9 | 13.2 | 240 | 1480 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-11-08 13:30 | 9.2 | 13.4 | 237.5 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-11-08 14:30 | 8.9 | 13.4 | 230 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-11-08 15:30 | 8.7 | 13.9 | 222.5 | 1490 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-11-08 16:30 | 8.9 | 14.8 | 222.5 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-11-08 17:30 | 9.1 | 14.9 | 227.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-08 18:30 | 9.1 | 14.7 | 230 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-08 19:30 | 9 | 14.8 | 230 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-08 20:30 | 9.1 | 14.5 | 230 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-08 21:30 | 9.4 | 13.6 | 230 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-11-08 22:30 | 9.6 | 13.2 | 230 | 1480 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-11-08 23:30 | 9.6 | 13.5 | 230 | 1490 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-11-09 00:30 | 9.6 | 13.6 | 230 | 1490 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-11-09 01:30 | 9.7 | 13.9 | 230 | 1490 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-11-09 02:30 | 9.8 | 14.3 | 230 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-11-09 03:30 | 9.9 | 14.3 | 227.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-09 04:30 | 10 | 13.9 | 222.5 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-11-09 05:30 | 9.9 | 13.7 | 220 | 1490 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-11-09 06:30 | 9.9 | 14 | 217.5 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-11-09 07:30 | 10.1 | 14.5 | 215 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-09 08:30 | 10.1 | 15.4 | 217.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-09 09:30 | 10 | 16 | 220 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-09 10:30 | 10.1 | 16 | 222.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-09 11:30 | 10.4 | 15.6 | 225 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-09 12:30 | 10.5 | 14.5 | 222.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-09 13:30 | 10.5 | 14 | 220 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-09 14:30 | 10.5 | 14.7 | 220 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-09 15:30 | 10.7 | 15.6 | 220 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-09 16:30 | 11 | 16.2 | 220 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-09 17:30 | 11 | 16.6 | 220 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-09 18:30 | 11.1 | 17 | 220 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-09 19:30 | 11.3 | 17.4 | 220 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-09 20:30 | 11.3 | 17.4 | 220 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-09 21:30 | 11.3 | 17.1 | 220 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-09 22:30 | 11.1 | 17 | 220 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-09 23:30 | 10.8 | 16.7 | 220 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-10 00:30 | 10.8 | 15.8 | 220 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-10 01:30 | 10.5 | 15 | 222.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-10 02:30 | 10.2 | 13.2 | 245 | 1480 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-11-10 03:30 | 10.4 | 8.6 | 280 | 770 | 1125 | 805 | 0 |  | 0 |  | 320
Lerwick | 1978-11-10 04:30 | 9 | 4.5 | 292.5 | 80 | 425 | 105 | 0 |  | 0 |  | 320
Lerwick | 1978-11-10 05:30 | 7.3 | 3.6 | 290 | 25 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-11-10 06:30 | 7.1 | 4.2 | 295 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-11-10 07:30 | 7 | 4.2 | 302.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-11-10 08:30 | 6.8 | 4 | 302.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-11-10 09:30 | 6.3 | 4.2 | 297.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-11-10 10:30 | 6 | 4.9 | 290 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-11-10 11:30 | 6.4 | 5.6 | 282.5 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-11-10 12:30 | 6.9 | 6 | 280 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-11-10 13:30 | 7.1 | 5.9 | 282.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-11-10 14:30 | 7 | 5.1 | 287.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-11-10 15:30 | 6.7 | 4.5 | 290 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-11-10 16:30 | 6.8 | 4.7 | 287.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-11-10 17:30 | 6.8 | 5 | 282.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-11-10 18:30 | 6.6 | 5.2 | 280 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-11-10 19:30 | 6.2 | 5.2 | 282.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-11-10 20:30 | 5.7 | 4.7 | 285 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-11-10 21:30 | 5.7 | 4.4 | 282.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-11-10 22:30 | 6.1 | 4.4 | 275 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-11-10 23:30 | 5.9 | 4.7 | 265 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-11-11 00:30 | 5.7 | 4.9 | 257.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-11-11 01:30 | 5.6 | 4.7 | 250 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-11-11 02:30 | 5.3 | 4.2 | 240 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-11-11 03:30 | 4.9 | 3.6 | 230 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-11-11 04:30 | 4.6 | 3.3 | 220 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-11-11 05:30 | 4.4 | 3.9 | 215 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-11-11 06:30 | 4.4 | 5.1 | 220 | 110 | 67.5 | 0 | 252.5 |  | 121.2 |  | 67.5
Lerwick | 1978-11-11 07:30 | 5.2 | 5.9 | 225 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-11-11 08:30 | 6 | 6.6 | 220 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-11-11 09:30 | 6.1 | 7.3 | 210 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-11-11 10:30 | 6.5 | 8.2 | 202.5 | 635 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-11 11:30 | 7.4 | 9 | 200 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-11 12:30 | 8.2 | 9.3 | 202.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-11-11 13:30 | 8.5 | 9.1 | 207.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-11-11 14:30 | 8.2 | 8.7 | 207.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-11-11 15:30 | 7.8 | 8.5 | 205 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-11-11 16:30 | 7.3 | 8.2 | 205 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-11 17:30 | 7.1 | 8.2 | 202.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-11-11 18:30 | 7.3 | 9.1 | 200 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-11 19:30 | 7.8 | 9.6 | 200 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-11 20:30 | 8.6 | 9.1 | 200 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-11 21:30 | 9.4 | 9 | 200 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-11-11 22:30 | 9.8 | 9.6 | 200 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-11 23:30 | 10.2 | 9.6 | 197.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-11-12 00:30 | 10.2 | 8.9 | 195 | 770 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-12 01:30 | 9.9 | 8.2 | 195 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-12 02:30 | 9.7 | 8 | 195 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-11-12 03:30 | 9.6 | 8.6 | 197.5 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-12 04:30 | 9.5 | 9.9 | 200 | 1025 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-12 05:30 | 9.7 | 10.7 | 197.5 | 1270 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-12 06:30 | 9.8 | 11.4 | 192.5 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-11-12 07:30 | 9.6 | 12.3 | 190 | 1450 | 1395 | 1075 | 0 |  | 0 |  | 320
Lerwick | 1978-11-12 08:30 | 9.6 | 13.2 | 190 | 1480 | 1465 | 1145 | 0 |  | 0 |  | 320
Lerwick | 1978-11-12 09:30 | 9.6 | 13.7 | 187.5 | 1490 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-11-12 10:30 | 9.5 | 13.9 | 182.5 | 1490 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-11-12 11:30 | 9.5 | 14.1 | 180 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-11-12 12:30 | 9.3 | 14.8 | 180 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-12 13:30 | 9 | 15.6 | 180 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-12 14:30 | 8.9 | 16.3 | 180 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-12 15:30 | 8.8 | 17 | 177.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-12 16:30 | 9 | 17.5 | 172.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-12 17:30 | 9.1 | 17.9 | 172.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-12 18:30 | 9 | 17.7 | 175 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-12 19:30 | 8.6 | 16.4 | 197.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-12 20:30 | 6.7 | 14.5 | 245 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-12 21:30 | 5.9 | 13.6 | 270 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-11-12 22:30 | 6.3 | 13 | 267.5 | 1480 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-11-12 23:30 | 6.2 | 11.7 | 260 | 1400 | 1440 | 1120 | 0 |  | 0 |  | 320
Lerwick | 1978-11-13 00:30 | 6 | 11.1 | 255 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-11-13 01:30 | 5.7 | 11.3 | 252.5 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-11-13 02:30 | 4.5 | 10.9 | 245 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-11-13 03:30 | 3.2 | 11.7 | 242.5 | 1400 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-11-13 04:30 | 4.1 | 13.8 | 247.5 | 1490 | 1445 | 1125 | 0 |  | 0 |  | 320
Lerwick | 1978-11-13 05:30 | 4.5 | 14.5 | 250 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-11-13 06:30 | 4.4 | 13.9 | 252.5 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-11-13 07:30 | 5.2 | 12.4 | 255 | 1450 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-11-13 08:30 | 4.9 | 12 | 247.5 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-11-13 09:30 | 4.6 | 13.4 | 232.5 | 1480 | 1465 | 1145 | 0 |  | 0 |  | 320
Lerwick | 1978-11-13 10:30 | 4.9 | 14.5 | 225 | 1500 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-11-13 11:30 | 5.2 | 13.9 | 225 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-11-13 12:30 | 4.7 | 13 | 222.5 | 1480 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-11-13 13:30 | 4.6 | 12.7 | 225 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-11-13 14:30 | 4.8 | 12.7 | 237.5 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-11-13 15:30 | 4.5 | 12.9 | 252.5 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-11-13 16:30 | 4.4 | 11.9 | 262.5 | 1400 | 1435 | 1115 | 0 |  | 0 |  | 320
Lerwick | 1978-11-13 17:30 | 4.4 | 11.5 | 260 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-11-13 18:30 | 4.3 | 11.7 | 255 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-11-13 19:30 | 4 | 11.1 | 257.5 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-11-13 20:30 | 3.9 | 11.1 | 257.5 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-11-13 21:30 | 3.3 | 11.9 | 250 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-11-13 22:30 | 3.9 | 12.4 | 242.5 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-11-13 23:30 | 5.4 | 12.2 | 242.5 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-11-14 00:30 | 5.7 | 12.2 | 247.5 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-11-14 01:30 | 5.4 | 11.6 | 247.5 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-11-14 02:30 | 5.7 | 10.1 | 237.5 | 1150 | 1275 | 955 | 0 |  | 0 |  | 320
Lerwick | 1978-11-14 03:30 | 6.3 | 9.1 | 220 | 900 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-11-14 04:30 | 6 | 9.6 | 202.5 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-14 05:30 | 5.6 | 12.2 | 187.5 | 1450 | 1237.5 | 917.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-14 06:30 | 5.7 | 15.2 | 180 | 1500 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-11-14 07:30 | 7 | 17.4 | 187.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-14 08:30 | 8.3 | 18.8 | 200 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-14 09:30 | 8.6 | 19.4 | 210 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-14 10:30 | 9.1 | 19.9 | 220 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-14 11:30 | 10 | 20.7 | 227.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-14 12:30 | 10.4 | 22.1 | 230 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-14 13:30 | 9.5 | 24 | 232.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-14 14:30 | 8.8 | 23.8 | 237.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-14 15:30 | 8.9 | 21.3 | 242.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-14 16:30 | 8.7 | 18.8 | 255 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-14 17:30 | 8.7 | 15.7 | 277.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-14 18:30 | 7.8 | 12.3 | 300 | 1450 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-11-14 19:30 | 5.6 | 9.8 | 312.5 | 1025 | 1237.5 | 917.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-14 20:30 | 4.5 | 8 | 310 | 635 | 830 | 510 | 0 |  | 0 |  | 320
Lerwick | 1978-11-14 21:30 | 4.6 | 6.4 | 300 | 220 | 427.5 | 107.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-14 22:30 | 4.6 | 4.8 | 290 | 80 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-11-14 23:30 | 4.5 | 3.8 | 277.5 | 25 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-11-15 00:30 | 4.2 | 3.1 | 260 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-11-15 01:30 | 4 | 2.4 | 237.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-11-15 02:30 | 3.8 | 2.1 | 220 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-11-15 03:30 | 3.8 | 2.7 | 212.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-11-15 04:30 | 3.9 | 3.4 | 207.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-11-15 05:30 | 4.2 | 3.4 | 200 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-11-15 06:30 | 4.2 | 3.2 | 192.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-11-15 07:30 | 4.5 | 2.9 | 192.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-11-15 08:30 | 4.7 | 3.1 | 182.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-11-15 09:30 | 4.6 | 4 | 150 | 60 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-11-15 10:30 | 4.4 | 4.6 | 112.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-11-15 11:30 | 4.2 | 5.5 | 87.5 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-11-15 12:30 | 4.1 | 6.9 | 77.5 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-11-15 13:30 | 4 | 8.1 | 65 | 635 | 467.5 | 147.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-15 14:30 | 3.9 | 8.6 | 40 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-15 15:30 | 3.9 | 8.9 | 190 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-11-15 16:30 | 4 | 9 | 345 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-11-15 17:30 | 3.7 | 8.5 | 330 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-11-15 18:30 | 3.3 | 8.1 | 320 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-15 19:30 | 3.5 | 8.3 | 310 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-11-15 20:30 | 3.8 | 7.8 | 300 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-15 21:30 | 3.9 | 6.5 | 290 | 300 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-11-15 22:30 | 3.8 | 5.2 | 282.5 | 110 | 205 | 0 | 115 |  | 55.2 |  | 205
Lerwick | 1978-11-15 23:30 | 3.5 | 3.1 | 300 | 0 | 55 | 0 | 265 |  | 127.2 |  | 55
Lerwick | 1978-11-16 00:30 | 3.5 | 2.8 | 310 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-11-16 01:30 | 3.1 | 6.7 | 275 | 300 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-11-16 02:30 | 2.6 | 11.4 | 255 | 1340 | 820 | 500 | 0 |  | 0 |  | 320
Lerwick | 1978-11-16 03:30 | 3.2 | 14.7 | 262.5 | 1500 | 1420 | 1100 | 0 |  | 0 |  | 320
Lerwick | 1978-11-16 04:30 | 3.9 | 14.9 | 270 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-16 05:30 | 3.3 | 12.6 | 275 | 1470 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-11-16 06:30 | 2.5 | 11 | 272.5 | 1340 | 1405 | 1085 | 0 |  | 0 |  | 320
Lerwick | 1978-11-16 07:30 | 3.2 | 10.3 | 265 | 1150 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-11-16 08:30 | 3.7 | 9.5 | 252.5 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-16 09:30 | 4.2 | 9.3 | 245 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-16 10:30 | 4.3 | 10.3 | 245 | 1150 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-11-16 11:30 | 4.7 | 12.1 | 242.5 | 1450 | 1300 | 980 | 0 |  | 0 |  | 320
Lerwick | 1978-11-16 12:30 | 5.3 | 12.6 | 240 | 1470 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-11-16 13:30 | 4.8 | 12.1 | 242.5 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-11-16 14:30 | 4.8 | 10.6 | 242.5 | 1270 | 1360 | 1040 | 0 |  | 0 |  | 320
Lerwick | 1978-11-16 15:30 | 4.1 | 9.2 | 235 | 900 | 1085 | 765 | 0 |  | 0 |  | 320
Lerwick | 1978-11-16 16:30 | 3.7 | 9.4 | 230 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-11-16 17:30 | 5 | 9.1 | 230 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-11-16 18:30 | 4.7 | 7.7 | 230 | 500 | 700 | 380 | 0 |  | 0 |  | 320
Lerwick | 1978-11-16 19:30 | 3.7 | 7.1 | 235 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-11-16 20:30 | 3.7 | 8 | 250 | 635 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-16 21:30 | 4.2 | 9.5 | 262.5 | 1025 | 830 | 510 | 0 |  | 0 |  | 320
Lerwick | 1978-11-16 22:30 | 4.9 | 11 | 262.5 | 1340 | 1182.5 | 862.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-16 23:30 | 5.3 | 12.1 | 260 | 1450 | 1395 | 1075 | 0 |  | 0 |  | 320
Lerwick | 1978-11-17 00:30 | 5.7 | 12.2 | 262.5 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-11-17 01:30 | 5.7 | 12.2 | 265 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-11-17 02:30 | 5.3 | 12.4 | 262.5 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-11-17 03:30 | 5.3 | 11.4 | 257.5 | 1340 | 1395 | 1075 | 0 |  | 0 |  | 320
Lerwick | 1978-11-17 04:30 | 5.5 | 10 | 252.5 | 1150 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-11-17 05:30 | 5.9 | 9.1 | 247.5 | 900 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-11-17 06:30 | 6.5 | 7.9 | 237.5 | 500 | 700 | 380 | 0 |  | 0 |  | 320
Lerwick | 1978-11-17 07:30 | 6.7 | 6.4 | 217.5 | 220 | 360 | 40 | 0 |  | 0 |  | 320
Lerwick | 1978-11-17 08:30 | 6.8 | 5.6 | 202.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-11-17 09:30 | 6.6 | 6.7 | 207.5 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-11-17 10:30 | 7 | 10 | 217.5 | 1150 | 725 | 405 | 0 |  | 0 |  | 320
Lerwick | 1978-11-17 11:30 | 8.4 | 12.5 | 220 | 1470 | 1310 | 990 | 0 |  | 0 |  | 320
Lerwick | 1978-11-17 12:30 | 9.6 | 13.2 | 220 | 1480 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-11-17 13:30 | 9.6 | 13.4 | 217.5 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-11-17 14:30 | 9.3 | 13.4 | 212.5 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-11-17 15:30 | 9.2 | 13.2 | 210 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-11-17 16:30 | 9.2 | 12.8 | 210 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-11-17 17:30 | 8.8 | 12.8 | 210 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-11-17 18:30 | 8.6 | 12.8 | 210 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-11-17 19:30 | 8.3 | 11.7 | 210 | 1400 | 1435 | 1115 | 0 |  | 0 |  | 320
Lerwick | 1978-11-17 20:30 | 8.3 | 11 | 210 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-11-17 21:30 | 8.4 | 11.1 | 210 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-11-17 22:30 | 8.3 | 11.3 | 210 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-11-17 23:30 | 8.2 | 11 | 215 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-11-18 00:30 | 8 | 11.3 | 225 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-11-18 01:30 | 8 | 12.1 | 235 | 1450 | 1395 | 1075 | 0 |  | 0 |  | 320
Lerwick | 1978-11-18 02:30 | 8.2 | 12.2 | 247.5 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-11-18 03:30 | 8.3 | 11.7 | 257.5 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-11-18 04:30 | 7.8 | 11 | 260 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-11-18 05:30 | 7.5 | 10.4 | 257.5 | 1150 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-11-18 06:30 | 7.5 | 10.3 | 250 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-11-18 07:30 | 7.4 | 10.3 | 242.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-11-18 08:30 | 7.4 | 10.3 | 240 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-11-18 09:30 | 7.6 | 10.3 | 240 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-11-18 10:30 | 7.8 | 9.8 | 240 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-18 11:30 | 7 | 8.2 | 240 | 635 | 830 | 510 | 0 |  | 0 |  | 320
Lerwick | 1978-11-18 12:30 | 6.7 | 6.7 | 237.5 | 300 | 467.5 | 147.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-18 13:30 | 7.2 | 6.2 | 230 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-11-18 14:30 | 7.3 | 6.2 | 220 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-11-18 15:30 | 7.4 | 6.2 | 210 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-11-18 16:30 | 7.1 | 6.7 | 200 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-11-18 17:30 | 7 | 8.2 | 190 | 635 | 467.5 | 147.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-18 18:30 | 7.4 | 10.1 | 182.5 | 1150 | 892.5 | 572.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-18 19:30 | 7.9 | 11.5 | 187.5 | 1400 | 1275 | 955 | 0 |  | 0 |  | 320
Lerwick | 1978-11-18 20:30 | 8.1 | 12.7 | 207.5 | 1470 | 1435 | 1115 | 0 |  | 0 |  | 320
Lerwick | 1978-11-18 21:30 | 8.4 | 13.6 | 225 | 1490 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-11-18 22:30 | 7.6 | 13.7 | 230 | 1490 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-11-18 23:30 | 6.4 | 13.7 | 232.5 | 1490 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-11-19 00:30 | 6.7 | 14 | 237.5 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-11-19 01:30 | 7.1 | 14 | 242.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-19 02:30 | 7.1 | 13.7 | 247.5 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-11-19 03:30 | 7.1 | 13.3 | 250 | 1480 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-11-19 04:30 | 6.7 | 12.4 | 250 | 1450 | 1465 | 1145 | 0 |  | 0 |  | 320
Lerwick | 1978-11-19 05:30 | 6.5 | 10.9 | 252.5 | 1270 | 1360 | 1040 | 0 |  | 0 |  | 320
Lerwick | 1978-11-19 06:30 | 6.2 | 9.2 | 255 | 900 | 1085 | 765 | 0 |  | 0 |  | 320
Lerwick | 1978-11-19 07:30 | 5.5 | 8.1 | 252.5 | 635 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-19 08:30 | 5.4 | 7.4 | 250 | 400 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-19 09:30 | 5.9 | 6.9 | 252.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-11-19 10:30 | 6.5 | 6.5 | 255 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-11-19 11:30 | 6 | 6.7 | 250 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-11-19 12:30 | 4.8 | 6.8 | 252.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-11-19 13:30 | 5.3 | 5.8 | 260 | 150 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-11-19 14:30 | 5.1 | 4.1 | 257.5 | 60 | 105 | 0 | 215 |  | 103.2 |  | 105
Lerwick | 1978-11-19 15:30 | 4.1 | 3.2 | 245 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-11-19 16:30 | 4 | 3.5 | 220 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-11-19 17:30 | 4 | 4.2 | 230 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-11-19 18:30 | 3.9 | 4.4 | 265 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-11-19 19:30 | 3.3 | 4 | 260 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-11-19 20:30 | 3.1 | 3.7 | 247.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-11-19 21:30 | 3.2 | 4.2 | 257.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-11-19 22:30 | 3.6 | 4.7 | 270 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-11-19 23:30 | 4.2 | 5.2 | 275 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-11-20 00:30 | 4.1 | 5.5 | 272.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-11-20 01:30 | 4.2 | 5.8 | 270 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-11-20 02:30 | 4.7 | 5.9 | 267.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-11-20 03:30 | 4 | 6 | 255 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-11-20 04:30 | 4 | 6.2 | 247.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-11-20 05:30 | 4.1 | 6.6 | 252.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-11-20 06:30 | 3.5 | 6.2 | 247.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-11-20 07:30 | 2.8 | 4.9 | 237.5 | 80 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-11-20 08:30 | 1.8 | 5.4 | 230 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-11-20 09:30 | 2.3 | 7 | 222.5 | 400 | 255 | 0 | 65 |  | 31.2 |  | 255
Lerwick | 1978-11-20 10:30 | 4.1 | 8.2 | 220 | 635 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-20 11:30 | 5.2 | 9.1 | 217.5 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-20 12:30 | 5.5 | 9.7 | 210 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-20 13:30 | 5.3 | 9.9 | 202.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-11-20 14:30 | 5.2 | 9.9 | 197.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-11-20 15:30 | 5.6 | 10.5 | 190 | 1270 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-20 16:30 | 5.7 | 11.9 | 182.5 | 1400 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-11-20 17:30 | 6.3 | 13.6 | 180 | 1490 | 1445 | 1125 | 0 |  | 0 |  | 320
Lerwick | 1978-11-20 18:30 | 6.2 | 14.6 | 180 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-11-20 19:30 | 5.8 | 15 | 185 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-20 20:30 | 6.2 | 14.9 | 197.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-20 21:30 | 6.9 | 14.1 | 215 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-20 22:30 | 7.2 | 13.9 | 232.5 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-11-20 23:30 | 7.5 | 14.5 | 240 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-11-21 00:30 | 7.9 | 15.3 | 240 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-21 01:30 | 7.8 | 15.9 | 242.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-21 02:30 | 7.6 | 16.1 | 245 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-21 03:30 | 7.6 | 16.1 | 242.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-21 04:30 | 7.8 | 16.1 | 237.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-21 05:30 | 8.1 | 15.8 | 232.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-21 06:30 | 7.9 | 15.8 | 230 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-21 07:30 | 7.9 | 15.7 | 230 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-21 08:30 | 7.8 | 15.4 | 230 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-21 09:30 | 7.9 | 15.9 | 230 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-21 10:30 | 8.4 | 16.9 | 230 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-21 11:30 | 8.6 | 17.1 | 230 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-21 12:30 | 8.3 | 16.5 | 230 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-21 13:30 | 7.6 | 15.3 | 232.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-21 14:30 | 7.7 | 14 | 235 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-21 15:30 | 7.6 | 12.9 | 232.5 | 1470 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-11-21 16:30 | 7.4 | 12.4 | 230 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-11-21 17:30 | 7.8 | 12.4 | 230 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-11-21 18:30 | 8.1 | 12.7 | 230 | 1470 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-11-21 19:30 | 8.4 | 13.6 | 230 | 1490 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-11-21 20:30 | 8.3 | 14.2 | 230 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-11-21 21:30 | 8.3 | 13.8 | 235 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-11-21 22:30 | 7.4 | 13.5 | 247.5 | 1490 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-11-21 23:30 | 6.8 | 13.9 | 260 | 1490 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-11-22 00:30 | 7.2 | 13.8 | 265 | 1490 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-11-22 01:30 | 6.8 | 12.9 | 262.5 | 1470 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-11-22 02:30 | 6.8 | 12 | 260 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-11-22 03:30 | 6.8 | 10.4 | 257.5 | 1150 | 1300 | 980 | 0 |  | 0 |  | 320
Lerwick | 1978-11-22 04:30 | 6.7 | 8.5 | 247.5 | 770 | 960 | 640 | 0 |  | 0 |  | 320
Lerwick | 1978-11-22 05:30 | 6.8 | 7.3 | 232.5 | 400 | 585 | 265 | 0 |  | 0 |  | 320
Lerwick | 1978-11-22 06:30 | 7 | 6.7 | 217.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-11-22 07:30 | 6.8 | 7.4 | 200 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-11-22 08:30 | 6.4 | 10.1 | 187.5 | 1150 | 775 | 455 | 0 |  | 0 |  | 320
Lerwick | 1978-11-22 09:30 | 6.4 | 13.6 | 190 | 1490 | 1320 | 1000 | 0 |  | 0 |  | 320
Lerwick | 1978-11-22 10:30 | 7.2 | 16.7 | 202.5 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-11-22 11:30 | 8.3 | 18.4 | 217.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-22 12:30 | 8.9 | 19.4 | 230 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-22 13:30 | 8.8 | 20.9 | 237.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-22 14:30 | 8.4 | 22.3 | 240 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-22 15:30 | 8.1 | 21.3 | 247.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-22 16:30 | 7.4 | 16.7 | 270 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-22 17:30 | 6.2 | 11.7 | 290 | 1400 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-11-22 18:30 | 5 | 8.9 | 290 | 770 | 1085 | 765 | 0 |  | 0 |  | 320
Lerwick | 1978-11-22 19:30 | 4.2 | 7.7 | 277.5 | 500 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-11-22 20:30 | 3.9 | 8.2 | 265 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-22 21:30 | 4.6 | 9.5 | 262.5 | 1025 | 830 | 510 | 0 |  | 0 |  | 320
Lerwick | 1978-11-22 22:30 | 4.6 | 9.5 | 270 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-11-22 23:30 | 3.1 | 8.2 | 277.5 | 635 | 830 | 510 | 0 |  | 0 |  | 320
Lerwick | 1978-11-23 00:30 | 2.5 | 7.7 | 275 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-23 01:30 | 3.1 | 8 | 265 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-23 02:30 | 3.9 | 7.6 | 255 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-23 03:30 | 4.1 | 7.1 | 240 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-11-23 04:30 | 4.2 | 8 | 222.5 | 635 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-23 05:30 | 4.1 | 10 | 215 | 1150 | 892.5 | 572.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-23 06:30 | 4.1 | 10.9 | 222.5 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-11-23 07:30 | 3.6 | 11.6 | 235 | 1400 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-11-23 08:30 | 3.9 | 13 | 240 | 1480 | 1440 | 1120 | 0 |  | 0 |  | 320
Lerwick | 1978-11-23 09:30 | 5.3 | 13.3 | 240 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-11-23 10:30 | 5.1 | 13 | 240 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-11-23 11:30 | 5.5 | 12.3 | 240 | 1450 | 1465 | 1145 | 0 |  | 0 |  | 320
Lerwick | 1978-11-23 12:30 | 5.9 | 11.4 | 240 | 1340 | 1395 | 1075 | 0 |  | 0 |  | 320
Lerwick | 1978-11-23 13:30 | 5.7 | 10.7 | 242.5 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-11-23 14:30 | 5.8 | 10.2 | 247.5 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-11-23 15:30 | 5.5 | 9.7 | 250 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-23 16:30 | 4.7 | 9 | 252.5 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-23 17:30 | 4.5 | 8.3 | 257.5 | 635 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-23 18:30 | 4.5 | 8.1 | 257.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-11-23 19:30 | 4.5 | 8 | 255 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-11-23 20:30 | 4.6 | 7.3 | 265 | 400 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-23 21:30 | 4.5 | 6 | 272.5 | 220 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-11-23 22:30 | 2.9 | 5.4 | 265 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-11-23 23:30 | 2.1 | 5.8 | 265 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-11-24 00:30 | 3 | 6.6 | 270 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-11-24 01:30 | 2.7 | 7.1 | 267.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-11-24 02:30 | 2.8 | 7.2 | 260 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-11-24 03:30 | 2.5 | 7.6 | 252.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-11-24 04:30 | 2.9 | 8.5 | 250 | 770 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-11-24 05:30 | 4 | 8.5 | 255 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-11-24 06:30 | 3.4 | 7.9 | 257.5 | 500 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-11-24 07:30 | 3 | 7.8 | 250 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-11-24 08:30 | 3 | 8 | 250 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-24 09:30 | 3.5 | 8.4 | 257.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-11-24 10:30 | 4.3 | 8.9 | 260 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-24 11:30 | 4.6 | 9 | 257.5 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-11-24 12:30 | 4.5 | 8.9 | 252.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-11-24 13:30 | 4.2 | 8.2 | 252.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-24 14:30 | 3.9 | 7.3 | 260 | 400 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-24 15:30 | 3.9 | 7 | 267.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-11-24 16:30 | 3.7 | 7.1 | 265 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-11-24 17:30 | 3.1 | 7.2 | 250 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-11-24 18:30 | 2.2 | 6.8 | 237.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-11-24 19:30 | 1.9 | 6 | 242.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-11-24 20:30 | 2 | 5.8 | 252.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-11-24 21:30 | 2.4 | 6 | 257.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-11-24 22:30 | 2.3 | 6.2 | 260 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-11-24 23:30 | 2.1 | 6 | 255 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-11-25 00:30 | 1.9 | 5.4 | 250 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-11-25 01:30 | 1.4 | 4.4 | 265 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-11-25 02:30 | 2 | 4.2 | 292.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-11-25 03:30 | 2 | 4.1 | 290 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-11-25 04:30 | 1.1 | 3 | 252.5 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-11-25 05:30 | 0.8 | 2.2 | 237.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-11-25 06:30 | 0.4 | 2.4 | 260 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-11-25 07:30 | 1.1 | 2.9 | 275 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-11-25 08:30 | 1.7 | 3.9 | 265 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-11-25 09:30 | 1.8 | 4.7 | 252.5 | 80 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-11-25 10:30 | 2.2 | 5.8 | 247.5 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-11-25 11:30 | 2.2 | 6.9 | 235 | 300 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-11-25 12:30 | 2.2 | 7.3 | 232.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-11-25 13:30 | 2.4 | 7.8 | 245 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-11-25 14:30 | 3 | 8.1 | 250 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-25 15:30 | 3.4 | 8.4 | 250 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-11-25 16:30 | 3.4 | 9 | 247.5 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-25 17:30 | 3.5 | 9 | 240 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-11-25 18:30 | 3.1 | 8.2 | 240 | 635 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-25 19:30 | 2.4 | 7.4 | 252.5 | 400 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-25 20:30 | 2.4 | 7.3 | 290 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-11-25 21:30 | 2.5 | 8.7 | 167.5 | 770 | 585 | 265 | 0 |  | 0 |  | 320
Lerwick | 1978-11-25 22:30 | 2.7 | 10.6 | 10 | 1270 | 1020 | 700 | 0 |  | 0 |  | 320
Lerwick | 1978-11-25 23:30 | 3.1 | 10.3 | 5 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-11-26 00:30 | 3 | 9.5 | 2.5 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-26 01:30 | 2.2 | 11.3 | 177.5 | 1340 | 1182.5 | 862.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-26 02:30 | 1.5 | 13.9 | 180 | 1490 | 1415 | 1095 | 0 |  | 0 |  | 320
Lerwick | 1978-11-26 03:30 | 1.5 | 14.2 | 5 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-11-26 04:30 | 2 | 12.5 | 180 | 1470 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-11-26 05:30 | 2.3 | 11.4 | 352.5 | 1340 | 1405 | 1085 | 0 |  | 0 |  | 320
Lerwick | 1978-11-26 06:30 | 2.2 | 10.9 | 350 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-11-26 07:30 | 1.7 | 9.5 | 347.5 | 1025 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-26 08:30 | 1.3 | 7.3 | 340 | 400 | 712.5 | 392.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-26 09:30 | 0.6 | 5.6 | 335 | 150 | 275 | 0 | 45 |  | 21.6 |  | 275
Lerwick | 1978-11-26 10:30 | 0.2 | 4.9 | 332.5 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-11-26 11:30 | 1 | 4.6 | 330 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-11-26 12:30 | 1.2 | 3.5 | 325 | 25 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-11-26 13:30 | 0.8 | 2.1 | 300 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-11-26 14:30 | 0.8 | 2.5 | 267.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-11-26 15:30 | 0.5 | 4.7 | 252.5 | 80 | 40 | 0 | 280 |  | 134.4 |  | 40
Lerwick | 1978-11-26 16:30 | 0.1 | 5.4 | 260 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-11-26 17:30 | 0.1 | 4.9 | 282.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-11-26 18:30 | 0.1 | 5.4 | 297.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-11-26 19:30 | -0.1 | 6 | 300 | 220 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-11-26 20:30 | 0 | 6.7 | 307.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-11-26 21:30 | 0.7 | 8.5 | 322.5 | 770 | 535 | 215 | 0 |  | 0 |  | 320
Lerwick | 1978-11-26 22:30 | 0.6 | 10.6 | 330 | 1270 | 1020 | 700 | 0 |  | 0 |  | 320
Lerwick | 1978-11-26 23:30 | -0.1 | 11.6 | 332.5 | 1400 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-11-27 00:30 | -0.4 | 11.9 | 335 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-11-27 01:30 | -0.6 | 12.2 | 335 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-11-27 02:30 | -0.9 | 12.2 | 335 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-11-27 03:30 | -1.1 | 12 | 335 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-11-27 04:30 | -1.4 | 11.7 | 335 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-11-27 05:30 | -2.2 | 10.9 | 335 | 1270 | 1335 | 1015 | 0 |  | 0 |  | 320
Lerwick | 1978-11-27 06:30 | -2.6 | 10 | 335 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-11-27 07:30 | -2.7 | 9.8 | 335 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-27 08:30 | -2.7 | 9.6 | 335 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-11-27 09:30 | -2.7 | 9.5 | 332.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-11-27 10:30 | -2.7 | 9.6 | 332.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-11-27 11:30 | -2.6 | 9.6 | 335 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-11-27 12:30 | -2.7 | 9.5 | 332.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-11-27 13:30 | -2.4 | 9.4 | 330 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-27 14:30 | -2.3 | 9 | 330 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-11-27 15:30 | -2.5 | 8.2 | 332.5 | 635 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-27 16:30 | -2 | 7.2 | 335 | 400 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-27 17:30 | -1.6 | 6.4 | 335 | 220 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-11-27 18:30 | -1.5 | 6.2 | 335 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-11-27 19:30 | -1.5 | 6.3 | 330 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-11-27 20:30 | -1.5 | 6.1 | 327.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-11-27 21:30 | -1.1 | 5.8 | 335 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-11-27 22:30 | -1.5 | 5.8 | 340 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-11-27 23:30 | -1.8 | 6 | 335 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-11-28 00:30 | -1.3 | 6 | 327.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-11-28 01:30 | -1.4 | 5.8 | 325 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-11-28 02:30 | -1.4 | 5.8 | 322.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-11-28 03:30 | -0.9 | 5.9 | 322.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-11-28 04:30 | -0.6 | 5.9 | 330 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-11-28 05:30 | -1.1 | 5.9 | 337.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-11-28 06:30 | -1.3 | 5.8 | 337.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-11-28 07:30 | -0.8 | 5.3 | 332.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-11-28 08:30 | -1.2 | 4.7 | 330 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-11-28 09:30 | -1.3 | 4.5 | 330 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-11-28 10:30 | -0.5 | 4.2 | 330 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-11-28 11:30 | -0.1 | 3.6 | 330 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-11-28 12:30 | 0.1 | 2.9 | 327.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-11-28 13:30 | 0.5 | 2 | 322.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-11-28 14:30 | 0.9 | 1 | 330 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-11-28 15:30 | 0.8 | 0.2 | 170 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-11-28 16:30 | -0.3 | 0.2 | 147.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-11-28 17:30 | -0.9 | 0.9 | 255 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-11-28 18:30 | -0.5 | 1.4 | 207.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-11-28 19:30 | 0.3 | 1.8 | 197.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-11-28 20:30 | 1.1 | 2.7 | 190 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-11-28 21:30 | 1.5 | 3.6 | 185 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-11-28 22:30 | 2.2 | 4.9 | 180 | 80 | 52.5 | 0 | 267.5 |  | 128.4 |  | 52.5
Lerwick | 1978-11-28 23:30 | 2.6 | 6.9 | 170 | 300 | 190 | 0 | 130 |  | 62.4 |  | 190
Lerwick | 1978-11-29 00:30 | 2.9 | 8 | 170 | 635 | 467.5 | 147.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-29 01:30 | 3.4 | 7.6 | 180 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-29 02:30 | 3.5 | 7.3 | 185 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-11-29 03:30 | 3.5 | 7.7 | 182.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-11-29 04:30 | 3.8 | 8 | 180 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-29 05:30 | 4 | 8.8 | 180 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-29 06:30 | 4.2 | 9.2 | 180 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-11-29 07:30 | 4.2 | 8.5 | 182.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-11-29 08:30 | 4.2 | 8.4 | 185 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-29 09:30 | 4.7 | 9 | 180 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-29 10:30 | 5 | 9.6 | 170 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-29 11:30 | 5 | 10.2 | 165 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-29 12:30 | 5.1 | 10.4 | 165 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-11-29 13:30 | 5.1 | 10.1 | 165 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-11-29 14:30 | 5.2 | 10.4 | 167.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-11-29 15:30 | 5.6 | 10.9 | 170 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-11-29 16:30 | 5.9 | 11.1 | 170 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-11-29 17:30 | 5.8 | 11.1 | 167.5 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-11-29 18:30 | 5.8 | 10.9 | 162.5 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-11-29 19:30 | 5.8 | 11 | 162.5 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-11-29 20:30 | 5.7 | 11.1 | 167.5 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-11-29 21:30 | 5.8 | 10.1 | 170 | 1150 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-11-29 22:30 | 6.1 | 8.4 | 170 | 635 | 892.5 | 572.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-29 23:30 | 5.6 | 7.8 | 167.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-30 00:30 | 4.7 | 8.7 | 162.5 | 770 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-11-30 01:30 | 4.9 | 9.5 | 157.5 | 1025 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-30 02:30 | 5.2 | 9.9 | 152.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-11-30 03:30 | 5.2 | 10 | 152.5 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-30 04:30 | 5.5 | 10.1 | 155 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-11-30 05:30 | 5.5 | 10.3 | 152.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-11-30 06:30 | 5.3 | 10 | 147.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-11-30 07:30 | 5.2 | 9.5 | 145 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-30 08:30 | 4.9 | 9.4 | 150 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-30 09:30 | 4.5 | 9.7 | 157.5 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-30 10:30 | 4.3 | 10.4 | 157.5 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-30 11:30 | 4.3 | 10.9 | 152.5 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-11-30 12:30 | 4.4 | 10.5 | 152.5 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-11-30 13:30 | 4.7 | 9.7 | 157.5 | 1025 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-30 14:30 | 4.5 | 9.4 | 160 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-30 15:30 | 4.1 | 9 | 157.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-11-30 16:30 | 3.8 | 8.8 | 150 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-11-30 17:30 | 3.4 | 8.9 | 142.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-11-30 18:30 | 3.6 | 9.4 | 140 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-11-30 19:30 | 3.9 | 9.9 | 140 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-30 20:30 | 3.9 | 9.5 | 137.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-11-30 21:30 | 4 | 8.5 | 135 | 770 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-30 22:30 | 3.9 | 8.3 | 140 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-11-30 23:30 | 3.6 | 8.6 | 145 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-01 00:30 | 3.7 | 8.9 | 142.5 | 770 | 770 | 450 | 0 |  | 0 | 22154.4 | 320 | 191925
Lerwick | 1978-12-01 01:30 | 3.9 | 9 | 140 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-12-01 02:30 | 3.7 | 9 | 137.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-12-01 03:30 | 3.6 | 9.4 | 132.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-12-01 04:30 | 3.6 | 9.8 | 135 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-01 05:30 | 3.6 | 9.6 | 142.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-12-01 06:30 | 3 | 9.5 | 140 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-12-01 07:30 | 2.4 | 9.6 | 132.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-12-01 08:30 | 3 | 9.9 | 135 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-12-01 09:30 | 3.4 | 9.7 | 142.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-12-01 10:30 | 3.4 | 9.6 | 142.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-12-01 11:30 | 3.8 | 9.9 | 137.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-12-01 12:30 | 3.8 | 9.7 | 132.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-12-01 13:30 | 3.7 | 9.4 | 132.5 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-01 14:30 | 3.5 | 9.3 | 137.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-12-01 15:30 | 3.6 | 9.3 | 137.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-12-01 16:30 | 3.3 | 9.3 | 132.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-12-01 17:30 | 3.4 | 9.4 | 132.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-12-01 18:30 | 4.1 | 9.6 | 135 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-01 19:30 | 3.7 | 9.6 | 132.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-12-01 20:30 | 3.8 | 9.5 | 130 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-12-01 21:30 | 4.3 | 9.5 | 127.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-12-01 22:30 | 4.1 | 9 | 125 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-01 23:30 | 4.1 | 8.2 | 125 | 635 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-02 00:30 | 4 | 8 | 125 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-12-02 01:30 | 3.8 | 8.4 | 125 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-12-02 02:30 | 4.1 | 8.8 | 127.5 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-02 03:30 | 4.5 | 8.9 | 132.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-12-02 04:30 | 4.2 | 9.4 | 135 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-12-02 05:30 | 4.6 | 10 | 137.5 | 1150 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-12-02 06:30 | 5.1 | 10.6 | 140 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-12-02 07:30 | 5.1 | 11.4 | 140 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-12-02 08:30 | 5.3 | 11.9 | 140 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-12-02 09:30 | 5.7 | 12 | 140 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-12-02 10:30 | 6 | 12.2 | 140 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-12-02 11:30 | 5.6 | 12.4 | 140 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-12-02 12:30 | 5.4 | 12.1 | 140 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-12-02 13:30 | 5.8 | 11.8 | 140 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-12-02 14:30 | 6.1 | 11.9 | 140 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-12-02 15:30 | 6.1 | 12.2 | 140 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-12-02 16:30 | 6.2 | 12.8 | 140 | 1470 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-12-02 17:30 | 6.4 | 13.2 | 140 | 1480 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-12-02 18:30 | 6.3 | 13.4 | 137.5 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-12-02 19:30 | 6.2 | 13.4 | 132.5 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-12-02 20:30 | 6.2 | 13.5 | 130 | 1490 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-12-02 21:30 | 6.1 | 13.6 | 130 | 1490 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-12-02 22:30 | 6.1 | 13.5 | 132.5 | 1490 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-12-02 23:30 | 6.1 | 13.2 | 137.5 | 1480 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-12-03 00:30 | 5.7 | 12.8 | 140 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-12-03 01:30 | 5.7 | 12.4 | 140 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-12-03 02:30 | 5.9 | 12.1 | 140 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-12-03 03:30 | 6.2 | 11.6 | 140 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-12-03 04:30 | 6.6 | 11.6 | 140 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-12-03 05:30 | 6.8 | 11.9 | 140 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-12-03 06:30 | 6.8 | 12 | 140 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-12-03 07:30 | 6.8 | 12 | 140 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-12-03 08:30 | 6.8 | 11.7 | 142.5 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-12-03 09:30 | 6.6 | 11.2 | 150 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-12-03 10:30 | 6.7 | 11.4 | 155 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-12-03 11:30 | 7 | 11.9 | 152.5 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-12-03 12:30 | 7.2 | 11.9 | 150 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-12-03 13:30 | 7.1 | 11.8 | 147.5 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-12-03 14:30 | 6.9 | 11.8 | 142.5 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-12-03 15:30 | 7 | 11.6 | 140 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-12-03 16:30 | 6.9 | 11.6 | 140 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-12-03 17:30 | 6.7 | 12.1 | 140 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-12-03 18:30 | 6.7 | 12.5 | 140 | 1470 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-12-03 19:30 | 6.8 | 12.5 | 140 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-12-03 20:30 | 6.7 | 12.4 | 137.5 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-12-03 21:30 | 6.7 | 12.4 | 132.5 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-12-03 22:30 | 6.8 | 13 | 130 | 1480 | 1465 | 1145 | 0 |  | 0 |  | 320
Lerwick | 1978-12-03 23:30 | 6.4 | 14.1 | 130 | 1500 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-12-04 00:30 | 6.1 | 14.8 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-04 01:30 | 5.8 | 15 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-04 02:30 | 5.8 | 15 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-04 03:30 | 6 | 14.8 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-04 04:30 | 6.1 | 14.8 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-04 05:30 | 6.3 | 14.8 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-04 06:30 | 6.2 | 14.7 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-04 07:30 | 6.1 | 14.8 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-04 08:30 | 6.4 | 14.8 | 132.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-04 09:30 | 6.1 | 14.4 | 135 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-04 10:30 | 5.8 | 14.3 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-04 11:30 | 5.5 | 14.3 | 122.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-04 12:30 | 5.3 | 14 | 122.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-04 13:30 | 5 | 14.1 | 127.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-04 14:30 | 4.4 | 14.4 | 127.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-04 15:30 | 4.6 | 14.4 | 122.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-04 16:30 | 4.9 | 14.3 | 120 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-04 17:30 | 5 | 13.9 | 120 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-12-04 18:30 | 5 | 13.6 | 120 | 1490 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-12-04 19:30 | 5 | 13.9 | 120 | 1490 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-12-04 20:30 | 5.1 | 14.3 | 120 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-12-04 21:30 | 5.1 | 14.5 | 120 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-04 22:30 | 5.1 | 14.5 | 122.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-04 23:30 | 5 | 14 | 127.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-05 00:30 | 5 | 13.7 | 127.5 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-12-05 01:30 | 5 | 14.1 | 125 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-12-05 02:30 | 5 | 14.4 | 125 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-05 03:30 | 5.2 | 14.3 | 125 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-05 04:30 | 5.2 | 13.9 | 127.5 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-12-05 05:30 | 5.4 | 13.3 | 132.5 | 1480 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-12-05 06:30 | 5.8 | 12.8 | 135 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-12-05 07:30 | 6.1 | 12.4 | 132.5 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-12-05 08:30 | 6.3 | 12.4 | 130 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-12-05 09:30 | 6.5 | 12.7 | 130 | 1470 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-12-05 10:30 | 6.5 | 12.7 | 132.5 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-12-05 11:30 | 6.2 | 12.4 | 140 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-12-05 12:30 | 6.1 | 12.4 | 150 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-12-05 13:30 | 6.5 | 12.2 | 157.5 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-12-05 14:30 | 6.9 | 11.6 | 160 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-12-05 15:30 | 7.2 | 11.3 | 160 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-12-05 16:30 | 7.3 | 11.3 | 160 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-12-05 17:30 | 7.2 | 11.1 | 160 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-12-05 18:30 | 7.2 | 11 | 157.5 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-12-05 19:30 | 7.2 | 11 | 152.5 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-12-05 20:30 | 7.1 | 10.9 | 150 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-12-05 21:30 | 7 | 10.8 | 150 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-12-05 22:30 | 6.8 | 10.6 | 150 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-12-05 23:30 | 6.6 | 10.4 | 150 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-12-06 00:30 | 6.6 | 10.3 | 150 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-12-06 01:30 | 6.5 | 10.3 | 150 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-12-06 02:30 | 6.3 | 10.3 | 147.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-12-06 03:30 | 6.2 | 10.3 | 142.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-12-06 04:30 | 6.1 | 10.3 | 140 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-12-06 05:30 | 6 | 10.4 | 140 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-12-06 06:30 | 6.2 | 10.7 | 140 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-12-06 07:30 | 6.3 | 11.1 | 140 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-12-06 08:30 | 6.2 | 11.3 | 140 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-12-06 09:30 | 6.2 | 11.3 | 140 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-12-06 10:30 | 6.2 | 11.3 | 140 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-12-06 11:30 | 6.1 | 11.4 | 140 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-12-06 12:30 | 6 | 11.6 | 140 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-12-06 13:30 | 6 | 11.8 | 140 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-12-06 14:30 | 6 | 11.9 | 140 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-12-06 15:30 | 6 | 12.2 | 140 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-12-06 16:30 | 6 | 12.7 | 140 | 1470 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-12-06 17:30 | 6 | 13 | 140 | 1480 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-12-06 18:30 | 5.9 | 13.2 | 140 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-12-06 19:30 | 5.9 | 13.4 | 140 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-12-06 20:30 | 5.9 | 13.4 | 140 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-12-06 21:30 | 5.9 | 13.5 | 140 | 1490 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-12-06 22:30 | 5.7 | 13.6 | 140 | 1490 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-12-06 23:30 | 5.3 | 13.3 | 137.5 | 1480 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-12-07 00:30 | 5.3 | 13.1 | 135 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-12-07 01:30 | 5.4 | 13.1 | 137.5 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-12-07 02:30 | 5.5 | 13.1 | 140 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-12-07 03:30 | 5.6 | 13.5 | 140 | 1490 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-12-07 04:30 | 5.5 | 14 | 140 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-12-07 05:30 | 5.4 | 14 | 140 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-07 06:30 | 5.4 | 13.9 | 140 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-12-07 07:30 | 5.4 | 13.7 | 140 | 1490 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-12-07 08:30 | 5.3 | 13.3 | 140 | 1480 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-12-07 09:30 | 5.3 | 13.2 | 140 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-12-07 10:30 | 5.4 | 13.6 | 140 | 1490 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-12-07 11:30 | 5.4 | 13.7 | 140 | 1490 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-12-07 12:30 | 5.4 | 13.6 | 140 | 1490 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-12-07 13:30 | 5.4 | 13.7 | 140 | 1490 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-12-07 14:30 | 5.2 | 14 | 140 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-12-07 15:30 | 5.1 | 14 | 140 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-07 16:30 | 5.3 | 13.7 | 140 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-12-07 17:30 | 5.3 | 14.1 | 140 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-12-07 18:30 | 5.2 | 15.2 | 140 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-07 19:30 | 5.2 | 15.7 | 140 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-07 20:30 | 5.2 | 15.7 | 137.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-07 21:30 | 5.1 | 15.8 | 132.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-07 22:30 | 5 | 16.1 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-07 23:30 | 4.9 | 16.3 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-08 00:30 | 4.9 | 16.6 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-08 01:30 | 5 | 17 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-08 02:30 | 4.9 | 17.3 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-08 03:30 | 4.9 | 17.1 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-08 04:30 | 4.8 | 17 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-08 05:30 | 4.8 | 16.8 | 127.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-08 06:30 | 4.7 | 16.6 | 122.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-08 07:30 | 4.5 | 16.5 | 120 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-08 08:30 | 4.6 | 16.5 | 120 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-08 09:30 | 4.7 | 16.2 | 120 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-08 10:30 | 4.7 | 15.8 | 120 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-08 11:30 | 4.7 | 15.7 | 120 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-08 12:30 | 4.7 | 15.5 | 120 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-08 13:30 | 4.6 | 15.4 | 120 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-08 14:30 | 4.5 | 15.4 | 117.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-08 15:30 | 4.5 | 15.5 | 112.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-08 16:30 | 4.5 | 15.5 | 110 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-08 17:30 | 4.5 | 15.1 | 110 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-08 18:30 | 4.4 | 14.8 | 110 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-08 19:30 | 4.1 | 14.4 | 110 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-08 20:30 | 3.9 | 13.8 | 110 | 1490 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-12-08 21:30 | 3.9 | 13.1 | 110 | 1480 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-12-08 22:30 | 3.8 | 12.7 | 110 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-12-08 23:30 | 3.6 | 12.2 | 107.5 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-12-09 00:30 | 3.6 | 11.7 | 105 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-12-09 01:30 | 3.7 | 11.1 | 107.5 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-12-09 02:30 | 3.7 | 10.5 | 107.5 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-12-09 03:30 | 3.6 | 10.3 | 105 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-12-09 04:30 | 3.4 | 10.3 | 105 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-12-09 05:30 | 3.3 | 10.1 | 102.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-12-09 06:30 | 3.3 | 9.6 | 100 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-09 07:30 | 3.3 | 8.9 | 100 | 770 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-09 08:30 | 3.4 | 8.2 | 102.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-09 09:30 | 3.2 | 8 | 107.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-12-09 10:30 | 3.3 | 8 | 110 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-12-09 11:30 | 3.6 | 8 | 107.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-12-09 12:30 | 3.6 | 8.2 | 102.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-12-09 13:30 | 3.6 | 8.6 | 100 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-09 14:30 | 3.7 | 8.9 | 102.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-12-09 15:30 | 3.7 | 9 | 105 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-12-09 16:30 | 3.7 | 8.9 | 105 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-12-09 17:30 | 3.7 | 8.6 | 107.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-12-09 18:30 | 3.9 | 8.3 | 110 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-09 19:30 | 4.1 | 8 | 110 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-12-09 20:30 | 4.3 | 7.8 | 110 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-09 21:30 | 4.4 | 7.7 | 110 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-09 22:30 | 4.4 | 7.7 | 110 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-09 23:30 | 4.4 | 7.6 | 110 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-10 00:30 | 4.6 | 7.3 | 112.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-12-10 01:30 | 4.8 | 7.3 | 117.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-12-10 02:30 | 4.8 | 7.6 | 120 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-12-10 03:30 | 4.9 | 7.7 | 120 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-10 04:30 | 5 | 7.6 | 120 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-10 05:30 | 5.1 | 7.6 | 120 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-10 06:30 | 5.2 | 7.9 | 120 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-10 07:30 | 5.3 | 8.3 | 117.5 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-10 08:30 | 5.4 | 8.9 | 115 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-10 09:30 | 5.4 | 9.5 | 115 | 1025 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-10 10:30 | 5.5 | 10.1 | 117.5 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-10 11:30 | 5.7 | 11 | 125 | 1340 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-12-10 12:30 | 5.9 | 11.7 | 130 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-12-10 13:30 | 6 | 12.2 | 130 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-12-10 14:30 | 6.2 | 12.7 | 127.5 | 1470 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-12-10 15:30 | 6.3 | 12.7 | 122.5 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-12-10 16:30 | 6.5 | 12.5 | 120 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-12-10 17:30 | 6.7 | 12.7 | 122.5 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-12-10 18:30 | 6.8 | 12.9 | 127.5 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-12-10 19:30 | 7.1 | 12.9 | 130 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-12-10 20:30 | 7.1 | 13 | 130 | 1480 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-12-10 21:30 | 6.8 | 13.1 | 130 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-12-10 22:30 | 6.7 | 12.8 | 132.5 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-12-10 23:30 | 6.6 | 12.4 | 137.5 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-12-11 00:30 | 6.8 | 12.4 | 140 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-12-11 01:30 | 7.1 | 11.9 | 140 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-12-11 02:30 | 7.2 | 11.1 | 140 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-12-11 03:30 | 7.3 | 10.3 | 142.5 | 1150 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-12-11 04:30 | 7.4 | 9.5 | 147.5 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-11 05:30 | 7.7 | 9.5 | 150 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-12-11 06:30 | 7.9 | 9.6 | 150 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-12-11 07:30 | 8 | 9 | 147.5 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-11 08:30 | 8 | 8.6 | 142.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-12-11 09:30 | 8 | 9.5 | 140 | 1025 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-11 10:30 | 7.8 | 10.4 | 140 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-11 11:30 | 7.6 | 10.5 | 140 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-12-11 12:30 | 7.5 | 10.4 | 137.5 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-12-11 13:30 | 7.5 | 9.9 | 132.5 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-11 14:30 | 7.5 | 9.4 | 130 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-11 15:30 | 7.6 | 9.5 | 130 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-11 16:30 | 7.7 | 10.3 | 130 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-11 17:30 | 7.8 | 11 | 130 | 1340 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-12-11 18:30 | 7.8 | 11.6 | 130 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-12-11 19:30 | 7.8 | 12.4 | 130 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-12-11 20:30 | 7.7 | 13 | 130 | 1480 | 1465 | 1145 | 0 |  | 0 |  | 320
Lerwick | 1978-12-11 21:30 | 7.6 | 13.2 | 130 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-12-11 22:30 | 7.5 | 13.8 | 130 | 1490 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-12-11 23:30 | 7.3 | 14.7 | 130 | 1500 | 1495 | 1175 | 0 |  | 0 |  | 320
Lerwick | 1978-12-12 00:30 | 7 | 15.2 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-12 01:30 | 6.8 | 15 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-12 02:30 | 6.7 | 14.8 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-12 03:30 | 6.7 | 14.5 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-12 04:30 | 6.7 | 14.5 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-12 05:30 | 6.6 | 14.8 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-12 06:30 | 6.6 | 14.9 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-12 07:30 | 6.6 | 14.9 | 130 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-12 08:30 | 6.6 | 14.8 | 127.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-12 09:30 | 6.4 | 14.7 | 122.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-12 10:30 | 6.2 | 14.7 | 120 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-12 11:30 | 6.3 | 14.7 | 117.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-12 12:30 | 6.5 | 14.9 | 112.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-12 13:30 | 6.5 | 15.4 | 110 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-12 14:30 | 6.5 | 16.1 | 110 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-12 15:30 | 6.6 | 16.2 | 110 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-12 16:30 | 6.6 | 14.9 | 112.5 | 1500 | 1500 | 1180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-12 17:30 | 6.6 | 13.4 | 117.5 | 1480 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-12-12 18:30 | 6.8 | 12.7 | 120 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-12-12 19:30 | 7 | 12.2 | 120 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-12-12 20:30 | 6.9 | 11.7 | 117.5 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-12-12 21:30 | 6.8 | 11.7 | 112.5 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-12-12 22:30 | 6.8 | 12.2 | 110 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-12-12 23:30 | 6.9 | 12.4 | 107.5 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-12-13 00:30 | 6.7 | 12.7 | 102.5 | 1470 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-12-13 01:30 | 6.3 | 13.1 | 100 | 1480 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-12-13 02:30 | 6.2 | 12.8 | 100 | 1470 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-12-13 03:30 | 6.2 | 12.2 | 102.5 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-12-13 04:30 | 6 | 11.9 | 105 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-12-13 05:30 | 6 | 11.8 | 102.5 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-12-13 06:30 | 6.2 | 11.9 | 100 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-12-13 07:30 | 6.4 | 12 | 97.5 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-12-13 08:30 | 6.2 | 11.7 | 92.5 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-12-13 09:30 | 5.8 | 11.2 | 90 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-12-13 10:30 | 5.7 | 10.9 | 90 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-12-13 11:30 | 5.6 | 10.8 | 90 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-12-13 12:30 | 5.5 | 10.6 | 90 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-12-13 13:30 | 5.6 | 10.4 | 90 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-12-13 14:30 | 5.6 | 10.1 | 90 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-12-13 15:30 | 5.6 | 9.7 | 90 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-13 16:30 | 5.7 | 9.2 | 87.5 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-13 17:30 | 5.7 | 8.7 | 82.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-12-13 18:30 | 5.8 | 8.3 | 80 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-13 19:30 | 5.8 | 8 | 80 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-12-13 20:30 | 5.8 | 7.8 | 80 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-13 21:30 | 5.8 | 7.6 | 82.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-13 22:30 | 5.6 | 7.2 | 87.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-12-13 23:30 | 5.5 | 6.7 | 90 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-12-14 00:30 | 5.5 | 6.1 | 90 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-12-14 01:30 | 5.3 | 5.9 | 90 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-12-14 02:30 | 5.2 | 5.6 | 87.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-12-14 03:30 | 5 | 4.9 | 80 | 80 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-12-14 04:30 | 4.6 | 4.4 | 77.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-12-14 05:30 | 4.5 | 4.2 | 85 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-12-14 06:30 | 4.5 | 3.8 | 87.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-12-14 07:30 | 4.4 | 3.6 | 82.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-12-14 08:30 | 4.5 | 4 | 85 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-12-14 09:30 | 4.7 | 4.4 | 95 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-12-14 10:30 | 4.6 | 4.5 | 95 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-12-14 11:30 | 4.5 | 4.5 | 87.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-12-14 12:30 | 4.5 | 4.5 | 90 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-12-14 13:30 | 4.6 | 4.5 | 95 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-12-14 14:30 | 4.8 | 4.5 | 90 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-12-14 15:30 | 4.8 | 4.4 | 85 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-12-14 16:30 | 4.5 | 4.2 | 87.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-12-14 17:30 | 4.3 | 3.9 | 87.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-12-14 18:30 | 4.3 | 3.7 | 82.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-12-14 19:30 | 4.3 | 3.4 | 82.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-12-14 20:30 | 4.4 | 2.9 | 80 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-12-14 21:30 | 4.5 | 2 | 55 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-12-14 22:30 | 4.4 | 1.6 | 25 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-12-14 23:30 | 4.4 | 2.9 | 17.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-12-15 00:30 | 4.3 | 4.9 | 22.5 | 80 | 40 | 0 | 280 |  | 134.4 |  | 40
Lerwick | 1978-12-15 01:30 | 3.9 | 6.1 | 27.5 | 220 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-12-15 02:30 | 3.9 | 6.8 | 27.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-12-15 03:30 | 4.3 | 7.3 | 22.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-12-15 04:30 | 4.5 | 7.6 | 20 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-12-15 05:30 | 4.4 | 7.9 | 17.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-15 06:30 | 4.2 | 8.1 | 15 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-15 07:30 | 3.8 | 8.4 | 15 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-12-15 08:30 | 3.3 | 9 | 12.5 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-15 09:30 | 3.1 | 9.3 | 10 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-12-15 10:30 | 3.3 | 9.1 | 7.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-12-15 11:30 | 3 | 8.7 | 2.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-12-15 12:30 | 2.7 | 8.2 | 0 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-15 13:30 | 2.4 | 8 | 177.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-12-15 14:30 | 2.4 | 8 | 355 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-12-15 15:30 | 2.1 | 7.8 | 177.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-15 16:30 | 1.9 | 7.8 | 0 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-15 17:30 | 2.3 | 7.6 | 0 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-15 18:30 | 2.3 | 6.7 | 0 | 300 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-12-15 19:30 | 2.5 | 6.2 | 0 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-12-15 20:30 | 2.6 | 6.3 | 177.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-12-15 21:30 | 2.2 | 6.5 | 352.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-12-15 22:30 | 1.4 | 6.3 | 352.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-12-15 23:30 | 1.7 | 5.6 | 352.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-12-16 00:30 | 2.5 | 5.2 | 347.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-12-16 01:30 | 2.3 | 4.4 | 342.5 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-12-16 02:30 | 2.1 | 3.5 | 327.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-12-16 03:30 | 2 | 3.2 | 307.5 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-12-16 04:30 | 2.2 | 3.6 | 297.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-12-16 05:30 | 2.4 | 3.9 | 295 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-12-16 06:30 | 2.1 | 3.9 | 297.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-12-16 07:30 | 1.5 | 3.9 | 302.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-12-16 08:30 | 1.5 | 4 | 307.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-12-16 09:30 | 1.5 | 4 | 307.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-12-16 10:30 | 1.6 | 4 | 305 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-12-16 11:30 | 2.2 | 4.2 | 312.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-12-16 12:30 | 2.2 | 5.3 | 327.5 | 110 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-12-16 13:30 | 1.8 | 6.9 | 340 | 300 | 205 | 0 | 115 |  | 55.2 |  | 205
Lerwick | 1978-12-16 14:30 | 1.4 | 7.9 | 342.5 | 500 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-12-16 15:30 | 1.4 | 8.3 | 335 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-16 16:30 | 1.7 | 8.6 | 330 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-16 17:30 | 1.5 | 8.6 | 335 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-12-16 18:30 | 1.1 | 8.6 | 347.5 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-12-16 19:30 | 1.4 | 9.1 | 177.5 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-12-16 20:30 | 1.7 | 9.4 | 0 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-12-16 21:30 | 1.5 | 8.9 | 177.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-12-16 22:30 | 1.4 | 8.2 | 355 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-16 23:30 | 0.7 | 8 | 355 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-12-17 00:30 | 0.1 | 8 | 355 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-12-17 01:30 | 0.2 | 7.3 | 355 | 400 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-17 02:30 | 0.7 | 6.2 | 350 | 220 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-12-17 03:30 | 0.8 | 5.3 | 340 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-12-17 04:30 | 0.5 | 4.7 | 335 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-12-17 05:30 | 0.5 | 4 | 335 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-12-17 06:30 | 0.5 | 3.3 | 327.5 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-12-17 07:30 | 0.5 | 2.8 | 315 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-12-17 08:30 | 0.7 | 1.8 | 322.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-12-17 09:30 | 0.7 | 0.5 | 167.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-12-17 10:30 | 0.2 | 0 | 0 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-12-17 11:30 | 0 | 0.5 | 137.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-12-17 12:30 | 1.1 | 1.8 | 235 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-12-17 13:30 | 1.6 | 3.3 | 197.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-12-17 14:30 | 1.5 | 3.9 | 200 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-12-17 15:30 | 1.9 | 4.2 | 202.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-12-17 16:30 | 2.1 | 5.2 | 212.5 | 110 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-12-17 17:30 | 2.4 | 5.9 | 222.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-12-17 18:30 | 2.6 | 5.6 | 222.5 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-12-17 19:30 | 2.5 | 6 | 217.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-12-17 20:30 | 2.9 | 7.6 | 212.5 | 500 | 360 | 40 | 0 |  | 0 |  | 320
Lerwick | 1978-12-17 21:30 | 3.4 | 8.7 | 210 | 770 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-12-17 22:30 | 3.6 | 9.1 | 212.5 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-12-17 23:30 | 3.9 | 9.8 | 217.5 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-18 00:30 | 4.2 | 10.6 | 220 | 1270 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-18 01:30 | 4.6 | 11.1 | 220 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-12-18 02:30 | 4.9 | 11.1 | 220 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-12-18 03:30 | 4.9 | 10.9 | 220 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-12-18 04:30 | 4.8 | 10.6 | 220 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-12-18 05:30 | 5.2 | 10.5 | 220 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-12-18 06:30 | 5.5 | 10.7 | 220 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-12-18 07:30 | 5.6 | 11.1 | 217.5 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-12-18 08:30 | 5.6 | 11.4 | 212.5 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-12-18 09:30 | 5.6 | 11.5 | 210 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-12-18 10:30 | 5.8 | 11.5 | 210 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-12-18 11:30 | 6.1 | 11.6 | 212.5 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-12-18 12:30 | 6.3 | 11.8 | 215 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-12-18 13:30 | 6.5 | 11.8 | 212.5 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-12-18 14:30 | 6.6 | 11.6 | 210 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-12-18 15:30 | 6.6 | 11.5 | 210 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-12-18 16:30 | 6.6 | 11.6 | 210 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-12-18 17:30 | 6.6 | 11.9 | 210 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-12-18 18:30 | 6.6 | 12 | 210 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-12-18 19:30 | 6.6 | 11.9 | 210 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-12-18 20:30 | 6.7 | 11.4 | 210 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-12-18 21:30 | 6.7 | 9.9 | 207.5 | 1025 | 1182.5 | 862.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-18 22:30 | 6.4 | 7.9 | 202.5 | 500 | 762.5 | 442.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-18 23:30 | 6 | 6.4 | 200 | 220 | 360 | 40 | 0 |  | 0 |  | 320
Lerwick | 1978-12-19 00:30 | 5.9 | 5.4 | 197.5 | 110 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-12-19 01:30 | 5.8 | 4.7 | 192.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-12-19 02:30 | 5.3 | 4.7 | 192.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-12-19 03:30 | 4.7 | 5.3 | 197.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-12-19 04:30 | 3.9 | 5.5 | 197.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-12-19 05:30 | 3.4 | 5.2 | 195 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-12-19 06:30 | 3.3 | 4.7 | 195 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-12-19 07:30 | 3.4 | 4 | 195 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-12-19 08:30 | 3.5 | 3.8 | 200 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-12-19 09:30 | 3.5 | 4.4 | 207.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-12-19 10:30 | 3.6 | 4.9 | 207.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-12-19 11:30 | 4.2 | 5 | 202.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-12-19 12:30 | 5.2 | 4.9 | 202.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-12-19 13:30 | 5.4 | 4.7 | 205 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-12-19 14:30 | 5.2 | 4.7 | 202.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-12-19 15:30 | 4.9 | 5 | 202.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-12-19 16:30 | 5.2 | 4.7 | 207.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-12-19 17:30 | 5.3 | 4.6 | 207.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-12-19 18:30 | 5.4 | 4.9 | 205 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-12-19 19:30 | 5.8 | 4.7 | 200 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-12-19 20:30 | 5.7 | 4.7 | 192.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-12-19 21:30 | 5.3 | 5 | 192.5 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-12-19 22:30 | 5.2 | 4.5 | 192.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-12-19 23:30 | 5 | 4 | 187.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-12-20 00:30 | 4.5 | 4.2 | 185 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-12-20 01:30 | 4.3 | 4.6 | 182.5 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-12-20 02:30 | 4.2 | 4.9 | 180 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-12-20 03:30 | 4.7 | 4.9 | 180 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-12-20 04:30 | 5.6 | 5.1 | 175 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-12-20 05:30 | 5.8 | 5.5 | 170 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-12-20 06:30 | 5.8 | 5.7 | 170 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-12-20 07:30 | 5.7 | 5.7 | 170 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-12-20 08:30 | 5.6 | 5.8 | 170 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-12-20 09:30 | 5.6 | 6.3 | 170 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-12-20 10:30 | 5.5 | 6.5 | 172.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-12-20 11:30 | 5.5 | 5.6 | 182.5 | 150 | 225 | 0 | 95 |  | 45.6 |  | 225
Lerwick | 1978-12-20 12:30 | 5.5 | 4.1 | 195 | 60 | 105 | 0 | 215 |  | 103.2 |  | 105
Lerwick | 1978-12-20 13:30 | 4.9 | 3.3 | 195 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-12-20 14:30 | 4 | 3.6 | 185 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-12-20 15:30 | 4.3 | 3.6 | 185 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-12-20 16:30 | 5 | 3.2 | 190 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-12-20 17:30 | 4.7 | 3.5 | 180 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-12-20 18:30 | 4.7 | 4.4 | 162.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-12-20 19:30 | 5 | 4.7 | 150 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-12-20 20:30 | 5.2 | 4.5 | 142.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-12-20 21:30 | 5.4 | 4.7 | 140 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-12-20 22:30 | 5.4 | 5 | 140 | 110 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-12-20 23:30 | 5.4 | 5.3 | 137.5 | 110 | 110 | 0 | 210 |  | 100.8 |  | 110
Lerwick | 1978-12-21 00:30 | 5.5 | 5.8 | 135 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-12-21 01:30 | 5.3 | 6 | 137.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-12-21 02:30 | 5 | 6.3 | 132.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-12-21 03:30 | 4.7 | 6 | 117.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-12-21 04:30 | 4.5 | 5.8 | 110 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-12-21 05:30 | 4.5 | 6.4 | 110 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-12-21 06:30 | 4.6 | 7.2 | 107.5 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-12-21 07:30 | 4.5 | 7.6 | 100 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-12-21 08:30 | 4.3 | 7.7 | 97.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-21 09:30 | 4.4 | 7.8 | 105 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-21 10:30 | 4.6 | 8.2 | 110 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-21 11:30 | 4.6 | 9 | 110 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-21 12:30 | 4.7 | 9.6 | 107.5 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-21 13:30 | 4.7 | 9.4 | 102.5 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-21 14:30 | 4.3 | 8.9 | 100 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-12-21 15:30 | 4.1 | 8.6 | 100 | 770 | 770 | 450 | 0 |  | 0 |  | 320
Lerwick | 1978-12-21 16:30 | 4.3 | 8.3 | 102.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-21 17:30 | 4.6 | 8 | 105 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-12-21 18:30 | 4.4 | 7.6 | 102.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-21 19:30 | 4.1 | 6.8 | 102.5 | 300 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-12-21 20:30 | 3.9 | 6.4 | 105 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-12-21 21:30 | 3.8 | 6.4 | 97.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-12-21 22:30 | 4 | 6.3 | 87.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-12-21 23:30 | 4.3 | 5.9 | 87.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-12-22 00:30 | 4.4 | 5.3 | 90 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-12-22 01:30 | 4.4 | 4.9 | 95 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-12-22 02:30 | 4.4 | 4.4 | 105 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-12-22 03:30 | 4.5 | 3.9 | 110 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-12-22 04:30 | 4.2 | 3.9 | 112.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-12-22 05:30 | 4.2 | 3.8 | 115 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-12-22 06:30 | 4.4 | 3.6 | 112.5 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-12-22 07:30 | 4.4 | 4 | 110 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-12-22 08:30 | 4.6 | 4.4 | 112.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-12-22 09:30 | 4.8 | 4.2 | 117.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-12-22 10:30 | 4.7 | 4.2 | 115 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-12-22 11:30 | 4.5 | 4.4 | 105 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-12-22 12:30 | 4.4 | 4.4 | 100 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-12-22 13:30 | 4.1 | 4.4 | 97.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-12-22 14:30 | 4 | 4.6 | 95 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-12-22 15:30 | 4 | 4.7 | 97.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-12-22 16:30 | 3.8 | 4.2 | 100 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-12-22 17:30 | 3.7 | 4.2 | 97.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-12-22 18:30 | 3.9 | 4.7 | 95 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-12-22 19:30 | 3.6 | 4.7 | 97.5 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-12-22 20:30 | 3.6 | 4.5 | 100 | 80 | 80 | 0 | 240 |  | 115.2 |  | 80
Lerwick | 1978-12-22 21:30 | 3.9 | 4.4 | 102.5 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-12-22 22:30 | 3.9 | 4.2 | 107.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-12-22 23:30 | 3.8 | 4.2 | 112.5 | 60 | 60 | 0 | 260 |  | 124.8 |  | 60
Lerwick | 1978-12-23 00:30 | 3.7 | 3.7 | 90 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-12-23 01:30 | 3 | 2.4 | 40 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-12-23 02:30 | 2 | 2.2 | 25 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-12-23 03:30 | 2.1 | 3.1 | 47.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-12-23 04:30 | 2.9 | 3.6 | 77.5 | 25 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-12-23 05:30 | 3.4 | 3.4 | 110 | 0 | 12.5 | 0 | 307.5 |  | 147.6 |  | 12.5
Lerwick | 1978-12-23 06:30 | 3.6 | 2.9 | 125 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-12-23 07:30 | 3.4 | 2.6 | 102.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-12-23 08:30 | 3.3 | 2.4 | 50 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-12-23 09:30 | 3 | 1.7 | 15 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-12-23 10:30 | 2.3 | 1.3 | 15 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-12-23 11:30 | 2.1 | 1.5 | 30 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-12-23 12:30 | 2.1 | 2.7 | 57.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-12-23 13:30 | 2.1 | 5 | 80 | 110 | 55 | 0 | 265 |  | 127.2 |  | 55
Lerwick | 1978-12-23 14:30 | 2.4 | 7.2 | 82.5 | 400 | 255 | 0 | 65 |  | 31.2 |  | 255
Lerwick | 1978-12-23 15:30 | 2.5 | 8.4 | 80 | 635 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-23 16:30 | 2.9 | 9.1 | 77.5 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-23 17:30 | 3.5 | 9.1 | 80 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-12-23 18:30 | 2.8 | 8.4 | 92.5 | 635 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-23 19:30 | 2.3 | 7.3 | 102.5 | 400 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-23 20:30 | 1.9 | 5.8 | 107.5 | 150 | 275 | 0 | 45 |  | 21.6 |  | 275
Lerwick | 1978-12-23 21:30 | 1.9 | 5.2 | 107.5 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-12-23 22:30 | 2.5 | 5.9 | 102.5 | 150 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-12-23 23:30 | 2.5 | 7 | 102.5 | 400 | 275 | 0 | 45 |  | 21.6 |  | 275
Lerwick | 1978-12-24 00:30 | 2.6 | 7.9 | 107.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-12-24 01:30 | 2.7 | 8.1 | 110 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-24 02:30 | 2.7 | 8.4 | 107.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-12-24 03:30 | 2.6 | 9.1 | 102.5 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-24 04:30 | 2.1 | 9.7 | 100 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-24 05:30 | 2.2 | 10.2 | 102.5 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-24 06:30 | 2.8 | 10.7 | 107.5 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-12-24 07:30 | 3 | 11.2 | 110 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-12-24 08:30 | 3 | 11.7 | 110 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-12-24 09:30 | 2.8 | 12.4 | 110 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-12-24 10:30 | 2.7 | 13.4 | 107.5 | 1480 | 1465 | 1145 | 0 |  | 0 |  | 320
Lerwick | 1978-12-24 11:30 | 2.7 | 13.9 | 105 | 1490 | 1485 | 1165 | 0 |  | 0 |  | 320
Lerwick | 1978-12-24 12:30 | 2.5 | 13.5 | 107.5 | 1490 | 1490 | 1170 | 0 |  | 0 |  | 320
Lerwick | 1978-12-24 13:30 | 2.3 | 12.8 | 110 | 1470 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-12-24 14:30 | 2.3 | 12.5 | 110 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-12-24 15:30 | 2.1 | 12.5 | 110 | 1470 | 1470 | 1150 | 0 |  | 0 |  | 320
Lerwick | 1978-12-24 16:30 | 1.9 | 12.4 | 107.5 | 1450 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-12-24 17:30 | 2.1 | 12.4 | 102.5 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-12-24 18:30 | 2.2 | 12.4 | 100 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-12-24 19:30 | 2 | 12.2 | 100 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-12-24 20:30 | 2 | 11.7 | 97.5 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-12-24 21:30 | 2 | 11.4 | 92.5 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-12-24 22:30 | 1.5 | 11.4 | 90 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-12-24 23:30 | 1.6 | 11.5 | 90 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-12-25 00:30 | 2.2 | 11.2 | 90 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-12-25 01:30 | 2.3 | 10.7 | 90 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-12-25 02:30 | 2.4 | 10.1 | 90 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-12-25 03:30 | 2.3 | 9.4 | 87.5 | 900 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-12-25 04:30 | 2.1 | 8.5 | 82.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-12-25 05:30 | 2.1 | 7.8 | 80 | 500 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-12-25 06:30 | 2.2 | 7.2 | 80 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-12-25 07:30 | 2.1 | 6.8 | 80 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-12-25 08:30 | 2.1 | 6.4 | 82.5 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-12-25 09:30 | 2.1 | 5.9 | 90 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-12-25 10:30 | 2.3 | 5.7 | 100 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-12-25 11:30 | 2.3 | 5.3 | 105 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-12-25 12:30 | 2.1 | 4.4 | 105 | 60 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-12-25 13:30 | 2 | 3.7 | 102.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-12-25 14:30 | 1.6 | 3.8 | 90 | 25 | 25 | 0 | 295 |  | 141.6 |  | 25
Lerwick | 1978-12-25 15:30 | 1.5 | 4.2 | 72.5 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-12-25 16:30 | 1.8 | 4.7 | 65 | 80 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-12-25 17:30 | 1.8 | 5.6 | 65 | 150 | 115 | 0 | 205 |  | 98.4 |  | 115
Lerwick | 1978-12-25 18:30 | 2 | 6.4 | 62.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-12-25 19:30 | 1.8 | 6.5 | 62.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-12-25 20:30 | 1.4 | 6.3 | 65 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-12-25 21:30 | 1.2 | 6.2 | 62.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-12-25 22:30 | 1.2 | 6.4 | 62.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-12-25 23:30 | 1.5 | 6.9 | 67.5 | 300 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-12-26 00:30 | 1.6 | 7.2 | 70 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-12-26 01:30 | 1.6 | 7.1 | 70 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-12-26 02:30 | 1.7 | 6.8 | 67.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-12-26 03:30 | 1.8 | 6.7 | 62.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-12-26 04:30 | 1.9 | 6.8 | 62.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-12-26 05:30 | 2 | 6.8 | 70 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-12-26 06:30 | 2 | 6.4 | 75 | 220 | 260 | 0 | 60 |  | 28.8 |  | 260
Lerwick | 1978-12-26 07:30 | 2.1 | 6.2 | 70 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-12-26 08:30 | 2.1 | 6.3 | 62.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-12-26 09:30 | 1.8 | 6.3 | 62.5 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-12-26 10:30 | 1.9 | 5.9 | 65 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-12-26 11:30 | 2.3 | 5.8 | 65 | 150 | 150 | 0 | 170 |  | 81.6 |  | 150
Lerwick | 1978-12-26 12:30 | 2.6 | 6 | 67.5 | 220 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-12-26 13:30 | 2.6 | 6 | 70 | 220 | 220 | 0 | 100 |  | 48 |  | 220
Lerwick | 1978-12-26 14:30 | 2.5 | 5.8 | 67.5 | 150 | 185 | 0 | 135 |  | 64.8 |  | 185
Lerwick | 1978-12-26 15:30 | 2.5 | 5.3 | 65 | 110 | 130 | 0 | 190 |  | 91.2 |  | 130
Lerwick | 1978-12-26 16:30 | 2.4 | 4.7 | 62.5 | 80 | 95 | 0 | 225 |  | 108 |  | 95
Lerwick | 1978-12-26 17:30 | 2.4 | 4.2 | 55 | 60 | 70 | 0 | 250 |  | 120 |  | 70
Lerwick | 1978-12-26 18:30 | 2.4 | 3.7 | 47.5 | 25 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-12-26 19:30 | 2.4 | 4 | 40 | 60 | 42.5 | 0 | 277.5 |  | 133.2 |  | 42.5
Lerwick | 1978-12-26 20:30 | 2.5 | 5.1 | 35 | 110 | 85 | 0 | 235 |  | 112.8 |  | 85
Lerwick | 1978-12-26 21:30 | 2.7 | 6.3 | 37.5 | 220 | 165 | 0 | 155 |  | 74.4 |  | 165
Lerwick | 1978-12-26 22:30 | 2.7 | 7.3 | 40 | 400 | 310 | 0 | 10 |  | 4.8 |  | 310
Lerwick | 1978-12-26 23:30 | 2.6 | 7.9 | 40 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-12-27 00:30 | 2.4 | 8.5 | 42.5 | 770 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-12-27 01:30 | 2.3 | 9.1 | 47.5 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-12-27 02:30 | 2.4 | 9.4 | 47.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-12-27 03:30 | 2.2 | 9.7 | 42.5 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-27 04:30 | 2.2 | 10 | 42.5 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-27 05:30 | 2.3 | 9.6 | 47.5 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-27 06:30 | 2.3 | 8.9 | 47.5 | 770 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-27 07:30 | 2.3 | 8.3 | 45 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-27 08:30 | 1.7 | 8 | 47.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-12-27 09:30 | 1.1 | 8 | 47.5 | 635 | 635 | 315 | 0 |  | 0 |  | 320
Lerwick | 1978-12-27 10:30 | 1.2 | 7.8 | 42.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-27 11:30 | 1.5 | 7.2 | 45 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-12-27 12:30 | 1.5 | 6.9 | 50 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-12-27 13:30 | 1.5 | 7.4 | 45 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-12-27 14:30 | 1.4 | 7.8 | 37.5 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-12-27 15:30 | 1.5 | 8.2 | 35 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-27 16:30 | 1.6 | 8.6 | 35 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-27 17:30 | 1.4 | 9.1 | 32.5 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-12-27 18:30 | 1.4 | 9.5 | 30 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-27 19:30 | 1 | 9.4 | 30 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-27 20:30 | 0.9 | 9.4 | 30 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-12-27 21:30 | 1.4 | 9.4 | 35 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-12-27 22:30 | 0.7 | 9.4 | 45 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-12-27 23:30 | 0 | 9.4 | 50 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-12-28 00:30 | 0 | 9 | 50 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-12-28 01:30 | 0 | 8.9 | 47.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-12-28 02:30 | 0.1 | 9 | 42.5 | 900 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-12-28 03:30 | 0.4 | 9.6 | 40 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-28 04:30 | 0.3 | 10 | 45 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-28 05:30 | 0.2 | 8.7 | 47.5 | 770 | 960 | 640 | 0 |  | 0 |  | 320
Lerwick | 1978-12-28 06:30 | 0 | 7.3 | 35 | 400 | 585 | 265 | 0 |  | 0 |  | 320
Lerwick | 1978-12-28 07:30 | -0.2 | 7.2 | 27.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-12-28 08:30 | 0.1 | 8 | 45 | 635 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-28 09:30 | 0.4 | 8.9 | 62.5 | 770 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-28 10:30 | 0.2 | 9.9 | 55 | 1025 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-28 11:30 | -0.1 | 10.7 | 45 | 1270 | 1147.5 | 827.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-28 12:30 | -0.3 | 10.5 | 50 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-12-28 13:30 | -0.7 | 9.4 | 55 | 900 | 1085 | 765 | 0 |  | 0 |  | 320
Lerwick | 1978-12-28 14:30 | -0.4 | 9.4 | 50 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-12-28 15:30 | -0.1 | 10.1 | 40 | 1150 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-12-28 16:30 | -0.1 | 9.8 | 37.5 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-28 17:30 | 0.1 | 9.4 | 45 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-28 18:30 | 0 | 10 | 52.5 | 1150 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-12-28 19:30 | 0.1 | 11 | 57.5 | 1340 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-12-28 20:30 | -0.1 | 11.4 | 55 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-12-28 21:30 | -0.6 | 11.4 | 45 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-12-28 22:30 | -0.4 | 11.7 | 40 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-12-28 23:30 | -0.5 | 12 | 42.5 | 1450 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-12-29 00:30 | -1.5 | 12 | 45 | 1450 | 1450 | 1130 | 0 |  | 0 |  | 320
Lerwick | 1978-12-29 01:30 | -1.6 | 11.9 | 47.5 | 1400 | 1425 | 1105 | 0 |  | 0 |  | 320
Lerwick | 1978-12-29 02:30 | -1.5 | 11.3 | 52.5 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-12-29 03:30 | -1.9 | 10.4 | 50 | 1150 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-12-29 04:30 | -1.7 | 10 | 42.5 | 1150 | 1150 | 830 | 0 |  | 0 |  | 320
Lerwick | 1978-12-29 05:30 | -1.5 | 9.6 | 45 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-29 06:30 | -2 | 8.9 | 52.5 | 770 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-29 07:30 | -2.3 | 8.3 | 42.5 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-29 08:30 | -2 | 7.4 | 22.5 | 400 | 517.5 | 197.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-29 09:30 | -1.9 | 5.8 | 40 | 150 | 275 | 0 | 45 |  | 21.6 |  | 275
Lerwick | 1978-12-29 10:30 | -2.1 | 4.3 | 105 | 60 | 105 | 0 | 215 |  | 103.2 |  | 105
Lerwick | 1978-12-29 11:30 | -1.9 | 3.1 | 172.5 | 0 | 30 | 0 | 290 |  | 139.2 |  | 30
Lerwick | 1978-12-29 12:30 | -1.9 | 2.6 | 212.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-12-29 13:30 | -2.5 | 2.3 | 240 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-12-29 14:30 | -3.3 | 1.9 | 247.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-12-29 15:30 | -3.4 | 2 | 222.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-12-29 16:30 | -3.2 | 2.9 | 202.5 | 0 | 0 | 0 | 320 |  | 153.6 |  | 0
Lerwick | 1978-12-29 17:30 | -3.2 | 4.5 | 187.5 | 80 | 40 | 0 | 280 |  | 134.4 |  | 40
Lerwick | 1978-12-29 18:30 | -2.6 | 6.5 | 170 | 300 | 190 | 0 | 130 |  | 62.4 |  | 190
Lerwick | 1978-12-29 19:30 | -1.9 | 8.5 | 165 | 770 | 535 | 215 | 0 |  | 0 |  | 320
Lerwick | 1978-12-29 20:30 | -1.9 | 9.5 | 162.5 | 1025 | 897.5 | 577.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-29 21:30 | -2.1 | 10 | 160 | 1150 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-29 22:30 | -1.7 | 10.5 | 160 | 1270 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-12-29 23:30 | -1.5 | 10.8 | 157.5 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-12-30 00:30 | -2 | 10.8 | 152.5 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-12-30 01:30 | -1.7 | 10.8 | 150 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-12-30 02:30 | -1.5 | 10.9 | 150 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-12-30 03:30 | -1.9 | 11.2 | 150 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-12-30 04:30 | -1.6 | 11.4 | 150 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-12-30 05:30 | -1.2 | 11.4 | 150 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-12-30 06:30 | -1.2 | 11.6 | 150 | 1400 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-12-30 07:30 | -1.2 | 11.5 | 150 | 1400 | 1400 | 1080 | 0 |  | 0 |  | 320
Lerwick | 1978-12-30 08:30 | -1.3 | 11.1 | 150 | 1340 | 1370 | 1050 | 0 |  | 0 |  | 320
Lerwick | 1978-12-30 09:30 | -1.8 | 10.9 | 150 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-12-30 10:30 | -1.9 | 10.9 | 150 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-12-30 11:30 | -1.4 | 11.1 | 150 | 1340 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-12-30 12:30 | -1.1 | 11.1 | 150 | 1340 | 1340 | 1020 | 0 |  | 0 |  | 320
Lerwick | 1978-12-30 13:30 | -1.1 | 10.9 | 152.5 | 1270 | 1305 | 985 | 0 |  | 0 |  | 320
Lerwick | 1978-12-30 14:30 | -1.2 | 10.8 | 157.5 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-12-30 15:30 | -1.4 | 10.6 | 160 | 1270 | 1270 | 950 | 0 |  | 0 |  | 320
Lerwick | 1978-12-30 16:30 | -1.6 | 10.2 | 160 | 1150 | 1210 | 890 | 0 |  | 0 |  | 320
Lerwick | 1978-12-30 17:30 | -1.9 | 9.9 | 157.5 | 1025 | 1087.5 | 767.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-30 18:30 | -2.2 | 9.6 | 152.5 | 1025 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-12-30 19:30 | -2.2 | 9.4 | 150 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-30 20:30 | -2 | 9.4 | 152.5 | 900 | 900 | 580 | 0 |  | 0 |  | 320
Lerwick | 1978-12-30 21:30 | -2.1 | 9.5 | 157.5 | 1025 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-30 22:30 | -2.3 | 9.2 | 155 | 900 | 962.5 | 642.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-30 23:30 | -2.5 | 8.7 | 147.5 | 770 | 835 | 515 | 0 |  | 0 |  | 320
Lerwick | 1978-12-31 00:30 | -2.4 | 8.2 | 145 | 635 | 702.5 | 382.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-31 01:30 | -2.2 | 7.7 | 142.5 | 500 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-31 02:30 | -2.6 | 7.1 | 142.5 | 400 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-12-31 03:30 | -3.1 | 6.5 | 147.5 | 300 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-12-31 04:30 | -3.3 | 6.7 | 152.5 | 300 | 300 | 0 | 20 |  | 9.6 |  | 300
Lerwick | 1978-12-31 05:30 | -3.4 | 7.1 | 157.5 | 400 | 350 | 30 | 0 |  | 0 |  | 320
Lerwick | 1978-12-31 06:30 | -3.7 | 7.1 | 157.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-12-31 07:30 | -3.7 | 7.1 | 152.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-12-31 08:30 | -3.5 | 7.3 | 152.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-12-31 09:30 | -3.5 | 7.3 | 157.5 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-12-31 10:30 | -3.7 | 7.4 | 160 | 400 | 400 | 80 | 0 |  | 0 |  | 320
Lerwick | 1978-12-31 11:30 | -3.6 | 7.8 | 160 | 500 | 450 | 130 | 0 |  | 0 |  | 320
Lerwick | 1978-12-31 12:30 | -3.2 | 7.7 | 162.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-31 13:30 | -3.1 | 7.5 | 167.5 | 500 | 500 | 180 | 0 |  | 0 |  | 320
Lerwick | 1978-12-31 14:30 | -3.1 | 8 | 170 | 635 | 567.5 | 247.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-31 15:30 | -2.9 | 9.1 | 167.5 | 900 | 767.5 | 447.5 | 0 |  | 0 |  | 320
Lerwick | 1978-12-31 16:30 | -3.1 | 10.3 | 162.5 | 1150 | 1025 | 705 | 0 |  | 0 |  | 320
Lerwick | 1978-12-31 17:30 | -3.3 | 11.3 | 157.5 | 1340 | 1245 | 925 | 0 |  | 0 |  | 320
Lerwick | 1978-12-31 18:30 | -3 | 12.1 | 155 | 1450 | 1395 | 1075 | 0 |  | 0 |  | 320
Lerwick | 1978-12-31 19:30 | -2.9 | 12.6 | 155 | 1470 | 1460 | 1140 | 0 |  | 0 |  | 320
Lerwick | 1978-12-31 20:30 | -3.1 | 13.1 | 152.5 | 1480 | 1475 | 1155 | 0 |  | 0 |  | 320
Lerwick | 1978-12-31 21:30 | -3.2 | 13.2 | 150 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-12-31 22:30 | -3.3 | 13.1 | 150 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Lerwick | 1978-12-31 23:30 | -2.9 | 13.2 | 150 | 1480 | 1480 | 1160 | 0 |  | 0 |  | 320
Note on C14: Kati Svehla: Note: accounting for internal use of gas in the AD plant is covered in the biogas page
Note on C18: Kati Svehla: manual input depending on turbine
Note on C19: Kati Svehla: manual input depending on turbine
Note on I13: Kati Svehla: Exactly 320kWh

## Wind turbine characteristics
Wind Power Calculations
Turbine characteristics
Wind speed | Vestas V52-850 | Vestas 2.0 MW | Vestas 112-3.0 MW | GE 1.5MW sle | Siemens SWT-2.3-101
m/s | kW | kW | kW | kW | kW
0 | 0 | 0 | 0 | 0 | 0
0.5 | 0 | 0 | 0 | 0 | 0
1 | 0 | 0 | 0 | 0 | 0
1.5 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0
2.5 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 50 | 0 | 0
3.5 | 0 | 0 | 130 | 25 | 0
4 | 20 | 50 | 200 | 60 | 38.3333
4.5 | 50 | 90 | 250 | 80 | 99.6667
5 | 70 | 100 | 320 | 110 | 170
5.5 | 100 | 135 | 420 | 150 | 250
6 | 120 | 200 | 540 | 220 | 380
6.5 | 160 | 300 | 720 | 300 | 560
7 | 195 | 400 | 900 | 400 | 740
7.5 | 250 | 516.5 | 1200 | 500 | 920
8 | 295 | 633 | 1500 | 635 | 1100
8.5 | 340 | 749.5 | 1800 | 770 | 1280
9 | 385 | 866 | 2100 | 900 | 1460
9.5 | 430 | 982.5 | 2400 | 1025 | 1640
10 | 475 | 1099 | 2650 | 1150 | 1820
10.5 | 520 | 1215.5 | 2800 | 1270 | 2000
11 | 565 | 1332 | 2870 | 1340 | 2150
11.5 | 610 | 1448.5 | 2950 | 1400 | 2236.1111
12 | 655 | 1565 | 3000 | 1450 | 2268.0556
12.5 | 700 | 1681.5 | 3000 | 1470 | 2300
13 | 750 | 1798 | 3000 | 1480 | 2300
13.5 | 770 | 1860 | 3000 | 1490 | 2300
14 | 795 | 1920 | 3000 | 1500 | 2300
14.5 | 815 | 1950 | 3000 | 1500 | 2300
15 | 825 | 1970 | 3000 | 1500 | 2300
15.5 | 840 | 1985 | 3000 | 1500 | 2300
16 | 850 | 2000 | 3000 | 1500 | 2300
16.5 | 850 | 2000 | 3000 | 1500 | 2300
17 | 850 | 2000 | 3000 | 1500 | 2300
17.5 | 850 | 2000 | 3000 | 1500 | 2300
18 | 850 | 2000 | 3000 | 1500 | 2300
18.5 | 850 | 2000 | 3000 | 1500 | 2300
19 | 850 | 2000 | 3000 | 1500 | 2300
19.5 | 850 | 2000 | 3000 | 1500 | 2300
20 | 850 | 2000 | 3000 | 1500 | 2300
20.5 | 850 | 2000 | 3000 | 1500 | 2300
21 | 850 | 2000 | 3000 | 1500 | 2300
21.5 | 850 | 2000 | 3000 | 1500 | 2300
22 | 850 | 2000 | 3000 | 1500 | 2300
22.5 | 850 | 2000 | 3000 | 1500 | 2300
23 | 850 | 2000 | 3000 | 1500 | 2300
23.5 | 850 | 2000 | 3000 | 1500 | 2300
24 | 850 | 2000 | 3000 | 1500 | 2300
24.5 | 850 | 2000 | 3000 | 1500 | 2300
25 | 850 | 2000 | 3000 | 1500 | 2300
25.5 | 0 | 0 | 0 | 0 | 0
26 | 0 | 0 | 0 | 0 | 0
26.5 | 0 | 0 | 0 | 0 | 0
27 | 0 | 0 | 0 | 0 | 0
27.5 | 0 | 0 | 0 | 0 | 0
27.5 | 0 | 0 | 0 | 0 | 0
Source: |  | (1) | Vestas 2.0 MW |  | brochure
|  | (2) | Vestas 112-3.0 MW
|  | (3) | Siemens SWT-2.3-101
all access checked on 27 March
|  | (4) | Vestas V52-850
|  | (5) | GE 1.5MW sle
all access checked on 13 April
Note on F6: Kati Svehla: This column is deduced from GE2.5 as wind speed characteristics are not on brochure