## Summary
Wind Power Calculations
Summary
Lerwick
Summary outputs from various turbines
|  | 320 | kW Data centre demand
Turbine | Total | Supply / demand | Excess Supply | Excess Demand | Net excess | Net excess
| kWh |  | kWh | kWh | kWh | days
V2.0 | 5198938.5 | 1.8546 | 3401691 | 1020863.5 | -567740.0556 | -33.266
V112-30 | 10867860 | 3.8769 | 8614440 | 548280 | 3088820 | 180.9855
GE3.6 | 9962925 | 3.5541 | 7903060 | 741585 | 2303563.3333 | 134.9744
GE2.5 | 8910954.7222 | 3.1789 | 6814062.0833 | 705057.3611 | 1840236.9059 | 107.8264
SWT-2.3-101 | 7827207.5 | 2.7922 | 5890620 | 866612.5 | 1019504.4444 | 59.7366
Longest continuous period with storage drawdown |  |  |  |  | 4.1667 | days
Max days' demand for storage (by inspection of graph) |  |  |  |  | 9.9609 | days
Add safety factor of 10% |  |  |  |  | 11 | days
Storage Devices Required
| Electroyser |  | capacity | 430.5214 | m3/h at 1 bar |  |  | 6 | 1200l/min electrolysers
| Compressor |  | capacity | 430.5214 | m3/h at from 1 to 200 bar
| H2 storage tank |  | capacity | 250 | m3at 250 bar |  | 249.6356 | 2.5 | 100m3 tanks
|  |  |  | 62500 | m3 metal hydride |  | 62408.9105
| Fuel cells |  | capacity | 320 | kW |  |  | 65 | 5kW | fuel cells
It should be possible to sell off any excess hydrogen production
Explosion hazard in storing compressed gas - tanks should be buried / located behind protective earthworks
Is the single year typical of the long term climate?
[10 empty] | Lerwick: | grid ref: | HU474414
[10 empty] | Average wind speed in 1978 (13) |  |  | 7.4151 | m/s | Assume at 10m height?
From (12):
[11 empty] | at 10m | 6.6 | m/s
[11 empty] | at 25m | 7.7 | m/s
[11 empty] | at 45m | 8.6 | m/s | BUT is 9.2 in next km to the W
Source
[10 empty] | (12) | DECC wind speed database for UK http://www.decc.gov.uk/en/windspeed/default.aspx
[10 empty] | (13) | MERIT: Time series wind speed data from University of Strathclyde energy supply/demand matching program
Conclusion: likely to produce more energy than calculated with a tall turbine
Also, possible to increase energy production by moving slightly to the West of the town
Power production profiled in next worksheet: | [6 empty] | Data centre demand: | 320 | kW | Turbine: | Siemens SWT-2.3-101

## Hydrogen storage
Hydrogen Storage Required
Assumptions in calcs: | [8 empty] | Sources:
Hydrogen fuel cells |  | Efficiency of storing (6) |  |  | 50% |  |  |  | (6) | Energy Resources & Policy lecture notes: round-trip efficiency of hydrogen fuel cells is 20-24%
|  | Efficiency of generating (6), (7) |  |  | 45% |  |  |  | (7) | Robertson, G: Wind-Hydrogen Community on the Isle of Lewis, MSc thesis U Starthclyde, 2009
Efficiency of generation at full loading is less than max efficiency
Demand |  | 320 | kW | [5 empty] | (8) | Scottish Hydrogen & Fuel cell Association, Hydrogen Properties & Safety Fact Sheet No. 1, December 2006 www.shfca.org.uk accessed 12 April 2010
Daily consumption |  | 7680 | kWh | [5 empty] | (9) | http://www3.statoil.com/hydrogentechnologies/svg03816.nsf?OpenDatabase accessed 12 April 1020
[9 empty] | (10) | Scottish Hydrogen & Fuel cell Association, Hydrogen Storage Fact Sheet No. 3, December 2006 www.shfca.org.uk accessed 12 April 2010
[9 empty] | (11) | http://www.thehydrogencompany.com/subsiteproducts_11-311.html#, accessed 12 April 2010
| Density of hydrogen (8) |  |  |  | 0.0899 | kg/m3 | at 1 bar
| Hydrogen energy density (8) |  |  |  | 33.33 | kWh/kg | at 1 bar
| Energy density per m3 |  |  |  | 2.9964 | kWh/m3 | at 1 bar |  |  | 3 | kWh/Nm3 | quoted in (7)
| Hydrogen energy density (8) |  |  |  | 0.53 | kWh/l | at 200bar
| Hydrogen density |  |  |  | 22.475 | kg/m3 | 250 |  |  | 22.2917 | kg/m3 quoted in (7)
| Energy density per m3 |  |  |  | 749.0918 | kWh/m3 | at 250bar
| Hydrogen density (10) |  |  |  | 60 | g/l | in metal hydride form
| Energy density |  |  |  | 1999.8 | kWh/m3 | in metal hydride form
Hydrogen equivalent of daily cons |  |  | 17066.6667 | kWh | 5695.7865 | m3 | at normal
[5 empty] | 22.7831 | m3 | at 200bar
[5 empty] | 8.5342 | m4 | in metal hydride
Devices required:
1) Hydrogen Production
Electrolyser capable of converting maximum excess power at any one time:
| From power production spreasdheet |  |  |  | 1290 | kWh | is max excess supply in 1 hr
| From power production spreadsheet: |  |  |  | 170000 |  | is max storage capacity
| Rate of conversion needed: |  |  |  | 430.5214 | Normal m3 per hour
[5 empty] | 7175.356 | litres/minute
| No. of electrolysers at |  | 1200 | l/min | 5.9795 |  | say | 6 | no |  | 72 | m3/hr | one electrolyser
[11 empty] | 215.7384 | Kwh/h | per electrolyser
Statoil produce electroysers capable of producing up to 485 Nm3/h and with energy use of 4.3 kWh/l produced (9) | [10 empty] | 647.2153 | 650 | three
Designed for continuous unattended operation, PLC system included
Capable of fast modulation in power
Type 5040, 4000Amp DC:
|  | 300-377 Nm3 H2/hr |  |  |  | Required | 2
Power: 4.0-4.2 kWh/Nm3H2
Water: 1l /Nm3H2
|  | Footprint | 4 x 13.5 m
Maintenance: 7-10 year intervals, 3-5 days' downtime
2) Storage
Only compressed gas storage & metal hydride considered - others are too expensive (liquid) or too experimental (carbon nanotube, glass microspheres) (10)
| Compressor needs to be capable of converting |  |  |  |  | 430.5214 | m3 hydrogen per hour
| Maximum storage required: |  |  | 9.9609 | m3
| Maximum kWh: |  |  | 170000 | kWh
| Compressed gas storage |  |  | 226.9415 | m3 | at 250 bar | say | 250 | m3 |  | Bottle capacity |  |  | 0.1508 | m3 | assume 440mm dia, 1.2m high
| Metal hydride storage |  |  | 56735.3732 | Nm3 |  | say | 58000 | Nm3 |  | Tank capacity |  |  | 5 | m3 | assume 2m x3m x3m
3) Generation - Fuel cells
Requires: Fuel cells capable of producing max 320kW
Cellcraft S-2000 is a long life / low maintenance fuel cell (11)
| Nominal power: |  | 2 | kW
| Life at nom power |  | 20000 | hours
| Dimesions: |  | 0.471 | 0.281 | 0.413 | m per side
| Startup time |  | 3-300 secs, above 0deg
| Assumed operates for |  | 12 | hours/day at nominal power
| No. Required |  | 160
| Lifetime |  | 4.5662 | years

## Power production
Wind Power Calculations
Time series calculations
Lerwick
Inputs | [15 empty] | Note: Paste turbine characteristics as values in column P
Data Centre Power Demand | [14 empty] | Wind speed | Siemens SWT-2.3-101
| IT power |  | 250 | kW | [10 empty] | m/s | kW
| Fixed infrastructure |  | 0.25 | PUE | [10 empty] | 0 | 0
| Cooling |  | 0.03 | PUE |  |  | Turbine is operating: | [7 empty] | 0.5 | 0
| Total |  | 320 | kW |  |  | Exactly on demand |  | 0% | 0 | days on average |  |  |  | 1 | 0
| Energy per time step |  | 320 | kWh |  |  | Excess supply |  | 68.34% | 249.4583 | days on average |  |  |  | 1.5 | 0
| Total demand in year |  | 2803200 | kWh |  |  | Excess demand |  | 31.64% | 115.5 | days on average |  |  |  | 2 | 0
[7 empty] | Turbine cut out |  | 0.04566% | 0.16667 | days on average |  |  |  | 2.5 | 0
| Efficiency of storing (7) | 50% |  |  |  |  | Turbine not cut in |  | 19.01% | 69.375 | days on average |  |  |  | 3 | 0
| Efficiency of generating (7) | 45% |  |  |  |  | Operating below demand |  | 14.84% | [5 empty] | 3.5 | 0
| Start level kWh | 50000 | 2.9297 | days | [10 empty] | 4 | 38.3333
| Max store kWh | 170000 | 9.9609 | days | [10 empty] | 4.5 | 99.6667
| Max processing kWh | 1290 | 6 | electorlysers | [10 empty] | 5 | 170
| Turbine cut-in | 4 | m/s | [11 empty] | 5.5 | 250
| Turbine cut-out | 25 | m/s | [11 empty] | 6 | 380
| No. of turbines | 2 |  |  | Totals | 15654415 | 13557946 | 706731 |  | kWh |  | -7051.7778 | Min kWh in store |  | 6.5 | 560
[12 empty] | -0.41319 | days |  | 7 | 740 | longest period with no addition to store |  |  |  | Max no wind
Site | Date/time | Ambient | Wind | Wind | Power | Energy | Excess | Excess | Processed | Stored | Used in | Level stored |  |  | 7.5 | 920 | days | 4.1667 |  | 2.2917
|  | temperature | speed | direction |  | in step | Supply | Demand |  |  | Generation |  |  |  | 8 | 1100 | hours | 100 |  | 55
|  | C | m/s | deg from N | kW | kWh | kWh | kWh | kWh | kWh | kWh | kWh | days |  | 8.5 | 1280
[12 empty] | 50000 | start point | 1300 | 9 | 1460
Lerwick | 1978-01-01 00:30 | 2.4 | 13.9 | 195 | 4600 | 2300 | 1980 | 0 | 1290 | 645 | 0 | 50645 | 2.9675 | 0 | 9.5 | 1640 | 0 | 0 | 0 | 0
Lerwick | 1978-01-01 01:30 | 7.6 | 15.2 | 240 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 51290 | 3.0053 | 0 | 10 | 1820 | 0 | 0 | 0 | 0
Lerwick | 1978-01-01 02:30 | 7.9 | 16 | 240 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 51935 | 3.0431 | 0 | 10.5 | 2000 | 0 | 0 | 0 | 0
Lerwick | 1978-01-01 03:30 | 8 | 15.8 | 240 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 52580 | 3.0809 | 0 | 11 | 2150 | 0 | 0 | 0 | 0
Lerwick | 1978-01-01 04:30 | 8 | 16.2 | 240 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 53225 | 3.1187 | 0 | 11.5 | 2236.1111 | 0 | 0 | 0 | 0
Lerwick | 1978-01-01 05:30 | 8 | 17 | 242.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 53870 | 3.1564 | 0 | 12 | 2268.0556 | 0 | 0 | 0 | 0
Lerwick | 1978-01-01 06:30 | 8 | 17 | 247.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 54515 | 3.1942 | 0 | 12.5 | 2300 | 0 | 0 | 0 | 0
Lerwick | 1978-01-01 07:30 | 7.8 | 16.4 | 250 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 55160 | 3.232 | 0 | 13 | 2300 | 0 | 0 | 0 | 0
Lerwick | 1978-01-01 08:30 | 7.3 | 16.7 | 250 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 55805 | 3.2698 | 0 | 13.5 | 2300 | 0 | 0 | 0 | 0
Lerwick | 1978-01-01 09:30 | 7 | 18 | 250 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 56450 | 3.3076 | 0 | 14 | 2300 | 0 | 0 | 0 | 0
Lerwick | 1978-01-01 10:30 | 6.7 | 19.4 | 250 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 57095 | 3.3454 | 0 | 14.5 | 2300 | 0 | 0 | 0 | 0
Lerwick | 1978-01-01 11:30 | 6.2 | 20.6 | 252.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 57740 | 3.3832 | 0 | 15 | 2300 | 0 | 0 | 0 | 0
Lerwick | 1978-01-01 12:30 | 6.1 | 20.8 | 257.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 58385 | 3.421 | 0 | 15.5 | 2300 | 0 | 0 | 0 | 0
Lerwick | 1978-01-01 13:30 | 5.6 | 19.9 | 262.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 59030 | 3.4588 | 0 | 16 | 2300 | 0 | 0 | 0 | 0
Lerwick | 1978-01-01 14:30 | 5.4 | 18.9 | 267.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 59675 | 3.4966 | 0 | 16.5 | 2300 | 0 | 0 | 0 | 0
Lerwick | 1978-01-01 15:30 | 5.9 | 18 | 272.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 60320 | 3.5344 | 0 | 17 | 2300 | 0 | 0 | 0 | 0
Lerwick | 1978-01-01 16:30 | 6 | 16.6 | 277.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 60965 | 3.5722 | 0 | 17.5 | 2300 | 0 | 0 | 0 | 0
Lerwick | 1978-01-01 17:30 | 5.5 | 14.5 | 280 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 61610 | 3.61 | 0 | 18 | 2300 | 0 | 0 | 0 | 0
Lerwick | 1978-01-01 18:30 | 4.7 | 12.2 | 280 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 645 | 0 | 62255 | 3.6478 | 0 | 18.5 | 2300 | 0 | 0 | 0 | 0
Lerwick | 1978-01-01 19:30 | 4.6 | 10.6 | 280 | 4000 | 4268.0556 | 3948.0556 | 0 | 1290 | 645 | 0 | 62900 | 3.6855 | 0 | 19 | 2300 | 0 | 0 | 0 | 0
Lerwick | 1978-01-01 20:30 | 4.5 | 10.6 | 275 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 63545 | 3.7233 | 0 | 19.5 | 2300 | 0 | 0 | 0 | 0
Lerwick | 1978-01-01 21:30 | 4.6 | 10.9 | 262.5 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 64190 | 3.7611 | 0 | 20 | 2300 | 0 | 0 | 0 | 0
Lerwick | 1978-01-01 22:30 | 4.5 | 10.4 | 255 | 3640 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 64835 | 3.7989 | 0 | 20.5 | 2300 | 0 | 0 | 0 | 0
Lerwick | 1978-01-01 23:30 | 4.4 | 10.4 | 255 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 65480 | 3.8367 | 0 | 21 | 2300 | 0 | 0 | 0 | 0
Lerwick | 1978-01-02 00:30 | 4.6 | 10.9 | 252.5 | 4000 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 66125 | 3.8745 | 0 | 21.5 | 2300 | 0 | 0 | 0 | 0
Lerwick | 1978-01-02 01:30 | 4.1 | 10.7 | 247.5 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 66770 | 3.9123 | 0 | 22 | 2300 | 0 | 0 | 0 | 0
Lerwick | 1978-01-02 02:30 | 4.1 | 9.7 | 255 | 3280 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 67415 | 3.9501 | 0 | 22.5 | 2300 | 0 | 0 | 0 | 0
Lerwick | 1978-01-02 03:30 | 4.1 | 8.3 | 275 | 2200 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 68060 | 3.9879 | 0 | 23 | 2300 | 0 | 0 | 0 | 0
Lerwick | 1978-01-02 04:30 | 3.1 | 7.6 | 277.5 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 68705 | 4.0257 | 0 | 23.5 | 2300 | 0 | 0 | 0 | 0
Lerwick | 1978-01-02 05:30 | 2.1 | 6.9 | 275 | 1120 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 69285 | 4.0597 | 0 | 24 | 2300 | 0 | 0 | 0 | 0
Lerwick | 1978-01-02 06:30 | 1.8 | 5.9 | 287.5 | 500 | 810 | 490 | 0 | 490 | 245 | 0 | 69530 | 4.074 | 0 | 24.5 | 2300 | 0 | 0 | 0 | 0
Lerwick | 1978-01-02 07:30 | 1.1 | 4.9 | 295 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 69544.8333 | 4.0749 | 0 | 25 | 2300 | 1 | 1 | 0 | 0
Lerwick | 1978-01-02 08:30 | 0.7 | 3.7 | 302.5 | 0 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 69055.2037 | 4.0462 | 1 | 25.5 | 0 | 1 | 2 | 0 | 0
Lerwick | 1978-01-02 09:30 | 1 | 2.9 | 312.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 68344.0926 | 4.0045 | 0 | 26 | 0 | 1 | 3 | 1 | 1
Lerwick | 1978-01-02 10:30 | 0.8 | 3.3 | 322.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 67632.9815 | 3.9629 | 0 | 26.5 | 0 | 1 | 4 | 1 | 2
Lerwick | 1978-01-02 11:30 | 0.5 | 4.5 | 337.5 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 67143.3519 | 3.9342 | 1 | 27 | 0 | 1 | 5 | 0 | 0
Lerwick | 1978-01-02 12:30 | 0.5 | 5 | 342.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 67031.5 | 3.9276 | 1 | 27.5 | 0 | 1 | 6 | 0 | 0
Lerwick | 1978-01-02 13:30 | 0.5 | 4.7 | 337.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 66919.6481 | 3.9211 | 1 | 27.5 | 0 | 1 | 7 | 0 | 0
Lerwick | 1978-01-02 14:30 | 0.4 | 4 | 332.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 66515.2037 | 3.8974 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-01-02 15:30 | 0.3 | 3.6 | 327.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 65889.2778 | 3.8607 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-01-02 16:30 | 0.3 | 3.4 | 325 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 65178.1667 | 3.819 | 0 |  |  | 1 | 10 | 1 | 1
Lerwick | 1978-01-02 17:30 | -0.1 | 3 | 327.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 64467.0556 | 3.7774 | 0 |  |  | 1 | 11 | 1 | 2
Lerwick | 1978-01-02 18:30 | -0.9 | 2.7 | 332.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 63755.9444 | 3.7357 | 0 |  |  | 1 | 12 | 1 | 3
Lerwick | 1978-01-02 19:30 | -2 | 3 | 337.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 63044.8333 | 3.694 | 0 |  |  | 1 | 13 | 1 | 4
Lerwick | 1978-01-02 20:30 | -2.5 | 3.3 | 337.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 62333.7222 | 3.6524 | 0 |  |  | 1 | 14 | 1 | 5
Lerwick | 1978-01-02 21:30 | -2.6 | 3.6 | 332.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 61622.6111 | 3.6107 | 0 |  |  | 1 | 15 | 1 | 6
Lerwick | 1978-01-02 22:30 | -2.9 | 4.8 | 335 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 61132.9815 | 3.582 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-02 23:30 | -1.9 | 6.2 | 170 | 760 | 479.6667 | 159.6667 | 0 | 159.6667 | 79.8333 | 0 | 61212.8148 | 3.5867 | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | By Inspection: logest periods with little power | 5001 | 6001
Lerwick | 1978-01-03 00:30 | -1.1 | 6.7 | 5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 61522.8148 | 3.6049 | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 2751 | 3501
Lerwick | 1978-01-03 01:30 | -1 | 6.7 | 10 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 61922.8148 | 3.6283 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-03 02:30 | -1 | 6.9 | 7.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 62322.8148 | 3.6517 | 0 |  |  | 0 | 0 | 0 | 0 |  | Wind speed characteristics
Lerwick | 1978-01-03 03:30 | -1.1 | 7.1 | 2.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 62812.8148 | 3.6804 | 0 |  |  | 0 | 0 | 0 | 0 |  | occasions below | % exceeded | m/s
Lerwick | 1978-01-03 04:30 | -1.2 | 6.8 | 177.5 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 63302.8148 | 3.7091 | 0 |  |  | 0 | 0 | 0 | 0 |  | 8760 | 0% | 30
Lerwick | 1978-01-03 05:30 | -1.2 | 6.9 | 352.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 63702.8148 | 3.7326 | 0 |  |  | 0 | 0 | 0 | 0 |  | 8759 | 0.01142% | 29
Lerwick | 1978-01-03 06:30 | -1.4 | 6.9 | 350 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 64102.8148 | 3.756 | 0 |  |  | 0 | 0 | 0 | 0 |  | 8759 | 0.01142% | 28
Lerwick | 1978-01-03 07:30 | -2 | 6.5 | 345 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 64502.8148 | 3.7795 | 0 |  |  | 0 | 0 | 0 | 0 |  | 8758 | 0.02283% | 27
Lerwick | 1978-01-03 08:30 | -2.5 | 6.5 | 335 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 64902.8148 | 3.8029 | 0 |  |  | 0 | 0 | 0 | 0 |  | 8757 | 0.03425% | 26
Lerwick | 1978-01-03 09:30 | -2.4 | 6.8 | 327.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 65302.8148 | 3.8263 | 0 |  |  | 0 | 0 | 0 | 0 |  | 8756 | 0.04566% | 25
Lerwick | 1978-01-03 10:30 | -1.5 | 7.2 | 322.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 65792.8148 | 3.855 | 0 |  |  | 0 | 0 | 0 | 0 |  | 8754 | 0.06849% | 24
Lerwick | 1978-01-03 11:30 | -0.5 | 8.2 | 322.5 | 2200 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 66437.8148 | 3.8928 | 0 |  |  | 0 | 0 | 0 | 0 |  | 8752 | 0.09132% | 23
Lerwick | 1978-01-03 12:30 | -0.4 | 9.9 | 325 | 3280 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 67082.8148 | 3.9306 | 0 |  |  | 0 | 0 | 0 | 0 |  | 8744 | 0.1826% | 22
Lerwick | 1978-01-03 13:30 | -0.4 | 11.4 | 325 | 4300 | 3790 | 3470 | 0 | 1290 | 645 | 0 | 67727.8148 | 3.9684 | 0 |  |  | 0 | 0 | 0 | 0 |  | 8735 | 0.2854% | 21
Lerwick | 1978-01-03 14:30 | -0.6 | 12.2 | 327.5 | 4536.1111 | 4418.0556 | 4098.0556 | 0 | 1290 | 645 | 0 | 68372.8148 | 4.0062 | 0 |  |  | 0 | 0 | 0 | 0 |  | 8722 | 0.4338% | 20
Lerwick | 1978-01-03 15:30 | -0.6 | 12.2 | 330 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 69017.8148 | 4.044 | 0 |  |  | 0 | 0 | 0 | 0 |  | 8703 | 0.6507% | 19
Lerwick | 1978-01-03 16:30 | -0.1 | 11.9 | 332.5 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 645 | 0 | 69662.8148 | 4.0818 | 0 |  |  | 0 | 0 | 0 | 0 |  | 8686 | 0.8447% | 18
Lerwick | 1978-01-03 17:30 | -0.1 | 11.5 | 335 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 645 | 0 | 70307.8148 | 4.1196 | 0 |  |  | 0 | 0 | 0 | 0 |  | 8634 | 1.438% | 17
Lerwick | 1978-01-03 18:30 | -0.3 | 11.3 | 330 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 70952.8148 | 4.1574 | 0 |  |  | 0 | 0 | 0 | 0 |  | 8558 | 2.306% | 16
Lerwick | 1978-01-03 19:30 | -1.4 | 11.4 | 322.5 | 4300 | 4300 | 3980 | 0 | 1290 | 645 | 0 | 71597.8148 | 4.1952 | 0 |  |  | 0 | 0 | 0 | 0 |  | 8445 | 3.596% | 15
Lerwick | 1978-01-03 20:30 | -2.1 | 11.1 | 322.5 | 4300 | 4300 | 3980 | 0 | 1290 | 645 | 0 | 72242.8148 | 4.233 | 0 |  |  | 0 | 0 | 0 | 0 |  | 8244 | 5.89% | 14
Lerwick | 1978-01-03 21:30 | -1.6 | 10.5 | 325 | 4000 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 72887.8148 | 4.2708 | 0 |  |  | 0 | 0 | 0 | 0 |  | 7977 | 8.938% | 13
Lerwick | 1978-01-03 22:30 | -1.4 | 10.1 | 322.5 | 3640 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 73532.8148 | 4.3086 | 0 |  |  | 0 | 0 | 0 | 0 |  | 7634 | 12.85% | 12
Lerwick | 1978-01-03 23:30 | -1.3 | 10 | 322.5 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 74177.8148 | 4.3464 | 0 |  |  | 0 | 0 | 0 | 0 |  | 7152 | 18.36% | 11
Lerwick | 1978-01-04 00:30 | -1 | 9.9 | 327.5 | 3280 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 74822.8148 | 4.3841 | 0 |  |  | 0 | 0 | 0 | 0 |  | 6596 | 24.7% | 10
Lerwick | 1978-01-04 01:30 | -0.4 | 9.4 | 330 | 2920 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 75467.8148 | 4.4219 | 0 |  |  | 0 | 0 | 0 | 0 |  | 5981 | 31.72% | 9
Lerwick | 1978-01-04 02:30 | 0 | 8.7 | 330 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 76112.8148 | 4.4597 | 0 |  |  | 0 | 0 | 0 | 0 |  | 5252 | 40.05% | 8
Lerwick | 1978-01-04 03:30 | 0 | 8.3 | 327.5 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 76757.8148 | 4.4975 | 0 |  |  | 0 | 0 | 0 | 0 |  | 4476 | 48.9% | 7
Lerwick | 1978-01-04 04:30 | -0.1 | 8 | 325 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 77402.8148 | 4.5353 | 0 |  |  | 0 | 0 | 0 | 0 |  | 3568 | 59.27% | 6
Lerwick | 1978-01-04 05:30 | 0.3 | 7.8 | 327.5 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 78047.8148 | 4.5731 | 0 |  |  | 0 | 0 | 0 | 0 |  | 2677 | 69.44% | 5
Lerwick | 1978-01-04 06:30 | 0.7 | 7.2 | 332.5 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 78692.8148 | 4.6109 | 0 |  |  | 0 | 0 | 0 | 0 |  | 1665 | 80.99% | 4
Lerwick | 1978-01-04 07:30 | 0.5 | 5.8 | 335 | 500 | 990 | 670 | 0 | 670 | 335 | 0 | 79027.8148 | 4.6305 | 0 |  |  | 1 | 1 | 0 | 0 |  | 838 | 90.43% | 3
Lerwick | 1978-01-04 08:30 | 0.4 | 4.4 | 332.5 | 76.6667 | 288.3333 | 0 | 31.6667 | 0 | 0 | 70.3704 | 78957.4444 | 4.6264 | 1 |  |  | 1 | 2 | 0 | 0 |  | 380 | 95.66% | 2
Lerwick | 1978-01-04 09:30 | 0.3 | 3.6 | 327.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 78331.5185 | 4.5897 | 1 |  |  | 1 | 3 | 0 | 0 |  | 83 | 99.05% | 1
Lerwick | 1978-01-04 10:30 | 0.1 | 3.2 | 317.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 77620.4074 | 4.5481 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-01-04 11:30 | 0.5 | 3.2 | 295 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 76909.2963 | 4.5064 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-01-04 12:30 | 1.1 | 3.4 | 267.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 76198.1852 | 4.4647 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-01-04 13:30 | 1.3 | 3.4 | 245 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 75487.0741 | 4.4231 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-01-04 14:30 | 0.9 | 3 | 222.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 74775.963 | 4.3814 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-01-04 15:30 | 0.2 | 3 | 205 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 74064.8519 | 4.3397 | 0 |  |  | 1 | 9 | 1 | 6
Lerwick | 1978-01-04 16:30 | 0 | 4.3 | 200 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 73438.9259 | 4.3031 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-04 17:30 | 0.4 | 6.5 | 197.5 | 1120 | 598.3333 | 278.3333 | 0 | 278.3333 | 139.1667 | 0 | 73578.0926 | 4.3112 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-04 18:30 | 1.8 | 8.7 | 192.5 | 2560 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 74223.0926 | 4.349 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-04 19:30 | 2.8 | 10.6 | 190 | 4000 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 74868.0926 | 4.3868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-04 20:30 | 3.1 | 12.4 | 190 | 4536.1111 | 4268.0556 | 3948.0556 | 0 | 1290 | 645 | 0 | 75513.0926 | 4.4246 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-04 21:30 | 3.2 | 14.1 | 190 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 645 | 0 | 76158.0926 | 4.4624 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-04 22:30 | 3.5 | 15.9 | 187.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 76803.0926 | 4.5002 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-04 23:30 | 2.9 | 18.1 | 182.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 77448.0926 | 4.538 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-05 00:30 | 2.4 | 19 | 182.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 78093.0926 | 4.5758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-05 01:30 | 2.4 | 17.9 | 190 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 78738.0926 | 4.6136 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-05 02:30 | 2 | 16.6 | 202.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 79383.0926 | 4.6514 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-05 03:30 | 3 | 15.3 | 217.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 80028.0926 | 4.6891 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-05 04:30 | 4.7 | 12.9 | 232.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 80673.0926 | 4.7269 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-05 05:30 | 6.1 | 10.7 | 247.5 | 4000 | 4300 | 3980 | 0 | 1290 | 645 | 0 | 81318.0926 | 4.7647 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-05 06:30 | 7.1 | 9.9 | 257.5 | 3280 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 81963.0926 | 4.8025 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-05 07:30 | 7.5 | 9.9 | 260 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 82608.0926 | 4.8403 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-05 08:30 | 7.2 | 10.2 | 260 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 83253.0926 | 4.8781 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-05 09:30 | 6.9 | 10.9 | 260 | 4000 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 83898.0926 | 4.9159 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-05 10:30 | 6.8 | 11.8 | 257.5 | 4472.2222 | 4236.1111 | 3916.1111 | 0 | 1290 | 645 | 0 | 84543.0926 | 4.9537 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-05 11:30 | 7 | 12.2 | 252.5 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 645 | 0 | 85188.0926 | 4.9915 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-05 12:30 | 7 | 11.5 | 247.5 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 645 | 0 | 85833.0926 | 5.0293 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-05 13:30 | 7.2 | 10.7 | 242.5 | 4000 | 4236.1111 | 3916.1111 | 0 | 1290 | 645 | 0 | 86478.0926 | 5.0671 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-05 14:30 | 7.2 | 10 | 237.5 | 3640 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 87123.0926 | 5.1049 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-05 15:30 | 7.2 | 9.4 | 232.5 | 2920 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 87768.0926 | 5.1427 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-05 16:30 | 7.4 | 10.3 | 230 | 3640 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 88413.0926 | 5.1805 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-05 17:30 | 7.4 | 12.1 | 230 | 4536.1111 | 4088.0556 | 3768.0556 | 0 | 1290 | 645 | 0 | 89058.0926 | 5.2182 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-05 18:30 | 7.6 | 13 | 230 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 645 | 0 | 89703.0926 | 5.256 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-05 19:30 | 7.6 | 13.2 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 90348.0926 | 5.2938 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-05 20:30 | 7.5 | 13.5 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 90993.0926 | 5.3316 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-05 21:30 | 7.5 | 13.9 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 91638.0926 | 5.3694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-05 22:30 | 7.8 | 14.3 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 92283.0926 | 5.4072 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-05 23:30 | 8 | 14.4 | 232.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 92928.0926 | 5.445 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-06 00:30 | 8 | 14.4 | 237.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 93573.0926 | 5.4828 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-06 01:30 | 8.2 | 14.3 | 240 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 94218.0926 | 5.5206 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-06 02:30 | 8.2 | 13.9 | 240 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 94863.0926 | 5.5584 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-06 03:30 | 8.2 | 13.6 | 240 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 95508.0926 | 5.5962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-06 04:30 | 8.3 | 13.9 | 240 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 96153.0926 | 5.634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-06 05:30 | 8.5 | 14.5 | 240 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 96798.0926 | 5.6718 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-06 06:30 | 8.5 | 14.9 | 237.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 97443.0926 | 5.7096 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-06 07:30 | 8.5 | 14.8 | 232.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 98088.0926 | 5.7473 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-06 08:30 | 8.5 | 15 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 98733.0926 | 5.7851 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-06 09:30 | 8.5 | 15.5 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 99378.0926 | 5.8229 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-06 10:30 | 8.5 | 15.9 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 100023.0926 | 5.8607 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-06 11:30 | 8.4 | 17.1 | 227.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 100668.0926 | 5.8985 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-06 12:30 | 8.3 | 18.6 | 222.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 101313.0926 | 5.9363 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-06 13:30 | 8.3 | 19 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 101958.0926 | 5.9741 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-06 14:30 | 8.2 | 17.5 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 102603.0926 | 6.0119 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-06 15:30 | 8 | 15.3 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 103248.0926 | 6.0497 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-06 16:30 | 7.9 | 14.3 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 103893.0926 | 6.0875 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-06 17:30 | 7.7 | 13.9 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 104538.0926 | 6.1253 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-06 18:30 | 7.8 | 13.3 | 217.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 105183.0926 | 6.1631 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-06 19:30 | 7.7 | 13 | 212.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 105828.0926 | 6.2009 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-06 20:30 | 7.6 | 13 | 210 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 106473.0926 | 6.2387 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-06 21:30 | 7.7 | 13.3 | 210 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 107118.0926 | 6.2765 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-06 22:30 | 7.6 | 13.6 | 210 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 107763.0926 | 6.3142 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-06 23:30 | 7.5 | 13.3 | 210 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 108408.0926 | 6.352 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-07 00:30 | 7.5 | 13 | 212.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 109053.0926 | 6.3898 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-07 01:30 | 7.7 | 12.9 | 215 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 109698.0926 | 6.4276 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-07 02:30 | 7.8 | 12.7 | 212.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 110343.0926 | 6.4654 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-07 03:30 | 7.7 | 12.7 | 210 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 110988.0926 | 6.5032 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-07 04:30 | 7.7 | 13 | 212.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 111633.0926 | 6.541 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-07 05:30 | 7.5 | 12.8 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 112278.0926 | 6.5788 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-07 06:30 | 7.4 | 12.2 | 227.5 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 645 | 0 | 112923.0926 | 6.6166 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-07 07:30 | 7.5 | 11.5 | 232.5 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 645 | 0 | 113568.0926 | 6.6544 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-07 08:30 | 7.3 | 10.2 | 235 | 3640 | 4056.1111 | 3736.1111 | 0 | 1290 | 645 | 0 | 114213.0926 | 6.6922 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-07 09:30 | 6.6 | 9.4 | 232.5 | 2920 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 114858.0926 | 6.73 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-07 10:30 | 6.1 | 10.1 | 227.5 | 3640 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 115503.0926 | 6.7678 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-07 11:30 | 6.3 | 11.9 | 225 | 4472.2222 | 4056.1111 | 3736.1111 | 0 | 1290 | 645 | 0 | 116148.0926 | 6.8056 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-07 12:30 | 6.8 | 13.2 | 225 | 4600 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 116793.0926 | 6.8433 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-07 13:30 | 7 | 14.1 | 225 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 117438.0926 | 6.8811 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-07 14:30 | 6.9 | 15.2 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 118083.0926 | 6.9189 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-07 15:30 | 6.1 | 15.8 | 237.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 118728.0926 | 6.9567 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-07 16:30 | 5.2 | 16 | 240 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 119373.0926 | 6.9945 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-07 17:30 | 5.3 | 15.7 | 240 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 120018.0926 | 7.0323 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-07 18:30 | 5.8 | 15 | 240 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 120663.0926 | 7.0701 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-07 19:30 | 5.9 | 14 | 240 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 121308.0926 | 7.1079 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-07 20:30 | 5.8 | 12.9 | 237.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 121953.0926 | 7.1457 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-07 21:30 | 5.9 | 12.7 | 232.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 122598.0926 | 7.1835 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-07 22:30 | 6.2 | 13.1 | 227.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 123243.0926 | 7.2213 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-07 23:30 | 6.3 | 13.5 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 123888.0926 | 7.2591 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-08 00:30 | 6.3 | 13.9 | 215 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 124533.0926 | 7.2969 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-08 01:30 | 5.9 | 14.7 | 215 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 125178.0926 | 7.3347 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-08 02:30 | 5.9 | 15.2 | 212.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 125823.0926 | 7.3724 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-08 03:30 | 6.4 | 15 | 212.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 126468.0926 | 7.4102 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-08 04:30 | 6.5 | 15 | 217.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 127113.0926 | 7.448 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-08 05:30 | 6.4 | 15.2 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 127758.0926 | 7.4858 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-08 06:30 | 6.5 | 15 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 128403.0926 | 7.5236 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-08 07:30 | 6.8 | 14.5 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 129048.0926 | 7.5614 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-08 08:30 | 6.8 | 13.8 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 129693.0926 | 7.5992 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-08 09:30 | 6.7 | 13.1 | 217.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 130338.0926 | 7.637 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-08 10:30 | 6.5 | 12.3 | 212.5 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 645 | 0 | 130983.0926 | 7.6748 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-08 11:30 | 6.4 | 11.5 | 207.5 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 645 | 0 | 131628.0926 | 7.7126 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-08 12:30 | 6.5 | 11 | 200 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 132273.0926 | 7.7504 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-08 13:30 | 6.3 | 10.8 | 195 | 4000 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 132918.0926 | 7.7882 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-08 14:30 | 6.1 | 11.1 | 197.5 | 4300 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 133563.0926 | 7.826 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-08 15:30 | 6 | 11.9 | 200 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 134208.0926 | 7.8638 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-08 16:30 | 6 | 12.6 | 200 | 4600 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 134853.0926 | 7.9015 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-08 17:30 | 6.1 | 13 | 200 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 135498.0926 | 7.9393 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-08 18:30 | 6.4 | 13.3 | 200 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 136143.0926 | 7.9771 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-08 19:30 | 6.6 | 13.9 | 200 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 136788.0926 | 8.0149 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-08 20:30 | 6.5 | 14.7 | 202.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 137433.0926 | 8.0527 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-08 21:30 | 6.5 | 15.7 | 210 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 138078.0926 | 8.0905 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-08 22:30 | 6.6 | 15.9 | 217.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 138723.0926 | 8.1283 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-08 23:30 | 6.7 | 14.8 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 139368.0926 | 8.1661 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-09 00:30 | 6.4 | 12.9 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 140013.0926 | 8.2039 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-09 01:30 | 5.7 | 11.5 | 222.5 | 4472.2222 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 140658.0926 | 8.2417 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-09 02:30 | 5.3 | 10.7 | 227.5 | 4000 | 4236.1111 | 3916.1111 | 0 | 1290 | 645 | 0 | 141303.0926 | 8.2795 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-09 03:30 | 5.1 | 10.4 | 230 | 3640 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 141948.0926 | 8.3173 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-09 04:30 | 4.8 | 10.3 | 230 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 142593.0926 | 8.3551 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-09 05:30 | 4.6 | 10.1 | 227.5 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 143238.0926 | 8.3929 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-09 06:30 | 3.9 | 10.1 | 222.5 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 143883.0926 | 8.4306 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-09 07:30 | 3.7 | 10.8 | 217.5 | 4000 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 144528.0926 | 8.4684 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-09 08:30 | 3.8 | 11.1 | 215 | 4300 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 145173.0926 | 8.5062 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-09 09:30 | 3 | 10.5 | 220 | 4000 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 145818.0926 | 8.544 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-09 10:30 | 2.7 | 10 | 230 | 3640 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 146463.0926 | 8.5818 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-09 11:30 | 3.3 | 10.1 | 240 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 147108.0926 | 8.6196 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-09 12:30 | 3.8 | 10.4 | 247.5 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 147753.0926 | 8.6574 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-09 13:30 | 3.9 | 10.7 | 250 | 4000 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 148398.0926 | 8.6952 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-09 14:30 | 3.9 | 11 | 252.5 | 4300 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 149043.0926 | 8.733 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-09 15:30 | 3.7 | 10.7 | 257.5 | 4000 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 149688.0926 | 8.7708 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-09 16:30 | 3 | 10 | 262.5 | 3640 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 150333.0926 | 8.8086 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-09 17:30 | 2.5 | 8.7 | 262.5 | 2560 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 150978.0926 | 8.8464 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-09 18:30 | 1.9 | 7.7 | 250 | 1840 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 151623.0926 | 8.8842 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-09 19:30 | 1.8 | 7.3 | 235 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 152268.0926 | 8.922 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-09 20:30 | 2.2 | 7.6 | 232.5 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 152913.0926 | 8.9598 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-09 21:30 | 2.1 | 8.3 | 230 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 153558.0926 | 8.9975 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-09 22:30 | 1.8 | 8.5 | 220 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 154203.0926 | 9.0353 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-09 23:30 | 1.9 | 9 | 217.5 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 154848.0926 | 9.0731 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-10 00:30 | 2.4 | 8.6 | 222.5 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 155493.0926 | 9.1109 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-10 01:30 | 1.2 | 6.9 | 225 | 1120 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 156138.0926 | 9.1487 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-10 02:30 | 0 | 6.9 | 227.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 156538.0926 | 9.1722 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-10 03:30 | 0.6 | 8.3 | 237.5 | 2200 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 157183.0926 | 9.2099 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-10 04:30 | 0.7 | 8.1 | 247.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 157828.0926 | 9.2477 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-10 05:30 | 0.6 | 7.2 | 250 | 1480 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 158473.0926 | 9.2855 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-10 06:30 | 1.1 | 7.6 | 255 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 159118.0926 | 9.3233 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-10 07:30 | 1.4 | 8 | 262.5 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 159763.0926 | 9.3611 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-10 08:30 | 1.7 | 8.8 | 260 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 160408.0926 | 9.3989 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-10 09:30 | 1.7 | 9.9 | 247.5 | 3280 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 161053.0926 | 9.4367 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-10 10:30 | 1.8 | 10.6 | 230 | 4000 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 161698.0926 | 9.4745 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-10 11:30 | 1.6 | 10.4 | 215 | 3640 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 162343.0926 | 9.5123 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-10 12:30 | 0.9 | 8.7 | 212.5 | 2560 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 162988.0926 | 9.5501 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-10 13:30 | 0.7 | 7.2 | 220 | 1480 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 163633.0926 | 9.5879 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-10 14:30 | 0.9 | 6 | 230 | 760 | 1120 | 800 | 0 | 800 | 400 | 0 | 164033.0926 | 9.6113 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-10 15:30 | 0.9 | 4.9 | 262.5 | 199.3333 | 479.6667 | 159.6667 | 0 | 159.6667 | 79.8333 | 0 | 164112.9259 | 9.616 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-01-10 16:30 | 0.9 | 4.6 | 305 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 163844.7778 | 9.6003 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-01-10 17:30 | 0.5 | 4.4 | 297.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 163440.3333 | 9.5766 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-01-10 18:30 | -0.1 | 3.6 | 262.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 162814.4074 | 9.5399 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-01-10 19:30 | -0.6 | 3.9 | 252.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162103.2963 | 9.4982 | 0 |  |  | 1 | 5 | 1 | 1
Lerwick | 1978-01-10 20:30 | -1 | 4.4 | 255 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 161477.3704 | 9.4616 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-01-10 21:30 | -0.8 | 3.8 | 257.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 160851.4444 | 9.4249 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-01-10 22:30 | -0.3 | 3.3 | 267.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160140.3333 | 9.3832 | 0 |  |  | 1 | 8 | 1 | 1
Lerwick | 1978-01-10 23:30 | 0.1 | 4.1 | 270 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 159514.4074 | 9.3465 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-01-11 00:30 | 0.6 | 5.8 | 255 | 500 | 288.3333 | 0 | 31.6667 | 0 | 0 | 70.3704 | 159444.037 | 9.3424 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-11 01:30 | 0.8 | 7.4 | 245 | 1480 | 990 | 670 | 0 | 670 | 335 | 0 | 159779.037 | 9.3621 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-11 02:30 | 0.5 | 8.5 | 260 | 2560 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 160424.037 | 9.3998 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-11 03:30 | 0.3 | 10.5 | 302.5 | 4000 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 161069.037 | 9.4376 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-11 04:30 | 0.6 | 14.3 | 167.5 | 4600 | 4300 | 3980 | 0 | 1290 | 645 | 0 | 161714.037 | 9.4754 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-11 05:30 | 1.3 | 17.7 | 10 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 162359.037 | 9.5132 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-11 06:30 | 1.7 | 19.2 | 17.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 163004.037 | 9.551 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-11 07:30 | 1.2 | 19.4 | 20 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 163649.037 | 9.5888 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-11 08:30 | 0.9 | 19.2 | 20 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 164294.037 | 9.6266 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-11 09:30 | 1.6 | 18.8 | 17.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 164939.037 | 9.6644 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-11 10:30 | 1.6 | 18 | 12.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 165584.037 | 9.7022 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-11 11:30 | 1.2 | 16.8 | 10 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 166229.037 | 9.74 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-11 12:30 | 0.9 | 15.7 | 7.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 166874.037 | 9.7778 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-11 13:30 | 0.5 | 14.8 | 2.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 167519.037 | 9.8156 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-11 14:30 | 0.2 | 13.6 | 177.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 168164.037 | 9.8534 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-11 15:30 | -0.1 | 12.4 | 350 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 645 | 0 | 168809.037 | 9.8912 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-11 16:30 | -0.6 | 12 | 342.5 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 169454.037 | 9.9289 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-11 17:30 | -1.6 | 11.9 | 340 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 645 | 0 | 170099.037 | 9.9667 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-11 18:30 | -2.3 | 11.8 | 340 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170099.037 | 9.9667 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-11 19:30 | -2.8 | 11.8 | 340 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170099.037 | 9.9667 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-11 20:30 | -2.6 | 11.5 | 340 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170099.037 | 9.9667 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-11 21:30 | -2.8 | 11.3 | 340 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170099.037 | 9.9667 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-11 22:30 | -2.8 | 11.6 | 340 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170099.037 | 9.9667 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-11 23:30 | -2.2 | 11.9 | 340 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170099.037 | 9.9667 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-12 00:30 | -2 | 11.8 | 340 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170099.037 | 9.9667 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-12 01:30 | -2 | 11.9 | 340 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170099.037 | 9.9667 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-12 02:30 | -2.2 | 11.5 | 340 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170099.037 | 9.9667 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-12 03:30 | -2 | 10.2 | 340 | 3640 | 4056.1111 | 3736.1111 | 0 | 1290 | 0 | 0 | 170099.037 | 9.9667 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-12 04:30 | -1.7 | 8.8 | 340 | 2560 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170099.037 | 9.9667 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-12 05:30 | -2.3 | 7.6 | 340 | 1840 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170099.037 | 9.9667 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-12 06:30 | -2.7 | 6.8 | 340 | 1120 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170099.037 | 9.9667 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-12 07:30 | -2.3 | 6.1 | 340 | 760 | 940 | 620 | 0 | 620 | 0 | 0 | 170099.037 | 9.9667 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-12 08:30 | -2 | 5.1 | 337.5 | 340 | 550 | 230 | 0 | 230 | 0 | 0 | 170099.037 | 9.9667 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-01-12 09:30 | -1.8 | 3.8 | 330 | 0 | 170 | 0 | 150 | 0 | 0 | 333.3333 | 169765.7037 | 9.9472 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-01-12 10:30 | -1.5 | 3 | 317.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 169054.5926 | 9.9055 | 0 |  |  | 1 | 3 | 1 | 1
Lerwick | 1978-01-12 11:30 | -1.2 | 2.4 | 302.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168343.4815 | 9.8639 | 0 |  |  | 1 | 4 | 1 | 2
Lerwick | 1978-01-12 12:30 | -0.9 | 1.9 | 287.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167632.3704 | 9.8222 | 0 |  |  | 1 | 5 | 1 | 3
Lerwick | 1978-01-12 13:30 | -0.9 | 1.9 | 265 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166921.2593 | 9.7805 | 0 |  |  | 1 | 6 | 1 | 4
Lerwick | 1978-01-12 14:30 | -1.2 | 3 | 240 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166210.1481 | 9.7389 | 0 |  |  | 1 | 7 | 1 | 5
Lerwick | 1978-01-12 15:30 | -0.9 | 5 | 227.5 | 340 | 170 | 0 | 150 | 0 | 0 | 333.3333 | 165876.8148 | 9.7193 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-12 16:30 | -0.2 | 7.3 | 222.5 | 1480 | 910 | 590 | 0 | 590 | 295 | 0 | 166171.8148 | 9.7366 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-12 17:30 | 0 | 9.6 | 217.5 | 3280 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 166816.8148 | 9.7744 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-12 18:30 | 0.4 | 11.6 | 212.5 | 4472.2222 | 3876.1111 | 3556.1111 | 0 | 1290 | 645 | 0 | 167461.8148 | 9.8122 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-12 19:30 | 1.2 | 13.4 | 210 | 4600 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 168106.8148 | 9.85 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-12 20:30 | 1.5 | 15 | 210 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 168751.8148 | 9.8878 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-12 21:30 | 1.4 | 16.1 | 212.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 169396.8148 | 9.9256 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-12 22:30 | 1.4 | 17 | 217.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-12 23:30 | 1.9 | 17.1 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-13 00:30 | 2.7 | 15.7 | 225 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-13 01:30 | 4.2 | 14.7 | 237.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-13 02:30 | 6.2 | 14.8 | 252.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-13 03:30 | 7.5 | 14.6 | 265 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-13 04:30 | 7.9 | 14.3 | 270 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-13 05:30 | 8 | 13.8 | 272.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-13 06:30 | 8 | 13.2 | 277.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-13 07:30 | 8 | 13.2 | 280 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-13 08:30 | 8.1 | 13.1 | 280 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-13 09:30 | 8.1 | 12.2 | 280 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-13 10:30 | 8.1 | 10.9 | 280 | 4000 | 4268.0556 | 3948.0556 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-13 11:30 | 8.1 | 10 | 280 | 3640 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-13 12:30 | 8.1 | 9.6 | 280 | 3280 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-13 13:30 | 8.1 | 9.1 | 280 | 2920 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-13 14:30 | 8 | 8.4 | 280 | 2200 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-13 15:30 | 8 | 8.3 | 280 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-13 16:30 | 8 | 8.9 | 280 | 2560 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-13 17:30 | 7.9 | 9.3 | 280 | 2920 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-13 18:30 | 7.7 | 9.1 | 280 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-13 19:30 | 7.8 | 9.1 | 277.5 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-13 20:30 | 8 | 9.5 | 272.5 | 3280 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-13 21:30 | 7.8 | 10 | 270 | 3640 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-13 22:30 | 7.6 | 10 | 267.5 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-13 23:30 | 7.5 | 10.1 | 265 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-14 00:30 | 7.6 | 11.2 | 267.5 | 4300 | 3970 | 3650 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-14 01:30 | 7.4 | 11.7 | 270 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-14 02:30 | 7.1 | 11.1 | 270 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-14 03:30 | 7 | 10.8 | 270 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-14 04:30 | 6.9 | 10.6 | 267.5 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-14 05:30 | 6.9 | 10.7 | 262.5 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-14 06:30 | 6.9 | 11 | 260 | 4300 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-14 07:30 | 6.8 | 11 | 260 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-14 08:30 | 6.7 | 11.4 | 260 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-14 09:30 | 6.7 | 11.8 | 257.5 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-14 10:30 | 6.7 | 11.9 | 252.5 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-14 11:30 | 6.8 | 12 | 250 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-14 12:30 | 7 | 11.9 | 250 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-14 13:30 | 7.1 | 11.8 | 250 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-14 14:30 | 7 | 11.9 | 250 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-14 15:30 | 7 | 12 | 250 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-14 16:30 | 7.1 | 12 | 247.5 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-14 17:30 | 7.1 | 12.4 | 242.5 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-14 18:30 | 7 | 13.4 | 240 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-14 19:30 | 6.9 | 14.4 | 240 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-14 20:30 | 6.9 | 14.9 | 240 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-14 21:30 | 7 | 14.5 | 240 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-14 22:30 | 7 | 14 | 237.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-14 23:30 | 7 | 13.9 | 232.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-15 00:30 | 7 | 13.7 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-15 01:30 | 7.1 | 13.5 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-15 02:30 | 7.1 | 13.4 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-15 03:30 | 7.1 | 13.2 | 227.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-15 04:30 | 7.1 | 12.8 | 222.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-15 05:30 | 6.9 | 12.5 | 217.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-15 06:30 | 6.4 | 12.5 | 215 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-15 07:30 | 6.2 | 12.2 | 217.5 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-15 08:30 | 6.3 | 11.7 | 220 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-15 09:30 | 6.6 | 11.2 | 217.5 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-15 10:30 | 6.8 | 10.4 | 207.5 | 3640 | 3970 | 3650 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-15 11:30 | 7.1 | 9.4 | 197.5 | 2920 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-15 12:30 | 7 | 9.6 | 200 | 3280 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-15 13:30 | 6.7 | 10.6 | 207.5 | 4000 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-15 14:30 | 6.9 | 10.5 | 207.5 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-15 15:30 | 6.7 | 9 | 200 | 2920 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-15 16:30 | 6.5 | 8.3 | 197.5 | 2200 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-15 17:30 | 6.4 | 8.9 | 202.5 | 2560 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-15 18:30 | 6.6 | 8.7 | 202.5 | 2560 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-15 19:30 | 6.8 | 8.5 | 202.5 | 2560 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-15 20:30 | 6.5 | 9.4 | 210 | 2920 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-15 21:30 | 6.1 | 9.4 | 217.5 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-15 22:30 | 6 | 8.5 | 222.5 | 2560 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-15 23:30 | 5.5 | 7.2 | 230 | 1480 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-16 00:30 | 5.1 | 5.9 | 247.5 | 500 | 990 | 670 | 0 | 670 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-16 01:30 | 5.1 | 4.9 | 265 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 0 | 0 | 170041.8148 | 9.9634 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-01-16 02:30 | 4.5 | 4 | 262.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 169637.3704 | 9.9397 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-01-16 03:30 | 4 | 3.7 | 265 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 169011.4444 | 9.903 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-01-16 04:30 | 4.2 | 3.6 | 290 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168300.3333 | 9.8613 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-01-16 05:30 | 4.2 | 3.3 | 310 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167589.2222 | 9.8197 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-01-16 06:30 | 4 | 3.6 | 317.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166878.1111 | 9.778 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-01-16 07:30 | 3.5 | 3.7 | 320 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166167 | 9.7363 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-01-16 08:30 | 3 | 3.3 | 317.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165455.8889 | 9.6947 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-01-16 09:30 | 2.8 | 2.8 | 312.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164744.7778 | 9.653 | 0 |  |  | 1 | 9 | 1 | 6
Lerwick | 1978-01-16 10:30 | 2.8 | 2.3 | 315 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164033.6667 | 9.6113 | 0 |  |  | 1 | 10 | 1 | 7
Lerwick | 1978-01-16 11:30 | 3 | 1.7 | 330 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163322.5556 | 9.5697 | 0 |  |  | 1 | 11 | 1 | 8
Lerwick | 1978-01-16 12:30 | 2.9 | 1.4 | 342.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162611.4444 | 9.528 | 0 |  |  | 1 | 12 | 1 | 9
Lerwick | 1978-01-16 13:30 | 2.9 | 1.8 | 342.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161900.3333 | 9.4863 | 0 |  |  | 1 | 13 | 1 | 10
Lerwick | 1978-01-16 14:30 | 2.8 | 2.6 | 342.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161189.2222 | 9.4447 | 0 |  |  | 1 | 14 | 1 | 11
Lerwick | 1978-01-16 15:30 | 2.5 | 3.3 | 172.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160478.1111 | 9.403 | 0 |  |  | 1 | 15 | 1 | 12
Lerwick | 1978-01-16 16:30 | 2.3 | 4 | 7.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 159852.1852 | 9.3663 | 1 |  |  | 1 | 16 | 0 | 0
Lerwick | 1978-01-16 17:30 | 2.4 | 5.1 | 20 | 340 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 159604.037 | 9.3518 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-16 18:30 | 2.6 | 5.8 | 25 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 159654.037 | 9.3547 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-16 19:30 | 2.5 | 6.1 | 25 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 159809.037 | 9.3638 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-16 20:30 | 2 | 6.7 | 30 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 160119.037 | 9.382 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-16 21:30 | 2 | 7.3 | 37.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 160609.037 | 9.4107 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-16 22:30 | 2.4 | 7.7 | 40 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 161254.037 | 9.4485 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-16 23:30 | 2.7 | 7.6 | 40 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 161899.037 | 9.4863 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-17 00:30 | 2.9 | 7.6 | 37.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 162544.037 | 9.5241 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-17 01:30 | 2.7 | 7.8 | 32.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 163189.037 | 9.5619 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-17 02:30 | 2.9 | 8.4 | 30 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 163834.037 | 9.5997 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-17 03:30 | 3.2 | 8.9 | 27.5 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 164479.037 | 9.6374 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-17 04:30 | 3.1 | 8.9 | 22.5 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 165124.037 | 9.6752 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-17 05:30 | 3.1 | 8.9 | 17.5 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 165769.037 | 9.713 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-17 06:30 | 3.3 | 8.7 | 7.5 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 166414.037 | 9.7508 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-17 07:30 | 3.3 | 7.6 | 175 | 1840 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 167059.037 | 9.7886 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-17 08:30 | 3 | 6.3 | 350 | 760 | 1300 | 980 | 0 | 980 | 490 | 0 | 167549.037 | 9.8173 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-17 09:30 | 3.1 | 5.9 | 350 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 167704.037 | 9.8264 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-17 10:30 | 3.3 | 5.2 | 350 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 167754.037 | 9.8293 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-01-17 11:30 | 3 | 3.8 | 180 | 0 | 170 | 0 | 150 | 0 | 0 | 333.3333 | 167420.7037 | 9.8098 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-01-17 12:30 | 3.1 | 3.2 | 20 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166709.5926 | 9.7681 | 0 |  |  | 1 | 3 | 1 | 1
Lerwick | 1978-01-17 13:30 | 3.9 | 4.1 | 30 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 166083.6667 | 9.7315 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-01-17 14:30 | 4.5 | 5.5 | 27.5 | 500 | 288.3333 | 0 | 31.6667 | 0 | 0 | 70.3704 | 166013.2963 | 9.7273 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-17 15:30 | 4.6 | 5.9 | 17.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 166103.2963 | 9.7326 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-17 16:30 | 4 | 5.3 | 5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 166153.2963 | 9.7355 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-17 17:30 | 3.6 | 5.2 | 0 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 166163.2963 | 9.7361 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-01-17 18:30 | 3.4 | 4.9 | 0 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 166051.4444 | 9.7296 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-01-17 19:30 | 3.3 | 4.7 | 5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 165783.2963 | 9.7139 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-01-17 20:30 | 3.2 | 5.3 | 17.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 165671.4444 | 9.7073 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-17 21:30 | 3.4 | 5.3 | 25 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 165681.4444 | 9.7079 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-01-17 22:30 | 3.7 | 4.9 | 27.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 165569.5926 | 9.7013 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-01-17 23:30 | 3.7 | 4.4 | 35 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 165165.1481 | 9.6776 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-01-18 00:30 | 4 | 3.5 | 45 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 164539.2222 | 9.641 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-01-18 01:30 | 4 | 2.2 | 40 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163828.1111 | 9.5993 | 0 |  |  | 1 | 5 | 1 | 1
Lerwick | 1978-01-18 02:30 | 3.9 | 0.6 | 15 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163117 | 9.5576 | 0 |  |  | 1 | 6 | 1 | 2
Lerwick | 1978-01-18 03:30 | 3.7 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162405.8889 | 9.516 | 0 |  |  | 1 | 7 | 1 | 3
Lerwick | 1978-01-18 04:30 | 3.4 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161694.7778 | 9.4743 | 0 |  |  | 1 | 8 | 1 | 4
Lerwick | 1978-01-18 05:30 | 3.3 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160983.6667 | 9.4326 | 0 |  |  | 1 | 9 | 1 | 5
Lerwick | 1978-01-18 06:30 | 3.6 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160272.5556 | 9.391 | 0 |  |  | 1 | 10 | 1 | 6
Lerwick | 1978-01-18 07:30 | 3.2 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 159561.4444 | 9.3493 | 0 |  |  | 1 | 11 | 1 | 7
Lerwick | 1978-01-18 08:30 | 2.1 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 158850.3333 | 9.3076 | 0 |  |  | 1 | 12 | 1 | 8
Lerwick | 1978-01-18 09:30 | 1.2 | 0.6 | 137.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 158139.2222 | 9.266 | 0 |  |  | 1 | 13 | 1 | 9
Lerwick | 1978-01-18 10:30 | 1.5 | 2.2 | 227.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 157428.1111 | 9.2243 | 0 |  |  | 1 | 14 | 1 | 10
Lerwick | 1978-01-18 11:30 | 2.6 | 3.8 | 175 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 156717 | 9.1826 | 0 |  |  | 1 | 15 | 1 | 11
Lerwick | 1978-01-18 12:30 | 3.7 | 4.7 | 172.5 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 156227.3704 | 9.1539 | 1 |  |  | 1 | 16 | 0 | 0
Lerwick | 1978-01-18 13:30 | 4.6 | 4.9 | 175 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 155959.2222 | 9.1382 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-18 14:30 | 4.7 | 5.6 | 170 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 155974.0556 | 9.1391 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-18 15:30 | 4 | 6.4 | 162.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 156129.0556 | 9.1482 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-18 16:30 | 3.8 | 7.1 | 160 | 1480 | 1120 | 800 | 0 | 800 | 400 | 0 | 156529.0556 | 9.1716 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-18 17:30 | 4.2 | 7.6 | 162.5 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 157174.0556 | 9.2094 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-18 18:30 | 4.3 | 7.4 | 165 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 157819.0556 | 9.2472 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-18 19:30 | 4.4 | 7.3 | 165 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 158399.0556 | 9.2812 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-18 20:30 | 4.4 | 8.1 | 167.5 | 2200 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 159044.0556 | 9.319 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-18 21:30 | 4.5 | 9 | 167.5 | 2920 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 159689.0556 | 9.3568 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-18 22:30 | 4.1 | 9.5 | 162.5 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 160334.0556 | 9.3946 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-18 23:30 | 3.6 | 10 | 160 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 160979.0556 | 9.4324 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-19 00:30 | 3.5 | 10.3 | 160 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 161624.0556 | 9.4702 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-19 01:30 | 3.5 | 10 | 157.5 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 162269.0556 | 9.508 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-19 02:30 | 3.3 | 9.5 | 152.5 | 3280 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 162914.0556 | 9.5457 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-19 03:30 | 3.2 | 9.3 | 150 | 2920 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 163559.0556 | 9.5835 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-19 04:30 | 3.1 | 9.4 | 150 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 164204.0556 | 9.6213 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-19 05:30 | 3.3 | 9.6 | 150 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 164849.0556 | 9.6591 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-19 06:30 | 3.3 | 9.9 | 150 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 165494.0556 | 9.6969 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-19 07:30 | 3.3 | 10.4 | 150 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 166139.0556 | 9.7347 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-19 08:30 | 3.5 | 11 | 150 | 4300 | 3970 | 3650 | 0 | 1290 | 645 | 0 | 166784.0556 | 9.7725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-19 09:30 | 3.3 | 11.3 | 150 | 4300 | 4300 | 3980 | 0 | 1290 | 645 | 0 | 167429.0556 | 9.8103 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-19 10:30 | 3.3 | 10.8 | 147.5 | 4000 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 168074.0556 | 9.8481 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-19 11:30 | 3 | 10.3 | 145 | 3640 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 168719.0556 | 9.8859 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-19 12:30 | 3.1 | 10.6 | 145 | 4000 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 169364.0556 | 9.9237 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-19 13:30 | 3.6 | 11.2 | 145 | 4300 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-19 14:30 | 3.5 | 11.9 | 147.5 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-19 15:30 | 3.3 | 12.4 | 150 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-19 16:30 | 3.3 | 12.2 | 147.5 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-19 17:30 | 3.5 | 11.4 | 145 | 4300 | 4418.0556 | 4098.0556 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-19 18:30 | 3.6 | 10.6 | 147.5 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-19 19:30 | 3.4 | 11 | 147.5 | 4300 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-19 20:30 | 3.4 | 11.6 | 142.5 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-19 21:30 | 3.9 | 11.6 | 140 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-19 22:30 | 4.5 | 11.1 | 145 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-19 23:30 | 4.7 | 10.9 | 152.5 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-20 00:30 | 4.8 | 11.2 | 152.5 | 4300 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-20 01:30 | 4.9 | 11.2 | 147.5 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-20 02:30 | 5.2 | 10.6 | 145 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-20 03:30 | 5.1 | 9.4 | 150 | 2920 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-20 04:30 | 4.4 | 9.1 | 152.5 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-20 05:30 | 4.4 | 10.9 | 145 | 4000 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-20 06:30 | 5 | 11.7 | 140 | 4472.2222 | 4236.1111 | 3916.1111 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-20 07:30 | 5 | 11.1 | 137.5 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-20 08:30 | 4.6 | 10.3 | 132.5 | 3640 | 3970 | 3650 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-20 09:30 | 4.5 | 9.4 | 135 | 2920 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-20 10:30 | 4.4 | 9 | 145 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-20 11:30 | 4.2 | 9 | 147.5 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-20 12:30 | 4.6 | 8.7 | 142.5 | 2560 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-20 13:30 | 4.8 | 8.3 | 137.5 | 2200 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-20 14:30 | 4.6 | 8.1 | 132.5 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-20 15:30 | 4.4 | 8.3 | 130 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-20 16:30 | 4.3 | 8.5 | 130 | 2560 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-20 17:30 | 4.4 | 8.5 | 130 | 2560 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-20 18:30 | 4.5 | 8.3 | 130 | 2200 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-20 19:30 | 4.2 | 7.4 | 130 | 1480 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-20 20:30 | 4.2 | 6.4 | 132.5 | 760 | 1120 | 800 | 0 | 800 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-20 21:30 | 4.2 | 6.6 | 137.5 | 1120 | 940 | 620 | 0 | 620 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-20 22:30 | 4.2 | 7.3 | 142.5 | 1480 | 1300 | 980 | 0 | 980 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-20 23:30 | 4.7 | 8.2 | 147.5 | 2200 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-21 00:30 | 4.9 | 9.1 | 150 | 2920 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-21 01:30 | 5 | 9.6 | 150 | 3280 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-21 02:30 | 5 | 9.9 | 150 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-21 03:30 | 5 | 10.2 | 150 | 3640 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-21 04:30 | 4.7 | 10.9 | 147.5 | 4000 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-21 05:30 | 4.5 | 11.4 | 142.5 | 4300 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-21 06:30 | 4.7 | 11.2 | 140 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-21 07:30 | 4.9 | 10.9 | 142.5 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-21 08:30 | 5.2 | 10.9 | 147.5 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-21 09:30 | 5.2 | 11.2 | 145 | 4300 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-21 10:30 | 5.3 | 11.9 | 137.5 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-21 11:30 | 5.2 | 12.4 | 137.5 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-21 12:30 | 5.2 | 12.4 | 140 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-21 13:30 | 5.4 | 12.2 | 140 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-21 14:30 | 5.3 | 11.7 | 140 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-21 15:30 | 5.3 | 11.5 | 140 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-21 16:30 | 5.2 | 11.6 | 140 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-21 17:30 | 5.1 | 11.9 | 140 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-21 18:30 | 5.3 | 12 | 140 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-21 19:30 | 5.3 | 11.9 | 142.5 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-21 20:30 | 5.2 | 11.6 | 147.5 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-21 21:30 | 4.9 | 11.6 | 147.5 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-21 22:30 | 4.9 | 11.9 | 142.5 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-21 23:30 | 5.1 | 12 | 140 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-22 00:30 | 5.4 | 12.4 | 140 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-22 01:30 | 5.2 | 13.1 | 140 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-22 02:30 | 5.1 | 13.4 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-22 03:30 | 5 | 13.4 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-22 04:30 | 4.6 | 13.6 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-22 05:30 | 4.3 | 14.4 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-22 06:30 | 4.3 | 15 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-22 07:30 | 4.1 | 14.9 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-22 08:30 | 4.2 | 14.4 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-22 09:30 | 4.6 | 14 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-22 10:30 | 4.9 | 13.7 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-22 11:30 | 5.1 | 13.3 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-22 12:30 | 5.3 | 13 | 142.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-22 13:30 | 5.6 | 12.7 | 147.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-22 14:30 | 5.7 | 12.5 | 150 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-22 15:30 | 5.7 | 12.7 | 150 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-22 16:30 | 5.6 | 12.9 | 152.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-22 17:30 | 5.5 | 13 | 157.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-22 18:30 | 5.6 | 12.8 | 160 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-22 19:30 | 5.4 | 11.6 | 157.5 | 4472.2222 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-22 20:30 | 5.3 | 10 | 157.5 | 3640 | 4056.1111 | 3736.1111 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-22 21:30 | 5.5 | 8.7 | 165 | 2560 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-22 22:30 | 5.4 | 7.2 | 172.5 | 1480 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-22 23:30 | 5.4 | 6.9 | 202.5 | 1120 | 1300 | 980 | 0 | 980 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-23 00:30 | 5.1 | 9.2 | 252.5 | 2920 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-23 01:30 | 3.8 | 11.1 | 270 | 4300 | 3610 | 3290 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-23 02:30 | 2.7 | 9.9 | 262.5 | 3280 | 3790 | 3470 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-23 03:30 | 2.7 | 7.6 | 255 | 1840 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-23 04:30 | 2.8 | 5.6 | 240 | 500 | 1170 | 850 | 0 | 850 | 0 | 0 | 170009.0556 | 9.9615 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-01-23 05:30 | 2.4 | 3.8 | 227.5 | 0 | 250 | 0 | 70 | 0 | 0 | 155.5556 | 169853.5 | 9.9524 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-01-23 06:30 | 1.7 | 2.6 | 217.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 169142.3889 | 9.9107 | 0 |  |  | 1 | 3 | 1 | 1
Lerwick | 1978-01-23 07:30 | 1.7 | 2.2 | 202.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168431.2778 | 9.869 | 0 |  |  | 1 | 4 | 1 | 2
Lerwick | 1978-01-23 08:30 | 1.9 | 2.7 | 197.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167720.1667 | 9.8274 | 0 |  |  | 1 | 5 | 1 | 3
Lerwick | 1978-01-23 09:30 | 1.7 | 3.3 | 200 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167009.0556 | 9.7857 | 0 |  |  | 1 | 6 | 1 | 4
Lerwick | 1978-01-23 10:30 | 1.7 | 3.9 | 195 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166297.9444 | 9.744 | 0 |  |  | 1 | 7 | 1 | 5
Lerwick | 1978-01-23 11:30 | 2.3 | 5.3 | 182.5 | 340 | 170 | 0 | 150 | 0 | 0 | 333.3333 | 165964.6111 | 9.7245 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-23 12:30 | 3.2 | 6.3 | 175 | 760 | 550 | 230 | 0 | 230 | 115 | 0 | 166079.6111 | 9.7312 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-23 13:30 | 3.5 | 6.4 | 175 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 166299.6111 | 9.7441 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-23 14:30 | 3.4 | 6.4 | 172.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 166519.6111 | 9.757 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-23 15:30 | 3.7 | 5.9 | 172.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 166674.6111 | 9.7661 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-23 16:30 | 3.4 | 4.9 | 167.5 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 166689.4444 | 9.767 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-01-23 17:30 | 2.5 | 4.9 | 145 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 166421.2963 | 9.7512 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-23 18:30 | 3 | 6 | 122.5 | 760 | 479.6667 | 159.6667 | 0 | 159.6667 | 79.8333 | 0 | 166501.1296 | 9.7559 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-23 19:30 | 3.8 | 6.8 | 115 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 166811.1296 | 9.7741 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-23 20:30 | 3.9 | 7.5 | 122.5 | 1840 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 167391.1296 | 9.8081 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-23 21:30 | 4.2 | 9 | 135 | 2920 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 168036.1296 | 9.8459 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-23 22:30 | 4.3 | 10.4 | 137.5 | 3640 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 168681.1296 | 9.8837 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-23 23:30 | 4.4 | 11 | 132.5 | 4300 | 3970 | 3650 | 0 | 1290 | 645 | 0 | 169326.1296 | 9.9215 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-24 00:30 | 4.3 | 11.4 | 127.5 | 4300 | 4300 | 3980 | 0 | 1290 | 645 | 0 | 169971.1296 | 9.9592 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-24 01:30 | 4.3 | 11.5 | 125 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 170616.1296 | 9.997 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-24 02:30 | 4.4 | 11.6 | 127.5 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170616.1296 | 9.997 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-24 03:30 | 4 | 11.5 | 130 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170616.1296 | 9.997 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-24 04:30 | 3.8 | 11 | 127.5 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170616.1296 | 9.997 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-24 05:30 | 3.6 | 11 | 122.5 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170616.1296 | 9.997 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-24 06:30 | 3.5 | 11.4 | 120 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170616.1296 | 9.997 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-24 07:30 | 3.6 | 11.1 | 120 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170616.1296 | 9.997 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-24 08:30 | 3.3 | 10.6 | 120 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170616.1296 | 9.997 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-24 09:30 | 3.2 | 10.9 | 117.5 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170616.1296 | 9.997 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-24 10:30 | 3.3 | 11.5 | 110 | 4472.2222 | 4236.1111 | 3916.1111 | 0 | 1290 | 0 | 0 | 170616.1296 | 9.997 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-24 11:30 | 3.1 | 11.6 | 102.5 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170616.1296 | 9.997 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-24 12:30 | 2.7 | 11.1 | 97.5 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170616.1296 | 9.997 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-24 13:30 | 2.4 | 10.3 | 90 | 3640 | 3970 | 3650 | 0 | 1290 | 0 | 0 | 170616.1296 | 9.997 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-24 14:30 | 2.5 | 9.3 | 82.5 | 2920 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170616.1296 | 9.997 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-24 15:30 | 2.5 | 8.4 | 82.5 | 2200 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170616.1296 | 9.997 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-24 16:30 | 2.1 | 7.7 | 82.5 | 1840 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170616.1296 | 9.997 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-24 17:30 | 2 | 6.8 | 75 | 1120 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170616.1296 | 9.997 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-24 18:30 | 1.8 | 6.2 | 67.5 | 760 | 940 | 620 | 0 | 620 | 0 | 0 | 170616.1296 | 9.997 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-24 19:30 | 2.1 | 6 | 62.5 | 760 | 760 | 440 | 0 | 440 | 0 | 0 | 170616.1296 | 9.997 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-24 20:30 | 2.3 | 4.7 | 57.5 | 199.3333 | 479.6667 | 159.6667 | 0 | 159.6667 | 0 | 0 | 170616.1296 | 9.997 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-01-24 21:30 | 2.1 | 3.1 | 35 | 0 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 170126.5 | 9.9683 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-01-24 22:30 | 2.5 | 3.1 | 177.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 169415.3889 | 9.9267 | 0 |  |  | 1 | 3 | 1 | 1
Lerwick | 1978-01-24 23:30 | 2.6 | 4 | 335 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 168789.463 | 9.89 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-01-25 00:30 | 2.3 | 4.7 | 322.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 168385.0185 | 9.8663 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-01-25 01:30 | 2 | 5.3 | 312.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 168273.1667 | 9.8598 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-25 02:30 | 2.2 | 6.2 | 312.5 | 760 | 550 | 230 | 0 | 230 | 115 | 0 | 168388.1667 | 9.8665 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-25 03:30 | 2.5 | 7.1 | 320 | 1480 | 1120 | 800 | 0 | 800 | 400 | 0 | 168788.1667 | 9.8899 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-25 04:30 | 2.3 | 7.3 | 327.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 169368.1667 | 9.9239 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-25 05:30 | 2.4 | 6.9 | 330 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 169858.1667 | 9.9526 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-25 06:30 | 2.5 | 6.5 | 330 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 170258.1667 | 9.9761 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-25 07:30 | 2.3 | 6.1 | 327.5 | 760 | 940 | 620 | 0 | 620 | 0 | 0 | 170258.1667 | 9.9761 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-25 08:30 | 2.1 | 5.4 | 327.5 | 340 | 550 | 230 | 0 | 230 | 0 | 0 | 170258.1667 | 9.9761 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-01-25 09:30 | 2.3 | 4.4 | 332.5 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 170010.0185 | 9.9615 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-01-25 10:30 | 2.4 | 4.2 | 327.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 169469.2778 | 9.9298 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-01-25 11:30 | 2.7 | 4.4 | 317.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 168928.537 | 9.8982 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-01-25 12:30 | 3.6 | 4.2 | 320 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 168387.7963 | 9.8665 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-01-25 13:30 | 3.5 | 3.6 | 320 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 167761.8704 | 9.8298 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-01-25 14:30 | 3.2 | 3.6 | 312.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167050.7593 | 9.7881 | 0 |  |  | 1 | 7 | 1 | 1
Lerwick | 1978-01-25 15:30 | 3.4 | 4.2 | 322.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 166424.8333 | 9.7515 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-01-25 16:30 | 3.1 | 4.4 | 335 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 165884.0926 | 9.7198 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-01-25 17:30 | 2.1 | 4.4 | 327.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 165343.3519 | 9.6881 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-01-25 18:30 | 1.7 | 4.2 | 312.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 164802.6111 | 9.6564 | 1 |  |  | 1 | 11 | 0 | 0
Lerwick | 1978-01-25 19:30 | 2 | 4 | 297.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 164261.8704 | 9.6247 | 1 |  |  | 1 | 12 | 0 | 0
Lerwick | 1978-01-25 20:30 | 1.8 | 4.2 | 287.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 163721.1296 | 9.593 | 1 |  |  | 1 | 13 | 0 | 0
Lerwick | 1978-01-25 21:30 | 1.7 | 4.9 | 285 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 163316.6852 | 9.5693 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-25 22:30 | 1.8 | 5.5 | 285 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 163331.5185 | 9.5702 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-25 23:30 | 2 | 5.5 | 280 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 163421.5185 | 9.5755 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-26 00:30 | 1.7 | 5.4 | 272.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 163471.5185 | 9.5784 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-26 01:30 | 1.5 | 5.5 | 270 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 163521.5185 | 9.5813 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-26 02:30 | 1.7 | 5.8 | 270 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 163611.5185 | 9.5866 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-26 03:30 | 1.9 | 5.9 | 272.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 163701.5185 | 9.5919 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-26 04:30 | 2 | 5.9 | 277.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 163791.5185 | 9.5972 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-26 05:30 | 2.2 | 6.1 | 277.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 163946.5185 | 9.6062 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-26 06:30 | 2.2 | 6.5 | 275 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 164256.5185 | 9.6244 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-26 07:30 | 2.3 | 6.7 | 275 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 164656.5185 | 9.6478 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-26 08:30 | 2.3 | 7.1 | 272.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 165146.5185 | 9.6766 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-26 09:30 | 1.8 | 7.7 | 270 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 165791.5185 | 9.7143 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-26 10:30 | 1.7 | 8 | 270 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 166436.5185 | 9.7521 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-26 11:30 | 1.7 | 8 | 267.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 167081.5185 | 9.7899 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-26 12:30 | 1.6 | 7.5 | 270 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 167726.5185 | 9.8277 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-26 13:30 | 1.8 | 6.6 | 290 | 1120 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 168306.5185 | 9.8617 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-26 14:30 | 2 | 6.4 | 310 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 168616.5185 | 9.8799 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-26 15:30 | 2 | 7.2 | 312.5 | 1480 | 1120 | 800 | 0 | 800 | 400 | 0 | 169016.5185 | 9.9033 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-26 16:30 | 2 | 8.1 | 317.5 | 2200 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 169661.5185 | 9.9411 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-26 17:30 | 1.7 | 8 | 332.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 170306.5185 | 9.9789 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-26 18:30 | 1.2 | 6.9 | 337.5 | 1120 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170306.5185 | 9.9789 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-26 19:30 | 1.1 | 6.7 | 330 | 1120 | 1120 | 800 | 0 | 800 | 0 | 0 | 170306.5185 | 9.9789 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-26 20:30 | 1.2 | 7 | 322.5 | 1480 | 1300 | 980 | 0 | 980 | 0 | 0 | 170306.5185 | 9.9789 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-26 21:30 | 1.1 | 6.7 | 322.5 | 1120 | 1300 | 980 | 0 | 980 | 0 | 0 | 170306.5185 | 9.9789 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-26 22:30 | 1 | 6.4 | 327.5 | 760 | 940 | 620 | 0 | 620 | 0 | 0 | 170306.5185 | 9.9789 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-26 23:30 | 0.7 | 6.4 | 327.5 | 760 | 760 | 440 | 0 | 440 | 0 | 0 | 170306.5185 | 9.9789 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-27 00:30 | 0.1 | 6.4 | 322.5 | 760 | 760 | 440 | 0 | 440 | 0 | 0 | 170306.5185 | 9.9789 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-27 01:30 | 0.2 | 6.3 | 317.5 | 760 | 760 | 440 | 0 | 440 | 0 | 0 | 170306.5185 | 9.9789 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-27 02:30 | 0.2 | 5.9 | 317.5 | 500 | 630 | 310 | 0 | 310 | 0 | 0 | 170306.5185 | 9.9789 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-27 03:30 | 0 | 5.1 | 317.5 | 340 | 420 | 100 | 0 | 100 | 0 | 0 | 170306.5185 | 9.9789 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-01-27 04:30 | 0 | 4.2 | 312.5 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 170058.3704 | 9.9644 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-01-27 05:30 | 0 | 3.9 | 320 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 169432.4444 | 9.9277 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-01-27 06:30 | 0 | 4.2 | 337.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 168806.5185 | 9.891 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-01-27 07:30 | -0.1 | 4.4 | 172.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 168265.7778 | 9.8593 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-01-27 08:30 | -0.1 | 4.4 | 5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 167725.037 | 9.8276 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-01-27 09:30 | 0.1 | 4.2 | 15 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 167184.2963 | 9.796 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-01-27 10:30 | 0.3 | 3.8 | 30 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 166558.3704 | 9.7593 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-01-27 11:30 | 0.2 | 4.2 | 22.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 165932.4444 | 9.7226 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-01-27 12:30 | 0.2 | 5.3 | 162.5 | 340 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 165684.2963 | 9.7081 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-27 13:30 | 0.2 | 5.5 | 320 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 165734.2963 | 9.711 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-27 14:30 | 0.1 | 5.6 | 165 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 165824.2963 | 9.7163 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-27 15:30 | 0.1 | 5.6 | 37.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 165914.2963 | 9.7215 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-27 16:30 | 0.1 | 4.6 | 70 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 165929.1296 | 9.7224 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-01-27 17:30 | 0 | 3.9 | 67.5 | 0 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 165439.5 | 9.6937 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-01-27 18:30 | 0 | 4.1 | 72.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 164813.5741 | 9.657 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-01-27 19:30 | 0 | 4.4 | 100 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 164272.8333 | 9.6254 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-01-27 20:30 | 0 | 4.7 | 107.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 163868.3889 | 9.6017 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-01-27 21:30 | 0 | 5.4 | 92.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 163756.537 | 9.5951 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-27 22:30 | 0 | 6.1 | 77.5 | 760 | 550 | 230 | 0 | 230 | 115 | 0 | 163871.537 | 9.6018 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-27 23:30 | 0 | 6.4 | 70 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 164091.537 | 9.6147 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-28 00:30 | 0 | 6.8 | 75 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 164401.537 | 9.6329 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-28 01:30 | 0 | 8 | 82.5 | 2200 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 165046.537 | 9.6707 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-28 02:30 | 0.3 | 9.6 | 80 | 3280 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 165691.537 | 9.7085 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-28 03:30 | 0.9 | 11.7 | 72.5 | 4472.2222 | 3876.1111 | 3556.1111 | 0 | 1290 | 645 | 0 | 166336.537 | 9.7463 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-28 04:30 | 1.2 | 13.5 | 67.5 | 4600 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 166981.537 | 9.7841 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-28 05:30 | 1.1 | 14.4 | 62.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 167626.537 | 9.8219 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-28 06:30 | 1 | 14.9 | 60 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 168271.537 | 9.8597 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-28 07:30 | 0.9 | 15.4 | 60 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 168916.537 | 9.8975 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-28 08:30 | 1.1 | 16.1 | 60 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 169561.537 | 9.9352 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-28 09:30 | 1.3 | 17.4 | 57.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 170206.537 | 9.973 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-28 10:30 | 1.1 | 19 | 52.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170206.537 | 9.973 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-28 11:30 | 0.7 | 19.8 | 50 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170206.537 | 9.973 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-28 12:30 | 0.3 | 19.9 | 50 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170206.537 | 9.973 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-28 13:30 | 0 | 20.3 | 47.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170206.537 | 9.973 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-28 14:30 | -0.1 | 20.7 | 42.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170206.537 | 9.973 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-28 15:30 | 0 | 20.9 | 40 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170206.537 | 9.973 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-28 16:30 | 0 | 21.2 | 40 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170206.537 | 9.973 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-28 17:30 | 0 | 21.7 | 40 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170206.537 | 9.973 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-28 18:30 | 0 | 22.1 | 40 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170206.537 | 9.973 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-28 19:30 | 0 | 21.7 | 37.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170206.537 | 9.973 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-28 20:30 | 0 | 21.5 | 32.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170206.537 | 9.973 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-28 21:30 | 0 | 22.3 | 30 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170206.537 | 9.973 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-28 22:30 | 0 | 22.9 | 30 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170206.537 | 9.973 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-28 23:30 | 0 | 22.9 | 30 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170206.537 | 9.973 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-29 00:30 | 0 | 22.5 | 30 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170206.537 | 9.973 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-29 01:30 | 0 | 11.1 | 15 | 4300 | 4450 | 4130 | 0 | 1290 | 0 | 0 | 170206.537 | 9.973 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-29 02:30 | 0 | 0 | 0 | 0 | 2150 | 1830 | 0 | 1290 | 0 | 0 | 170206.537 | 9.973 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-01-29 03:30 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 169495.4259 | 9.9314 | 0 |  |  | 0 | 0 | 1 | 1
Lerwick | 1978-01-29 04:30 | 0 | 10.9 | 12.5 | 4000 | 2000 | 1680 | 0 | 1290 | 645 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-29 05:30 | 0 | 21.3 | 27.5 | 4600 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-29 06:30 | 0.1 | 20.4 | 27.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-29 07:30 | 0.2 | 19.8 | 22.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-29 08:30 | 0.3 | 19 | 20 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-29 09:30 | 0.3 | 18 | 20 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-29 10:30 | 0.4 | 17.1 | 20 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-29 11:30 | 0.7 | 16.4 | 20 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-29 12:30 | 1 | 16.2 | 17.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-29 13:30 | 0.9 | 16.3 | 12.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-29 14:30 | 0.4 | 16.3 | 7.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-29 15:30 | 0.2 | 16.2 | 2.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-29 16:30 | 0.4 | 15.9 | 2.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-29 17:30 | 0.2 | 15.5 | 5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-29 18:30 | 0.2 | 15.5 | 2.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-29 19:30 | 0.6 | 15.3 | 0 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-29 20:30 | 0.5 | 14.4 | 0 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-29 21:30 | 0.1 | 13.5 | 0 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-29 22:30 | 0 | 12.2 | 177.5 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-29 23:30 | -0.2 | 10.6 | 355 | 4000 | 4268.0556 | 3948.0556 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-30 00:30 | -0.4 | 10.1 | 177.5 | 3640 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-30 01:30 | -0.4 | 10.3 | 177.5 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-30 02:30 | -0.2 | 10.3 | 352.5 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-30 03:30 | -0.6 | 10.3 | 352.5 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-30 04:30 | -1.2 | 10.1 | 355 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-30 05:30 | -1 | 9.5 | 352.5 | 3280 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-30 06:30 | -0.6 | 8.9 | 350 | 2560 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-30 07:30 | -0.4 | 8.6 | 347.5 | 2560 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-30 08:30 | -0.9 | 8 | 342.5 | 2200 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-30 09:30 | -1.8 | 7.5 | 342.5 | 1840 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-30 10:30 | -1.6 | 7.8 | 350 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-30 11:30 | -0.6 | 7.8 | 350 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-30 12:30 | -0.3 | 7.1 | 337.5 | 1480 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-30 13:30 | -0.5 | 7.1 | 330 | 1480 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-30 14:30 | -0.8 | 7.8 | 335 | 1840 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-30 15:30 | -0.4 | 8.3 | 345 | 2200 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-30 16:30 | -0.4 | 8.6 | 352.5 | 2560 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-30 17:30 | -0.8 | 4.4 | 177.5 | 76.6667 | 1318.3333 | 998.3333 | 0 | 998.3333 | 0 | 0 | 170140.4259 | 9.9692 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-01-30 18:30 | -1 | 0 | 0 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 169514.5 | 9.9325 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-01-30 19:30 | -0.8 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168803.3889 | 9.8908 | 0 |  |  | 1 | 3 | 1 | 1
Lerwick | 1978-01-30 20:30 | -1.1 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168092.2778 | 9.8492 | 0 |  |  | 1 | 4 | 1 | 2
Lerwick | 1978-01-30 21:30 | -0.8 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167381.1667 | 9.8075 | 0 |  |  | 1 | 5 | 1 | 3
Lerwick | 1978-01-30 22:30 | -0.2 | 3.2 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166670.0556 | 9.7658 | 0 |  |  | 0 | 0 | 1 | 4
Lerwick | 1978-01-30 23:30 | -0.7 | 6.3 | 0 | 760 | 380 | 60 | 0 | 60 | 30 | 0 | 166700.0556 | 9.7676 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-31 00:30 | -0.8 | 5.8 | 177.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 166855.0556 | 9.7767 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-31 01:30 | -0.7 | 4.9 | 350 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 166869.8889 | 9.7775 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-01-31 02:30 | -1.5 | 4 | 342.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 166465.4444 | 9.7538 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-01-31 03:30 | -1.3 | 3.6 | 342.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 165839.5185 | 9.7172 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-01-31 04:30 | -1.1 | 3.8 | 175 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165128.4074 | 9.6755 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-01-31 05:30 | -2.1 | 3.3 | 2.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164417.2963 | 9.6338 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-01-31 06:30 | -1.6 | 2.2 | 170 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163706.1852 | 9.5922 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-01-31 07:30 | -1.3 | 2.4 | 175 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162995.0741 | 9.5505 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-01-31 08:30 | -2.4 | 2.6 | 40 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162283.963 | 9.5088 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-01-31 09:30 | -1.5 | 1.7 | 72.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161572.8519 | 9.4672 | 0 |  |  | 1 | 9 | 1 | 6
Lerwick | 1978-01-31 10:30 | 0 | 1.5 | 200 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160861.7407 | 9.4255 | 0 |  |  | 1 | 10 | 1 | 7
Lerwick | 1978-01-31 11:30 | 0 | 2.4 | 250 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160150.6296 | 9.3838 | 0 |  |  | 1 | 11 | 1 | 8
Lerwick | 1978-01-31 12:30 | 0.5 | 3.7 | 145 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 159439.5185 | 9.3422 | 0 |  |  | 1 | 12 | 1 | 9
Lerwick | 1978-01-31 13:30 | 1.1 | 4.4 | 117.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 158813.5926 | 9.3055 | 1 |  |  | 1 | 13 | 0 | 0
Lerwick | 1978-01-31 14:30 | 0.9 | 4.4 | 120 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 158272.8519 | 9.2738 | 1 |  |  | 1 | 14 | 0 | 0
Lerwick | 1978-01-31 15:30 | 1.1 | 4.9 | 117.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 157868.4074 | 9.2501 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-31 16:30 | 1.6 | 5.5 | 110 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 157883.2407 | 9.251 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-31 17:30 | 1 | 5.8 | 105 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 157973.2407 | 9.2562 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-31 18:30 | 0.5 | 6.1 | 110 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 158128.2407 | 9.2653 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-31 19:30 | 1.3 | 6.8 | 120 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 158438.2407 | 9.2835 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-31 20:30 | 2.3 | 7.6 | 125 | 1840 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 159018.2407 | 9.3175 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-31 21:30 | 1.8 | 8.4 | 122.5 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 159663.2407 | 9.3553 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-31 22:30 | 1.2 | 9 | 120 | 2920 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 160308.2407 | 9.3931 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-01-31 23:30 | 1.2 | 9.4 | 120 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 160953.2407 | 9.4309 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-01 00:30 | 1.6 | 9.5 | 120 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 161598.2407 | 9.4686 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-01 01:30 | 2 | 9.6 | 122.5 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 162243.2407 | 9.5064 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-01 02:30 | 2.1 | 10.3 | 127.5 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 162888.2407 | 9.5442 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-01 03:30 | 2.6 | 11.1 | 132.5 | 4300 | 3970 | 3650 | 0 | 1290 | 645 | 0 | 163533.2407 | 9.582 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-01 04:30 | 3.2 | 11.9 | 137.5 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 164178.2407 | 9.6198 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-01 05:30 | 3.3 | 12.4 | 140 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 645 | 0 | 164823.2407 | 9.6576 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-01 06:30 | 3.3 | 12.2 | 140 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 165468.2407 | 9.6954 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-01 07:30 | 3 | 12.2 | 142.5 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 166113.2407 | 9.7332 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-01 08:30 | 3.3 | 12.7 | 147.5 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 645 | 0 | 166758.2407 | 9.771 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-01 09:30 | 3.8 | 13.5 | 150 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 167403.2407 | 9.8088 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-01 10:30 | 3.7 | 14.4 | 150 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 168048.2407 | 9.8466 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-01 11:30 | 3.9 | 15.1 | 147.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 168693.2407 | 9.8844 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-01 12:30 | 4 | 15.4 | 142.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 169338.2407 | 9.9222 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-01 13:30 | 3.9 | 15.3 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 169983.2407 | 9.96 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-01 14:30 | 3.9 | 15.2 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-01 15:30 | 3.9 | 15 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-01 16:30 | 3.8 | 14.8 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-01 17:30 | 3.9 | 14.7 | 137.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-01 18:30 | 4 | 14.7 | 135 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-01 19:30 | 4 | 14.7 | 137.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-01 20:30 | 3.9 | 14.1 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-01 21:30 | 3.9 | 13.2 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-01 22:30 | 3.7 | 12.7 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-01 23:30 | 3.6 | 12.1 | 142.5 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-02 00:30 | 3.4 | 11.5 | 147.5 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-02 01:30 | 3.4 | 11.1 | 150 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-02 02:30 | 3.6 | 10.7 | 147.5 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-02 03:30 | 3.3 | 10.2 | 142.5 | 3640 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-02 04:30 | 2.9 | 10 | 142.5 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-02 05:30 | 2.9 | 10.1 | 147.5 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-02 06:30 | 3.3 | 10.3 | 150 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-02 07:30 | 3.5 | 10.4 | 150 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-02 08:30 | 3.4 | 10.6 | 150 | 4000 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-02 09:30 | 3.3 | 10.6 | 150 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-02 10:30 | 3.2 | 10.4 | 150 | 3640 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-02 11:30 | 3.2 | 10.3 | 150 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-02 12:30 | 3.4 | 10.3 | 150 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-02 13:30 | 3.1 | 10.3 | 150 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-02 14:30 | 2.5 | 10.3 | 147.5 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-02 15:30 | 2.5 | 10.1 | 145 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-02 16:30 | 2.9 | 9.7 | 150 | 3280 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-02 17:30 | 3.2 | 9.6 | 157.5 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-02 18:30 | 3 | 10.1 | 160 | 3640 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-02 19:30 | 3 | 10.9 | 162.5 | 4000 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-02 20:30 | 3.6 | 11.8 | 167.5 | 4472.2222 | 4236.1111 | 3916.1111 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-02 21:30 | 3.5 | 12.6 | 170 | 4600 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-02 22:30 | 2.9 | 13.1 | 170 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-02 23:30 | 2.6 | 13.5 | 170 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-03 00:30 | 2.4 | 13 | 170 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-03 01:30 | 2.4 | 11.1 | 172.5 | 4300 | 4450 | 4130 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-03 02:30 | 2.7 | 8 | 185 | 2200 | 3250 | 2930 | 0 | 1290 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-03 03:30 | 2.8 | 5.8 | 207.5 | 500 | 1350 | 1030 | 0 | 1030 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-03 04:30 | 3.2 | 5.4 | 225 | 340 | 420 | 100 | 0 | 100 | 0 | 0 | 170628.2407 | 9.9977 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-02-03 05:30 | 3.2 | 4.9 | 230 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 170516.3889 | 9.9912 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-02-03 06:30 | 2.7 | 4.2 | 227.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 170111.9444 | 9.9675 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-02-03 07:30 | 2.5 | 4 | 220 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 169571.2037 | 9.9358 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-02-03 08:30 | 2.4 | 3.9 | 210 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 168945.2778 | 9.8991 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-02-03 09:30 | 2.2 | 3.9 | 202.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168234.1667 | 9.8575 | 0 |  |  | 1 | 6 | 1 | 1
Lerwick | 1978-02-03 10:30 | 2.3 | 4.4 | 197.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 167608.2407 | 9.8208 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-02-03 11:30 | 3.2 | 5.4 | 190 | 340 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 167360.0926 | 9.8063 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-03 12:30 | 4 | 6.7 | 182.5 | 1120 | 730 | 410 | 0 | 410 | 205 | 0 | 167565.0926 | 9.8183 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-03 13:30 | 4.3 | 8 | 180 | 2200 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 168210.0926 | 9.8561 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-03 14:30 | 4.5 | 8.9 | 177.5 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 168855.0926 | 9.8939 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-03 15:30 | 4.4 | 9.5 | 172.5 | 3280 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 169500.0926 | 9.9316 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-03 16:30 | 4.4 | 10.1 | 170 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-03 17:30 | 4.3 | 11 | 170 | 4300 | 3970 | 3650 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-03 18:30 | 4.4 | 11.9 | 170 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-03 19:30 | 4.6 | 12.9 | 170 | 4600 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-03 20:30 | 4.7 | 13.8 | 167.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-03 21:30 | 4.7 | 14.3 | 162.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-03 22:30 | 4.7 | 14.5 | 160 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-03 23:30 | 4.7 | 14.9 | 160 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-04 00:30 | 4.6 | 15.6 | 160 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-04 01:30 | 4.4 | 16.2 | 162.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-04 02:30 | 4.2 | 16.3 | 165 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-04 03:30 | 3.9 | 16.3 | 165 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-04 04:30 | 3.9 | 16.7 | 167.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-04 05:30 | 4 | 16.8 | 167.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-04 06:30 | 3.7 | 16.8 | 162.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-04 07:30 | 3.6 | 17.2 | 160 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-04 08:30 | 3.7 | 17.4 | 162.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-04 09:30 | 3.7 | 17.3 | 167.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-04 10:30 | 3.8 | 17.3 | 170 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-04 11:30 | 3.8 | 17.1 | 170 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-04 12:30 | 3.7 | 17 | 170 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-04 13:30 | 3.5 | 17 | 170 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-04 14:30 | 3.4 | 16.8 | 167.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-04 15:30 | 3.5 | 16.7 | 162.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-04 16:30 | 3.5 | 16.7 | 160 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-04 17:30 | 3.6 | 16.7 | 160 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-04 18:30 | 3.7 | 16.7 | 160 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-04 19:30 | 3.7 | 16.6 | 160 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-04 20:30 | 3.6 | 16.3 | 160 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-04 21:30 | 3.5 | 15.9 | 160 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-04 22:30 | 3.5 | 15.4 | 160 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-04 23:30 | 3.5 | 15.3 | 160 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-05 00:30 | 3.4 | 15.5 | 160 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-05 01:30 | 3.5 | 15.4 | 160 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-05 02:30 | 3.8 | 14.8 | 160 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-05 03:30 | 4 | 14.1 | 160 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-05 04:30 | 4.1 | 13.9 | 157.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-05 05:30 | 4.1 | 13.7 | 152.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-05 06:30 | 3.9 | 13.3 | 150 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-05 07:30 | 3.9 | 13 | 150 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-05 08:30 | 3.9 | 12.7 | 150 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-05 09:30 | 3.9 | 12.4 | 150 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-05 10:30 | 4 | 12.1 | 150 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-05 11:30 | 4.1 | 11.6 | 150 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-05 12:30 | 4.1 | 11.7 | 150 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-05 13:30 | 3.9 | 12.2 | 147.5 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-05 14:30 | 3.9 | 12.7 | 142.5 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-05 15:30 | 3.9 | 12.9 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-05 16:30 | 3.8 | 12.9 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-05 17:30 | 3.8 | 12.7 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-05 18:30 | 3.9 | 12.4 | 140 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-05 19:30 | 3.9 | 12.4 | 140 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-05 20:30 | 4 | 12.4 | 140 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-05 21:30 | 3.9 | 12.7 | 140 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-05 22:30 | 3.7 | 12.9 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-05 23:30 | 3.6 | 12.7 | 137.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-06 00:30 | 3.7 | 12.2 | 132.5 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-06 01:30 | 3.7 | 11.9 | 132.5 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-06 02:30 | 3.5 | 11.8 | 137.5 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-06 03:30 | 3.4 | 11.8 | 140 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-06 04:30 | 3.2 | 11.8 | 140 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-06 05:30 | 3 | 11.6 | 140 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-06 06:30 | 3 | 11.1 | 140 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-06 07:30 | 2.7 | 10.5 | 140 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-06 08:30 | 2.6 | 10.5 | 140 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-06 09:30 | 3 | 11.1 | 140 | 4300 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-06 10:30 | 2.9 | 11.6 | 140 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-06 11:30 | 2.6 | 11.6 | 140 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-06 12:30 | 2.6 | 11.4 | 140 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-06 13:30 | 2.5 | 11.1 | 140 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-06 14:30 | 2.5 | 10.6 | 140 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-06 15:30 | 2.8 | 10.1 | 140 | 3640 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-06 16:30 | 3 | 10 | 137.5 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-06 17:30 | 2.8 | 9.9 | 132.5 | 3280 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-06 18:30 | 2.7 | 9.6 | 130 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-06 19:30 | 2.7 | 9.4 | 127.5 | 2920 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-06 20:30 | 2.5 | 9 | 125 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-06 21:30 | 2.4 | 8.4 | 130 | 2200 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-06 22:30 | 2.9 | 8 | 137.5 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-06 23:30 | 2.7 | 8 | 142.5 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-07 00:30 | 2.2 | 8 | 150 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-07 01:30 | 2.6 | 8.1 | 155 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-07 02:30 | 3 | 8.1 | 152.5 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-07 03:30 | 3 | 8.3 | 150 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-07 04:30 | 2.8 | 8.5 | 152.5 | 2560 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-07 05:30 | 2.6 | 8.3 | 157.5 | 2200 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-07 06:30 | 2.7 | 8.1 | 160 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-07 07:30 | 2.7 | 8.1 | 157.5 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-07 08:30 | 2.8 | 7.9 | 152.5 | 1840 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-07 09:30 | 3 | 7.4 | 147.5 | 1480 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-07 10:30 | 3 | 7.2 | 142.5 | 1480 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-07 11:30 | 3.1 | 6.9 | 140 | 1120 | 1300 | 980 | 0 | 980 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-07 12:30 | 3.4 | 6.2 | 142.5 | 760 | 940 | 620 | 0 | 620 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-07 13:30 | 3.7 | 5.3 | 147.5 | 340 | 550 | 230 | 0 | 230 | 0 | 0 | 170145.0926 | 9.9694 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-02-07 14:30 | 3.6 | 4.7 | 150 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 170033.2407 | 9.9629 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-02-07 15:30 | 3 | 4.7 | 150 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 169765.0926 | 9.9472 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-02-07 16:30 | 2.5 | 4.9 | 147.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 169496.9444 | 9.9315 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-02-07 17:30 | 2.1 | 4.9 | 142.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 169228.7963 | 9.9157 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-02-07 18:30 | 1.9 | 4.9 | 140 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 168960.6481 | 9.9 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-02-07 19:30 | 1.9 | 4.9 | 140 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 168692.5 | 9.8843 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-02-07 20:30 | 2.1 | 4.9 | 142.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 168424.3519 | 9.8686 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-02-07 21:30 | 2.4 | 5 | 145 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 168312.5 | 9.8621 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-02-07 22:30 | 2.6 | 4.9 | 142.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 168200.6481 | 9.8555 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-02-07 23:30 | 2.6 | 4.7 | 140 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 167932.5 | 9.8398 | 1 |  |  | 1 | 11 | 0 | 0
Lerwick | 1978-02-08 00:30 | 2.4 | 4.5 | 145 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 167664.3519 | 9.8241 | 1 |  |  | 1 | 12 | 0 | 0
Lerwick | 1978-02-08 01:30 | 2.4 | 4.4 | 155 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 167259.9074 | 9.8004 | 1 |  |  | 1 | 13 | 0 | 0
Lerwick | 1978-02-08 02:30 | 2.6 | 4.2 | 160 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 166719.1667 | 9.7687 | 1 |  |  | 1 | 14 | 0 | 0
Lerwick | 1978-02-08 03:30 | 2.6 | 4 | 160 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 166178.4259 | 9.737 | 1 |  |  | 1 | 15 | 0 | 0
Lerwick | 1978-02-08 04:30 | 2.4 | 4.2 | 157.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 165637.6852 | 9.7053 | 1 |  |  | 1 | 16 | 0 | 0
Lerwick | 1978-02-08 05:30 | 2.3 | 4.6 | 157.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 165233.2407 | 9.6816 | 1 |  |  | 1 | 17 | 0 | 0
Lerwick | 1978-02-08 06:30 | 2.5 | 5.1 | 165 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 165121.3889 | 9.6751 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-08 07:30 | 2.3 | 5.5 | 170 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 165171.3889 | 9.678 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-08 08:30 | 2.4 | 5.3 | 175 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 165221.3889 | 9.6809 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-02-08 09:30 | 2.6 | 4.7 | 190 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 165109.537 | 9.6744 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-02-08 10:30 | 2.3 | 4.7 | 202.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 164841.3889 | 9.6587 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-02-08 11:30 | 2 | 5 | 202.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 164729.537 | 9.6521 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-02-08 12:30 | 1.9 | 4.4 | 197.5 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 164481.3889 | 9.6376 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-02-08 13:30 | 2.1 | 3.9 | 190 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 163855.463 | 9.6009 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-02-08 14:30 | 2.4 | 3.9 | 180 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163144.3519 | 9.5592 | 0 |  |  | 1 | 7 | 1 | 1
Lerwick | 1978-02-08 15:30 | 2.6 | 3.9 | 180 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162433.2407 | 9.5176 | 0 |  |  | 1 | 8 | 1 | 2
Lerwick | 1978-02-08 16:30 | 2.5 | 3.7 | 205 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161722.1296 | 9.4759 | 0 |  |  | 1 | 9 | 1 | 3
Lerwick | 1978-02-08 17:30 | 2.3 | 3.6 | 232.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161011.0185 | 9.4342 | 0 |  |  | 1 | 10 | 1 | 4
Lerwick | 1978-02-08 18:30 | 2.1 | 3.6 | 235 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160299.9074 | 9.3926 | 0 |  |  | 1 | 11 | 1 | 5
Lerwick | 1978-02-08 19:30 | 2 | 3.6 | 232.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 159588.7963 | 9.3509 | 0 |  |  | 1 | 12 | 1 | 6
Lerwick | 1978-02-08 20:30 | 1.9 | 3.6 | 240 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 158877.6852 | 9.3092 | 0 |  |  | 1 | 13 | 1 | 7
Lerwick | 1978-02-08 21:30 | 1.9 | 3.6 | 247.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 158166.5741 | 9.2676 | 0 |  |  | 1 | 14 | 1 | 8
Lerwick | 1978-02-08 22:30 | 2 | 3.4 | 250 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 157455.463 | 9.2259 | 0 |  |  | 1 | 15 | 1 | 9
Lerwick | 1978-02-08 23:30 | 2 | 3.6 | 252.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 156744.3519 | 9.1842 | 0 |  |  | 1 | 16 | 1 | 10
Lerwick | 1978-02-09 00:30 | 2 | 4.1 | 257.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 156118.4259 | 9.1476 | 1 |  |  | 1 | 17 | 0 | 0
Lerwick | 1978-02-09 01:30 | 2.2 | 4.4 | 260 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 155577.6852 | 9.1159 | 1 |  |  | 1 | 18 | 0 | 0
Lerwick | 1978-02-09 02:30 | 2.4 | 4.7 | 262.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 155173.2407 | 9.0922 | 1 |  |  | 1 | 19 | 0 | 0
Lerwick | 1978-02-09 03:30 | 2.3 | 4.9 | 267.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 154905.0926 | 9.0765 | 1 |  |  | 1 | 20 | 0 | 0
Lerwick | 1978-02-09 04:30 | 2.3 | 4.9 | 267.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 154636.9444 | 9.0608 | 1 |  |  | 1 | 21 | 0 | 0
Lerwick | 1978-02-09 05:30 | 2.6 | 5.1 | 262.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 154525.0926 | 9.0542 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-09 06:30 | 2.8 | 5.2 | 262.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 154535.0926 | 9.0548 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-02-09 07:30 | 2.7 | 4.7 | 270 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 154423.2407 | 9.0482 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-02-09 08:30 | 2.6 | 4 | 277.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 154018.7963 | 9.0245 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-02-09 09:30 | 2.6 | 3.1 | 312.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 153392.8704 | 8.9879 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-02-09 10:30 | 2.8 | 2.6 | 205 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 152681.7593 | 8.9462 | 0 |  |  | 1 | 5 | 1 | 1
Lerwick | 1978-02-09 11:30 | 3 | 3.3 | 77.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 151970.6481 | 8.9045 | 0 |  |  | 1 | 6 | 1 | 2
Lerwick | 1978-02-09 12:30 | 2.8 | 4.4 | 97.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 151344.7222 | 8.8679 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-02-09 13:30 | 2.7 | 4.9 | 110 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 150940.2778 | 8.8442 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-02-09 14:30 | 2.4 | 5.1 | 115 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 150828.4259 | 8.8376 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-09 15:30 | 2.1 | 5.8 | 110 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 150878.4259 | 8.8405 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-09 16:30 | 2 | 6 | 100 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 151033.4259 | 8.8496 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-09 17:30 | 1.8 | 5.8 | 90 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 151188.4259 | 8.8587 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-09 18:30 | 1.6 | 5.8 | 82.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 151278.4259 | 8.864 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-09 19:30 | 1.5 | 5.9 | 80 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 151368.4259 | 8.8692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-09 20:30 | 1.3 | 5.8 | 80 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 151458.4259 | 8.8745 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-09 21:30 | 1 | 5.9 | 77.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 151548.4259 | 8.8798 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-09 22:30 | 1 | 6.4 | 70 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 151703.4259 | 8.8889 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-09 23:30 | 1.2 | 6.5 | 60 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 152013.4259 | 8.907 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-10 00:30 | 1.1 | 6.4 | 52.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 152323.4259 | 8.9252 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-10 01:30 | 1 | 6 | 52.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 152543.4259 | 8.9381 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-10 02:30 | 1 | 5.3 | 70 | 340 | 550 | 230 | 0 | 230 | 115 | 0 | 152658.4259 | 8.9448 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-10 03:30 | 1 | 5.7 | 97.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 152708.4259 | 8.9478 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-10 04:30 | 1.4 | 6.7 | 112.5 | 1120 | 810 | 490 | 0 | 490 | 245 | 0 | 152953.4259 | 8.9621 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-10 05:30 | 1.8 | 7 | 120 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 153443.4259 | 8.9908 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-10 06:30 | 1.7 | 7.1 | 125 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 154023.4259 | 9.0248 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-10 07:30 | 1.6 | 7.2 | 120 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 154603.4259 | 9.0588 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-10 08:30 | 1.6 | 7.2 | 115 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 155183.4259 | 9.0928 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-10 09:30 | 1.4 | 6.9 | 117.5 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 155673.4259 | 9.1215 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-10 10:30 | 1.3 | 6.5 | 120 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 156073.4259 | 9.1449 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-10 11:30 | 1.3 | 6.4 | 120 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 156383.4259 | 9.1631 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-10 12:30 | 1.2 | 6.1 | 120 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 156603.4259 | 9.176 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-10 13:30 | 1.2 | 5.8 | 120 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 156758.4259 | 9.1851 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-10 14:30 | 1.3 | 5.5 | 117.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 156848.4259 | 9.1903 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-10 15:30 | 0.8 | 5.2 | 115 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 156898.4259 | 9.1933 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-10 16:30 | 0.1 | 5 | 115 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 156908.4259 | 9.1939 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-10 17:30 | 0 | 5 | 115 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 156918.4259 | 9.1944 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-10 18:30 | 0 | 5 | 115 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 156928.4259 | 9.195 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-02-10 19:30 | -0.1 | 4.7 | 115 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 156816.5741 | 9.1885 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-02-10 20:30 | -0.2 | 4.2 | 115 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 156412.1296 | 9.1648 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-02-10 21:30 | -0.4 | 4.2 | 117.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 155871.3889 | 9.1331 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-02-10 22:30 | -0.3 | 4.4 | 125 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 155330.6481 | 9.1014 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-02-10 23:30 | -0.1 | 4.2 | 130 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 154789.9074 | 9.0697 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-02-11 00:30 | -0.2 | 3.6 | 130 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 154163.9815 | 9.033 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-02-11 01:30 | -0.2 | 3 | 127.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 153452.8704 | 8.9914 | 0 |  |  | 1 | 8 | 1 | 1
Lerwick | 1978-02-11 02:30 | -0.2 | 2.7 | 125 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 152741.7593 | 8.9497 | 0 |  |  | 1 | 9 | 1 | 2
Lerwick | 1978-02-11 03:30 | -0.2 | 2.6 | 125 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 152030.6481 | 8.908 | 0 |  |  | 1 | 10 | 1 | 3
Lerwick | 1978-02-11 04:30 | -0.4 | 2 | 112.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 151319.537 | 8.8664 | 0 |  |  | 1 | 11 | 1 | 4
Lerwick | 1978-02-11 05:30 | -0.3 | 1.4 | 82.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 150608.4259 | 8.8247 | 0 |  |  | 1 | 12 | 1 | 5
Lerwick | 1978-02-11 06:30 | -0.3 | 1.4 | 37.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 149897.3148 | 8.783 | 0 |  |  | 1 | 13 | 1 | 6
Lerwick | 1978-02-11 07:30 | -0.7 | 1.4 | 180 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 149186.2037 | 8.7414 | 0 |  |  | 1 | 14 | 1 | 7
Lerwick | 1978-02-11 08:30 | -1.3 | 1.3 | 197.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 148475.0926 | 8.6997 | 0 |  |  | 1 | 15 | 1 | 8
Lerwick | 1978-02-11 09:30 | -1.5 | 1.5 | 72.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 147763.9815 | 8.658 | 0 |  |  | 1 | 16 | 1 | 9
Lerwick | 1978-02-11 10:30 | -0.4 | 1.9 | 115 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 147052.8704 | 8.6164 | 0 |  |  | 1 | 17 | 1 | 10
Lerwick | 1978-02-11 11:30 | 0.7 | 2.3 | 135 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 146341.7593 | 8.5747 | 0 |  |  | 1 | 18 | 1 | 11
Lerwick | 1978-02-11 12:30 | 1.1 | 2.8 | 150 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 145630.6481 | 8.533 | 0 |  |  | 1 | 19 | 1 | 12
Lerwick | 1978-02-11 13:30 | 1.4 | 2.9 | 180 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 144919.537 | 8.4914 | 0 |  |  | 1 | 20 | 1 | 13
Lerwick | 1978-02-11 14:30 | 0.8 | 2.6 | 210 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 144208.4259 | 8.4497 | 0 |  |  | 1 | 21 | 1 | 14
Lerwick | 1978-02-11 15:30 | 0.2 | 2.4 | 230 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 143497.3148 | 8.408 | 0 |  |  | 1 | 22 | 1 | 15
Lerwick | 1978-02-11 16:30 | 0.3 | 1.8 | 262.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 142786.2037 | 8.3664 | 0 |  |  | 1 | 23 | 1 | 16
Lerwick | 1978-02-11 17:30 | -0.1 | 1.2 | 297.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 142075.0926 | 8.3247 | 0 |  |  | 1 | 24 | 1 | 17
Lerwick | 1978-02-11 18:30 | -1 | 0.7 | 322.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 141363.9815 | 8.283 | 0 |  |  | 1 | 25 | 1 | 18
Lerwick | 1978-02-11 19:30 | -2 | 1.3 | 177.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 140652.8704 | 8.2414 | 0 |  |  | 1 | 26 | 1 | 19
Lerwick | 1978-02-11 20:30 | -2.5 | 2.7 | 20 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 139941.7593 | 8.1997 | 0 |  |  | 1 | 27 | 1 | 20
Lerwick | 1978-02-11 21:30 | -1.9 | 2.9 | 185 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 139230.6481 | 8.158 | 0 |  |  | 1 | 28 | 1 | 21
Lerwick | 1978-02-11 22:30 | -2.6 | 2.6 | 340 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 138519.537 | 8.1164 | 0 |  |  | 1 | 29 | 1 | 22
Lerwick | 1978-02-11 23:30 | -4.2 | 2.9 | 327.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 137808.4259 | 8.0747 | 0 |  |  | 1 | 30 | 1 | 23
Lerwick | 1978-02-12 00:30 | -4.4 | 3.3 | 330 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 137097.3148 | 8.033 | 0 |  |  | 1 | 31 | 1 | 24
Lerwick | 1978-02-12 01:30 | -3.6 | 3.6 | 337.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 136386.2037 | 7.9914 | 0 |  |  | 1 | 32 | 1 | 25
Lerwick | 1978-02-12 02:30 | -3.2 | 3.6 | 335 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 135675.0926 | 7.9497 | 0 |  |  | 1 | 33 | 1 | 26
Lerwick | 1978-02-12 03:30 | -3.4 | 3.6 | 330 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 134963.9815 | 7.908 | 0 |  |  | 1 | 34 | 1 | 27
Lerwick | 1978-02-12 04:30 | -2.5 | 3.7 | 335 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 134252.8704 | 7.8664 | 0 |  |  | 1 | 35 | 1 | 28
Lerwick | 1978-02-12 05:30 | -2.7 | 3.7 | 340 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 133541.7593 | 7.8247 | 0 |  |  | 1 | 36 | 1 | 29
Lerwick | 1978-02-12 06:30 | -2.6 | 3.6 | 170 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 132830.6481 | 7.783 | 0 |  |  | 1 | 37 | 1 | 30
Lerwick | 1978-02-12 07:30 | -1.6 | 4.2 | 15 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 132204.7222 | 7.7464 | 1 |  |  | 1 | 38 | 0 | 0
Lerwick | 1978-02-12 08:30 | -1.5 | 5.4 | 35 | 340 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 131956.5741 | 7.7318 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-12 09:30 | -0.6 | 5.9 | 40 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 132006.5741 | 7.7348 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-12 10:30 | 0 | 5.6 | 42.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 132096.5741 | 7.74 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-12 11:30 | 0.1 | 5.5 | 45 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 132186.5741 | 7.7453 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-12 12:30 | 0.6 | 6.4 | 42.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 132341.5741 | 7.7544 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-12 13:30 | 1 | 7.8 | 40 | 1840 | 1300 | 980 | 0 | 980 | 490 | 0 | 132831.5741 | 7.7831 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-12 14:30 | 1.3 | 9 | 40 | 2920 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 133476.5741 | 7.8209 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-12 15:30 | 1.5 | 9.4 | 40 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 134121.5741 | 7.8587 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-12 16:30 | 1.5 | 8.9 | 40 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 134766.5741 | 7.8965 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-12 17:30 | 1.6 | 9 | 40 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 135411.5741 | 7.9343 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-12 18:30 | 1.9 | 9.7 | 40 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 136056.5741 | 7.9721 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-12 19:30 | 1.9 | 10 | 40 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 136701.5741 | 8.0099 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-12 20:30 | 1.7 | 10.1 | 42.5 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 137346.5741 | 8.0477 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-12 21:30 | 1.4 | 10.1 | 47.5 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 137991.5741 | 8.0854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-12 22:30 | 0.9 | 9.5 | 50 | 3280 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 138636.5741 | 8.1232 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-12 23:30 | 0.7 | 8.7 | 47.5 | 2560 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 139281.5741 | 8.161 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-13 00:30 | 1 | 8.3 | 42.5 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 139926.5741 | 8.1988 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-13 01:30 | 1.3 | 8.4 | 42.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 140571.5741 | 8.2366 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-13 02:30 | 1.5 | 8.9 | 50 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 141216.5741 | 8.2744 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-13 03:30 | 1.6 | 9.7 | 50 | 3280 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 141861.5741 | 8.3122 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-13 04:30 | 1.3 | 11.9 | 37.5 | 4472.2222 | 3876.1111 | 3556.1111 | 0 | 1290 | 645 | 0 | 142506.5741 | 8.35 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-13 05:30 | 1.8 | 13.9 | 32.5 | 4600 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 143151.5741 | 8.3878 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-13 06:30 | 2.7 | 14.5 | 37.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 143796.5741 | 8.4256 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-13 07:30 | 2.7 | 14.3 | 40 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 144441.5741 | 8.4634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-13 08:30 | 2.7 | 13.5 | 40 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 145086.5741 | 8.5012 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-13 09:30 | 2.8 | 12.5 | 35 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 145731.5741 | 8.539 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-13 10:30 | 2.9 | 11.7 | 27.5 | 4472.2222 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 146376.5741 | 8.5768 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-13 11:30 | 2.4 | 11.7 | 27.5 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 645 | 0 | 147021.5741 | 8.6145 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-13 12:30 | 2.4 | 12.2 | 32.5 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 645 | 0 | 147666.5741 | 8.6523 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-13 13:30 | 2.7 | 11.9 | 35 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 645 | 0 | 148311.5741 | 8.6901 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-13 14:30 | 2.7 | 11.4 | 35 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 148956.5741 | 8.7279 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-13 15:30 | 2.6 | 11.5 | 37.5 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 149601.5741 | 8.7657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-13 16:30 | 2.3 | 11.8 | 37.5 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 645 | 0 | 150246.5741 | 8.8035 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-13 17:30 | 2 | 11.9 | 35 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 645 | 0 | 150891.5741 | 8.8413 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-13 18:30 | 1.8 | 12.4 | 37.5 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 645 | 0 | 151536.5741 | 8.8791 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-13 19:30 | 1.9 | 13 | 40 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 645 | 0 | 152181.5741 | 8.9169 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-13 20:30 | 1.9 | 12.8 | 42.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 152826.5741 | 8.9547 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-13 21:30 | 1.8 | 12.1 | 45 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 645 | 0 | 153471.5741 | 8.9925 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-13 22:30 | 1.5 | 11.5 | 42.5 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 645 | 0 | 154116.5741 | 9.0303 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-13 23:30 | 1.6 | 10.5 | 40 | 4000 | 4236.1111 | 3916.1111 | 0 | 1290 | 645 | 0 | 154761.5741 | 9.0681 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-14 00:30 | 1.7 | 8.9 | 40 | 2560 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 155406.5741 | 9.1059 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-14 01:30 | 1.2 | 7.8 | 37.5 | 1840 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 156051.5741 | 9.1436 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-14 02:30 | 1.1 | 7.4 | 32.5 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 156696.5741 | 9.1814 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-14 03:30 | 1.1 | 6.8 | 27.5 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 157186.5741 | 9.2102 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-14 04:30 | 0.9 | 6.1 | 22.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 157496.5741 | 9.2283 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-14 05:30 | 1 | 5.4 | 22.5 | 340 | 550 | 230 | 0 | 230 | 115 | 0 | 157611.5741 | 9.2351 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-02-14 06:30 | 0.8 | 4.9 | 25 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 157499.7222 | 9.2285 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-02-14 07:30 | 0.3 | 5.3 | 27.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 157387.8704 | 9.2219 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-14 08:30 | 0.3 | 5.5 | 35 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 157437.8704 | 9.2249 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-14 09:30 | 0.7 | 5.1 | 37.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 157487.8704 | 9.2278 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-02-14 10:30 | 1.3 | 4.6 | 27.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 157376.0185 | 9.2213 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-02-14 11:30 | 1.9 | 4.2 | 15 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 156971.5741 | 9.1976 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-02-14 12:30 | 1.9 | 4 | 7.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 156430.8333 | 9.1659 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-02-14 13:30 | 1.8 | 4 | 2.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 155890.0926 | 9.1342 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-02-14 14:30 | 2 | 4 | 2.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 155349.3519 | 9.1025 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-02-14 15:30 | 1.6 | 3.9 | 7.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 154723.4259 | 9.0658 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-02-14 16:30 | 1 | 3.3 | 180 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 154012.3148 | 9.0242 | 0 |  |  | 1 | 8 | 1 | 1
Lerwick | 1978-02-14 17:30 | 0.5 | 2.1 | 337.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 153301.2037 | 8.9825 | 0 |  |  | 1 | 9 | 1 | 2
Lerwick | 1978-02-14 18:30 | -0.6 | 1.4 | 310 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 152590.0926 | 8.9408 | 0 |  |  | 1 | 10 | 1 | 3
Lerwick | 1978-02-14 19:30 | -1.5 | 1.4 | 282.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 151878.9815 | 8.8992 | 0 |  |  | 1 | 11 | 1 | 4
Lerwick | 1978-02-14 20:30 | -0.9 | 1.1 | 292.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 151167.8704 | 8.8575 | 0 |  |  | 1 | 12 | 1 | 5
Lerwick | 1978-02-14 21:30 | -0.1 | 0.8 | 307.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 150456.7593 | 8.8158 | 0 |  |  | 1 | 13 | 1 | 6
Lerwick | 1978-02-14 22:30 | -0.1 | 1.3 | 270 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 149745.6481 | 8.7742 | 0 |  |  | 1 | 14 | 1 | 7
Lerwick | 1978-02-14 23:30 | 0 | 1.6 | 245 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 149034.537 | 8.7325 | 0 |  |  | 1 | 15 | 1 | 8
Lerwick | 1978-02-15 00:30 | 0.1 | 1 | 280 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 148323.4259 | 8.6908 | 0 |  |  | 1 | 16 | 1 | 9
Lerwick | 1978-02-15 01:30 | 0 | 2 | 302.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 147612.3148 | 8.6492 | 0 |  |  | 1 | 17 | 1 | 10
Lerwick | 1978-02-15 02:30 | -0.1 | 4.9 | 260 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 147122.6852 | 8.6205 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-15 03:30 | 0.1 | 6.3 | 225 | 760 | 479.6667 | 159.6667 | 0 | 159.6667 | 79.8333 | 0 | 147202.5185 | 8.6251 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-15 04:30 | 0 | 7 | 230 | 1480 | 1120 | 800 | 0 | 800 | 400 | 0 | 147602.5185 | 8.6486 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-15 05:30 | -0.1 | 7.3 | 232.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 148182.5185 | 8.6826 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-15 06:30 | 0 | 6 | 242.5 | 760 | 1120 | 800 | 0 | 800 | 400 | 0 | 148582.5185 | 8.706 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-15 07:30 | 0 | 4.4 | 265 | 76.6667 | 418.3333 | 98.3333 | 0 | 98.3333 | 49.1667 | 0 | 148631.6852 | 8.7089 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-02-15 08:30 | -0.2 | 3.9 | 265 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 148005.7593 | 8.6722 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-02-15 09:30 | -0.4 | 4.2 | 255 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 147379.8333 | 8.6355 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-02-15 10:30 | -0.5 | 4.4 | 260 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 146839.0926 | 8.6039 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-02-15 11:30 | -0.3 | 3.5 | 265 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 146213.1667 | 8.5672 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-02-15 12:30 | -0.1 | 2.4 | 262.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 145502.0556 | 8.5255 | 0 |  |  | 1 | 6 | 1 | 1
Lerwick | 1978-02-15 13:30 | -0.1 | 1.9 | 270 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 144790.9444 | 8.4838 | 0 |  |  | 1 | 7 | 1 | 2
Lerwick | 1978-02-15 14:30 | 0 | 2.7 | 305 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 144079.8333 | 8.4422 | 0 |  |  | 1 | 8 | 1 | 3
Lerwick | 1978-02-15 15:30 | -0.1 | 5.8 | 175 | 500 | 250 | 0 | 70 | 0 | 0 | 155.5556 | 143924.2778 | 8.4331 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-15 16:30 | -0.1 | 9.8 | 27.5 | 3280 | 1890 | 1570 | 0 | 1290 | 645 | 0 | 144569.2778 | 8.4709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-15 17:30 | -0.1 | 11.7 | 37.5 | 4472.2222 | 3876.1111 | 3556.1111 | 0 | 1290 | 645 | 0 | 145214.2778 | 8.5086 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-15 18:30 | -0.4 | 11.4 | 45 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 145859.2778 | 8.5464 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-15 19:30 | -0.3 | 10.5 | 50 | 4000 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 146504.2778 | 8.5842 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-15 20:30 | 0 | 9.8 | 47.5 | 3280 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 147149.2778 | 8.622 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-15 21:30 | 0 | 8.7 | 45 | 2560 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 147794.2778 | 8.6598 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-15 22:30 | 0.2 | 8.4 | 47.5 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 148439.2778 | 8.6976 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-15 23:30 | 0.4 | 8.8 | 47.5 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 149084.2778 | 8.7354 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-16 00:30 | 0.4 | 8.4 | 42.5 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 149729.2778 | 8.7732 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-16 01:30 | 0.3 | 7.7 | 40 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 150374.2778 | 8.811 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-16 02:30 | 0 | 7.1 | 40 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 151019.2778 | 8.8488 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-16 03:30 | -0.1 | 6.7 | 35 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 151509.2778 | 8.8775 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-16 04:30 | 0 | 6.5 | 22.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 151909.2778 | 8.9009 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-16 05:30 | -0.1 | 6 | 185 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 152219.2778 | 8.9191 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-16 06:30 | -0.5 | 5.5 | 350 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 152374.2778 | 8.9282 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-16 07:30 | -1.2 | 5.1 | 345 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 152424.2778 | 8.9311 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-02-16 08:30 | -1.4 | 4.6 | 342.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 152312.4259 | 8.9246 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-02-16 09:30 | -2.2 | 4.4 | 340 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 151907.9815 | 8.9009 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-02-16 10:30 | -2.7 | 5 | 340 | 340 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 151659.8333 | 8.8863 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-16 11:30 | -1.6 | 5.3 | 340 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 151669.8333 | 8.8869 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-02-16 12:30 | -1.2 | 4.1 | 340 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 151421.6852 | 8.8724 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-02-16 13:30 | -1.2 | 3.3 | 330 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 150795.7593 | 8.8357 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-02-16 14:30 | -0.8 | 3 | 315 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 150084.6481 | 8.794 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-02-16 15:30 | -0.8 | 2.9 | 317.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 149373.537 | 8.7524 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-02-16 16:30 | -0.9 | 3.5 | 320 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 148662.4259 | 8.7107 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-02-16 17:30 | -2.4 | 3.9 | 312.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 147951.3148 | 8.669 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-02-16 18:30 | -3 | 4.6 | 325 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 147461.6852 | 8.6403 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-16 19:30 | -2.2 | 6.5 | 170 | 1120 | 659.6667 | 339.6667 | 0 | 339.6667 | 169.8333 | 0 | 147631.5185 | 8.6503 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-16 20:30 | -1.8 | 7.7 | 0 | 1840 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 148211.5185 | 8.6843 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-16 21:30 | -1.6 | 7 | 177.5 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 148856.5185 | 8.7221 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-16 22:30 | -1.9 | 6.9 | 352.5 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 149346.5185 | 8.7508 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-16 23:30 | -2.8 | 8.9 | 352.5 | 2560 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 149991.5185 | 8.7886 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-17 00:30 | -3 | 11.1 | 177.5 | 4300 | 3430 | 3110 | 0 | 1290 | 645 | 0 | 150636.5185 | 8.8264 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-17 01:30 | -2.1 | 12.2 | 0 | 4536.1111 | 4418.0556 | 4098.0556 | 0 | 1290 | 645 | 0 | 151281.5185 | 8.8642 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-17 02:30 | -2.3 | 11.7 | 2.5 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 645 | 0 | 151926.5185 | 8.9019 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-17 03:30 | -2.8 | 10.6 | 5 | 4000 | 4236.1111 | 3916.1111 | 0 | 1290 | 645 | 0 | 152571.5185 | 8.9397 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-17 04:30 | -2.7 | 9.8 | 2.5 | 3280 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 153216.5185 | 8.9775 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-17 05:30 | -3.1 | 8.7 | 177.5 | 2560 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 153861.5185 | 9.0153 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-17 06:30 | -3.5 | 8 | 352.5 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 154506.5185 | 9.0531 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-17 07:30 | -3.8 | 8 | 350 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 155151.5185 | 9.0909 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-17 08:30 | -3.9 | 8.4 | 352.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 155796.5185 | 9.1287 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-17 09:30 | -4.2 | 8.9 | 355 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 156441.5185 | 9.1665 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-17 10:30 | -3.6 | 8.5 | 350 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 157086.5185 | 9.2043 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-17 11:30 | -3 | 7.5 | 345 | 1840 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 157731.5185 | 9.2421 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-17 12:30 | -3.5 | 7 | 347.5 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 158376.5185 | 9.2799 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-17 13:30 | -3.3 | 7.3 | 350 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 158956.5185 | 9.3139 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-17 14:30 | -3.3 | 7.8 | 347.5 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 159601.5185 | 9.3517 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-17 15:30 | -3.3 | 7.8 | 345 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 160246.5185 | 9.3894 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-17 16:30 | -3.6 | 7.6 | 345 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 160891.5185 | 9.4272 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-17 17:30 | -4.2 | 7.3 | 342.5 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 161536.5185 | 9.465 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-17 18:30 | -4.1 | 7.2 | 342.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 162116.5185 | 9.499 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-17 19:30 | -3.9 | 6.9 | 347.5 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 162606.5185 | 9.5277 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-17 20:30 | -4 | 6.7 | 350 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 163006.5185 | 9.5512 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-17 21:30 | -4.3 | 6.7 | 347.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 163406.5185 | 9.5746 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-17 22:30 | -4.5 | 6.5 | 342.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 163806.5185 | 9.598 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-17 23:30 | -5 | 6.5 | 340 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 164206.5185 | 9.6215 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-18 00:30 | -5 | 6.8 | 340 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 164606.5185 | 9.6449 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-18 01:30 | -4.4 | 7.1 | 337.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 165096.5185 | 9.6736 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-18 02:30 | -4.5 | 6.7 | 335 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 165586.5185 | 9.7023 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-18 03:30 | -4.4 | 6.2 | 335 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 165896.5185 | 9.7205 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-18 04:30 | -4.7 | 6.6 | 332.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 166206.5185 | 9.7387 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-18 05:30 | -4.9 | 7 | 335 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 166696.5185 | 9.7674 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-18 06:30 | -4.4 | 7.2 | 345 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 167276.5185 | 9.8014 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-18 07:30 | -4.4 | 7.3 | 347.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 167856.5185 | 9.8353 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-18 08:30 | -4.6 | 6.9 | 340 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 168346.5185 | 9.8641 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-18 09:30 | -4.3 | 6.4 | 335 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 168656.5185 | 9.8822 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-18 10:30 | -3.8 | 5.8 | 337.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 168811.5185 | 9.8913 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-18 11:30 | -3.6 | 4.9 | 342.5 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 168826.3519 | 9.8922 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-02-18 12:30 | -3.5 | 4.4 | 345 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 168421.9074 | 9.8685 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-02-18 13:30 | -3.2 | 4.2 | 340 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 167881.1667 | 9.8368 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-02-18 14:30 | -3 | 3.8 | 335 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 167255.2407 | 9.8001 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-02-18 15:30 | -3.2 | 3.4 | 335 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166544.1296 | 9.7584 | 0 |  |  | 1 | 5 | 1 | 1
Lerwick | 1978-02-18 16:30 | -3.7 | 3 | 332.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165833.0185 | 9.7168 | 0 |  |  | 1 | 6 | 1 | 2
Lerwick | 1978-02-18 17:30 | -4.5 | 2.4 | 327.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165121.9074 | 9.6751 | 0 |  |  | 1 | 7 | 1 | 3
Lerwick | 1978-02-18 18:30 | -4.9 | 2.2 | 322.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164410.7963 | 9.6334 | 0 |  |  | 1 | 8 | 1 | 4
Lerwick | 1978-02-18 19:30 | -4.6 | 2.4 | 317.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163699.6852 | 9.5918 | 0 |  |  | 1 | 9 | 1 | 5
Lerwick | 1978-02-18 20:30 | -3.9 | 3.1 | 317.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162988.5741 | 9.5501 | 0 |  |  | 1 | 10 | 1 | 6
Lerwick | 1978-02-18 21:30 | -3 | 3.4 | 322.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162277.463 | 9.5084 | 0 |  |  | 1 | 11 | 1 | 7
Lerwick | 1978-02-18 22:30 | -2.7 | 3 | 315 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161566.3519 | 9.4668 | 0 |  |  | 1 | 12 | 1 | 8
Lerwick | 1978-02-18 23:30 | -2.7 | 2.9 | 295 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160855.2407 | 9.4251 | 0 |  |  | 1 | 13 | 1 | 9
Lerwick | 1978-02-19 00:30 | -2.3 | 3.1 | 280 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160144.1296 | 9.3834 | 0 |  |  | 1 | 14 | 1 | 10
Lerwick | 1978-02-19 01:30 | -2.1 | 3.1 | 272.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 159433.0185 | 9.3418 | 0 |  |  | 1 | 15 | 1 | 11
Lerwick | 1978-02-19 02:30 | -2.1 | 2.9 | 270 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 158721.9074 | 9.3001 | 0 |  |  | 1 | 16 | 1 | 12
Lerwick | 1978-02-19 03:30 | -2.1 | 2.6 | 285 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 158010.7963 | 9.2584 | 0 |  |  | 1 | 17 | 1 | 13
Lerwick | 1978-02-19 04:30 | -2 | 2.6 | 310 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 157299.6852 | 9.2168 | 0 |  |  | 1 | 18 | 1 | 14
Lerwick | 1978-02-19 05:30 | -2 | 2.7 | 317.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 156588.5741 | 9.1751 | 0 |  |  | 1 | 19 | 1 | 15
Lerwick | 1978-02-19 06:30 | -1.9 | 2.6 | 317.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 155877.463 | 9.1334 | 0 |  |  | 1 | 20 | 1 | 16
Lerwick | 1978-02-19 07:30 | -2.9 | 2.4 | 320 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 155166.3519 | 9.0918 | 0 |  |  | 1 | 21 | 1 | 17
Lerwick | 1978-02-19 08:30 | -4.1 | 2.1 | 322.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 154455.2407 | 9.0501 | 0 |  |  | 1 | 22 | 1 | 18
Lerwick | 1978-02-19 09:30 | -4.4 | 2.1 | 327.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 153744.1296 | 9.0084 | 0 |  |  | 1 | 23 | 1 | 19
Lerwick | 1978-02-19 10:30 | -4.6 | 2.4 | 330 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 153033.0185 | 8.9668 | 0 |  |  | 1 | 24 | 1 | 20
Lerwick | 1978-02-19 11:30 | -3.8 | 2.6 | 327.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 152321.9074 | 8.9251 | 0 |  |  | 1 | 25 | 1 | 21
Lerwick | 1978-02-19 12:30 | -3.2 | 2.4 | 322.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 151610.7963 | 8.8834 | 0 |  |  | 1 | 26 | 1 | 22
Lerwick | 1978-02-19 13:30 | -2.7 | 2 | 312.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 150899.6852 | 8.8418 | 0 |  |  | 1 | 27 | 1 | 23
Lerwick | 1978-02-19 14:30 | -2 | 2.2 | 295 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 150188.5741 | 8.8001 | 0 |  |  | 1 | 28 | 1 | 24
Lerwick | 1978-02-19 15:30 | -1 | 3.2 | 280 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 149477.463 | 8.7584 | 0 |  |  | 1 | 29 | 1 | 25
Lerwick | 1978-02-19 16:30 | -0.1 | 4.1 | 275 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 148851.537 | 8.7218 | 1 |  |  | 1 | 30 | 0 | 0
Lerwick | 1978-02-19 17:30 | -0.2 | 4.6 | 277.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 148447.0926 | 8.6981 | 1 |  |  | 1 | 31 | 0 | 0
Lerwick | 1978-02-19 18:30 | -0.2 | 5.3 | 277.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 148335.2407 | 8.6915 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-19 19:30 | 0 | 5.9 | 272.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 148385.2407 | 8.6944 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-19 20:30 | 0 | 6.3 | 270 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 148540.2407 | 8.7035 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-19 21:30 | -0.1 | 6.8 | 267.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 148850.2407 | 8.7217 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-19 22:30 | 0.2 | 7.2 | 267.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 149340.2407 | 8.7504 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-19 23:30 | 0.7 | 6.8 | 275 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 149830.2407 | 8.7791 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-20 00:30 | 1.1 | 6.4 | 280 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 150140.2407 | 8.7973 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-20 01:30 | 1.5 | 6.8 | 280 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 150450.2407 | 8.8154 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-20 02:30 | 1.9 | 7.6 | 280 | 1840 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 151030.2407 | 8.8494 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-20 03:30 | 2.2 | 8 | 280 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 151675.2407 | 8.8872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-20 04:30 | 2.4 | 7.7 | 280 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 152320.2407 | 8.925 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-20 05:30 | 2.3 | 7.6 | 277.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 152965.2407 | 8.9628 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-20 06:30 | 2.4 | 7.6 | 272.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 153610.2407 | 9.0006 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-20 07:30 | 2.7 | 7.5 | 270 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 154255.2407 | 9.0384 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-20 08:30 | 2.6 | 7.7 | 270 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 154900.2407 | 9.0762 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-20 09:30 | 2.7 | 8.2 | 270 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 155545.2407 | 9.114 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-20 10:30 | 3 | 8.5 | 270 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 156190.2407 | 9.1518 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-20 11:30 | 3 | 8.3 | 270 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 156835.2407 | 9.1896 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-20 12:30 | 3 | 8.1 | 270 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 157480.2407 | 9.2274 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-20 13:30 | 3 | 8 | 270 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 158125.2407 | 9.2652 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-20 14:30 | 2.9 | 7.3 | 270 | 1480 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 158770.2407 | 9.3029 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-20 15:30 | 2.6 | 6.2 | 270 | 760 | 1120 | 800 | 0 | 800 | 400 | 0 | 159170.2407 | 9.3264 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-20 16:30 | 2.5 | 5.3 | 267.5 | 340 | 550 | 230 | 0 | 230 | 115 | 0 | 159285.2407 | 9.3331 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-02-20 17:30 | 2.3 | 4.7 | 260 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 159173.3889 | 9.3266 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-02-20 18:30 | 1.8 | 4.5 | 252.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 158905.2407 | 9.3109 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-02-20 19:30 | 1.4 | 4.4 | 247.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 158500.7963 | 9.2872 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-02-20 20:30 | 1 | 4 | 245 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 157960.0556 | 9.2555 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-02-20 21:30 | 0.9 | 2.9 | 245 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 157334.1296 | 9.2188 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-02-20 22:30 | 0.6 | 1.7 | 242.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 156623.0185 | 9.1771 | 0 |  |  | 1 | 7 | 1 | 1
Lerwick | 1978-02-20 23:30 | -0.3 | 1.1 | 230 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 155911.9074 | 9.1355 | 0 |  |  | 1 | 8 | 1 | 2
Lerwick | 1978-02-21 00:30 | -0.8 | 1 | 212.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 155200.7963 | 9.0938 | 0 |  |  | 1 | 9 | 1 | 3
Lerwick | 1978-02-21 01:30 | -1.1 | 1 | 207.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 154489.6852 | 9.0521 | 0 |  |  | 1 | 10 | 1 | 4
Lerwick | 1978-02-21 02:30 | -1.8 | 0.7 | 247.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 153778.5741 | 9.0105 | 0 |  |  | 1 | 11 | 1 | 5
Lerwick | 1978-02-21 03:30 | -1.9 | 0.2 | 142.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 153067.463 | 8.9688 | 0 |  |  | 1 | 12 | 1 | 6
Lerwick | 1978-02-21 04:30 | -2.4 | 0.2 | 45 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 152356.3519 | 8.9271 | 0 |  |  | 1 | 13 | 1 | 7
Lerwick | 1978-02-21 05:30 | -3.5 | 0.9 | 135 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 151645.2407 | 8.8855 | 0 |  |  | 1 | 14 | 1 | 8
Lerwick | 1978-02-21 06:30 | -3.6 | 1.9 | 177.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 150934.1296 | 8.8438 | 0 |  |  | 1 | 15 | 1 | 9
Lerwick | 1978-02-21 07:30 | -2 | 3.1 | 170 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 150223.0185 | 8.8021 | 0 |  |  | 1 | 16 | 1 | 10
Lerwick | 1978-02-21 08:30 | 0 | 3.6 | 162.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 149511.9074 | 8.7605 | 0 |  |  | 1 | 17 | 1 | 11
Lerwick | 1978-02-21 09:30 | 1.2 | 3.6 | 157.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 148800.7963 | 8.7188 | 0 |  |  | 1 | 18 | 1 | 12
Lerwick | 1978-02-21 10:30 | 1.7 | 3.7 | 150 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 148089.6852 | 8.6771 | 0 |  |  | 1 | 19 | 1 | 13
Lerwick | 1978-02-21 11:30 | 2.2 | 3.9 | 140 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 147378.5741 | 8.6355 | 0 |  |  | 1 | 20 | 1 | 14
Lerwick | 1978-02-21 12:30 | 2.6 | 4 | 135 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 146752.6481 | 8.5988 | 1 |  |  | 1 | 21 | 0 | 0
Lerwick | 1978-02-21 13:30 | 2.6 | 4 | 142.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 146211.9074 | 8.5671 | 1 |  |  | 1 | 22 | 0 | 0
Lerwick | 1978-02-21 14:30 | 2.7 | 4 | 152.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 145671.1667 | 8.5354 | 1 |  |  | 1 | 23 | 0 | 0
Lerwick | 1978-02-21 15:30 | 2.3 | 4.2 | 152.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 145130.4259 | 8.5037 | 1 |  |  | 1 | 24 | 0 | 0
Lerwick | 1978-02-21 16:30 | 1.8 | 4.4 | 145 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 144589.6852 | 8.4721 | 1 |  |  | 1 | 25 | 0 | 0
Lerwick | 1978-02-21 17:30 | 1.3 | 4.5 | 135 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 144185.2407 | 8.4484 | 1 |  |  | 1 | 26 | 0 | 0
Lerwick | 1978-02-21 18:30 | 1 | 4.5 | 130 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 143917.0926 | 8.4326 | 1 |  |  | 1 | 27 | 0 | 0
Lerwick | 1978-02-21 19:30 | 1.1 | 4.5 | 125 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 143648.9444 | 8.4169 | 1 |  |  | 1 | 28 | 0 | 0
Lerwick | 1978-02-21 20:30 | 1.2 | 4.4 | 112.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 143244.5 | 8.3932 | 1 |  |  | 1 | 29 | 0 | 0
Lerwick | 1978-02-21 21:30 | 1 | 4.2 | 102.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 142703.7593 | 8.3615 | 1 |  |  | 1 | 30 | 0 | 0
Lerwick | 1978-02-21 22:30 | 1 | 3.9 | 97.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 142077.8333 | 8.3249 | 1 |  |  | 1 | 31 | 0 | 0
Lerwick | 1978-02-21 23:30 | 1.2 | 3.9 | 80 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 141366.7222 | 8.2832 | 0 |  |  | 1 | 32 | 1 | 1
Lerwick | 1978-02-22 00:30 | 1.3 | 4.2 | 55 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 140740.7963 | 8.2465 | 1 |  |  | 1 | 33 | 0 | 0
Lerwick | 1978-02-22 01:30 | 1 | 5.3 | 50 | 340 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 140492.6481 | 8.232 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-22 02:30 | 0.8 | 6.7 | 57.5 | 1120 | 730 | 410 | 0 | 410 | 205 | 0 | 140697.6481 | 8.244 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-22 03:30 | 0.7 | 7.6 | 60 | 1840 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 141277.6481 | 8.278 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-22 04:30 | 0.8 | 8.5 | 62.5 | 2560 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 141922.6481 | 8.3158 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-22 05:30 | 1 | 9.1 | 67.5 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 142567.6481 | 8.3536 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-22 06:30 | 1 | 9.4 | 70 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 143212.6481 | 8.3914 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-22 07:30 | 1 | 9.7 | 72.5 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 143857.6481 | 8.4292 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-22 08:30 | 1 | 10 | 77.5 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 144502.6481 | 8.467 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-22 09:30 | 0.8 | 10.1 | 80 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 145147.6481 | 8.5047 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-22 10:30 | 0.7 | 10.4 | 80 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 145792.6481 | 8.5425 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-22 11:30 | 1 | 10.2 | 82.5 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 146437.6481 | 8.5803 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-22 12:30 | 0.6 | 9.9 | 87.5 | 3280 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 147082.6481 | 8.6181 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-22 13:30 | 0.5 | 9.8 | 90 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 147727.6481 | 8.6559 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-22 14:30 | 1.1 | 9.9 | 90 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 148372.6481 | 8.6937 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-22 15:30 | 1.1 | 10.1 | 90 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 149017.6481 | 8.7315 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-22 16:30 | 1 | 10.3 | 87.5 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 149662.6481 | 8.7693 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-22 17:30 | 0.8 | 10.3 | 82.5 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 150307.6481 | 8.8071 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-22 18:30 | 0.4 | 10.3 | 82.5 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 150952.6481 | 8.8449 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-22 19:30 | 0.4 | 10.3 | 87.5 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 151597.6481 | 8.8827 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-22 20:30 | 0.5 | 10.3 | 90 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 152242.6481 | 8.9205 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-22 21:30 | 0.5 | 10.3 | 90 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 152887.6481 | 8.9583 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-22 22:30 | 0.4 | 10.1 | 92.5 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 153532.6481 | 8.9961 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-22 23:30 | 0.5 | 10.1 | 100 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 154177.6481 | 9.0338 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-23 00:30 | 0.9 | 11.3 | 110 | 4300 | 3970 | 3650 | 0 | 1290 | 645 | 0 | 154822.6481 | 9.0716 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-23 01:30 | 1.6 | 13.5 | 120 | 4600 | 4450 | 4130 | 0 | 1290 | 645 | 0 | 155467.6481 | 9.1094 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-23 02:30 | 2.2 | 15.2 | 127.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 156112.6481 | 9.1472 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-23 03:30 | 2.2 | 16.2 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 156757.6481 | 9.185 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-23 04:30 | 1.6 | 17.1 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 157402.6481 | 9.2228 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-23 05:30 | 1.1 | 17.5 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 158047.6481 | 9.2606 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-23 06:30 | 1 | 17.6 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 158692.6481 | 9.2984 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-23 07:30 | 1.1 | 17.9 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 159337.6481 | 9.3362 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-23 08:30 | 1.2 | 17.9 | 132.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 159982.6481 | 9.374 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-23 09:30 | 1.3 | 17.8 | 137.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 160627.6481 | 9.4118 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-23 10:30 | 1.5 | 17.9 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 161272.6481 | 9.4496 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-23 11:30 | 1.8 | 18 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 161917.6481 | 9.4874 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-23 12:30 | 2.1 | 17.9 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 162562.6481 | 9.5252 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-23 13:30 | 2.2 | 17.5 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 163207.6481 | 9.5629 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-23 14:30 | 2.3 | 17.3 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 163852.6481 | 9.6007 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-23 15:30 | 2.5 | 17.1 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 164497.6481 | 9.6385 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-23 16:30 | 2.7 | 16.6 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 165142.6481 | 9.6763 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-23 17:30 | 2.7 | 15.9 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 165787.6481 | 9.7141 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-23 18:30 | 2.8 | 15.7 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 166432.6481 | 9.7519 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-23 19:30 | 2.8 | 15.8 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 167077.6481 | 9.7897 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-23 20:30 | 2.7 | 16 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 167722.6481 | 9.8275 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-23 21:30 | 2.7 | 15.7 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 168367.6481 | 9.8653 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-23 22:30 | 2.7 | 15.1 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 169012.6481 | 9.9031 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-23 23:30 | 2.9 | 14.5 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 169657.6481 | 9.9409 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-24 00:30 | 2.8 | 13.5 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 170302.6481 | 9.9787 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-24 01:30 | 2.7 | 12.4 | 140 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170302.6481 | 9.9787 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-24 02:30 | 2.8 | 11.7 | 140 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170302.6481 | 9.9787 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-24 03:30 | 3 | 11.2 | 140 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170302.6481 | 9.9787 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-24 04:30 | 3.4 | 10.6 | 140 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170302.6481 | 9.9787 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-24 05:30 | 3.7 | 9.9 | 142.5 | 3280 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170302.6481 | 9.9787 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-24 06:30 | 3.9 | 9.4 | 147.5 | 2920 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170302.6481 | 9.9787 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-24 07:30 | 4.2 | 9.4 | 150 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170302.6481 | 9.9787 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-24 08:30 | 4.7 | 9.4 | 152.5 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170302.6481 | 9.9787 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-24 09:30 | 4.9 | 8.7 | 157.5 | 2560 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170302.6481 | 9.9787 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-24 10:30 | 5 | 7.6 | 160 | 1840 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170302.6481 | 9.9787 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-24 11:30 | 5.1 | 6.8 | 165 | 1120 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170302.6481 | 9.9787 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-24 12:30 | 5.3 | 6.1 | 180 | 760 | 940 | 620 | 0 | 620 | 0 | 0 | 170302.6481 | 9.9787 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-24 13:30 | 5.5 | 6 | 197.5 | 760 | 760 | 440 | 0 | 440 | 0 | 0 | 170302.6481 | 9.9787 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-24 14:30 | 5.4 | 6.4 | 207.5 | 760 | 760 | 440 | 0 | 440 | 0 | 0 | 170302.6481 | 9.9787 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-24 15:30 | 5.5 | 6.5 | 205 | 1120 | 940 | 620 | 0 | 620 | 0 | 0 | 170302.6481 | 9.9787 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-24 16:30 | 5.8 | 5.7 | 195 | 500 | 810 | 490 | 0 | 490 | 0 | 0 | 170302.6481 | 9.9787 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-24 17:30 | 5.4 | 5 | 190 | 340 | 420 | 100 | 0 | 100 | 0 | 0 | 170302.6481 | 9.9787 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-24 18:30 | 4.7 | 5.6 | 190 | 500 | 420 | 100 | 0 | 100 | 0 | 0 | 170302.6481 | 9.9787 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-24 19:30 | 4.6 | 5.9 | 190 | 500 | 500 | 180 | 0 | 180 | 0 | 0 | 170302.6481 | 9.9787 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-24 20:30 | 4.9 | 5.5 | 192.5 | 500 | 500 | 180 | 0 | 180 | 0 | 0 | 170302.6481 | 9.9787 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-24 21:30 | 5.1 | 6 | 200 | 760 | 630 | 310 | 0 | 310 | 0 | 0 | 170302.6481 | 9.9787 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-24 22:30 | 5.2 | 7.1 | 210 | 1480 | 1120 | 800 | 0 | 800 | 0 | 0 | 170302.6481 | 9.9787 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-24 23:30 | 5.6 | 7.7 | 217.5 | 1840 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170302.6481 | 9.9787 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-25 00:30 | 5.7 | 7.8 | 215 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170302.6481 | 9.9787 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-25 01:30 | 5.8 | 7.6 | 210 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170302.6481 | 9.9787 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-25 02:30 | 5.8 | 8.1 | 217.5 | 2200 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170302.6481 | 9.9787 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-25 03:30 | 5.7 | 8.4 | 227.5 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170302.6481 | 9.9787 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-25 04:30 | 6 | 6.5 | 217.5 | 1120 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170302.6481 | 9.9787 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-25 05:30 | 5.8 | 4.7 | 195 | 199.3333 | 659.6667 | 339.6667 | 0 | 339.6667 | 0 | 0 | 170302.6481 | 9.9787 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-02-25 06:30 | 5.4 | 4.7 | 185 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 170034.5 | 9.963 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-02-25 07:30 | 4.8 | 4.7 | 180 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 169766.3519 | 9.9472 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-02-25 08:30 | 4.5 | 4.5 | 172.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 169498.2037 | 9.9315 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-02-25 09:30 | 4.8 | 5.2 | 172.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 169386.3519 | 9.925 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-25 10:30 | 5.4 | 6 | 175 | 760 | 550 | 230 | 0 | 230 | 115 | 0 | 169501.3519 | 9.9317 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-25 11:30 | 5.9 | 5.8 | 170 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 169656.3519 | 9.9408 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-25 12:30 | 6 | 4.9 | 162.5 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 169671.1852 | 9.9417 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-02-25 13:30 | 6.1 | 4.5 | 157.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 169403.037 | 9.926 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-02-25 14:30 | 6.1 | 4.9 | 152.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 169134.8889 | 9.9102 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-25 15:30 | 6.1 | 5.5 | 150 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 169149.7222 | 9.9111 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-25 16:30 | 5.9 | 5.7 | 147.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 169239.7222 | 9.9164 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-25 17:30 | 5.9 | 5.9 | 140 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 169329.7222 | 9.9217 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-25 18:30 | 5.8 | 6.4 | 132.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 169484.7222 | 9.9307 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-25 19:30 | 5.6 | 6.9 | 127.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 169794.7222 | 9.9489 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-25 20:30 | 5.5 | 7.2 | 125 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-25 21:30 | 5.3 | 6.9 | 127.5 | 1120 | 1300 | 980 | 0 | 980 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-25 22:30 | 5.2 | 6.7 | 132.5 | 1120 | 1120 | 800 | 0 | 800 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-25 23:30 | 5.3 | 6.4 | 140 | 760 | 940 | 620 | 0 | 620 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-26 00:30 | 5.5 | 5.8 | 145 | 500 | 630 | 310 | 0 | 310 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-26 01:30 | 5.5 | 5.4 | 142.5 | 340 | 420 | 100 | 0 | 100 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-26 02:30 | 5.5 | 5.6 | 140 | 500 | 420 | 100 | 0 | 100 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-26 03:30 | 5.5 | 5.9 | 140 | 500 | 500 | 180 | 0 | 180 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-26 04:30 | 5.5 | 5.9 | 140 | 500 | 500 | 180 | 0 | 180 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-26 05:30 | 5.5 | 5.9 | 137.5 | 500 | 500 | 180 | 0 | 180 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-26 06:30 | 5.6 | 5.9 | 132.5 | 500 | 500 | 180 | 0 | 180 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-26 07:30 | 5.7 | 6.1 | 127.5 | 760 | 630 | 310 | 0 | 310 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-26 08:30 | 5.7 | 7.2 | 122.5 | 1480 | 1120 | 800 | 0 | 800 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-26 09:30 | 5.8 | 8.7 | 122.5 | 2560 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-26 10:30 | 5.8 | 9.2 | 130 | 2920 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-26 11:30 | 5.7 | 8.5 | 140 | 2560 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-26 12:30 | 5.7 | 8.1 | 150 | 2200 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-26 13:30 | 5.8 | 8.3 | 157.5 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-26 14:30 | 5.9 | 8.7 | 160 | 2560 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-26 15:30 | 5.9 | 9 | 157.5 | 2920 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-26 16:30 | 5.8 | 9 | 145 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-26 17:30 | 5.5 | 9.4 | 127.5 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-26 18:30 | 5.5 | 9.9 | 117.5 | 3280 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-26 19:30 | 5.7 | 9.6 | 112.5 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-26 20:30 | 5.6 | 8.6 | 112.5 | 2560 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-26 21:30 | 5.5 | 7.5 | 122.5 | 1840 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-26 22:30 | 5.5 | 7.2 | 140 | 1480 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-26 23:30 | 5.6 | 7.7 | 157.5 | 1840 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-27 00:30 | 5.7 | 7.8 | 167.5 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-27 01:30 | 5.6 | 7.8 | 170 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-27 02:30 | 5.5 | 7.8 | 170 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-27 03:30 | 5.3 | 7.8 | 170 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-27 04:30 | 5.2 | 8.4 | 170 | 2200 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-27 05:30 | 5.2 | 8.6 | 170 | 2560 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-27 06:30 | 5.2 | 8.1 | 172.5 | 2200 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-27 07:30 | 5.2 | 7.2 | 177.5 | 1480 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-27 08:30 | 5.3 | 6.3 | 180 | 760 | 1120 | 800 | 0 | 800 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-27 09:30 | 5.3 | 6.1 | 185 | 760 | 760 | 440 | 0 | 440 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-27 10:30 | 5.3 | 7 | 200 | 1480 | 1120 | 800 | 0 | 800 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-27 11:30 | 5.8 | 7.8 | 212.5 | 1840 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-27 12:30 | 6.8 | 7.7 | 210 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-27 13:30 | 7.3 | 7.2 | 202.5 | 1480 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-27 14:30 | 7 | 6.8 | 202.5 | 1120 | 1300 | 980 | 0 | 980 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-27 15:30 | 6.9 | 6.2 | 202.5 | 760 | 940 | 620 | 0 | 620 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-02-27 16:30 | 6.9 | 4.8 | 192.5 | 199.3333 | 479.6667 | 159.6667 | 0 | 159.6667 | 0 | 0 | 170284.7222 | 9.9776 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-02-27 17:30 | 6.6 | 3.8 | 180 | 0 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 169795.0926 | 9.9489 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-02-27 18:30 | 6 | 3.7 | 180 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 169083.9815 | 9.9073 | 0 |  |  | 1 | 3 | 1 | 1
Lerwick | 1978-02-27 19:30 | 5.8 | 4.1 | 192.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 168458.0556 | 9.8706 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-02-27 20:30 | 5.9 | 4.2 | 200 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 167917.3148 | 9.8389 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-02-27 21:30 | 5.8 | 3.6 | 200 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 167291.3889 | 9.8022 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-02-27 22:30 | 5.3 | 3.3 | 202.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166580.2778 | 9.7606 | 0 |  |  | 1 | 7 | 1 | 1
Lerwick | 1978-02-27 23:30 | 4.8 | 3.6 | 210 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165869.1667 | 9.7189 | 0 |  |  | 1 | 8 | 1 | 2
Lerwick | 1978-02-28 00:30 | 4.6 | 3.9 | 212.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165158.0556 | 9.6772 | 0 |  |  | 1 | 9 | 1 | 3
Lerwick | 1978-02-28 01:30 | 4.5 | 3.6 | 200 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164446.9444 | 9.6356 | 0 |  |  | 1 | 10 | 1 | 4
Lerwick | 1978-02-28 02:30 | 3.9 | 3 | 190 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163735.8333 | 9.5939 | 0 |  |  | 1 | 11 | 1 | 5
Lerwick | 1978-02-28 03:30 | 3.5 | 2.4 | 190 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163024.7222 | 9.5522 | 0 |  |  | 1 | 12 | 1 | 6
Lerwick | 1978-02-28 04:30 | 3.3 | 2.1 | 180 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162313.6111 | 9.5106 | 0 |  |  | 1 | 13 | 1 | 7
Lerwick | 1978-02-28 05:30 | 2.8 | 2.1 | 162.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161602.5 | 9.4689 | 0 |  |  | 1 | 14 | 1 | 8
Lerwick | 1978-02-28 06:30 | 3.7 | 2.1 | 152.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160891.3889 | 9.4272 | 0 |  |  | 1 | 15 | 1 | 9
Lerwick | 1978-02-28 07:30 | 4.6 | 2.3 | 147.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160180.2778 | 9.3856 | 0 |  |  | 1 | 16 | 1 | 10
Lerwick | 1978-02-28 08:30 | 4.8 | 2.8 | 140 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 159469.1667 | 9.3439 | 0 |  |  | 1 | 17 | 1 | 11
Lerwick | 1978-02-28 09:30 | 5.2 | 3.1 | 127.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 158758.0556 | 9.3022 | 0 |  |  | 1 | 18 | 1 | 12
Lerwick | 1978-02-28 10:30 | 4.8 | 2.6 | 112.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 158046.9444 | 9.2606 | 0 |  |  | 1 | 19 | 1 | 13
Lerwick | 1978-02-28 11:30 | 4.4 | 1.8 | 90 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 157335.8333 | 9.2189 | 0 |  |  | 1 | 20 | 1 | 14
Lerwick | 1978-02-28 12:30 | 4.4 | 2.1 | 77.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 156624.7222 | 9.1772 | 0 |  |  | 1 | 21 | 1 | 15
Lerwick | 1978-02-28 13:30 | 4.8 | 3.3 | 95 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 155913.6111 | 9.1356 | 0 |  |  | 1 | 22 | 1 | 16
Lerwick | 1978-02-28 14:30 | 4.8 | 3.9 | 110 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 155202.5 | 9.0939 | 0 |  |  | 1 | 23 | 1 | 17
Lerwick | 1978-02-28 15:30 | 4.5 | 3.6 | 100 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 154491.3889 | 9.0522 | 0 |  |  | 1 | 24 | 1 | 18
Lerwick | 1978-02-28 16:30 | 4.4 | 3.3 | 80 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 153780.2778 | 9.0106 | 0 |  |  | 1 | 25 | 1 | 19
Lerwick | 1978-02-28 17:30 | 4.5 | 3.2 | 80 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 153069.1667 | 8.9689 | 0 |  |  | 1 | 26 | 1 | 20
Lerwick | 1978-02-28 18:30 | 4.8 | 3.1 | 107.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 152358.0556 | 8.9272 | 0 |  |  | 1 | 27 | 1 | 21
Lerwick | 1978-02-28 19:30 | 5.1 | 3.3 | 135 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 151646.9444 | 8.8856 | 0 |  |  | 1 | 28 | 1 | 22
Lerwick | 1978-02-28 20:30 | 5.2 | 4 | 150 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 151021.0185 | 8.8489 | 1 |  |  | 1 | 29 | 0 | 0
Lerwick | 1978-02-28 21:30 | 5 | 4.6 | 157.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 150616.5741 | 8.8252 | 1 |  |  | 1 | 30 | 0 | 0
Lerwick | 1978-02-28 22:30 | 4.7 | 4.4 | 157.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 150212.1296 | 8.8015 | 1 |  |  | 1 | 31 | 0 | 0
Lerwick | 1978-02-28 23:30 | 4.5 | 3.8 | 155 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 149586.2037 | 8.7648 | 1 |  |  | 1 | 32 | 0 | 0
Lerwick | 1978-03-01 00:30 | 4.7 | 3.3 | 155 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 148875.0926 | 8.7231 | 0 |  |  | 1 | 33 | 1 | 1
Lerwick | 1978-03-01 01:30 | 4.9 | 2.4 | 155 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 148163.9815 | 8.6815 | 0 |  |  | 1 | 34 | 1 | 2
Lerwick | 1978-03-01 02:30 | 4.9 | 2.2 | 157.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 147452.8704 | 8.6398 | 0 |  |  | 1 | 35 | 1 | 3
Lerwick | 1978-03-01 03:30 | 4.6 | 3.3 | 160 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 146741.7593 | 8.5981 | 0 |  |  | 1 | 36 | 1 | 4
Lerwick | 1978-03-01 04:30 | 4.1 | 4.7 | 160 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 146252.1296 | 8.5695 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-01 05:30 | 4.7 | 6.3 | 160 | 760 | 479.6667 | 159.6667 | 0 | 159.6667 | 79.8333 | 0 | 146331.963 | 8.5741 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-01 06:30 | 5.2 | 7.3 | 157.5 | 1480 | 1120 | 800 | 0 | 800 | 400 | 0 | 146731.963 | 8.5976 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-01 07:30 | 4.9 | 6.8 | 150 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 147221.963 | 8.6263 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-01 08:30 | 4.9 | 6 | 142.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 147531.963 | 8.6445 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-01 09:30 | 5.1 | 6.5 | 140 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 147841.963 | 8.6626 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-01 10:30 | 5.1 | 7.6 | 137.5 | 1840 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 148421.963 | 8.6966 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-01 11:30 | 4.9 | 8 | 132.5 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 149066.963 | 8.7344 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-01 12:30 | 5 | 8.1 | 130 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 149711.963 | 8.7722 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-01 13:30 | 5.2 | 8.3 | 130 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 150356.963 | 8.81 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-01 14:30 | 5.3 | 8.7 | 130 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 151001.963 | 8.8478 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-01 15:30 | 5.4 | 9 | 130 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 151646.963 | 8.8856 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-01 16:30 | 5.6 | 9.1 | 127.5 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 152291.963 | 8.9234 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-01 17:30 | 5.7 | 9.6 | 122.5 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 152936.963 | 8.9612 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-01 18:30 | 5.6 | 10.2 | 120 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 153581.963 | 8.9989 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-01 19:30 | 5.5 | 10.9 | 120 | 4000 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 154226.963 | 9.0367 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-01 20:30 | 5.3 | 11.5 | 120 | 4472.2222 | 4236.1111 | 3916.1111 | 0 | 1290 | 645 | 0 | 154871.963 | 9.0745 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-01 21:30 | 5.2 | 12.1 | 122.5 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 645 | 0 | 155516.963 | 9.1123 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-01 22:30 | 5.3 | 12.7 | 127.5 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 645 | 0 | 156161.963 | 9.1501 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-01 23:30 | 5.3 | 13.2 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 156806.963 | 9.1879 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-02 00:30 | 5.1 | 13.2 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 157451.963 | 9.2257 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-02 01:30 | 5.1 | 13.1 | 127.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 158096.963 | 9.2635 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-02 02:30 | 5.2 | 13.3 | 125 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 158741.963 | 9.3013 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-02 03:30 | 5.2 | 13.6 | 127.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 159386.963 | 9.3391 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-02 04:30 | 5.1 | 13.3 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 160031.963 | 9.3769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-02 05:30 | 5.1 | 13 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 160676.963 | 9.4147 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-02 06:30 | 5.2 | 13 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 161321.963 | 9.4525 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-02 07:30 | 5.2 | 13.1 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 161966.963 | 9.4903 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-02 08:30 | 5.1 | 12.8 | 132.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 162611.963 | 9.528 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-02 09:30 | 5.1 | 12.4 | 140 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 645 | 0 | 163256.963 | 9.5658 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-02 10:30 | 5.3 | 12.2 | 147.5 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 163901.963 | 9.6036 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-02 11:30 | 5.4 | 11.6 | 150 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 645 | 0 | 164546.963 | 9.6414 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-02 12:30 | 5.5 | 10.8 | 150 | 4000 | 4236.1111 | 3916.1111 | 0 | 1290 | 645 | 0 | 165191.963 | 9.6792 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-02 13:30 | 5.5 | 9.9 | 150 | 3280 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 165836.963 | 9.717 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-02 14:30 | 5.4 | 9.4 | 152.5 | 2920 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 166481.963 | 9.7548 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-02 15:30 | 5.5 | 9.4 | 157.5 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 167126.963 | 9.7926 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-02 16:30 | 5.6 | 9.7 | 160 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 167771.963 | 9.8304 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-02 17:30 | 5.4 | 10.2 | 160 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 168416.963 | 9.8682 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-02 18:30 | 5.2 | 10.7 | 160 | 4000 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 169061.963 | 9.906 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-02 19:30 | 5 | 11 | 162.5 | 4300 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 169706.963 | 9.9438 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-02 20:30 | 4.9 | 10.9 | 165 | 4000 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 170351.963 | 9.9816 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-02 21:30 | 4.9 | 10.6 | 162.5 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170351.963 | 9.9816 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-02 22:30 | 5 | 10.4 | 160 | 3640 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170351.963 | 9.9816 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-02 23:30 | 5 | 10.4 | 160 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170351.963 | 9.9816 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-03 00:30 | 5.2 | 10.4 | 160 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170351.963 | 9.9816 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-03 01:30 | 5.4 | 9.9 | 162.5 | 3280 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170351.963 | 9.9816 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-03 02:30 | 5.5 | 9.4 | 167.5 | 2920 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170351.963 | 9.9816 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-03 03:30 | 5.5 | 9.1 | 170 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170351.963 | 9.9816 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-03 04:30 | 5.6 | 8.9 | 170 | 2560 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170351.963 | 9.9816 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-03 05:30 | 5.7 | 8.8 | 170 | 2560 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170351.963 | 9.9816 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-03 06:30 | 5.8 | 8.6 | 170 | 2560 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170351.963 | 9.9816 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-03 07:30 | 5.8 | 8.3 | 170 | 2200 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170351.963 | 9.9816 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-03 08:30 | 5.7 | 8 | 170 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170351.963 | 9.9816 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-03 09:30 | 5.7 | 7.8 | 170 | 1840 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170351.963 | 9.9816 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-03 10:30 | 5.8 | 7.6 | 170 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170351.963 | 9.9816 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-03 11:30 | 5.9 | 7.3 | 172.5 | 1480 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170351.963 | 9.9816 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-03 12:30 | 6 | 7.2 | 177.5 | 1480 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170351.963 | 9.9816 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-03 13:30 | 5.8 | 7.2 | 180 | 1480 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170351.963 | 9.9816 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-03 14:30 | 5.8 | 7.3 | 180 | 1480 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170351.963 | 9.9816 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-03 15:30 | 5.9 | 7.6 | 180 | 1840 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170351.963 | 9.9816 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-03 16:30 | 5.8 | 7.6 | 180 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170351.963 | 9.9816 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-03 17:30 | 5.6 | 7.3 | 177.5 | 1480 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170351.963 | 9.9816 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-03 18:30 | 5.5 | 7.2 | 172.5 | 1480 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170351.963 | 9.9816 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-03 19:30 | 5.5 | 7.3 | 170 | 1480 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170351.963 | 9.9816 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-03 20:30 | 5.5 | 7.3 | 175 | 1480 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170351.963 | 9.9816 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-03 21:30 | 5.5 | 6.8 | 185 | 1120 | 1300 | 980 | 0 | 980 | 0 | 0 | 170351.963 | 9.9816 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-03 22:30 | 5.4 | 6.4 | 190 | 760 | 940 | 620 | 0 | 620 | 0 | 0 | 170351.963 | 9.9816 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-03 23:30 | 5.3 | 6.1 | 187.5 | 760 | 760 | 440 | 0 | 440 | 0 | 0 | 170351.963 | 9.9816 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-04 00:30 | 4.9 | 5.4 | 185 | 340 | 550 | 230 | 0 | 230 | 0 | 0 | 170351.963 | 9.9816 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-03-04 01:30 | 4.9 | 4.4 | 187.5 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 170103.8148 | 9.967 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-03-04 02:30 | 5.2 | 3.5 | 195 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 169477.8889 | 9.9303 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-03-04 03:30 | 5.1 | 3.3 | 207.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168766.7778 | 9.8887 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-03-04 04:30 | 4.9 | 4 | 217.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 168140.8519 | 9.852 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-03-04 05:30 | 4.4 | 4.2 | 217.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 167600.1111 | 9.8203 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-03-04 06:30 | 3.8 | 3.9 | 222.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 166974.1852 | 9.7836 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-03-04 07:30 | 3.5 | 4.9 | 242.5 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 166484.5556 | 9.755 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-04 08:30 | 3.8 | 6.4 | 255 | 760 | 479.6667 | 159.6667 | 0 | 159.6667 | 79.8333 | 0 | 166564.3889 | 9.7596 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-04 09:30 | 3.6 | 6.7 | 252.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 166874.3889 | 9.7778 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-04 10:30 | 3.7 | 6.9 | 252.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 167274.3889 | 9.8012 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-04 11:30 | 5 | 7.8 | 252.5 | 1840 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 167854.3889 | 9.8352 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-04 12:30 | 5.4 | 8.1 | 247.5 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 168499.3889 | 9.873 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-04 13:30 | 5.5 | 8.4 | 247.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 169144.3889 | 9.9108 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-04 14:30 | 5 | 9.1 | 252.5 | 2920 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 169789.3889 | 9.9486 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-04 15:30 | 4.1 | 9.4 | 260 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 170434.3889 | 9.9864 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-04 16:30 | 4 | 8.6 | 272.5 | 2560 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170434.3889 | 9.9864 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-04 17:30 | 3.2 | 7.5 | 285 | 1840 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170434.3889 | 9.9864 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-04 18:30 | 2.3 | 6.4 | 295 | 760 | 1300 | 980 | 0 | 980 | 0 | 0 | 170434.3889 | 9.9864 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-04 19:30 | 2.2 | 5.2 | 307.5 | 340 | 550 | 230 | 0 | 230 | 0 | 0 | 170434.3889 | 9.9864 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-03-04 20:30 | 2.1 | 4.4 | 320 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 170186.2407 | 9.9719 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-03-04 21:30 | 1.7 | 4.2 | 322.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 169645.5 | 9.9402 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-03-04 22:30 | 1.3 | 3.9 | 310 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 169019.5741 | 9.9035 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-03-04 23:30 | 1.5 | 3.9 | 300 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168308.463 | 9.8618 | 0 |  |  | 1 | 5 | 1 | 1
Lerwick | 1978-03-05 00:30 | 2 | 4 | 302.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 167682.537 | 9.8251 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-03-05 01:30 | 2 | 4 | 305 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 167141.7963 | 9.7935 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-03-05 02:30 | 1.9 | 4.4 | 302.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 166601.0556 | 9.7618 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-03-05 03:30 | 1.7 | 5.5 | 295 | 500 | 288.3333 | 0 | 31.6667 | 0 | 0 | 70.3704 | 166530.6852 | 9.7577 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-05 04:30 | 1.5 | 6.6 | 290 | 1120 | 810 | 490 | 0 | 490 | 245 | 0 | 166775.6852 | 9.772 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-05 05:30 | 1.4 | 7.3 | 290 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 167265.6852 | 9.8007 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-05 06:30 | 1 | 7.6 | 290 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 167910.6852 | 9.8385 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-05 07:30 | 0.8 | 6.9 | 297.5 | 1120 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 168490.6852 | 9.8725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-05 08:30 | 0.9 | 6.4 | 310 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 168800.6852 | 9.8907 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-05 09:30 | 1.3 | 6.7 | 312.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 169110.6852 | 9.9088 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-05 10:30 | 2.1 | 7.2 | 312.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 169600.6852 | 9.9375 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-05 11:30 | 2.5 | 7.5 | 317.5 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 170245.6852 | 9.9753 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-05 12:30 | 2.5 | 7.3 | 320 | 1480 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170245.6852 | 9.9753 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-05 13:30 | 2.4 | 7.1 | 322.5 | 1480 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170245.6852 | 9.9753 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-05 14:30 | 2.5 | 6.7 | 327.5 | 1120 | 1300 | 980 | 0 | 980 | 0 | 0 | 170245.6852 | 9.9753 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-05 15:30 | 2.5 | 6.1 | 332.5 | 760 | 940 | 620 | 0 | 620 | 0 | 0 | 170245.6852 | 9.9753 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-05 16:30 | 2.3 | 5.2 | 337.5 | 340 | 550 | 230 | 0 | 230 | 0 | 0 | 170245.6852 | 9.9753 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-03-05 17:30 | 1.7 | 4 | 342.5 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 169997.537 | 9.9608 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-03-05 18:30 | 0.8 | 3.4 | 345 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 169371.6111 | 9.9241 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-03-05 19:30 | -0.1 | 3 | 342.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168660.5 | 9.8825 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-03-05 20:30 | -0.3 | 2.7 | 342.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167949.3889 | 9.8408 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-03-05 21:30 | -0.5 | 2.9 | 347.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167238.2778 | 9.7991 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-03-05 22:30 | -1.4 | 2.6 | 350 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166527.1667 | 9.7575 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-03-05 23:30 | -1.4 | 1.7 | 347.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165816.0556 | 9.7158 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-03-06 00:30 | -1 | 1.4 | 172.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165104.9444 | 9.6741 | 0 |  |  | 1 | 9 | 1 | 6
Lerwick | 1978-03-06 01:30 | -0.8 | 1.5 | 12.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164393.8333 | 9.6325 | 0 |  |  | 1 | 10 | 1 | 7
Lerwick | 1978-03-06 02:30 | -0.2 | 1 | 20 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163682.7222 | 9.5908 | 0 |  |  | 1 | 11 | 1 | 8
Lerwick | 1978-03-06 03:30 | -0.3 | 0.6 | 27.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162971.6111 | 9.5491 | 0 |  |  | 1 | 12 | 1 | 9
Lerwick | 1978-03-06 04:30 | -0.7 | 1.5 | 67.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162260.5 | 9.5075 | 0 |  |  | 1 | 13 | 1 | 10
Lerwick | 1978-03-06 05:30 | -0.3 | 2.9 | 105 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161549.3889 | 9.4658 | 0 |  |  | 1 | 14 | 1 | 11
Lerwick | 1978-03-06 06:30 | 0.2 | 4.2 | 120 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 160923.463 | 9.4291 | 1 |  |  | 1 | 15 | 0 | 0
Lerwick | 1978-03-06 07:30 | 0.4 | 5.5 | 130 | 500 | 288.3333 | 0 | 31.6667 | 0 | 0 | 70.3704 | 160853.0926 | 9.425 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-06 08:30 | 1 | 6.4 | 137.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 161008.0926 | 9.4341 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-06 09:30 | 1.6 | 6.9 | 140 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 161318.0926 | 9.4522 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-06 10:30 | 1.8 | 7.6 | 142.5 | 1840 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 161898.0926 | 9.4862 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-06 11:30 | 2.2 | 8 | 147.5 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 162543.0926 | 9.524 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-06 12:30 | 2 | 8.3 | 150 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 163188.0926 | 9.5618 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-06 13:30 | 1.6 | 8.7 | 150 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 163833.0926 | 9.5996 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-06 14:30 | 1.8 | 9.1 | 150 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 164478.0926 | 9.6374 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-06 15:30 | 2.2 | 9 | 150 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 165123.0926 | 9.6752 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-06 16:30 | 2.8 | 8.4 | 152.5 | 2200 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 165768.0926 | 9.713 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-06 17:30 | 3.6 | 8.1 | 157.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 166413.0926 | 9.7508 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-06 18:30 | 4 | 7.6 | 165 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 167058.0926 | 9.7886 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-06 19:30 | 4.3 | 6.5 | 177.5 | 1120 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 167638.0926 | 9.8225 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-06 20:30 | 4.4 | 5.6 | 185 | 500 | 810 | 490 | 0 | 490 | 245 | 0 | 167883.0926 | 9.8369 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-06 21:30 | 4.2 | 5.2 | 182.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 167933.0926 | 9.8398 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-03-06 22:30 | 4.3 | 4.9 | 180 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 167821.2407 | 9.8333 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-03-06 23:30 | 4.6 | 4.9 | 187.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 167553.0926 | 9.8176 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-03-07 00:30 | 4.8 | 5.4 | 207.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 167441.2407 | 9.811 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-07 01:30 | 5.3 | 6 | 225 | 760 | 550 | 230 | 0 | 230 | 115 | 0 | 167556.2407 | 9.8177 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-07 02:30 | 5.8 | 5.9 | 230 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 167711.2407 | 9.8268 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-07 03:30 | 5.9 | 5.8 | 230 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 167801.2407 | 9.8321 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-07 04:30 | 6.1 | 5.9 | 227.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 167891.2407 | 9.8374 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-07 05:30 | 6.1 | 5.4 | 217.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 167941.2407 | 9.8403 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-03-07 06:30 | 5.9 | 4.4 | 200 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 167693.0926 | 9.8258 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-03-07 07:30 | 5.4 | 4.2 | 185 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 167152.3519 | 9.7941 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-03-07 08:30 | 5.2 | 4.9 | 180 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 166747.9074 | 9.7704 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-07 09:30 | 5.6 | 5.8 | 182.5 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 166762.7407 | 9.7713 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-07 10:30 | 6.2 | 6.6 | 187.5 | 1120 | 810 | 490 | 0 | 490 | 245 | 0 | 167007.7407 | 9.7856 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-07 11:30 | 6.4 | 7 | 192.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 167497.7407 | 9.8143 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-07 12:30 | 6.3 | 6.8 | 195 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 167987.7407 | 9.843 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-07 13:30 | 6.5 | 6.4 | 190 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 168297.7407 | 9.8612 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-07 14:30 | 6.6 | 5.9 | 185 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 168452.7407 | 9.8703 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-07 15:30 | 6.3 | 5.8 | 187.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 168542.7407 | 9.8756 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-07 16:30 | 6.1 | 5.9 | 190 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 168632.7407 | 9.8808 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-07 17:30 | 5.8 | 5.8 | 190 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 168722.7407 | 9.8861 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-07 18:30 | 5.6 | 5.7 | 187.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 168812.7407 | 9.8914 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-07 19:30 | 5.5 | 6 | 182.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 168967.7407 | 9.9005 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-07 20:30 | 5.5 | 6.9 | 182.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 169277.7407 | 9.9186 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-07 21:30 | 5.5 | 7.7 | 187.5 | 1840 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 169857.7407 | 9.9526 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-07 22:30 | 5.6 | 8.2 | 187.5 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-07 23:30 | 5.8 | 9 | 182.5 | 2920 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-08 00:30 | 5.8 | 9.9 | 182.5 | 3280 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-08 01:30 | 5.6 | 10.1 | 187.5 | 3640 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-08 02:30 | 5.5 | 9.7 | 192.5 | 3280 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-08 03:30 | 5.5 | 9.2 | 197.5 | 2920 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-08 04:30 | 5.5 | 8.5 | 200 | 2560 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-08 05:30 | 5.5 | 8.4 | 207.5 | 2200 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-08 06:30 | 5.5 | 9.3 | 230 | 2920 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-08 07:30 | 5.7 | 10.5 | 262.5 | 4000 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-08 08:30 | 6.3 | 11.9 | 290 | 4472.2222 | 4236.1111 | 3916.1111 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-08 09:30 | 6.5 | 12.8 | 297.5 | 4600 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-08 10:30 | 5.9 | 13.6 | 292.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-08 11:30 | 5.7 | 14.4 | 290 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-08 12:30 | 5.9 | 14.7 | 287.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-08 13:30 | 6.5 | 14.1 | 282.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-08 14:30 | 6.5 | 13.2 | 280 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-08 15:30 | 6.1 | 12.9 | 280 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-08 16:30 | 6.2 | 12.9 | 280 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-08 17:30 | 6.2 | 12.3 | 280 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-08 18:30 | 6.1 | 10.9 | 280 | 4000 | 4268.0556 | 3948.0556 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-08 19:30 | 6.2 | 9.5 | 280 | 3280 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-08 20:30 | 5.8 | 8.5 | 277.5 | 2560 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-08 21:30 | 5.3 | 8 | 267.5 | 2200 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-08 22:30 | 5.6 | 8.9 | 255 | 2560 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-08 23:30 | 6.1 | 10.6 | 250 | 4000 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-09 00:30 | 6.2 | 11.6 | 250 | 4472.2222 | 4236.1111 | 3916.1111 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-09 01:30 | 6.3 | 11.4 | 250 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-09 02:30 | 6.5 | 10.5 | 252.5 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-09 03:30 | 6.5 | 9.6 | 255 | 3280 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-09 04:30 | 6.5 | 9.4 | 252.5 | 2920 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-09 05:30 | 6.5 | 9.7 | 247.5 | 3280 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-09 06:30 | 6.5 | 10.2 | 245 | 3640 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-09 07:30 | 6.5 | 10.7 | 247.5 | 4000 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-09 08:30 | 6.5 | 11.2 | 250 | 4300 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-09 09:30 | 6.5 | 11.2 | 250 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-09 10:30 | 6.6 | 10.2 | 250 | 3640 | 3970 | 3650 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-09 11:30 | 6.8 | 8.8 | 250 | 2560 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-09 12:30 | 6.7 | 8 | 247.5 | 2200 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-09 13:30 | 6.6 | 7.8 | 242.5 | 1840 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-09 14:30 | 6.6 | 6.9 | 237.5 | 1120 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-09 15:30 | 6.5 | 5.9 | 232.5 | 500 | 810 | 490 | 0 | 490 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-09 16:30 | 6.5 | 5.5 | 222.5 | 500 | 500 | 180 | 0 | 180 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-09 17:30 | 6.2 | 4.7 | 205 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 0 | 0 | 170502.7407 | 9.9904 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-03-09 18:30 | 5.7 | 4.2 | 192.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 170098.2963 | 9.9667 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-03-09 19:30 | 5.4 | 4.9 | 192.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 169693.8519 | 9.943 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-09 20:30 | 5.2 | 5.6 | 197.5 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 169708.6852 | 9.9439 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-09 21:30 | 5 | 6 | 200 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 169863.6852 | 9.953 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-09 22:30 | 5 | 6.2 | 200 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 170083.6852 | 9.9658 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-09 23:30 | 5.1 | 6.3 | 200 | 760 | 760 | 440 | 0 | 440 | 0 | 0 | 170083.6852 | 9.9658 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-10 00:30 | 5.3 | 6.8 | 200 | 1120 | 940 | 620 | 0 | 620 | 0 | 0 | 170083.6852 | 9.9658 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-10 01:30 | 5.6 | 8.5 | 205 | 2560 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170083.6852 | 9.9658 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-10 02:30 | 6.1 | 10.9 | 217.5 | 4000 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170083.6852 | 9.9658 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-10 03:30 | 6.8 | 12.2 | 227.5 | 4536.1111 | 4268.0556 | 3948.0556 | 0 | 1290 | 0 | 0 | 170083.6852 | 9.9658 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-10 04:30 | 7 | 12.7 | 232.5 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170083.6852 | 9.9658 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-10 05:30 | 7.1 | 12.7 | 240 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170083.6852 | 9.9658 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-10 06:30 | 7.2 | 12.4 | 250 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170083.6852 | 9.9658 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-10 07:30 | 7.2 | 12.2 | 262.5 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170083.6852 | 9.9658 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-10 08:30 | 7.3 | 11.9 | 272.5 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170083.6852 | 9.9658 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-10 09:30 | 7.5 | 11.8 | 272.5 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170083.6852 | 9.9658 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-10 10:30 | 7.7 | 11.8 | 272.5 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170083.6852 | 9.9658 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-10 11:30 | 8.2 | 11.8 | 280 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170083.6852 | 9.9658 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-10 12:30 | 8.5 | 11.8 | 285 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170083.6852 | 9.9658 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-10 13:30 | 8.6 | 11.8 | 280 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170083.6852 | 9.9658 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-10 14:30 | 8.8 | 11.5 | 275 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170083.6852 | 9.9658 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-10 15:30 | 8.5 | 10.5 | 277.5 | 4000 | 4236.1111 | 3916.1111 | 0 | 1290 | 0 | 0 | 170083.6852 | 9.9658 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-10 16:30 | 8.1 | 8.7 | 280 | 2560 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170083.6852 | 9.9658 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-10 17:30 | 7.6 | 7 | 280 | 1480 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170083.6852 | 9.9658 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-10 18:30 | 6.8 | 6.1 | 277.5 | 760 | 1120 | 800 | 0 | 800 | 0 | 0 | 170083.6852 | 9.9658 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-10 19:30 | 6.3 | 5.8 | 272.5 | 500 | 630 | 310 | 0 | 310 | 0 | 0 | 170083.6852 | 9.9658 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-10 20:30 | 5.9 | 5.5 | 267.5 | 500 | 500 | 180 | 0 | 180 | 0 | 0 | 170083.6852 | 9.9658 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-10 21:30 | 5.7 | 4.9 | 262.5 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 0 | 0 | 170083.6852 | 9.9658 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-03-10 22:30 | 5.3 | 3.7 | 252.5 | 0 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 169594.0556 | 9.9372 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-03-10 23:30 | 5.3 | 2.8 | 252.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168882.9444 | 9.8955 | 0 |  |  | 1 | 3 | 1 | 1
Lerwick | 1978-03-11 00:30 | 5.7 | 2.2 | 130 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168171.8333 | 9.8538 | 0 |  |  | 1 | 4 | 1 | 2
Lerwick | 1978-03-11 01:30 | 5 | 1.8 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167460.7222 | 9.8122 | 0 |  |  | 1 | 5 | 1 | 3
Lerwick | 1978-03-11 02:30 | 3.7 | 2.2 | 65 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166749.6111 | 9.7705 | 0 |  |  | 1 | 6 | 1 | 4
Lerwick | 1978-03-11 03:30 | 3.4 | 2.6 | 150 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166038.5 | 9.7288 | 0 |  |  | 1 | 7 | 1 | 5
Lerwick | 1978-03-11 04:30 | 4.1 | 2.6 | 165 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165327.3889 | 9.6872 | 0 |  |  | 1 | 8 | 1 | 6
Lerwick | 1978-03-11 05:30 | 4.4 | 3.3 | 152.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164616.2778 | 9.6455 | 0 |  |  | 1 | 9 | 1 | 7
Lerwick | 1978-03-11 06:30 | 4.6 | 4.6 | 147.5 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 164126.6481 | 9.6168 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-11 07:30 | 5 | 5.9 | 155 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 164141.4815 | 9.6177 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-11 08:30 | 5.2 | 6.7 | 160 | 1120 | 810 | 490 | 0 | 490 | 245 | 0 | 164386.4815 | 9.632 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-11 09:30 | 5.3 | 7 | 160 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 164876.4815 | 9.6607 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-11 10:30 | 5.6 | 6.8 | 160 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 165366.4815 | 9.6894 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-11 11:30 | 5.6 | 7.3 | 162.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 165856.4815 | 9.7182 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-11 12:30 | 5.6 | 8.6 | 167.5 | 2560 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 166501.4815 | 9.7559 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-11 13:30 | 5.9 | 9.1 | 172.5 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 167146.4815 | 9.7937 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-11 14:30 | 6.1 | 8.5 | 177.5 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 167791.4815 | 9.8315 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-11 15:30 | 6 | 7.8 | 177.5 | 1840 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 168436.4815 | 9.8693 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-11 16:30 | 6.1 | 6.9 | 175 | 1120 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 169016.4815 | 9.9033 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-11 17:30 | 6.2 | 6 | 177.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 169326.4815 | 9.9215 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-11 18:30 | 6.1 | 5.5 | 182.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 169481.4815 | 9.9306 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-11 19:30 | 6 | 5.1 | 182.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 169531.4815 | 9.9335 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-03-11 20:30 | 6 | 4.6 | 177.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 169419.6296 | 9.9269 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-03-11 21:30 | 5.8 | 4.4 | 180 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 169015.1852 | 9.9032 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-03-11 22:30 | 5.8 | 4.4 | 192.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 168474.4444 | 9.8715 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-03-11 23:30 | 5.8 | 3.3 | 200 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 167848.5185 | 9.8349 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-03-12 00:30 | 5.7 | 1.6 | 192.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167137.4074 | 9.7932 | 0 |  |  | 1 | 6 | 1 | 1
Lerwick | 1978-03-12 01:30 | 5.6 | 1.1 | 185 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166426.2963 | 9.7515 | 0 |  |  | 1 | 7 | 1 | 2
Lerwick | 1978-03-12 02:30 | 5.5 | 1.3 | 190 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165715.1852 | 9.7099 | 0 |  |  | 1 | 8 | 1 | 3
Lerwick | 1978-03-12 03:30 | 5.5 | 1.1 | 200 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165004.0741 | 9.6682 | 0 |  |  | 1 | 9 | 1 | 4
Lerwick | 1978-03-12 04:30 | 5.6 | 1 | 207.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164292.963 | 9.6265 | 0 |  |  | 1 | 10 | 1 | 5
Lerwick | 1978-03-12 05:30 | 5.7 | 1 | 217.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163581.8519 | 9.5849 | 0 |  |  | 1 | 11 | 1 | 6
Lerwick | 1978-03-12 06:30 | 5.8 | 1 | 227.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162870.7407 | 9.5432 | 0 |  |  | 1 | 12 | 1 | 7
Lerwick | 1978-03-12 07:30 | 6.1 | 1.4 | 225 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162159.6296 | 9.5015 | 0 |  |  | 1 | 13 | 1 | 8
Lerwick | 1978-03-12 08:30 | 6.1 | 2.2 | 225 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161448.5185 | 9.4599 | 0 |  |  | 1 | 14 | 1 | 9
Lerwick | 1978-03-12 09:30 | 6.2 | 2.6 | 230 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160737.4074 | 9.4182 | 0 |  |  | 1 | 15 | 1 | 10
Lerwick | 1978-03-12 10:30 | 6.6 | 2.6 | 215 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160026.2963 | 9.3765 | 0 |  |  | 1 | 16 | 1 | 11
Lerwick | 1978-03-12 11:30 | 6.7 | 2.8 | 190 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 159315.1852 | 9.3349 | 0 |  |  | 1 | 17 | 1 | 12
Lerwick | 1978-03-12 12:30 | 6.5 | 3.1 | 182.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 158604.0741 | 9.2932 | 0 |  |  | 1 | 18 | 1 | 13
Lerwick | 1978-03-12 13:30 | 6.2 | 3.1 | 182.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 157892.963 | 9.2515 | 0 |  |  | 1 | 19 | 1 | 14
Lerwick | 1978-03-12 14:30 | 5.9 | 3.2 | 172.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 157181.8519 | 9.2099 | 0 |  |  | 1 | 20 | 1 | 15
Lerwick | 1978-03-12 15:30 | 5.7 | 3.3 | 165 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 156470.7407 | 9.1682 | 0 |  |  | 1 | 21 | 1 | 16
Lerwick | 1978-03-12 16:30 | 5.6 | 3.6 | 170 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 155759.6296 | 9.1265 | 0 |  |  | 1 | 22 | 1 | 17
Lerwick | 1978-03-12 17:30 | 5.6 | 4.2 | 177.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 155133.7037 | 9.0899 | 1 |  |  | 1 | 23 | 0 | 0
Lerwick | 1978-03-12 18:30 | 5.4 | 4.1 | 182.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 154592.963 | 9.0582 | 1 |  |  | 1 | 24 | 0 | 0
Lerwick | 1978-03-12 19:30 | 5.4 | 4.4 | 197.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 154052.2222 | 9.0265 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-12 20:30 | 5.4 | 6.1 | 220 | 760 | 418.3333 | 98.3333 | 0 | 98.3333 | 49.1667 | 0 | 154101.3889 | 9.0294 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-12 21:30 | 5 | 7.6 | 232.5 | 1840 | 1300 | 980 | 0 | 980 | 490 | 0 | 154591.3889 | 9.0581 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-12 22:30 | 4.2 | 8.4 | 242.5 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 155236.3889 | 9.0959 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-12 23:30 | 4 | 9.3 | 260 | 2920 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 155881.3889 | 9.1337 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-13 00:30 | 4.1 | 10.5 | 275 | 4000 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 156526.3889 | 9.1715 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-13 01:30 | 4.5 | 11.5 | 280 | 4472.2222 | 4236.1111 | 3916.1111 | 0 | 1290 | 645 | 0 | 157171.3889 | 9.2093 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-13 02:30 | 4.6 | 11.8 | 280 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 645 | 0 | 157816.3889 | 9.2471 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-13 03:30 | 4.6 | 12.3 | 280 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 645 | 0 | 158461.3889 | 9.2848 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-13 04:30 | 4.8 | 13 | 280 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 645 | 0 | 159106.3889 | 9.3226 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-13 05:30 | 4.8 | 12.2 | 282.5 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 645 | 0 | 159751.3889 | 9.3604 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-13 06:30 | 4.9 | 10.5 | 285 | 4000 | 4268.0556 | 3948.0556 | 0 | 1290 | 645 | 0 | 160396.3889 | 9.3982 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-13 07:30 | 4.8 | 9.6 | 282.5 | 3280 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 161041.3889 | 9.436 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-13 08:30 | 4.8 | 9.9 | 277.5 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 161686.3889 | 9.4738 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-13 09:30 | 4.9 | 10.4 | 272.5 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 162331.3889 | 9.5116 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-13 10:30 | 5.6 | 10.1 | 270 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 162976.3889 | 9.5494 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-13 11:30 | 6.3 | 9.4 | 267.5 | 2920 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 163621.3889 | 9.5872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-13 12:30 | 6.6 | 8.9 | 262.5 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 164266.3889 | 9.625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-13 13:30 | 6.7 | 8.4 | 257.5 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 164911.3889 | 9.6628 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-13 14:30 | 6.4 | 7.9 | 255 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 165556.3889 | 9.7006 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-13 15:30 | 6.2 | 7.3 | 252.5 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 166201.3889 | 9.7384 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-13 16:30 | 6.2 | 6.2 | 245 | 760 | 1120 | 800 | 0 | 800 | 400 | 0 | 166601.3889 | 9.7618 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-13 17:30 | 5.7 | 4.9 | 240 | 199.3333 | 479.6667 | 159.6667 | 0 | 159.6667 | 79.8333 | 0 | 166681.2222 | 9.7665 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-03-13 18:30 | 4.7 | 4 | 232.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 166276.7778 | 9.7428 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-03-13 19:30 | 3.3 | 2.9 | 220 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 165650.8519 | 9.7061 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-03-13 20:30 | 2.3 | 1.7 | 212.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164939.7407 | 9.6644 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-03-13 21:30 | 1.8 | 0.9 | 245 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164228.6296 | 9.6228 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-03-13 22:30 | 1.2 | 0.2 | 140 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163517.5185 | 9.5811 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-03-13 23:30 | 0.5 | 0.4 | 27.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162806.4074 | 9.5394 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-03-14 00:30 | 0.4 | 1.7 | 82.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162095.2963 | 9.4978 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-03-14 01:30 | 1.3 | 3.5 | 110 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161384.1852 | 9.4561 | 0 |  |  | 1 | 9 | 1 | 6
Lerwick | 1978-03-14 02:30 | 2.7 | 4.7 | 107.5 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 160894.5556 | 9.4274 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-03-14 03:30 | 3.3 | 5.4 | 100 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 160782.7037 | 9.4209 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-14 04:30 | 3.1 | 6.7 | 92.5 | 1120 | 730 | 410 | 0 | 410 | 205 | 0 | 160987.7037 | 9.4329 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-14 05:30 | 3.1 | 8.1 | 90 | 2200 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 161632.7037 | 9.4707 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-14 06:30 | 3.2 | 9.3 | 90 | 2920 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 162277.7037 | 9.5085 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-14 07:30 | 3.4 | 10.1 | 90 | 3640 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 162922.7037 | 9.5463 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-14 08:30 | 3.8 | 10.9 | 90 | 4000 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 163567.7037 | 9.584 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-14 09:30 | 4.1 | 11.8 | 90 | 4472.2222 | 4236.1111 | 3916.1111 | 0 | 1290 | 645 | 0 | 164212.7037 | 9.6218 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-14 10:30 | 4.4 | 12.7 | 87.5 | 4600 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 164857.7037 | 9.6596 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-14 11:30 | 4.5 | 13.5 | 80 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 165502.7037 | 9.6974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-14 12:30 | 4.4 | 14.1 | 72.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 166147.7037 | 9.7352 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-14 13:30 | 4.3 | 14.4 | 70 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 166792.7037 | 9.773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-14 14:30 | 4 | 14.4 | 70 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 167437.7037 | 9.8108 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-14 15:30 | 3.7 | 14.4 | 70 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 168082.7037 | 9.8486 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-14 16:30 | 3.5 | 14.5 | 70 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 168727.7037 | 9.8864 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-14 17:30 | 3.4 | 14.5 | 70 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 169372.7037 | 9.9242 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-14 18:30 | 3.3 | 14.3 | 67.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-14 19:30 | 3.4 | 14.3 | 62.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-14 20:30 | 3.6 | 14.3 | 60 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-14 21:30 | 3.6 | 14 | 60 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-14 22:30 | 3.5 | 13.7 | 60 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-14 23:30 | 3.3 | 13.3 | 57.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-15 00:30 | 3.2 | 13.2 | 52.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-15 01:30 | 2.8 | 13.6 | 50 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-15 02:30 | 2.5 | 13.6 | 50 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-15 03:30 | 2.3 | 13.1 | 50 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-15 04:30 | 2.1 | 12.9 | 50 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-15 05:30 | 2 | 12.9 | 50 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-15 06:30 | 2 | 12.7 | 50 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-15 07:30 | 2 | 12.4 | 50 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-15 08:30 | 2.1 | 12.4 | 50 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-15 09:30 | 2.3 | 12.4 | 50 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-15 10:30 | 2.6 | 12.4 | 50 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-15 11:30 | 2.7 | 12.4 | 50 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-15 12:30 | 3.1 | 12.2 | 50 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-15 13:30 | 3.4 | 11.9 | 50 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-15 14:30 | 3.1 | 11.6 | 50 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-15 15:30 | 2.8 | 11.2 | 50 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-15 16:30 | 2.7 | 10.7 | 50 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-15 17:30 | 2.5 | 10.5 | 50 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-15 18:30 | 2.2 | 10.6 | 50 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-15 19:30 | 1.8 | 10.8 | 50 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-15 20:30 | 1.5 | 10.8 | 50 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-15 21:30 | 1.1 | 10.9 | 50 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-15 22:30 | 1.3 | 11.2 | 50 | 4300 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-15 23:30 | 1.6 | 11.5 | 47.5 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-16 00:30 | 1.6 | 11.2 | 42.5 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-16 01:30 | 1.5 | 11.2 | 40 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-16 02:30 | 1.5 | 11.7 | 40 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-16 03:30 | 1.5 | 12 | 37.5 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-16 04:30 | 1.4 | 12.7 | 35 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-16 05:30 | 1.2 | 13.6 | 35 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-16 06:30 | 1.2 | 13.4 | 32.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-16 07:30 | 1 | 12.3 | 32.5 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-16 08:30 | 0.9 | 11.8 | 35 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-16 09:30 | 1 | 12.1 | 32.5 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-16 10:30 | 1 | 12.4 | 30 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-16 11:30 | 1.1 | 12.8 | 30 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-16 12:30 | 1.3 | 13.1 | 30 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-16 13:30 | 1.2 | 13 | 30 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-16 14:30 | 1.4 | 12.7 | 27.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-16 15:30 | 1.7 | 12.4 | 22.5 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-16 16:30 | 1.5 | 12.4 | 20 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-16 17:30 | 0.9 | 12.6 | 20 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-16 18:30 | 0.8 | 13.1 | 17.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-16 19:30 | 0.7 | 13.1 | 12.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-16 20:30 | 0.7 | 12.7 | 12.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-16 21:30 | 0.9 | 12.5 | 15 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-16 22:30 | 0.6 | 12 | 12.5 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-16 23:30 | 0.7 | 10.9 | 7.5 | 4000 | 4268.0556 | 3948.0556 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-17 00:30 | 0.8 | 9.6 | 180 | 3280 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-17 01:30 | 0.6 | 8.5 | 355 | 2560 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-17 02:30 | 0.1 | 7.6 | 355 | 1840 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-17 03:30 | -0.2 | 6.9 | 350 | 1120 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-17 04:30 | -0.5 | 6.2 | 342.5 | 760 | 940 | 620 | 0 | 620 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-17 05:30 | -0.9 | 5.3 | 335 | 340 | 550 | 230 | 0 | 230 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-17 06:30 | -1.6 | 5.4 | 325 | 340 | 340 | 20 | 0 | 20 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-17 07:30 | -1.2 | 6 | 322.5 | 760 | 550 | 230 | 0 | 230 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-17 08:30 | 0 | 6.3 | 325 | 760 | 760 | 440 | 0 | 440 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-17 09:30 | 0.4 | 6.9 | 322.5 | 1120 | 940 | 620 | 0 | 620 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-17 10:30 | 1.3 | 8.2 | 322.5 | 2200 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-17 11:30 | 2.2 | 9.4 | 327.5 | 2920 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-17 12:30 | 2.4 | 9.4 | 327.5 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-17 13:30 | 2.3 | 8.5 | 322.5 | 2560 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-17 14:30 | 2.3 | 8 | 320 | 2200 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-17 15:30 | 2.1 | 8.1 | 325 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-17 16:30 | 2.2 | 7.2 | 335 | 1480 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-17 17:30 | 1.7 | 5.7 | 337.5 | 500 | 990 | 670 | 0 | 670 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-17 18:30 | 1 | 4.7 | 325 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 0 | 0 | 170017.7037 | 9.962 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-03-17 19:30 | 0.7 | 4.2 | 307.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 169613.2593 | 9.9383 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-03-17 20:30 | 0.5 | 3.7 | 295 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 168987.3333 | 9.9016 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-03-17 21:30 | 0.2 | 3.6 | 282.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168276.2222 | 9.8599 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-03-17 22:30 | 0.4 | 3.6 | 270 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167565.1111 | 9.8183 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-03-17 23:30 | 1 | 3.3 | 260 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166854 | 9.7766 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-03-18 00:30 | 1 | 3.2 | 250 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166142.8889 | 9.7349 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-03-18 01:30 | 1 | 3.6 | 257.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165431.7778 | 9.6933 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-03-18 02:30 | 1.8 | 3.6 | 280 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164720.6667 | 9.6516 | 0 |  |  | 1 | 9 | 1 | 6
Lerwick | 1978-03-18 03:30 | 1.9 | 3.4 | 287.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164009.5556 | 9.6099 | 0 |  |  | 1 | 10 | 1 | 7
Lerwick | 1978-03-18 04:30 | 1.6 | 3.6 | 287.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163298.4444 | 9.5683 | 0 |  |  | 1 | 11 | 1 | 8
Lerwick | 1978-03-18 05:30 | 2 | 3.3 | 287.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162587.3333 | 9.5266 | 0 |  |  | 1 | 12 | 1 | 9
Lerwick | 1978-03-18 06:30 | 2.1 | 2.9 | 270 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161876.2222 | 9.4849 | 0 |  |  | 1 | 13 | 1 | 10
Lerwick | 1978-03-18 07:30 | 1.9 | 3 | 250 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161165.1111 | 9.4433 | 0 |  |  | 1 | 14 | 1 | 11
Lerwick | 1978-03-18 08:30 | 2.3 | 4.1 | 255 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 160539.1852 | 9.4066 | 1 |  |  | 1 | 15 | 0 | 0
Lerwick | 1978-03-18 09:30 | 3.8 | 5.6 | 265 | 500 | 288.3333 | 0 | 31.6667 | 0 | 0 | 70.3704 | 160468.8148 | 9.4025 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-18 10:30 | 5.3 | 6.9 | 262.5 | 1120 | 810 | 490 | 0 | 490 | 245 | 0 | 160713.8148 | 9.4168 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-18 11:30 | 5.9 | 7.8 | 260 | 1840 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 161293.8148 | 9.4508 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-18 12:30 | 6.2 | 8.1 | 260 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 161938.8148 | 9.4886 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-18 13:30 | 5.9 | 8 | 260 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 162583.8148 | 9.5264 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-18 14:30 | 6.3 | 7.2 | 270 | 1480 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 163228.8148 | 9.5642 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-18 15:30 | 6.5 | 5.4 | 282.5 | 340 | 910 | 590 | 0 | 590 | 295 | 0 | 163523.8148 | 9.5815 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-03-18 16:30 | 5.7 | 4.7 | 272.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 163411.963 | 9.5749 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-03-18 17:30 | 5.4 | 5.4 | 255 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 163300.1111 | 9.5684 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-18 18:30 | 5.7 | 5.6 | 247.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 163350.1111 | 9.5713 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-18 19:30 | 5.5 | 5.2 | 242.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 163400.1111 | 9.5742 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-18 20:30 | 5.3 | 5 | 240 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 163410.1111 | 9.5748 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-18 21:30 | 5.1 | 5 | 235 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 163420.1111 | 9.5754 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-03-18 22:30 | 5 | 4.7 | 217.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 163308.2593 | 9.5688 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-03-18 23:30 | 4.9 | 4.4 | 195 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 162903.8148 | 9.5451 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-03-19 00:30 | 4.6 | 4.7 | 182.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 162499.3704 | 9.5214 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-19 01:30 | 4.5 | 5.6 | 177.5 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 162514.2037 | 9.5223 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-19 02:30 | 4.6 | 6.8 | 172.5 | 1120 | 810 | 490 | 0 | 490 | 245 | 0 | 162759.2037 | 9.5367 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-19 03:30 | 4.7 | 8.4 | 170 | 2200 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 163404.2037 | 9.5745 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-19 04:30 | 4.6 | 10.3 | 167.5 | 3640 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 164049.2037 | 9.6123 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-19 05:30 | 4.4 | 12.6 | 162.5 | 4600 | 4120 | 3800 | 0 | 1290 | 645 | 0 | 164694.2037 | 9.6501 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-19 06:30 | 4.4 | 14.8 | 160 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 165339.2037 | 9.6878 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-19 07:30 | 4.5 | 15.9 | 160 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 165984.2037 | 9.7256 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-19 08:30 | 4.7 | 16.8 | 160 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 166629.2037 | 9.7634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-19 09:30 | 5.1 | 18.3 | 160 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 167274.2037 | 9.8012 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-19 10:30 | 5.1 | 19.6 | 160 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 167919.2037 | 9.839 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-19 11:30 | 4.7 | 20.7 | 160 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 168564.2037 | 9.8768 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-19 12:30 | 4.6 | 21.8 | 160 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 169209.2037 | 9.9146 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-19 13:30 | 4.5 | 21.9 | 162.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 169854.2037 | 9.9524 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-19 14:30 | 4 | 20.6 | 170 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 170499.2037 | 9.9902 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-19 15:30 | 3.9 | 18.7 | 177.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170499.2037 | 9.9902 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-19 16:30 | 3.7 | 16.2 | 180 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170499.2037 | 9.9902 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-19 17:30 | 3.4 | 13 | 185 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170499.2037 | 9.9902 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-19 18:30 | 3.6 | 10.4 | 197.5 | 3640 | 4120 | 3800 | 0 | 1290 | 0 | 0 | 170499.2037 | 9.9902 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-19 19:30 | 4.2 | 9 | 207.5 | 2920 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170499.2037 | 9.9902 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-19 20:30 | 4.3 | 8.5 | 210 | 2560 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170499.2037 | 9.9902 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-19 21:30 | 4 | 8.6 | 212.5 | 2560 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170499.2037 | 9.9902 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-19 22:30 | 3.9 | 8.8 | 215 | 2560 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170499.2037 | 9.9902 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-19 23:30 | 3.9 | 8.4 | 215 | 2200 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170499.2037 | 9.9902 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-20 00:30 | 3.9 | 7.7 | 217.5 | 1840 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170499.2037 | 9.9902 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-20 01:30 | 4 | 7.7 | 222.5 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170499.2037 | 9.9902 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-20 02:30 | 3.6 | 8.2 | 225 | 2200 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170499.2037 | 9.9902 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-20 03:30 | 3 | 8.6 | 225 | 2560 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170499.2037 | 9.9902 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-20 04:30 | 3 | 8.4 | 225 | 2200 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170499.2037 | 9.9902 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-20 05:30 | 3 | 8 | 222.5 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170499.2037 | 9.9902 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-20 06:30 | 2.9 | 8 | 225 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170499.2037 | 9.9902 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-20 07:30 | 3.1 | 8 | 235 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170499.2037 | 9.9902 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-20 08:30 | 3.2 | 8.2 | 235 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170499.2037 | 9.9902 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-20 09:30 | 3.4 | 9 | 225 | 2920 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170499.2037 | 9.9902 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-20 10:30 | 4.1 | 9.2 | 225 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170499.2037 | 9.9902 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-20 11:30 | 5 | 8.5 | 232.5 | 2560 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170499.2037 | 9.9902 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-20 12:30 | 4.8 | 8.1 | 232.5 | 2200 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170499.2037 | 9.9902 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-20 13:30 | 5.2 | 7.9 | 230 | 1840 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170499.2037 | 9.9902 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-20 14:30 | 5.2 | 7.3 | 230 | 1480 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170499.2037 | 9.9902 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-20 15:30 | 5 | 6.7 | 237.5 | 1120 | 1300 | 980 | 0 | 980 | 0 | 0 | 170499.2037 | 9.9902 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-20 16:30 | 4.4 | 5.9 | 245 | 500 | 810 | 490 | 0 | 490 | 0 | 0 | 170499.2037 | 9.9902 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-20 17:30 | 3.2 | 4.9 | 237.5 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 0 | 0 | 170499.2037 | 9.9902 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-03-20 18:30 | 2.6 | 4.1 | 235 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 170094.7593 | 9.9665 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-03-20 19:30 | 2 | 3.2 | 237.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 169468.8333 | 9.9298 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-03-20 20:30 | 1.5 | 2 | 220 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168757.7222 | 9.8881 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-03-20 21:30 | 1.4 | 1.4 | 202.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168046.6111 | 9.8465 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-03-20 22:30 | 1.4 | 1.4 | 207.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167335.5 | 9.8048 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-03-20 23:30 | 1.2 | 1.5 | 197.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166624.3889 | 9.7631 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-03-21 00:30 | 0.9 | 1.2 | 90 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165913.2778 | 9.7215 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-03-21 01:30 | 0.8 | 0.7 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165202.1667 | 9.6798 | 0 |  |  | 1 | 9 | 1 | 6
Lerwick | 1978-03-21 02:30 | 0.8 | 0.2 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164491.0556 | 9.6381 | 0 |  |  | 1 | 10 | 1 | 7
Lerwick | 1978-03-21 03:30 | 0.3 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163779.9444 | 9.5965 | 0 |  |  | 1 | 11 | 1 | 8
Lerwick | 1978-03-21 04:30 | 0 | 0.9 | 170 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163068.8333 | 9.5548 | 0 |  |  | 1 | 12 | 1 | 9
Lerwick | 1978-03-21 05:30 | -0.2 | 2 | 170 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162357.7222 | 9.5131 | 0 |  |  | 1 | 13 | 1 | 10
Lerwick | 1978-03-21 06:30 | -0.1 | 1.3 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161646.6111 | 9.4715 | 0 |  |  | 1 | 14 | 1 | 11
Lerwick | 1978-03-21 07:30 | 0.1 | 0.5 | 152.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160935.5 | 9.4298 | 0 |  |  | 1 | 15 | 1 | 12
Lerwick | 1978-03-21 08:30 | 0.2 | 0.9 | 270 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160224.3889 | 9.3881 | 0 |  |  | 1 | 16 | 1 | 13
Lerwick | 1978-03-21 09:30 | 1.2 | 2 | 235 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 159513.2778 | 9.3465 | 0 |  |  | 1 | 17 | 1 | 14
Lerwick | 1978-03-21 10:30 | 2.4 | 3.6 | 245 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 158802.1667 | 9.3048 | 0 |  |  | 1 | 18 | 1 | 15
Lerwick | 1978-03-21 11:30 | 3.9 | 5.1 | 257.5 | 340 | 170 | 0 | 150 | 0 | 0 | 333.3333 | 158468.8333 | 9.2853 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-21 12:30 | 5.3 | 6.3 | 260 | 760 | 550 | 230 | 0 | 230 | 115 | 0 | 158583.8333 | 9.292 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-21 13:30 | 5.5 | 7.2 | 257.5 | 1480 | 1120 | 800 | 0 | 800 | 400 | 0 | 158983.8333 | 9.3155 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-21 14:30 | 5.7 | 7.3 | 257.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 159563.8333 | 9.3494 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-21 15:30 | 5.9 | 6.8 | 267.5 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 160053.8333 | 9.3782 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-21 16:30 | 5.5 | 5.4 | 272.5 | 340 | 730 | 410 | 0 | 410 | 205 | 0 | 160258.8333 | 9.3902 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-03-21 17:30 | 5.2 | 4.2 | 262.5 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 160010.6852 | 9.3756 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-03-21 18:30 | 4 | 4.1 | 250 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 159469.9444 | 9.3439 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-03-21 19:30 | 2.5 | 5.1 | 245 | 340 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 159221.7963 | 9.3294 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-21 20:30 | 2.3 | 5.9 | 242.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 159271.7963 | 9.3323 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-21 21:30 | 2.4 | 5.8 | 237.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 159361.7963 | 9.3376 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-21 22:30 | 2.5 | 5.8 | 242.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 159451.7963 | 9.3429 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-21 23:30 | 2.8 | 5.6 | 250 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 159541.7963 | 9.3482 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-22 00:30 | 2.7 | 5.5 | 245 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 159631.7963 | 9.3534 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-22 01:30 | 2.6 | 5.7 | 237.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 159721.7963 | 9.3587 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-22 02:30 | 2.6 | 5.8 | 232.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 159811.7963 | 9.364 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-22 03:30 | 2.6 | 5.9 | 225 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 159901.7963 | 9.3692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-22 04:30 | 2.5 | 5.9 | 215 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 159991.7963 | 9.3745 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-22 05:30 | 2.7 | 6.3 | 207.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 160146.7963 | 9.3836 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-22 06:30 | 3.3 | 7.4 | 200 | 1480 | 1120 | 800 | 0 | 800 | 400 | 0 | 160546.7963 | 9.407 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-22 07:30 | 3.9 | 8.9 | 190 | 2560 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 161191.7963 | 9.4448 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-22 08:30 | 4.3 | 10 | 182.5 | 3640 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 161836.7963 | 9.4826 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-22 09:30 | 4.6 | 10.6 | 177.5 | 4000 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 162481.7963 | 9.5204 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-22 10:30 | 5 | 11.7 | 175 | 4472.2222 | 4236.1111 | 3916.1111 | 0 | 1290 | 645 | 0 | 163126.7963 | 9.5582 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-22 11:30 | 5.5 | 12.7 | 177.5 | 4600 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 163771.7963 | 9.596 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-22 12:30 | 5.3 | 13.5 | 180 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 164416.7963 | 9.6338 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-22 13:30 | 4.8 | 14 | 180 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 165061.7963 | 9.6716 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-22 14:30 | 4.3 | 13.8 | 180 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 165706.7963 | 9.7094 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-22 15:30 | 3.8 | 12.1 | 185 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 645 | 0 | 166351.7963 | 9.7472 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-22 16:30 | 3.6 | 9.9 | 202.5 | 3280 | 3908.0556 | 3588.0556 | 0 | 1290 | 645 | 0 | 166996.7963 | 9.785 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-22 17:30 | 4.1 | 8.5 | 225 | 2560 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 167641.7963 | 9.8228 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-22 18:30 | 4 | 7.3 | 240 | 1480 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 168286.7963 | 9.8606 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-22 19:30 | 3.7 | 6 | 257.5 | 760 | 1120 | 800 | 0 | 800 | 400 | 0 | 168686.7963 | 9.884 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-22 20:30 | 3.5 | 4 | 262.5 | 76.6667 | 418.3333 | 98.3333 | 0 | 98.3333 | 49.1667 | 0 | 168735.963 | 9.8869 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-03-22 21:30 | 3.3 | 2 | 240 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 168110.037 | 9.8502 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-03-22 22:30 | 2.8 | 1.1 | 227.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167398.9259 | 9.8085 | 0 |  |  | 1 | 3 | 1 | 1
Lerwick | 1978-03-22 23:30 | 1.8 | 1 | 235 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166687.8148 | 9.7669 | 0 |  |  | 1 | 4 | 1 | 2
Lerwick | 1978-03-23 00:30 | 1.1 | 1 | 255 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165976.7037 | 9.7252 | 0 |  |  | 1 | 5 | 1 | 3
Lerwick | 1978-03-23 01:30 | 0.6 | 1.5 | 282.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165265.5926 | 9.6835 | 0 |  |  | 1 | 6 | 1 | 4
Lerwick | 1978-03-23 02:30 | 0.8 | 2.7 | 300 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164554.4815 | 9.6419 | 0 |  |  | 1 | 7 | 1 | 5
Lerwick | 1978-03-23 03:30 | 2.2 | 3.4 | 310 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163843.3704 | 9.6002 | 0 |  |  | 1 | 8 | 1 | 6
Lerwick | 1978-03-23 04:30 | 2.9 | 3.6 | 320 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163132.2593 | 9.5585 | 0 |  |  | 1 | 9 | 1 | 7
Lerwick | 1978-03-23 05:30 | 2.1 | 3.4 | 330 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162421.1481 | 9.5169 | 0 |  |  | 1 | 10 | 1 | 8
Lerwick | 1978-03-23 06:30 | 2.1 | 3.3 | 337.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161710.037 | 9.4752 | 0 |  |  | 1 | 11 | 1 | 9
Lerwick | 1978-03-23 07:30 | 1.7 | 3.6 | 337.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160998.9259 | 9.4335 | 0 |  |  | 1 | 12 | 1 | 10
Lerwick | 1978-03-23 08:30 | 2 | 3.9 | 330 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160287.8148 | 9.3919 | 0 |  |  | 1 | 13 | 1 | 11
Lerwick | 1978-03-23 09:30 | 3.9 | 4 | 322.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 159661.8889 | 9.3552 | 1 |  |  | 1 | 14 | 0 | 0
Lerwick | 1978-03-23 10:30 | 4.8 | 4.2 | 317.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 159121.1481 | 9.3235 | 1 |  |  | 1 | 15 | 0 | 0
Lerwick | 1978-03-23 11:30 | 5.7 | 4.9 | 315 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 158716.7037 | 9.2998 | 1 |  |  | 1 | 16 | 0 | 0
Lerwick | 1978-03-23 12:30 | 6.2 | 5.4 | 317.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 158604.8519 | 9.2933 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-23 13:30 | 6.6 | 5.4 | 325 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 158614.8519 | 9.2938 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-23 14:30 | 6.5 | 5.4 | 335 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 158624.8519 | 9.2944 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-23 15:30 | 6.4 | 5.1 | 340 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 158634.8519 | 9.295 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-03-23 16:30 | 6.3 | 4.4 | 335 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 158386.7037 | 9.2805 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-03-23 17:30 | 5.9 | 3.8 | 327.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 157760.7778 | 9.2438 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-03-23 18:30 | 5.3 | 3.4 | 327.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 157049.6667 | 9.2021 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-03-23 19:30 | 4.4 | 3 | 330 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 156338.5556 | 9.1605 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-03-23 20:30 | 3.3 | 2.7 | 327.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 155627.4444 | 9.1188 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-03-23 21:30 | 3 | 2.9 | 320 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 154916.3333 | 9.0771 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-03-23 22:30 | 3.2 | 3.1 | 312.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 154205.2222 | 9.0355 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-03-23 23:30 | 3.1 | 3.1 | 310 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 153494.1111 | 8.9938 | 0 |  |  | 1 | 9 | 1 | 6
Lerwick | 1978-03-24 00:30 | 3 | 3.1 | 310 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 152783 | 8.9521 | 0 |  |  | 1 | 10 | 1 | 7
Lerwick | 1978-03-24 01:30 | 3.1 | 3.3 | 312.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 152071.8889 | 8.9105 | 0 |  |  | 1 | 11 | 1 | 8
Lerwick | 1978-03-24 02:30 | 3.1 | 3.8 | 315 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 151360.7778 | 8.8688 | 0 |  |  | 1 | 12 | 1 | 9
Lerwick | 1978-03-24 03:30 | 3 | 4 | 315 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 150734.8519 | 8.8321 | 1 |  |  | 1 | 13 | 0 | 0
Lerwick | 1978-03-24 04:30 | 3.2 | 4 | 315 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 150194.1111 | 8.8004 | 1 |  |  | 1 | 14 | 0 | 0
Lerwick | 1978-03-24 05:30 | 3.2 | 4.2 | 312.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 149653.3704 | 8.7688 | 1 |  |  | 1 | 15 | 0 | 0
Lerwick | 1978-03-24 06:30 | 2.8 | 4.7 | 307.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 149248.9259 | 8.7451 | 1 |  |  | 1 | 16 | 0 | 0
Lerwick | 1978-03-24 07:30 | 2.9 | 5.3 | 302.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 149137.0741 | 8.7385 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-24 08:30 | 3.9 | 5.9 | 297.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 149187.0741 | 8.7414 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-24 09:30 | 5.1 | 6.6 | 290 | 1120 | 810 | 490 | 0 | 490 | 245 | 0 | 149432.0741 | 8.7558 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-24 10:30 | 6.1 | 7 | 280 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 149922.0741 | 8.7845 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-24 11:30 | 6.6 | 6.8 | 270 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 150412.0741 | 8.8132 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-24 12:30 | 6.8 | 6.8 | 262.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 150812.0741 | 8.8366 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-24 13:30 | 7 | 7 | 260 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 151302.0741 | 8.8654 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-24 14:30 | 6.9 | 7.1 | 257.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 151882.0741 | 8.8993 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-24 15:30 | 7.1 | 7.2 | 250 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 152462.0741 | 8.9333 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-24 16:30 | 7 | 6.5 | 240 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 152952.0741 | 8.962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-24 17:30 | 6.3 | 5.4 | 230 | 340 | 730 | 410 | 0 | 410 | 205 | 0 | 153157.0741 | 8.974 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-03-24 18:30 | 5.4 | 4.4 | 217.5 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 152908.9259 | 8.9595 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-03-24 19:30 | 4.4 | 4.5 | 200 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 152504.4815 | 8.9358 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-24 20:30 | 3.9 | 6.5 | 182.5 | 1120 | 659.6667 | 339.6667 | 0 | 339.6667 | 169.8333 | 0 | 152674.3148 | 8.9458 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-24 21:30 | 4.4 | 9.3 | 172.5 | 2920 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 153319.3148 | 8.9836 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-24 22:30 | 4.9 | 11.4 | 175 | 4300 | 3610 | 3290 | 0 | 1290 | 645 | 0 | 153964.3148 | 9.0213 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-24 23:30 | 4.9 | 12.1 | 185 | 4536.1111 | 4418.0556 | 4098.0556 | 0 | 1290 | 645 | 0 | 154609.3148 | 9.0591 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-25 00:30 | 4 | 10.4 | 200 | 3640 | 4088.0556 | 3768.0556 | 0 | 1290 | 645 | 0 | 155254.3148 | 9.0969 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-25 01:30 | 3.2 | 8.7 | 225 | 2560 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 155899.3148 | 9.1347 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-25 02:30 | 4.1 | 9 | 245 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 156544.3148 | 9.1725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-25 03:30 | 4.9 | 9.5 | 252.5 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 157189.3148 | 9.2103 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-25 04:30 | 5 | 9.4 | 257.5 | 2920 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 157834.3148 | 9.2481 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-25 05:30 | 5 | 9.3 | 260 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 158479.3148 | 9.2859 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-25 06:30 | 4.7 | 9.1 | 260 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 159124.3148 | 9.3237 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-25 07:30 | 4.6 | 9.6 | 260 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 159769.3148 | 9.3615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-25 08:30 | 4.8 | 11 | 260 | 4300 | 3790 | 3470 | 0 | 1290 | 645 | 0 | 160414.3148 | 9.3993 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-25 09:30 | 5.1 | 11.9 | 265 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 161059.3148 | 9.4371 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-25 10:30 | 5.7 | 11.7 | 270 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 645 | 0 | 161704.3148 | 9.4749 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-25 11:30 | 5.7 | 11.1 | 262.5 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 162349.3148 | 9.5127 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-25 12:30 | 5.3 | 10.5 | 257.5 | 4000 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 162994.3148 | 9.5504 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-25 13:30 | 5.7 | 10.1 | 262.5 | 3640 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 163639.3148 | 9.5882 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-25 14:30 | 6.3 | 10 | 265 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 164284.3148 | 9.626 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-25 15:30 | 6.7 | 9.6 | 265 | 3280 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 164929.3148 | 9.6638 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-25 16:30 | 6.3 | 9 | 260 | 2920 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 165574.3148 | 9.7016 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-25 17:30 | 5.9 | 8.2 | 252.5 | 2200 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 166219.3148 | 9.7394 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-25 18:30 | 5.1 | 7 | 252.5 | 1480 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 166864.3148 | 9.7772 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-25 19:30 | 3.9 | 5.9 | 255 | 500 | 990 | 670 | 0 | 670 | 335 | 0 | 167199.3148 | 9.7968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-25 20:30 | 3.2 | 4.9 | 255 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 167214.1481 | 9.7977 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-03-25 21:30 | 2.9 | 4.5 | 257.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 166946 | 9.782 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-03-25 22:30 | 2.6 | 4.4 | 257.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 166541.5556 | 9.7583 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-03-25 23:30 | 2.1 | 4.2 | 252.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 166000.8148 | 9.7266 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-03-26 00:30 | 1.9 | 4 | 250 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 165460.0741 | 9.6949 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-03-26 01:30 | 1.9 | 4 | 250 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 164919.3333 | 9.6632 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-03-26 02:30 | 1.8 | 4.2 | 250 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 164378.5926 | 9.6316 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-03-26 03:30 | 1.7 | 4.7 | 252.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 163974.1481 | 9.6079 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-03-26 04:30 | 1.8 | 5 | 257.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 163862.2963 | 9.6013 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-03-26 05:30 | 1.8 | 4.7 | 260 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 163750.4444 | 9.5948 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-03-26 06:30 | 1.8 | 4.2 | 252.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 163346 | 9.5711 | 1 |  |  | 1 | 11 | 0 | 0
Lerwick | 1978-03-26 07:30 | 2.2 | 3.9 | 230 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 162720.0741 | 9.5344 | 1 |  |  | 1 | 12 | 0 | 0
Lerwick | 1978-03-26 08:30 | 3.3 | 3.7 | 212.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162008.963 | 9.4927 | 0 |  |  | 1 | 13 | 1 | 1
Lerwick | 1978-03-26 09:30 | 4.3 | 3.6 | 215 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161297.8519 | 9.451 | 0 |  |  | 1 | 14 | 1 | 2
Lerwick | 1978-03-26 10:30 | 4.9 | 4 | 217.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 160671.9259 | 9.4144 | 1 |  |  | 1 | 15 | 0 | 0
Lerwick | 1978-03-26 11:30 | 5.7 | 4.7 | 210 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 160267.4815 | 9.3907 | 1 |  |  | 1 | 16 | 0 | 0
Lerwick | 1978-03-26 12:30 | 5.7 | 5.2 | 200 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 160155.6296 | 9.3841 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-26 13:30 | 5.3 | 5.5 | 192.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 160205.6296 | 9.387 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-26 14:30 | 6 | 5.3 | 187.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 160255.6296 | 9.39 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-03-26 15:30 | 6.2 | 4.7 | 180 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 160143.7778 | 9.3834 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-03-26 16:30 | 5.3 | 4.5 | 172.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 159875.6296 | 9.3677 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-03-26 17:30 | 5.3 | 4.2 | 170 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 159471.1852 | 9.344 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-03-26 18:30 | 4.7 | 3.8 | 167.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 158845.2593 | 9.3073 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-03-26 19:30 | 3.3 | 3.7 | 162.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 158134.1481 | 9.2657 | 0 |  |  | 1 | 6 | 1 | 1
Lerwick | 1978-03-26 20:30 | 3 | 4.1 | 160 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 157508.2222 | 9.229 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-03-26 21:30 | 3.2 | 4.6 | 160 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 157103.7778 | 9.2053 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-03-26 22:30 | 3.3 | 4.9 | 160 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 156835.6296 | 9.1896 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-03-26 23:30 | 3.6 | 4.9 | 160 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 156567.4815 | 9.1739 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-03-27 00:30 | 3.7 | 5.1 | 160 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 156455.6296 | 9.1673 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-27 01:30 | 3.6 | 5.6 | 160 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 156505.6296 | 9.1703 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-27 02:30 | 3.6 | 6.3 | 160 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 156660.6296 | 9.1793 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-27 03:30 | 3.9 | 7.1 | 160 | 1480 | 1120 | 800 | 0 | 800 | 400 | 0 | 157060.6296 | 9.2028 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-27 04:30 | 4.1 | 8 | 160 | 2200 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 157705.6296 | 9.2406 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-27 05:30 | 4.2 | 9.2 | 160 | 2920 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 158350.6296 | 9.2784 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-27 06:30 | 4.1 | 10.4 | 160 | 3640 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 158995.6296 | 9.3162 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-27 07:30 | 4.2 | 10.8 | 162.5 | 4000 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 159640.6296 | 9.3539 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-27 08:30 | 4.7 | 10.6 | 167.5 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 160285.6296 | 9.3917 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-27 09:30 | 4.9 | 10.6 | 172.5 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 160930.6296 | 9.4295 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-27 10:30 | 4.4 | 10.8 | 177.5 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 161575.6296 | 9.4673 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-27 11:30 | 3.5 | 10 | 180 | 3640 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 162220.6296 | 9.5051 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-27 12:30 | 2.7 | 8.4 | 187.5 | 2200 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 162865.6296 | 9.5429 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-27 13:30 | 2.9 | 7.7 | 212.5 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 163510.6296 | 9.5807 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-27 14:30 | 4.4 | 8.6 | 240 | 2560 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 164155.6296 | 9.6185 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-27 15:30 | 6.4 | 9.3 | 250 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 164800.6296 | 9.6563 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-27 16:30 | 7.1 | 9 | 250 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 165445.6296 | 9.6941 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-27 17:30 | 6.4 | 8.4 | 247.5 | 2200 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 166090.6296 | 9.7319 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-27 18:30 | 5.8 | 8 | 240 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 166735.6296 | 9.7697 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-27 19:30 | 5.6 | 8.2 | 232.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 167380.6296 | 9.8075 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-27 20:30 | 5.5 | 9 | 230 | 2920 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 168025.6296 | 9.8453 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-27 21:30 | 5.5 | 9.5 | 230 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 168670.6296 | 9.883 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-27 22:30 | 5.5 | 9.4 | 232.5 | 2920 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 169315.6296 | 9.9208 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-27 23:30 | 5.5 | 9.5 | 235 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 169960.6296 | 9.9586 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-28 00:30 | 5.4 | 9.4 | 232.5 | 2920 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-28 01:30 | 4.9 | 9 | 230 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-28 02:30 | 4.5 | 8.9 | 227.5 | 2560 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-28 03:30 | 4.2 | 8 | 220 | 2200 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-28 04:30 | 4.1 | 7.2 | 215 | 1480 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-28 05:30 | 4.2 | 7.1 | 217.5 | 1480 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-28 06:30 | 4.1 | 6.7 | 217.5 | 1120 | 1300 | 980 | 0 | 980 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-28 07:30 | 4.2 | 6.8 | 210 | 1120 | 1120 | 800 | 0 | 800 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-28 08:30 | 4.9 | 7.6 | 200 | 1840 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-28 09:30 | 5.7 | 8.2 | 192.5 | 2200 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-28 10:30 | 6.4 | 8.9 | 190 | 2560 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-28 11:30 | 6.9 | 9.5 | 190 | 3280 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-28 12:30 | 6.9 | 9.6 | 187.5 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-28 13:30 | 6.9 | 9.5 | 180 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-28 14:30 | 7.2 | 9.6 | 170 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-28 15:30 | 6.9 | 9.8 | 162.5 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-28 16:30 | 6.3 | 9.9 | 160 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-28 17:30 | 6.1 | 10.7 | 157.5 | 4000 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-28 18:30 | 5.7 | 12.5 | 157.5 | 4600 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-28 19:30 | 5.7 | 14.6 | 170 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-28 20:30 | 6.3 | 17.7 | 195 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-28 21:30 | 5.9 | 20.2 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-28 22:30 | 4.3 | 18.8 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-28 23:30 | 4 | 15.7 | 227.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-29 00:30 | 4.5 | 12.8 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-29 01:30 | 4.7 | 10.1 | 212.5 | 3640 | 4120 | 3800 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-29 02:30 | 5 | 8.9 | 210 | 2560 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-29 03:30 | 5.1 | 8.4 | 210 | 2200 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-29 04:30 | 5.1 | 8 | 210 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-29 05:30 | 4.7 | 8.4 | 207.5 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-29 06:30 | 4.6 | 9 | 202.5 | 2920 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-29 07:30 | 5 | 9.6 | 200 | 3280 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-29 08:30 | 5.4 | 10 | 200 | 3640 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-29 09:30 | 5.8 | 10.4 | 200 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-29 10:30 | 6.5 | 11.1 | 200 | 4300 | 3970 | 3650 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-29 11:30 | 6.9 | 11.2 | 202.5 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-29 12:30 | 6.8 | 10.7 | 207.5 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-29 13:30 | 6.7 | 10.2 | 210 | 3640 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-29 14:30 | 6.9 | 9.4 | 212.5 | 2920 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-29 15:30 | 7.4 | 8.6 | 217.5 | 2560 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-29 16:30 | 7 | 9.1 | 220 | 2920 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-29 17:30 | 5.8 | 10.1 | 222.5 | 3640 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-29 18:30 | 5.4 | 10.7 | 225 | 4000 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-29 19:30 | 5.5 | 11.5 | 222.5 | 4472.2222 | 4236.1111 | 3916.1111 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-29 20:30 | 5.4 | 12.8 | 220 | 4600 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-29 21:30 | 5.5 | 13.6 | 222.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-29 22:30 | 5.6 | 12.5 | 227.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-29 23:30 | 5.3 | 11 | 227.5 | 4300 | 4450 | 4130 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-30 00:30 | 5.2 | 10.9 | 222.5 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-30 01:30 | 5.2 | 11.6 | 220 | 4472.2222 | 4236.1111 | 3916.1111 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-30 02:30 | 5.3 | 12 | 220 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-30 03:30 | 5.5 | 11.7 | 220 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-30 04:30 | 5.5 | 11.5 | 220 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-30 05:30 | 5.5 | 11.4 | 220 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-30 06:30 | 5.4 | 11.3 | 220 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-30 07:30 | 5.4 | 11.5 | 220 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-30 08:30 | 5.7 | 11.8 | 220 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-30 09:30 | 6.2 | 11.5 | 220 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-30 10:30 | 6.2 | 11.1 | 220 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-30 11:30 | 6.3 | 11.1 | 220 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-30 12:30 | 6.8 | 11.1 | 220 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-30 13:30 | 7.4 | 10.7 | 220 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-30 14:30 | 7.8 | 10 | 222.5 | 3640 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-30 15:30 | 7.1 | 8.8 | 227.5 | 2560 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-30 16:30 | 6.4 | 7.2 | 225 | 1480 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-30 17:30 | 6.4 | 5.6 | 212.5 | 500 | 990 | 670 | 0 | 670 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-30 18:30 | 6 | 4.9 | 205 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 0 | 0 | 170605.6296 | 9.9964 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-03-30 19:30 | 5.6 | 4.6 | 207.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 170337.4815 | 9.9807 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-03-30 20:30 | 5.1 | 4.4 | 212.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 169933.037 | 9.957 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-03-30 21:30 | 4.8 | 4.4 | 220 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 169392.2963 | 9.9253 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-03-30 22:30 | 4.7 | 4 | 235 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 168851.5556 | 9.8936 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-03-30 23:30 | 4.6 | 3.3 | 252.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 168225.6296 | 9.857 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-03-31 00:30 | 4.4 | 2.8 | 257.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167514.5185 | 9.8153 | 0 |  |  | 1 | 7 | 1 | 1
Lerwick | 1978-03-31 01:30 | 4.4 | 2.6 | 250 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166803.4074 | 9.7736 | 0 |  |  | 1 | 8 | 1 | 2
Lerwick | 1978-03-31 02:30 | 4 | 3.1 | 242.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166092.2963 | 9.732 | 0 |  |  | 1 | 9 | 1 | 3
Lerwick | 1978-03-31 03:30 | 4 | 3.8 | 240 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165381.1852 | 9.6903 | 0 |  |  | 1 | 10 | 1 | 4
Lerwick | 1978-03-31 04:30 | 4.2 | 4.2 | 237.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 164755.2593 | 9.6536 | 1 |  |  | 1 | 11 | 0 | 0
Lerwick | 1978-03-31 05:30 | 4 | 4.5 | 237.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 164350.8148 | 9.6299 | 1 |  |  | 1 | 12 | 0 | 0
Lerwick | 1978-03-31 06:30 | 4 | 4.5 | 240 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 164082.6667 | 9.6142 | 1 |  |  | 1 | 13 | 0 | 0
Lerwick | 1978-03-31 07:30 | 4.5 | 5.1 | 232.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 163970.8148 | 9.6077 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-31 08:30 | 5.4 | 6 | 222.5 | 760 | 550 | 230 | 0 | 230 | 115 | 0 | 164085.8148 | 9.6144 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-31 09:30 | 6.2 | 6.5 | 220 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 164395.8148 | 9.6326 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-31 10:30 | 6.8 | 6.5 | 215 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 164795.8148 | 9.656 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-31 11:30 | 7 | 6.4 | 200 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 165105.8148 | 9.6742 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-31 12:30 | 7.2 | 6.5 | 185 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 165415.8148 | 9.6923 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-31 13:30 | 7.2 | 6.5 | 177.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 165815.8148 | 9.7158 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-31 14:30 | 7.5 | 6.3 | 172.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 166125.8148 | 9.7339 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-31 15:30 | 7.9 | 6 | 170 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 166345.8148 | 9.7468 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-03-31 16:30 | 7.3 | 5.4 | 170 | 340 | 550 | 230 | 0 | 230 | 115 | 0 | 166460.8148 | 9.7536 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-03-31 17:30 | 6.6 | 4.4 | 165 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 166212.6667 | 9.739 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-03-31 18:30 | 6 | 3.5 | 152.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 165586.7407 | 9.7023 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-03-31 19:30 | 5 | 3.1 | 140 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164875.6296 | 9.6607 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-03-31 20:30 | 4.5 | 3.1 | 137.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164164.5185 | 9.619 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-03-31 21:30 | 4.6 | 2.6 | 145 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163453.4074 | 9.5773 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-03-31 22:30 | 5.1 | 2.2 | 147.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162742.2963 | 9.5357 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-03-31 23:30 | 5.5 | 3 | 140 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162031.1852 | 9.494 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-04-01 00:30 | 5.4 | 4.4 | 132.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 161405.2593 | 9.4573 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-04-01 01:30 | 5.2 | 4.9 | 127.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 161000.8148 | 9.4336 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-04-01 02:30 | 5 | 5.2 | 125 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 160888.963 | 9.4271 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-01 03:30 | 5 | 5.5 | 125 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 160938.963 | 9.43 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-01 04:30 | 5 | 5.7 | 122.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 161028.963 | 9.4353 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-01 05:30 | 5 | 5.9 | 117.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 161118.963 | 9.4406 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-01 06:30 | 5.2 | 6.7 | 110 | 1120 | 810 | 490 | 0 | 490 | 245 | 0 | 161363.963 | 9.4549 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-01 07:30 | 5.4 | 7.6 | 102.5 | 1840 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 161943.963 | 9.4889 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-01 08:30 | 5.8 | 8.2 | 97.5 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 162588.963 | 9.5267 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-01 09:30 | 6.3 | 9 | 95 | 2920 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 163233.963 | 9.5645 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-01 10:30 | 6.6 | 10 | 97.5 | 3640 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 163878.963 | 9.6023 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-01 11:30 | 6.9 | 10.6 | 97.5 | 4000 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 164523.963 | 9.6401 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-01 12:30 | 7 | 10.8 | 92.5 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 165168.963 | 9.6779 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-01 13:30 | 7 | 10.8 | 90 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 165813.963 | 9.7157 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-01 14:30 | 7 | 10.8 | 87.5 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 166458.963 | 9.7535 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-01 15:30 | 7.1 | 10.9 | 82.5 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 167103.963 | 9.7912 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-01 16:30 | 6.8 | 11 | 80 | 4300 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 167748.963 | 9.829 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-01 17:30 | 6.4 | 10.7 | 80 | 4000 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 168393.963 | 9.8668 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-01 18:30 | 6.1 | 10.2 | 80 | 3640 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 169038.963 | 9.9046 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-01 19:30 | 6 | 10 | 77.5 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 169683.963 | 9.9424 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-01 20:30 | 6 | 10.1 | 72.5 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 170328.963 | 9.9802 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-01 21:30 | 6 | 9.8 | 72.5 | 3280 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170328.963 | 9.9802 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-01 22:30 | 6 | 8.2 | 80 | 2200 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170328.963 | 9.9802 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-01 23:30 | 5.7 | 6.1 | 92.5 | 760 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170328.963 | 9.9802 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-02 00:30 | 5.3 | 4.3 | 115 | 76.6667 | 418.3333 | 98.3333 | 0 | 98.3333 | 0 | 0 | 170328.963 | 9.9802 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-04-02 01:30 | 5.2 | 3.1 | 135 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 169703.037 | 9.9435 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-04-02 02:30 | 5 | 2.4 | 120 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168991.9259 | 9.9019 | 0 |  |  | 1 | 3 | 1 | 1
Lerwick | 1978-04-02 03:30 | 4.8 | 2.1 | 85 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168280.8148 | 9.8602 | 0 |  |  | 1 | 4 | 1 | 2
Lerwick | 1978-04-02 04:30 | 4.6 | 2.3 | 72.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167569.7037 | 9.8185 | 0 |  |  | 1 | 5 | 1 | 3
Lerwick | 1978-04-02 05:30 | 4.4 | 3.2 | 75 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166858.5926 | 9.7769 | 0 |  |  | 1 | 6 | 1 | 4
Lerwick | 1978-04-02 06:30 | 4.8 | 4.6 | 75 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 166368.963 | 9.7482 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-02 07:30 | 5.3 | 5.9 | 80 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 166383.7963 | 9.7491 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-02 08:30 | 5.6 | 6.3 | 90 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 166538.7963 | 9.7581 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-02 09:30 | 5.7 | 6.2 | 100 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 166758.7963 | 9.771 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-02 10:30 | 5.8 | 6.3 | 107.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 166978.7963 | 9.7839 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-02 11:30 | 6 | 6.7 | 110 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 167288.7963 | 9.8021 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-02 12:30 | 6 | 7.3 | 112.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 167778.7963 | 9.8308 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-02 13:30 | 6 | 7.7 | 117.5 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 168423.7963 | 9.8686 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-02 14:30 | 5.8 | 7.6 | 120 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 169068.7963 | 9.9064 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-02 15:30 | 5.7 | 7.2 | 120 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 169713.7963 | 9.9442 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-02 16:30 | 5.6 | 6.7 | 120 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 170203.7963 | 9.9729 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-02 17:30 | 5.9 | 6.4 | 120 | 760 | 940 | 620 | 0 | 620 | 0 | 0 | 170203.7963 | 9.9729 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-02 18:30 | 5.9 | 6.1 | 120 | 760 | 760 | 440 | 0 | 440 | 0 | 0 | 170203.7963 | 9.9729 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-02 19:30 | 5.3 | 5.4 | 122.5 | 340 | 550 | 230 | 0 | 230 | 0 | 0 | 170203.7963 | 9.9729 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-02 20:30 | 5.2 | 5.3 | 127.5 | 340 | 340 | 20 | 0 | 20 | 0 | 0 | 170203.7963 | 9.9729 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-02 21:30 | 5.3 | 5.8 | 130 | 500 | 420 | 100 | 0 | 100 | 0 | 0 | 170203.7963 | 9.9729 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-02 22:30 | 5.3 | 5.6 | 132.5 | 500 | 500 | 180 | 0 | 180 | 0 | 0 | 170203.7963 | 9.9729 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-02 23:30 | 5.1 | 4.9 | 140 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 0 | 0 | 170203.7963 | 9.9729 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-04-03 00:30 | 5 | 4.4 | 142.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 169799.3519 | 9.9492 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-04-03 01:30 | 5 | 4.1 | 130 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 169258.6111 | 9.9175 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-04-03 02:30 | 5 | 3.6 | 105 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 168632.6852 | 9.8808 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-04-03 03:30 | 4.9 | 3.6 | 80 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167921.5741 | 9.8392 | 0 |  |  | 1 | 5 | 1 | 1
Lerwick | 1978-04-03 04:30 | 4.8 | 4.2 | 75 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 167295.6481 | 9.8025 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-04-03 05:30 | 4.8 | 4.9 | 87.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 166891.2037 | 9.7788 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-03 06:30 | 4.8 | 5.5 | 107.5 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 166906.037 | 9.7797 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-03 07:30 | 4.7 | 5.5 | 130 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 166996.037 | 9.7849 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-03 08:30 | 4.6 | 4.9 | 140 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 167010.8704 | 9.7858 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-04-03 09:30 | 4.8 | 4 | 137.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 166606.4259 | 9.7621 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-04-03 10:30 | 5 | 3.3 | 130 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 165980.5 | 9.7254 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-04-03 11:30 | 5.3 | 3.2 | 110 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165269.3889 | 9.6838 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-04-03 12:30 | 5.7 | 3.6 | 77.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164558.2778 | 9.6421 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-04-03 13:30 | 6 | 4.2 | 57.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 163932.3519 | 9.6054 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-04-03 14:30 | 6.1 | 4.5 | 57.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 163527.9074 | 9.5817 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-04-03 15:30 | 6 | 4.5 | 60 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 163259.7593 | 9.566 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-04-03 16:30 | 5.8 | 4.4 | 57.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 162855.3148 | 9.5423 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-04-03 17:30 | 5.7 | 4.2 | 52.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 162314.5741 | 9.5106 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-04-03 18:30 | 5.6 | 4.2 | 50 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 161773.8333 | 9.4789 | 1 |  |  | 1 | 11 | 0 | 0
Lerwick | 1978-04-03 19:30 | 5.5 | 4.4 | 52.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 161233.0926 | 9.4473 | 1 |  |  | 1 | 12 | 0 | 0
Lerwick | 1978-04-03 20:30 | 5.6 | 4.2 | 55 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 160692.3519 | 9.4156 | 1 |  |  | 1 | 13 | 0 | 0
Lerwick | 1978-04-03 21:30 | 5.8 | 3.6 | 52.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 160066.4259 | 9.3789 | 1 |  |  | 1 | 14 | 0 | 0
Lerwick | 1978-04-03 22:30 | 5.9 | 3.2 | 47.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 159355.3148 | 9.3372 | 0 |  |  | 1 | 15 | 1 | 1
Lerwick | 1978-04-03 23:30 | 5.9 | 3.1 | 42.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 158644.2037 | 9.2956 | 0 |  |  | 1 | 16 | 1 | 2
Lerwick | 1978-04-04 00:30 | 5.8 | 2.9 | 42.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 157933.0926 | 9.2539 | 0 |  |  | 1 | 17 | 1 | 3
Lerwick | 1978-04-04 01:30 | 5.7 | 2.4 | 45 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 157221.9815 | 9.2122 | 0 |  |  | 1 | 18 | 1 | 4
Lerwick | 1978-04-04 02:30 | 5.7 | 1.7 | 40 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 156510.8704 | 9.1706 | 0 |  |  | 1 | 19 | 1 | 5
Lerwick | 1978-04-04 03:30 | 5.6 | 1.7 | 32.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 155799.7593 | 9.1289 | 0 |  |  | 1 | 20 | 1 | 6
Lerwick | 1978-04-04 04:30 | 5.5 | 2.4 | 30 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 155088.6481 | 9.0872 | 0 |  |  | 1 | 21 | 1 | 7
Lerwick | 1978-04-04 05:30 | 5.5 | 2.7 | 30 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 154377.537 | 9.0456 | 0 |  |  | 1 | 22 | 1 | 8
Lerwick | 1978-04-04 06:30 | 5.2 | 2.7 | 30 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 153666.4259 | 9.0039 | 0 |  |  | 1 | 23 | 1 | 9
Lerwick | 1978-04-04 07:30 | 5.3 | 2.9 | 30 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 152955.3148 | 8.9622 | 0 |  |  | 1 | 24 | 1 | 10
Lerwick | 1978-04-04 08:30 | 5.8 | 3.5 | 30 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 152244.2037 | 8.9206 | 0 |  |  | 1 | 25 | 1 | 11
Lerwick | 1978-04-04 09:30 | 6.1 | 4.1 | 35 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 151618.2778 | 8.8839 | 1 |  |  | 1 | 26 | 0 | 0
Lerwick | 1978-04-04 10:30 | 6.4 | 4.2 | 42.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 151077.537 | 8.8522 | 1 |  |  | 1 | 27 | 0 | 0
Lerwick | 1978-04-04 11:30 | 6.8 | 3.9 | 42.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 150451.6111 | 8.8155 | 1 |  |  | 1 | 28 | 0 | 0
Lerwick | 1978-04-04 12:30 | 6.9 | 3.9 | 47.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 149740.5 | 8.7739 | 0 |  |  | 1 | 29 | 1 | 1
Lerwick | 1978-04-04 13:30 | 7 | 3.6 | 67.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 149029.3889 | 8.7322 | 0 |  |  | 1 | 30 | 1 | 2
Lerwick | 1978-04-04 14:30 | 7.5 | 3.2 | 72.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 148318.2778 | 8.6905 | 0 |  |  | 1 | 31 | 1 | 3
Lerwick | 1978-04-04 15:30 | 7.5 | 3.2 | 50 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 147607.1667 | 8.6489 | 0 |  |  | 1 | 32 | 1 | 4
Lerwick | 1978-04-04 16:30 | 7 | 3 | 30 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 146896.0556 | 8.6072 | 0 |  |  | 1 | 33 | 1 | 5
Lerwick | 1978-04-04 17:30 | 6.5 | 2.1 | 25 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 146184.9444 | 8.5655 | 0 |  |  | 1 | 34 | 1 | 6
Lerwick | 1978-04-04 18:30 | 6.1 | 1.2 | 190 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 145473.8333 | 8.5239 | 0 |  |  | 1 | 35 | 1 | 7
Lerwick | 1978-04-04 19:30 | 5.5 | 1.6 | 342.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 144762.7222 | 8.4822 | 0 |  |  | 1 | 36 | 1 | 8
Lerwick | 1978-04-04 20:30 | 4.6 | 2.7 | 335 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 144051.6111 | 8.4405 | 0 |  |  | 1 | 37 | 1 | 9
Lerwick | 1978-04-04 21:30 | 3.7 | 3.2 | 342.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 143340.5 | 8.3989 | 0 |  |  | 1 | 38 | 1 | 10
Lerwick | 1978-04-04 22:30 | 3.2 | 3.1 | 345 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 142629.3889 | 8.3572 | 0 |  |  | 1 | 39 | 1 | 11
Lerwick | 1978-04-04 23:30 | 2.8 | 3.1 | 340 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 141918.2778 | 8.3155 | 0 |  |  | 1 | 40 | 1 | 12
Lerwick | 1978-04-05 00:30 | 2.5 | 3.1 | 332.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 141207.1667 | 8.2739 | 0 |  |  | 1 | 41 | 1 | 13
Lerwick | 1978-04-05 01:30 | 2.1 | 3.1 | 332.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 140496.0556 | 8.2322 | 0 |  |  | 1 | 42 | 1 | 14
Lerwick | 1978-04-05 02:30 | 2.1 | 3.1 | 337.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 139784.9444 | 8.1905 | 0 |  |  | 1 | 43 | 1 | 15
Lerwick | 1978-04-05 03:30 | 3.1 | 3.1 | 340 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 139073.8333 | 8.1489 | 0 |  |  | 1 | 44 | 1 | 16
Lerwick | 1978-04-05 04:30 | 3.8 | 3.2 | 342.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 138362.7222 | 8.1072 | 0 |  |  | 1 | 45 | 1 | 17
Lerwick | 1978-04-05 05:30 | 4.1 | 3.4 | 347.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 137651.6111 | 8.0655 | 0 |  |  | 1 | 46 | 1 | 18
Lerwick | 1978-04-05 06:30 | 4.5 | 3.6 | 350 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 136940.5 | 8.0239 | 0 |  |  | 1 | 47 | 1 | 19
Lerwick | 1978-04-05 07:30 | 4.8 | 3.4 | 352.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 136229.3889 | 7.9822 | 0 |  |  | 1 | 48 | 1 | 20
Lerwick | 1978-04-05 08:30 | 5.3 | 3 | 185 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 135518.2778 | 7.9405 | 0 |  |  | 1 | 49 | 1 | 21
Lerwick | 1978-04-05 09:30 | 5.9 | 2.4 | 25 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 134807.1667 | 7.8989 | 0 |  |  | 1 | 50 | 1 | 22
Lerwick | 1978-04-05 10:30 | 6.4 | 1.7 | 42.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 134096.0556 | 7.8572 | 0 |  |  | 1 | 51 | 1 | 23
Lerwick | 1978-04-05 11:30 | 6.8 | 1.3 | 47.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 133384.9444 | 7.8155 | 0 |  |  | 1 | 52 | 1 | 24
Lerwick | 1978-04-05 12:30 | 7 | 1.5 | 187.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 132673.8333 | 7.7739 | 0 |  |  | 1 | 53 | 1 | 25
Lerwick | 1978-04-05 13:30 | 7.2 | 2.2 | 295 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 131962.7222 | 7.7322 | 0 |  |  | 1 | 54 | 1 | 26
Lerwick | 1978-04-05 14:30 | 7.2 | 3.3 | 255 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 131251.6111 | 7.6905 | 0 |  |  | 1 | 55 | 1 | 27
Lerwick | 1978-04-05 15:30 | 7 | 3.7 | 252.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 130540.5 | 7.6489 | 0 |  |  | 1 | 56 | 1 | 28
Lerwick | 1978-04-05 16:30 | 6.8 | 3.3 | 267.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 129829.3889 | 7.6072 | 0 |  |  | 1 | 57 | 1 | 29
Lerwick | 1978-04-05 17:30 | 6.8 | 2.9 | 290 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 129118.2778 | 7.5655 | 0 |  |  | 1 | 58 | 1 | 30
Lerwick | 1978-04-05 18:30 | 7.1 | 2.6 | 300 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 128407.1667 | 7.5239 | 0 |  |  | 1 | 59 | 1 | 31
Lerwick | 1978-04-05 19:30 | 7.1 | 2.4 | 292.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 127696.0556 | 7.4822 | 0 |  |  | 1 | 60 | 1 | 32
Lerwick | 1978-04-05 20:30 | 6.8 | 2.2 | 277.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 126984.9444 | 7.4405 | 0 |  |  | 1 | 61 | 1 | 33
Lerwick | 1978-04-05 21:30 | 6.4 | 2.4 | 265 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 126273.8333 | 7.3989 | 0 |  |  | 1 | 62 | 1 | 34
Lerwick | 1978-04-05 22:30 | 6.1 | 2.9 | 257.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 125562.7222 | 7.3572 | 0 |  |  | 1 | 63 | 1 | 35
Lerwick | 1978-04-05 23:30 | 5.9 | 3.1 | 257.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 124851.6111 | 7.3155 | 0 |  |  | 1 | 64 | 1 | 36
Lerwick | 1978-04-06 00:30 | 5.9 | 3.1 | 262.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 124140.5 | 7.2739 | 0 |  |  | 1 | 65 | 1 | 37
Lerwick | 1978-04-06 01:30 | 5.9 | 3.1 | 270 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 123429.3889 | 7.2322 | 0 |  |  | 1 | 66 | 1 | 38
Lerwick | 1978-04-06 02:30 | 5.9 | 3.2 | 277.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 122718.2778 | 7.1905 | 0 |  |  | 1 | 67 | 1 | 39
Lerwick | 1978-04-06 03:30 | 5.9 | 3.4 | 277.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 122007.1667 | 7.1489 | 0 |  |  | 1 | 68 | 1 | 40
Lerwick | 1978-04-06 04:30 | 5.9 | 3.7 | 272.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 121296.0556 | 7.1072 | 0 |  |  | 1 | 69 | 1 | 41
Lerwick | 1978-04-06 05:30 | 6 | 3.9 | 270 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 120584.9444 | 7.0655 | 0 |  |  | 1 | 70 | 1 | 42
Lerwick | 1978-04-06 06:30 | 6 | 4.2 | 270 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 119959.0185 | 7.0288 | 1 |  |  | 1 | 71 | 0 | 0
Lerwick | 1978-04-06 07:30 | 6 | 4.7 | 270 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 119554.5741 | 7.0052 | 1 |  |  | 1 | 72 | 0 | 0
Lerwick | 1978-04-06 08:30 | 6 | 4.7 | 272.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 119286.4259 | 6.9894 | 1 |  |  | 1 | 73 | 0 | 0
Lerwick | 1978-04-06 09:30 | 6 | 4.5 | 275 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 119018.2778 | 6.9737 | 1 |  |  | 1 | 74 | 0 | 0
Lerwick | 1978-04-06 10:30 | 6 | 4.7 | 270 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 118750.1296 | 6.958 | 1 |  |  | 1 | 75 | 0 | 0
Lerwick | 1978-04-06 11:30 | 6.2 | 4.9 | 262.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 118481.9815 | 6.9423 | 1 |  |  | 1 | 76 | 0 | 0
Lerwick | 1978-04-06 12:30 | 6.6 | 4.9 | 260 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 118213.8333 | 6.9266 | 1 |  |  | 1 | 77 | 0 | 0
Lerwick | 1978-04-06 13:30 | 7 | 5.3 | 257.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 118101.9815 | 6.92 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-06 14:30 | 7.3 | 5.8 | 252.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 118151.9815 | 6.923 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-06 15:30 | 7.6 | 5.9 | 247.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 118241.9815 | 6.9282 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-06 16:30 | 7.4 | 5.6 | 242.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 118331.9815 | 6.9335 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-06 17:30 | 6.8 | 4.9 | 240 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 118346.8148 | 6.9344 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-04-06 18:30 | 6.1 | 3.7 | 237.5 | 0 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 117857.1852 | 6.9057 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-04-06 19:30 | 4.7 | 2.9 | 235 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 117146.0741 | 6.864 | 0 |  |  | 1 | 3 | 1 | 1
Lerwick | 1978-04-06 20:30 | 4.2 | 3 | 235 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 116434.963 | 6.8224 | 0 |  |  | 1 | 4 | 1 | 2
Lerwick | 1978-04-06 21:30 | 4.7 | 3.3 | 240 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 115723.8519 | 6.7807 | 0 |  |  | 1 | 5 | 1 | 3
Lerwick | 1978-04-06 22:30 | 5.1 | 3.4 | 255 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 115012.7407 | 6.739 | 0 |  |  | 1 | 6 | 1 | 4
Lerwick | 1978-04-06 23:30 | 5.3 | 4 | 270 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 114386.8148 | 6.7024 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-04-07 00:30 | 5.6 | 4.2 | 277.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 113846.0741 | 6.6707 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-04-07 01:30 | 5.6 | 3.9 | 280 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 113220.1481 | 6.634 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-04-07 02:30 | 5.6 | 3.9 | 280 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 112509.037 | 6.5923 | 0 |  |  | 1 | 10 | 1 | 1
Lerwick | 1978-04-07 03:30 | 5.7 | 3.6 | 277.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 111797.9259 | 6.5507 | 0 |  |  | 1 | 11 | 1 | 2
Lerwick | 1978-04-07 04:30 | 5.8 | 3 | 270 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 111086.8148 | 6.509 | 0 |  |  | 1 | 12 | 1 | 3
Lerwick | 1978-04-07 05:30 | 6 | 2.9 | 260 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 110375.7037 | 6.4673 | 0 |  |  | 1 | 13 | 1 | 4
Lerwick | 1978-04-07 06:30 | 6.1 | 3.5 | 252.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 109664.5926 | 6.4257 | 0 |  |  | 1 | 14 | 1 | 5
Lerwick | 1978-04-07 07:30 | 6.1 | 4.4 | 250 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 109038.6667 | 6.389 | 1 |  |  | 1 | 15 | 0 | 0
Lerwick | 1978-04-07 08:30 | 6.1 | 5.1 | 250 | 340 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 108790.5185 | 6.3744 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-07 09:30 | 6.3 | 5.2 | 260 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 108800.5185 | 6.375 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-04-07 10:30 | 6.5 | 4.7 | 275 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 108688.6667 | 6.3685 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-04-07 11:30 | 7.3 | 4.4 | 272.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 108284.2222 | 6.3448 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-04-07 12:30 | 7.8 | 4.9 | 262.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 107879.7778 | 6.3211 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-07 13:30 | 7.8 | 5.5 | 260 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 107894.6111 | 6.3219 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-07 14:30 | 7.6 | 5.8 | 260 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 107984.6111 | 6.3272 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-07 15:30 | 7.3 | 6.1 | 260 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 108139.6111 | 6.3363 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-07 16:30 | 7.2 | 6.8 | 260 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 108449.6111 | 6.3545 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-07 17:30 | 6.9 | 7.4 | 260 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 108939.6111 | 6.3832 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-07 18:30 | 6.8 | 7.8 | 260 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 109584.6111 | 6.421 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-07 19:30 | 6.4 | 7.6 | 260 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 110229.6111 | 6.4588 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-07 20:30 | 6 | 6.4 | 257.5 | 760 | 1300 | 980 | 0 | 980 | 490 | 0 | 110719.6111 | 6.4875 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-07 21:30 | 6.2 | 5.8 | 255 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 110874.6111 | 6.4966 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-07 22:30 | 6.5 | 5.8 | 262.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 110964.6111 | 6.5018 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-07 23:30 | 6.6 | 4.8 | 275 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 110979.4444 | 6.5027 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-04-08 00:30 | 6.5 | 3.3 | 272.5 | 0 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 110489.8148 | 6.474 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-04-08 01:30 | 6.4 | 2.6 | 252.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 109778.7037 | 6.4323 | 0 |  |  | 1 | 3 | 1 | 1
Lerwick | 1978-04-08 02:30 | 5.9 | 2.8 | 235 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 109067.5926 | 6.3907 | 0 |  |  | 1 | 4 | 1 | 2
Lerwick | 1978-04-08 03:30 | 5.5 | 3.5 | 227.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 108356.4815 | 6.349 | 0 |  |  | 1 | 5 | 1 | 3
Lerwick | 1978-04-08 04:30 | 5.3 | 4.7 | 225 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 107866.8519 | 6.3203 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-08 05:30 | 5.3 | 5.5 | 227.5 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 107881.6852 | 6.3212 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-08 06:30 | 5.5 | 5.7 | 232.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 107971.6852 | 6.3265 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-08 07:30 | 5.9 | 6 | 237.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 108126.6852 | 6.3355 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-08 08:30 | 6 | 6.8 | 237.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 108436.6852 | 6.3537 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-08 09:30 | 6.3 | 8.1 | 232.5 | 2200 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 109081.6852 | 6.3915 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-08 10:30 | 7.2 | 9.7 | 230 | 3280 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 109726.6852 | 6.4293 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-08 11:30 | 7.6 | 10.5 | 232.5 | 4000 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 110371.6852 | 6.4671 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-08 12:30 | 7.6 | 10.5 | 235 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 111016.6852 | 6.5049 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-08 13:30 | 8.1 | 10.6 | 235 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 111661.6852 | 6.5427 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-08 14:30 | 8.4 | 10.9 | 235 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 112306.6852 | 6.5805 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-08 15:30 | 8.1 | 11 | 232.5 | 4300 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 112951.6852 | 6.6183 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-08 16:30 | 7.6 | 10.9 | 230 | 4000 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 113596.6852 | 6.6561 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-08 17:30 | 6.9 | 10.8 | 230 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 114241.6852 | 6.6938 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-08 18:30 | 6.1 | 10.8 | 230 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 114886.6852 | 6.7316 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-08 19:30 | 5.7 | 10.4 | 230 | 3640 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 115531.6852 | 6.7694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-08 20:30 | 5.5 | 9.6 | 232.5 | 3280 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 116176.6852 | 6.8072 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-08 21:30 | 5.1 | 9 | 240 | 2920 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 116821.6852 | 6.845 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-08 22:30 | 4.6 | 8.2 | 250 | 2200 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 117466.6852 | 6.8828 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-08 23:30 | 3.8 | 6.9 | 255 | 1120 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 118111.6852 | 6.9206 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-09 00:30 | 3.3 | 6 | 257.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 118421.6852 | 6.9388 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-09 01:30 | 3.5 | 6.4 | 265 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 118641.6852 | 6.9517 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-09 02:30 | 3.6 | 6.7 | 277.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 118951.6852 | 6.9698 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-09 03:30 | 3.6 | 6 | 302.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 119261.6852 | 6.988 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-09 04:30 | 3.2 | 5.7 | 330 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 119416.6852 | 6.9971 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-09 05:30 | 2.5 | 5.3 | 342.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 119466.6852 | 7 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-09 06:30 | 2 | 5 | 347.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 119476.6852 | 7.0006 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-09 07:30 | 1.9 | 5.6 | 352.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 119526.6852 | 7.0035 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-09 08:30 | 1.9 | 6.3 | 352.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 119681.6852 | 7.0126 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-09 09:30 | 2.4 | 6.3 | 347.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 119901.6852 | 7.0255 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-09 10:30 | 2.6 | 6 | 342.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 120121.6852 | 7.0384 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-09 11:30 | 3.1 | 6.3 | 332.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 120341.6852 | 7.0513 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-09 12:30 | 3.6 | 7.3 | 325 | 1480 | 1120 | 800 | 0 | 800 | 400 | 0 | 120741.6852 | 7.0747 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-09 13:30 | 2.7 | 8 | 327.5 | 2200 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 121386.6852 | 7.1125 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-09 14:30 | 2.1 | 8 | 335 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 122031.6852 | 7.1503 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-09 15:30 | 2.2 | 8.8 | 347.5 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 122676.6852 | 7.1881 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-09 16:30 | 1.6 | 9.9 | 177.5 | 3280 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 123321.6852 | 7.2259 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-09 17:30 | 0.8 | 10.4 | 175 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 123966.6852 | 7.2637 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-09 18:30 | -0.3 | 10.6 | 345 | 4000 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 124611.6852 | 7.3015 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-09 19:30 | -1.4 | 10.6 | 340 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 125256.6852 | 7.3393 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-09 20:30 | -1.6 | 10.1 | 340 | 3640 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 125901.6852 | 7.3771 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-09 21:30 | -1.5 | 9.4 | 340 | 2920 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 126546.6852 | 7.4148 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-09 22:30 | -1.4 | 8.5 | 340 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 127191.6852 | 7.4526 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-09 23:30 | -1.7 | 8 | 342.5 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 127836.6852 | 7.4904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-10 00:30 | -2.1 | 7.8 | 347.5 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 128481.6852 | 7.5282 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-10 01:30 | -2.4 | 7.3 | 347.5 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 129126.6852 | 7.566 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-10 02:30 | -2.6 | 6.7 | 342.5 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 129616.6852 | 7.5947 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-10 03:30 | -2.6 | 6.5 | 345 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 130016.6852 | 7.6182 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-10 04:30 | -2.9 | 7.4 | 175 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 130506.6852 | 7.6469 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-10 05:30 | -3 | 8.3 | 0 | 2200 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 131151.6852 | 7.6847 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-10 06:30 | -2.6 | 8.2 | 177.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 131796.6852 | 7.7225 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-10 07:30 | -2.1 | 8.4 | 352.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 132441.6852 | 7.7603 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-10 08:30 | -1.6 | 8.6 | 350 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 133086.6852 | 7.798 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-10 09:30 | -2 | 8.2 | 345 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 133731.6852 | 7.8358 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-10 10:30 | -2.1 | 8.4 | 335 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 134376.6852 | 7.8736 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-10 11:30 | -0.8 | 8.6 | 330 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 135021.6852 | 7.9114 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-10 12:30 | 0 | 8.6 | 335 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 135666.6852 | 7.9492 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-10 13:30 | 0 | 9.1 | 340 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 136311.6852 | 7.987 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-10 14:30 | -0.1 | 9.4 | 335 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 136956.6852 | 8.0248 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-10 15:30 | 0 | 9.4 | 330 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 137601.6852 | 8.0626 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-10 16:30 | 0.2 | 9.7 | 332.5 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 138246.6852 | 8.1004 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-10 17:30 | 0.6 | 10.1 | 337.5 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 138891.6852 | 8.1382 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-10 18:30 | 0.7 | 9.9 | 340 | 3280 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 139536.6852 | 8.176 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-10 19:30 | 0.3 | 9.6 | 337.5 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 140181.6852 | 8.2138 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-10 20:30 | 0 | 9.9 | 335 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 140826.6852 | 8.2516 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-10 21:30 | 0 | 9.5 | 337.5 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 141471.6852 | 8.2894 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-10 22:30 | 0 | 8.5 | 340 | 2560 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 142116.6852 | 8.3271 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-10 23:30 | 0 | 7.6 | 340 | 1840 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 142761.6852 | 8.3649 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-11 00:30 | 0 | 6.7 | 340 | 1120 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 143341.6852 | 8.3989 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-11 01:30 | 0.1 | 5.9 | 337.5 | 500 | 810 | 490 | 0 | 490 | 245 | 0 | 143586.6852 | 8.4133 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-11 02:30 | 0 | 5.7 | 335 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 143676.6852 | 8.4186 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-11 03:30 | -0.4 | 5.7 | 332.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 143766.6852 | 8.4238 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-11 04:30 | -0.9 | 5.7 | 330 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 143856.6852 | 8.4291 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-11 05:30 | -0.5 | 5.8 | 332.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 143946.6852 | 8.4344 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-11 06:30 | -0.1 | 6.1 | 335 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 144101.6852 | 8.4435 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-11 07:30 | -0.2 | 6.7 | 337.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 144411.6852 | 8.4616 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-11 08:30 | -0.2 | 7.5 | 340 | 1840 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 144991.6852 | 8.4956 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-11 09:30 | 0.8 | 8.9 | 345 | 2560 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 145636.6852 | 8.5334 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-11 10:30 | 2.1 | 9.9 | 175 | 3280 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 146281.6852 | 8.5712 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-11 11:30 | 2.5 | 9.5 | 177.5 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 146926.6852 | 8.609 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-11 12:30 | 3.2 | 8.3 | 350 | 2200 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 147571.6852 | 8.6468 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-11 13:30 | 3.7 | 7.4 | 337.5 | 1480 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 148216.6852 | 8.6846 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-11 14:30 | 3.4 | 7.1 | 320 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 148796.6852 | 8.7186 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-11 15:30 | 3.3 | 7 | 302.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 149376.6852 | 8.7525 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-11 16:30 | 3.2 | 7 | 292.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 149956.6852 | 8.7865 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-11 17:30 | 2.5 | 7 | 287.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 150536.6852 | 8.8205 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-11 18:30 | 2.4 | 7.3 | 287.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 151116.6852 | 8.8545 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-11 19:30 | 2.3 | 7.3 | 305 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 151696.6852 | 8.8885 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-11 20:30 | 1 | 6.3 | 327.5 | 760 | 1120 | 800 | 0 | 800 | 400 | 0 | 152096.6852 | 8.9119 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-11 21:30 | -0.3 | 5.7 | 332.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 152251.6852 | 8.921 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-11 22:30 | -0.3 | 5.7 | 327.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 152341.6852 | 8.9263 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-11 23:30 | -0.1 | 5.5 | 322.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 152431.6852 | 8.9315 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-12 00:30 | -0.1 | 5.1 | 315 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 152481.6852 | 8.9345 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-04-12 01:30 | -0.2 | 4.7 | 307.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 152369.8333 | 8.9279 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-04-12 02:30 | -0.5 | 4.5 | 305 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 152101.6852 | 8.9122 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-04-12 03:30 | -0.8 | 4.7 | 305 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 151833.537 | 8.8965 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-12 04:30 | -0.6 | 5.5 | 310 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 151848.3704 | 8.8974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-12 05:30 | -0.4 | 6.8 | 317.5 | 1120 | 810 | 490 | 0 | 490 | 245 | 0 | 152093.3704 | 8.9117 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-12 06:30 | -0.2 | 7.5 | 325 | 1840 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 152673.3704 | 8.9457 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-12 07:30 | 0.1 | 7.6 | 332.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 153318.3704 | 8.9835 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-12 08:30 | 0.1 | 8.2 | 332.5 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 153963.3704 | 9.0213 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-12 09:30 | 0.5 | 9 | 330 | 2920 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 154608.3704 | 9.0591 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-12 10:30 | 1.5 | 9.3 | 327.5 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 155253.3704 | 9.0969 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-12 11:30 | 2.2 | 9.1 | 322.5 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 155898.3704 | 9.1347 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-12 12:30 | 2.4 | 9 | 317.5 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 156543.3704 | 9.1725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-12 13:30 | 2.6 | 9.2 | 312.5 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 157188.3704 | 9.2103 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-12 14:30 | 3 | 9.5 | 310 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 157833.3704 | 9.248 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-12 15:30 | 3.2 | 9.4 | 312.5 | 2920 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 158478.3704 | 9.2858 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-12 16:30 | 2.5 | 8.9 | 317.5 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 159123.3704 | 9.3236 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-12 17:30 | 1.8 | 8.1 | 317.5 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 159768.3704 | 9.3614 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-12 18:30 | 1.8 | 7.6 | 312.5 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 160413.3704 | 9.3992 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-12 19:30 | 1.6 | 7.3 | 310 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 161058.3704 | 9.437 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-12 20:30 | 1.1 | 7.1 | 307.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 161638.3704 | 9.471 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-12 21:30 | 1.1 | 6.7 | 302.5 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 162128.3704 | 9.4997 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-12 22:30 | 0.9 | 6.1 | 300 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 162438.3704 | 9.5179 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-12 23:30 | 0.3 | 5.9 | 297.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 162593.3704 | 9.527 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-13 00:30 | 0 | 5.8 | 297.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 162683.3704 | 9.5322 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-13 01:30 | 0.1 | 5.3 | 305 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 162733.3704 | 9.5352 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-13 02:30 | 0.3 | 5.2 | 310 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 162743.3704 | 9.5357 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-13 03:30 | 0.1 | 5.4 | 310 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 162753.3704 | 9.5363 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-13 04:30 | 0 | 5.1 | 307.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 162763.3704 | 9.5369 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-04-13 05:30 | -0.1 | 4.9 | 307.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 162651.5185 | 9.5304 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-04-13 06:30 | -0.1 | 5.3 | 312.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 162539.6667 | 9.5238 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-13 07:30 | 0 | 6.2 | 312.5 | 760 | 550 | 230 | 0 | 230 | 115 | 0 | 162654.6667 | 9.5305 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-13 08:30 | 0.4 | 6.8 | 312.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 162964.6667 | 9.5487 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-13 09:30 | 1.1 | 7 | 317.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 163454.6667 | 9.5774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-13 10:30 | 1.7 | 7.2 | 315 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 164034.6667 | 9.6114 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-13 11:30 | 2.4 | 7.5 | 307.5 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 164679.6667 | 9.6492 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-13 12:30 | 2.8 | 7.1 | 307.5 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 165324.6667 | 9.687 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-13 13:30 | 3 | 6.5 | 312.5 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 165814.6667 | 9.7157 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-13 14:30 | 2.8 | 6.3 | 317.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 166124.6667 | 9.7339 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-13 15:30 | 2.9 | 5.6 | 315 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 166279.6667 | 9.7429 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-13 16:30 | 3.2 | 5 | 297.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 166329.6667 | 9.7459 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-04-13 17:30 | 2.9 | 4.5 | 267.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 166217.8148 | 9.7393 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-04-13 18:30 | 1.4 | 3.3 | 257.5 | 0 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 165728.1852 | 9.7106 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-04-13 19:30 | 0 | 2.4 | 282.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165017.0741 | 9.669 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-04-13 20:30 | 0.3 | 2 | 307.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164305.963 | 9.6273 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-04-13 21:30 | 0.7 | 1.6 | 312.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163594.8519 | 9.5856 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-04-13 22:30 | 0.7 | 2 | 307.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162883.7407 | 9.544 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-04-13 23:30 | 0.7 | 3.2 | 315 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162172.6296 | 9.5023 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-04-14 00:30 | 0.6 | 3.9 | 330 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161461.5185 | 9.4606 | 0 |  |  | 1 | 9 | 1 | 6
Lerwick | 1978-04-14 01:30 | 0 | 4.4 | 337.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 160835.5926 | 9.424 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-04-14 02:30 | -0.3 | 5.3 | 340 | 340 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 160587.4444 | 9.4094 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-14 03:30 | 0 | 5.5 | 342.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 160637.4444 | 9.4124 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-14 04:30 | -0.3 | 4.9 | 345 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 160652.2778 | 9.4132 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-04-14 05:30 | -0.7 | 4.2 | 342.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 160247.8333 | 9.3895 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-04-14 06:30 | -0.5 | 4 | 340 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 159707.0926 | 9.3578 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-04-14 07:30 | 0.7 | 4.2 | 337.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 159166.3519 | 9.3262 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-04-14 08:30 | 2.1 | 5.2 | 335 | 340 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 158918.2037 | 9.3116 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-14 09:30 | 3.5 | 6.5 | 345 | 1120 | 730 | 410 | 0 | 410 | 205 | 0 | 159123.2037 | 9.3236 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-14 10:30 | 4.2 | 7.6 | 182.5 | 1840 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 159703.2037 | 9.3576 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-14 11:30 | 4.6 | 8.4 | 7.5 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 160348.2037 | 9.3954 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-14 12:30 | 5.2 | 8.4 | 5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 160993.2037 | 9.4332 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-14 13:30 | 5.7 | 7.8 | 177.5 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 161638.2037 | 9.471 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-14 14:30 | 5.5 | 7.9 | 337.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 162283.2037 | 9.5088 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-14 15:30 | 4.6 | 8 | 330 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 162928.2037 | 9.5466 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-14 16:30 | 3.9 | 7.7 | 342.5 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 163573.2037 | 9.5844 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-14 17:30 | 3.9 | 6.9 | 347.5 | 1120 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 164153.2037 | 9.6184 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-14 18:30 | 4 | 5.6 | 342.5 | 500 | 810 | 490 | 0 | 490 | 245 | 0 | 164398.2037 | 9.6327 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-04-14 19:30 | 3.1 | 4.4 | 342.5 | 76.6667 | 288.3333 | 0 | 31.6667 | 0 | 0 | 70.3704 | 164327.8333 | 9.6286 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-04-14 20:30 | 2.2 | 3.9 | 340 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 163701.9074 | 9.5919 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-04-14 21:30 | 2.1 | 3.7 | 327.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162990.7963 | 9.5502 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-04-14 22:30 | 2 | 3.4 | 320 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162279.6852 | 9.5086 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-04-14 23:30 | 2 | 3.2 | 325 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161568.5741 | 9.4669 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-04-15 00:30 | 2.1 | 3.2 | 335 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160857.463 | 9.4252 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-04-15 01:30 | 2 | 3.6 | 340 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160146.3519 | 9.3836 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-04-15 02:30 | 1.9 | 4.2 | 342.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 159520.4259 | 9.3469 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-04-15 03:30 | 2.1 | 4.2 | 345 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 158979.6852 | 9.3152 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-04-15 04:30 | 1.2 | 3.5 | 345 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 158353.7593 | 9.2785 | 1 |  |  | 1 | 11 | 0 | 0
Lerwick | 1978-04-15 05:30 | 0.4 | 2.8 | 342.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 157642.6481 | 9.2369 | 0 |  |  | 1 | 12 | 1 | 1
Lerwick | 1978-04-15 06:30 | 0.7 | 2.6 | 335 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 156931.537 | 9.1952 | 0 |  |  | 1 | 13 | 1 | 2
Lerwick | 1978-04-15 07:30 | 1.7 | 2.8 | 335 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 156220.4259 | 9.1535 | 0 |  |  | 1 | 14 | 1 | 3
Lerwick | 1978-04-15 08:30 | 3.1 | 2.9 | 175 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 155509.3148 | 9.1119 | 0 |  |  | 1 | 15 | 1 | 4
Lerwick | 1978-04-15 09:30 | 3.6 | 2.6 | 47.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 154798.2037 | 9.0702 | 0 |  |  | 1 | 16 | 1 | 5
Lerwick | 1978-04-15 10:30 | 4.1 | 2.6 | 110 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 154087.0926 | 9.0285 | 0 |  |  | 1 | 17 | 1 | 6
Lerwick | 1978-04-15 11:30 | 5 | 2.9 | 132.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 153375.9815 | 8.9869 | 0 |  |  | 1 | 18 | 1 | 7
Lerwick | 1978-04-15 12:30 | 5.2 | 3.1 | 132.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 152664.8704 | 8.9452 | 0 |  |  | 1 | 19 | 1 | 8
Lerwick | 1978-04-15 13:30 | 5 | 2.9 | 140 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 151953.7593 | 8.9035 | 0 |  |  | 1 | 20 | 1 | 9
Lerwick | 1978-04-15 14:30 | 4.9 | 2.7 | 147.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 151242.6481 | 8.8619 | 0 |  |  | 1 | 21 | 1 | 10
Lerwick | 1978-04-15 15:30 | 4.8 | 2.9 | 157.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 150531.537 | 8.8202 | 0 |  |  | 1 | 22 | 1 | 11
Lerwick | 1978-04-15 16:30 | 4.9 | 3.2 | 190 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 149820.4259 | 8.7785 | 0 |  |  | 1 | 23 | 1 | 12
Lerwick | 1978-04-15 17:30 | 5.3 | 3.3 | 235 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 149109.3148 | 8.7369 | 0 |  |  | 1 | 24 | 1 | 13
Lerwick | 1978-04-15 18:30 | 5.3 | 3 | 260 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 148398.2037 | 8.6952 | 0 |  |  | 1 | 25 | 1 | 14
Lerwick | 1978-04-15 19:30 | 4.4 | 2.2 | 255 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 147687.0926 | 8.6535 | 0 |  |  | 1 | 26 | 1 | 15
Lerwick | 1978-04-15 20:30 | 3.5 | 1.4 | 227.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 146975.9815 | 8.6119 | 0 |  |  | 1 | 27 | 1 | 16
Lerwick | 1978-04-15 21:30 | 2.6 | 1 | 205 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 146264.8704 | 8.5702 | 0 |  |  | 1 | 28 | 1 | 17
Lerwick | 1978-04-15 22:30 | 1.7 | 1 | 202.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 145553.7593 | 8.5285 | 0 |  |  | 1 | 29 | 1 | 18
Lerwick | 1978-04-15 23:30 | 1.7 | 1.5 | 205 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 144842.6481 | 8.4869 | 0 |  |  | 1 | 30 | 1 | 19
Lerwick | 1978-04-16 00:30 | 2.1 | 2.4 | 205 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 144131.537 | 8.4452 | 0 |  |  | 1 | 31 | 1 | 20
Lerwick | 1978-04-16 01:30 | 2.3 | 2.7 | 205 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 143420.4259 | 8.4035 | 0 |  |  | 1 | 32 | 1 | 21
Lerwick | 1978-04-16 02:30 | 2.3 | 3 | 202.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 142709.3148 | 8.3619 | 0 |  |  | 1 | 33 | 1 | 22
Lerwick | 1978-04-16 03:30 | 2.3 | 3.6 | 200 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 141998.2037 | 8.3202 | 0 |  |  | 1 | 34 | 1 | 23
Lerwick | 1978-04-16 04:30 | 2.5 | 4.1 | 200 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 141372.2778 | 8.2835 | 1 |  |  | 1 | 35 | 0 | 0
Lerwick | 1978-04-16 05:30 | 2.6 | 4.9 | 200 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 140967.8333 | 8.2598 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-16 06:30 | 3.3 | 6.2 | 200 | 760 | 479.6667 | 159.6667 | 0 | 159.6667 | 79.8333 | 0 | 141047.6667 | 8.2645 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-16 07:30 | 4.2 | 7.3 | 200 | 1480 | 1120 | 800 | 0 | 800 | 400 | 0 | 141447.6667 | 8.2879 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-16 08:30 | 5 | 7.8 | 202.5 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 142092.6667 | 8.3257 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-16 09:30 | 5.2 | 8.5 | 207.5 | 2560 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 142737.6667 | 8.3635 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-16 10:30 | 5 | 9.7 | 212.5 | 3280 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 143382.6667 | 8.4013 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-16 11:30 | 5.1 | 10.7 | 220 | 4000 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 144027.6667 | 8.4391 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-16 12:30 | 5.1 | 10.6 | 230 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 144672.6667 | 8.4769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-16 13:30 | 5.2 | 9.9 | 240 | 3280 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 145317.6667 | 8.5147 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-16 14:30 | 5.9 | 9.2 | 250 | 2920 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 145962.6667 | 8.5525 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-16 15:30 | 6.6 | 8.9 | 257.5 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 146607.6667 | 8.5903 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-16 16:30 | 6.9 | 8.8 | 260 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 147252.6667 | 8.6281 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-16 17:30 | 7 | 9 | 262.5 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 147897.6667 | 8.6659 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-16 18:30 | 7 | 9.3 | 267.5 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 148542.6667 | 8.7037 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-16 19:30 | 6.8 | 9.1 | 267.5 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 149187.6667 | 8.7415 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-16 20:30 | 6.4 | 8.7 | 262.5 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 149832.6667 | 8.7793 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-16 21:30 | 6.2 | 8 | 260 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 150477.6667 | 8.8171 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-16 22:30 | 6.3 | 7.3 | 262.5 | 1480 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 151122.6667 | 8.8548 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-16 23:30 | 6.4 | 7.1 | 270 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 151702.6667 | 8.8888 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-17 00:30 | 6.4 | 6.7 | 282.5 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 152192.6667 | 8.9175 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-17 01:30 | 6.5 | 6.1 | 312.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 152502.6667 | 8.9357 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-17 02:30 | 6.3 | 5.8 | 182.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 152657.6667 | 8.9448 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-17 03:30 | 5.6 | 5.7 | 40 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 152747.6667 | 8.9501 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-17 04:30 | 4.8 | 5.8 | 50 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 152837.6667 | 8.9553 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-17 05:30 | 4.4 | 6.1 | 50 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 152992.6667 | 8.9644 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-17 06:30 | 4.2 | 6.5 | 50 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 153302.6667 | 8.9826 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-17 07:30 | 4.1 | 6.7 | 50 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 153702.6667 | 9.006 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-17 08:30 | 4.5 | 6.9 | 50 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 154102.6667 | 9.0295 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-17 09:30 | 4.8 | 7.6 | 50 | 1840 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 154682.6667 | 9.0634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-17 10:30 | 4.8 | 8.4 | 50 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 155327.6667 | 9.1012 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-17 11:30 | 5.1 | 8.6 | 50 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 155972.6667 | 9.139 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-17 12:30 | 5.3 | 8.2 | 50 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 156617.6667 | 9.1768 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-17 13:30 | 5.2 | 7.8 | 50 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 157262.6667 | 9.2146 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-17 14:30 | 5 | 7.8 | 50 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 157907.6667 | 9.2524 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-17 15:30 | 4.9 | 8 | 50 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 158552.6667 | 9.2902 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-17 16:30 | 4.9 | 7.6 | 52.5 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 159197.6667 | 9.328 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-17 17:30 | 4.7 | 6.9 | 57.5 | 1120 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 159777.6667 | 9.362 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-17 18:30 | 4.4 | 6.4 | 60 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 160087.6667 | 9.3801 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-17 19:30 | 3.8 | 5.8 | 57.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 160242.6667 | 9.3892 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-17 20:30 | 3.3 | 5.2 | 52.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 160292.6667 | 9.3921 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-17 21:30 | 3.1 | 5 | 50 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 160302.6667 | 9.3927 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-17 22:30 | 2.7 | 5 | 47.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 160312.6667 | 9.3933 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-17 23:30 | 2.5 | 5.2 | 45 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 160322.6667 | 9.3939 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-18 00:30 | 2.7 | 5.4 | 47.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 160332.6667 | 9.3945 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-18 01:30 | 2.4 | 5.1 | 47.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 160342.6667 | 9.3951 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-04-18 02:30 | 2.3 | 4.7 | 42.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 160230.8148 | 9.3885 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-04-18 03:30 | 2.3 | 4.4 | 40 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 159826.3704 | 9.3648 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-04-18 04:30 | 2.2 | 4.2 | 37.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 159285.6296 | 9.3331 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-04-18 05:30 | 2.2 | 4.2 | 32.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 158744.8889 | 9.3015 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-04-18 06:30 | 2.7 | 4.7 | 32.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 158340.4444 | 9.2778 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-04-18 07:30 | 3.5 | 4.7 | 37.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 158072.2963 | 9.262 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-04-18 08:30 | 4.1 | 4.7 | 37.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 157804.1481 | 9.2463 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-04-18 09:30 | 4.5 | 4.9 | 32.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 157536 | 9.2306 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-04-18 10:30 | 4.8 | 5 | 32.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 157424.1481 | 9.2241 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-04-18 11:30 | 5.3 | 4.9 | 42.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 157312.2963 | 9.2175 | 1 |  |  | 1 | 11 | 0 | 0
Lerwick | 1978-04-18 12:30 | 5.4 | 4.4 | 57.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 156907.8519 | 9.1938 | 1 |  |  | 1 | 12 | 0 | 0
Lerwick | 1978-04-18 13:30 | 6 | 3.8 | 67.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 156281.9259 | 9.1571 | 1 |  |  | 1 | 13 | 0 | 0
Lerwick | 1978-04-18 14:30 | 6.6 | 3.4 | 70 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 155570.8148 | 9.1155 | 0 |  |  | 1 | 14 | 1 | 1
Lerwick | 1978-04-18 15:30 | 6.3 | 3 | 77.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 154859.7037 | 9.0738 | 0 |  |  | 1 | 15 | 1 | 2
Lerwick | 1978-04-18 16:30 | 6.1 | 2.4 | 102.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 154148.5926 | 9.0321 | 0 |  |  | 1 | 16 | 1 | 3
Lerwick | 1978-04-18 17:30 | 5.8 | 2 | 132.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 153437.4815 | 8.9905 | 0 |  |  | 1 | 17 | 1 | 4
Lerwick | 1978-04-18 18:30 | 5.4 | 1.5 | 140 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 152726.3704 | 8.9488 | 0 |  |  | 1 | 18 | 1 | 5
Lerwick | 1978-04-18 19:30 | 4.7 | 0.9 | 97.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 152015.2593 | 8.9071 | 0 |  |  | 1 | 19 | 1 | 6
Lerwick | 1978-04-18 20:30 | 3.6 | 0.2 | 30 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 151304.1481 | 8.8655 | 0 |  |  | 1 | 20 | 1 | 7
Lerwick | 1978-04-18 21:30 | 2.2 | 0.2 | 22.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 150593.037 | 8.8238 | 0 |  |  | 1 | 21 | 1 | 8
Lerwick | 1978-04-18 22:30 | 1.1 | 0.7 | 72.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 149881.9259 | 8.7821 | 0 |  |  | 1 | 22 | 1 | 9
Lerwick | 1978-04-18 23:30 | 1.6 | 1.6 | 107.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 149170.8148 | 8.7405 | 0 |  |  | 1 | 23 | 1 | 10
Lerwick | 1978-04-19 00:30 | 2.5 | 3 | 122.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 148459.7037 | 8.6988 | 0 |  |  | 1 | 24 | 1 | 11
Lerwick | 1978-04-19 01:30 | 2.7 | 4.1 | 132.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 147833.7778 | 8.6621 | 1 |  |  | 1 | 25 | 0 | 0
Lerwick | 1978-04-19 02:30 | 3.3 | 4.2 | 127.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 147293.037 | 8.6305 | 1 |  |  | 1 | 26 | 0 | 0
Lerwick | 1978-04-19 03:30 | 3.6 | 3.8 | 115 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 146667.1111 | 8.5938 | 1 |  |  | 1 | 27 | 0 | 0
Lerwick | 1978-04-19 04:30 | 3.7 | 3.6 | 117.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 145956 | 8.5521 | 0 |  |  | 1 | 28 | 1 | 1
Lerwick | 1978-04-19 05:30 | 4.2 | 3.8 | 137.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 145244.8889 | 8.5104 | 0 |  |  | 1 | 29 | 1 | 2
Lerwick | 1978-04-19 06:30 | 4.9 | 4.5 | 155 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 144755.2593 | 8.4818 | 1 |  |  | 1 | 30 | 0 | 0
Lerwick | 1978-04-19 07:30 | 5.6 | 5.3 | 157.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 144643.4074 | 8.4752 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-19 08:30 | 5.9 | 5.8 | 152.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 144693.4074 | 8.4781 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-19 09:30 | 6.4 | 5.8 | 150 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 144783.4074 | 8.4834 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-19 10:30 | 6.8 | 5.5 | 152.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 144873.4074 | 8.4887 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-19 11:30 | 6.8 | 5.5 | 155 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 144963.4074 | 8.4939 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-19 12:30 | 6.7 | 5.5 | 152.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 145053.4074 | 8.4992 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-19 13:30 | 6.9 | 5.2 | 150 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 145103.4074 | 8.5022 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-19 14:30 | 6.7 | 5.2 | 150 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 145113.4074 | 8.5027 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-19 15:30 | 6.2 | 5.5 | 150 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 145163.4074 | 8.5057 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-19 16:30 | 6 | 5.8 | 152.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 145253.4074 | 8.5109 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-19 17:30 | 6 | 6.1 | 157.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 145408.4074 | 8.52 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-19 18:30 | 6 | 6.5 | 160 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 145718.4074 | 8.5382 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-19 19:30 | 5.9 | 6.7 | 160 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 146118.4074 | 8.5616 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-19 20:30 | 5.9 | 6.5 | 162.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 146518.4074 | 8.5851 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-19 21:30 | 5.8 | 6.3 | 167.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 146828.4074 | 8.6032 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-19 22:30 | 5.7 | 6.6 | 167.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 147138.4074 | 8.6214 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-19 23:30 | 5.7 | 7.1 | 162.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 147628.4074 | 8.6501 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-20 00:30 | 5.6 | 7.3 | 162.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 148208.4074 | 8.6841 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-20 01:30 | 5.5 | 7.7 | 165 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 148853.4074 | 8.7219 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-20 02:30 | 5.5 | 8 | 162.5 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 149498.4074 | 8.7597 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-20 03:30 | 5.2 | 8 | 157.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 150143.4074 | 8.7975 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-20 04:30 | 5.2 | 8 | 155 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 150788.4074 | 8.8353 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-20 05:30 | 5.2 | 8 | 155 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 151433.4074 | 8.8731 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-20 06:30 | 5.2 | 7.7 | 152.5 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 152078.4074 | 8.9108 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-20 07:30 | 6.2 | 7.2 | 147.5 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 152723.4074 | 8.9486 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-20 08:30 | 6.9 | 6.8 | 145 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 153213.4074 | 8.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-20 09:30 | 7.2 | 6.7 | 147.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 153613.4074 | 9.0008 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-20 10:30 | 7.2 | 6.7 | 147.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 154013.4074 | 9.0242 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-20 11:30 | 7.3 | 7.1 | 145 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 154503.4074 | 9.0529 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-20 12:30 | 7 | 7.8 | 147.5 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 155148.4074 | 9.0907 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-20 13:30 | 6.1 | 8.1 | 150 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 155793.4074 | 9.1285 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-20 14:30 | 5.8 | 8 | 150 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 156438.4074 | 9.1663 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-20 15:30 | 5.7 | 8 | 150 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 157083.4074 | 9.2041 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-20 16:30 | 5.5 | 8.2 | 150 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 157728.4074 | 9.2419 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-20 17:30 | 5.5 | 8.5 | 150 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 158373.4074 | 9.2797 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-20 18:30 | 5.4 | 8.5 | 150 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 159018.4074 | 9.3175 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-20 19:30 | 5.1 | 8.6 | 150 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 159663.4074 | 9.3553 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-20 20:30 | 4.8 | 8.8 | 150 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 160308.4074 | 9.3931 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-20 21:30 | 4.9 | 8.6 | 150 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 160953.4074 | 9.4309 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-20 22:30 | 4.9 | 8.2 | 147.5 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 161598.4074 | 9.4687 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-20 23:30 | 4.8 | 7.8 | 145 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 162243.4074 | 9.5064 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-21 00:30 | 4.8 | 7.8 | 147.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 162888.4074 | 9.5442 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-21 01:30 | 4.8 | 8 | 150 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 163533.4074 | 9.582 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-21 02:30 | 4.8 | 7.6 | 150 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 164178.4074 | 9.6198 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-21 03:30 | 5 | 6.9 | 150 | 1120 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 164758.4074 | 9.6538 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-21 04:30 | 5 | 6.7 | 150 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 165158.4074 | 9.6773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-21 05:30 | 5 | 6.9 | 150 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 165558.4074 | 9.7007 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-21 06:30 | 5.1 | 7.4 | 150 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 166048.4074 | 9.7294 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-21 07:30 | 5.1 | 7.6 | 150 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 166693.4074 | 9.7672 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-21 08:30 | 5.2 | 7.3 | 150 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 167338.4074 | 9.805 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-21 09:30 | 5.6 | 7.1 | 150 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 167918.4074 | 9.839 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-21 10:30 | 5.6 | 6.7 | 150 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 168408.4074 | 9.8677 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-21 11:30 | 6 | 6.3 | 150 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 168718.4074 | 9.8858 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-21 12:30 | 6.2 | 6.2 | 150 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 168938.4074 | 9.8987 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-21 13:30 | 5.9 | 6.2 | 152.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 169158.4074 | 9.9116 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-21 14:30 | 5.8 | 6 | 157.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 169378.4074 | 9.9245 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-21 15:30 | 5.7 | 5.8 | 160 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 169533.4074 | 9.9336 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-21 16:30 | 5.7 | 5.7 | 160 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 169623.4074 | 9.9389 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-21 17:30 | 5.7 | 5.5 | 160 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 169713.4074 | 9.9441 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-21 18:30 | 5.7 | 5.4 | 157.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 169763.4074 | 9.9471 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-21 19:30 | 5.7 | 5.4 | 152.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 169773.4074 | 9.9477 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-21 20:30 | 5.8 | 5.4 | 155 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 169783.4074 | 9.9482 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-21 21:30 | 5.8 | 5.6 | 165 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 169833.4074 | 9.9512 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-21 22:30 | 5.6 | 6.1 | 170 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 169988.4074 | 9.9603 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-21 23:30 | 5.5 | 6.9 | 172.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 170298.4074 | 9.9784 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-22 00:30 | 5.5 | 7.7 | 177.5 | 1840 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170298.4074 | 9.9784 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-22 01:30 | 5.3 | 8 | 180 | 2200 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170298.4074 | 9.9784 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-22 02:30 | 5.1 | 8 | 180 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170298.4074 | 9.9784 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-22 03:30 | 4.9 | 8.3 | 177.5 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170298.4074 | 9.9784 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-22 04:30 | 4.5 | 8.6 | 175 | 2560 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170298.4074 | 9.9784 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-22 05:30 | 4.3 | 8.8 | 177.5 | 2560 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170298.4074 | 9.9784 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-22 06:30 | 4.5 | 8.8 | 180 | 2560 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170298.4074 | 9.9784 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-22 07:30 | 4.9 | 8.4 | 182.5 | 2200 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170298.4074 | 9.9784 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-22 08:30 | 5 | 7.8 | 187.5 | 1840 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170298.4074 | 9.9784 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-22 09:30 | 5.1 | 7.5 | 187.5 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170298.4074 | 9.9784 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-22 10:30 | 5.3 | 7.5 | 182.5 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170298.4074 | 9.9784 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-22 11:30 | 5.8 | 7.2 | 177.5 | 1480 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170298.4074 | 9.9784 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-22 12:30 | 6.2 | 6.8 | 175 | 1120 | 1300 | 980 | 0 | 980 | 0 | 0 | 170298.4074 | 9.9784 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-22 13:30 | 6.2 | 6.8 | 180 | 1120 | 1120 | 800 | 0 | 800 | 0 | 0 | 170298.4074 | 9.9784 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-22 14:30 | 6.4 | 7.2 | 187.5 | 1480 | 1300 | 980 | 0 | 980 | 0 | 0 | 170298.4074 | 9.9784 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-22 15:30 | 6.7 | 7.3 | 192.5 | 1480 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170298.4074 | 9.9784 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-22 16:30 | 6.6 | 6.9 | 200 | 1120 | 1300 | 980 | 0 | 980 | 0 | 0 | 170298.4074 | 9.9784 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-22 17:30 | 6.8 | 6.7 | 207.5 | 1120 | 1120 | 800 | 0 | 800 | 0 | 0 | 170298.4074 | 9.9784 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-22 18:30 | 6.7 | 6.7 | 210 | 1120 | 1120 | 800 | 0 | 800 | 0 | 0 | 170298.4074 | 9.9784 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-22 19:30 | 6.3 | 6.3 | 212.5 | 760 | 940 | 620 | 0 | 620 | 0 | 0 | 170298.4074 | 9.9784 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-22 20:30 | 6.1 | 4.9 | 227.5 | 199.3333 | 479.6667 | 159.6667 | 0 | 159.6667 | 0 | 0 | 170298.4074 | 9.9784 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-04-22 21:30 | 6 | 3 | 250 | 0 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 169808.7778 | 9.9497 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-04-22 22:30 | 6 | 2.4 | 265 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 169097.6667 | 9.9081 | 0 |  |  | 1 | 3 | 1 | 1
Lerwick | 1978-04-22 23:30 | 6 | 3 | 265 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168386.5556 | 9.8664 | 0 |  |  | 1 | 4 | 1 | 2
Lerwick | 1978-04-23 00:30 | 5.7 | 2.9 | 247.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167675.4444 | 9.8247 | 0 |  |  | 1 | 5 | 1 | 3
Lerwick | 1978-04-23 01:30 | 5.6 | 2.2 | 247.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166964.3333 | 9.7831 | 0 |  |  | 1 | 6 | 1 | 4
Lerwick | 1978-04-23 02:30 | 5.7 | 1.8 | 297.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166253.2222 | 9.7414 | 0 |  |  | 1 | 7 | 1 | 5
Lerwick | 1978-04-23 03:30 | 5.7 | 1.6 | 172.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165542.1111 | 9.6997 | 0 |  |  | 1 | 8 | 1 | 6
Lerwick | 1978-04-23 04:30 | 5.4 | 1.2 | 7.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164831 | 9.6581 | 0 |  |  | 1 | 9 | 1 | 7
Lerwick | 1978-04-23 05:30 | 5.2 | 1 | 12.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164119.8889 | 9.6164 | 0 |  |  | 1 | 10 | 1 | 8
Lerwick | 1978-04-23 06:30 | 5.2 | 1.1 | 12.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163408.7778 | 9.5747 | 0 |  |  | 1 | 11 | 1 | 9
Lerwick | 1978-04-23 07:30 | 5.3 | 1.5 | 172.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162697.6667 | 9.5331 | 0 |  |  | 1 | 12 | 1 | 10
Lerwick | 1978-04-23 08:30 | 5.6 | 2 | 340 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161986.5556 | 9.4914 | 0 |  |  | 1 | 13 | 1 | 11
Lerwick | 1978-04-23 09:30 | 5.8 | 2.4 | 330 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161275.4444 | 9.4497 | 0 |  |  | 1 | 14 | 1 | 12
Lerwick | 1978-04-23 10:30 | 6.3 | 3 | 315 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160564.3333 | 9.4081 | 0 |  |  | 1 | 15 | 1 | 13
Lerwick | 1978-04-23 11:30 | 7 | 3.6 | 315 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 159853.2222 | 9.3664 | 0 |  |  | 1 | 16 | 1 | 14
Lerwick | 1978-04-23 12:30 | 7.7 | 3.9 | 320 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 159142.1111 | 9.3247 | 0 |  |  | 1 | 17 | 1 | 15
Lerwick | 1978-04-23 13:30 | 8.3 | 4 | 320 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 158516.1852 | 9.2881 | 1 |  |  | 1 | 18 | 0 | 0
Lerwick | 1978-04-23 14:30 | 8.3 | 4.2 | 317.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 157975.4444 | 9.2564 | 1 |  |  | 1 | 19 | 0 | 0
Lerwick | 1978-04-23 15:30 | 7.9 | 4.7 | 312.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 157571 | 9.2327 | 1 |  |  | 1 | 20 | 0 | 0
Lerwick | 1978-04-23 16:30 | 7.3 | 4.9 | 312.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 157302.8519 | 9.217 | 1 |  |  | 1 | 21 | 0 | 0
Lerwick | 1978-04-23 17:30 | 6.8 | 4.9 | 320 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 157034.7037 | 9.2013 | 1 |  |  | 1 | 22 | 0 | 0
Lerwick | 1978-04-23 18:30 | 6.2 | 5.1 | 330 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 156922.8519 | 9.1947 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-23 19:30 | 5.4 | 5.6 | 337.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 156972.8519 | 9.1976 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-23 20:30 | 4.8 | 5.8 | 340 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 157062.8519 | 9.2029 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-23 21:30 | 4.9 | 5.3 | 337.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 157112.8519 | 9.2058 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-23 22:30 | 4.9 | 5.3 | 332.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 157122.8519 | 9.2064 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-23 23:30 | 4.9 | 6.3 | 332.5 | 760 | 550 | 230 | 0 | 230 | 115 | 0 | 157237.8519 | 9.2132 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-24 00:30 | 4.8 | 7 | 337.5 | 1480 | 1120 | 800 | 0 | 800 | 400 | 0 | 157637.8519 | 9.2366 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-24 01:30 | 4.6 | 6.6 | 342.5 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 158127.8519 | 9.2653 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-24 02:30 | 4.6 | 6.4 | 350 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 158437.8519 | 9.2835 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-24 03:30 | 4.7 | 6.7 | 177.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 158747.8519 | 9.3016 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-24 04:30 | 4.5 | 6.3 | 177.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 159057.8519 | 9.3198 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-24 05:30 | 4.3 | 6.1 | 355 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 159277.8519 | 9.3327 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-24 06:30 | 4.4 | 7 | 355 | 1480 | 1120 | 800 | 0 | 800 | 400 | 0 | 159677.8519 | 9.3561 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-24 07:30 | 4.7 | 7.9 | 355 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 160322.8519 | 9.3939 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-24 08:30 | 5.9 | 8.4 | 180 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 160967.8519 | 9.4317 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-24 09:30 | 7.4 | 9.1 | 10 | 2920 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 161612.8519 | 9.4695 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-24 10:30 | 7.7 | 9.7 | 20 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 162257.8519 | 9.5073 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-24 11:30 | 7.7 | 9.7 | 25 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 162902.8519 | 9.5451 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-24 12:30 | 7.9 | 9.1 | 22.5 | 2920 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 163547.8519 | 9.5829 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-24 13:30 | 8 | 9 | 20 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 164192.8519 | 9.6207 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-24 14:30 | 8 | 9.3 | 20 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 164837.8519 | 9.6585 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-24 15:30 | 7.6 | 9 | 20 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 165482.8519 | 9.6963 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-24 16:30 | 7.4 | 8.8 | 17.5 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 166127.8519 | 9.7341 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-24 17:30 | 7.1 | 8.4 | 12.5 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 166772.8519 | 9.7718 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-24 18:30 | 6.1 | 8 | 10 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 167417.8519 | 9.8096 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-24 19:30 | 5.2 | 8 | 10 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 168062.8519 | 9.8474 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-24 20:30 | 4.7 | 7.7 | 7.5 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 168707.8519 | 9.8852 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-24 21:30 | 4.3 | 7.3 | 2.5 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 169352.8519 | 9.923 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-24 22:30 | 4 | 6.9 | 177.5 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 169842.8519 | 9.9517 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-24 23:30 | 3.8 | 6.5 | 352.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 170242.8519 | 9.9752 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-25 00:30 | 3.8 | 6.7 | 350 | 1120 | 1120 | 800 | 0 | 800 | 0 | 0 | 170242.8519 | 9.9752 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-25 01:30 | 3.4 | 7.1 | 350 | 1480 | 1300 | 980 | 0 | 980 | 0 | 0 | 170242.8519 | 9.9752 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-25 02:30 | 2.9 | 7.1 | 350 | 1480 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170242.8519 | 9.9752 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-25 03:30 | 2 | 6.8 | 350 | 1120 | 1300 | 980 | 0 | 980 | 0 | 0 | 170242.8519 | 9.9752 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-25 04:30 | 1.6 | 6.9 | 350 | 1120 | 1120 | 800 | 0 | 800 | 0 | 0 | 170242.8519 | 9.9752 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-25 05:30 | 2.1 | 7.6 | 352.5 | 1840 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170242.8519 | 9.9752 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-25 06:30 | 2.5 | 8.1 | 177.5 | 2200 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170242.8519 | 9.9752 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-25 07:30 | 1.6 | 7.8 | 7.5 | 1840 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170242.8519 | 9.9752 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-25 08:30 | 1 | 7.2 | 20 | 1480 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170242.8519 | 9.9752 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-25 09:30 | 1.2 | 7.3 | 22.5 | 1480 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170242.8519 | 9.9752 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-25 10:30 | 2.1 | 8.2 | 25 | 2200 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170242.8519 | 9.9752 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-25 11:30 | 2.1 | 8.8 | 35 | 2560 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170242.8519 | 9.9752 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-25 12:30 | 1.8 | 8.6 | 40 | 2560 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170242.8519 | 9.9752 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-25 13:30 | 3 | 8.1 | 37.5 | 2200 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170242.8519 | 9.9752 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-25 14:30 | 3.3 | 7.2 | 32.5 | 1480 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170242.8519 | 9.9752 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-25 15:30 | 3.4 | 6.4 | 27.5 | 760 | 1120 | 800 | 0 | 800 | 0 | 0 | 170242.8519 | 9.9752 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-25 16:30 | 3.1 | 5.9 | 15 | 500 | 630 | 310 | 0 | 310 | 0 | 0 | 170242.8519 | 9.9752 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-25 17:30 | 2.3 | 5.3 | 170 | 340 | 420 | 100 | 0 | 100 | 0 | 0 | 170242.8519 | 9.9752 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-04-25 18:30 | 1.4 | 4.7 | 325 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 170131 | 9.9686 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-04-25 19:30 | 0.9 | 4.4 | 305 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 169726.5556 | 9.9449 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-04-25 20:30 | 0.5 | 4.4 | 287.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 169185.8148 | 9.9132 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-04-25 21:30 | 0 | 4.1 | 277.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 168645.0741 | 9.8815 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-04-25 22:30 | 0 | 3.9 | 272.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 168019.1481 | 9.8449 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-04-25 23:30 | 0.1 | 3 | 292.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167308.037 | 9.8032 | 0 |  |  | 1 | 7 | 1 | 1
Lerwick | 1978-04-26 00:30 | 0.1 | 1.7 | 195 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166596.9259 | 9.7615 | 0 |  |  | 1 | 8 | 1 | 2
Lerwick | 1978-04-26 01:30 | -0.5 | 1.7 | 130 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165885.8148 | 9.7199 | 0 |  |  | 1 | 9 | 1 | 3
Lerwick | 1978-04-26 02:30 | -0.9 | 2.1 | 197.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165174.7037 | 9.6782 | 0 |  |  | 1 | 10 | 1 | 4
Lerwick | 1978-04-26 03:30 | -0.4 | 2.1 | 202.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164463.5926 | 9.6365 | 0 |  |  | 1 | 11 | 1 | 5
Lerwick | 1978-04-26 04:30 | -0.3 | 2.6 | 182.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163752.4815 | 9.5949 | 0 |  |  | 1 | 12 | 1 | 6
Lerwick | 1978-04-26 05:30 | 0.1 | 3.5 | 160 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163041.3704 | 9.5532 | 0 |  |  | 1 | 13 | 1 | 7
Lerwick | 1978-04-26 06:30 | 1.2 | 4.1 | 145 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 162415.4444 | 9.5165 | 1 |  |  | 1 | 14 | 0 | 0
Lerwick | 1978-04-26 07:30 | 2.3 | 4.4 | 135 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 161874.7037 | 9.4848 | 1 |  |  | 1 | 15 | 0 | 0
Lerwick | 1978-04-26 08:30 | 3.6 | 4.5 | 127.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 161470.2593 | 9.4611 | 1 |  |  | 1 | 16 | 0 | 0
Lerwick | 1978-04-26 09:30 | 4.1 | 4.5 | 122.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 161202.1111 | 9.4454 | 1 |  |  | 1 | 17 | 0 | 0
Lerwick | 1978-04-26 10:30 | 4.6 | 4.7 | 115 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 160933.963 | 9.4297 | 1 |  |  | 1 | 18 | 0 | 0
Lerwick | 1978-04-26 11:30 | 5 | 5.1 | 102.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 160822.1111 | 9.4232 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-26 12:30 | 4.8 | 5.6 | 92.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 160872.1111 | 9.4261 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-26 13:30 | 5.1 | 6.1 | 87.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 161027.1111 | 9.4352 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-26 14:30 | 5.7 | 6.5 | 80 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 161337.1111 | 9.4533 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-26 15:30 | 5.7 | 6.3 | 77.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 161647.1111 | 9.4715 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-26 16:30 | 5.2 | 5.6 | 87.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 161802.1111 | 9.4806 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-26 17:30 | 4.9 | 5.5 | 97.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 161892.1111 | 9.4859 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-26 18:30 | 4.6 | 5.7 | 100 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 161982.1111 | 9.4911 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-26 19:30 | 4.1 | 5.5 | 100 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 162072.1111 | 9.4964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-26 20:30 | 3.8 | 5.2 | 100 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 162122.1111 | 9.4993 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-04-26 21:30 | 3.4 | 4.7 | 97.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 162010.2593 | 9.4928 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-04-26 22:30 | 2.7 | 4.7 | 90 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 161742.1111 | 9.4771 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-04-26 23:30 | 2.6 | 5.3 | 80 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 161630.2593 | 9.4705 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-27 00:30 | 2.8 | 5.3 | 70 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 161640.2593 | 9.4711 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-04-27 01:30 | 2.6 | 4.9 | 62.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 161528.4074 | 9.4646 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-04-27 02:30 | 2.7 | 5.1 | 55 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 161416.5556 | 9.458 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-27 03:30 | 2.9 | 5.6 | 45 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 161466.5556 | 9.4609 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-27 04:30 | 2.9 | 5.9 | 42.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 161556.5556 | 9.4662 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-27 05:30 | 2.4 | 5.8 | 50 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 161646.5556 | 9.4715 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-27 06:30 | 2.8 | 5.9 | 57.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 161736.5556 | 9.4768 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-27 07:30 | 3.8 | 6.3 | 60 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 161891.5556 | 9.4858 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-27 08:30 | 4.3 | 6.5 | 55 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 162201.5556 | 9.504 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-27 09:30 | 4.5 | 6.5 | 45 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 162601.5556 | 9.5274 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-27 10:30 | 3.9 | 6.3 | 40 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 162911.5556 | 9.5456 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-27 11:30 | 4.1 | 6.4 | 42.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 163131.5556 | 9.5585 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-27 12:30 | 4.9 | 6.9 | 47.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 163441.5556 | 9.5767 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-27 13:30 | 5 | 7.1 | 52.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 163931.5556 | 9.6054 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-27 14:30 | 5.3 | 6.4 | 60 | 760 | 1120 | 800 | 0 | 800 | 400 | 0 | 164331.5556 | 9.6288 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-27 15:30 | 5.5 | 5.4 | 72.5 | 340 | 550 | 230 | 0 | 230 | 115 | 0 | 164446.5556 | 9.6355 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-04-27 16:30 | 5.4 | 4.5 | 85 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 164334.7037 | 9.629 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-04-27 17:30 | 5.1 | 3.8 | 92.5 | 0 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 163845.0741 | 9.6003 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-04-27 18:30 | 4.6 | 3.4 | 97.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163133.963 | 9.5586 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-04-27 19:30 | 3.9 | 2.7 | 85 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162422.8519 | 9.517 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-04-27 20:30 | 3 | 1.9 | 67.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161711.7407 | 9.4753 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-04-27 21:30 | 2.3 | 2.4 | 77.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161000.6296 | 9.4336 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-04-27 22:30 | 2.4 | 3.5 | 90 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160289.5185 | 9.392 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-04-27 23:30 | 2.4 | 3.9 | 87.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 159578.4074 | 9.3503 | 0 |  |  | 1 | 9 | 1 | 6
Lerwick | 1978-04-28 00:30 | 2.3 | 3.9 | 82.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 158867.2963 | 9.3086 | 0 |  |  | 1 | 10 | 1 | 7
Lerwick | 1978-04-28 01:30 | 2.3 | 3.9 | 80 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 158156.1852 | 9.267 | 0 |  |  | 1 | 11 | 1 | 8
Lerwick | 1978-04-28 02:30 | 2.2 | 4.2 | 80 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 157530.2593 | 9.2303 | 1 |  |  | 1 | 12 | 0 | 0
Lerwick | 1978-04-28 03:30 | 2.4 | 4.5 | 80 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 157125.8148 | 9.2066 | 1 |  |  | 1 | 13 | 0 | 0
Lerwick | 1978-04-28 04:30 | 2.7 | 4.7 | 80 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 156857.6667 | 9.1909 | 1 |  |  | 1 | 14 | 0 | 0
Lerwick | 1978-04-28 05:30 | 3 | 5.3 | 77.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 156745.8148 | 9.1843 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-28 06:30 | 3.6 | 6.2 | 72.5 | 760 | 550 | 230 | 0 | 230 | 115 | 0 | 156860.8148 | 9.1911 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-28 07:30 | 4.4 | 7.1 | 70 | 1480 | 1120 | 800 | 0 | 800 | 400 | 0 | 157260.8148 | 9.2145 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-28 08:30 | 5.3 | 7.8 | 67.5 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 157905.8148 | 9.2523 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-28 09:30 | 5.8 | 8.3 | 62.5 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 158550.8148 | 9.2901 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-28 10:30 | 5.7 | 8.2 | 60 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 159195.8148 | 9.3279 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-28 11:30 | 5.3 | 7.7 | 62.5 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 159840.8148 | 9.3657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-28 12:30 | 5.6 | 7.3 | 67.5 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 160485.8148 | 9.4035 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-28 13:30 | 6.6 | 6.8 | 82.5 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 160975.8148 | 9.4322 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-28 14:30 | 6.4 | 5.9 | 110 | 500 | 810 | 490 | 0 | 490 | 245 | 0 | 161220.8148 | 9.4465 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-28 15:30 | 6.2 | 5.1 | 122.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 161270.8148 | 9.4495 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-04-28 16:30 | 6.6 | 4.7 | 115 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 161158.963 | 9.4429 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-04-28 17:30 | 6.2 | 4.5 | 110 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 160890.8148 | 9.4272 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-04-28 18:30 | 5.5 | 4.4 | 107.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 160486.3704 | 9.4035 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-04-28 19:30 | 4.7 | 4.1 | 102.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 159945.6296 | 9.3718 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-04-28 20:30 | 3.9 | 3.7 | 100 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 159319.7037 | 9.3351 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-04-28 21:30 | 3.5 | 3.4 | 100 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 158608.5926 | 9.2935 | 0 |  |  | 1 | 7 | 1 | 1
Lerwick | 1978-04-28 22:30 | 3.4 | 2.7 | 100 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 157897.4815 | 9.2518 | 0 |  |  | 1 | 8 | 1 | 2
Lerwick | 1978-04-28 23:30 | 3.1 | 1.5 | 75 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 157186.3704 | 9.2101 | 0 |  |  | 1 | 9 | 1 | 3
Lerwick | 1978-04-29 00:30 | 2.8 | 0.4 | 25 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 156475.2593 | 9.1685 | 0 |  |  | 1 | 10 | 1 | 4
Lerwick | 1978-04-29 01:30 | 2.4 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 155764.1481 | 9.1268 | 0 |  |  | 1 | 11 | 1 | 5
Lerwick | 1978-04-29 02:30 | 2.3 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 155053.037 | 9.0851 | 0 |  |  | 1 | 12 | 1 | 6
Lerwick | 1978-04-29 03:30 | 1.9 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 154341.9259 | 9.0435 | 0 |  |  | 1 | 13 | 1 | 7
Lerwick | 1978-04-29 04:30 | 1.1 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 153630.8148 | 9.0018 | 0 |  |  | 1 | 14 | 1 | 8
Lerwick | 1978-04-29 05:30 | 0.5 | 0.4 | 10 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 152919.7037 | 8.9601 | 0 |  |  | 1 | 15 | 1 | 9
Lerwick | 1978-04-29 06:30 | 2 | 1.7 | 30 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 152208.5926 | 8.9185 | 0 |  |  | 1 | 16 | 1 | 10
Lerwick | 1978-04-29 07:30 | 4.1 | 3.5 | 42.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 151497.4815 | 8.8768 | 0 |  |  | 1 | 17 | 1 | 11
Lerwick | 1978-04-29 08:30 | 5 | 4.9 | 50 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 151007.8519 | 8.8481 | 1 |  |  | 1 | 18 | 0 | 0
Lerwick | 1978-04-29 09:30 | 5.7 | 5.1 | 57.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 150896 | 8.8416 | 1 |  |  | 1 | 19 | 0 | 0
Lerwick | 1978-04-29 10:30 | 5.8 | 4.6 | 62.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 150784.1481 | 8.835 | 1 |  |  | 1 | 20 | 0 | 0
Lerwick | 1978-04-29 11:30 | 5.8 | 4.2 | 67.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 150379.7037 | 8.8113 | 1 |  |  | 1 | 21 | 0 | 0
Lerwick | 1978-04-29 12:30 | 6 | 3.9 | 70 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 149753.7778 | 8.7746 | 1 |  |  | 1 | 22 | 0 | 0
Lerwick | 1978-04-29 13:30 | 6.5 | 3.7 | 72.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 149042.6667 | 8.733 | 0 |  |  | 1 | 23 | 1 | 1
Lerwick | 1978-04-29 14:30 | 6.9 | 3.4 | 75 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 148331.5556 | 8.6913 | 0 |  |  | 1 | 24 | 1 | 2
Lerwick | 1978-04-29 15:30 | 6.8 | 3 | 72.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 147620.4444 | 8.6496 | 0 |  |  | 1 | 25 | 1 | 3
Lerwick | 1978-04-29 16:30 | 6.3 | 2.6 | 80 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 146909.3333 | 8.608 | 0 |  |  | 1 | 26 | 1 | 4
Lerwick | 1978-04-29 17:30 | 5.9 | 2.6 | 100 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 146198.2222 | 8.5663 | 0 |  |  | 1 | 27 | 1 | 5
Lerwick | 1978-04-29 18:30 | 5.7 | 2.4 | 107.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 145487.1111 | 8.5246 | 0 |  |  | 1 | 28 | 1 | 6
Lerwick | 1978-04-29 19:30 | 5 | 2 | 95 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 144776 | 8.483 | 0 |  |  | 1 | 29 | 1 | 7
Lerwick | 1978-04-29 20:30 | 3.8 | 1.5 | 42.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 144064.8889 | 8.4413 | 0 |  |  | 1 | 30 | 1 | 8
Lerwick | 1978-04-29 21:30 | 2.9 | 1.4 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 143353.7778 | 8.3996 | 0 |  |  | 1 | 31 | 1 | 9
Lerwick | 1978-04-29 22:30 | 2.6 | 1.5 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 142642.6667 | 8.358 | 0 |  |  | 1 | 32 | 1 | 10
Lerwick | 1978-04-29 23:30 | 2.5 | 1.8 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 141931.5556 | 8.3163 | 0 |  |  | 1 | 33 | 1 | 11
Lerwick | 1978-04-30 00:30 | 2.7 | 2.1 | 22.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 141220.4444 | 8.2746 | 0 |  |  | 1 | 34 | 1 | 12
Lerwick | 1978-04-30 01:30 | 2.4 | 1.7 | 27.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 140509.3333 | 8.233 | 0 |  |  | 1 | 35 | 1 | 13
Lerwick | 1978-04-30 02:30 | 2.1 | 1.1 | 7.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 139798.2222 | 8.1913 | 0 |  |  | 1 | 36 | 1 | 14
Lerwick | 1978-04-30 03:30 | 2.2 | 1 | 12.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 139087.1111 | 8.1496 | 0 |  |  | 1 | 37 | 1 | 15
Lerwick | 1978-04-30 04:30 | 2 | 1 | 30 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 138376 | 8.108 | 0 |  |  | 1 | 38 | 1 | 16
Lerwick | 1978-04-30 05:30 | 2 | 1.8 | 45 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 137664.8889 | 8.0663 | 0 |  |  | 1 | 39 | 1 | 17
Lerwick | 1978-04-30 06:30 | 2.7 | 3.7 | 55 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 136953.7778 | 8.0246 | 0 |  |  | 1 | 40 | 1 | 18
Lerwick | 1978-04-30 07:30 | 4.4 | 5.4 | 57.5 | 340 | 170 | 0 | 150 | 0 | 0 | 333.3333 | 136620.4444 | 8.0051 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-30 08:30 | 5.9 | 6.1 | 50 | 760 | 550 | 230 | 0 | 230 | 115 | 0 | 136735.4444 | 8.0118 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-30 09:30 | 6.6 | 6.7 | 45 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 137045.4444 | 8.03 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-30 10:30 | 6.9 | 7 | 45 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 137535.4444 | 8.0587 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-30 11:30 | 7.2 | 7 | 45 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 138115.4444 | 8.0927 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-30 12:30 | 7.8 | 7.1 | 50 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 138695.4444 | 8.1267 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-30 13:30 | 7.8 | 7.2 | 57.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 139275.4444 | 8.1607 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-30 14:30 | 7.5 | 7.2 | 62.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 139855.4444 | 8.1947 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-30 15:30 | 7.4 | 6.9 | 67.5 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 140345.4444 | 8.2234 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-30 16:30 | 7.3 | 6 | 70 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 140655.4444 | 8.2415 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-30 17:30 | 6.6 | 5.1 | 67.5 | 340 | 550 | 230 | 0 | 230 | 115 | 0 | 140770.4444 | 8.2483 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-04-30 18:30 | 6.2 | 4.9 | 62.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 140658.5926 | 8.2417 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-04-30 19:30 | 5.8 | 5 | 60 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 140546.7407 | 8.2352 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-30 20:30 | 5 | 5.2 | 60 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 140556.7407 | 8.2357 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-04-30 21:30 | 4.5 | 5.2 | 60 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 140566.7407 | 8.2363 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-04-30 22:30 | 4.2 | 4.7 | 57.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 140454.8889 | 8.2298 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-04-30 23:30 | 3.9 | 4 | 50 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 140050.4444 | 8.2061 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-05-01 00:30 | 3.5 | 3.4 | 42.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 139424.5185 | 8.1694 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-05-01 01:30 | 3.2 | 3.6 | 40 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 138713.4074 | 8.1277 | 0 |  |  | 1 | 5 | 1 | 1
Lerwick | 1978-05-01 02:30 | 3.4 | 4.4 | 40 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 138087.4815 | 8.0911 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-05-01 03:30 | 3.5 | 5.1 | 40 | 340 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 137839.3333 | 8.0765 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-01 04:30 | 3.6 | 5.6 | 42.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 137889.3333 | 8.0795 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-01 05:30 | 4 | 6.1 | 47.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 138044.3333 | 8.0885 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-01 06:30 | 4.2 | 6.7 | 50 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 138354.3333 | 8.1067 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-01 07:30 | 5.1 | 7.1 | 50 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 138844.3333 | 8.1354 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-01 08:30 | 5.8 | 7.2 | 50 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 139424.3333 | 8.1694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-01 09:30 | 6.3 | 7.2 | 50 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 140004.3333 | 8.2034 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-01 10:30 | 6.6 | 7.2 | 50 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 140584.3333 | 8.2374 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-01 11:30 | 6.7 | 7.1 | 52.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 141164.3333 | 8.2713 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-01 12:30 | 7 | 6.6 | 55 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 141654.3333 | 8.3001 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-01 13:30 | 7.1 | 5.9 | 50 | 500 | 810 | 490 | 0 | 490 | 245 | 0 | 141899.3333 | 8.3144 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-01 14:30 | 6.7 | 5.5 | 42.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 141989.3333 | 8.3197 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-01 15:30 | 6.7 | 5.2 | 42.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 142039.3333 | 8.3226 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-01 16:30 | 6.4 | 5 | 45 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 142049.3333 | 8.3232 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-01 17:30 | 5.8 | 5.2 | 35 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 142059.3333 | 8.3238 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-01 18:30 | 5.3 | 5.4 | 20 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 142069.3333 | 8.3244 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-05-01 19:30 | 4.9 | 4.9 | 10 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 141957.4815 | 8.3178 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-05-01 20:30 | 4.2 | 4.7 | 180 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 141689.3333 | 8.3021 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-05-01 21:30 | 3.4 | 5.1 | 355 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 141577.4815 | 8.2956 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-01 22:30 | 2.6 | 5.5 | 352.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 141627.4815 | 8.2985 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-01 23:30 | 1.7 | 5.3 | 352.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 141677.4815 | 8.3014 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-05-02 00:30 | 1.4 | 4.4 | 182.5 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 141429.3333 | 8.2869 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-05-02 01:30 | 2.2 | 3.9 | 10 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 140803.4074 | 8.2502 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-05-02 02:30 | 2.9 | 3.9 | 182.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 140092.2963 | 8.2085 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-05-02 03:30 | 2.7 | 4.1 | 355 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 139466.3704 | 8.1719 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-05-02 04:30 | 2.6 | 4.4 | 355 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 138925.6296 | 8.1402 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-05-02 05:30 | 2.4 | 4.2 | 180 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 138384.8889 | 8.1085 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-05-02 06:30 | 2.4 | 4 | 15 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 137844.1481 | 8.0768 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-05-02 07:30 | 3.3 | 4.2 | 25 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 137303.4074 | 8.0451 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-05-02 08:30 | 4.6 | 4.7 | 27.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 136898.963 | 8.0214 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-05-02 09:30 | 4.8 | 5.2 | 35 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 136787.1111 | 8.0149 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-02 10:30 | 5.3 | 5.5 | 40 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 136837.1111 | 8.0178 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-02 11:30 | 6.4 | 5.5 | 42.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 136927.1111 | 8.0231 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-02 12:30 | 6.3 | 5.4 | 50 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 136977.1111 | 8.026 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-02 13:30 | 6.4 | 5.1 | 52.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 136987.1111 | 8.0266 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-05-02 14:30 | 6.5 | 4.6 | 45 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 136875.2593 | 8.02 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-05-02 15:30 | 6.3 | 4.4 | 45 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 136470.8148 | 7.9963 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-05-02 16:30 | 6.1 | 4.4 | 55 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 135930.0741 | 7.9647 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-05-02 17:30 | 5.6 | 4 | 60 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 135389.3333 | 7.933 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-05-02 18:30 | 5.3 | 3.3 | 57.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 134763.4074 | 7.8963 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-05-02 19:30 | 5 | 2.9 | 55 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 134052.2963 | 7.8546 | 0 |  |  | 1 | 7 | 1 | 1
Lerwick | 1978-05-02 20:30 | 4.7 | 2.4 | 50 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 133341.1852 | 7.813 | 0 |  |  | 1 | 8 | 1 | 2
Lerwick | 1978-05-02 21:30 | 4.2 | 1.8 | 22.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 132630.0741 | 7.7713 | 0 |  |  | 1 | 9 | 1 | 3
Lerwick | 1978-05-02 22:30 | 4.1 | 1.2 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 131918.963 | 7.7296 | 0 |  |  | 1 | 10 | 1 | 4
Lerwick | 1978-05-02 23:30 | 4.1 | 0.7 | 25 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 131207.8519 | 7.688 | 0 |  |  | 1 | 11 | 1 | 5
Lerwick | 1978-05-03 00:30 | 3.9 | 0.2 | 25 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 130496.7407 | 7.6463 | 0 |  |  | 1 | 12 | 1 | 6
Lerwick | 1978-05-03 01:30 | 3.9 | 0.2 | 170 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 129785.6296 | 7.6046 | 0 |  |  | 1 | 13 | 1 | 7
Lerwick | 1978-05-03 02:30 | 3.6 | 0.7 | 327.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 129074.5185 | 7.563 | 0 |  |  | 1 | 14 | 1 | 8
Lerwick | 1978-05-03 03:30 | 3.3 | 0.7 | 325 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 128363.4074 | 7.5213 | 0 |  |  | 1 | 15 | 1 | 9
Lerwick | 1978-05-03 04:30 | 3.5 | 0.7 | 207.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 127652.2963 | 7.4796 | 0 |  |  | 1 | 16 | 1 | 10
Lerwick | 1978-05-03 05:30 | 3.6 | 1.6 | 120 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 126941.1852 | 7.438 | 0 |  |  | 1 | 17 | 1 | 11
Lerwick | 1978-05-03 06:30 | 3.9 | 2.6 | 160 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 126230.0741 | 7.3963 | 0 |  |  | 1 | 18 | 1 | 12
Lerwick | 1978-05-03 07:30 | 4.5 | 3.5 | 157.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 125518.963 | 7.3546 | 0 |  |  | 1 | 19 | 1 | 13
Lerwick | 1978-05-03 08:30 | 5 | 4.1 | 152.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 124893.037 | 7.318 | 1 |  |  | 1 | 20 | 0 | 0
Lerwick | 1978-05-03 09:30 | 5.6 | 4.6 | 152.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 124488.5926 | 7.2943 | 1 |  |  | 1 | 21 | 0 | 0
Lerwick | 1978-05-03 10:30 | 6.3 | 5.1 | 157.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 124376.7407 | 7.2877 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-03 11:30 | 6.7 | 5.4 | 160 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 124386.7407 | 7.2883 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-03 12:30 | 6.3 | 5.1 | 157.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 124396.7407 | 7.2889 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-05-03 13:30 | 6.3 | 4.9 | 152.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 124284.8889 | 7.2823 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-05-03 14:30 | 6.6 | 4.9 | 155 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 124016.7407 | 7.2666 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-05-03 15:30 | 6.3 | 4.9 | 162.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 123748.5926 | 7.2509 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-05-03 16:30 | 5.7 | 4.7 | 162.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 123480.4444 | 7.2352 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-05-03 17:30 | 5.7 | 4.4 | 157.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 123076 | 7.2115 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-05-03 18:30 | 5.7 | 4.1 | 150 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 122535.2593 | 7.1798 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-05-03 19:30 | 5 | 3.9 | 140 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 121909.3333 | 7.1431 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-05-03 20:30 | 4.1 | 3.9 | 127.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 121198.2222 | 7.1015 | 0 |  |  | 1 | 9 | 1 | 1
Lerwick | 1978-05-03 21:30 | 3.8 | 4.2 | 117.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 120572.2963 | 7.0648 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-05-03 22:30 | 3.9 | 4.7 | 115 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 120167.8519 | 7.0411 | 1 |  |  | 1 | 11 | 0 | 0
Lerwick | 1978-05-03 23:30 | 4.1 | 4.9 | 115 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 119899.7037 | 7.0254 | 1 |  |  | 1 | 12 | 0 | 0
Lerwick | 1978-05-04 00:30 | 4.4 | 5.3 | 115 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 119787.8519 | 7.0188 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-04 01:30 | 4.6 | 5.7 | 115 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 119837.8519 | 7.0217 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-04 02:30 | 4.8 | 5.7 | 117.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 119927.8519 | 7.027 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-04 03:30 | 4.8 | 5.7 | 117.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 120017.8519 | 7.0323 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-04 04:30 | 4.7 | 5.5 | 112.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 120107.8519 | 7.0376 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-04 05:30 | 4.6 | 5.4 | 112.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 120157.8519 | 7.0405 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-04 06:30 | 4.5 | 5.5 | 115 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 120207.8519 | 7.0434 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-04 07:30 | 4.4 | 5.8 | 107.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 120297.8519 | 7.0487 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-04 08:30 | 4.6 | 6.5 | 95 | 1120 | 810 | 490 | 0 | 490 | 245 | 0 | 120542.8519 | 7.0631 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-04 09:30 | 4.8 | 7.8 | 90 | 1840 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 121122.8519 | 7.097 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-04 10:30 | 5.5 | 8.9 | 90 | 2560 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 121767.8519 | 7.1348 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-04 11:30 | 6.5 | 9.6 | 95 | 3280 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 122412.8519 | 7.1726 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-04 12:30 | 6.8 | 9.9 | 105 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 123057.8519 | 7.2104 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-04 13:30 | 6.6 | 9.5 | 105 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 123702.8519 | 7.2482 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-04 14:30 | 6.2 | 9.1 | 95 | 2920 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 124347.8519 | 7.286 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-04 15:30 | 5.4 | 8.9 | 90 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 124992.8519 | 7.3238 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-04 16:30 | 4.7 | 8.6 | 90 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 125637.8519 | 7.3616 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-04 17:30 | 4.7 | 8.6 | 87.5 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 126282.8519 | 7.3994 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-04 18:30 | 4.8 | 8.9 | 85 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 126927.8519 | 7.4372 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-04 19:30 | 5 | 8.9 | 87.5 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 127572.8519 | 7.475 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-04 20:30 | 5.2 | 8.4 | 90 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 128217.8519 | 7.5128 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-04 21:30 | 5.5 | 7.8 | 90 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 128862.8519 | 7.5506 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-04 22:30 | 5.6 | 7.3 | 87.5 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 129507.8519 | 7.5884 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-04 23:30 | 5.5 | 7.3 | 80 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 130087.8519 | 7.6223 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-05 00:30 | 5.5 | 7.1 | 75 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 130667.8519 | 7.6563 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-05 01:30 | 5.5 | 6.3 | 75 | 760 | 1120 | 800 | 0 | 800 | 400 | 0 | 131067.8519 | 7.6798 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-05 02:30 | 5.5 | 6.1 | 70 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 131287.8519 | 7.6926 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-05 03:30 | 5.5 | 6.7 | 62.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 131597.8519 | 7.7108 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-05 04:30 | 5.4 | 7.1 | 60 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 132087.8519 | 7.7395 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-05 05:30 | 5.4 | 7.3 | 60 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 132667.8519 | 7.7735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-05 06:30 | 5.7 | 7.6 | 60 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 133312.8519 | 7.8113 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-05 07:30 | 6 | 7.7 | 60 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 133957.8519 | 7.8491 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-05 08:30 | 6.2 | 7.9 | 57.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 134602.8519 | 7.8869 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-05 09:30 | 6.4 | 8.5 | 52.5 | 2560 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 135247.8519 | 7.9247 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-05 10:30 | 6.6 | 9.2 | 50 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 135892.8519 | 7.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-05 11:30 | 7.1 | 9.7 | 50 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 136537.8519 | 8.0003 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-05 12:30 | 7.4 | 10.1 | 50 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 137182.8519 | 8.0381 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-05 13:30 | 7.5 | 10.1 | 50 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 137827.8519 | 8.0759 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-05 14:30 | 7.3 | 9.9 | 50 | 3280 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 138472.8519 | 8.1136 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-05 15:30 | 6.8 | 9.4 | 50 | 2920 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 139117.8519 | 8.1514 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-05 16:30 | 6.7 | 8.3 | 50 | 2200 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 139762.8519 | 8.1892 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-05 17:30 | 6.5 | 7.3 | 52.5 | 1480 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 140407.8519 | 8.227 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-05 18:30 | 6.5 | 6.8 | 60 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 140897.8519 | 8.2557 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-05 19:30 | 6.5 | 6.8 | 67.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 141297.8519 | 8.2792 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-05 20:30 | 6.4 | 7.1 | 67.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 141787.8519 | 8.3079 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-05 21:30 | 6.2 | 7.1 | 60 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 142367.8519 | 8.3419 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-05 22:30 | 6 | 6.7 | 55 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 142857.8519 | 8.3706 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-05 23:30 | 5.9 | 6.5 | 57.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 143257.8519 | 8.394 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-06 00:30 | 5.8 | 6.7 | 60 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 143657.8519 | 8.4175 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-06 01:30 | 5.6 | 6.5 | 57.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 144057.8519 | 8.4409 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-06 02:30 | 5.6 | 6.5 | 55 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 144457.8519 | 8.4643 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-06 03:30 | 5.7 | 6.8 | 57.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 144857.8519 | 8.4878 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-06 04:30 | 5.6 | 7.1 | 60 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 145347.8519 | 8.5165 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-06 05:30 | 5.5 | 7.1 | 60 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 145927.8519 | 8.5505 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-06 06:30 | 5.6 | 6.7 | 60 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 146417.8519 | 8.5792 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-06 07:30 | 6.1 | 6 | 55 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 146727.8519 | 8.5973 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-06 08:30 | 6.5 | 5.5 | 47.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 146882.8519 | 8.6064 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-06 09:30 | 7 | 5.6 | 50 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 146972.8519 | 8.6117 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-06 10:30 | 8.2 | 6.4 | 57.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 147127.8519 | 8.6208 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-06 11:30 | 8.8 | 7.2 | 62.5 | 1480 | 1120 | 800 | 0 | 800 | 400 | 0 | 147527.8519 | 8.6442 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-06 12:30 | 8.9 | 7.2 | 67.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 148107.8519 | 8.6782 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-06 13:30 | 9.3 | 7 | 70 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 148687.8519 | 8.7122 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-06 14:30 | 9.5 | 7 | 72.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 149267.8519 | 8.7462 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-06 15:30 | 9.3 | 6.8 | 80 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 149757.8519 | 8.7749 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-06 16:30 | 8.8 | 6.2 | 85 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 150067.8519 | 8.793 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-06 17:30 | 8.5 | 4.8 | 75 | 199.3333 | 479.6667 | 159.6667 | 0 | 159.6667 | 79.8333 | 0 | 150147.6852 | 8.7977 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-05-06 18:30 | 8.1 | 3.9 | 55 | 0 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 149658.0556 | 8.769 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-05-06 19:30 | 7.5 | 4.2 | 52.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 149032.1296 | 8.7324 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-05-06 20:30 | 7.3 | 4.2 | 47.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 148491.3889 | 8.7007 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-05-06 21:30 | 7.5 | 3 | 195 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 147865.463 | 8.664 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-05-06 22:30 | 6.5 | 2.4 | 352.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 147154.3519 | 8.6223 | 0 |  |  | 1 | 6 | 1 | 1
Lerwick | 1978-05-06 23:30 | 5.2 | 2.9 | 192.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 146443.2407 | 8.5807 | 0 |  |  | 1 | 7 | 1 | 2
Lerwick | 1978-05-07 00:30 | 5.3 | 3.3 | 42.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 145732.1296 | 8.539 | 0 |  |  | 1 | 8 | 1 | 3
Lerwick | 1978-05-07 01:30 | 6.2 | 3.4 | 32.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 145021.0185 | 8.4973 | 0 |  |  | 1 | 9 | 1 | 4
Lerwick | 1978-05-07 02:30 | 5.8 | 3.8 | 20 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 144309.9074 | 8.4557 | 0 |  |  | 1 | 10 | 1 | 5
Lerwick | 1978-05-07 03:30 | 5.3 | 4 | 27.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 143683.9815 | 8.419 | 1 |  |  | 1 | 11 | 0 | 0
Lerwick | 1978-05-07 04:30 | 5.6 | 3.5 | 30 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 143058.0556 | 8.3823 | 1 |  |  | 1 | 12 | 0 | 0
Lerwick | 1978-05-07 05:30 | 5.7 | 2.9 | 35 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 142346.9444 | 8.3406 | 0 |  |  | 1 | 13 | 1 | 1
Lerwick | 1978-05-07 06:30 | 6.4 | 3.3 | 45 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 141635.8333 | 8.299 | 0 |  |  | 1 | 14 | 1 | 2
Lerwick | 1978-05-07 07:30 | 7.6 | 3.9 | 50 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 140924.7222 | 8.2573 | 0 |  |  | 1 | 15 | 1 | 3
Lerwick | 1978-05-07 08:30 | 8.8 | 4.2 | 55 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 140298.7963 | 8.2206 | 1 |  |  | 1 | 16 | 0 | 0
Lerwick | 1978-05-07 09:30 | 9.7 | 4.7 | 67.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 139894.3519 | 8.1969 | 1 |  |  | 1 | 17 | 0 | 0
Lerwick | 1978-05-07 10:30 | 11 | 4.7 | 90 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 139626.2037 | 8.1812 | 1 |  |  | 1 | 18 | 0 | 0
Lerwick | 1978-05-07 11:30 | 11.6 | 4.4 | 120 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 139221.7593 | 8.1575 | 1 |  |  | 1 | 19 | 0 | 0
Lerwick | 1978-05-07 12:30 | 11.2 | 4.4 | 140 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 138681.0185 | 8.1258 | 1 |  |  | 1 | 20 | 0 | 0
Lerwick | 1978-05-07 13:30 | 11 | 4.5 | 147.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 138276.5741 | 8.1021 | 1 |  |  | 1 | 21 | 0 | 0
Lerwick | 1978-05-07 14:30 | 11 | 4.4 | 150 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 137872.1296 | 8.0784 | 1 |  |  | 1 | 22 | 0 | 0
Lerwick | 1978-05-07 15:30 | 10.7 | 4.1 | 150 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 137331.3889 | 8.0468 | 1 |  |  | 1 | 23 | 0 | 0
Lerwick | 1978-05-07 16:30 | 10.7 | 3.6 | 150 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 136705.463 | 8.0101 | 1 |  |  | 1 | 24 | 0 | 0
Lerwick | 1978-05-07 17:30 | 10.6 | 3 | 145 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 135994.3519 | 7.9684 | 0 |  |  | 1 | 25 | 1 | 1
Lerwick | 1978-05-07 18:30 | 9.9 | 2.4 | 132.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 135283.2407 | 7.9268 | 0 |  |  | 1 | 26 | 1 | 2
Lerwick | 1978-05-07 19:30 | 9.5 | 1.7 | 107.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 134572.1296 | 7.8851 | 0 |  |  | 1 | 27 | 1 | 3
Lerwick | 1978-05-07 20:30 | 8.9 | 1.1 | 92.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 133861.0185 | 7.8434 | 0 |  |  | 1 | 28 | 1 | 4
Lerwick | 1978-05-07 21:30 | 8 | 1.6 | 112.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 133149.9074 | 7.8018 | 0 |  |  | 1 | 29 | 1 | 5
Lerwick | 1978-05-07 22:30 | 7 | 2.7 | 130 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 132438.7963 | 7.7601 | 0 |  |  | 1 | 30 | 1 | 6
Lerwick | 1978-05-07 23:30 | 7 | 3.3 | 130 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 131727.6852 | 7.7184 | 0 |  |  | 1 | 31 | 1 | 7
Lerwick | 1978-05-08 00:30 | 7.1 | 3.6 | 132.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 131016.5741 | 7.6768 | 0 |  |  | 1 | 32 | 1 | 8
Lerwick | 1978-05-08 01:30 | 7.3 | 3.3 | 140 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 130305.463 | 7.6351 | 0 |  |  | 1 | 33 | 1 | 9
Lerwick | 1978-05-08 02:30 | 7.4 | 2 | 187.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 129594.3519 | 7.5934 | 0 |  |  | 1 | 34 | 1 | 10
Lerwick | 1978-05-08 03:30 | 6.3 | 1.1 | 275 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 128883.2407 | 7.5518 | 0 |  |  | 1 | 35 | 1 | 11
Lerwick | 1978-05-08 04:30 | 5.3 | 1 | 335 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 128172.1296 | 7.5101 | 0 |  |  | 1 | 36 | 1 | 12
Lerwick | 1978-05-08 05:30 | 5.2 | 1 | 182.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 127461.0185 | 7.4684 | 0 |  |  | 1 | 37 | 1 | 13
Lerwick | 1978-05-08 06:30 | 7 | 1.8 | 22.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 126749.9074 | 7.4268 | 0 |  |  | 1 | 38 | 1 | 14
Lerwick | 1978-05-08 07:30 | 9.2 | 3.3 | 35 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 126038.7963 | 7.3851 | 0 |  |  | 1 | 39 | 1 | 15
Lerwick | 1978-05-08 08:30 | 9.6 | 4.5 | 37.5 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 125549.1667 | 7.3564 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-08 09:30 | 10.1 | 5.8 | 32.5 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 125564 | 7.3573 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-08 10:30 | 11.7 | 7.1 | 30 | 1480 | 990 | 670 | 0 | 670 | 335 | 0 | 125899 | 7.3769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-08 11:30 | 11.7 | 7.5 | 30 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 126544 | 7.4147 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-08 12:30 | 10.7 | 7.2 | 30 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 127189 | 7.4525 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-08 13:30 | 11 | 6.7 | 30 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 127679 | 7.4812 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-08 14:30 | 10.9 | 6.3 | 30 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 127989 | 7.4994 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-08 15:30 | 10 | 6.3 | 30 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 128209 | 7.5122 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-08 16:30 | 9.1 | 6.5 | 30 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 128519 | 7.5304 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-08 17:30 | 8.3 | 6.5 | 27.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 128919 | 7.5538 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-08 18:30 | 8.1 | 6.3 | 22.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 129229 | 7.572 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-08 19:30 | 7.8 | 6.2 | 20 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 129449 | 7.5849 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-08 20:30 | 7 | 6.2 | 17.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 129669 | 7.5978 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-08 21:30 | 6.1 | 6.3 | 12.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 129889 | 7.6107 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-08 22:30 | 5.5 | 6.5 | 7.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 130199 | 7.6288 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-08 23:30 | 5.2 | 6.8 | 2.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 130599 | 7.6523 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-09 00:30 | 4.5 | 7.2 | 0 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 131089 | 7.681 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-09 01:30 | 4 | 7.7 | 0 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 131734 | 7.7188 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-09 02:30 | 4.2 | 8 | 2.5 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 132379 | 7.7566 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-09 03:30 | 5.2 | 8.1 | 7.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 133024 | 7.7944 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-09 04:30 | 6.2 | 8.3 | 10 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 133669 | 7.8322 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-09 05:30 | 6.6 | 8.6 | 12.5 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 134314 | 7.87 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-09 06:30 | 7.4 | 8.9 | 17.5 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 134959 | 7.9078 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-09 07:30 | 8.5 | 9.1 | 20 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 135604 | 7.9455 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-09 08:30 | 9.6 | 9 | 22.5 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 136249 | 7.9833 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-09 09:30 | 10.5 | 8.6 | 27.5 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 136894 | 8.0211 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-09 10:30 | 11 | 8.6 | 30 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 137539 | 8.0589 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-09 11:30 | 11.4 | 8.4 | 30 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 138184 | 8.0967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-09 12:30 | 11.9 | 7.9 | 30 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 138829 | 8.1345 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-09 13:30 | 12 | 7.6 | 30 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 139474 | 8.1723 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-09 14:30 | 12.6 | 7.2 | 27.5 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 140119 | 8.2101 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-09 15:30 | 12.7 | 6.8 | 25 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 140609 | 8.2388 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-09 16:30 | 11.5 | 6.8 | 27.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 141009 | 8.2622 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-09 17:30 | 10.3 | 7 | 30 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 141499 | 8.291 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-09 18:30 | 8.8 | 6.8 | 30 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 141989 | 8.3197 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-09 19:30 | 7.5 | 6.8 | 30 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 142389 | 8.3431 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-09 20:30 | 6.7 | 7.2 | 27.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 142879 | 8.3718 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-09 21:30 | 6.4 | 7.3 | 22.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 143459 | 8.4058 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-09 22:30 | 6.4 | 6.9 | 20 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 143949 | 8.4345 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-09 23:30 | 6.3 | 6.4 | 22.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 144259 | 8.4527 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-10 00:30 | 6.1 | 5.8 | 22.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 144414 | 8.4618 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-10 01:30 | 5.8 | 5.1 | 15 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 144464 | 8.4647 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-05-10 02:30 | 5.3 | 4.4 | 7.5 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 144215.8519 | 8.4501 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-05-10 03:30 | 5 | 3.8 | 7.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 143589.9259 | 8.4135 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-05-10 04:30 | 5.4 | 3.7 | 17.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 142878.8148 | 8.3718 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-05-10 05:30 | 5.8 | 3.9 | 30 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 142167.7037 | 8.3301 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-05-10 06:30 | 6 | 3.9 | 37.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 141456.5926 | 8.2885 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-05-10 07:30 | 6.6 | 3.6 | 47.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 140745.4815 | 8.2468 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-05-10 08:30 | 7.3 | 3.3 | 70 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 140034.3704 | 8.2051 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-05-10 09:30 | 7.9 | 3.6 | 102.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 139323.2593 | 8.1635 | 0 |  |  | 1 | 9 | 1 | 6
Lerwick | 1978-05-10 10:30 | 8.4 | 4.4 | 135 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 138697.3333 | 8.1268 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-05-10 11:30 | 8.6 | 5.3 | 157.5 | 340 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 138449.1852 | 8.1123 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-10 12:30 | 8.4 | 6.2 | 167.5 | 760 | 550 | 230 | 0 | 230 | 115 | 0 | 138564.1852 | 8.119 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-10 13:30 | 9.1 | 7.1 | 170 | 1480 | 1120 | 800 | 0 | 800 | 400 | 0 | 138964.1852 | 8.1424 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-10 14:30 | 9.5 | 7.6 | 172.5 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 139609.1852 | 8.1802 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-10 15:30 | 9.1 | 7.7 | 177.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 140254.1852 | 8.218 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-10 16:30 | 8.4 | 7.7 | 182.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 140899.1852 | 8.2558 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-10 17:30 | 7.8 | 7.8 | 185 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 141544.1852 | 8.2936 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-10 18:30 | 7.5 | 8 | 182.5 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 142189.1852 | 8.3314 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-10 19:30 | 7.4 | 7.8 | 177.5 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 142834.1852 | 8.3692 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-10 20:30 | 7.2 | 7.8 | 172.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 143479.1852 | 8.407 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-10 21:30 | 7.2 | 8.2 | 170 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 144124.1852 | 8.4448 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-10 22:30 | 7.2 | 8.5 | 172.5 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 144769.1852 | 8.4826 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-10 23:30 | 7.1 | 8.6 | 177.5 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 145414.1852 | 8.5204 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-11 00:30 | 6.9 | 9.3 | 180 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 146059.1852 | 8.5582 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-11 01:30 | 6.8 | 10.3 | 180 | 3640 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 146704.1852 | 8.5959 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-11 02:30 | 6.7 | 11.1 | 180 | 4300 | 3970 | 3650 | 0 | 1290 | 645 | 0 | 147349.1852 | 8.6337 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-11 03:30 | 6.6 | 11.9 | 180 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 147994.1852 | 8.6715 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-11 04:30 | 6.5 | 12.6 | 180 | 4600 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 148639.1852 | 8.7093 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-11 05:30 | 6.4 | 12.7 | 180 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 149284.1852 | 8.7471 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-11 06:30 | 6.4 | 12.4 | 180 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 645 | 0 | 149929.1852 | 8.7849 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-11 07:30 | 6.3 | 12.2 | 180 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 150574.1852 | 8.8227 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-11 08:30 | 6.5 | 11.2 | 182.5 | 4300 | 4418.0556 | 4098.0556 | 0 | 1290 | 645 | 0 | 151219.1852 | 8.8605 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-11 09:30 | 6.8 | 9.5 | 192.5 | 3280 | 3790 | 3470 | 0 | 1290 | 645 | 0 | 151864.1852 | 8.8983 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-11 10:30 | 6.9 | 7.8 | 205 | 1840 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 152509.1852 | 8.9361 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-11 11:30 | 7.1 | 7.1 | 217.5 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 153154.1852 | 8.9739 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-11 12:30 | 7.2 | 7 | 232.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 153734.1852 | 9.0079 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-11 13:30 | 7.1 | 7 | 235 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 154314.1852 | 9.0418 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-11 14:30 | 7.2 | 7.5 | 225 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 154959.1852 | 9.0796 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-11 15:30 | 7.6 | 8.4 | 222.5 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 155604.1852 | 9.1174 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-11 16:30 | 7.9 | 8.8 | 227.5 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 156249.1852 | 9.1552 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-11 17:30 | 8.1 | 8.4 | 232.5 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 156894.1852 | 9.193 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-11 18:30 | 8 | 7.5 | 237.5 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 157539.1852 | 9.2308 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-11 19:30 | 7.5 | 6.6 | 240 | 1120 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 158119.1852 | 9.2648 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-11 20:30 | 7.1 | 6.2 | 240 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 158429.1852 | 9.283 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-11 21:30 | 6.9 | 6.2 | 240 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 158649.1852 | 9.2959 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-11 22:30 | 6.8 | 5.9 | 240 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 158804.1852 | 9.3049 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-11 23:30 | 6.8 | 5.3 | 242.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 158854.1852 | 9.3079 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-05-12 00:30 | 6.5 | 4.9 | 245 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 158742.3333 | 9.3013 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-05-12 01:30 | 6 | 4.9 | 240 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 158474.1852 | 9.2856 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-05-12 02:30 | 5.8 | 4.4 | 235 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 158069.7407 | 9.2619 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-05-12 03:30 | 5.4 | 3.9 | 235 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 157443.8148 | 9.2252 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-05-12 04:30 | 5.3 | 4.1 | 230 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 156817.8889 | 9.1885 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-05-12 05:30 | 5.5 | 5 | 222.5 | 340 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 156569.7407 | 9.174 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-12 06:30 | 5.9 | 5.8 | 220 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 156619.7407 | 9.1769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-12 07:30 | 6.4 | 5.8 | 220 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 156709.7407 | 9.1822 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-12 08:30 | 6.9 | 5.7 | 217.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 156799.7407 | 9.1875 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-12 09:30 | 7.2 | 5.5 | 212.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 156889.7407 | 9.1928 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-12 10:30 | 7.5 | 5.2 | 197.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 156939.7407 | 9.1957 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-05-12 11:30 | 8 | 4.9 | 167.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 156827.8889 | 9.1891 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-05-12 12:30 | 7.6 | 4.7 | 150 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 156559.7407 | 9.1734 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-05-12 13:30 | 6.7 | 4.4 | 152.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 156155.2963 | 9.1497 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-05-12 14:30 | 7 | 4 | 150 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 155614.5556 | 9.118 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-05-12 15:30 | 7.4 | 3.4 | 142.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 154988.6296 | 9.0814 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-05-12 16:30 | 7.4 | 3.3 | 137.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 154277.5185 | 9.0397 | 0 |  |  | 1 | 7 | 1 | 1
Lerwick | 1978-05-12 17:30 | 7.4 | 3 | 130 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 153566.4074 | 8.998 | 0 |  |  | 1 | 8 | 1 | 2
Lerwick | 1978-05-12 18:30 | 7.3 | 2.4 | 120 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 152855.2963 | 8.9564 | 0 |  |  | 1 | 9 | 1 | 3
Lerwick | 1978-05-12 19:30 | 7.1 | 2 | 105 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 152144.1852 | 8.9147 | 0 |  |  | 1 | 10 | 1 | 4
Lerwick | 1978-05-12 20:30 | 6.7 | 1.5 | 77.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 151433.0741 | 8.873 | 0 |  |  | 1 | 11 | 1 | 5
Lerwick | 1978-05-12 21:30 | 6 | 1.1 | 40 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 150721.963 | 8.8314 | 0 |  |  | 1 | 12 | 1 | 6
Lerwick | 1978-05-12 22:30 | 5.2 | 0.7 | 10 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 150010.8519 | 8.7897 | 0 |  |  | 1 | 13 | 1 | 7
Lerwick | 1978-05-12 23:30 | 5 | 0.2 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 149299.7407 | 8.748 | 0 |  |  | 1 | 14 | 1 | 8
Lerwick | 1978-05-13 00:30 | 4.9 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 148588.6296 | 8.7064 | 0 |  |  | 1 | 15 | 1 | 9
Lerwick | 1978-05-13 01:30 | 4.8 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 147877.5185 | 8.6647 | 0 |  |  | 1 | 16 | 1 | 10
Lerwick | 1978-05-13 02:30 | 5.1 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 147166.4074 | 8.623 | 0 |  |  | 1 | 17 | 1 | 11
Lerwick | 1978-05-13 03:30 | 5.3 | 0.2 | 155 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 146455.2963 | 8.5814 | 0 |  |  | 1 | 18 | 1 | 12
Lerwick | 1978-05-13 04:30 | 5.3 | 0.9 | 287.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 145744.1852 | 8.5397 | 0 |  |  | 1 | 19 | 1 | 13
Lerwick | 1978-05-13 05:30 | 5.6 | 1.7 | 237.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 145033.0741 | 8.498 | 0 |  |  | 1 | 20 | 1 | 14
Lerwick | 1978-05-13 06:30 | 6.1 | 2.3 | 177.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 144321.963 | 8.4564 | 0 |  |  | 1 | 21 | 1 | 15
Lerwick | 1978-05-13 07:30 | 6.5 | 2.6 | 142.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 143610.8519 | 8.4147 | 0 |  |  | 1 | 22 | 1 | 16
Lerwick | 1978-05-13 08:30 | 7.2 | 2.8 | 145 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 142899.7407 | 8.373 | 0 |  |  | 1 | 23 | 1 | 17
Lerwick | 1978-05-13 09:30 | 7.9 | 3.5 | 152.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 142188.6296 | 8.3314 | 0 |  |  | 1 | 24 | 1 | 18
Lerwick | 1978-05-13 10:30 | 8.7 | 4.1 | 155 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 141562.7037 | 8.2947 | 1 |  |  | 1 | 25 | 0 | 0
Lerwick | 1978-05-13 11:30 | 9.2 | 4.4 | 155 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 141021.963 | 8.263 | 1 |  |  | 1 | 26 | 0 | 0
Lerwick | 1978-05-13 12:30 | 9.2 | 4.7 | 152.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 140617.5185 | 8.2393 | 1 |  |  | 1 | 27 | 0 | 0
Lerwick | 1978-05-13 13:30 | 9.3 | 4.9 | 155 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 140349.3704 | 8.2236 | 1 |  |  | 1 | 28 | 0 | 0
Lerwick | 1978-05-13 14:30 | 9.2 | 5.2 | 165 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 140237.5185 | 8.217 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-13 15:30 | 8.9 | 5.4 | 170 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 140247.5185 | 8.2176 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-13 16:30 | 8.1 | 5.1 | 167.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 140257.5185 | 8.2182 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-05-13 17:30 | 7.3 | 4.6 | 157.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 140145.6667 | 8.2117 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-05-13 18:30 | 6.9 | 4.2 | 150 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 139741.2222 | 8.188 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-05-13 19:30 | 6.5 | 4.2 | 160 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 139200.4815 | 8.1563 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-05-13 20:30 | 6.5 | 4.7 | 175 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 138796.037 | 8.1326 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-05-13 21:30 | 6.3 | 4.9 | 177.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 138527.8889 | 8.1169 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-05-13 22:30 | 6.3 | 5.4 | 172.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 138416.037 | 8.1103 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-13 23:30 | 6.4 | 6.3 | 170 | 760 | 550 | 230 | 0 | 230 | 115 | 0 | 138531.037 | 8.1171 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-14 00:30 | 6.3 | 6.9 | 170 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 138841.037 | 8.1352 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-14 01:30 | 6.1 | 7.3 | 167.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 139331.037 | 8.1639 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-14 02:30 | 6 | 7.6 | 165 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 139976.037 | 8.2017 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-14 03:30 | 6.1 | 7.7 | 167.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 140621.037 | 8.2395 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-14 04:30 | 6 | 7.6 | 170 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 141266.037 | 8.2773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-14 05:30 | 5.9 | 7.2 | 172.5 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 141911.037 | 8.3151 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-14 06:30 | 6 | 6.7 | 177.5 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 142401.037 | 8.3438 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-14 07:30 | 6.1 | 6.4 | 177.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 142711.037 | 8.362 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-14 08:30 | 6.2 | 6.4 | 172.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 142931.037 | 8.3749 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-14 09:30 | 6.4 | 6.4 | 167.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 143151.037 | 8.3878 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-14 10:30 | 7.3 | 6.5 | 162.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 143461.037 | 8.4059 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-14 11:30 | 8.5 | 6.5 | 157.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 143861.037 | 8.4294 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-14 12:30 | 7.9 | 6.3 | 152.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 144171.037 | 8.4475 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-14 13:30 | 7.6 | 6.2 | 150 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 144391.037 | 8.4604 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-14 14:30 | 8.6 | 6.2 | 150 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 144611.037 | 8.4733 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-14 15:30 | 8.4 | 6.2 | 150 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 144831.037 | 8.4862 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-14 16:30 | 7.9 | 6.2 | 152.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 145051.037 | 8.4991 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-14 17:30 | 8.1 | 6 | 155 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 145271.037 | 8.512 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-14 18:30 | 7.9 | 5.4 | 152.5 | 340 | 550 | 230 | 0 | 230 | 115 | 0 | 145386.037 | 8.5187 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-05-14 19:30 | 7.3 | 4.7 | 150 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 145274.1852 | 8.5122 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-05-14 20:30 | 6.7 | 4.5 | 150 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 145006.037 | 8.4964 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-05-14 21:30 | 5.9 | 4.5 | 150 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 144737.8889 | 8.4807 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-05-14 22:30 | 5.4 | 4.7 | 150 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 144469.7407 | 8.465 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-05-14 23:30 | 5.6 | 4.9 | 147.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 144201.5926 | 8.4493 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-05-15 00:30 | 5.5 | 4.6 | 145 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 143933.4444 | 8.4336 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-05-15 01:30 | 5.4 | 4.2 | 147.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 143529 | 8.4099 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-05-15 02:30 | 5.2 | 4 | 150 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 142988.2593 | 8.3782 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-05-15 03:30 | 5 | 4 | 150 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 142447.5185 | 8.3465 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-05-15 04:30 | 5.1 | 4 | 152.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 141906.7778 | 8.3149 | 1 |  |  | 1 | 11 | 0 | 0
Lerwick | 1978-05-15 05:30 | 5.6 | 4.2 | 155 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 141366.037 | 8.2832 | 1 |  |  | 1 | 12 | 0 | 0
Lerwick | 1978-05-15 06:30 | 6.1 | 4.6 | 152.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 140961.5926 | 8.2595 | 1 |  |  | 1 | 13 | 0 | 0
Lerwick | 1978-05-15 07:30 | 6.6 | 4.9 | 150 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 140693.4444 | 8.2438 | 1 |  |  | 1 | 14 | 0 | 0
Lerwick | 1978-05-15 08:30 | 7.7 | 5 | 150 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 140581.5926 | 8.2372 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-15 09:30 | 8.7 | 5 | 147.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 140591.5926 | 8.2378 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-15 10:30 | 9 | 5 | 142.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 140601.5926 | 8.2384 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-15 11:30 | 9.2 | 5.2 | 142.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 140611.5926 | 8.239 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-15 12:30 | 9.4 | 5.4 | 147.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 140621.5926 | 8.2395 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-15 13:30 | 9.4 | 5.2 | 150 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 140631.5926 | 8.2401 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-05-15 14:30 | 9 | 4.9 | 150 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 140519.7407 | 8.2336 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-05-15 15:30 | 8.8 | 4.7 | 150 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 140251.5926 | 8.2179 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-05-15 16:30 | 8.8 | 4.4 | 150 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 139847.1481 | 8.1942 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-05-15 17:30 | 8.5 | 4.4 | 150 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 139306.4074 | 8.1625 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-05-15 18:30 | 8 | 4.4 | 150 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 138765.6667 | 8.1308 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-05-15 19:30 | 7.1 | 4.7 | 150 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 138361.2222 | 8.1071 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-05-15 20:30 | 6.5 | 4.9 | 150 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 138093.0741 | 8.0914 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-05-15 21:30 | 6.3 | 5.2 | 152.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 137981.2222 | 8.0848 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-15 22:30 | 6.1 | 5.5 | 157.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 138031.2222 | 8.0878 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-15 23:30 | 5.9 | 5.5 | 160 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 138121.2222 | 8.093 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-16 00:30 | 5.7 | 5.2 | 160 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 138171.2222 | 8.096 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-16 01:30 | 5.3 | 5.2 | 160 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 138181.2222 | 8.0966 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-16 02:30 | 5.4 | 5.5 | 160 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 138231.2222 | 8.0995 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-16 03:30 | 5.6 | 5.7 | 160 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 138321.2222 | 8.1048 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-16 04:30 | 5.7 | 5.8 | 160 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 138411.2222 | 8.11 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-16 05:30 | 6.2 | 6.1 | 160 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 138566.2222 | 8.1191 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-16 06:30 | 6.6 | 6.5 | 160 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 138876.2222 | 8.1373 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-16 07:30 | 7 | 6.8 | 160 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 139276.2222 | 8.1607 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-16 08:30 | 7.1 | 7.3 | 160 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 139766.2222 | 8.1894 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-16 09:30 | 7.3 | 7.8 | 162.5 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 140411.2222 | 8.2272 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-16 10:30 | 7.8 | 8 | 170 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 141056.2222 | 8.265 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-16 11:30 | 8 | 8.2 | 175 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 141701.2222 | 8.3028 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-16 12:30 | 8.6 | 8.5 | 175 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 142346.2222 | 8.3406 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-16 13:30 | 9 | 8.2 | 175 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 142991.2222 | 8.3784 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-16 14:30 | 8.7 | 7.8 | 172.5 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 143636.2222 | 8.4162 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-16 15:30 | 8.9 | 7.4 | 170 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 144281.2222 | 8.454 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-16 16:30 | 9.4 | 6.5 | 170 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 144771.2222 | 8.4827 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-16 17:30 | 9.2 | 5.4 | 170 | 340 | 730 | 410 | 0 | 410 | 205 | 0 | 144976.2222 | 8.4947 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-05-16 18:30 | 8.6 | 4.9 | 170 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 144864.3704 | 8.4881 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-05-16 19:30 | 8 | 4.6 | 170 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 144596.2222 | 8.4724 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-05-16 20:30 | 7.5 | 4.1 | 167.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 144191.7778 | 8.4487 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-05-16 21:30 | 7.3 | 3.6 | 165 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 143565.8519 | 8.4121 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-05-16 22:30 | 7.3 | 3 | 165 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 142854.7407 | 8.3704 | 0 |  |  | 1 | 6 | 1 | 1
Lerwick | 1978-05-16 23:30 | 7.4 | 2.7 | 165 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 142143.6296 | 8.3287 | 0 |  |  | 1 | 7 | 1 | 2
Lerwick | 1978-05-17 00:30 | 7.3 | 2.7 | 165 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 141432.5185 | 8.2871 | 0 |  |  | 1 | 8 | 1 | 3
Lerwick | 1978-05-17 01:30 | 7.3 | 2.6 | 165 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 140721.4074 | 8.2454 | 0 |  |  | 1 | 9 | 1 | 4
Lerwick | 1978-05-17 02:30 | 7.6 | 3.1 | 182.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 140010.2963 | 8.2037 | 0 |  |  | 1 | 10 | 1 | 5
Lerwick | 1978-05-17 03:30 | 7.9 | 3.7 | 210 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 139299.1852 | 8.1621 | 0 |  |  | 1 | 11 | 1 | 6
Lerwick | 1978-05-17 04:30 | 8.1 | 3.5 | 212.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 138588.0741 | 8.1204 | 0 |  |  | 1 | 12 | 1 | 7
Lerwick | 1978-05-17 05:30 | 8.4 | 2.9 | 195 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 137876.963 | 8.0787 | 0 |  |  | 1 | 13 | 1 | 8
Lerwick | 1978-05-17 06:30 | 8.7 | 3 | 192.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 137165.8519 | 8.0371 | 0 |  |  | 1 | 14 | 1 | 9
Lerwick | 1978-05-17 07:30 | 8.8 | 3.6 | 215 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 136454.7407 | 7.9954 | 0 |  |  | 1 | 15 | 1 | 10
Lerwick | 1978-05-17 08:30 | 8.9 | 4.4 | 235 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 135828.8148 | 7.9587 | 1 |  |  | 1 | 16 | 0 | 0
Lerwick | 1978-05-17 09:30 | 9.3 | 5.5 | 245 | 500 | 288.3333 | 0 | 31.6667 | 0 | 0 | 70.3704 | 135758.4444 | 7.9546 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-17 10:30 | 9.7 | 5.9 | 250 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 135848.4444 | 7.9599 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-17 11:30 | 10.7 | 5 | 225 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 135898.4444 | 7.9628 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-05-17 12:30 | 12 | 3.8 | 172.5 | 0 | 170 | 0 | 150 | 0 | 0 | 333.3333 | 135565.1111 | 7.9433 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-05-17 13:30 | 12.1 | 3.4 | 145 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 134854 | 7.9016 | 0 |  |  | 1 | 3 | 1 | 1
Lerwick | 1978-05-17 14:30 | 11.6 | 3.8 | 147.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 134142.8889 | 7.8599 | 0 |  |  | 1 | 4 | 1 | 2
Lerwick | 1978-05-17 15:30 | 12.1 | 3.9 | 152.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 133431.7778 | 7.8183 | 0 |  |  | 1 | 5 | 1 | 3
Lerwick | 1978-05-17 16:30 | 11.8 | 3.6 | 155 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 132720.6667 | 7.7766 | 0 |  |  | 1 | 6 | 1 | 4
Lerwick | 1978-05-17 17:30 | 11.2 | 3 | 162.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 132009.5556 | 7.7349 | 0 |  |  | 1 | 7 | 1 | 5
Lerwick | 1978-05-17 18:30 | 11.1 | 2.4 | 170 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 131298.4444 | 7.6933 | 0 |  |  | 1 | 8 | 1 | 6
Lerwick | 1978-05-17 19:30 | 10.4 | 2.1 | 160 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 130587.3333 | 7.6516 | 0 |  |  | 1 | 9 | 1 | 7
Lerwick | 1978-05-17 20:30 | 9.6 | 2.4 | 155 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 129876.2222 | 7.6099 | 0 |  |  | 1 | 10 | 1 | 8
Lerwick | 1978-05-17 21:30 | 7.9 | 3 | 162.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 129165.1111 | 7.5683 | 0 |  |  | 1 | 11 | 1 | 9
Lerwick | 1978-05-17 22:30 | 6.9 | 3.4 | 162.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 128454 | 7.5266 | 0 |  |  | 1 | 12 | 1 | 10
Lerwick | 1978-05-17 23:30 | 6.9 | 3.7 | 160 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 127742.8889 | 7.4849 | 0 |  |  | 1 | 13 | 1 | 11
Lerwick | 1978-05-18 00:30 | 6.6 | 3.9 | 160 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 127031.7778 | 7.4433 | 0 |  |  | 1 | 14 | 1 | 12
Lerwick | 1978-05-18 01:30 | 6.5 | 3.6 | 157.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 126320.6667 | 7.4016 | 0 |  |  | 1 | 15 | 1 | 13
Lerwick | 1978-05-18 02:30 | 6.4 | 3.2 | 152.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 125609.5556 | 7.3599 | 0 |  |  | 1 | 16 | 1 | 14
Lerwick | 1978-05-18 03:30 | 6.2 | 3.1 | 147.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 124898.4444 | 7.3183 | 0 |  |  | 1 | 17 | 1 | 15
Lerwick | 1978-05-18 04:30 | 5.8 | 3.1 | 142.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 124187.3333 | 7.2766 | 0 |  |  | 1 | 18 | 1 | 16
Lerwick | 1978-05-18 05:30 | 5.8 | 2.9 | 135 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 123476.2222 | 7.2349 | 0 |  |  | 1 | 19 | 1 | 17
Lerwick | 1978-05-18 06:30 | 5.8 | 2.6 | 125 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 122765.1111 | 7.1933 | 0 |  |  | 1 | 20 | 1 | 18
Lerwick | 1978-05-18 07:30 | 5.8 | 2.6 | 120 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 122054 | 7.1516 | 0 |  |  | 1 | 21 | 1 | 19
Lerwick | 1978-05-18 08:30 | 6 | 2.8 | 120 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 121342.8889 | 7.1099 | 0 |  |  | 1 | 22 | 1 | 20
Lerwick | 1978-05-18 09:30 | 6.3 | 3.2 | 122.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 120631.7778 | 7.0683 | 0 |  |  | 1 | 23 | 1 | 21
Lerwick | 1978-05-18 10:30 | 6.5 | 3 | 132.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 119920.6667 | 7.0266 | 0 |  |  | 1 | 24 | 1 | 22
Lerwick | 1978-05-18 11:30 | 6.9 | 2.7 | 145 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 119209.5556 | 6.9849 | 0 |  |  | 1 | 25 | 1 | 23
Lerwick | 1978-05-18 12:30 | 7.3 | 2.9 | 147.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 118498.4444 | 6.9433 | 0 |  |  | 1 | 26 | 1 | 24
Lerwick | 1978-05-18 13:30 | 7.3 | 3.1 | 135 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 117787.3333 | 6.9016 | 0 |  |  | 1 | 27 | 1 | 25
Lerwick | 1978-05-18 14:30 | 7.2 | 3.1 | 120 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 117076.2222 | 6.8599 | 0 |  |  | 1 | 28 | 1 | 26
Lerwick | 1978-05-18 15:30 | 7.3 | 2.9 | 110 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 116365.1111 | 6.8183 | 0 |  |  | 1 | 29 | 1 | 27
Lerwick | 1978-05-18 16:30 | 7.5 | 2.7 | 100 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 115654 | 6.7766 | 0 |  |  | 1 | 30 | 1 | 28
Lerwick | 1978-05-18 17:30 | 7.5 | 3 | 95 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 114942.8889 | 6.7349 | 0 |  |  | 1 | 31 | 1 | 29
Lerwick | 1978-05-18 18:30 | 7.3 | 3.4 | 90 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 114231.7778 | 6.6933 | 0 |  |  | 1 | 32 | 1 | 30
Lerwick | 1978-05-18 19:30 | 7 | 3.6 | 77.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 113520.6667 | 6.6516 | 0 |  |  | 1 | 33 | 1 | 31
Lerwick | 1978-05-18 20:30 | 6.8 | 3.6 | 67.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 112809.5556 | 6.6099 | 0 |  |  | 1 | 34 | 1 | 32
Lerwick | 1978-05-18 21:30 | 6.5 | 3.4 | 70 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 112098.4444 | 6.5683 | 0 |  |  | 1 | 35 | 1 | 33
Lerwick | 1978-05-18 22:30 | 6.2 | 3.3 | 80 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 111387.3333 | 6.5266 | 0 |  |  | 1 | 36 | 1 | 34
Lerwick | 1978-05-18 23:30 | 6.1 | 3.2 | 87.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 110676.2222 | 6.4849 | 0 |  |  | 1 | 37 | 1 | 35
Lerwick | 1978-05-19 00:30 | 6.3 | 2.9 | 85 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 109965.1111 | 6.4433 | 0 |  |  | 1 | 38 | 1 | 36
Lerwick | 1978-05-19 01:30 | 6.4 | 3.1 | 72.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 109254 | 6.4016 | 0 |  |  | 1 | 39 | 1 | 37
Lerwick | 1978-05-19 02:30 | 6.4 | 3.8 | 60 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 108542.8889 | 6.3599 | 0 |  |  | 1 | 40 | 1 | 38
Lerwick | 1978-05-19 03:30 | 6.5 | 4 | 55 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 107916.963 | 6.3233 | 1 |  |  | 1 | 41 | 0 | 0
Lerwick | 1978-05-19 04:30 | 6.7 | 4 | 62.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 107376.2222 | 6.2916 | 1 |  |  | 1 | 42 | 0 | 0
Lerwick | 1978-05-19 05:30 | 6.9 | 4.2 | 75 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 106835.4815 | 6.2599 | 1 |  |  | 1 | 43 | 0 | 0
Lerwick | 1978-05-19 06:30 | 6.9 | 4.6 | 77.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 106431.037 | 6.2362 | 1 |  |  | 1 | 44 | 0 | 0
Lerwick | 1978-05-19 07:30 | 6.8 | 4.7 | 75 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 106162.8889 | 6.2205 | 1 |  |  | 1 | 45 | 0 | 0
Lerwick | 1978-05-19 08:30 | 6.6 | 4.4 | 80 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 105758.4444 | 6.1968 | 1 |  |  | 1 | 46 | 0 | 0
Lerwick | 1978-05-19 09:30 | 6.6 | 4.4 | 90 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 105217.7037 | 6.1651 | 1 |  |  | 1 | 47 | 0 | 0
Lerwick | 1978-05-19 10:30 | 6.7 | 4.5 | 100 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 104813.2593 | 6.1414 | 1 |  |  | 1 | 48 | 0 | 0
Lerwick | 1978-05-19 11:30 | 6.8 | 4.4 | 110 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 104408.8148 | 6.1177 | 1 |  |  | 1 | 49 | 0 | 0
Lerwick | 1978-05-19 12:30 | 7 | 4.1 | 115 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 103868.0741 | 6.086 | 1 |  |  | 1 | 50 | 0 | 0
Lerwick | 1978-05-19 13:30 | 7.7 | 3.7 | 110 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 103242.1481 | 6.0493 | 1 |  |  | 1 | 51 | 0 | 0
Lerwick | 1978-05-19 14:30 | 8.4 | 3.8 | 107.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 102531.037 | 6.0077 | 0 |  |  | 1 | 52 | 1 | 1
Lerwick | 1978-05-19 15:30 | 8.5 | 4.2 | 120 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 101905.1111 | 5.971 | 1 |  |  | 1 | 53 | 0 | 0
Lerwick | 1978-05-19 16:30 | 8.3 | 4.1 | 137.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 101364.3704 | 5.9393 | 1 |  |  | 1 | 54 | 0 | 0
Lerwick | 1978-05-19 17:30 | 8.4 | 3.7 | 140 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 100738.4444 | 5.9026 | 1 |  |  | 1 | 55 | 0 | 0
Lerwick | 1978-05-19 18:30 | 8.6 | 3.8 | 127.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 100027.3333 | 5.861 | 0 |  |  | 1 | 56 | 1 | 1
Lerwick | 1978-05-19 19:30 | 8.3 | 4 | 117.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 99401.4074 | 5.8243 | 1 |  |  | 1 | 57 | 0 | 0
Lerwick | 1978-05-19 20:30 | 8 | 3.6 | 110 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 98775.4815 | 5.7876 | 1 |  |  | 1 | 58 | 0 | 0
Lerwick | 1978-05-19 21:30 | 7.6 | 3.2 | 102.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 98064.3704 | 5.746 | 0 |  |  | 1 | 59 | 1 | 1
Lerwick | 1978-05-19 22:30 | 7.5 | 3.5 | 102.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 97353.2593 | 5.7043 | 0 |  |  | 1 | 60 | 1 | 2
Lerwick | 1978-05-19 23:30 | 7.5 | 4.5 | 107.5 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 96863.6296 | 5.6756 | 1 |  |  | 1 | 61 | 0 | 0
Lerwick | 1978-05-20 00:30 | 7.4 | 4.7 | 110 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 96595.4815 | 5.6599 | 1 |  |  | 1 | 62 | 0 | 0
Lerwick | 1978-05-20 01:30 | 7.2 | 4 | 110 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 96191.037 | 5.6362 | 1 |  |  | 1 | 63 | 0 | 0
Lerwick | 1978-05-20 02:30 | 7 | 3.7 | 110 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 95565.1111 | 5.5995 | 1 |  |  | 1 | 64 | 0 | 0
Lerwick | 1978-05-20 03:30 | 6.9 | 3.9 | 110 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 94854 | 5.5579 | 0 |  |  | 1 | 65 | 1 | 1
Lerwick | 1978-05-20 04:30 | 7.1 | 3.7 | 107.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 94142.8889 | 5.5162 | 0 |  |  | 1 | 66 | 1 | 2
Lerwick | 1978-05-20 05:30 | 7.3 | 3.7 | 107.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 93431.7778 | 5.4745 | 0 |  |  | 1 | 67 | 1 | 3
Lerwick | 1978-05-20 06:30 | 7.5 | 3.9 | 117.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 92720.6667 | 5.4329 | 0 |  |  | 1 | 68 | 1 | 4
Lerwick | 1978-05-20 07:30 | 7.8 | 3.7 | 127.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 92009.5556 | 5.3912 | 0 |  |  | 1 | 69 | 1 | 5
Lerwick | 1978-05-20 08:30 | 7.9 | 3.6 | 130 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 91298.4444 | 5.3495 | 0 |  |  | 1 | 70 | 1 | 6
Lerwick | 1978-05-20 09:30 | 8.1 | 3.6 | 130 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 90587.3333 | 5.3079 | 0 |  |  | 1 | 71 | 1 | 7
Lerwick | 1978-05-20 10:30 | 8.4 | 3.6 | 130 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 89876.2222 | 5.2662 | 0 |  |  | 1 | 72 | 1 | 8
Lerwick | 1978-05-20 11:30 | 9 | 3.6 | 130 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 89165.1111 | 5.2245 | 0 |  |  | 1 | 73 | 1 | 9
Lerwick | 1978-05-20 12:30 | 9.4 | 3.6 | 130 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 88454 | 5.1829 | 0 |  |  | 1 | 74 | 1 | 10
Lerwick | 1978-05-20 13:30 | 9.6 | 3.7 | 132.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 87742.8889 | 5.1412 | 0 |  |  | 1 | 75 | 1 | 11
Lerwick | 1978-05-20 14:30 | 9.7 | 3.9 | 137.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 87031.7778 | 5.0995 | 0 |  |  | 1 | 76 | 1 | 12
Lerwick | 1978-05-20 15:30 | 9.5 | 3.7 | 140 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 86320.6667 | 5.0579 | 0 |  |  | 1 | 77 | 1 | 13
Lerwick | 1978-05-20 16:30 | 9.4 | 3.4 | 137.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 85609.5556 | 5.0162 | 0 |  |  | 1 | 78 | 1 | 14
Lerwick | 1978-05-20 17:30 | 9.2 | 3.2 | 125 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 84898.4444 | 4.9745 | 0 |  |  | 1 | 79 | 1 | 15
Lerwick | 1978-05-20 18:30 | 8.7 | 3.2 | 107.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 84187.3333 | 4.9329 | 0 |  |  | 1 | 80 | 1 | 16
Lerwick | 1978-05-20 19:30 | 7.8 | 3.4 | 105 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 83476.2222 | 4.8912 | 0 |  |  | 1 | 81 | 1 | 17
Lerwick | 1978-05-20 20:30 | 7.1 | 3.4 | 117.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 82765.1111 | 4.8495 | 0 |  |  | 1 | 82 | 1 | 18
Lerwick | 1978-05-20 21:30 | 7 | 3 | 127.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 82054 | 4.8079 | 0 |  |  | 1 | 83 | 1 | 19
Lerwick | 1978-05-20 22:30 | 6.8 | 2.6 | 130 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 81342.8889 | 4.7662 | 0 |  |  | 1 | 84 | 1 | 20
Lerwick | 1978-05-20 23:30 | 6.5 | 2.3 | 127.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 80631.7778 | 4.7245 | 0 |  |  | 1 | 85 | 1 | 21
Lerwick | 1978-05-21 00:30 | 6.3 | 1.9 | 125 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 79920.6667 | 4.6829 | 0 |  |  | 1 | 86 | 1 | 22
Lerwick | 1978-05-21 01:30 | 6.1 | 1.8 | 122.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 79209.5556 | 4.6412 | 0 |  |  | 1 | 87 | 1 | 23
Lerwick | 1978-05-21 02:30 | 5.9 | 1.6 | 117.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 78498.4444 | 4.5995 | 0 |  |  | 1 | 88 | 1 | 24
Lerwick | 1978-05-21 03:30 | 5.8 | 1.5 | 110 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 77787.3333 | 4.5579 | 0 |  |  | 1 | 89 | 1 | 25
Lerwick | 1978-05-21 04:30 | 5.6 | 1.5 | 97.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 77076.2222 | 4.5162 | 0 |  |  | 1 | 90 | 1 | 26
Lerwick | 1978-05-21 05:30 | 5.5 | 1.6 | 85 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 76365.1111 | 4.4745 | 0 |  |  | 1 | 91 | 1 | 27
Lerwick | 1978-05-21 06:30 | 5.7 | 1.8 | 72.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 75654 | 4.4329 | 0 |  |  | 1 | 92 | 1 | 28
Lerwick | 1978-05-21 07:30 | 6.2 | 1.9 | 57.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 74942.8889 | 4.3912 | 0 |  |  | 1 | 93 | 1 | 29
Lerwick | 1978-05-21 08:30 | 6.4 | 2.4 | 45 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 74231.7778 | 4.3495 | 0 |  |  | 1 | 94 | 1 | 30
Lerwick | 1978-05-21 09:30 | 6.5 | 3 | 45 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 73520.6667 | 4.3079 | 0 |  |  | 1 | 95 | 1 | 31
Lerwick | 1978-05-21 10:30 | 6.6 | 3.6 | 47.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 72809.5556 | 4.2662 | 0 |  |  | 1 | 96 | 1 | 32
Lerwick | 1978-05-21 11:30 | 6.9 | 3.9 | 37.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 72098.4444 | 4.2245 | 0 |  |  | 1 | 97 | 1 | 33
Lerwick | 1978-05-21 12:30 | 7.1 | 4 | 30 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 71472.5185 | 4.1878 | 1 |  |  | 1 | 98 | 0 | 0
Lerwick | 1978-05-21 13:30 | 7.3 | 4 | 35 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 70931.7778 | 4.1562 | 1 |  |  | 1 | 99 | 0 | 0
Lerwick | 1978-05-21 14:30 | 7.5 | 4.2 | 42.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 70391.037 | 4.1245 | 1 |  |  | 1 | 100 | 0 | 0
Lerwick | 1978-05-21 15:30 | 7.3 | 4.9 | 42.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 69986.5926 | 4.1008 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-21 16:30 | 7.2 | 5.5 | 37.5 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 70001.4259 | 4.1016 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-21 17:30 | 7.1 | 5.7 | 32.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 70091.4259 | 4.1069 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-21 18:30 | 6.7 | 5.8 | 32.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 70181.4259 | 4.1122 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-21 19:30 | 6.6 | 5.9 | 37.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 70271.4259 | 4.1175 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-21 20:30 | 6.4 | 5.6 | 40 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 70361.4259 | 4.1227 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-21 21:30 | 6.3 | 5.2 | 40 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 70411.4259 | 4.1257 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-21 22:30 | 6.5 | 5 | 40 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 70421.4259 | 4.1263 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-21 23:30 | 6.4 | 5.2 | 37.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 70431.4259 | 4.1268 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-22 00:30 | 6.3 | 5.1 | 35 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 70441.4259 | 4.1274 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-05-22 01:30 | 6.1 | 4.7 | 35 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 70329.5741 | 4.1209 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-05-22 02:30 | 6 | 4.9 | 30 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 70061.4259 | 4.1052 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-22 03:30 | 5.8 | 5.8 | 27.5 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 70076.2593 | 4.106 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-22 04:30 | 5.7 | 6.3 | 32.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 70231.2593 | 4.1151 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-22 05:30 | 5.8 | 6.3 | 35 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 70451.2593 | 4.128 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-22 06:30 | 6.1 | 6 | 35 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 70671.2593 | 4.1409 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-22 07:30 | 6.2 | 6 | 30 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 70891.2593 | 4.1538 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-22 08:30 | 6.3 | 6.4 | 27.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 71111.2593 | 4.1667 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-22 09:30 | 6.5 | 6.5 | 32.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 71421.2593 | 4.1848 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-22 10:30 | 6.9 | 6.1 | 32.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 71731.2593 | 4.203 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-22 11:30 | 7.3 | 5.8 | 30 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 71886.2593 | 4.2121 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-22 12:30 | 7.6 | 5.7 | 32.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 71976.2593 | 4.2174 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-22 13:30 | 7.9 | 5.7 | 35 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 72066.2593 | 4.2226 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-22 14:30 | 8.2 | 5.7 | 35 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 72156.2593 | 4.2279 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-22 15:30 | 8.1 | 5.5 | 35 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 72246.2593 | 4.2332 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-22 16:30 | 7.7 | 4.9 | 35 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 72261.0926 | 4.234 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-05-22 17:30 | 7.5 | 4.2 | 32.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 71856.6481 | 4.2104 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-05-22 18:30 | 7.2 | 4.2 | 27.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 71315.9074 | 4.1787 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-05-22 19:30 | 7 | 4.4 | 27.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 70775.1667 | 4.147 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-05-22 20:30 | 6.7 | 4.4 | 30 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 70234.4259 | 4.1153 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-05-22 21:30 | 6.4 | 4.4 | 30 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 69693.6852 | 4.0836 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-05-22 22:30 | 6.3 | 4.4 | 30 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 69152.9444 | 4.0519 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-05-22 23:30 | 6.1 | 4.5 | 30 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 68748.5 | 4.0282 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-05-23 00:30 | 6 | 4.5 | 27.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 68480.3519 | 4.0125 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-05-23 01:30 | 6 | 4.5 | 22.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 68212.2037 | 3.9968 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-05-23 02:30 | 6 | 4.7 | 20 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 67944.0556 | 3.9811 | 1 |  |  | 1 | 11 | 0 | 0
Lerwick | 1978-05-23 03:30 | 6.1 | 4.7 | 17.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 67675.9074 | 3.9654 | 1 |  |  | 1 | 12 | 0 | 0
Lerwick | 1978-05-23 04:30 | 6.2 | 4.2 | 15 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 67271.463 | 3.9417 | 1 |  |  | 1 | 13 | 0 | 0
Lerwick | 1978-05-23 05:30 | 6.3 | 4 | 17.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 66730.7222 | 3.91 | 1 |  |  | 1 | 14 | 0 | 0
Lerwick | 1978-05-23 06:30 | 6.5 | 4.2 | 20 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 66189.9815 | 3.8783 | 1 |  |  | 1 | 15 | 0 | 0
Lerwick | 1978-05-23 07:30 | 6.7 | 4.4 | 20 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 65649.2407 | 3.8466 | 1 |  |  | 1 | 16 | 0 | 0
Lerwick | 1978-05-23 08:30 | 6.8 | 4.2 | 20 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 65108.5 | 3.815 | 1 |  |  | 1 | 17 | 0 | 0
Lerwick | 1978-05-23 09:30 | 7.1 | 4.2 | 22.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 64567.7593 | 3.7833 | 1 |  |  | 1 | 18 | 0 | 0
Lerwick | 1978-05-23 10:30 | 8.5 | 4.4 | 27.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 64027.0185 | 3.7516 | 1 |  |  | 1 | 19 | 0 | 0
Lerwick | 1978-05-23 11:30 | 10 | 4 | 30 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 63486.2778 | 3.7199 | 1 |  |  | 1 | 20 | 0 | 0
Lerwick | 1978-05-23 12:30 | 9.8 | 3.7 | 30 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 62860.3519 | 3.6832 | 1 |  |  | 1 | 21 | 0 | 0
Lerwick | 1978-05-23 13:30 | 9.2 | 3.9 | 30 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 62149.2407 | 3.6416 | 0 |  |  | 1 | 22 | 1 | 1
Lerwick | 1978-05-23 14:30 | 9.9 | 3.9 | 27.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 61438.1296 | 3.5999 | 0 |  |  | 1 | 23 | 1 | 2
Lerwick | 1978-05-23 15:30 | 9.3 | 3.7 | 25 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 60727.0185 | 3.5582 | 0 |  |  | 1 | 24 | 1 | 3
Lerwick | 1978-05-23 16:30 | 8.5 | 3.3 | 27.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 60015.9074 | 3.5166 | 0 |  |  | 1 | 25 | 1 | 4
Lerwick | 1978-05-23 17:30 | 8.5 | 2.6 | 30 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 59304.7963 | 3.4749 | 0 |  |  | 1 | 26 | 1 | 5
Lerwick | 1978-05-23 18:30 | 8.6 | 2.1 | 30 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 58593.6852 | 3.4332 | 0 |  |  | 1 | 27 | 1 | 6
Lerwick | 1978-05-23 19:30 | 8.6 | 2.4 | 15 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 57882.5741 | 3.3916 | 0 |  |  | 1 | 28 | 1 | 7
Lerwick | 1978-05-23 20:30 | 8.1 | 3.5 | 162.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 57171.463 | 3.3499 | 0 |  |  | 1 | 29 | 1 | 8
Lerwick | 1978-05-23 21:30 | 7.9 | 4.7 | 322.5 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 56681.8333 | 3.3212 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-23 22:30 | 7.8 | 5.6 | 320 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 56696.6667 | 3.3221 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-23 23:30 | 7.4 | 6.9 | 317.5 | 1120 | 810 | 490 | 0 | 490 | 245 | 0 | 56941.6667 | 3.3364 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-24 00:30 | 7.5 | 8.1 | 312.5 | 2200 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 57586.6667 | 3.3742 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-24 01:30 | 7.8 | 8.6 | 312.5 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 58231.6667 | 3.412 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-24 02:30 | 7.9 | 9 | 317.5 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 58876.6667 | 3.4498 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-24 03:30 | 7.8 | 9.5 | 315 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 59521.6667 | 3.4876 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-24 04:30 | 7.4 | 9.8 | 305 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 60166.6667 | 3.5254 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-24 05:30 | 6.7 | 9.6 | 300 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 60811.6667 | 3.5632 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-24 06:30 | 6.5 | 9.5 | 297.5 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 61456.6667 | 3.601 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-24 07:30 | 7 | 9.2 | 292.5 | 2920 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 62101.6667 | 3.6388 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-24 08:30 | 7.6 | 8.9 | 287.5 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 62746.6667 | 3.6766 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-24 09:30 | 8.1 | 9.1 | 280 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 63391.6667 | 3.7144 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-24 10:30 | 8.7 | 9.5 | 272.5 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 64036.6667 | 3.7521 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-24 11:30 | 9.3 | 9.2 | 270 | 2920 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 64681.6667 | 3.7899 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-24 12:30 | 9.5 | 9 | 270 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 65326.6667 | 3.8277 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-24 13:30 | 9.3 | 9 | 267.5 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 65971.6667 | 3.8655 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-24 14:30 | 8.9 | 8.9 | 262.5 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 66616.6667 | 3.9033 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-24 15:30 | 9.3 | 8.6 | 260 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 67261.6667 | 3.9411 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-24 16:30 | 9.2 | 8.2 | 257.5 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 67906.6667 | 3.9789 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-24 17:30 | 8.6 | 7.6 | 255 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 68551.6667 | 4.0167 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-24 18:30 | 8.6 | 6.7 | 255 | 1120 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 69131.6667 | 4.0507 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-24 19:30 | 8.5 | 5.5 | 250 | 500 | 810 | 490 | 0 | 490 | 245 | 0 | 69376.6667 | 4.065 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-05-24 20:30 | 8 | 4.4 | 242.5 | 76.6667 | 288.3333 | 0 | 31.6667 | 0 | 0 | 70.3704 | 69306.2963 | 4.0609 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-05-24 21:30 | 6.9 | 3.6 | 237.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 68680.3704 | 4.0242 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-05-24 22:30 | 5.9 | 3.3 | 232.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 67969.2593 | 3.9826 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-05-24 23:30 | 5.8 | 3.4 | 227.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 67258.1481 | 3.9409 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-05-25 00:30 | 6 | 3.7 | 222.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 66547.037 | 3.8992 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-05-25 01:30 | 6.5 | 4.4 | 220 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 65921.1111 | 3.8626 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-05-25 02:30 | 7.1 | 5.7 | 220 | 500 | 288.3333 | 0 | 31.6667 | 0 | 0 | 70.3704 | 65850.7407 | 3.8584 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-25 03:30 | 7.2 | 6.5 | 217.5 | 1120 | 810 | 490 | 0 | 490 | 245 | 0 | 66095.7407 | 3.8728 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-25 04:30 | 7.4 | 7.1 | 215 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 66585.7407 | 3.9015 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-25 05:30 | 7.7 | 7.8 | 215 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 67230.7407 | 3.9393 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-25 06:30 | 7.9 | 8.5 | 210 | 2560 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 67875.7407 | 3.9771 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-25 07:30 | 8.1 | 9.1 | 202.5 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 68520.7407 | 4.0149 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-25 08:30 | 8.7 | 9 | 200 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 69165.7407 | 4.0527 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-25 09:30 | 9 | 8.8 | 202.5 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 69810.7407 | 4.0905 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-25 10:30 | 9.1 | 8.6 | 207.5 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 70455.7407 | 4.1283 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-25 11:30 | 9 | 8.5 | 210 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 71100.7407 | 4.1661 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-25 12:30 | 9 | 8.9 | 212.5 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 71745.7407 | 4.2039 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-25 13:30 | 9.5 | 9.8 | 217.5 | 3280 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 72390.7407 | 4.2416 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-25 14:30 | 10.6 | 10.6 | 220 | 4000 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 73035.7407 | 4.2794 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-25 15:30 | 11.3 | 10.9 | 217.5 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 73680.7407 | 4.3172 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-25 16:30 | 11 | 10.5 | 215 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 74325.7407 | 4.355 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-25 17:30 | 10.2 | 10.1 | 217.5 | 3640 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 74970.7407 | 4.3928 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-25 18:30 | 9.5 | 9.5 | 220 | 3280 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 75615.7407 | 4.4306 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-25 19:30 | 9.1 | 8.3 | 220 | 2200 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 76260.7407 | 4.4684 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-25 20:30 | 9.1 | 7.4 | 220 | 1480 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 76905.7407 | 4.5062 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-25 21:30 | 9.1 | 7.6 | 222.5 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 77550.7407 | 4.544 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-25 22:30 | 8.9 | 8.5 | 230 | 2560 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 78195.7407 | 4.5818 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-25 23:30 | 8.8 | 8.5 | 237.5 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 78840.7407 | 4.6196 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-26 00:30 | 8.7 | 7.5 | 240 | 1840 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 79485.7407 | 4.6574 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-26 01:30 | 8.7 | 6.7 | 240 | 1120 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 80065.7407 | 4.6914 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-26 02:30 | 8.8 | 6.4 | 237.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 80375.7407 | 4.7095 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-26 03:30 | 9.1 | 6.1 | 232.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 80595.7407 | 4.7224 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-26 04:30 | 9.3 | 6 | 230 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 80815.7407 | 4.7353 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-26 05:30 | 9.1 | 6.8 | 230 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 81125.7407 | 4.7535 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-26 06:30 | 9.1 | 8 | 230 | 2200 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 81770.7407 | 4.7913 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-26 07:30 | 9.6 | 8.6 | 225 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 82415.7407 | 4.829 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-26 08:30 | 10.3 | 8.8 | 212.5 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 83060.7407 | 4.8668 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-26 09:30 | 10.5 | 8.1 | 200 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 83705.7407 | 4.9046 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-26 10:30 | 11 | 6.6 | 192.5 | 1120 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 84350.7407 | 4.9424 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-26 11:30 | 11 | 5.5 | 187.5 | 500 | 810 | 490 | 0 | 490 | 245 | 0 | 84595.7407 | 4.9568 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-26 12:30 | 10.7 | 5.8 | 190 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 84685.7407 | 4.9621 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-26 13:30 | 11.5 | 6.8 | 205 | 1120 | 810 | 490 | 0 | 490 | 245 | 0 | 84930.7407 | 4.9764 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-26 14:30 | 11.5 | 7.8 | 217.5 | 1840 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 85510.7407 | 5.0104 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-26 15:30 | 10.9 | 8.1 | 222.5 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 86155.7407 | 5.0482 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-26 16:30 | 10.7 | 7.6 | 227.5 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 86800.7407 | 5.086 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-26 17:30 | 10.5 | 6.3 | 230 | 760 | 1300 | 980 | 0 | 980 | 490 | 0 | 87290.7407 | 5.1147 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-26 18:30 | 10.2 | 4.9 | 222.5 | 199.3333 | 479.6667 | 159.6667 | 0 | 159.6667 | 79.8333 | 0 | 87370.5741 | 5.1194 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-05-26 19:30 | 9.6 | 4.4 | 212.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 86966.1296 | 5.0957 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-05-26 20:30 | 9.3 | 4.7 | 217.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 86561.6852 | 5.072 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-05-26 21:30 | 9.2 | 4.4 | 225 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 86157.2407 | 5.0483 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-05-26 22:30 | 8.9 | 3.7 | 220 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 85531.3148 | 5.0116 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-05-26 23:30 | 8.9 | 4.5 | 217.5 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 85041.6852 | 4.9829 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-27 00:30 | 9 | 6.3 | 222.5 | 760 | 479.6667 | 159.6667 | 0 | 159.6667 | 79.8333 | 0 | 85121.5185 | 4.9876 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-27 01:30 | 9.1 | 7.4 | 222.5 | 1480 | 1120 | 800 | 0 | 800 | 400 | 0 | 85521.5185 | 5.011 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-27 02:30 | 9.2 | 7.6 | 222.5 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 86166.5185 | 5.0488 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-27 03:30 | 9.1 | 7.5 | 227.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 86811.5185 | 5.0866 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-27 04:30 | 9 | 7.6 | 227.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 87456.5185 | 5.1244 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-27 05:30 | 9 | 7.8 | 225 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 88101.5185 | 5.1622 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-27 06:30 | 9.3 | 8 | 225 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 88746.5185 | 5.2 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-27 07:30 | 9.6 | 8 | 225 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 89391.5185 | 5.2378 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-27 08:30 | 9.8 | 7.6 | 225 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 90036.5185 | 5.2756 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-27 09:30 | 10 | 7.2 | 225 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 90681.5185 | 5.3134 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-27 10:30 | 10.2 | 7.4 | 225 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 91261.5185 | 5.3474 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-27 11:30 | 10.6 | 7.8 | 227.5 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 91906.5185 | 5.3851 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-27 12:30 | 10.9 | 7.8 | 230 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 92551.5185 | 5.4229 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-27 13:30 | 11.5 | 7.3 | 225 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 93196.5185 | 5.4607 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-27 14:30 | 11.7 | 7 | 222.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 93776.5185 | 5.4947 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-27 15:30 | 11.4 | 6.8 | 227.5 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 94266.5185 | 5.5234 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-27 16:30 | 11.2 | 6.2 | 227.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 94576.5185 | 5.5416 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-27 17:30 | 11 | 5.3 | 222.5 | 340 | 550 | 230 | 0 | 230 | 115 | 0 | 94691.5185 | 5.5483 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-05-27 18:30 | 11 | 4.7 | 217.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 94579.6667 | 5.5418 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-05-27 19:30 | 10 | 4.5 | 215 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 94311.5185 | 5.5261 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-05-27 20:30 | 8.7 | 4.5 | 217.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 94043.3704 | 5.5104 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-05-27 21:30 | 8.5 | 4.4 | 217.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 93638.9259 | 5.4867 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-05-27 22:30 | 8.9 | 4.4 | 215 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 93098.1852 | 5.455 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-05-27 23:30 | 9 | 4.4 | 217.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 92557.4444 | 5.4233 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-05-28 00:30 | 8.9 | 4 | 220 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 92016.7037 | 5.3916 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-05-28 01:30 | 9 | 3.4 | 215 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 91390.7778 | 5.3549 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-05-28 02:30 | 9.1 | 3.3 | 210 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 90679.6667 | 5.3133 | 0 |  |  | 1 | 10 | 1 | 1
Lerwick | 1978-05-28 03:30 | 9.3 | 2.7 | 202.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 89968.5556 | 5.2716 | 0 |  |  | 1 | 11 | 1 | 2
Lerwick | 1978-05-28 04:30 | 9.7 | 1.8 | 182.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 89257.4444 | 5.2299 | 0 |  |  | 1 | 12 | 1 | 3
Lerwick | 1978-05-28 05:30 | 9.8 | 1.6 | 165 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 88546.3333 | 5.1883 | 0 |  |  | 1 | 13 | 1 | 4
Lerwick | 1978-05-28 06:30 | 9.7 | 2 | 157.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 87835.2222 | 5.1466 | 0 |  |  | 1 | 14 | 1 | 5
Lerwick | 1978-05-28 07:30 | 9.5 | 2.4 | 152.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 87124.1111 | 5.1049 | 0 |  |  | 1 | 15 | 1 | 6
Lerwick | 1978-05-28 08:30 | 10.2 | 3.1 | 147.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 86413 | 5.0633 | 0 |  |  | 1 | 16 | 1 | 7
Lerwick | 1978-05-28 09:30 | 11.2 | 4 | 150 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 85787.0741 | 5.0266 | 1 |  |  | 1 | 17 | 0 | 0
Lerwick | 1978-05-28 10:30 | 11.2 | 4.6 | 160 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 85382.6296 | 5.0029 | 1 |  |  | 1 | 18 | 0 | 0
Lerwick | 1978-05-28 11:30 | 10.7 | 5.1 | 167.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 85270.7778 | 4.9963 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-28 12:30 | 10.1 | 5.6 | 165 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 85320.7778 | 4.9993 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-28 13:30 | 10.1 | 5.4 | 157.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 85370.7778 | 5.0022 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-05-28 14:30 | 11 | 4 | 170 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 85122.6296 | 4.9877 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-05-28 15:30 | 11.7 | 2.8 | 197.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 84496.7037 | 4.951 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-05-28 16:30 | 12.5 | 2.4 | 205 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 83785.5926 | 4.9093 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-05-28 17:30 | 13.4 | 2.1 | 200 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 83074.4815 | 4.8676 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-05-28 18:30 | 13.3 | 1.9 | 195 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 82363.3704 | 4.826 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-05-28 19:30 | 12.3 | 1.6 | 182.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 81652.2593 | 4.7843 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-05-28 20:30 | 11.9 | 1.5 | 177.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 80941.1481 | 4.7426 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-05-28 21:30 | 11.7 | 1.5 | 180 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 80230.037 | 4.701 | 0 |  |  | 1 | 9 | 1 | 6
Lerwick | 1978-05-28 22:30 | 11.7 | 1.5 | 190 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 79518.9259 | 4.6593 | 0 |  |  | 1 | 10 | 1 | 7
Lerwick | 1978-05-28 23:30 | 11.9 | 1.8 | 215 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 78807.8148 | 4.6176 | 0 |  |  | 1 | 11 | 1 | 8
Lerwick | 1978-05-29 00:30 | 12.1 | 2.1 | 232.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 78096.7037 | 4.576 | 0 |  |  | 1 | 12 | 1 | 9
Lerwick | 1978-05-29 01:30 | 12 | 1.7 | 222.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 77385.5926 | 4.5343 | 0 |  |  | 1 | 13 | 1 | 10
Lerwick | 1978-05-29 02:30 | 11.6 | 1.1 | 205 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 76674.4815 | 4.4926 | 0 |  |  | 1 | 14 | 1 | 11
Lerwick | 1978-05-29 03:30 | 10.7 | 1 | 210 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 75963.3704 | 4.451 | 0 |  |  | 1 | 15 | 1 | 12
Lerwick | 1978-05-29 04:30 | 10.3 | 1.1 | 220 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 75252.2593 | 4.4093 | 0 |  |  | 1 | 16 | 1 | 13
Lerwick | 1978-05-29 05:30 | 10.8 | 1.7 | 212.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 74541.1481 | 4.3676 | 0 |  |  | 1 | 17 | 1 | 14
Lerwick | 1978-05-29 06:30 | 11.3 | 2.4 | 210 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 73830.037 | 4.326 | 0 |  |  | 1 | 18 | 1 | 15
Lerwick | 1978-05-29 07:30 | 12.1 | 3.1 | 222.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 73118.9259 | 4.2843 | 0 |  |  | 1 | 19 | 1 | 16
Lerwick | 1978-05-29 08:30 | 13.7 | 4 | 232.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 72493 | 4.2476 | 1 |  |  | 1 | 20 | 0 | 0
Lerwick | 1978-05-29 09:30 | 14.8 | 4.2 | 225 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 71952.2593 | 4.216 | 1 |  |  | 1 | 21 | 0 | 0
Lerwick | 1978-05-29 10:30 | 15.2 | 3.5 | 192.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 71326.3333 | 4.1793 | 1 |  |  | 1 | 22 | 0 | 0
Lerwick | 1978-05-29 11:30 | 15.4 | 3.3 | 162.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 70615.2222 | 4.1376 | 0 |  |  | 1 | 23 | 1 | 1
Lerwick | 1978-05-29 12:30 | 15.5 | 4 | 157.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 69989.2963 | 4.1009 | 1 |  |  | 1 | 24 | 0 | 0
Lerwick | 1978-05-29 13:30 | 15.1 | 4.5 | 160 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 69584.8519 | 4.0772 | 1 |  |  | 1 | 25 | 0 | 0
Lerwick | 1978-05-29 14:30 | 15.6 | 4.2 | 162.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 69180.4074 | 4.0535 | 1 |  |  | 1 | 26 | 0 | 0
Lerwick | 1978-05-29 15:30 | 16.3 | 4 | 170 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 68639.6667 | 4.0219 | 1 |  |  | 1 | 27 | 0 | 0
Lerwick | 1978-05-29 16:30 | 15.5 | 4 | 175 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 68098.9259 | 3.9902 | 1 |  |  | 1 | 28 | 0 | 0
Lerwick | 1978-05-29 17:30 | 14.6 | 4 | 172.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 67558.1852 | 3.9585 | 1 |  |  | 1 | 29 | 0 | 0
Lerwick | 1978-05-29 18:30 | 13.8 | 4 | 172.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 67017.4444 | 3.9268 | 1 |  |  | 1 | 30 | 0 | 0
Lerwick | 1978-05-29 19:30 | 12.9 | 3.8 | 177.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 66391.5185 | 3.8901 | 1 |  |  | 1 | 31 | 0 | 0
Lerwick | 1978-05-29 20:30 | 12.1 | 3.6 | 177.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 65680.4074 | 3.8485 | 0 |  |  | 1 | 32 | 1 | 1
Lerwick | 1978-05-29 21:30 | 11.4 | 3.7 | 175 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 64969.2963 | 3.8068 | 0 |  |  | 1 | 33 | 1 | 2
Lerwick | 1978-05-29 22:30 | 10.7 | 3.2 | 180 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 64258.1852 | 3.7651 | 0 |  |  | 1 | 34 | 1 | 3
Lerwick | 1978-05-29 23:30 | 10.4 | 1.9 | 185 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 63547.0741 | 3.7235 | 0 |  |  | 1 | 35 | 1 | 4
Lerwick | 1978-05-30 00:30 | 9.9 | 1.3 | 190 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 62835.963 | 3.6818 | 0 |  |  | 1 | 36 | 1 | 5
Lerwick | 1978-05-30 01:30 | 9.3 | 1.7 | 212.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 62124.8519 | 3.6401 | 0 |  |  | 1 | 37 | 1 | 6
Lerwick | 1978-05-30 02:30 | 9.5 | 2.3 | 250 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 61413.7407 | 3.5985 | 0 |  |  | 1 | 38 | 1 | 7
Lerwick | 1978-05-30 03:30 | 11.1 | 2.6 | 282.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 60702.6296 | 3.5568 | 0 |  |  | 1 | 39 | 1 | 8
Lerwick | 1978-05-30 04:30 | 12.1 | 2.3 | 297.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 59991.5185 | 3.5151 | 0 |  |  | 1 | 40 | 1 | 9
Lerwick | 1978-05-30 05:30 | 12.8 | 1.7 | 155 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 59280.4074 | 3.4735 | 0 |  |  | 1 | 41 | 1 | 10
Lerwick | 1978-05-30 06:30 | 14.5 | 1.3 | 47.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 58569.2963 | 3.4318 | 0 |  |  | 1 | 42 | 1 | 11
Lerwick | 1978-05-30 07:30 | 16 | 1.4 | 87.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 57858.1852 | 3.3901 | 0 |  |  | 1 | 43 | 1 | 12
Lerwick | 1978-05-30 08:30 | 16 | 1.8 | 105 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 57147.0741 | 3.3485 | 0 |  |  | 1 | 44 | 1 | 13
Lerwick | 1978-05-30 09:30 | 15.5 | 2.6 | 135 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 56435.963 | 3.3068 | 0 |  |  | 1 | 45 | 1 | 14
Lerwick | 1978-05-30 10:30 | 15.4 | 3.2 | 150 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 55724.8519 | 3.2651 | 0 |  |  | 1 | 46 | 1 | 15
Lerwick | 1978-05-30 11:30 | 15.2 | 3.2 | 152.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 55013.7407 | 3.2235 | 0 |  |  | 1 | 47 | 1 | 16
Lerwick | 1978-05-30 12:30 | 16.1 | 3.3 | 155 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 54302.6296 | 3.1818 | 0 |  |  | 1 | 48 | 1 | 17
Lerwick | 1978-05-30 13:30 | 16.2 | 4 | 155 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 53676.7037 | 3.1451 | 1 |  |  | 1 | 49 | 0 | 0
Lerwick | 1978-05-30 14:30 | 14.9 | 4.4 | 160 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 53135.963 | 3.1134 | 1 |  |  | 1 | 50 | 0 | 0
Lerwick | 1978-05-30 15:30 | 14.3 | 4.4 | 167.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 52595.2222 | 3.0818 | 1 |  |  | 1 | 51 | 0 | 0
Lerwick | 1978-05-30 16:30 | 14.3 | 4.7 | 170 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 52190.7778 | 3.0581 | 1 |  |  | 1 | 52 | 0 | 0
Lerwick | 1978-05-30 17:30 | 14.3 | 4.9 | 172.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 51922.6296 | 3.0423 | 1 |  |  | 1 | 53 | 0 | 0
Lerwick | 1978-05-30 18:30 | 13.8 | 4.7 | 172.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 51654.4815 | 3.0266 | 1 |  |  | 1 | 54 | 0 | 0
Lerwick | 1978-05-30 19:30 | 12.8 | 4.5 | 167.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 51386.3333 | 3.0109 | 1 |  |  | 1 | 55 | 0 | 0
Lerwick | 1978-05-30 20:30 | 11.7 | 4.2 | 167.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 50981.8889 | 2.9872 | 1 |  |  | 1 | 56 | 0 | 0
Lerwick | 1978-05-30 21:30 | 10.5 | 3.9 | 170 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 50355.963 | 2.9505 | 1 |  |  | 1 | 57 | 0 | 0
Lerwick | 1978-05-30 22:30 | 10 | 4.2 | 170 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 49730.037 | 2.9139 | 1 |  |  | 1 | 58 | 0 | 0
Lerwick | 1978-05-30 23:30 | 10.1 | 4.4 | 170 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 49189.2963 | 2.8822 | 1 |  |  | 1 | 59 | 0 | 0
Lerwick | 1978-05-31 00:30 | 10.2 | 4.4 | 172.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 48648.5556 | 2.8505 | 1 |  |  | 1 | 60 | 0 | 0
Lerwick | 1978-05-31 01:30 | 10 | 4.1 | 175 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 48107.8148 | 2.8188 | 1 |  |  | 1 | 61 | 0 | 0
Lerwick | 1978-05-31 02:30 | 9.7 | 3.9 | 172.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 47481.8889 | 2.7821 | 1 |  |  | 1 | 62 | 0 | 0
Lerwick | 1978-05-31 03:30 | 9.5 | 4.2 | 175 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 46855.963 | 2.7455 | 1 |  |  | 1 | 63 | 0 | 0
Lerwick | 1978-05-31 04:30 | 9.6 | 4.9 | 180 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 46451.5185 | 2.7218 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-31 05:30 | 10 | 5.8 | 170 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 46466.3519 | 2.7226 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-31 06:30 | 10.4 | 6 | 155 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 46621.3519 | 2.7317 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-31 07:30 | 10.9 | 5.4 | 145 | 340 | 550 | 230 | 0 | 230 | 115 | 0 | 46736.3519 | 2.7385 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-05-31 08:30 | 11.5 | 4.9 | 135 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 46624.5 | 2.7319 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-05-31 09:30 | 12 | 5.1 | 135 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 46512.6481 | 2.7254 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-31 10:30 | 12.7 | 5.6 | 152.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 46562.6481 | 2.7283 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-31 11:30 | 13 | 6.1 | 170 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 46717.6481 | 2.7374 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-31 12:30 | 13.2 | 6.7 | 172.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 47027.6481 | 2.7555 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-31 13:30 | 13.7 | 7.2 | 170 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 47517.6481 | 2.7842 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-31 14:30 | 13.9 | 7.5 | 170 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 48162.6481 | 2.822 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-31 15:30 | 13.9 | 7.2 | 170 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 48807.6481 | 2.8598 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-31 16:30 | 13.8 | 6.4 | 167.5 | 760 | 1120 | 800 | 0 | 800 | 400 | 0 | 49207.6481 | 2.8833 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-05-31 17:30 | 13.5 | 5.1 | 162.5 | 340 | 550 | 230 | 0 | 230 | 115 | 0 | 49322.6481 | 2.89 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-05-31 18:30 | 13 | 3.7 | 160 | 0 | 170 | 0 | 150 | 0 | 0 | 333.3333 | 48989.3148 | 2.8705 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-05-31 19:30 | 12.3 | 2.8 | 162.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 48278.2037 | 2.8288 | 0 |  |  | 1 | 3 | 1 | 1
Lerwick | 1978-05-31 20:30 | 11.5 | 2.6 | 167.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 47567.0926 | 2.7871 | 0 |  |  | 1 | 4 | 1 | 2
Lerwick | 1978-05-31 21:30 | 10.6 | 2.4 | 175 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 46855.9815 | 2.7455 | 0 |  |  | 1 | 5 | 1 | 3
Lerwick | 1978-05-31 22:30 | 9.9 | 2.1 | 185 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 46144.8704 | 2.7038 | 0 |  |  | 1 | 6 | 1 | 4
Lerwick | 1978-05-31 23:30 | 9.7 | 2.3 | 190 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 45433.7593 | 2.6621 | 0 |  |  | 1 | 7 | 1 | 5
Lerwick | 1978-06-01 00:30 | 9.8 | 2.6 | 187.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 44722.6481 | 2.6205 | 0 |  |  | 1 | 8 | 1 | 6
Lerwick | 1978-06-01 01:30 | 9.7 | 2.4 | 182.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 44011.537 | 2.5788 | 0 |  |  | 1 | 9 | 1 | 7
Lerwick | 1978-06-01 02:30 | 9.8 | 2.2 | 177.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 43300.4259 | 2.5371 | 0 |  |  | 1 | 10 | 1 | 8
Lerwick | 1978-06-01 03:30 | 9.9 | 2.6 | 172.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 42589.3148 | 2.4955 | 0 |  |  | 1 | 11 | 1 | 9
Lerwick | 1978-06-01 04:30 | 9.5 | 3.5 | 167.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 41878.2037 | 2.4538 | 0 |  |  | 1 | 12 | 1 | 10
Lerwick | 1978-06-01 05:30 | 9.9 | 4.4 | 162.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 41252.2778 | 2.4171 | 1 |  |  | 1 | 13 | 0 | 0
Lerwick | 1978-06-01 06:30 | 11 | 4.9 | 160 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 40847.8333 | 2.3934 | 1 |  |  | 1 | 14 | 0 | 0
Lerwick | 1978-06-01 07:30 | 11.8 | 5.2 | 162.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 40735.9815 | 2.3869 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-01 08:30 | 12.8 | 5.5 | 165 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 40785.9815 | 2.3898 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-01 09:30 | 13.6 | 5.7 | 162.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 40875.9815 | 2.3951 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-01 10:30 | 14.2 | 5.9 | 162.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 40965.9815 | 2.4004 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-01 11:30 | 14.5 | 6.4 | 167.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 41120.9815 | 2.4094 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-01 12:30 | 14.4 | 6.5 | 170 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 41430.9815 | 2.4276 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-01 13:30 | 14.5 | 6.3 | 170 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 41740.9815 | 2.4458 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-01 14:30 | 14.6 | 5.8 | 167.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 41895.9815 | 2.4548 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-01 15:30 | 14.3 | 5.2 | 162.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 41945.9815 | 2.4578 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-01 16:30 | 13.9 | 5 | 160 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 41955.9815 | 2.4584 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-06-01 17:30 | 13.9 | 4.5 | 162.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 41844.1296 | 2.4518 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-06-01 18:30 | 13.5 | 3.8 | 167.5 | 0 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 41354.5 | 2.4231 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-06-01 19:30 | 12.7 | 3.3 | 167.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 40643.3889 | 2.3814 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-06-01 20:30 | 12 | 3.1 | 165 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 39932.2778 | 2.3398 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-06-01 21:30 | 11 | 3.2 | 167.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 39221.1667 | 2.2981 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-06-01 22:30 | 10.6 | 3.3 | 172.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 38510.0556 | 2.2564 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-06-01 23:30 | 10.4 | 3.2 | 177.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 37798.9444 | 2.2148 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-06-02 00:30 | 10 | 3.2 | 177.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 37087.8333 | 2.1731 | 0 |  |  | 1 | 9 | 1 | 6
Lerwick | 1978-06-02 01:30 | 10.2 | 3.9 | 175 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 36376.7222 | 2.1314 | 0 |  |  | 1 | 10 | 1 | 7
Lerwick | 1978-06-02 02:30 | 10.6 | 4.7 | 177.5 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 35887.0926 | 2.1028 | 1 |  |  | 1 | 11 | 0 | 0
Lerwick | 1978-06-02 03:30 | 10.7 | 5 | 180 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 35775.2407 | 2.0962 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-02 04:30 | 10.5 | 5 | 180 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 35785.2407 | 2.0968 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-06-02 05:30 | 10.7 | 4.9 | 182.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 35673.3889 | 2.0902 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-06-02 06:30 | 11.2 | 4.7 | 185 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 35405.2407 | 2.0745 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-06-02 07:30 | 11.6 | 4.7 | 182.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 35137.0926 | 2.0588 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-06-02 08:30 | 12.1 | 4.9 | 180 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 34868.9444 | 2.0431 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-06-02 09:30 | 12.8 | 4.9 | 180 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 34600.7963 | 2.0274 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-06-02 10:30 | 13.5 | 4.9 | 180 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 34332.6481 | 2.0117 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-06-02 11:30 | 14.1 | 4.7 | 187.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 34064.5 | 1.996 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-06-02 12:30 | 15.2 | 5.1 | 202.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 33952.6481 | 1.9894 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-02 13:30 | 16.3 | 5.7 | 210 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 34002.6481 | 1.9923 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-02 14:30 | 17.6 | 5 | 215 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 34052.6481 | 1.9953 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-06-02 15:30 | 17.8 | 4.4 | 227.5 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 33804.5 | 1.9807 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-06-02 16:30 | 16.8 | 5 | 240 | 340 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 33556.3519 | 1.9662 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-02 17:30 | 15.8 | 6.2 | 252.5 | 760 | 550 | 230 | 0 | 230 | 115 | 0 | 33671.3519 | 1.9729 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-02 18:30 | 14.4 | 6.4 | 267.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 33891.3519 | 1.9858 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-02 19:30 | 13.6 | 5.6 | 280 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 34046.3519 | 1.9949 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-06-02 20:30 | 13.2 | 4.3 | 302.5 | 76.6667 | 288.3333 | 0 | 31.6667 | 0 | 0 | 70.3704 | 33975.9815 | 1.9908 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-06-02 21:30 | 13.1 | 3.1 | 322.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 33350.0556 | 1.9541 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-06-02 22:30 | 13.3 | 3 | 312.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 32638.9444 | 1.9124 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-06-02 23:30 | 12.9 | 3.4 | 307.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 31927.8333 | 1.8708 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-06-03 00:30 | 12.2 | 3.3 | 322.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 31216.7222 | 1.8291 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-06-03 01:30 | 11.7 | 2.4 | 165 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 30505.6111 | 1.7874 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-06-03 02:30 | 11.3 | 1.5 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 29794.5 | 1.7458 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-06-03 03:30 | 11.1 | 1.4 | 112.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 29083.3889 | 1.7041 | 0 |  |  | 1 | 9 | 1 | 6
Lerwick | 1978-06-03 04:30 | 11 | 1.8 | 220 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 28372.2778 | 1.6624 | 0 |  |  | 1 | 10 | 1 | 7
Lerwick | 1978-06-03 05:30 | 11 | 2.4 | 217.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 27661.1667 | 1.6208 | 0 |  |  | 1 | 11 | 1 | 8
Lerwick | 1978-06-03 06:30 | 10.9 | 2.6 | 210 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 26950.0556 | 1.5791 | 0 |  |  | 1 | 12 | 1 | 9
Lerwick | 1978-06-03 07:30 | 11.2 | 2.3 | 187.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 26238.9444 | 1.5374 | 0 |  |  | 1 | 13 | 1 | 10
Lerwick | 1978-06-03 08:30 | 12.2 | 2.1 | 180 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 25527.8333 | 1.4958 | 0 |  |  | 1 | 14 | 1 | 11
Lerwick | 1978-06-03 09:30 | 12.7 | 2.4 | 182.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 24816.7222 | 1.4541 | 0 |  |  | 1 | 15 | 1 | 12
Lerwick | 1978-06-03 10:30 | 13.2 | 3 | 170 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 24105.6111 | 1.4124 | 0 |  |  | 1 | 16 | 1 | 13
Lerwick | 1978-06-03 11:30 | 14.2 | 3.3 | 165 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 23394.5 | 1.3708 | 0 |  |  | 1 | 17 | 1 | 14
Lerwick | 1978-06-03 12:30 | 14.7 | 3.4 | 185 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 22683.3889 | 1.3291 | 0 |  |  | 1 | 18 | 1 | 15
Lerwick | 1978-06-03 13:30 | 15.4 | 4 | 210 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 22057.463 | 1.2924 | 1 |  |  | 1 | 19 | 0 | 0
Lerwick | 1978-06-03 14:30 | 16 | 4.4 | 220 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 21516.7222 | 1.2607 | 1 |  |  | 1 | 20 | 0 | 0
Lerwick | 1978-06-03 15:30 | 15.8 | 4.1 | 210 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 20975.9815 | 1.2291 | 1 |  |  | 1 | 21 | 0 | 0
Lerwick | 1978-06-03 16:30 | 15.3 | 3.7 | 187.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 20350.0556 | 1.1924 | 1 |  |  | 1 | 22 | 0 | 0
Lerwick | 1978-06-03 17:30 | 14.4 | 3.7 | 175 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 19638.9444 | 1.1507 | 0 |  |  | 1 | 23 | 1 | 1
Lerwick | 1978-06-03 18:30 | 13.4 | 3.7 | 180 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 18927.8333 | 1.1091 | 0 |  |  | 1 | 24 | 1 | 2
Lerwick | 1978-06-03 19:30 | 12.9 | 3.3 | 190 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 18216.7222 | 1.0674 | 0 |  |  | 1 | 25 | 1 | 3
Lerwick | 1978-06-03 20:30 | 12.6 | 3.1 | 190 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 17505.6111 | 1.0257 | 0 |  |  | 1 | 26 | 1 | 4
Lerwick | 1978-06-03 21:30 | 12.5 | 3.2 | 182.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 16794.5 | 0.98405 | 0 |  |  | 1 | 27 | 1 | 5
Lerwick | 1978-06-03 22:30 | 12.3 | 3.4 | 185 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 16083.3889 | 0.94239 | 0 |  |  | 1 | 28 | 1 | 6
Lerwick | 1978-06-03 23:30 | 11.7 | 3.6 | 190 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 15372.2778 | 0.90072 | 0 |  |  | 1 | 29 | 1 | 7
Lerwick | 1978-06-04 00:30 | 11.4 | 3.4 | 192.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 14661.1667 | 0.85905 | 0 |  |  | 1 | 30 | 1 | 8
Lerwick | 1978-06-04 01:30 | 11.4 | 3.6 | 192.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 13950.0556 | 0.81739 | 0 |  |  | 1 | 31 | 1 | 9
Lerwick | 1978-06-04 02:30 | 11.9 | 3.9 | 185 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 13238.9444 | 0.77572 | 0 |  |  | 1 | 32 | 1 | 10
Lerwick | 1978-06-04 03:30 | 11.9 | 3.5 | 180 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 12527.8333 | 0.73405 | 0 |  |  | 1 | 33 | 1 | 11
Lerwick | 1978-06-04 04:30 | 11.6 | 2.9 | 177.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 11816.7222 | 0.69239 | 0 |  |  | 1 | 34 | 1 | 12
Lerwick | 1978-06-04 05:30 | 11.6 | 3 | 177.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 11105.6111 | 0.65072 | 0 |  |  | 1 | 35 | 1 | 13
Lerwick | 1978-06-04 06:30 | 12 | 3.6 | 182.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 10394.5 | 0.60905 | 0 |  |  | 1 | 36 | 1 | 14
Lerwick | 1978-06-04 07:30 | 12.9 | 4.2 | 180 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 9768.5741 | 0.57238 | 1 |  |  | 1 | 37 | 0 | 0
Lerwick | 1978-06-04 08:30 | 13.4 | 4.5 | 172.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 9364.1296 | 0.54868 | 1 |  |  | 1 | 38 | 0 | 0
Lerwick | 1978-06-04 09:30 | 14.2 | 4.4 | 172.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 8959.6852 | 0.52498 | 1 |  |  | 1 | 39 | 0 | 0
Lerwick | 1978-06-04 10:30 | 13.6 | 4.1 | 175 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 8418.9444 | 0.4933 | 1 |  |  | 1 | 40 | 0 | 0
Lerwick | 1978-06-04 11:30 | 13.1 | 3.9 | 172.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 7793.0185 | 0.45662 | 1 |  |  | 1 | 41 | 0 | 0
Lerwick | 1978-06-04 12:30 | 13.7 | 4.4 | 170 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 7167.0926 | 0.41995 | 1 |  |  | 1 | 42 | 0 | 0
Lerwick | 1978-06-04 13:30 | 12.8 | 4.9 | 167.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 6762.6481 | 0.39625 | 1 |  |  | 1 | 43 | 0 | 0
Lerwick | 1978-06-04 14:30 | 11.8 | 4.9 | 160 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 6494.5 | 0.38054 | 1 |  |  | 1 | 44 | 0 | 0
Lerwick | 1978-06-04 15:30 | 11.5 | 4.7 | 150 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 6226.3519 | 0.36483 | 1 |  |  | 1 | 45 | 0 | 0
Lerwick | 1978-06-04 16:30 | 11.5 | 4.7 | 140 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 5958.2037 | 0.34911 | 1 |  |  | 1 | 46 | 0 | 0
Lerwick | 1978-06-04 17:30 | 11.4 | 4.9 | 132.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 5690.0556 | 0.3334 | 1 |  |  | 1 | 47 | 0 | 0
Lerwick | 1978-06-04 18:30 | 11.4 | 4.7 | 130 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 5421.9074 | 0.31769 | 1 |  |  | 1 | 48 | 0 | 0
Lerwick | 1978-06-04 19:30 | 11.2 | 4.2 | 130 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 5017.463 | 0.29399 | 1 |  |  | 1 | 49 | 0 | 0
Lerwick | 1978-06-04 20:30 | 11.2 | 4 | 132.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 4476.7222 | 0.26231 | 1 |  |  | 1 | 50 | 0 | 0
Lerwick | 1978-06-04 21:30 | 11.1 | 4.2 | 142.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 3935.9815 | 0.23062 | 1 |  |  | 1 | 51 | 0 | 0
Lerwick | 1978-06-04 22:30 | 10.9 | 4.4 | 155 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 3395.2407 | 0.19894 | 1 |  |  | 1 | 52 | 0 | 0
Lerwick | 1978-06-04 23:30 | 11.2 | 4.2 | 160 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 2854.5 | 0.16726 | 1 |  |  | 1 | 53 | 0 | 0
Lerwick | 1978-06-05 00:30 | 11.5 | 4.5 | 160 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 2450.0556 | 0.14356 | 1 |  |  | 1 | 54 | 0 | 0
Lerwick | 1978-06-05 01:30 | 11.4 | 5.3 | 157.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 2338.2037 | 0.137 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-05 02:30 | 11.2 | 5.8 | 152.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 2388.2037 | 0.13993 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-05 03:30 | 11.3 | 5.9 | 150 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 2478.2037 | 0.14521 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-05 04:30 | 11.3 | 5.4 | 145 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 2528.2037 | 0.14814 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-06-05 05:30 | 11 | 4.6 | 132.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 2416.3519 | 0.14158 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-06-05 06:30 | 11 | 4.6 | 127.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 2148.2037 | 0.12587 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-06-05 07:30 | 11 | 5.1 | 130 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 2036.3519 | 0.11932 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-05 08:30 | 11.3 | 5.9 | 125 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 2086.3519 | 0.12225 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-05 09:30 | 11.8 | 6.4 | 122.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 2241.3519 | 0.13133 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-05 10:30 | 12.6 | 6 | 130 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 2461.3519 | 0.14422 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-05 11:30 | 12.5 | 5.8 | 140 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 2616.3519 | 0.1533 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-05 12:30 | 11.7 | 5.6 | 150 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 2706.3519 | 0.15858 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-05 13:30 | 11.5 | 5.5 | 162.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 2796.3519 | 0.16385 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-05 14:30 | 11.7 | 5.9 | 175 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 2886.3519 | 0.16912 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-05 15:30 | 11.7 | 6 | 180 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 3041.3519 | 0.1782 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-05 16:30 | 11.2 | 5.6 | 180 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 3196.3519 | 0.18729 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-05 17:30 | 11.6 | 4.9 | 185 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 3211.1852 | 0.18816 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-06-05 18:30 | 12.3 | 4.5 | 192.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 2943.037 | 0.17244 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-06-05 19:30 | 12 | 4.2 | 190 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 2538.5926 | 0.14875 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-06-05 20:30 | 11.5 | 3.6 | 180 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 1912.6667 | 0.11207 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-06-05 21:30 | 10.7 | 3.3 | 182.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 1201.5556 | 0.070404 | 0 |  |  | 1 | 5 | 1 | 1
Lerwick | 1978-06-05 22:30 | 9.7 | 3.3 | 197.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 490.4444 | 0.028737 | 0 |  |  | 1 | 6 | 1 | 2
Lerwick | 1978-06-05 23:30 | 9.4 | 3.4 | 200 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | -220.6667 | -0.01293 | 0 |  |  | 1 | 7 | 1 | 3
Lerwick | 1978-06-06 00:30 | 9.6 | 3.1 | 192.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | -931.7778 | -0.054596 | 0 |  |  | 1 | 8 | 1 | 4
Lerwick | 1978-06-06 01:30 | 9.7 | 2 | 187.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | -1642.8889 | -0.096263 | 0 |  |  | 1 | 9 | 1 | 5
Lerwick | 1978-06-06 02:30 | 9.7 | 1.8 | 185 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | -2354 | -0.13793 | 0 |  |  | 1 | 10 | 1 | 6
Lerwick | 1978-06-06 03:30 | 9.3 | 2.3 | 182.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | -3065.1111 | -0.1796 | 0 |  |  | 1 | 11 | 1 | 7
Lerwick | 1978-06-06 04:30 | 9.1 | 2.6 | 172.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | -3776.2222 | -0.22126 | 0 |  |  | 1 | 12 | 1 | 8
Lerwick | 1978-06-06 05:30 | 10.1 | 3.1 | 162.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | -4487.3333 | -0.26293 | 0 |  |  | 1 | 13 | 1 | 9
Lerwick | 1978-06-06 06:30 | 11 | 3.8 | 162.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | -5198.4444 | -0.3046 | 0 |  |  | 1 | 14 | 1 | 10
Lerwick | 1978-06-06 07:30 | 11.3 | 3.9 | 162.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | -5909.5556 | -0.34626 | 0 |  |  | 1 | 15 | 1 | 11
Lerwick | 1978-06-06 08:30 | 11.5 | 4.1 | 160 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | -6535.4815 | -0.38294 | 1 |  |  | 1 | 16 | 0 | 0
Lerwick | 1978-06-06 09:30 | 11.5 | 4.7 | 165 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | -6939.9259 | -0.40664 | 1 |  |  | 1 | 17 | 0 | 0
Lerwick | 1978-06-06 10:30 | 11.4 | 5.4 | 172.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | -7051.7778 | -0.41319 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-06 11:30 | 11.6 | 6.5 | 175 | 1120 | 730 | 410 | 0 | 410 | 205 | 0 | -6846.7778 | -0.40118 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-06 12:30 | 12.6 | 7.4 | 172.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | -6356.7778 | -0.37247 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-06 13:30 | 13.2 | 7.6 | 170 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | -5711.7778 | -0.33467 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-06 14:30 | 13.2 | 7.2 | 170 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | -5066.7778 | -0.29688 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-06 15:30 | 13.3 | 6.8 | 170 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | -4576.7778 | -0.26817 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-06 16:30 | 12.8 | 6.5 | 167.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | -4176.7778 | -0.24473 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-06 17:30 | 12.1 | 5.6 | 157.5 | 500 | 810 | 490 | 0 | 490 | 245 | 0 | -3931.7778 | -0.23038 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-06 18:30 | 11.7 | 4.9 | 157.5 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | -3916.9444 | -0.22951 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-06 19:30 | 11 | 6.3 | 185 | 760 | 479.6667 | 159.6667 | 0 | 159.6667 | 79.8333 | 0 | -3837.1111 | -0.22483 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-06 20:30 | 11.1 | 8.7 | 212.5 | 2560 | 1660 | 1340 | 0 | 1290 | 645 | 0 | -3192.1111 | -0.18704 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-06 21:30 | 11.2 | 10 | 220 | 3640 | 3100 | 2780 | 0 | 1290 | 645 | 0 | -2547.1111 | -0.14924 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-06 22:30 | 10.6 | 10.4 | 222.5 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | -1902.1111 | -0.11145 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-06 23:30 | 10.3 | 10.2 | 227.5 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | -1257.1111 | -0.073659 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-07 00:30 | 10.1 | 9.4 | 227.5 | 2920 | 3280 | 2960 | 0 | 1290 | 645 | 0 | -612.1111 | -0.035866 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-07 01:30 | 9.7 | 8.4 | 225 | 2200 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 32.8889 | 0.0019271 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-07 02:30 | 9.5 | 7.5 | 222.5 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 677.8889 | 0.03972 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-07 03:30 | 9.4 | 6.2 | 207.5 | 760 | 1300 | 980 | 0 | 980 | 490 | 0 | 1167.8889 | 0.068431 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-07 04:30 | 9.4 | 5.1 | 185 | 340 | 550 | 230 | 0 | 230 | 115 | 0 | 1282.8889 | 0.075169 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-07 05:30 | 9.4 | 5.8 | 177.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 1332.8889 | 0.078099 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-07 06:30 | 9.4 | 7.7 | 187.5 | 1840 | 1170 | 850 | 0 | 850 | 425 | 0 | 1757.8889 | 0.103 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-07 07:30 | 9.6 | 9.5 | 200 | 3280 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 2402.8889 | 0.14079 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-07 08:30 | 9.9 | 10.8 | 210 | 4000 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 3047.8889 | 0.17859 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-07 09:30 | 10.2 | 11.3 | 222.5 | 4300 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 3692.8889 | 0.21638 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-07 10:30 | 10.7 | 11.3 | 235 | 4300 | 4300 | 3980 | 0 | 1290 | 645 | 0 | 4337.8889 | 0.25417 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-07 11:30 | 11.1 | 11 | 240 | 4300 | 4300 | 3980 | 0 | 1290 | 645 | 0 | 4982.8889 | 0.29197 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-07 12:30 | 10.9 | 10.6 | 240 | 4000 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 5627.8889 | 0.32976 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-07 13:30 | 10.9 | 10.6 | 240 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 6272.8889 | 0.36755 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-07 14:30 | 11.4 | 10.8 | 237.5 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 6917.8889 | 0.40535 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-07 15:30 | 11.5 | 10.8 | 235 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 7562.8889 | 0.44314 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-07 16:30 | 11 | 10.8 | 237.5 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 8207.8889 | 0.48093 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-07 17:30 | 10.3 | 10.6 | 237.5 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 8852.8889 | 0.51872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-07 18:30 | 9.9 | 10 | 232.5 | 3640 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 9497.8889 | 0.55652 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-07 19:30 | 9.5 | 9 | 230 | 2920 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 10142.8889 | 0.59431 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-07 20:30 | 8.8 | 8.3 | 227.5 | 2200 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 10787.8889 | 0.6321 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-07 21:30 | 8.8 | 8 | 222.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 11432.8889 | 0.6699 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-07 22:30 | 8.8 | 8 | 220 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 12077.8889 | 0.70769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-07 23:30 | 8.3 | 8.4 | 220 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 12722.8889 | 0.74548 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-08 00:30 | 8.1 | 9 | 220 | 2920 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 13367.8889 | 0.78327 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-08 01:30 | 8.2 | 9.3 | 220 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 14012.8889 | 0.82107 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-08 02:30 | 8.4 | 9.1 | 222.5 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 14657.8889 | 0.85886 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-08 03:30 | 8.5 | 8.7 | 227.5 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 15302.8889 | 0.89665 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-08 04:30 | 8.5 | 8.5 | 232.5 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 15947.8889 | 0.93445 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-08 05:30 | 8.7 | 8.6 | 235 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 16592.8889 | 0.97224 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-08 06:30 | 8.5 | 8.6 | 232.5 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 17237.8889 | 1.01 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-08 07:30 | 8.4 | 8.7 | 230 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 17882.8889 | 1.0478 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-08 08:30 | 9 | 9.5 | 227.5 | 3280 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 18527.8889 | 1.0856 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-08 09:30 | 9.5 | 9.6 | 225 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 19172.8889 | 1.1234 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-08 10:30 | 9.2 | 9 | 227.5 | 2920 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 19817.8889 | 1.1612 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-08 11:30 | 8.3 | 9 | 230 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 20462.8889 | 1.199 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-08 12:30 | 8.8 | 9.1 | 230 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 21107.8889 | 1.2368 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-08 13:30 | 9.8 | 9.1 | 230 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 21752.8889 | 1.2746 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-08 14:30 | 9.8 | 9.3 | 232.5 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 22397.8889 | 1.3124 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-08 15:30 | 9.7 | 9.3 | 237.5 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 23042.8889 | 1.3502 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-08 16:30 | 9.3 | 9.6 | 240 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 23687.8889 | 1.388 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-08 17:30 | 8.4 | 9.9 | 240 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 24332.8889 | 1.4258 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-08 18:30 | 8.5 | 9.4 | 240 | 2920 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 24977.8889 | 1.4635 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-08 19:30 | 8.7 | 8.3 | 240 | 2200 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 25622.8889 | 1.5013 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-08 20:30 | 8.3 | 6.9 | 240 | 1120 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 26267.8889 | 1.5391 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-08 21:30 | 8.1 | 5.8 | 242.5 | 500 | 810 | 490 | 0 | 490 | 245 | 0 | 26512.8889 | 1.5535 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-08 22:30 | 8 | 5.2 | 245 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 26562.8889 | 1.5564 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-08 23:30 | 7.7 | 5.3 | 245 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 26572.8889 | 1.557 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-09 00:30 | 7.9 | 5.9 | 252.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 26622.8889 | 1.5599 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-09 01:30 | 8.5 | 6 | 265 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 26777.8889 | 1.569 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-09 02:30 | 8.6 | 5.6 | 270 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 26932.8889 | 1.5781 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-09 03:30 | 8.4 | 5.5 | 270 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 27022.8889 | 1.5834 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-09 04:30 | 8.4 | 5.8 | 272.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 27112.8889 | 1.5886 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-09 05:30 | 8.3 | 6.3 | 277.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 27267.8889 | 1.5977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-09 06:30 | 8.3 | 7.4 | 280 | 1480 | 1120 | 800 | 0 | 800 | 400 | 0 | 27667.8889 | 1.6212 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-09 07:30 | 8.5 | 8.3 | 280 | 2200 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 28312.8889 | 1.659 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-09 08:30 | 8.5 | 8.6 | 280 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 28957.8889 | 1.6968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-09 09:30 | 8.7 | 9 | 280 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 29602.8889 | 1.7345 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-09 10:30 | 9.1 | 9 | 282.5 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 30247.8889 | 1.7723 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-09 11:30 | 9.4 | 8.6 | 285 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 30892.8889 | 1.8101 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-09 12:30 | 9.9 | 8.7 | 282.5 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 31537.8889 | 1.8479 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-09 13:30 | 10.3 | 9.4 | 280 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 32182.8889 | 1.8857 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-09 14:30 | 9.7 | 9.9 | 280 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 32827.8889 | 1.9235 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-09 15:30 | 9.3 | 9.7 | 280 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 33472.8889 | 1.9613 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-09 16:30 | 9.5 | 9.1 | 280 | 2920 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 34117.8889 | 1.9991 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-09 17:30 | 9.3 | 8.9 | 280 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 34762.8889 | 2.0369 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-09 18:30 | 9.1 | 9.1 | 282.5 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 35407.8889 | 2.0747 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-09 19:30 | 9 | 8.9 | 287.5 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 36052.8889 | 2.1125 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-09 20:30 | 9 | 8.7 | 290 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 36697.8889 | 2.1503 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-09 21:30 | 8.7 | 9.2 | 290 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 37342.8889 | 2.1881 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-09 22:30 | 8.5 | 9.4 | 290 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 37987.8889 | 2.2259 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-09 23:30 | 8.4 | 9.1 | 290 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 38632.8889 | 2.2636 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-10 00:30 | 8.3 | 9 | 290 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 39277.8889 | 2.3014 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-10 01:30 | 8.1 | 9.1 | 290 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 39922.8889 | 2.3392 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-10 02:30 | 7.9 | 9.4 | 292.5 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 40567.8889 | 2.377 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-10 03:30 | 7.7 | 9.5 | 297.5 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 41212.8889 | 2.4148 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-10 04:30 | 7.7 | 9.5 | 302.5 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 41857.8889 | 2.4526 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-10 05:30 | 7.6 | 9.5 | 307.5 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 42502.8889 | 2.4904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-10 06:30 | 7.5 | 9.4 | 310 | 2920 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 43147.8889 | 2.5282 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-10 07:30 | 7.4 | 9.3 | 307.5 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 43792.8889 | 2.566 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-10 08:30 | 7.2 | 9.4 | 302.5 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 44437.8889 | 2.6038 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-10 09:30 | 7.1 | 9.7 | 300 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 45082.8889 | 2.6416 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-10 10:30 | 7.1 | 10.1 | 300 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 45727.8889 | 2.6794 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-10 11:30 | 7.3 | 10.3 | 300 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 46372.8889 | 2.7172 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-10 12:30 | 7.4 | 10.3 | 300 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 47017.8889 | 2.755 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-10 13:30 | 7.3 | 10.3 | 302.5 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 47662.8889 | 2.7927 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-10 14:30 | 7.2 | 10.4 | 307.5 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 48307.8889 | 2.8305 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-10 15:30 | 7.2 | 10.5 | 310 | 4000 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 48952.8889 | 2.8683 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-10 16:30 | 7.6 | 10.4 | 310 | 3640 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 49597.8889 | 2.9061 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-10 17:30 | 7.8 | 10 | 310 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 50242.8889 | 2.9439 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-10 18:30 | 7.7 | 9.3 | 307.5 | 2920 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 50887.8889 | 2.9817 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-10 19:30 | 7.9 | 9 | 300 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 51532.8889 | 3.0195 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-10 20:30 | 7.8 | 9.3 | 290 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 52177.8889 | 3.0573 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-10 21:30 | 7.6 | 9 | 280 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 52822.8889 | 3.0951 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-10 22:30 | 7.9 | 8.9 | 270 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 53467.8889 | 3.1329 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-10 23:30 | 8.3 | 8.9 | 257.5 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 54112.8889 | 3.1707 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-11 00:30 | 8.3 | 9.1 | 247.5 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 54757.8889 | 3.2085 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-11 01:30 | 8.4 | 10.1 | 250 | 3640 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 55402.8889 | 3.2463 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-11 02:30 | 8.9 | 11.6 | 260 | 4472.2222 | 4056.1111 | 3736.1111 | 0 | 1290 | 645 | 0 | 56047.8889 | 3.2841 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-11 03:30 | 9 | 12.7 | 267.5 | 4600 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 56692.8889 | 3.3218 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-11 04:30 | 8.9 | 13.3 | 267.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 57337.8889 | 3.3596 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-11 05:30 | 8.7 | 14.1 | 265 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 57982.8889 | 3.3974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-11 06:30 | 8.5 | 14.7 | 267.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 58627.8889 | 3.4352 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-11 07:30 | 8.5 | 14.4 | 270 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 59272.8889 | 3.473 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-11 08:30 | 8.8 | 13.8 | 270 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 59917.8889 | 3.5108 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-11 09:30 | 8.9 | 13.1 | 272.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 60562.8889 | 3.5486 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-11 10:30 | 9.2 | 12.9 | 280 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 61207.8889 | 3.5864 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-11 11:30 | 9.4 | 12.7 | 290 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 61852.8889 | 3.6242 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-11 12:30 | 9.1 | 12.1 | 295 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 645 | 0 | 62497.8889 | 3.662 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-11 13:30 | 9.1 | 11.6 | 292.5 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 645 | 0 | 63142.8889 | 3.6998 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-11 14:30 | 9.8 | 11.7 | 292.5 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 645 | 0 | 63787.8889 | 3.7376 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-11 15:30 | 9.8 | 12.2 | 297.5 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 645 | 0 | 64432.8889 | 3.7754 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-11 16:30 | 9.4 | 12.8 | 300 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 645 | 0 | 65077.8889 | 3.8132 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-11 17:30 | 8.8 | 13.1 | 302.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 65722.8889 | 3.851 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-11 18:30 | 7.7 | 12.7 | 307.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 66367.8889 | 3.8887 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-11 19:30 | 6.9 | 11.9 | 310 | 4472.2222 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 67012.8889 | 3.9265 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-11 20:30 | 6.5 | 11.6 | 310 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 645 | 0 | 67657.8889 | 3.9643 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-11 21:30 | 6.7 | 11.9 | 310 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 645 | 0 | 68302.8889 | 4.0021 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-11 22:30 | 6.5 | 11.7 | 312.5 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 645 | 0 | 68947.8889 | 4.0399 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-11 23:30 | 6.4 | 11.2 | 317.5 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 69592.8889 | 4.0777 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-12 00:30 | 6 | 10.7 | 320 | 4000 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 70237.8889 | 4.1155 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-12 01:30 | 5.7 | 10.1 | 320 | 3640 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 70882.8889 | 4.1533 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-12 02:30 | 5.6 | 9.3 | 320 | 2920 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 71527.8889 | 4.1911 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-12 03:30 | 5.7 | 8.6 | 320 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 72172.8889 | 4.2289 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-12 04:30 | 6.1 | 8.9 | 322.5 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 72817.8889 | 4.2667 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-12 05:30 | 6.2 | 9.4 | 327.5 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 73462.8889 | 4.3045 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-12 06:30 | 6.3 | 9.4 | 330 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 74107.8889 | 4.3423 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-12 07:30 | 6.8 | 9.3 | 330 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 74752.8889 | 4.3801 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-12 08:30 | 7.6 | 9.3 | 330 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 75397.8889 | 4.4178 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-12 09:30 | 8 | 9.1 | 330 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 76042.8889 | 4.4556 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-12 10:30 | 8.3 | 9 | 330 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 76687.8889 | 4.4934 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-12 11:30 | 8.3 | 9 | 330 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 77332.8889 | 4.5312 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-12 12:30 | 8.5 | 8.9 | 330 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 77977.8889 | 4.569 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-12 13:30 | 9 | 8.8 | 330 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 78622.8889 | 4.6068 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-12 14:30 | 9 | 8.6 | 330 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 79267.8889 | 4.6446 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-12 15:30 | 8.8 | 8.1 | 330 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 79912.8889 | 4.6824 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-12 16:30 | 8.7 | 7.7 | 330 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 80557.8889 | 4.7202 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-12 17:30 | 8.3 | 7.8 | 332.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 81202.8889 | 4.758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-12 18:30 | 7.7 | 7.7 | 337.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 81847.8889 | 4.7958 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-12 19:30 | 7.5 | 7.2 | 337.5 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 82492.8889 | 4.8336 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-12 20:30 | 7.3 | 6.8 | 332.5 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 82982.8889 | 4.8623 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-12 21:30 | 7.1 | 6.5 | 335 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 83382.8889 | 4.8857 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-12 22:30 | 6.9 | 6.4 | 345 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 83692.8889 | 4.9039 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-12 23:30 | 6.5 | 6.4 | 350 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 83912.8889 | 4.9168 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-13 00:30 | 6.2 | 6.3 | 350 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 84132.8889 | 4.9297 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-13 01:30 | 6.1 | 6 | 347.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 84352.8889 | 4.9426 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-13 02:30 | 6 | 5.8 | 345 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 84507.8889 | 4.9516 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-13 03:30 | 6 | 5.8 | 345 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 84597.8889 | 4.9569 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-13 04:30 | 6.2 | 5.9 | 342.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 84687.8889 | 4.9622 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-13 05:30 | 6.5 | 6.1 | 340 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 84842.8889 | 4.9713 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-13 06:30 | 7 | 6.8 | 342.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 85152.8889 | 4.9894 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-13 07:30 | 7.4 | 7.2 | 347.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 85642.8889 | 5.0181 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-13 08:30 | 7.9 | 7.2 | 175 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 86222.8889 | 5.0521 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-13 09:30 | 8.5 | 7.1 | 7.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 86802.8889 | 5.0861 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-13 10:30 | 8.8 | 6.8 | 20 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 87292.8889 | 5.1148 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-13 11:30 | 9.1 | 6.8 | 25 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 87692.8889 | 5.1383 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-13 12:30 | 9.3 | 7.1 | 22.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 88182.8889 | 5.167 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-13 13:30 | 9.8 | 6.9 | 20 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 88672.8889 | 5.1957 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-13 14:30 | 10.1 | 6.4 | 20 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 88982.8889 | 5.2138 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-13 15:30 | 10.2 | 6.2 | 20 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 89202.8889 | 5.2267 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-13 16:30 | 10.3 | 6.2 | 20 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 89422.8889 | 5.2396 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-13 17:30 | 9.9 | 6.3 | 20 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 89642.8889 | 5.2525 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-13 18:30 | 9.2 | 6.3 | 20 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 89862.8889 | 5.2654 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-13 19:30 | 8.6 | 5.8 | 17.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 90017.8889 | 5.2745 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-13 20:30 | 8.2 | 5.2 | 10 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 90067.8889 | 5.2774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-13 21:30 | 8 | 5 | 2.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 90077.8889 | 5.278 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-13 22:30 | 8 | 5.2 | 2.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 90087.8889 | 5.2786 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-13 23:30 | 7.9 | 5.5 | 7.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 90137.8889 | 5.2815 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-14 00:30 | 7.9 | 5.8 | 10 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 90227.8889 | 5.2868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-14 01:30 | 7.7 | 5.9 | 10 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 90317.8889 | 5.2921 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-14 02:30 | 7.6 | 5.4 | 5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 90367.8889 | 5.295 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-06-14 03:30 | 7.7 | 4.4 | 172.5 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 90119.7407 | 5.2805 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-06-14 04:30 | 7.5 | 4 | 345 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 89579 | 5.2488 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-06-14 05:30 | 7.3 | 4.2 | 177.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 89038.2593 | 5.2171 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-06-14 06:30 | 7.8 | 4.4 | 17.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 88497.5185 | 5.1854 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-06-14 07:30 | 8.6 | 4.1 | 22.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 87956.7778 | 5.1537 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-06-14 08:30 | 8.9 | 3.7 | 20 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 87330.8519 | 5.117 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-06-14 09:30 | 9.1 | 3.4 | 20 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 86619.7407 | 5.0754 | 0 |  |  | 1 | 8 | 1 | 1
Lerwick | 1978-06-14 10:30 | 9.3 | 2.7 | 42.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 85908.6296 | 5.0337 | 0 |  |  | 1 | 9 | 1 | 2
Lerwick | 1978-06-14 11:30 | 9.6 | 2.2 | 95 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 85197.5185 | 4.992 | 0 |  |  | 1 | 10 | 1 | 3
Lerwick | 1978-06-14 12:30 | 10.1 | 2.7 | 130 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 84486.4074 | 4.9504 | 0 |  |  | 1 | 11 | 1 | 4
Lerwick | 1978-06-14 13:30 | 10.3 | 3.6 | 140 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 83775.2963 | 4.9087 | 0 |  |  | 1 | 12 | 1 | 5
Lerwick | 1978-06-14 14:30 | 10.3 | 4.1 | 155 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 83149.3704 | 4.872 | 1 |  |  | 1 | 13 | 0 | 0
Lerwick | 1978-06-14 15:30 | 10.2 | 4.4 | 175 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 82608.6296 | 4.8403 | 1 |  |  | 1 | 14 | 0 | 0
Lerwick | 1978-06-14 16:30 | 9.8 | 4.4 | 185 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 82067.8889 | 4.8087 | 1 |  |  | 1 | 15 | 0 | 0
Lerwick | 1978-06-14 17:30 | 9.6 | 4.7 | 175 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 81663.4444 | 4.785 | 1 |  |  | 1 | 16 | 0 | 0
Lerwick | 1978-06-14 18:30 | 9.4 | 4.6 | 162.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 81395.2963 | 4.7693 | 1 |  |  | 1 | 17 | 0 | 0
Lerwick | 1978-06-14 19:30 | 9 | 4.2 | 157.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 80990.8519 | 4.7456 | 1 |  |  | 1 | 18 | 0 | 0
Lerwick | 1978-06-14 20:30 | 8.4 | 4.4 | 152.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 80450.1111 | 4.7139 | 1 |  |  | 1 | 19 | 0 | 0
Lerwick | 1978-06-14 21:30 | 8 | 5.3 | 150 | 340 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 80201.963 | 4.6993 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-14 22:30 | 8 | 5.8 | 147.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 80251.963 | 4.7023 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-14 23:30 | 7.8 | 6.1 | 142.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 80406.963 | 4.7113 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-15 00:30 | 7.8 | 6.5 | 140 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 80716.963 | 4.7295 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-15 01:30 | 7.9 | 6.7 | 140 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 81116.963 | 4.7529 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-15 02:30 | 7.9 | 6.7 | 140 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 81516.963 | 4.7764 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-15 03:30 | 8 | 6.7 | 140 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 81916.963 | 4.7998 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-15 04:30 | 8.1 | 6.8 | 140 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 82316.963 | 4.8233 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-15 05:30 | 8 | 6.8 | 137.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 82716.963 | 4.8467 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-15 06:30 | 8.3 | 6.5 | 132.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 83116.963 | 4.8701 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-15 07:30 | 8.8 | 6.5 | 127.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 83516.963 | 4.8936 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-15 08:30 | 9.5 | 6.7 | 120 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 83916.963 | 4.917 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-15 09:30 | 10.3 | 6.7 | 112.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 84316.963 | 4.9404 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-15 10:30 | 10.4 | 6.5 | 110 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 84716.963 | 4.9639 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-15 11:30 | 10.6 | 6.1 | 112.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 85026.963 | 4.982 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-15 12:30 | 11 | 5.8 | 117.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 85181.963 | 4.9911 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-15 13:30 | 11 | 5.5 | 117.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 85271.963 | 4.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-15 14:30 | 11.3 | 5.4 | 107.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 85321.963 | 4.9993 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-15 15:30 | 11.3 | 5.6 | 90 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 85371.963 | 5.0023 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-15 16:30 | 11.1 | 6.3 | 72.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 85526.963 | 5.0113 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-15 17:30 | 11 | 6.8 | 60 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 85836.963 | 5.0295 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-15 18:30 | 10.8 | 6.7 | 50 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 86236.963 | 5.0529 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-15 19:30 | 10.3 | 6.3 | 40 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 86546.963 | 5.0711 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-15 20:30 | 9.8 | 6.4 | 32.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 86766.963 | 5.084 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-15 21:30 | 9.4 | 6.9 | 32.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 87076.963 | 5.1022 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-15 22:30 | 9.2 | 7.2 | 37.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 87566.963 | 5.1309 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-15 23:30 | 9 | 7.2 | 40 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 88146.963 | 5.1649 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-16 00:30 | 8.7 | 7.1 | 37.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 88726.963 | 5.1988 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-16 01:30 | 8.2 | 6.8 | 32.5 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 89216.963 | 5.2276 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-16 02:30 | 8 | 6.8 | 27.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 89616.963 | 5.251 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-16 03:30 | 8 | 7.1 | 25 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 90106.963 | 5.2797 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-16 04:30 | 8 | 7.4 | 25 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 90686.963 | 5.3137 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-16 05:30 | 8.2 | 8.1 | 22.5 | 2200 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 91331.963 | 5.3515 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-16 06:30 | 8.3 | 8.5 | 20 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 91976.963 | 5.3893 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-16 07:30 | 8.3 | 8.2 | 17.5 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 92621.963 | 5.4271 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-16 08:30 | 8.7 | 8 | 12.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 93266.963 | 5.4649 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-16 09:30 | 9 | 8.5 | 10 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 93911.963 | 5.5027 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-16 10:30 | 9.4 | 9.4 | 12.5 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 94556.963 | 5.5404 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-16 11:30 | 9.8 | 10.1 | 15 | 3640 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 95201.963 | 5.5782 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-16 12:30 | 10.6 | 10.6 | 12.5 | 4000 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 95846.963 | 5.616 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-16 13:30 | 11.7 | 10.6 | 12.5 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 96491.963 | 5.6538 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-16 14:30 | 11.2 | 10.7 | 17.5 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 97136.963 | 5.6916 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-16 15:30 | 10.3 | 11.2 | 20 | 4300 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 97781.963 | 5.7294 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-16 16:30 | 10.2 | 11.1 | 17.5 | 4300 | 4300 | 3980 | 0 | 1290 | 645 | 0 | 98426.963 | 5.7672 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-16 17:30 | 9.9 | 10.5 | 12.5 | 4000 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 99071.963 | 5.805 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-16 18:30 | 9.3 | 10.3 | 10 | 3640 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 99716.963 | 5.8428 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-16 19:30 | 9.1 | 10.3 | 10 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 100361.963 | 5.8806 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-16 20:30 | 8.9 | 10.5 | 10 | 4000 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 101006.963 | 5.9184 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-16 21:30 | 8.5 | 10.8 | 7.5 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 101651.963 | 5.9562 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-16 22:30 | 8.3 | 10.5 | 2.5 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 102296.963 | 5.994 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-16 23:30 | 8 | 10.5 | 0 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 102941.963 | 6.0318 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-17 00:30 | 7.7 | 11.6 | 2.5 | 4472.2222 | 4236.1111 | 3916.1111 | 0 | 1290 | 645 | 0 | 103586.963 | 6.0695 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-17 01:30 | 7.7 | 12.4 | 7.5 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 645 | 0 | 104231.963 | 6.1073 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-17 02:30 | 7.7 | 11.7 | 7.5 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 645 | 0 | 104876.963 | 6.1451 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-17 03:30 | 7.7 | 10.9 | 5 | 4000 | 4236.1111 | 3916.1111 | 0 | 1290 | 645 | 0 | 105521.963 | 6.1829 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-17 04:30 | 7.7 | 10.8 | 7.5 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 106166.963 | 6.2207 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-17 05:30 | 7.8 | 10.6 | 10 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 106811.963 | 6.2585 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-17 06:30 | 8.1 | 10.5 | 10 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 107456.963 | 6.2963 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-17 07:30 | 9.1 | 11 | 12.5 | 4300 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 108101.963 | 6.3341 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-17 08:30 | 9.6 | 11.6 | 15 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 108746.963 | 6.3719 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-17 09:30 | 9.6 | 11.3 | 15 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 109391.963 | 6.4097 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-17 10:30 | 10.2 | 10.4 | 17.5 | 3640 | 3970 | 3650 | 0 | 1290 | 645 | 0 | 110036.963 | 6.4475 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-17 11:30 | 10.7 | 9.9 | 20 | 3280 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 110681.963 | 6.4853 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-17 12:30 | 11 | 9.5 | 20 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 111326.963 | 6.5231 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-17 13:30 | 11.3 | 8.6 | 20 | 2560 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 111971.963 | 6.5609 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-17 14:30 | 11.6 | 7.8 | 20 | 1840 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 112616.963 | 6.5987 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-17 15:30 | 11.6 | 7.9 | 20 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 113261.963 | 6.6364 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-17 16:30 | 11.4 | 8.1 | 17.5 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 113906.963 | 6.6742 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-17 17:30 | 10.9 | 8 | 12.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 114551.963 | 6.712 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-17 18:30 | 10.2 | 7.6 | 10 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 115196.963 | 6.7498 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-17 19:30 | 9.5 | 6.9 | 10 | 1120 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 115776.963 | 6.7838 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-17 20:30 | 8.8 | 6.5 | 10 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 116176.963 | 6.8072 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-17 21:30 | 8.3 | 6.1 | 10 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 116486.963 | 6.8254 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-17 22:30 | 7.7 | 5.6 | 10 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 116641.963 | 6.8345 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-17 23:30 | 7.5 | 5.1 | 7.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 116691.963 | 6.8374 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-06-18 00:30 | 7.4 | 4.6 | 2.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 116580.1111 | 6.8309 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-06-18 01:30 | 7.3 | 4.1 | 175 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 116175.6667 | 6.8072 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-06-18 02:30 | 7.1 | 3.6 | 342.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 115549.7407 | 6.7705 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-06-18 03:30 | 6.8 | 3.2 | 335 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 114838.6296 | 6.7288 | 0 |  |  | 1 | 5 | 1 | 1
Lerwick | 1978-06-18 04:30 | 6.6 | 2.6 | 345 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 114127.5185 | 6.6872 | 0 |  |  | 1 | 6 | 1 | 2
Lerwick | 1978-06-18 05:30 | 6.7 | 1.8 | 345 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 113416.4074 | 6.6455 | 0 |  |  | 1 | 7 | 1 | 3
Lerwick | 1978-06-18 06:30 | 7.1 | 1.6 | 317.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 112705.2963 | 6.6038 | 0 |  |  | 1 | 8 | 1 | 4
Lerwick | 1978-06-18 07:30 | 7.5 | 2 | 290 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 111994.1852 | 6.5622 | 0 |  |  | 1 | 9 | 1 | 5
Lerwick | 1978-06-18 08:30 | 7.8 | 2.7 | 270 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 111283.0741 | 6.5205 | 0 |  |  | 1 | 10 | 1 | 6
Lerwick | 1978-06-18 09:30 | 8.3 | 3.8 | 257.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 110571.963 | 6.4788 | 0 |  |  | 1 | 11 | 1 | 7
Lerwick | 1978-06-18 10:30 | 8.8 | 4.7 | 252.5 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 110082.3333 | 6.4501 | 1 |  |  | 1 | 12 | 0 | 0
Lerwick | 1978-06-18 11:30 | 9.2 | 5.3 | 250 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 109970.4815 | 6.4436 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-18 12:30 | 9.4 | 5.5 | 250 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 110020.4815 | 6.4465 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-18 13:30 | 9.4 | 5.2 | 250 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 110070.4815 | 6.4494 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-18 14:30 | 9.2 | 5 | 250 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 110080.4815 | 6.45 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-18 15:30 | 8.8 | 5.2 | 250 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 110090.4815 | 6.4506 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-18 16:30 | 8.5 | 5.6 | 247.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 110140.4815 | 6.4535 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-18 17:30 | 8.8 | 6 | 242.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 110295.4815 | 6.4626 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-18 18:30 | 8.8 | 6.3 | 240 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 110515.4815 | 6.4755 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-18 19:30 | 8.4 | 6.7 | 242.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 110825.4815 | 6.4937 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-18 20:30 | 8.1 | 6.8 | 242.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 111225.4815 | 6.5171 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-18 21:30 | 8.1 | 6.4 | 232.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 111535.4815 | 6.5353 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-18 22:30 | 8.2 | 6.2 | 220 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 111755.4815 | 6.5482 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-18 23:30 | 8.3 | 6.2 | 212.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 111975.4815 | 6.5611 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-19 00:30 | 8.5 | 6.4 | 210 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 112195.4815 | 6.574 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-19 01:30 | 8.6 | 7.3 | 210 | 1480 | 1120 | 800 | 0 | 800 | 400 | 0 | 112595.4815 | 6.5974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-19 02:30 | 8.6 | 8.7 | 210 | 2560 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 113240.4815 | 6.6352 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-19 03:30 | 8.7 | 10 | 210 | 3640 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 113885.4815 | 6.673 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-19 04:30 | 8.7 | 10.7 | 210 | 4000 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 114530.4815 | 6.7108 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-19 05:30 | 8.5 | 11.1 | 210 | 4300 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 115175.4815 | 6.7486 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-19 06:30 | 8.4 | 10.5 | 215 | 4000 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 115820.4815 | 6.7864 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-19 07:30 | 8.5 | 8.9 | 225 | 2560 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 116465.4815 | 6.8241 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-19 08:30 | 8.7 | 8.3 | 232.5 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 117110.4815 | 6.8619 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-19 09:30 | 9.1 | 9 | 237.5 | 2920 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 117755.4815 | 6.8997 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-19 10:30 | 10.5 | 9.9 | 240 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 118400.4815 | 6.9375 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-19 11:30 | 11.5 | 10 | 240 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 119045.4815 | 6.9753 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-19 12:30 | 11.3 | 9.5 | 240 | 3280 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 119690.4815 | 7.0131 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-19 13:30 | 10.3 | 9.6 | 240 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 120335.4815 | 7.0509 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-19 14:30 | 10.5 | 10.2 | 240 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 120980.4815 | 7.0887 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-19 15:30 | 11.5 | 10.4 | 240 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 121625.4815 | 7.1265 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-19 16:30 | 11.2 | 10.3 | 237.5 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 122270.4815 | 7.1643 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-19 17:30 | 11 | 10.1 | 232.5 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 122915.4815 | 7.2021 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-19 18:30 | 10.7 | 9.6 | 230 | 3280 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 123560.4815 | 7.2399 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-19 19:30 | 10.2 | 9 | 230 | 2920 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 124205.4815 | 7.2777 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-19 20:30 | 9.5 | 8.6 | 227.5 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 124850.4815 | 7.3155 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-19 21:30 | 8.9 | 8.2 | 222.5 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 125495.4815 | 7.3533 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-19 22:30 | 8.8 | 7.8 | 217.5 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 126140.4815 | 7.391 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-19 23:30 | 8.6 | 7.8 | 212.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 126785.4815 | 7.4288 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-20 00:30 | 8.5 | 8.2 | 205 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 127430.4815 | 7.4666 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-20 01:30 | 8.8 | 8.9 | 195 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 128075.4815 | 7.5044 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-20 02:30 | 9.2 | 10.1 | 195 | 3640 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 128720.4815 | 7.5422 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-20 03:30 | 9.1 | 11.7 | 205 | 4472.2222 | 4056.1111 | 3736.1111 | 0 | 1290 | 645 | 0 | 129365.4815 | 7.58 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-20 04:30 | 8.9 | 12.7 | 210 | 4600 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 130010.4815 | 7.6178 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-20 05:30 | 9.2 | 12.7 | 210 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 130655.4815 | 7.6556 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-20 06:30 | 9.3 | 12.2 | 210 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 645 | 0 | 131300.4815 | 7.6934 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-20 07:30 | 9.5 | 11.9 | 210 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 645 | 0 | 131945.4815 | 7.7312 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-20 08:30 | 10.7 | 11.4 | 207.5 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 132590.4815 | 7.769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-20 09:30 | 11.4 | 10.2 | 195 | 3640 | 3970 | 3650 | 0 | 1290 | 645 | 0 | 133235.4815 | 7.8068 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-20 10:30 | 11.1 | 9.5 | 177.5 | 3280 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 133880.4815 | 7.8446 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-20 11:30 | 10.9 | 9.9 | 175 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 134525.4815 | 7.8824 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-20 12:30 | 11.1 | 10.4 | 185 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 135170.4815 | 7.9201 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-20 13:30 | 10.3 | 10.2 | 195 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 135815.4815 | 7.9579 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-20 14:30 | 9.8 | 9.4 | 200 | 2920 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 136460.4815 | 7.9957 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-20 15:30 | 10 | 8.8 | 195 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 137105.4815 | 8.0335 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-20 16:30 | 9.7 | 8.8 | 190 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 137750.4815 | 8.0713 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-20 17:30 | 9.4 | 8.9 | 195 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 138395.4815 | 8.1091 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-20 18:30 | 10.3 | 9 | 202.5 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 139040.4815 | 8.1469 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-20 19:30 | 10.9 | 8.5 | 202.5 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 139685.4815 | 8.1847 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-20 20:30 | 10.3 | 7.9 | 202.5 | 1840 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 140330.4815 | 8.2225 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-20 21:30 | 9.8 | 7.3 | 207.5 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 140975.4815 | 8.2603 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-20 22:30 | 9.3 | 6.7 | 215 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 141465.4815 | 8.289 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-20 23:30 | 9.1 | 6 | 225 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 141775.4815 | 8.3072 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-21 00:30 | 8.7 | 5 | 237.5 | 340 | 550 | 230 | 0 | 230 | 115 | 0 | 141890.4815 | 8.3139 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-06-21 01:30 | 8.2 | 4 | 250 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 141642.3333 | 8.2994 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-06-21 02:30 | 7.6 | 3.7 | 255 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 141016.4074 | 8.2627 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-06-21 03:30 | 7.3 | 3.9 | 255 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 140305.2963 | 8.221 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-06-21 04:30 | 7.6 | 4 | 250 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 139679.3704 | 8.1843 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-06-21 05:30 | 7.8 | 4.2 | 245 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 139138.6296 | 8.1527 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-06-21 06:30 | 8.4 | 4.4 | 245 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 138597.8889 | 8.121 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-06-21 07:30 | 9.3 | 4.7 | 240 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 138193.4444 | 8.0973 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-06-21 08:30 | 9.6 | 4.9 | 240 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 137925.2963 | 8.0816 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-06-21 09:30 | 10.2 | 4.9 | 252.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 137657.1481 | 8.0658 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-06-21 10:30 | 10.2 | 4.7 | 255 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 137389 | 8.0501 | 1 |  |  | 1 | 11 | 0 | 0
Lerwick | 1978-06-21 11:30 | 10.2 | 4.4 | 245 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 136984.5556 | 8.0264 | 1 |  |  | 1 | 12 | 0 | 0
Lerwick | 1978-06-21 12:30 | 11.4 | 4.2 | 240 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 136443.8148 | 7.9948 | 1 |  |  | 1 | 13 | 0 | 0
Lerwick | 1978-06-21 13:30 | 12.2 | 4 | 220 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 135903.0741 | 7.9631 | 1 |  |  | 1 | 14 | 0 | 0
Lerwick | 1978-06-21 14:30 | 12.7 | 4.2 | 180 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 135362.3333 | 7.9314 | 1 |  |  | 1 | 15 | 0 | 0
Lerwick | 1978-06-21 15:30 | 12.4 | 4.4 | 155 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 134821.5926 | 7.8997 | 1 |  |  | 1 | 16 | 0 | 0
Lerwick | 1978-06-21 16:30 | 12.2 | 4 | 147.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 134280.8519 | 7.868 | 1 |  |  | 1 | 17 | 0 | 0
Lerwick | 1978-06-21 17:30 | 11.7 | 3.3 | 142.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 133654.9259 | 7.8313 | 1 |  |  | 1 | 18 | 0 | 0
Lerwick | 1978-06-21 18:30 | 11 | 3.1 | 132.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 132943.8148 | 7.7897 | 0 |  |  | 1 | 19 | 1 | 1
Lerwick | 1978-06-21 19:30 | 10.5 | 3.2 | 107.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 132232.7037 | 7.748 | 0 |  |  | 1 | 20 | 1 | 2
Lerwick | 1978-06-21 20:30 | 9.7 | 3.6 | 75 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 131521.5926 | 7.7063 | 0 |  |  | 1 | 21 | 1 | 3
Lerwick | 1978-06-21 21:30 | 9.2 | 4.4 | 60 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 130895.6667 | 7.6697 | 1 |  |  | 1 | 22 | 0 | 0
Lerwick | 1978-06-21 22:30 | 8.8 | 5.4 | 57.5 | 340 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 130647.5185 | 7.6551 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-21 23:30 | 8.5 | 6 | 50 | 760 | 550 | 230 | 0 | 230 | 115 | 0 | 130762.5185 | 7.6619 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-22 00:30 | 8.8 | 6.6 | 42.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 131072.5185 | 7.68 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-22 01:30 | 9.1 | 7.5 | 40 | 1840 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 131652.5185 | 7.714 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-22 02:30 | 9.1 | 8.2 | 40 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 132297.5185 | 7.7518 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-22 03:30 | 9 | 8.7 | 37.5 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 132942.5185 | 7.7896 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-22 04:30 | 9 | 9.4 | 32.5 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 133587.5185 | 7.8274 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-22 05:30 | 8.9 | 10.1 | 30 | 3640 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 134232.5185 | 7.8652 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-22 06:30 | 8.9 | 10.9 | 27.5 | 4000 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 134877.5185 | 7.903 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-22 07:30 | 9.1 | 11.3 | 25 | 4300 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 135522.5185 | 7.9408 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-22 08:30 | 9.1 | 10.3 | 30 | 3640 | 3970 | 3650 | 0 | 1290 | 645 | 0 | 136167.5185 | 7.9786 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-22 09:30 | 9.3 | 8.2 | 40 | 2200 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 136812.5185 | 8.0164 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-22 10:30 | 9.7 | 6.8 | 60 | 1120 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 137457.5185 | 8.0542 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-22 11:30 | 10.2 | 6.3 | 90 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 137767.5185 | 8.0723 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-22 12:30 | 10.4 | 6.2 | 107.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 137987.5185 | 8.0852 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-22 13:30 | 10.5 | 6.3 | 110 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 138207.5185 | 8.0981 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-22 14:30 | 10.8 | 6.4 | 107.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 138427.5185 | 8.111 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-22 15:30 | 10.9 | 6.4 | 102.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 138647.5185 | 8.1239 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-22 16:30 | 10.4 | 6.5 | 97.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 138957.5185 | 8.142 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-22 17:30 | 10.2 | 6.4 | 92.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 139267.5185 | 8.1602 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-22 18:30 | 10.4 | 5.8 | 87.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 139422.5185 | 8.1693 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-22 19:30 | 10.4 | 4.9 | 80 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 139437.3519 | 8.1702 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-06-22 20:30 | 10.3 | 4 | 72.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 139032.9074 | 8.1465 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-06-22 21:30 | 10.2 | 2.9 | 70 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 138406.9815 | 8.1098 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-06-22 22:30 | 10.1 | 1.7 | 77.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 137695.8704 | 8.0681 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-06-22 23:30 | 10.2 | 1.7 | 97.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 136984.7593 | 8.0265 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-06-23 00:30 | 10.2 | 2.6 | 112.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 136273.6481 | 7.9848 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-06-23 01:30 | 10 | 2.9 | 105 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 135562.537 | 7.9431 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-06-23 02:30 | 10 | 3 | 90 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 134851.4259 | 7.9015 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-06-23 03:30 | 10 | 3.9 | 90 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 134140.3148 | 7.8598 | 0 |  |  | 1 | 9 | 1 | 6
Lerwick | 1978-06-23 04:30 | 9.9 | 4.7 | 97.5 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 133650.6852 | 7.8311 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-06-23 05:30 | 9.9 | 4.9 | 100 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 133382.537 | 7.8154 | 1 |  |  | 1 | 11 | 0 | 0
Lerwick | 1978-06-23 06:30 | 10 | 4.7 | 102.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 133114.3889 | 7.7997 | 1 |  |  | 1 | 12 | 0 | 0
Lerwick | 1978-06-23 07:30 | 9.9 | 4.4 | 107.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 132709.9444 | 7.776 | 1 |  |  | 1 | 13 | 0 | 0
Lerwick | 1978-06-23 08:30 | 10.2 | 4.4 | 110 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 132169.2037 | 7.7443 | 1 |  |  | 1 | 14 | 0 | 0
Lerwick | 1978-06-23 09:30 | 10.4 | 4.5 | 110 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 131764.7593 | 7.7206 | 1 |  |  | 1 | 15 | 0 | 0
Lerwick | 1978-06-23 10:30 | 10.4 | 4.5 | 110 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 131496.6111 | 7.7049 | 1 |  |  | 1 | 16 | 0 | 0
Lerwick | 1978-06-23 11:30 | 11 | 4.7 | 110 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 131228.463 | 7.6892 | 1 |  |  | 1 | 17 | 0 | 0
Lerwick | 1978-06-23 12:30 | 11.6 | 5.2 | 110 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 131116.6111 | 7.6826 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-23 13:30 | 11.9 | 5.4 | 110 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 131126.6111 | 7.6832 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-23 14:30 | 11.9 | 5.2 | 110 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 131136.6111 | 7.6838 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-06-23 15:30 | 11.7 | 4.7 | 110 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 131024.7593 | 7.6772 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-06-23 16:30 | 11.6 | 4.4 | 110 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 130620.3148 | 7.6535 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-06-23 17:30 | 11.8 | 4.2 | 110 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 130079.5741 | 7.6219 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-06-23 18:30 | 12.2 | 3.9 | 102.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 129453.6481 | 7.5852 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-06-23 19:30 | 11.7 | 3.6 | 82.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 128742.537 | 7.5435 | 0 |  |  | 1 | 6 | 1 | 1
Lerwick | 1978-06-23 20:30 | 10.7 | 3.2 | 60 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 128031.4259 | 7.5018 | 0 |  |  | 1 | 7 | 1 | 2
Lerwick | 1978-06-23 21:30 | 10.1 | 3.2 | 42.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 127320.3148 | 7.4602 | 0 |  |  | 1 | 8 | 1 | 3
Lerwick | 1978-06-23 22:30 | 9.3 | 3.4 | 32.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 126609.2037 | 7.4185 | 0 |  |  | 1 | 9 | 1 | 4
Lerwick | 1978-06-23 23:30 | 9.1 | 4 | 25 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 125983.2778 | 7.3818 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-06-24 00:30 | 9.1 | 4.7 | 12.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 125578.8333 | 7.3581 | 1 |  |  | 1 | 11 | 0 | 0
Lerwick | 1978-06-24 01:30 | 8.9 | 5.4 | 2.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 125466.9815 | 7.3516 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-24 02:30 | 8.9 | 6.1 | 0 | 760 | 550 | 230 | 0 | 230 | 115 | 0 | 125581.9815 | 7.3583 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-24 03:30 | 8.6 | 6.3 | 177.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 125801.9815 | 7.3712 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-24 04:30 | 8.5 | 6.4 | 350 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 126021.9815 | 7.3841 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-24 05:30 | 9 | 7.2 | 342.5 | 1480 | 1120 | 800 | 0 | 800 | 400 | 0 | 126421.9815 | 7.4075 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-24 06:30 | 9.8 | 8.2 | 340 | 2200 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 127066.9815 | 7.4453 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-24 07:30 | 10.3 | 9.3 | 340 | 2920 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 127711.9815 | 7.4831 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-24 08:30 | 11.2 | 10.1 | 337.5 | 3640 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 128356.9815 | 7.5209 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-24 09:30 | 12.5 | 10.5 | 332.5 | 4000 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 129001.9815 | 7.5587 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-24 10:30 | 12.8 | 10.2 | 330 | 3640 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 129646.9815 | 7.5965 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-24 11:30 | 12.7 | 10 | 332.5 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 130291.9815 | 7.6343 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-24 12:30 | 12.9 | 10 | 337.5 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 130936.9815 | 7.6721 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-24 13:30 | 12.7 | 9.9 | 342.5 | 3280 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 131581.9815 | 7.7099 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-24 14:30 | 12.5 | 9.1 | 350 | 2920 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 132226.9815 | 7.7477 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-24 15:30 | 12.8 | 8 | 177.5 | 2200 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 132871.9815 | 7.7855 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-24 16:30 | 12.8 | 7.5 | 177.5 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 133516.9815 | 7.8233 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-24 17:30 | 11.8 | 7.6 | 177.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 134161.9815 | 7.8611 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-24 18:30 | 11.4 | 8.2 | 5 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 134806.9815 | 7.8988 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-24 19:30 | 11.3 | 8.6 | 7.5 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 135451.9815 | 7.9366 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-24 20:30 | 11 | 7.7 | 180 | 1840 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 136096.9815 | 7.9744 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-24 21:30 | 10.8 | 6.7 | 350 | 1120 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 136676.9815 | 8.0084 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-24 22:30 | 10.5 | 6.9 | 340 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 137076.9815 | 8.0319 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-24 23:30 | 10.4 | 7.8 | 332.5 | 1840 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 137656.9815 | 8.0658 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-25 00:30 | 9.9 | 7.9 | 332.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 138301.9815 | 8.1036 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-25 01:30 | 9.2 | 7.4 | 332.5 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 138946.9815 | 8.1414 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-25 02:30 | 9.1 | 7.1 | 327.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 139526.9815 | 8.1754 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-25 03:30 | 8.9 | 7.1 | 325 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 140106.9815 | 8.2094 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-25 04:30 | 8.4 | 7.2 | 322.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 140686.9815 | 8.2434 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-25 05:30 | 8 | 6.9 | 320 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 141176.9815 | 8.2721 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-25 06:30 | 8 | 6.8 | 320 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 141576.9815 | 8.2955 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-25 07:30 | 8 | 7.1 | 320 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 142066.9815 | 8.3242 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-25 08:30 | 7.9 | 7.1 | 320 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 142646.9815 | 8.3582 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-25 09:30 | 7.8 | 6.8 | 320 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 143136.9815 | 8.3869 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-25 10:30 | 7.8 | 6.7 | 317.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 143536.9815 | 8.4104 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-25 11:30 | 7.9 | 6.9 | 310 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 143936.9815 | 8.4338 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-25 12:30 | 8.2 | 7.4 | 302.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 144426.9815 | 8.4625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-25 13:30 | 8.5 | 7.8 | 302.5 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 145071.9815 | 8.5003 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-25 14:30 | 8.5 | 7.8 | 307.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 145716.9815 | 8.5381 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-25 15:30 | 8.4 | 7.6 | 310 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 146361.9815 | 8.5759 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-25 16:30 | 8.2 | 7.5 | 312.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 147006.9815 | 8.6137 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-25 17:30 | 7.9 | 7.2 | 315 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 147651.9815 | 8.6515 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-25 18:30 | 7.5 | 6.8 | 315 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 148141.9815 | 8.6802 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-25 19:30 | 7.4 | 6.7 | 315 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 148541.9815 | 8.7036 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-25 20:30 | 7.4 | 6.3 | 312.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 148851.9815 | 8.7218 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-25 21:30 | 7.4 | 5.6 | 310 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 149006.9815 | 8.7309 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-25 22:30 | 7.4 | 5.5 | 310 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 149096.9815 | 8.7362 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-25 23:30 | 7.2 | 5.9 | 312.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 149186.9815 | 8.7414 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-26 00:30 | 6.8 | 6.3 | 317.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 149341.9815 | 8.7505 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-26 01:30 | 6.6 | 6.1 | 320 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 149561.9815 | 8.7634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-26 02:30 | 6.3 | 5.8 | 320 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 149716.9815 | 8.7725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-26 03:30 | 6.2 | 5.7 | 317.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 149806.9815 | 8.7778 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-26 04:30 | 6.2 | 5.5 | 310 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 149896.9815 | 8.783 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-26 05:30 | 6.3 | 5.2 | 305 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 149946.9815 | 8.786 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-26 06:30 | 6.6 | 5 | 310 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 149956.9815 | 8.7865 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-26 07:30 | 6.7 | 5.2 | 315 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 149966.9815 | 8.7871 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-26 08:30 | 6.9 | 5.5 | 312.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 150016.9815 | 8.7901 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-26 09:30 | 7.3 | 5.8 | 307.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 150106.9815 | 8.7953 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-26 10:30 | 7.4 | 5.9 | 302.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 150196.9815 | 8.8006 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-26 11:30 | 7.3 | 5.8 | 300 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 150286.9815 | 8.8059 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-26 12:30 | 7.4 | 5.7 | 300 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 150376.9815 | 8.8112 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-26 13:30 | 7.7 | 5.3 | 302.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 150426.9815 | 8.8141 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-06-26 14:30 | 8 | 4.9 | 305 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 150315.1296 | 8.8075 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-06-26 15:30 | 8.6 | 5.1 | 300 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 150203.2778 | 8.801 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-26 16:30 | 9.6 | 5.6 | 290 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 150253.2778 | 8.8039 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-26 17:30 | 10 | 5.9 | 282.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 150343.2778 | 8.8092 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-26 18:30 | 9.7 | 5.8 | 277.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 150433.2778 | 8.8144 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-26 19:30 | 9.5 | 5.3 | 272.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 150483.2778 | 8.8174 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-06-26 20:30 | 8.9 | 4.7 | 267.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 150371.4259 | 8.8108 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-06-26 21:30 | 8.3 | 4.2 | 260 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 149966.9815 | 8.7871 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-06-26 22:30 | 7.5 | 4.2 | 252.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 149426.2407 | 8.7554 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-06-26 23:30 | 7.2 | 4.5 | 242.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 149021.7963 | 8.7317 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-06-27 00:30 | 7.9 | 4.7 | 227.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 148753.6481 | 8.716 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-27 01:30 | 8.4 | 5.7 | 220 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 148768.4815 | 8.7169 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-27 02:30 | 8.7 | 6.7 | 225 | 1120 | 810 | 490 | 0 | 490 | 245 | 0 | 149013.4815 | 8.7313 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-27 03:30 | 8.9 | 7.3 | 237.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 149503.4815 | 8.76 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-27 04:30 | 9.2 | 7.6 | 250 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 150148.4815 | 8.7978 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-27 05:30 | 9.5 | 7.3 | 257.5 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 150793.4815 | 8.8356 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-27 06:30 | 9.5 | 7.6 | 260 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 151438.4815 | 8.8733 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-27 07:30 | 9.7 | 8 | 260 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 152083.4815 | 8.9111 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-27 08:30 | 9.8 | 8 | 260 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 152728.4815 | 8.9489 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-27 09:30 | 9.7 | 8.2 | 260 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 153373.4815 | 8.9867 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-27 10:30 | 9.6 | 8.3 | 257.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 154018.4815 | 9.0245 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-27 11:30 | 9.7 | 8 | 252.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 154663.4815 | 9.0623 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-27 12:30 | 9.8 | 8 | 250 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 155308.4815 | 9.1001 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-27 13:30 | 9.8 | 7.8 | 250 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 155953.4815 | 9.1379 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-27 14:30 | 9.9 | 7.6 | 250 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 156598.4815 | 9.1757 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-27 15:30 | 10 | 7.1 | 247.5 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 157243.4815 | 9.2135 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-27 16:30 | 9.9 | 6.3 | 242.5 | 760 | 1120 | 800 | 0 | 800 | 400 | 0 | 157643.4815 | 9.2369 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-27 17:30 | 9.9 | 5.9 | 237.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 157798.4815 | 9.246 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-27 18:30 | 10 | 5.4 | 232.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 157848.4815 | 9.2489 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-06-27 19:30 | 9.9 | 4.5 | 225 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 157736.6296 | 9.2424 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-06-27 20:30 | 9.7 | 3.9 | 212.5 | 0 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 157247 | 9.2137 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-06-27 21:30 | 9.6 | 3.7 | 202.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 156535.8889 | 9.172 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-06-27 22:30 | 9.6 | 3.7 | 200 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 155824.7778 | 9.1304 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-06-27 23:30 | 9.7 | 3.6 | 187.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 155113.6667 | 9.0887 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-06-28 00:30 | 9.8 | 3 | 162.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 154402.5556 | 9.047 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-06-28 01:30 | 9.7 | 3.3 | 152.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 153691.4444 | 9.0054 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-06-28 02:30 | 9.5 | 4.4 | 155 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 153065.5185 | 8.9687 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-06-28 03:30 | 9.5 | 4.7 | 150 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 152661.0741 | 8.945 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-06-28 04:30 | 9.5 | 4.4 | 137.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 152256.6296 | 8.9213 | 1 |  |  | 1 | 11 | 0 | 0
Lerwick | 1978-06-28 05:30 | 9.4 | 4.6 | 125 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 151852.1852 | 8.8976 | 1 |  |  | 1 | 12 | 0 | 0
Lerwick | 1978-06-28 06:30 | 9.5 | 4.4 | 125 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 151447.7407 | 8.8739 | 1 |  |  | 1 | 13 | 0 | 0
Lerwick | 1978-06-28 07:30 | 9.8 | 4 | 142.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 150907 | 8.8422 | 1 |  |  | 1 | 14 | 0 | 0
Lerwick | 1978-06-28 08:30 | 10.2 | 4.5 | 162.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 150502.5556 | 8.8185 | 1 |  |  | 1 | 15 | 0 | 0
Lerwick | 1978-06-28 09:30 | 10.4 | 5.2 | 170 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 150390.7037 | 8.812 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-28 10:30 | 10.4 | 5.4 | 182.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 150400.7037 | 8.8125 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-28 11:30 | 10.4 | 5.8 | 210 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 150450.7037 | 8.8155 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-28 12:30 | 10.8 | 6.3 | 225 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 150605.7037 | 8.8246 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-28 13:30 | 11.3 | 6.1 | 222.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 150825.7037 | 8.8374 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-28 14:30 | 10.9 | 5.9 | 220 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 150980.7037 | 8.8465 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-28 15:30 | 10.5 | 6 | 220 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 151135.7037 | 8.8556 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-28 16:30 | 10.5 | 6.2 | 220 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 151355.7037 | 8.8685 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-28 17:30 | 10.7 | 6.2 | 217.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 151575.7037 | 8.8814 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-28 18:30 | 10.9 | 5.9 | 210 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 151730.7037 | 8.8905 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-28 19:30 | 10.7 | 5.3 | 197.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 151780.7037 | 8.8934 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-28 20:30 | 10.5 | 5 | 182.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 151790.7037 | 8.894 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-06-28 21:30 | 10.3 | 4.9 | 172.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 151678.8519 | 8.8874 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-06-28 22:30 | 10 | 5.1 | 167.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 151567 | 8.8809 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-28 23:30 | 10 | 5.6 | 162.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 151617 | 8.8838 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-29 00:30 | 10 | 5.8 | 162.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 151707 | 8.8891 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-29 01:30 | 10 | 5.5 | 167.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 151797 | 8.8944 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-29 02:30 | 10 | 4.9 | 167.5 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 151811.8333 | 8.8952 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-06-29 03:30 | 10 | 4 | 160 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 151407.3889 | 8.8715 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-06-29 04:30 | 10 | 3.6 | 155 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 150781.463 | 8.8349 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-06-29 05:30 | 10 | 3.7 | 157.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 150070.3519 | 8.7932 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-06-29 06:30 | 10.2 | 3.6 | 160 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 149359.2407 | 8.7515 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-06-29 07:30 | 10.3 | 3.3 | 160 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 148648.1296 | 8.7099 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-06-29 08:30 | 10.4 | 3.9 | 160 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 147937.0185 | 8.6682 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-06-29 09:30 | 11 | 5.1 | 162.5 | 340 | 170 | 0 | 150 | 0 | 0 | 333.3333 | 147603.6852 | 8.6487 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-29 10:30 | 11.4 | 5.8 | 175 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 147653.6852 | 8.6516 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-29 11:30 | 12 | 5.9 | 197.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 147743.6852 | 8.6569 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-29 12:30 | 11.9 | 5.4 | 215 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 147793.6852 | 8.6598 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-06-29 13:30 | 11.6 | 4.7 | 227.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 147681.8333 | 8.6532 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-06-29 14:30 | 12 | 4.5 | 237.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 147413.6852 | 8.6375 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-06-29 15:30 | 12.3 | 4.4 | 235 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 147009.2407 | 8.6138 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-06-29 16:30 | 11.9 | 4 | 230 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 146468.5 | 8.5821 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-06-29 17:30 | 11.2 | 3.3 | 235 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 145842.5741 | 8.5455 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-06-29 18:30 | 11 | 3.1 | 247.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 145131.463 | 8.5038 | 0 |  |  | 1 | 7 | 1 | 1
Lerwick | 1978-06-29 19:30 | 10.5 | 3.1 | 257.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 144420.3519 | 8.4621 | 0 |  |  | 1 | 8 | 1 | 2
Lerwick | 1978-06-29 20:30 | 10.1 | 2.8 | 262.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 143709.2407 | 8.4205 | 0 |  |  | 1 | 9 | 1 | 3
Lerwick | 1978-06-29 21:30 | 9.9 | 2.3 | 257.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 142998.1296 | 8.3788 | 0 |  |  | 1 | 10 | 1 | 4
Lerwick | 1978-06-29 22:30 | 9.6 | 2.3 | 245 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 142287.0185 | 8.3371 | 0 |  |  | 1 | 11 | 1 | 5
Lerwick | 1978-06-29 23:30 | 9.3 | 3.1 | 247.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 141575.9074 | 8.2955 | 0 |  |  | 1 | 12 | 1 | 6
Lerwick | 1978-06-30 00:30 | 8.8 | 3.7 | 257.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 140864.7963 | 8.2538 | 0 |  |  | 1 | 13 | 1 | 7
Lerwick | 1978-06-30 01:30 | 8.7 | 3.9 | 262.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 140153.6852 | 8.2121 | 0 |  |  | 1 | 14 | 1 | 8
Lerwick | 1978-06-30 02:30 | 8.7 | 3.7 | 270 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 139442.5741 | 8.1705 | 0 |  |  | 1 | 15 | 1 | 9
Lerwick | 1978-06-30 03:30 | 8.5 | 3.1 | 280 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 138731.463 | 8.1288 | 0 |  |  | 1 | 16 | 1 | 10
Lerwick | 1978-06-30 04:30 | 8.6 | 2.4 | 285 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 138020.3519 | 8.0871 | 0 |  |  | 1 | 17 | 1 | 11
Lerwick | 1978-06-30 05:30 | 8.9 | 2.4 | 277.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 137309.2407 | 8.0455 | 0 |  |  | 1 | 18 | 1 | 12
Lerwick | 1978-06-30 06:30 | 9.4 | 2.4 | 260 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 136598.1296 | 8.0038 | 0 |  |  | 1 | 19 | 1 | 13
Lerwick | 1978-06-30 07:30 | 9.8 | 2 | 245 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 135887.0185 | 7.9621 | 0 |  |  | 1 | 20 | 1 | 14
Lerwick | 1978-06-30 08:30 | 10.3 | 2.2 | 217.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 135175.9074 | 7.9205 | 0 |  |  | 1 | 21 | 1 | 15
Lerwick | 1978-06-30 09:30 | 11 | 3.1 | 170 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 134464.7963 | 7.8788 | 0 |  |  | 1 | 22 | 1 | 16
Lerwick | 1978-06-30 10:30 | 11.6 | 3.7 | 167.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 133753.6852 | 7.8371 | 0 |  |  | 1 | 23 | 1 | 17
Lerwick | 1978-06-30 11:30 | 11.7 | 4.1 | 217.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 133127.7593 | 7.8005 | 1 |  |  | 1 | 24 | 0 | 0
Lerwick | 1978-06-30 12:30 | 11.6 | 4.9 | 245 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 132723.3148 | 7.7768 | 1 |  |  | 1 | 25 | 0 | 0
Lerwick | 1978-06-30 13:30 | 11.9 | 5.4 | 245 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 132611.463 | 7.7702 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-06-30 14:30 | 11.6 | 5.1 | 247.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 132621.463 | 7.7708 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-06-30 15:30 | 11.3 | 4.9 | 250 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 132509.6111 | 7.7642 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-06-30 16:30 | 11.3 | 4.9 | 250 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 132241.463 | 7.7485 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-06-30 17:30 | 11.1 | 4.7 | 250 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 131973.3148 | 7.7328 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-06-30 18:30 | 10.7 | 4.7 | 250 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 131705.1667 | 7.7171 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-06-30 19:30 | 10.2 | 4.9 | 252.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 131437.0185 | 7.7014 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-06-30 20:30 | 9.8 | 4.6 | 260 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 131168.8704 | 7.6857 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-06-30 21:30 | 9.5 | 4.2 | 267.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 130764.4259 | 7.662 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-06-30 22:30 | 9.3 | 4 | 267.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 130223.6852 | 7.6303 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-06-30 23:30 | 9.1 | 3.8 | 260 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 129597.7593 | 7.5936 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-07-01 00:30 | 9.1 | 3.4 | 252.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 128886.6481 | 7.552 | 0 |  |  | 1 | 11 | 1 | 1
Lerwick | 1978-07-01 01:30 | 9 | 3.6 | 252.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 128175.537 | 7.5103 | 0 |  |  | 1 | 12 | 1 | 2
Lerwick | 1978-07-01 02:30 | 8.8 | 3.9 | 257.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 127464.4259 | 7.4686 | 0 |  |  | 1 | 13 | 1 | 3
Lerwick | 1978-07-01 03:30 | 8.3 | 3.8 | 255 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 126753.3148 | 7.427 | 0 |  |  | 1 | 14 | 1 | 4
Lerwick | 1978-07-01 04:30 | 8.3 | 3.4 | 245 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 126042.2037 | 7.3853 | 0 |  |  | 1 | 15 | 1 | 5
Lerwick | 1978-07-01 05:30 | 8.5 | 3.4 | 242.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 125331.0926 | 7.3436 | 0 |  |  | 1 | 16 | 1 | 6
Lerwick | 1978-07-01 06:30 | 9 | 3.1 | 245 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 124619.9815 | 7.302 | 0 |  |  | 1 | 17 | 1 | 7
Lerwick | 1978-07-01 07:30 | 9.7 | 2.9 | 222.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 123908.8704 | 7.2603 | 0 |  |  | 1 | 18 | 1 | 8
Lerwick | 1978-07-01 08:30 | 10.2 | 3.8 | 180 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 123197.7593 | 7.2186 | 0 |  |  | 1 | 19 | 1 | 9
Lerwick | 1978-07-01 09:30 | 10.6 | 4.7 | 157.5 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 122708.1296 | 7.1899 | 1 |  |  | 1 | 20 | 0 | 0
Lerwick | 1978-07-01 10:30 | 10.9 | 4.9 | 155 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 122439.9815 | 7.1742 | 1 |  |  | 1 | 21 | 0 | 0
Lerwick | 1978-07-01 11:30 | 10.7 | 5.3 | 157.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 122328.1296 | 7.1677 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-01 12:30 | 11.2 | 5.7 | 157.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 122378.1296 | 7.1706 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-01 13:30 | 11.5 | 5.7 | 155 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 122468.1296 | 7.1759 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-01 14:30 | 11.5 | 5.5 | 155 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 122558.1296 | 7.1811 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-01 15:30 | 11.7 | 5.2 | 150 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 122608.1296 | 7.1841 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-01 16:30 | 11.5 | 5.4 | 145 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 122618.1296 | 7.1847 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-01 17:30 | 11.1 | 6.1 | 147.5 | 760 | 550 | 230 | 0 | 230 | 115 | 0 | 122733.1296 | 7.1914 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-01 18:30 | 10.9 | 6.3 | 152.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 122953.1296 | 7.2043 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-01 19:30 | 10.8 | 6 | 160 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 123173.1296 | 7.2172 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-01 20:30 | 10.4 | 5.6 | 167.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 123328.1296 | 7.2263 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-01 21:30 | 10.2 | 4.9 | 172.5 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 123342.963 | 7.2271 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-07-01 22:30 | 9.9 | 4.2 | 177.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 122938.5185 | 7.2034 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-07-01 23:30 | 9.9 | 3.7 | 190 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 122312.5926 | 7.1668 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-07-02 00:30 | 9.9 | 3.6 | 210 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 121601.4815 | 7.1251 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-07-02 01:30 | 9.7 | 3.4 | 217.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 120890.3704 | 7.0834 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-07-02 02:30 | 9.5 | 3 | 212.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 120179.2593 | 7.0418 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-07-02 03:30 | 9.4 | 2.9 | 215 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 119468.1481 | 7.0001 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-07-02 04:30 | 9.4 | 3.5 | 222.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 118757.037 | 6.9584 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-07-02 05:30 | 9.3 | 4.2 | 225 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 118131.1111 | 6.9217 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-07-02 06:30 | 9.4 | 4.7 | 230 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 117726.6667 | 6.898 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-07-02 07:30 | 9.7 | 4.9 | 235 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 117458.5185 | 6.8823 | 1 |  |  | 1 | 11 | 0 | 0
Lerwick | 1978-07-02 08:30 | 10.2 | 5.4 | 232.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 117346.6667 | 6.8758 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-02 09:30 | 10.9 | 6.3 | 230 | 760 | 550 | 230 | 0 | 230 | 115 | 0 | 117461.6667 | 6.8825 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-02 10:30 | 11.4 | 7.2 | 235 | 1480 | 1120 | 800 | 0 | 800 | 400 | 0 | 117861.6667 | 6.906 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-02 11:30 | 11.3 | 7.8 | 245 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 118506.6667 | 6.9437 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-02 12:30 | 10.7 | 8 | 250 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 119151.6667 | 6.9815 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-02 13:30 | 10.4 | 8 | 250 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 119796.6667 | 7.0193 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-02 14:30 | 10.8 | 8 | 245 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 120441.6667 | 7.0571 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-02 15:30 | 11.8 | 7.6 | 235 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 121086.6667 | 7.0949 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-02 16:30 | 12.2 | 6.9 | 230 | 1120 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 121666.6667 | 7.1289 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-02 17:30 | 11.6 | 6.4 | 230 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 121976.6667 | 7.1471 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-02 18:30 | 11 | 5.8 | 230 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 122131.6667 | 7.1562 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-02 19:30 | 10.6 | 4.9 | 230 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 122146.5 | 7.157 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-07-02 20:30 | 10.2 | 4 | 230 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 121742.0556 | 7.1333 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-07-02 21:30 | 9.4 | 3.1 | 230 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 121116.1296 | 7.0966 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-07-02 22:30 | 8.3 | 2.2 | 227.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 120405.0185 | 7.055 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-07-02 23:30 | 7.6 | 1.1 | 257.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 119693.9074 | 7.0133 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-07-03 00:30 | 7.6 | 0.5 | 317.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 118982.7963 | 6.9716 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-07-03 01:30 | 7.6 | 0.7 | 342.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 118271.6852 | 6.93 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-07-03 02:30 | 7.6 | 1.5 | 345 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 117560.5741 | 6.8883 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-07-03 03:30 | 7 | 2.4 | 352.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 116849.463 | 6.8466 | 0 |  |  | 1 | 9 | 1 | 6
Lerwick | 1978-07-03 04:30 | 7.3 | 3 | 345 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 116138.3519 | 6.805 | 0 |  |  | 1 | 10 | 1 | 7
Lerwick | 1978-07-03 05:30 | 8.4 | 3.9 | 340 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 115427.2407 | 6.7633 | 0 |  |  | 1 | 11 | 1 | 8
Lerwick | 1978-07-03 06:30 | 9.4 | 5.1 | 182.5 | 340 | 170 | 0 | 150 | 0 | 0 | 333.3333 | 115093.9074 | 6.7438 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-03 07:30 | 10.4 | 5.9 | 20 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 115143.9074 | 6.7467 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-03 08:30 | 11 | 6.3 | 17.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 115298.9074 | 6.7558 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-03 09:30 | 11.2 | 6.8 | 7.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 115608.9074 | 6.774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-03 10:30 | 11.5 | 7.4 | 175 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 116098.9074 | 6.8027 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-03 11:30 | 11.2 | 7.8 | 347.5 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 116743.9074 | 6.8405 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-03 12:30 | 10.5 | 8.6 | 347.5 | 2560 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 117388.9074 | 6.8783 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-03 13:30 | 10.4 | 9.9 | 177.5 | 3280 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 118033.9074 | 6.916 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-03 14:30 | 10.6 | 10.7 | 7.5 | 4000 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 118678.9074 | 6.9538 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-03 15:30 | 10.7 | 11.5 | 10 | 4472.2222 | 4236.1111 | 3916.1111 | 0 | 1290 | 645 | 0 | 119323.9074 | 6.9916 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-03 16:30 | 10.4 | 11.9 | 10 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 645 | 0 | 119968.9074 | 7.0294 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-03 17:30 | 10.4 | 11 | 10 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 120613.9074 | 7.0672 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-03 18:30 | 10.2 | 9.9 | 7.5 | 3280 | 3790 | 3470 | 0 | 1290 | 645 | 0 | 121258.9074 | 7.105 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-03 19:30 | 10 | 9.4 | 5 | 2920 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 121903.9074 | 7.1428 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-03 20:30 | 9.9 | 9 | 5 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 122548.9074 | 7.1806 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-03 21:30 | 9.8 | 8.8 | 2.5 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 123193.9074 | 7.2184 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-03 22:30 | 9.7 | 9.1 | 0 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 123838.9074 | 7.2562 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-03 23:30 | 9.5 | 9.9 | 0 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 124483.9074 | 7.294 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-04 00:30 | 9.5 | 10.5 | 177.5 | 4000 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 125128.9074 | 7.3318 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-04 01:30 | 9.4 | 10.6 | 352.5 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 125773.9074 | 7.3696 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-04 02:30 | 9.4 | 10.6 | 352.5 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 126418.9074 | 7.4074 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-04 03:30 | 9.7 | 11 | 177.5 | 4300 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 127063.9074 | 7.4452 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-04 04:30 | 10 | 11.3 | 0 | 4300 | 4300 | 3980 | 0 | 1290 | 645 | 0 | 127708.9074 | 7.4829 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-04 05:30 | 9.9 | 11.3 | 0 | 4300 | 4300 | 3980 | 0 | 1290 | 645 | 0 | 128353.9074 | 7.5207 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-04 06:30 | 9.7 | 11.4 | 0 | 4300 | 4300 | 3980 | 0 | 1290 | 645 | 0 | 128998.9074 | 7.5585 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-04 07:30 | 9.6 | 11.7 | 0 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 129643.9074 | 7.5963 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-04 08:30 | 9.8 | 12.2 | 0 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 645 | 0 | 130288.9074 | 7.6341 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-04 09:30 | 10 | 12.4 | 0 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 130933.9074 | 7.6719 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-04 10:30 | 10.2 | 12.1 | 0 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 131578.9074 | 7.7097 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-04 11:30 | 10.7 | 11.9 | 0 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 645 | 0 | 132223.9074 | 7.7475 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-04 12:30 | 10.8 | 12.2 | 0 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 645 | 0 | 132868.9074 | 7.7853 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-04 13:30 | 10.8 | 12.4 | 0 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 133513.9074 | 7.8231 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-04 14:30 | 10.7 | 12.4 | 0 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 134158.9074 | 7.8609 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-04 15:30 | 10.5 | 12.4 | 0 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 134803.9074 | 7.8987 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-04 16:30 | 10.4 | 12.4 | 0 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 135448.9074 | 7.9365 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-04 17:30 | 10.1 | 12.7 | 0 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 645 | 0 | 136093.9074 | 7.9743 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-04 18:30 | 9.7 | 12.6 | 0 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 136738.9074 | 8.012 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-04 19:30 | 9.5 | 12.2 | 0 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 645 | 0 | 137383.9074 | 8.0498 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-04 20:30 | 9.2 | 12 | 0 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 138028.9074 | 8.0876 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-04 21:30 | 9 | 11.9 | 0 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 645 | 0 | 138673.9074 | 8.1254 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-04 22:30 | 9 | 11.6 | 0 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 645 | 0 | 139318.9074 | 8.1632 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-04 23:30 | 8.9 | 11.4 | 0 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 139963.9074 | 8.201 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-05 00:30 | 8.8 | 11.5 | 0 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 140608.9074 | 8.2388 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-05 01:30 | 8.9 | 11.9 | 0 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 645 | 0 | 141253.9074 | 8.2766 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-05 02:30 | 8.9 | 12 | 177.5 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 645 | 0 | 141898.9074 | 8.3144 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-05 03:30 | 8.7 | 11.9 | 355 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 645 | 0 | 142543.9074 | 8.3522 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-05 04:30 | 8.7 | 11.4 | 355 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 143188.9074 | 8.39 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-05 05:30 | 8.8 | 11 | 352.5 | 4300 | 4300 | 3980 | 0 | 1290 | 645 | 0 | 143833.9074 | 8.4278 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-05 06:30 | 8.9 | 11 | 347.5 | 4300 | 4300 | 3980 | 0 | 1290 | 645 | 0 | 144478.9074 | 8.4656 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-05 07:30 | 9.1 | 10.9 | 342.5 | 4000 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 145123.9074 | 8.5034 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-05 08:30 | 9.1 | 10.9 | 340 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 145768.9074 | 8.5411 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-05 09:30 | 9.2 | 11.2 | 340 | 4300 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 146413.9074 | 8.5789 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-05 10:30 | 9.5 | 11.6 | 340 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 147058.9074 | 8.6167 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-05 11:30 | 9.8 | 11.8 | 340 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 645 | 0 | 147703.9074 | 8.6545 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-05 12:30 | 10 | 11.8 | 340 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 645 | 0 | 148348.9074 | 8.6923 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-05 13:30 | 10.2 | 11.9 | 340 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 645 | 0 | 148993.9074 | 8.7301 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-05 14:30 | 9.9 | 11.9 | 337.5 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 645 | 0 | 149638.9074 | 8.7679 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-05 15:30 | 9.6 | 11.4 | 332.5 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 150283.9074 | 8.8057 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-05 16:30 | 9.5 | 10.7 | 330 | 4000 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 150928.9074 | 8.8435 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-05 17:30 | 9.2 | 10.4 | 332.5 | 3640 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 151573.9074 | 8.8813 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-05 18:30 | 9.2 | 10.3 | 337.5 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 152218.9074 | 8.9191 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-05 19:30 | 9.3 | 10.1 | 340 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 152863.9074 | 8.9569 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-05 20:30 | 9.3 | 9.7 | 340 | 3280 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 153508.9074 | 8.9947 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-05 21:30 | 9.3 | 9.5 | 340 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 154153.9074 | 9.0325 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-05 22:30 | 9.2 | 9.7 | 340 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 154798.9074 | 9.0702 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-05 23:30 | 8.8 | 10.4 | 340 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 155443.9074 | 9.108 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-06 00:30 | 8.6 | 11 | 337.5 | 4300 | 3970 | 3650 | 0 | 1290 | 645 | 0 | 156088.9074 | 9.1458 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-06 01:30 | 8.6 | 10.8 | 330 | 4000 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 156733.9074 | 9.1836 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-06 02:30 | 8.5 | 9.9 | 322.5 | 3280 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 157378.9074 | 9.2214 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-06 03:30 | 8.3 | 9.6 | 317.5 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 158023.9074 | 9.2592 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-06 04:30 | 8.3 | 9.5 | 315 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 158668.9074 | 9.297 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-06 05:30 | 8.7 | 9.4 | 320 | 2920 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 159313.9074 | 9.3348 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-06 06:30 | 9.1 | 10.1 | 330 | 3640 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 159958.9074 | 9.3726 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-06 07:30 | 9.5 | 11.3 | 337.5 | 4300 | 3970 | 3650 | 0 | 1290 | 645 | 0 | 160603.9074 | 9.4104 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-06 08:30 | 9.9 | 12.1 | 342.5 | 4536.1111 | 4418.0556 | 4098.0556 | 0 | 1290 | 645 | 0 | 161248.9074 | 9.4482 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-06 09:30 | 9.9 | 11.9 | 347.5 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 645 | 0 | 161893.9074 | 9.486 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-06 10:30 | 9.9 | 11 | 352.5 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 162538.9074 | 9.5238 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-06 11:30 | 9.9 | 10.4 | 355 | 3640 | 3970 | 3650 | 0 | 1290 | 645 | 0 | 163183.9074 | 9.5616 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-06 12:30 | 10.1 | 10.4 | 352.5 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 163828.9074 | 9.5994 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-06 13:30 | 10.2 | 10.5 | 350 | 4000 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 164473.9074 | 9.6371 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-06 14:30 | 10.2 | 10.4 | 350 | 3640 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 165118.9074 | 9.6749 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-06 15:30 | 10.2 | 10.3 | 347.5 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 165763.9074 | 9.7127 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-06 16:30 | 10 | 10 | 342.5 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 166408.9074 | 9.7505 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-06 17:30 | 9.7 | 9.3 | 337.5 | 2920 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 167053.9074 | 9.7883 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-06 18:30 | 9.4 | 8.4 | 332.5 | 2200 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 167698.9074 | 9.8261 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-06 19:30 | 9.2 | 8 | 330 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 168343.9074 | 9.8639 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-06 20:30 | 8.8 | 8 | 327.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 168988.9074 | 9.9017 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-06 21:30 | 8.4 | 8.1 | 325 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 169633.9074 | 9.9395 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-06 22:30 | 8.1 | 8.1 | 325 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-06 23:30 | 7.9 | 8.1 | 322.5 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-07 00:30 | 7.8 | 8.1 | 320 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-07 01:30 | 7.7 | 8.1 | 320 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-07 02:30 | 7.7 | 8.1 | 320 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-07 03:30 | 7.5 | 8.3 | 320 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-07 04:30 | 7.3 | 8.6 | 320 | 2560 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-07 05:30 | 7.4 | 9 | 317.5 | 2920 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-07 06:30 | 7.4 | 9.5 | 312.5 | 3280 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-07 07:30 | 7.5 | 9.8 | 312.5 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-07 08:30 | 7.6 | 9.9 | 317.5 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-07 09:30 | 8 | 10.1 | 317.5 | 3640 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-07 10:30 | 8 | 10.3 | 312.5 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-07 11:30 | 8 | 10.3 | 310 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-07 12:30 | 8.3 | 10.4 | 307.5 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-07 13:30 | 8.2 | 10.7 | 302.5 | 4000 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-07 14:30 | 8.2 | 11.2 | 297.5 | 4300 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-07 15:30 | 8.2 | 11.7 | 292.5 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-07 16:30 | 8.3 | 11.9 | 290 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-07 17:30 | 8.1 | 11.6 | 290 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-07 18:30 | 7.6 | 11.6 | 290 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-07 19:30 | 7.3 | 11.5 | 290 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-07 20:30 | 7.2 | 11.4 | 287.5 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-07 21:30 | 7 | 12 | 282.5 | 4536.1111 | 4418.0556 | 4098.0556 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-07 22:30 | 6.9 | 12.8 | 280 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-07 23:30 | 6.7 | 13.2 | 280 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-08 00:30 | 6.7 | 13.2 | 280 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-08 01:30 | 6.7 | 12.8 | 280 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-08 02:30 | 6.6 | 12.1 | 282.5 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-08 03:30 | 6.6 | 11.3 | 285 | 4300 | 4418.0556 | 4098.0556 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-08 04:30 | 6.8 | 10.5 | 285 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-08 05:30 | 7 | 10.1 | 287.5 | 3640 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-08 06:30 | 7.3 | 9.9 | 290 | 3280 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-08 07:30 | 7.5 | 9.6 | 290 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-08 08:30 | 7.8 | 9.1 | 292.5 | 2920 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-08 09:30 | 8 | 8.4 | 297.5 | 2200 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-08 10:30 | 8.4 | 8 | 300 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-08 11:30 | 8.9 | 7.8 | 300 | 1840 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-08 12:30 | 9.5 | 7.6 | 297.5 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-08 13:30 | 10.3 | 7.2 | 292.5 | 1480 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-08 14:30 | 10.8 | 6.7 | 290 | 1120 | 1300 | 980 | 0 | 980 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-08 15:30 | 11.1 | 6.3 | 290 | 760 | 940 | 620 | 0 | 620 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-08 16:30 | 11.2 | 6.2 | 290 | 760 | 760 | 440 | 0 | 440 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-08 17:30 | 10.8 | 6.4 | 287.5 | 760 | 760 | 440 | 0 | 440 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-08 18:30 | 10.2 | 7.2 | 282.5 | 1480 | 1120 | 800 | 0 | 800 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-08 19:30 | 9.5 | 7.9 | 280 | 1840 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-08 20:30 | 9.2 | 8.1 | 280 | 2200 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-08 21:30 | 8.9 | 7.9 | 282.5 | 1840 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-08 22:30 | 8.4 | 6.9 | 287.5 | 1120 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-08 23:30 | 8.1 | 5.3 | 290 | 340 | 730 | 410 | 0 | 410 | 0 | 0 | 170278.9074 | 9.9773 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-07-09 00:30 | 8.1 | 3.8 | 287.5 | 0 | 170 | 0 | 150 | 0 | 0 | 333.3333 | 169945.5741 | 9.9577 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-07-09 01:30 | 8.1 | 4.1 | 282.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 169319.6481 | 9.9211 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-07-09 02:30 | 7.9 | 5.6 | 282.5 | 500 | 288.3333 | 0 | 31.6667 | 0 | 0 | 70.3704 | 169249.2778 | 9.9169 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-09 03:30 | 8.1 | 6.3 | 285 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 169404.2778 | 9.926 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-09 04:30 | 8.7 | 6 | 285 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 169624.2778 | 9.9389 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-09 05:30 | 8.8 | 5.2 | 287.5 | 340 | 550 | 230 | 0 | 230 | 115 | 0 | 169739.2778 | 9.9457 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-07-09 06:30 | 9.8 | 4 | 290 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 169491.1296 | 9.9311 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-07-09 07:30 | 11.6 | 3.7 | 290 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 168865.2037 | 9.8944 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-07-09 08:30 | 12.8 | 3.9 | 297.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168154.0926 | 9.8528 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-07-09 09:30 | 13.6 | 4.2 | 330 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 167528.1667 | 9.8161 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-07-09 10:30 | 15.3 | 4.4 | 192.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 166987.4259 | 9.7844 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-07-09 11:30 | 15.6 | 4.2 | 27.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 166446.6852 | 9.7527 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-07-09 12:30 | 13.5 | 3.8 | 22.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 165820.7593 | 9.7161 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-07-09 13:30 | 12.1 | 3.3 | 27.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165109.6481 | 9.6744 | 0 |  |  | 1 | 9 | 1 | 1
Lerwick | 1978-07-09 14:30 | 12 | 2.9 | 37.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164398.537 | 9.6327 | 0 |  |  | 1 | 10 | 1 | 2
Lerwick | 1978-07-09 15:30 | 12.7 | 2.6 | 37.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163687.4259 | 9.5911 | 0 |  |  | 1 | 11 | 1 | 3
Lerwick | 1978-07-09 16:30 | 13.4 | 2.2 | 17.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162976.3148 | 9.5494 | 0 |  |  | 1 | 12 | 1 | 4
Lerwick | 1978-07-09 17:30 | 13 | 1.5 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162265.2037 | 9.5077 | 0 |  |  | 1 | 13 | 1 | 5
Lerwick | 1978-07-09 18:30 | 11.9 | 1.1 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161554.0926 | 9.4661 | 0 |  |  | 1 | 14 | 1 | 6
Lerwick | 1978-07-09 19:30 | 11.1 | 1.1 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160842.9815 | 9.4244 | 0 |  |  | 1 | 15 | 1 | 7
Lerwick | 1978-07-09 20:30 | 10.5 | 1.4 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160131.8704 | 9.3827 | 0 |  |  | 1 | 16 | 1 | 8
Lerwick | 1978-07-09 21:30 | 9.9 | 1.4 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 159420.7593 | 9.3411 | 0 |  |  | 1 | 17 | 1 | 9
Lerwick | 1978-07-09 22:30 | 9.4 | 1.1 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 158709.6481 | 9.2994 | 0 |  |  | 1 | 18 | 1 | 10
Lerwick | 1978-07-09 23:30 | 9 | 1.1 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 157998.537 | 9.2577 | 0 |  |  | 1 | 19 | 1 | 11
Lerwick | 1978-07-10 00:30 | 8.7 | 1.7 | 120 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 157287.4259 | 9.2161 | 0 |  |  | 1 | 20 | 1 | 12
Lerwick | 1978-07-10 01:30 | 8.2 | 2.3 | 227.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 156576.3148 | 9.1744 | 0 |  |  | 1 | 21 | 1 | 13
Lerwick | 1978-07-10 02:30 | 8 | 2.3 | 215 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 155865.2037 | 9.1327 | 0 |  |  | 1 | 22 | 1 | 14
Lerwick | 1978-07-10 03:30 | 8 | 1.8 | 222.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 155154.0926 | 9.0911 | 0 |  |  | 1 | 23 | 1 | 15
Lerwick | 1978-07-10 04:30 | 7.8 | 1.5 | 230 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 154442.9815 | 9.0494 | 0 |  |  | 1 | 24 | 1 | 16
Lerwick | 1978-07-10 05:30 | 7.6 | 1.5 | 232.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 153731.8704 | 9.0077 | 0 |  |  | 1 | 25 | 1 | 17
Lerwick | 1978-07-10 06:30 | 7.7 | 1.4 | 237.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 153020.7593 | 8.9661 | 0 |  |  | 1 | 26 | 1 | 18
Lerwick | 1978-07-10 07:30 | 7.8 | 1.1 | 247.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 152309.6481 | 8.9244 | 0 |  |  | 1 | 27 | 1 | 19
Lerwick | 1978-07-10 08:30 | 7.9 | 1 | 127.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 151598.537 | 8.8827 | 0 |  |  | 1 | 28 | 1 | 20
Lerwick | 1978-07-10 09:30 | 8.3 | 1.2 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 150887.4259 | 8.8411 | 0 |  |  | 1 | 29 | 1 | 21
Lerwick | 1978-07-10 10:30 | 9.3 | 1.8 | 80 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 150176.3148 | 8.7994 | 0 |  |  | 1 | 30 | 1 | 22
Lerwick | 1978-07-10 11:30 | 10 | 2.3 | 165 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 149465.2037 | 8.7577 | 0 |  |  | 1 | 31 | 1 | 23
Lerwick | 1978-07-10 12:30 | 10.8 | 2.8 | 157.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 148754.0926 | 8.7161 | 0 |  |  | 1 | 32 | 1 | 24
Lerwick | 1978-07-10 13:30 | 11.8 | 2.8 | 145 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 148042.9815 | 8.6744 | 0 |  |  | 1 | 33 | 1 | 25
Lerwick | 1978-07-10 14:30 | 11.9 | 2.2 | 145 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 147331.8704 | 8.6327 | 0 |  |  | 1 | 34 | 1 | 26
Lerwick | 1978-07-10 15:30 | 11.6 | 1.6 | 157.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 146620.7593 | 8.5911 | 0 |  |  | 1 | 35 | 1 | 27
Lerwick | 1978-07-10 16:30 | 11.1 | 1.5 | 157.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 145909.6481 | 8.5494 | 0 |  |  | 1 | 36 | 1 | 28
Lerwick | 1978-07-10 17:30 | 10.5 | 1.5 | 112.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 145198.537 | 8.5077 | 0 |  |  | 1 | 37 | 1 | 29
Lerwick | 1978-07-10 18:30 | 10 | 1.5 | 60 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 144487.4259 | 8.4661 | 0 |  |  | 1 | 38 | 1 | 30
Lerwick | 1978-07-10 19:30 | 9.7 | 1.8 | 30 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 143776.3148 | 8.4244 | 0 |  |  | 1 | 39 | 1 | 31
Lerwick | 1978-07-10 20:30 | 9.4 | 2.7 | 22.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 143065.2037 | 8.3827 | 0 |  |  | 1 | 40 | 1 | 32
Lerwick | 1978-07-10 21:30 | 9.1 | 3.3 | 25 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 142354.0926 | 8.3411 | 0 |  |  | 1 | 41 | 1 | 33
Lerwick | 1978-07-10 22:30 | 8.6 | 3.2 | 22.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 141642.9815 | 8.2994 | 0 |  |  | 1 | 42 | 1 | 34
Lerwick | 1978-07-10 23:30 | 8.4 | 3.1 | 15 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 140931.8704 | 8.2577 | 0 |  |  | 1 | 43 | 1 | 35
Lerwick | 1978-07-11 00:30 | 8.4 | 3.2 | 182.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 140220.7593 | 8.2161 | 0 |  |  | 1 | 44 | 1 | 36
Lerwick | 1978-07-11 01:30 | 8.3 | 3.4 | 177.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 139509.6481 | 8.1744 | 0 |  |  | 1 | 45 | 1 | 37
Lerwick | 1978-07-11 02:30 | 8.5 | 3.6 | 5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 138798.537 | 8.1327 | 0 |  |  | 1 | 46 | 1 | 38
Lerwick | 1978-07-11 03:30 | 8.8 | 3.6 | 10 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 138087.4259 | 8.0911 | 0 |  |  | 1 | 47 | 1 | 39
Lerwick | 1978-07-11 04:30 | 9 | 3.7 | 10 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 137376.3148 | 8.0494 | 0 |  |  | 1 | 48 | 1 | 40
Lerwick | 1978-07-11 05:30 | 9.1 | 4.2 | 10 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 136750.3889 | 8.0127 | 1 |  |  | 1 | 49 | 0 | 0
Lerwick | 1978-07-11 06:30 | 9.4 | 4.9 | 12.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 136345.9444 | 7.989 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-11 07:30 | 9.4 | 5.5 | 17.5 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 136360.7778 | 7.9899 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-11 08:30 | 9.6 | 5.7 | 22.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 136450.7778 | 7.9952 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-11 09:30 | 9.8 | 5.7 | 27.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 136540.7778 | 8.0004 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-11 10:30 | 10.5 | 5.8 | 30 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 136630.7778 | 8.0057 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-11 11:30 | 11.1 | 5.9 | 30 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 136720.7778 | 8.011 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-11 12:30 | 11.2 | 5.9 | 30 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 136810.7778 | 8.0163 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-11 13:30 | 11.7 | 6 | 30 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 136965.7778 | 8.0253 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-11 14:30 | 11.8 | 6.2 | 30 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 137185.7778 | 8.0382 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-11 15:30 | 11.8 | 6.2 | 30 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 137405.7778 | 8.0511 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-11 16:30 | 11.7 | 6.3 | 27.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 137625.7778 | 8.064 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-11 17:30 | 11.4 | 6.4 | 22.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 137845.7778 | 8.0769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-11 18:30 | 10.9 | 6.1 | 20 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 138065.7778 | 8.0898 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-11 19:30 | 10.3 | 5.8 | 17.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 138220.7778 | 8.0989 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-11 20:30 | 9.7 | 5.7 | 10 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 138310.7778 | 8.1041 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-11 21:30 | 9.3 | 5.3 | 180 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 138360.7778 | 8.1071 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-07-11 22:30 | 9.1 | 4.7 | 352.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 138248.9259 | 8.1005 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-07-11 23:30 | 8.9 | 4.2 | 347.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 137844.4815 | 8.0768 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-07-12 00:30 | 8.7 | 3.9 | 340 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 137218.5556 | 8.0401 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-07-12 01:30 | 8.7 | 4.1 | 337.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 136592.6296 | 8.0035 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-07-12 02:30 | 9 | 4.7 | 347.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 136188.1852 | 7.9798 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-07-12 03:30 | 8.7 | 5.2 | 177.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 136076.3333 | 7.9732 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-12 04:30 | 8.4 | 5.5 | 2.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 136126.3333 | 7.9762 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-12 05:30 | 8.4 | 5.7 | 7.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 136216.3333 | 7.9814 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-12 06:30 | 8.6 | 5.7 | 10 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 136306.3333 | 7.9867 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-12 07:30 | 8.9 | 5.5 | 7.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 136396.3333 | 7.992 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-12 08:30 | 9 | 5.1 | 5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 136446.3333 | 7.9949 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-07-12 09:30 | 9.2 | 4.6 | 10 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 136334.4815 | 7.9883 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-07-12 10:30 | 9.5 | 4.2 | 7.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 135930.037 | 7.9647 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-07-12 11:30 | 9.7 | 3.9 | 172.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 135304.1111 | 7.928 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-07-12 12:30 | 10 | 3.9 | 350 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 134593 | 7.8863 | 0 |  |  | 1 | 5 | 1 | 1
Lerwick | 1978-07-12 13:30 | 10.5 | 3.9 | 347.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 133881.8889 | 7.8446 | 0 |  |  | 1 | 6 | 1 | 2
Lerwick | 1978-07-12 14:30 | 10.6 | 4 | 330 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 133255.963 | 7.808 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-07-12 15:30 | 10.2 | 4 | 320 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 132715.2222 | 7.7763 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-07-12 16:30 | 10.1 | 3.9 | 317.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 132089.2963 | 7.7396 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-07-12 17:30 | 10.1 | 3.9 | 312.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 131378.1852 | 7.6979 | 0 |  |  | 1 | 10 | 1 | 1
Lerwick | 1978-07-12 18:30 | 10 | 3.9 | 310 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 130667.0741 | 7.6563 | 0 |  |  | 1 | 11 | 1 | 2
Lerwick | 1978-07-12 19:30 | 9.9 | 3.9 | 307.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 129955.963 | 7.6146 | 0 |  |  | 1 | 12 | 1 | 3
Lerwick | 1978-07-12 20:30 | 9.7 | 3.7 | 300 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 129244.8519 | 7.5729 | 0 |  |  | 1 | 13 | 1 | 4
Lerwick | 1978-07-12 21:30 | 9.5 | 3.6 | 292.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 128533.7407 | 7.5313 | 0 |  |  | 1 | 14 | 1 | 5
Lerwick | 1978-07-12 22:30 | 9.2 | 3.6 | 290 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 127822.6296 | 7.4896 | 0 |  |  | 1 | 15 | 1 | 6
Lerwick | 1978-07-12 23:30 | 9 | 3.8 | 290 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 127111.5185 | 7.4479 | 0 |  |  | 1 | 16 | 1 | 7
Lerwick | 1978-07-13 00:30 | 8.9 | 4.4 | 290 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 126485.5926 | 7.4113 | 1 |  |  | 1 | 17 | 0 | 0
Lerwick | 1978-07-13 01:30 | 8.8 | 4.9 | 285 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 126081.1481 | 7.3876 | 1 |  |  | 1 | 18 | 0 | 0
Lerwick | 1978-07-13 02:30 | 8.8 | 4.9 | 275 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 125813 | 7.3719 | 1 |  |  | 1 | 19 | 0 | 0
Lerwick | 1978-07-13 03:30 | 8.6 | 4.9 | 270 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 125544.8519 | 7.3561 | 1 |  |  | 1 | 20 | 0 | 0
Lerwick | 1978-07-13 04:30 | 8.5 | 5.3 | 270 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 125433 | 7.3496 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-13 05:30 | 8.4 | 6.2 | 272.5 | 760 | 550 | 230 | 0 | 230 | 115 | 0 | 125548 | 7.3563 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-13 06:30 | 8.6 | 6.9 | 277.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 125858 | 7.3745 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-13 07:30 | 8.5 | 7.2 | 277.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 126348 | 7.4032 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-13 08:30 | 8.2 | 7.2 | 275 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 126928 | 7.4372 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-13 09:30 | 8.4 | 7.3 | 275 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 127508 | 7.4712 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-13 10:30 | 8.8 | 7.7 | 272.5 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 128153 | 7.509 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-13 11:30 | 9.3 | 8.5 | 270 | 2560 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 128798 | 7.5468 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-13 12:30 | 9.7 | 9.5 | 270 | 3280 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 129443 | 7.5846 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-13 13:30 | 10.2 | 9.9 | 272.5 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 130088 | 7.6223 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-13 14:30 | 10.8 | 9.3 | 280 | 2920 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 130733 | 7.6601 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-13 15:30 | 11 | 8.2 | 287.5 | 2200 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 131378 | 7.6979 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-13 16:30 | 10.8 | 7 | 292.5 | 1480 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 132023 | 7.7357 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-13 17:30 | 10.6 | 6.1 | 297.5 | 760 | 1120 | 800 | 0 | 800 | 400 | 0 | 132423 | 7.7592 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-13 18:30 | 10.4 | 6.4 | 297.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 132643 | 7.7721 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-13 19:30 | 10.1 | 7.3 | 295 | 1480 | 1120 | 800 | 0 | 800 | 400 | 0 | 133043 | 7.7955 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-13 20:30 | 9.4 | 7.8 | 300 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 133688 | 7.8333 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-13 21:30 | 9.1 | 8 | 310 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 134333 | 7.8711 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-13 22:30 | 8.8 | 7.5 | 317.5 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 134978 | 7.9089 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-13 23:30 | 8.2 | 6.7 | 320 | 1120 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 135558 | 7.9429 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-14 00:30 | 8 | 6.5 | 320 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 135958 | 7.9663 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-14 01:30 | 8 | 6.8 | 320 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 136358 | 7.9897 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-14 02:30 | 7.7 | 7.2 | 320 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 136848 | 8.0184 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-14 03:30 | 7.3 | 7.5 | 320 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 137493 | 8.0562 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-14 04:30 | 7.1 | 7.5 | 320 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 138138 | 8.094 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-14 05:30 | 7.1 | 7.6 | 322.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 138783 | 8.1318 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-14 06:30 | 7.2 | 7.7 | 325 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 139428 | 8.1696 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-14 07:30 | 7.5 | 7.7 | 322.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 140073 | 8.2074 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-14 08:30 | 7.8 | 7.8 | 320 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 140718 | 8.2452 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-14 09:30 | 8.5 | 8 | 320 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 141363 | 8.283 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-14 10:30 | 8.7 | 7.8 | 320 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 142008 | 8.3208 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-14 11:30 | 8.6 | 7.7 | 317.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 142653 | 8.3586 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-14 12:30 | 8.7 | 7.6 | 312.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 143298 | 8.3964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-14 13:30 | 8.7 | 7.3 | 310 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 143943 | 8.4342 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-14 14:30 | 8.5 | 7.3 | 310 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 144523 | 8.4681 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-14 15:30 | 8.6 | 7.5 | 310 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 145168 | 8.5059 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-14 16:30 | 8.7 | 7.2 | 312.5 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 145813 | 8.5437 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-14 17:30 | 8.4 | 6.8 | 315 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 146303 | 8.5724 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-14 18:30 | 8.2 | 6.7 | 312.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 146703 | 8.5959 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-14 19:30 | 7.9 | 6.5 | 310 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 147103 | 8.6193 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-14 20:30 | 7.8 | 6.4 | 305 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 147413 | 8.6375 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-14 21:30 | 7.7 | 6.4 | 292.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 147633 | 8.6504 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-14 22:30 | 7.5 | 6 | 282.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 147853 | 8.6633 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-14 23:30 | 7.5 | 5.3 | 280 | 340 | 550 | 230 | 0 | 230 | 115 | 0 | 147968 | 8.67 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-07-15 00:30 | 7.6 | 4.9 | 280 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 147856.1481 | 8.6634 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-07-15 01:30 | 7.8 | 5.3 | 277.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 147744.2963 | 8.6569 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-15 02:30 | 7.9 | 5.7 | 270 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 147794.2963 | 8.6598 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-15 03:30 | 7.9 | 5.7 | 262.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 147884.2963 | 8.6651 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-15 04:30 | 7.9 | 5.8 | 257.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 147974.2963 | 8.6704 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-15 05:30 | 8 | 5.8 | 252.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 148064.2963 | 8.6756 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-15 06:30 | 8.2 | 5.5 | 250 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 148154.2963 | 8.6809 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-15 07:30 | 8.1 | 5.5 | 247.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 148244.2963 | 8.6862 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-15 08:30 | 8.4 | 5.8 | 247.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 148334.2963 | 8.6915 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-15 09:30 | 8.8 | 6.1 | 257.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 148489.2963 | 8.7005 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-15 10:30 | 9.1 | 6.5 | 267.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 148799.2963 | 8.7187 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-15 11:30 | 9.7 | 6.7 | 270 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 149199.2963 | 8.7421 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-15 12:30 | 9.9 | 6.7 | 272.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 149599.2963 | 8.7656 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-15 13:30 | 10 | 6.7 | 280 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 149999.2963 | 8.789 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-15 14:30 | 10.2 | 6.9 | 290 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 150399.2963 | 8.8125 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-15 15:30 | 10.4 | 7.1 | 297.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 150889.2963 | 8.8412 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-15 16:30 | 10.5 | 7 | 302.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 151469.2963 | 8.8752 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-15 17:30 | 10.4 | 7.3 | 310 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 152049.2963 | 8.9091 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-15 18:30 | 9.7 | 7.8 | 317.5 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 152694.2963 | 8.9469 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-15 19:30 | 9.2 | 7.8 | 317.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 153339.2963 | 8.9847 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-15 20:30 | 8.8 | 7.3 | 312.5 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 153984.2963 | 9.0225 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-15 21:30 | 7.8 | 6.6 | 312.5 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 154474.2963 | 9.0512 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-15 22:30 | 7.1 | 5.6 | 317.5 | 500 | 810 | 490 | 0 | 490 | 245 | 0 | 154719.2963 | 9.0656 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-15 23:30 | 6.9 | 4.9 | 320 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 154734.1296 | 9.0665 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-07-16 00:30 | 6.6 | 5.1 | 320 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 154622.2778 | 9.0599 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-16 01:30 | 6.5 | 5.6 | 320 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 154672.2778 | 9.0628 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-16 02:30 | 6.7 | 6.1 | 320 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 154827.2778 | 9.0719 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-16 03:30 | 6.9 | 6.1 | 317.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 155047.2778 | 9.0848 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-16 04:30 | 6.9 | 5.8 | 312.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 155202.2778 | 9.0939 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-16 05:30 | 6.9 | 5.9 | 312.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 155292.2778 | 9.0992 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-16 06:30 | 7.3 | 6 | 317.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 155447.2778 | 9.1082 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-16 07:30 | 8.1 | 5.8 | 317.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 155602.2778 | 9.1173 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-16 08:30 | 8.7 | 5.7 | 310 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 155692.2778 | 9.1226 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-16 09:30 | 9.2 | 5.8 | 302.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 155782.2778 | 9.1279 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-16 10:30 | 9.2 | 5.9 | 302.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 155872.2778 | 9.1331 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-16 11:30 | 9.1 | 5.8 | 307.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 155962.2778 | 9.1384 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-16 12:30 | 9.3 | 5.7 | 307.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 156052.2778 | 9.1437 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-16 13:30 | 9.8 | 5.5 | 302.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 156142.2778 | 9.149 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-16 14:30 | 10.6 | 5.9 | 290 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 156232.2778 | 9.1542 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-16 15:30 | 11.1 | 6.8 | 272.5 | 1120 | 810 | 490 | 0 | 490 | 245 | 0 | 156477.2778 | 9.1686 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-16 16:30 | 10.4 | 6.7 | 267.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 156877.2778 | 9.192 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-16 17:30 | 9.5 | 5.6 | 275 | 500 | 810 | 490 | 0 | 490 | 245 | 0 | 157122.2778 | 9.2064 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-16 18:30 | 8.9 | 4.5 | 282.5 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 157137.1111 | 9.2073 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-07-16 19:30 | 8.5 | 3.8 | 282.5 | 0 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 156647.4815 | 9.1786 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-07-16 20:30 | 8.3 | 3.4 | 277.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 155936.3704 | 9.1369 | 0 |  |  | 1 | 3 | 1 | 1
Lerwick | 1978-07-16 21:30 | 8 | 3.3 | 270 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 155225.2593 | 9.0952 | 0 |  |  | 1 | 4 | 1 | 2
Lerwick | 1978-07-16 22:30 | 7.9 | 3.2 | 257.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 154514.1481 | 9.0536 | 0 |  |  | 1 | 5 | 1 | 3
Lerwick | 1978-07-16 23:30 | 7.8 | 2.6 | 245 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 153803.037 | 9.0119 | 0 |  |  | 1 | 6 | 1 | 4
Lerwick | 1978-07-17 00:30 | 7.7 | 2 | 235 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 153091.9259 | 8.9702 | 0 |  |  | 1 | 7 | 1 | 5
Lerwick | 1978-07-17 01:30 | 7.6 | 2.2 | 225 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 152380.8148 | 8.9286 | 0 |  |  | 1 | 8 | 1 | 6
Lerwick | 1978-07-17 02:30 | 7.7 | 3.2 | 217.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 151669.7037 | 8.8869 | 0 |  |  | 1 | 9 | 1 | 7
Lerwick | 1978-07-17 03:30 | 8.1 | 4.1 | 212.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 151043.7778 | 8.8502 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-07-17 04:30 | 8.3 | 4.7 | 207.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 150639.3333 | 8.8265 | 1 |  |  | 1 | 11 | 0 | 0
Lerwick | 1978-07-17 05:30 | 8.4 | 5.4 | 202.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 150527.4815 | 8.82 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-17 06:30 | 8.8 | 6.3 | 202.5 | 760 | 550 | 230 | 0 | 230 | 115 | 0 | 150642.4815 | 8.8267 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-17 07:30 | 9.2 | 6.9 | 207.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 150952.4815 | 8.8449 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-17 08:30 | 9.3 | 7.2 | 210 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 151442.4815 | 8.8736 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-17 09:30 | 9.4 | 7.2 | 210 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 152022.4815 | 8.9076 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-17 10:30 | 9.4 | 7.4 | 212.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 152602.4815 | 8.9416 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-17 11:30 | 9.7 | 7.7 | 215 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 153247.4815 | 8.9793 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-17 12:30 | 10 | 7.4 | 210 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 153892.4815 | 9.0171 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-17 13:30 | 10 | 6.9 | 200 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 154382.4815 | 9.0458 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-17 14:30 | 10 | 6.4 | 192.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 154692.4815 | 9.064 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-17 15:30 | 10 | 6.2 | 187.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 154912.4815 | 9.0769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-17 16:30 | 10 | 6 | 182.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 155132.4815 | 9.0898 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-17 17:30 | 10.2 | 5.6 | 180 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 155287.4815 | 9.0989 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-17 18:30 | 10.5 | 4.9 | 177.5 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 155302.3148 | 9.0997 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-07-17 19:30 | 10.2 | 4.1 | 175 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 154897.8704 | 9.076 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-07-17 20:30 | 9.7 | 3.9 | 175 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 154271.9444 | 9.0394 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-07-17 21:30 | 9.4 | 3.7 | 170 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 153560.8333 | 8.9977 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-07-17 22:30 | 9.5 | 3.6 | 162.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 152849.7222 | 8.956 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-07-17 23:30 | 9.5 | 3.1 | 157.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 152138.6111 | 8.9144 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-07-18 00:30 | 9.5 | 2.1 | 160 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 151427.5 | 8.8727 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-07-18 01:30 | 9.5 | 1.2 | 207.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 150716.3889 | 8.831 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-07-18 02:30 | 9.6 | 1.2 | 287.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 150005.2778 | 8.7894 | 0 |  |  | 1 | 9 | 1 | 6
Lerwick | 1978-07-18 03:30 | 9.6 | 1.8 | 330 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 149294.1667 | 8.7477 | 0 |  |  | 1 | 10 | 1 | 7
Lerwick | 1978-07-18 04:30 | 9.6 | 2.4 | 337.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 148583.0556 | 8.706 | 0 |  |  | 1 | 11 | 1 | 8
Lerwick | 1978-07-18 05:30 | 9.6 | 2.9 | 342.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 147871.9444 | 8.6644 | 0 |  |  | 1 | 12 | 1 | 9
Lerwick | 1978-07-18 06:30 | 9.7 | 2.9 | 345 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 147160.8333 | 8.6227 | 0 |  |  | 1 | 13 | 1 | 10
Lerwick | 1978-07-18 07:30 | 9.9 | 2.9 | 340 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 146449.7222 | 8.581 | 0 |  |  | 1 | 14 | 1 | 11
Lerwick | 1978-07-18 08:30 | 10 | 3.3 | 330 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 145738.6111 | 8.5394 | 0 |  |  | 1 | 15 | 1 | 12
Lerwick | 1978-07-18 09:30 | 10 | 3.4 | 322.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 145027.5 | 8.4977 | 0 |  |  | 1 | 16 | 1 | 13
Lerwick | 1978-07-18 10:30 | 10.2 | 2.9 | 327.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 144316.3889 | 8.456 | 0 |  |  | 1 | 17 | 1 | 14
Lerwick | 1978-07-18 11:30 | 10.5 | 2.6 | 327.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 143605.2778 | 8.4144 | 0 |  |  | 1 | 18 | 1 | 15
Lerwick | 1978-07-18 12:30 | 10.5 | 3.2 | 300 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 142894.1667 | 8.3727 | 0 |  |  | 1 | 19 | 1 | 16
Lerwick | 1978-07-18 13:30 | 10.9 | 4.4 | 277.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 142268.2407 | 8.336 | 1 |  |  | 1 | 20 | 0 | 0
Lerwick | 1978-07-18 14:30 | 11.4 | 5.1 | 277.5 | 340 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 142020.0926 | 8.3215 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-18 15:30 | 11.5 | 5.4 | 282.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 142030.0926 | 8.3221 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-18 16:30 | 11.2 | 5.4 | 285 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 142040.0926 | 8.3227 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-18 17:30 | 11 | 5.5 | 280 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 142090.0926 | 8.3256 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-18 18:30 | 10.7 | 5.7 | 272.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 142180.0926 | 8.3309 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-18 19:30 | 9.9 | 5.3 | 270 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 142230.0926 | 8.3338 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-07-18 20:30 | 8.9 | 4.4 | 267.5 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 141981.9444 | 8.3193 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-07-18 21:30 | 8.5 | 3.9 | 262.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 141356.0185 | 8.2826 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-07-18 22:30 | 8.1 | 3.9 | 260 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 140644.9074 | 8.2409 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-07-18 23:30 | 7.8 | 3.9 | 260 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 139933.7963 | 8.1992 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-07-19 00:30 | 8 | 3.9 | 257.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 139222.6852 | 8.1576 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-07-19 01:30 | 8.1 | 3.6 | 252.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 138511.5741 | 8.1159 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-07-19 02:30 | 8 | 3 | 252.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 137800.463 | 8.0742 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-07-19 03:30 | 7.9 | 2.6 | 260 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 137089.3519 | 8.0326 | 0 |  |  | 1 | 9 | 1 | 6
Lerwick | 1978-07-19 04:30 | 7.9 | 2.3 | 270 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 136378.2407 | 7.9909 | 0 |  |  | 1 | 10 | 1 | 7
Lerwick | 1978-07-19 05:30 | 8 | 1.8 | 280 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 135667.1296 | 7.9492 | 0 |  |  | 1 | 11 | 1 | 8
Lerwick | 1978-07-19 06:30 | 8.1 | 1.6 | 285 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 134956.0185 | 7.9076 | 0 |  |  | 1 | 12 | 1 | 9
Lerwick | 1978-07-19 07:30 | 8.3 | 2 | 280 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 134244.9074 | 7.8659 | 0 |  |  | 1 | 13 | 1 | 10
Lerwick | 1978-07-19 08:30 | 9 | 2.4 | 137.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 133533.7963 | 7.8242 | 0 |  |  | 1 | 14 | 1 | 11
Lerwick | 1978-07-19 09:30 | 9.4 | 2.2 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 132822.6852 | 7.7826 | 0 |  |  | 1 | 15 | 1 | 12
Lerwick | 1978-07-19 10:30 | 9.6 | 1.5 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 132111.5741 | 7.7409 | 0 |  |  | 1 | 16 | 1 | 13
Lerwick | 1978-07-19 11:30 | 9.6 | 1.4 | 32.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 131400.463 | 7.6992 | 0 |  |  | 1 | 17 | 1 | 14
Lerwick | 1978-07-19 12:30 | 9.4 | 1.4 | 32.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 130689.3519 | 7.6576 | 0 |  |  | 1 | 18 | 1 | 15
Lerwick | 1978-07-19 13:30 | 9.2 | 1.1 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 129978.2407 | 7.6159 | 0 |  |  | 1 | 19 | 1 | 16
Lerwick | 1978-07-19 14:30 | 9 | 1 | 57.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 129267.1296 | 7.5742 | 0 |  |  | 1 | 20 | 1 | 17
Lerwick | 1978-07-19 15:30 | 9 | 1.1 | 95 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 128556.0185 | 7.5326 | 0 |  |  | 1 | 21 | 1 | 18
Lerwick | 1978-07-19 16:30 | 9 | 1.9 | 57.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 127844.9074 | 7.4909 | 0 |  |  | 1 | 22 | 1 | 19
Lerwick | 1978-07-19 17:30 | 9.2 | 3.7 | 37.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 127133.7963 | 7.4492 | 0 |  |  | 1 | 23 | 1 | 20
Lerwick | 1978-07-19 18:30 | 9.2 | 5.8 | 40 | 500 | 250 | 0 | 70 | 0 | 0 | 155.5556 | 126978.2407 | 7.4401 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-19 19:30 | 9 | 6.9 | 45 | 1120 | 810 | 490 | 0 | 490 | 245 | 0 | 127223.2407 | 7.4545 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-19 20:30 | 9 | 7.3 | 40 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 127713.2407 | 7.4832 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-19 21:30 | 9.2 | 7.5 | 30 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 128358.2407 | 7.521 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-19 22:30 | 9.3 | 7.2 | 22.5 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 129003.2407 | 7.5588 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-19 23:30 | 9.1 | 6.8 | 15 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 129493.2407 | 7.5875 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-20 00:30 | 8.8 | 6.3 | 182.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 129803.2407 | 7.6057 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-20 01:30 | 8.3 | 5.6 | 352.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 129958.2407 | 7.6147 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-20 02:30 | 8.1 | 5.8 | 347.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 130048.2407 | 7.62 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-20 03:30 | 8 | 6.4 | 345 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 130203.2407 | 7.6291 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-20 04:30 | 7.9 | 6.9 | 342.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 130513.2407 | 7.6473 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-20 05:30 | 8.2 | 7.4 | 335 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 131003.2407 | 7.676 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-20 06:30 | 8.7 | 7.9 | 330 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 131648.2407 | 7.7138 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-20 07:30 | 9.5 | 8.3 | 327.5 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 132293.2407 | 7.7516 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-20 08:30 | 9.8 | 8.5 | 322.5 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 132938.2407 | 7.7894 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-20 09:30 | 9.6 | 8.6 | 320 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 133583.2407 | 7.8271 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-20 10:30 | 9.4 | 8.6 | 320 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 134228.2407 | 7.8649 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-20 11:30 | 9.4 | 8.3 | 320 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 134873.2407 | 7.9027 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-20 12:30 | 9.4 | 8.3 | 322.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 135518.2407 | 7.9405 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-20 13:30 | 9.4 | 8.6 | 327.5 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 136163.2407 | 7.9783 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-20 14:30 | 9.6 | 8.9 | 330 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 136808.2407 | 8.0161 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-20 15:30 | 9.8 | 9.1 | 330 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 137453.2407 | 8.0539 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-20 16:30 | 10.1 | 9 | 330 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 138098.2407 | 8.0917 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-20 17:30 | 10.1 | 8.4 | 330 | 2200 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 138743.2407 | 8.1295 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-20 18:30 | 9.7 | 8.3 | 327.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 139388.2407 | 8.1673 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-20 19:30 | 9.3 | 8.5 | 322.5 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 140033.2407 | 8.2051 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-20 20:30 | 8.8 | 8.5 | 317.5 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 140678.2407 | 8.2429 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-20 21:30 | 8.4 | 8.6 | 315 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 141323.2407 | 8.2807 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-20 22:30 | 8.2 | 8.4 | 315 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 141968.2407 | 8.3185 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-20 23:30 | 8 | 8 | 315 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 142613.2407 | 8.3562 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-21 00:30 | 7.8 | 8.4 | 315 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 143258.2407 | 8.394 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-21 01:30 | 7.5 | 8.8 | 310 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 143903.2407 | 8.4318 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-21 02:30 | 7.1 | 8.8 | 302.5 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 144548.2407 | 8.4696 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-21 03:30 | 7 | 8.9 | 300 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 145193.2407 | 8.5074 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-21 04:30 | 7 | 8.7 | 300 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 145838.2407 | 8.5452 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-21 05:30 | 7 | 8.2 | 297.5 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 146483.2407 | 8.583 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-21 06:30 | 7 | 8 | 292.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 147128.2407 | 8.6208 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-21 07:30 | 7.1 | 8.7 | 290 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 147773.2407 | 8.6586 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-21 08:30 | 7.4 | 9.3 | 290 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 148418.2407 | 8.6964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-21 09:30 | 7.6 | 9.1 | 287.5 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 149063.2407 | 8.7342 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-21 10:30 | 7.8 | 9.1 | 282.5 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 149708.2407 | 8.772 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-21 11:30 | 7.9 | 9.1 | 280 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 150353.2407 | 8.8098 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-21 12:30 | 8.4 | 8.7 | 280 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 150998.2407 | 8.8476 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-21 13:30 | 8.9 | 8.3 | 277.5 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 151643.2407 | 8.8853 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-21 14:30 | 8.9 | 8 | 272.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 152288.2407 | 8.9231 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-21 15:30 | 8.7 | 8 | 267.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 152933.2407 | 8.9609 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-21 16:30 | 8.7 | 8 | 262.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 153578.2407 | 8.9987 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-21 17:30 | 8.7 | 7.5 | 262.5 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 154223.2407 | 9.0365 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-21 18:30 | 8.5 | 6.3 | 262.5 | 760 | 1300 | 980 | 0 | 980 | 490 | 0 | 154713.2407 | 9.0652 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-21 19:30 | 8.5 | 4.8 | 250 | 199.3333 | 479.6667 | 159.6667 | 0 | 159.6667 | 79.8333 | 0 | 154793.0741 | 9.0699 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-07-21 20:30 | 8.3 | 3.6 | 230 | 0 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 154303.4444 | 9.0412 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-07-21 21:30 | 8 | 3.3 | 212.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 153592.3333 | 8.9996 | 0 |  |  | 1 | 3 | 1 | 1
Lerwick | 1978-07-21 22:30 | 8.2 | 3.4 | 202.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 152881.2222 | 8.9579 | 0 |  |  | 1 | 4 | 1 | 2
Lerwick | 1978-07-21 23:30 | 7.9 | 3.7 | 200 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 152170.1111 | 8.9162 | 0 |  |  | 1 | 5 | 1 | 3
Lerwick | 1978-07-22 00:30 | 7.7 | 3.9 | 197.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 151459 | 8.8746 | 0 |  |  | 1 | 6 | 1 | 4
Lerwick | 1978-07-22 01:30 | 8.2 | 4.2 | 190 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 150833.0741 | 8.8379 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-07-22 02:30 | 8.5 | 4.9 | 180 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 150428.6296 | 8.8142 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-22 03:30 | 8.8 | 5.9 | 170 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 150443.463 | 8.815 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-22 04:30 | 9 | 6.9 | 160 | 1120 | 810 | 490 | 0 | 490 | 245 | 0 | 150688.463 | 8.8294 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-22 05:30 | 9.2 | 7.6 | 152.5 | 1840 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 151268.463 | 8.8634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-22 06:30 | 9.7 | 7.7 | 150 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 151913.463 | 8.9012 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-22 07:30 | 9.7 | 7.8 | 150 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 152558.463 | 8.939 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-22 08:30 | 9.8 | 8 | 150 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 153203.463 | 8.9768 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-22 09:30 | 10.3 | 7.7 | 150 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 153848.463 | 9.0146 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-22 10:30 | 11 | 7.3 | 150 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 154493.463 | 9.0524 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-22 11:30 | 12.3 | 7.3 | 150 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 155073.463 | 9.0863 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-22 12:30 | 12.8 | 7.6 | 152.5 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 155718.463 | 9.1241 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-22 13:30 | 11.9 | 7.8 | 157.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 156363.463 | 9.1619 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-22 14:30 | 11.4 | 8 | 160 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 157008.463 | 9.1997 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-22 15:30 | 11.3 | 8 | 160 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 157653.463 | 9.2375 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-22 16:30 | 11.4 | 8.5 | 160 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 158298.463 | 9.2753 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-22 17:30 | 11.4 | 9.4 | 160 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 158943.463 | 9.3131 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-22 18:30 | 11.4 | 9.6 | 160 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 159588.463 | 9.3509 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-22 19:30 | 11.3 | 8.8 | 160 | 2560 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 160233.463 | 9.3887 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-22 20:30 | 11.1 | 7.9 | 160 | 1840 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 160878.463 | 9.4265 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-22 21:30 | 11 | 7.6 | 160 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 161523.463 | 9.4643 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-22 22:30 | 11 | 7.1 | 160 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 162168.463 | 9.5021 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-22 23:30 | 11 | 6.3 | 162.5 | 760 | 1120 | 800 | 0 | 800 | 400 | 0 | 162568.463 | 9.5255 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-23 00:30 | 11 | 5.4 | 167.5 | 340 | 550 | 230 | 0 | 230 | 115 | 0 | 162683.463 | 9.5322 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-07-23 01:30 | 11 | 4.7 | 170 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 162571.6111 | 9.5257 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-07-23 02:30 | 11 | 4.7 | 170 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 162303.463 | 9.51 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-07-23 03:30 | 10.9 | 4.7 | 167.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 162035.3148 | 9.4943 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-07-23 04:30 | 10.7 | 4.5 | 165 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 161767.1667 | 9.4785 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-07-23 05:30 | 10.7 | 4.7 | 165 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 161499.0185 | 9.4628 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-07-23 06:30 | 10.9 | 5.3 | 162.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 161387.1667 | 9.4563 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-23 07:30 | 11 | 5.7 | 160 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 161437.1667 | 9.4592 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-23 08:30 | 11.1 | 5.5 | 162.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 161527.1667 | 9.4645 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-23 09:30 | 11 | 4.9 | 165 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 161542 | 9.4654 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-07-23 10:30 | 11.1 | 4.4 | 165 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 161137.5556 | 9.4417 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-07-23 11:30 | 11.3 | 4.7 | 167.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 160733.1111 | 9.418 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-23 12:30 | 11.3 | 5.6 | 167.5 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 160747.9444 | 9.4188 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-23 13:30 | 12.4 | 6.3 | 162.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 160902.9444 | 9.4279 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-23 14:30 | 13.8 | 6.3 | 162.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 161122.9444 | 9.4408 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-23 15:30 | 14.3 | 6 | 165 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 161342.9444 | 9.4537 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-23 16:30 | 13.8 | 5.8 | 162.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 161497.9444 | 9.4628 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-23 17:30 | 13 | 5.8 | 162.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 161587.9444 | 9.468 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-23 18:30 | 12.4 | 5.8 | 165 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 161677.9444 | 9.4733 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-23 19:30 | 11.8 | 5.1 | 157.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 161727.9444 | 9.4762 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-07-23 20:30 | 11.4 | 4.4 | 150 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 161479.7963 | 9.4617 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-07-23 21:30 | 10.9 | 4.2 | 157.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 160939.0556 | 9.43 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-07-23 22:30 | 10.5 | 3.8 | 177.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 160313.1296 | 9.3933 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-07-23 23:30 | 10.5 | 3.3 | 202.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 159602.0185 | 9.3517 | 0 |  |  | 1 | 5 | 1 | 1
Lerwick | 1978-07-24 00:30 | 10.7 | 2.4 | 107.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 158890.9074 | 9.31 | 0 |  |  | 1 | 6 | 1 | 2
Lerwick | 1978-07-24 01:30 | 11 | 1.1 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 158179.7963 | 9.2683 | 0 |  |  | 1 | 7 | 1 | 3
Lerwick | 1978-07-24 02:30 | 10.9 | 0.2 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 157468.6852 | 9.2267 | 0 |  |  | 1 | 8 | 1 | 4
Lerwick | 1978-07-24 03:30 | 10.4 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 156757.5741 | 9.185 | 0 |  |  | 1 | 9 | 1 | 5
Lerwick | 1978-07-24 04:30 | 9.8 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 156046.463 | 9.1433 | 0 |  |  | 1 | 10 | 1 | 6
Lerwick | 1978-07-24 05:30 | 9.8 | 1.1 | 145 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 155335.3519 | 9.1017 | 0 |  |  | 1 | 11 | 1 | 7
Lerwick | 1978-07-24 06:30 | 11 | 3.8 | 262.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 154624.2407 | 9.06 | 0 |  |  | 1 | 12 | 1 | 8
Lerwick | 1978-07-24 07:30 | 11.5 | 5.9 | 240 | 500 | 250 | 0 | 70 | 0 | 0 | 155.5556 | 154468.6852 | 9.0509 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-24 08:30 | 11.7 | 6.4 | 235 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 154623.6852 | 9.06 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-24 09:30 | 12.5 | 6.4 | 205 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 154843.6852 | 9.0729 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-24 10:30 | 12.8 | 6.7 | 175 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 155153.6852 | 9.091 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-24 11:30 | 13.6 | 7.2 | 167.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 155643.6852 | 9.1197 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-24 12:30 | 13.7 | 7.7 | 172.5 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 156288.6852 | 9.1575 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-24 13:30 | 13.6 | 7.7 | 177.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 156933.6852 | 9.1953 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-24 14:30 | 14.1 | 6.9 | 180 | 1120 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 157513.6852 | 9.2293 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-24 15:30 | 13.4 | 6.1 | 177.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 157823.6852 | 9.2475 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-24 16:30 | 12.2 | 5.9 | 175 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 157978.6852 | 9.2566 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-24 17:30 | 11.7 | 5.9 | 177.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 158068.6852 | 9.2618 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-24 18:30 | 11.9 | 6 | 182.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 158223.6852 | 9.2709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-24 19:30 | 12 | 6.7 | 192.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 158533.6852 | 9.2891 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-24 20:30 | 11.4 | 7.1 | 200 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 159023.6852 | 9.3178 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-24 21:30 | 11 | 7 | 195 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 159603.6852 | 9.3518 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-24 22:30 | 11 | 7.3 | 190 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 160183.6852 | 9.3858 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-24 23:30 | 10.5 | 7.9 | 192.5 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 160828.6852 | 9.4236 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-25 00:30 | 10.1 | 8.5 | 195 | 2560 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 161473.6852 | 9.4613 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-25 01:30 | 9.9 | 9.1 | 195 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 162118.6852 | 9.4991 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-25 02:30 | 9.7 | 9.8 | 200 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 162763.6852 | 9.5369 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-25 03:30 | 9.8 | 10.8 | 207.5 | 4000 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 163408.6852 | 9.5747 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-25 04:30 | 10 | 11.1 | 210 | 4300 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 164053.6852 | 9.6125 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-25 05:30 | 10.1 | 11.2 | 210 | 4300 | 4300 | 3980 | 0 | 1290 | 645 | 0 | 164698.6852 | 9.6503 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-25 06:30 | 10.3 | 12 | 212.5 | 4536.1111 | 4418.0556 | 4098.0556 | 0 | 1290 | 645 | 0 | 165343.6852 | 9.6881 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-25 07:30 | 10.3 | 12.5 | 217.5 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 645 | 0 | 165988.6852 | 9.7259 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-25 08:30 | 10.4 | 12.2 | 222.5 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 645 | 0 | 166633.6852 | 9.7637 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-25 09:30 | 10.7 | 12 | 227.5 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 167278.6852 | 9.8015 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-25 10:30 | 10.9 | 11.9 | 230 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 645 | 0 | 167923.6852 | 9.8393 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-25 11:30 | 11.1 | 11.5 | 232.5 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 645 | 0 | 168568.6852 | 9.8771 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-25 12:30 | 11.1 | 11.1 | 232.5 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 169213.6852 | 9.9149 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-25 13:30 | 11.6 | 10.4 | 222.5 | 3640 | 3970 | 3650 | 0 | 1290 | 645 | 0 | 169858.6852 | 9.9527 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-25 14:30 | 12.2 | 8.9 | 212.5 | 2560 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 170503.6852 | 9.9905 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-25 15:30 | 11.7 | 7.2 | 202.5 | 1480 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170503.6852 | 9.9905 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-25 16:30 | 11.9 | 6 | 185 | 760 | 1120 | 800 | 0 | 800 | 0 | 0 | 170503.6852 | 9.9905 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-25 17:30 | 12.4 | 5.1 | 172.5 | 340 | 550 | 230 | 0 | 230 | 0 | 0 | 170503.6852 | 9.9905 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-07-25 18:30 | 12 | 4 | 170 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 170255.537 | 9.9759 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-07-25 19:30 | 11.1 | 3.7 | 165 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 169629.6111 | 9.9392 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-07-25 20:30 | 10.7 | 4.4 | 157.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 169003.6852 | 9.9026 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-07-25 21:30 | 10.4 | 5.3 | 157.5 | 340 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 168755.537 | 9.888 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-25 22:30 | 10.3 | 5.3 | 157.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 168765.537 | 9.8886 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-07-25 23:30 | 10.3 | 4.7 | 150 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 168653.6852 | 9.8821 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-07-26 00:30 | 10.3 | 4.9 | 145 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 168385.537 | 9.8663 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-26 01:30 | 10.5 | 5.8 | 147.5 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 168400.3704 | 9.8672 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-26 02:30 | 10.7 | 6.6 | 150 | 1120 | 810 | 490 | 0 | 490 | 245 | 0 | 168645.3704 | 9.8816 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-26 03:30 | 10.8 | 7 | 150 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 169135.3704 | 9.9103 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-26 04:30 | 10.7 | 7 | 147.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 169715.3704 | 9.9443 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-26 05:30 | 10.5 | 7.2 | 142.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 170295.3704 | 9.9782 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-26 06:30 | 10.7 | 7.6 | 140 | 1840 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170295.3704 | 9.9782 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-26 07:30 | 11 | 7.7 | 142.5 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170295.3704 | 9.9782 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-26 08:30 | 11 | 7.6 | 147.5 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170295.3704 | 9.9782 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-26 09:30 | 11 | 7.5 | 150 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170295.3704 | 9.9782 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-26 10:30 | 11.2 | 7.7 | 150 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170295.3704 | 9.9782 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-26 11:30 | 11.7 | 8.2 | 152.5 | 2200 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170295.3704 | 9.9782 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-26 12:30 | 11.9 | 8.6 | 157.5 | 2560 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170295.3704 | 9.9782 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-26 13:30 | 11.6 | 8.2 | 157.5 | 2200 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170295.3704 | 9.9782 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-26 14:30 | 11.6 | 7.3 | 152.5 | 1480 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170295.3704 | 9.9782 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-26 15:30 | 11.6 | 7.2 | 147.5 | 1480 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170295.3704 | 9.9782 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-26 16:30 | 11.4 | 7.6 | 142.5 | 1840 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170295.3704 | 9.9782 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-26 17:30 | 11.4 | 7.4 | 140 | 1480 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170295.3704 | 9.9782 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-26 18:30 | 11.3 | 6.7 | 140 | 1120 | 1300 | 980 | 0 | 980 | 0 | 0 | 170295.3704 | 9.9782 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-26 19:30 | 11.2 | 5.8 | 142.5 | 500 | 810 | 490 | 0 | 490 | 0 | 0 | 170295.3704 | 9.9782 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-26 20:30 | 11.1 | 5.1 | 147.5 | 340 | 420 | 100 | 0 | 100 | 0 | 0 | 170295.3704 | 9.9782 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-07-26 21:30 | 11.1 | 4.6 | 150 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 170183.5185 | 9.9717 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-07-26 22:30 | 11.1 | 4 | 150 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 169779.0741 | 9.948 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-07-26 23:30 | 11 | 3.1 | 157.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 169153.1481 | 9.9113 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-07-27 00:30 | 11 | 2.4 | 177.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168442.037 | 9.8697 | 0 |  |  | 1 | 5 | 1 | 1
Lerwick | 1978-07-27 01:30 | 11 | 2 | 190 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167730.9259 | 9.828 | 0 |  |  | 1 | 6 | 1 | 2
Lerwick | 1978-07-27 02:30 | 11.2 | 1.6 | 182.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167019.8148 | 9.7863 | 0 |  |  | 1 | 7 | 1 | 3
Lerwick | 1978-07-27 03:30 | 11 | 1.5 | 172.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166308.7037 | 9.7447 | 0 |  |  | 1 | 8 | 1 | 4
Lerwick | 1978-07-27 04:30 | 10.9 | 1.5 | 175 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165597.5926 | 9.703 | 0 |  |  | 1 | 9 | 1 | 5
Lerwick | 1978-07-27 05:30 | 10.9 | 1.8 | 182.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164886.4815 | 9.6613 | 0 |  |  | 1 | 10 | 1 | 6
Lerwick | 1978-07-27 06:30 | 10.9 | 3 | 182.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164175.3704 | 9.6197 | 0 |  |  | 1 | 11 | 1 | 7
Lerwick | 1978-07-27 07:30 | 11.1 | 4.4 | 180 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 163549.4444 | 9.583 | 1 |  |  | 1 | 12 | 0 | 0
Lerwick | 1978-07-27 08:30 | 11.3 | 5.3 | 177.5 | 340 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 163301.2963 | 9.5684 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-27 09:30 | 11.2 | 5.7 | 172.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 163351.2963 | 9.5714 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-27 10:30 | 10.7 | 5.3 | 165 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 163401.2963 | 9.5743 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-07-27 11:30 | 10.7 | 4.7 | 157.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 163289.4444 | 9.5677 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-07-27 12:30 | 11.2 | 4.9 | 160 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 163021.2963 | 9.552 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-27 13:30 | 11.9 | 6 | 165 | 760 | 479.6667 | 159.6667 | 0 | 159.6667 | 79.8333 | 0 | 163101.1296 | 9.5567 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-27 14:30 | 12.4 | 7.2 | 162.5 | 1480 | 1120 | 800 | 0 | 800 | 400 | 0 | 163501.1296 | 9.5801 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-27 15:30 | 12.4 | 8.1 | 160 | 2200 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 164146.1296 | 9.6179 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-27 16:30 | 12.4 | 8.6 | 160 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 164791.1296 | 9.6557 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-27 17:30 | 12.2 | 8.8 | 160 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 165436.1296 | 9.6935 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-27 18:30 | 11.8 | 8.4 | 162.5 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 166081.1296 | 9.7313 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-27 19:30 | 11.5 | 8 | 167.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 166726.1296 | 9.7691 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-27 20:30 | 11.5 | 7.8 | 170 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 167371.1296 | 9.8069 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-27 21:30 | 11.5 | 7.2 | 172.5 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 168016.1296 | 9.8447 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-27 22:30 | 11.5 | 6.2 | 177.5 | 760 | 1120 | 800 | 0 | 800 | 400 | 0 | 168416.1296 | 9.8681 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-27 23:30 | 11.5 | 5.3 | 180 | 340 | 550 | 230 | 0 | 230 | 115 | 0 | 168531.1296 | 9.8749 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-28 00:30 | 11.5 | 5.3 | 177.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 168541.1296 | 9.8755 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-28 01:30 | 11.5 | 5.9 | 172.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 168591.1296 | 9.8784 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-28 02:30 | 11.7 | 6.6 | 170 | 1120 | 810 | 490 | 0 | 490 | 245 | 0 | 168836.1296 | 9.8927 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-28 03:30 | 11.7 | 7 | 172.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 169326.1296 | 9.9215 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-28 04:30 | 11.5 | 6.6 | 177.5 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 169816.1296 | 9.9502 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-28 05:30 | 11.5 | 6.2 | 177.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 170126.1296 | 9.9683 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-28 06:30 | 11.5 | 5.5 | 172.5 | 500 | 630 | 310 | 0 | 310 | 0 | 0 | 170126.1296 | 9.9683 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-07-28 07:30 | 11.5 | 4.4 | 170 | 76.6667 | 288.3333 | 0 | 31.6667 | 0 | 0 | 70.3704 | 170055.7593 | 9.9642 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-07-28 08:30 | 11.5 | 4.8 | 170 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 169651.3148 | 9.9405 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-28 09:30 | 11.7 | 6.4 | 167.5 | 760 | 479.6667 | 159.6667 | 0 | 159.6667 | 79.8333 | 0 | 169731.1481 | 9.9452 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-28 10:30 | 12.8 | 7.4 | 165 | 1480 | 1120 | 800 | 0 | 800 | 400 | 0 | 170131.1481 | 9.9686 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-28 11:30 | 13.8 | 8.3 | 175 | 2200 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170131.1481 | 9.9686 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-28 12:30 | 13.4 | 9.7 | 202.5 | 3280 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170131.1481 | 9.9686 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-28 13:30 | 13 | 11 | 232.5 | 4300 | 3790 | 3470 | 0 | 1290 | 0 | 0 | 170131.1481 | 9.9686 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-28 14:30 | 12.7 | 11.2 | 247.5 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170131.1481 | 9.9686 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-28 15:30 | 12.7 | 10.4 | 247.5 | 3640 | 3970 | 3650 | 0 | 1290 | 0 | 0 | 170131.1481 | 9.9686 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-28 16:30 | 13.5 | 9.4 | 240 | 2920 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170131.1481 | 9.9686 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-28 17:30 | 14 | 9 | 230 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170131.1481 | 9.9686 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-28 18:30 | 13.7 | 8.5 | 220 | 2560 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170131.1481 | 9.9686 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-28 19:30 | 13.1 | 7.1 | 205 | 1480 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170131.1481 | 9.9686 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-28 20:30 | 12.6 | 5.3 | 190 | 340 | 910 | 590 | 0 | 590 | 0 | 0 | 170131.1481 | 9.9686 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-07-28 21:30 | 11.7 | 4.1 | 182.5 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 169883 | 9.9541 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-07-28 22:30 | 11 | 3.9 | 175 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 169257.0741 | 9.9174 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-07-28 23:30 | 11 | 3.7 | 172.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168545.963 | 9.8757 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-07-29 00:30 | 10.7 | 3.6 | 175 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167834.8519 | 9.8341 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-07-29 01:30 | 10.4 | 3.6 | 172.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167123.7407 | 9.7924 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-07-29 02:30 | 10.4 | 3.4 | 165 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166412.6296 | 9.7507 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-07-29 03:30 | 10.4 | 3.3 | 155 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165701.5185 | 9.7091 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-07-29 04:30 | 10.4 | 3.3 | 152.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164990.4074 | 9.6674 | 0 |  |  | 1 | 9 | 1 | 6
Lerwick | 1978-07-29 05:30 | 10.7 | 3.4 | 157.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164279.2963 | 9.6257 | 0 |  |  | 1 | 10 | 1 | 7
Lerwick | 1978-07-29 06:30 | 11.5 | 4 | 160 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 163653.3704 | 9.5891 | 1 |  |  | 1 | 11 | 0 | 0
Lerwick | 1978-07-29 07:30 | 11.8 | 4.4 | 162.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 163112.6296 | 9.5574 | 1 |  |  | 1 | 12 | 0 | 0
Lerwick | 1978-07-29 08:30 | 12.2 | 4.4 | 162.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 162571.8889 | 9.5257 | 1 |  |  | 1 | 13 | 0 | 0
Lerwick | 1978-07-29 09:30 | 13.1 | 4.4 | 157.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 162031.1481 | 9.494 | 1 |  |  | 1 | 14 | 0 | 0
Lerwick | 1978-07-29 10:30 | 13.5 | 4.4 | 157.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 161490.4074 | 9.4623 | 1 |  |  | 1 | 15 | 0 | 0
Lerwick | 1978-07-29 11:30 | 13.9 | 4.9 | 160 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 161085.963 | 9.4386 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-29 12:30 | 14 | 5.8 | 160 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 161100.7963 | 9.4395 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-29 13:30 | 14 | 5.9 | 157.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 161190.7963 | 9.4448 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-29 14:30 | 14.3 | 5.3 | 155 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 161240.7963 | 9.4477 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-29 15:30 | 14.7 | 5 | 157.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 161250.7963 | 9.4483 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-07-29 16:30 | 14.5 | 4.7 | 157.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 161138.9444 | 9.4417 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-07-29 17:30 | 14.1 | 4.2 | 155 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 160734.5 | 9.418 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-07-29 18:30 | 13.3 | 3.8 | 160 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 160108.5741 | 9.3814 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-07-29 19:30 | 12.6 | 2.9 | 165 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 159397.463 | 9.3397 | 0 |  |  | 1 | 5 | 1 | 1
Lerwick | 1978-07-29 20:30 | 12 | 1.8 | 177.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 158686.3519 | 9.298 | 0 |  |  | 1 | 6 | 1 | 2
Lerwick | 1978-07-29 21:30 | 10.9 | 1.5 | 95 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 157975.2407 | 9.2564 | 0 |  |  | 1 | 7 | 1 | 3
Lerwick | 1978-07-29 22:30 | 10.3 | 1.4 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 157264.1296 | 9.2147 | 0 |  |  | 1 | 8 | 1 | 4
Lerwick | 1978-07-29 23:30 | 9.8 | 1.1 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 156553.0185 | 9.173 | 0 |  |  | 1 | 9 | 1 | 5
Lerwick | 1978-07-30 00:30 | 9.5 | 1 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 155841.9074 | 9.1314 | 0 |  |  | 1 | 10 | 1 | 6
Lerwick | 1978-07-30 01:30 | 9.3 | 1 | 77.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 155130.7963 | 9.0897 | 0 |  |  | 1 | 11 | 1 | 7
Lerwick | 1978-07-30 02:30 | 9.4 | 1 | 157.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 154419.6852 | 9.048 | 0 |  |  | 1 | 12 | 1 | 8
Lerwick | 1978-07-30 03:30 | 9.6 | 1.1 | 157.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 153708.5741 | 9.0064 | 0 |  |  | 1 | 13 | 1 | 9
Lerwick | 1978-07-30 04:30 | 9.6 | 1.3 | 147.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 152997.463 | 8.9647 | 0 |  |  | 1 | 14 | 1 | 10
Lerwick | 1978-07-30 05:30 | 9.9 | 1.4 | 142.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 152286.3519 | 8.923 | 0 |  |  | 1 | 15 | 1 | 11
Lerwick | 1978-07-30 06:30 | 10.7 | 1.8 | 150 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 151575.2407 | 8.8814 | 0 |  |  | 1 | 16 | 1 | 12
Lerwick | 1978-07-30 07:30 | 11.4 | 2.4 | 152.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 150864.1296 | 8.8397 | 0 |  |  | 1 | 17 | 1 | 13
Lerwick | 1978-07-30 08:30 | 12 | 2.6 | 152.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 150153.0185 | 8.798 | 0 |  |  | 1 | 18 | 1 | 14
Lerwick | 1978-07-30 09:30 | 12.3 | 2.4 | 165 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 149441.9074 | 8.7564 | 0 |  |  | 1 | 19 | 1 | 15
Lerwick | 1978-07-30 10:30 | 12.5 | 2.1 | 172.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 148730.7963 | 8.7147 | 0 |  |  | 1 | 20 | 1 | 16
Lerwick | 1978-07-30 11:30 | 13 | 2.3 | 160 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 148019.6852 | 8.673 | 0 |  |  | 1 | 21 | 1 | 17
Lerwick | 1978-07-30 12:30 | 13 | 2.6 | 150 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 147308.5741 | 8.6314 | 0 |  |  | 1 | 22 | 1 | 18
Lerwick | 1978-07-30 13:30 | 12.6 | 2.6 | 152.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 146597.463 | 8.5897 | 0 |  |  | 1 | 23 | 1 | 19
Lerwick | 1978-07-30 14:30 | 12.7 | 2.3 | 152.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 145886.3519 | 8.548 | 0 |  |  | 1 | 24 | 1 | 20
Lerwick | 1978-07-30 15:30 | 13.1 | 2.1 | 125 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 145175.2407 | 8.5064 | 0 |  |  | 1 | 25 | 1 | 21
Lerwick | 1978-07-30 16:30 | 13.3 | 2.1 | 67.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 144464.1296 | 8.4647 | 0 |  |  | 1 | 26 | 1 | 22
Lerwick | 1978-07-30 17:30 | 13.1 | 2.1 | 25 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 143753.0185 | 8.423 | 0 |  |  | 1 | 27 | 1 | 23
Lerwick | 1978-07-30 18:30 | 12.6 | 2.9 | 20 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 143041.9074 | 8.3814 | 0 |  |  | 1 | 28 | 1 | 24
Lerwick | 1978-07-30 19:30 | 12.1 | 4 | 25 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 142415.9815 | 8.3447 | 1 |  |  | 1 | 29 | 0 | 0
Lerwick | 1978-07-30 20:30 | 11.6 | 4.7 | 22.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 142011.537 | 8.321 | 1 |  |  | 1 | 30 | 0 | 0
Lerwick | 1978-07-30 21:30 | 11.2 | 5.2 | 17.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 141899.6852 | 8.3144 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-30 22:30 | 11 | 5.8 | 10 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 141949.6852 | 8.3174 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-30 23:30 | 11 | 6.8 | 2.5 | 1120 | 810 | 490 | 0 | 490 | 245 | 0 | 142194.6852 | 8.3317 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-31 00:30 | 11 | 8.1 | 0 | 2200 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 142839.6852 | 8.3695 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-31 01:30 | 10.7 | 9 | 0 | 2920 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 143484.6852 | 8.4073 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-31 02:30 | 10.5 | 9.3 | 0 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 144129.6852 | 8.4451 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-31 03:30 | 10.5 | 9.4 | 0 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 144774.6852 | 8.4829 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-31 04:30 | 10.7 | 9.5 | 0 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 145419.6852 | 8.5207 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-31 05:30 | 10.8 | 9.4 | 0 | 2920 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 146064.6852 | 8.5585 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-31 06:30 | 10.8 | 9.3 | 177.5 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 146709.6852 | 8.5963 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-31 07:30 | 10.9 | 9.1 | 352.5 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 147354.6852 | 8.6341 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-31 08:30 | 11 | 8.7 | 350 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 147999.6852 | 8.6719 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-31 09:30 | 11.3 | 8.5 | 350 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 148644.6852 | 8.7096 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-31 10:30 | 11.5 | 8.6 | 352.5 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 149289.6852 | 8.7474 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-31 11:30 | 11.9 | 9 | 177.5 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 149934.6852 | 8.7852 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-31 12:30 | 12.7 | 9.5 | 2.5 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 150579.6852 | 8.823 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-31 13:30 | 13.5 | 9.6 | 5 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 151224.6852 | 8.8608 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-31 14:30 | 13.9 | 9.2 | 5 | 2920 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 151869.6852 | 8.8986 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-31 15:30 | 14.4 | 8.7 | 10 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 152514.6852 | 8.9364 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-31 16:30 | 13.8 | 8.1 | 15 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 153159.6852 | 8.9742 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-31 17:30 | 12.8 | 7.4 | 12.5 | 1480 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 153804.6852 | 9.012 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-31 18:30 | 12.5 | 7.2 | 10 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 154384.6852 | 9.046 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-31 19:30 | 12.1 | 7.3 | 7.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 154964.6852 | 9.08 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-31 20:30 | 11.8 | 7.8 | 2.5 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 155609.6852 | 9.1178 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-31 21:30 | 11.3 | 8.4 | 0 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 156254.6852 | 9.1555 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-31 22:30 | 11 | 8.8 | 2.5 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 156899.6852 | 9.1933 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-07-31 23:30 | 11 | 8.9 | 7.5 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 157544.6852 | 9.2311 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-01 00:30 | 11 | 9.4 | 10 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 158189.6852 | 9.2689 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-01 01:30 | 11 | 9.9 | 10 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 158834.6852 | 9.3067 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-01 02:30 | 10.9 | 9.9 | 10 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 159479.6852 | 9.3445 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-01 03:30 | 10.9 | 9.9 | 10 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 160124.6852 | 9.3823 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-01 04:30 | 10.9 | 10.4 | 10 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 160769.6852 | 9.4201 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-01 05:30 | 10.7 | 11 | 12.5 | 4300 | 3970 | 3650 | 0 | 1290 | 645 | 0 | 161414.6852 | 9.4579 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-01 06:30 | 10.5 | 11.3 | 17.5 | 4300 | 4300 | 3980 | 0 | 1290 | 645 | 0 | 162059.6852 | 9.4957 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-01 07:30 | 10.5 | 11.4 | 20 | 4300 | 4300 | 3980 | 0 | 1290 | 645 | 0 | 162704.6852 | 9.5335 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-01 08:30 | 10.7 | 11.7 | 20 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 163349.6852 | 9.5713 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-01 09:30 | 10.7 | 12 | 20 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 645 | 0 | 163994.6852 | 9.6091 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-01 10:30 | 10.7 | 11.7 | 20 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 645 | 0 | 164639.6852 | 9.6469 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-01 11:30 | 10.9 | 11.4 | 20 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 165284.6852 | 9.6846 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-01 12:30 | 11 | 11.3 | 20 | 4300 | 4300 | 3980 | 0 | 1290 | 645 | 0 | 165929.6852 | 9.7224 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-01 13:30 | 11 | 11.3 | 20 | 4300 | 4300 | 3980 | 0 | 1290 | 645 | 0 | 166574.6852 | 9.7602 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-01 14:30 | 11 | 11.3 | 20 | 4300 | 4300 | 3980 | 0 | 1290 | 645 | 0 | 167219.6852 | 9.798 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-01 15:30 | 11.1 | 11.1 | 22.5 | 4300 | 4300 | 3980 | 0 | 1290 | 645 | 0 | 167864.6852 | 9.8358 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-01 16:30 | 11.3 | 10.7 | 25 | 4000 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 168509.6852 | 9.8736 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-01 17:30 | 11.4 | 10 | 25 | 3640 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 169154.6852 | 9.9114 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-01 18:30 | 11.2 | 9.2 | 27.5 | 2920 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 169799.6852 | 9.9492 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-01 19:30 | 11 | 9 | 30 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 170444.6852 | 9.987 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-01 20:30 | 10.9 | 8.5 | 30 | 2560 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170444.6852 | 9.987 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-01 21:30 | 10.6 | 7.5 | 30 | 1840 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170444.6852 | 9.987 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-01 22:30 | 10.5 | 6.4 | 30 | 760 | 1300 | 980 | 0 | 980 | 0 | 0 | 170444.6852 | 9.987 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-01 23:30 | 10.5 | 5.6 | 30 | 500 | 630 | 310 | 0 | 310 | 0 | 0 | 170444.6852 | 9.987 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-02 00:30 | 10.5 | 5.5 | 30 | 500 | 500 | 180 | 0 | 180 | 0 | 0 | 170444.6852 | 9.987 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-02 01:30 | 10.6 | 5.9 | 27.5 | 500 | 500 | 180 | 0 | 180 | 0 | 0 | 170444.6852 | 9.987 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-02 02:30 | 10.9 | 6.3 | 22.5 | 760 | 630 | 310 | 0 | 310 | 0 | 0 | 170444.6852 | 9.987 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-02 03:30 | 10.7 | 6.3 | 17.5 | 760 | 760 | 440 | 0 | 440 | 0 | 0 | 170444.6852 | 9.987 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-02 04:30 | 10.5 | 6 | 15 | 760 | 760 | 440 | 0 | 440 | 0 | 0 | 170444.6852 | 9.987 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-02 05:30 | 10.5 | 5.4 | 20 | 340 | 550 | 230 | 0 | 230 | 0 | 0 | 170444.6852 | 9.987 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-08-02 06:30 | 11 | 4.4 | 30 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 170196.537 | 9.9725 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-08-02 07:30 | 11.5 | 3.6 | 57.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 169570.6111 | 9.9358 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-08-02 08:30 | 12 | 3 | 105 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168859.5 | 9.8941 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-08-02 09:30 | 12.6 | 2.4 | 137.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168148.3889 | 9.8524 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-08-02 10:30 | 13.2 | 2.6 | 150 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167437.2778 | 9.8108 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-08-02 11:30 | 13.4 | 2.9 | 177.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166726.1667 | 9.7691 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-08-02 12:30 | 13.1 | 2.4 | 200 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166015.0556 | 9.7274 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-08-02 13:30 | 13.3 | 2.4 | 175 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165303.9444 | 9.6858 | 0 |  |  | 1 | 9 | 1 | 6
Lerwick | 1978-08-02 14:30 | 13.7 | 2.6 | 150 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164592.8333 | 9.6441 | 0 |  |  | 1 | 10 | 1 | 7
Lerwick | 1978-08-02 15:30 | 13.1 | 2.6 | 155 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163881.7222 | 9.6024 | 0 |  |  | 1 | 11 | 1 | 8
Lerwick | 1978-08-02 16:30 | 12.4 | 2.4 | 165 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163170.6111 | 9.5608 | 0 |  |  | 1 | 12 | 1 | 9
Lerwick | 1978-08-02 17:30 | 12.1 | 2.1 | 137.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162459.5 | 9.5191 | 0 |  |  | 1 | 13 | 1 | 10
Lerwick | 1978-08-02 18:30 | 12 | 2.4 | 67.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161748.3889 | 9.4774 | 0 |  |  | 1 | 14 | 1 | 11
Lerwick | 1978-08-02 19:30 | 11.9 | 3 | 27.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161037.2778 | 9.4358 | 0 |  |  | 1 | 15 | 1 | 12
Lerwick | 1978-08-02 20:30 | 11.3 | 3.6 | 25 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160326.1667 | 9.3941 | 0 |  |  | 1 | 16 | 1 | 13
Lerwick | 1978-08-02 21:30 | 10.7 | 3.9 | 25 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 159615.0556 | 9.3524 | 0 |  |  | 1 | 17 | 1 | 14
Lerwick | 1978-08-02 22:30 | 10.4 | 4 | 22.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 158989.1296 | 9.3158 | 1 |  |  | 1 | 18 | 0 | 0
Lerwick | 1978-08-02 23:30 | 10.3 | 4.2 | 20 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 158448.3889 | 9.2841 | 1 |  |  | 1 | 19 | 0 | 0
Lerwick | 1978-08-03 00:30 | 10.2 | 4.4 | 17.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 157907.6481 | 9.2524 | 1 |  |  | 1 | 20 | 0 | 0
Lerwick | 1978-08-03 01:30 | 10.1 | 4.5 | 10 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 157503.2037 | 9.2287 | 1 |  |  | 1 | 21 | 0 | 0
Lerwick | 1978-08-03 02:30 | 10 | 4.5 | 5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 157235.0556 | 9.213 | 1 |  |  | 1 | 22 | 0 | 0
Lerwick | 1978-08-03 03:30 | 10.7 | 5.1 | 10 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 157123.2037 | 9.2064 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-03 04:30 | 11.6 | 6.4 | 17.5 | 760 | 550 | 230 | 0 | 230 | 115 | 0 | 157238.2037 | 9.2132 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-03 05:30 | 11.6 | 7.6 | 20 | 1840 | 1300 | 980 | 0 | 980 | 490 | 0 | 157728.2037 | 9.2419 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-03 06:30 | 11.7 | 8.2 | 20 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 158373.2037 | 9.2797 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-03 07:30 | 12.3 | 8.3 | 22.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 159018.2037 | 9.3175 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-03 08:30 | 13.1 | 7.8 | 27.5 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 159663.2037 | 9.3553 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-03 09:30 | 13.1 | 7.3 | 30 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 160308.2037 | 9.3931 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-03 10:30 | 12.8 | 6.9 | 30 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 160798.2037 | 9.4218 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-03 11:30 | 13.1 | 6.4 | 32.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 161108.2037 | 9.4399 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-03 12:30 | 13.3 | 5.9 | 37.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 161263.2037 | 9.449 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-03 13:30 | 13.1 | 5.1 | 40 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 161313.2037 | 9.4519 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-08-03 14:30 | 12.7 | 4.2 | 40 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 161065.0556 | 9.4374 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-08-03 15:30 | 12.8 | 3.8 | 37.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 160439.1296 | 9.4007 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-08-03 16:30 | 12.8 | 3.1 | 30 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 159728.0185 | 9.3591 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-08-03 17:30 | 12.3 | 2.4 | 15 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 159016.9074 | 9.3174 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-08-03 18:30 | 12.2 | 1.4 | 180 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 158305.7963 | 9.2757 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-08-03 19:30 | 12.4 | 0.6 | 327.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 157594.6852 | 9.2341 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-08-03 20:30 | 12.3 | 0.7 | 270 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 156883.5741 | 9.1924 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-08-03 21:30 | 12 | 1.4 | 225 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 156172.463 | 9.1507 | 0 |  |  | 1 | 9 | 1 | 6
Lerwick | 1978-08-03 22:30 | 11.8 | 2.2 | 195 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 155461.3519 | 9.1091 | 0 |  |  | 1 | 10 | 1 | 7
Lerwick | 1978-08-03 23:30 | 11.6 | 3 | 180 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 154750.2407 | 9.0674 | 0 |  |  | 1 | 11 | 1 | 8
Lerwick | 1978-08-04 00:30 | 11.3 | 3.4 | 182.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 154039.1296 | 9.0257 | 0 |  |  | 1 | 12 | 1 | 9
Lerwick | 1978-08-04 01:30 | 11.3 | 3.7 | 187.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 153328.0185 | 8.9841 | 0 |  |  | 1 | 13 | 1 | 10
Lerwick | 1978-08-04 02:30 | 11.1 | 3.9 | 190 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 152616.9074 | 8.9424 | 0 |  |  | 1 | 14 | 1 | 11
Lerwick | 1978-08-04 03:30 | 11 | 3.9 | 187.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 151905.7963 | 8.9007 | 0 |  |  | 1 | 15 | 1 | 12
Lerwick | 1978-08-04 04:30 | 11 | 4.2 | 185 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 151279.8704 | 8.8641 | 1 |  |  | 1 | 16 | 0 | 0
Lerwick | 1978-08-04 05:30 | 10.9 | 4 | 182.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 150739.1296 | 8.8324 | 1 |  |  | 1 | 17 | 0 | 0
Lerwick | 1978-08-04 06:30 | 10.9 | 3.3 | 175 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 150113.2037 | 8.7957 | 1 |  |  | 1 | 18 | 0 | 0
Lerwick | 1978-08-04 07:30 | 11 | 3.1 | 170 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 149402.0926 | 8.754 | 0 |  |  | 1 | 19 | 1 | 1
Lerwick | 1978-08-04 08:30 | 11.2 | 3.1 | 167.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 148690.9815 | 8.7124 | 0 |  |  | 1 | 20 | 1 | 2
Lerwick | 1978-08-04 09:30 | 11.6 | 3.2 | 162.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 147979.8704 | 8.6707 | 0 |  |  | 1 | 21 | 1 | 3
Lerwick | 1978-08-04 10:30 | 12 | 3.3 | 155 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 147268.7593 | 8.629 | 0 |  |  | 1 | 22 | 1 | 4
Lerwick | 1978-08-04 11:30 | 12.8 | 3.2 | 150 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 146557.6481 | 8.5874 | 0 |  |  | 1 | 23 | 1 | 5
Lerwick | 1978-08-04 12:30 | 13.5 | 2.9 | 155 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 145846.537 | 8.5457 | 0 |  |  | 1 | 24 | 1 | 6
Lerwick | 1978-08-04 13:30 | 13.5 | 2.4 | 157.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 145135.4259 | 8.504 | 0 |  |  | 1 | 25 | 1 | 7
Lerwick | 1978-08-04 14:30 | 13.3 | 2 | 157.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 144424.3148 | 8.4624 | 0 |  |  | 1 | 26 | 1 | 8
Lerwick | 1978-08-04 15:30 | 13 | 1.5 | 160 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 143713.2037 | 8.4207 | 0 |  |  | 1 | 27 | 1 | 9
Lerwick | 1978-08-04 16:30 | 13.1 | 1.1 | 160 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 143002.0926 | 8.379 | 0 |  |  | 1 | 28 | 1 | 10
Lerwick | 1978-08-04 17:30 | 13.2 | 1 | 157.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 142290.9815 | 8.3374 | 0 |  |  | 1 | 29 | 1 | 11
Lerwick | 1978-08-04 18:30 | 12.8 | 1 | 147.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 141579.8704 | 8.2957 | 0 |  |  | 1 | 30 | 1 | 12
Lerwick | 1978-08-04 19:30 | 12.6 | 1.2 | 145 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 140868.7593 | 8.254 | 0 |  |  | 1 | 31 | 1 | 13
Lerwick | 1978-08-04 20:30 | 12.5 | 1.8 | 155 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 140157.6481 | 8.2124 | 0 |  |  | 1 | 32 | 1 | 14
Lerwick | 1978-08-04 21:30 | 12.2 | 2.4 | 165 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 139446.537 | 8.1707 | 0 |  |  | 1 | 33 | 1 | 15
Lerwick | 1978-08-04 22:30 | 12 | 2.4 | 180 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 138735.4259 | 8.129 | 0 |  |  | 1 | 34 | 1 | 16
Lerwick | 1978-08-04 23:30 | 11.9 | 1.8 | 195 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 138024.3148 | 8.0874 | 0 |  |  | 1 | 35 | 1 | 17
Lerwick | 1978-08-05 00:30 | 11.7 | 1.5 | 187.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 137313.2037 | 8.0457 | 0 |  |  | 1 | 36 | 1 | 18
Lerwick | 1978-08-05 01:30 | 11.8 | 1.6 | 162.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 136602.0926 | 8.004 | 0 |  |  | 1 | 37 | 1 | 19
Lerwick | 1978-08-05 02:30 | 11.5 | 1.9 | 157.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 135890.9815 | 7.9624 | 0 |  |  | 1 | 38 | 1 | 20
Lerwick | 1978-08-05 03:30 | 11.5 | 1.9 | 172.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 135179.8704 | 7.9207 | 0 |  |  | 1 | 39 | 1 | 21
Lerwick | 1978-08-05 04:30 | 11.9 | 1.5 | 170 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 134468.7593 | 7.879 | 0 |  |  | 1 | 40 | 1 | 22
Lerwick | 1978-08-05 05:30 | 11.9 | 1.1 | 145 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 133757.6481 | 7.8374 | 0 |  |  | 1 | 41 | 1 | 23
Lerwick | 1978-08-05 06:30 | 11.9 | 1 | 132.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 133046.537 | 7.7957 | 0 |  |  | 1 | 42 | 1 | 24
Lerwick | 1978-08-05 07:30 | 12 | 1 | 147.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 132335.4259 | 7.754 | 0 |  |  | 1 | 43 | 1 | 25
Lerwick | 1978-08-05 08:30 | 12.2 | 1.1 | 162.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 131624.3148 | 7.7124 | 0 |  |  | 1 | 44 | 1 | 26
Lerwick | 1978-08-05 09:30 | 12.4 | 1.5 | 155 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 130913.2037 | 7.6707 | 0 |  |  | 1 | 45 | 1 | 27
Lerwick | 1978-08-05 10:30 | 13.2 | 2.2 | 142.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 130202.0926 | 7.629 | 0 |  |  | 1 | 46 | 1 | 28
Lerwick | 1978-08-05 11:30 | 14.6 | 2.6 | 140 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 129490.9815 | 7.5874 | 0 |  |  | 1 | 47 | 1 | 29
Lerwick | 1978-08-05 12:30 | 15.2 | 2.9 | 137.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 128779.8704 | 7.5457 | 0 |  |  | 1 | 48 | 1 | 30
Lerwick | 1978-08-05 13:30 | 15.2 | 3.3 | 137.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 128068.7593 | 7.504 | 0 |  |  | 1 | 49 | 1 | 31
Lerwick | 1978-08-05 14:30 | 15.1 | 3.4 | 142.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 127357.6481 | 7.4624 | 0 |  |  | 1 | 50 | 1 | 32
Lerwick | 1978-08-05 15:30 | 14.4 | 3 | 147.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 126646.537 | 7.4207 | 0 |  |  | 1 | 51 | 1 | 33
Lerwick | 1978-08-05 16:30 | 13.8 | 2.4 | 155 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 125935.4259 | 7.379 | 0 |  |  | 1 | 52 | 1 | 34
Lerwick | 1978-08-05 17:30 | 13.7 | 1.8 | 160 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 125224.3148 | 7.3374 | 0 |  |  | 1 | 53 | 1 | 35
Lerwick | 1978-08-05 18:30 | 13.4 | 1.2 | 157.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 124513.2037 | 7.2957 | 0 |  |  | 1 | 54 | 1 | 36
Lerwick | 1978-08-05 19:30 | 12.9 | 0.7 | 117.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 123802.0926 | 7.254 | 0 |  |  | 1 | 55 | 1 | 37
Lerwick | 1978-08-05 20:30 | 12.6 | 1.3 | 55 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 123090.9815 | 7.2124 | 0 |  |  | 1 | 56 | 1 | 38
Lerwick | 1978-08-05 21:30 | 12.5 | 3 | 45 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 122379.8704 | 7.1707 | 0 |  |  | 1 | 57 | 1 | 39
Lerwick | 1978-08-05 22:30 | 12.4 | 3.6 | 57.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 121668.7593 | 7.129 | 0 |  |  | 1 | 58 | 1 | 40
Lerwick | 1978-08-05 23:30 | 12 | 3.3 | 47.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 120957.6481 | 7.0874 | 0 |  |  | 1 | 59 | 1 | 41
Lerwick | 1978-08-06 00:30 | 11.8 | 3.6 | 35 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 120246.537 | 7.0457 | 0 |  |  | 1 | 60 | 1 | 42
Lerwick | 1978-08-06 01:30 | 11.4 | 3.7 | 32.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 119535.4259 | 7.004 | 0 |  |  | 1 | 61 | 1 | 43
Lerwick | 1978-08-06 02:30 | 10.8 | 3.1 | 37.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 118824.3148 | 6.9624 | 0 |  |  | 1 | 62 | 1 | 44
Lerwick | 1978-08-06 03:30 | 10.5 | 2.7 | 40 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 118113.2037 | 6.9207 | 0 |  |  | 1 | 63 | 1 | 45
Lerwick | 1978-08-06 04:30 | 10.5 | 3 | 40 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 117402.0926 | 6.879 | 0 |  |  | 1 | 64 | 1 | 46
Lerwick | 1978-08-06 05:30 | 10.3 | 3.4 | 37.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 116690.9815 | 6.8374 | 0 |  |  | 1 | 65 | 1 | 47
Lerwick | 1978-08-06 06:30 | 10.2 | 3.6 | 32.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 115979.8704 | 6.7957 | 0 |  |  | 1 | 66 | 1 | 48
Lerwick | 1978-08-06 07:30 | 10.4 | 3.1 | 35 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 115268.7593 | 6.754 | 0 |  |  | 1 | 67 | 1 | 49
Lerwick | 1978-08-06 08:30 | 10.5 | 2.2 | 42.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 114557.6481 | 6.7124 | 0 |  |  | 1 | 68 | 1 | 50
Lerwick | 1978-08-06 09:30 | 10.9 | 1.9 | 197.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 113846.537 | 6.6707 | 0 |  |  | 1 | 69 | 1 | 51
Lerwick | 1978-08-06 10:30 | 11.1 | 2.4 | 327.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 113135.4259 | 6.629 | 0 |  |  | 1 | 70 | 1 | 52
Lerwick | 1978-08-06 11:30 | 11.7 | 3 | 310 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 112424.3148 | 6.5874 | 0 |  |  | 1 | 71 | 1 | 53
Lerwick | 1978-08-06 12:30 | 12.7 | 3.6 | 317.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 111713.2037 | 6.5457 | 0 |  |  | 1 | 72 | 1 | 54
Lerwick | 1978-08-06 13:30 | 12.5 | 3.9 | 320 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 111002.0926 | 6.504 | 0 |  |  | 1 | 73 | 1 | 55
Lerwick | 1978-08-06 14:30 | 12.2 | 4 | 322.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 110376.1667 | 6.4674 | 1 |  |  | 1 | 74 | 0 | 0
Lerwick | 1978-08-06 15:30 | 12.5 | 3.9 | 327.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 109750.2407 | 6.4307 | 1 |  |  | 1 | 75 | 0 | 0
Lerwick | 1978-08-06 16:30 | 12.1 | 3.7 | 330 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 109039.1296 | 6.389 | 0 |  |  | 1 | 76 | 1 | 1
Lerwick | 1978-08-06 17:30 | 11.6 | 3.8 | 330 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 108328.0185 | 6.3473 | 0 |  |  | 1 | 77 | 1 | 2
Lerwick | 1978-08-06 18:30 | 11.5 | 4 | 330 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 107702.0926 | 6.3107 | 1 |  |  | 1 | 78 | 0 | 0
Lerwick | 1978-08-06 19:30 | 11.2 | 3.5 | 332.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 107076.1667 | 6.274 | 1 |  |  | 1 | 79 | 0 | 0
Lerwick | 1978-08-06 20:30 | 10.9 | 2.9 | 337.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 106365.0556 | 6.2323 | 0 |  |  | 1 | 80 | 1 | 1
Lerwick | 1978-08-06 21:30 | 10.8 | 2.7 | 337.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 105653.9444 | 6.1907 | 0 |  |  | 1 | 81 | 1 | 2
Lerwick | 1978-08-06 22:30 | 10.6 | 2.6 | 332.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 104942.8333 | 6.149 | 0 |  |  | 1 | 82 | 1 | 3
Lerwick | 1978-08-06 23:30 | 10.4 | 2.3 | 340 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 104231.7222 | 6.1073 | 0 |  |  | 1 | 83 | 1 | 4
Lerwick | 1978-08-07 00:30 | 10.2 | 1.8 | 177.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 103520.6111 | 6.0657 | 0 |  |  | 1 | 84 | 1 | 5
Lerwick | 1978-08-07 01:30 | 9.9 | 1.4 | 10 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 102809.5 | 6.024 | 0 |  |  | 1 | 85 | 1 | 6
Lerwick | 1978-08-07 02:30 | 9.9 | 1.1 | 22.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 102098.3889 | 5.9823 | 0 |  |  | 1 | 86 | 1 | 7
Lerwick | 1978-08-07 03:30 | 10 | 1.1 | 32.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 101387.2778 | 5.9407 | 0 |  |  | 1 | 87 | 1 | 8
Lerwick | 1978-08-07 04:30 | 10.1 | 1.4 | 37.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 100676.1667 | 5.899 | 0 |  |  | 1 | 88 | 1 | 9
Lerwick | 1978-08-07 05:30 | 10.1 | 1.6 | 40 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 99965.0556 | 5.8573 | 0 |  |  | 1 | 89 | 1 | 10
Lerwick | 1978-08-07 06:30 | 10.2 | 2.2 | 40 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 99253.9444 | 5.8157 | 0 |  |  | 1 | 90 | 1 | 11
Lerwick | 1978-08-07 07:30 | 10.3 | 2.9 | 40 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 98542.8333 | 5.774 | 0 |  |  | 1 | 91 | 1 | 12
Lerwick | 1978-08-07 08:30 | 10.4 | 3.3 | 42.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 97831.7222 | 5.7323 | 0 |  |  | 1 | 92 | 1 | 13
Lerwick | 1978-08-07 09:30 | 10.8 | 3.3 | 45 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 97120.6111 | 5.6907 | 0 |  |  | 1 | 93 | 1 | 14
Lerwick | 1978-08-07 10:30 | 11.4 | 3.6 | 42.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 96409.5 | 5.649 | 0 |  |  | 1 | 94 | 1 | 15
Lerwick | 1978-08-07 11:30 | 12.1 | 3.9 | 40 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 95698.3889 | 5.6073 | 0 |  |  | 1 | 95 | 1 | 16
Lerwick | 1978-08-07 12:30 | 12.2 | 4.5 | 37.5 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 95208.7593 | 5.5786 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-07 13:30 | 12.2 | 5.7 | 32.5 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 95223.5926 | 5.5795 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-07 14:30 | 12.2 | 6.7 | 30 | 1120 | 810 | 490 | 0 | 490 | 245 | 0 | 95468.5926 | 5.5939 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-07 15:30 | 11.7 | 7.1 | 30 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 95958.5926 | 5.6226 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-07 16:30 | 11.4 | 6.9 | 30 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 96448.5926 | 5.6513 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-07 17:30 | 11.4 | 6.5 | 30 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 96848.5926 | 5.6747 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-07 18:30 | 11.5 | 6.5 | 30 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 97248.5926 | 5.6982 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-07 19:30 | 11.4 | 6.7 | 30 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 97648.5926 | 5.7216 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-07 20:30 | 11.1 | 6.5 | 30 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 98048.5926 | 5.745 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-07 21:30 | 10.9 | 6.3 | 30 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 98358.5926 | 5.7632 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-07 22:30 | 10.8 | 6 | 30 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 98578.5926 | 5.7761 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-07 23:30 | 10.7 | 5.9 | 30 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 98733.5926 | 5.7852 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-08 00:30 | 10.6 | 6.3 | 30 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 98888.5926 | 5.7943 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-08 01:30 | 10.7 | 7.1 | 30 | 1480 | 1120 | 800 | 0 | 800 | 400 | 0 | 99288.5926 | 5.8177 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-08 02:30 | 10.8 | 7.2 | 27.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 99868.5926 | 5.8517 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-08 03:30 | 10.7 | 6.4 | 22.5 | 760 | 1120 | 800 | 0 | 800 | 400 | 0 | 100268.5926 | 5.8751 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-08 04:30 | 10.6 | 5.6 | 17.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 100423.5926 | 5.8842 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-08 05:30 | 10.6 | 5.2 | 12.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 100473.5926 | 5.8871 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-08 06:30 | 10.7 | 5 | 12.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 100483.5926 | 5.8877 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-08 07:30 | 11.1 | 5.3 | 17.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 100493.5926 | 5.8883 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-08 08:30 | 11.9 | 6 | 22.5 | 760 | 550 | 230 | 0 | 230 | 115 | 0 | 100608.5926 | 5.895 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-08 09:30 | 12.7 | 6.7 | 30 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 100918.5926 | 5.9132 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-08 10:30 | 12.8 | 7.1 | 37.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 101408.5926 | 5.9419 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-08 11:30 | 12.7 | 7.3 | 37.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 101988.5926 | 5.9759 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-08 12:30 | 12.8 | 7.3 | 35 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 102568.5926 | 6.0099 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-08 13:30 | 12.9 | 6.8 | 35 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 103058.5926 | 6.0386 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-08 14:30 | 12.9 | 6.4 | 32.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 103368.5926 | 6.0568 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-08 15:30 | 12.6 | 6.4 | 30 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 103588.5926 | 6.0696 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-08 16:30 | 12.1 | 6.4 | 27.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 103808.5926 | 6.0825 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-08 17:30 | 11.9 | 6.5 | 25 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 104118.5926 | 6.1007 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-08 18:30 | 11.7 | 6.7 | 27.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 104518.5926 | 6.1241 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-08 19:30 | 11.2 | 6.5 | 30 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 104918.5926 | 6.1476 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-08 20:30 | 10.9 | 6.4 | 27.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 105228.5926 | 6.1657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-08 21:30 | 10.9 | 6.4 | 22.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 105448.5926 | 6.1786 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-08 22:30 | 10.6 | 6.1 | 20 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 105668.5926 | 6.1915 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-08 23:30 | 10.3 | 6 | 20 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 105888.5926 | 6.2044 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-09 00:30 | 10.2 | 6.3 | 20 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 106108.5926 | 6.2173 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-09 01:30 | 10 | 6.3 | 17.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 106328.5926 | 6.2302 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-09 02:30 | 9.9 | 6.2 | 17.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 106548.5926 | 6.2431 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-09 03:30 | 9.8 | 6.2 | 22.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 106768.5926 | 6.256 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-09 04:30 | 9.7 | 6.2 | 25 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 106988.5926 | 6.2689 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-09 05:30 | 9.6 | 6 | 27.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 107208.5926 | 6.2818 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-09 06:30 | 9.6 | 5.9 | 30 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 107363.5926 | 6.2908 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-09 07:30 | 10 | 5.9 | 30 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 107453.5926 | 6.2961 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-09 08:30 | 10.4 | 6.3 | 30 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 107608.5926 | 6.3052 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-09 09:30 | 10.4 | 6.9 | 30 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 107918.5926 | 6.3234 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-09 10:30 | 11 | 6.9 | 27.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 108318.5926 | 6.3468 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-09 11:30 | 11.5 | 6.9 | 22.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 108718.5926 | 6.3702 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-09 12:30 | 11.6 | 7.3 | 20 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 109208.5926 | 6.3989 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-09 13:30 | 11.7 | 7.2 | 20 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 109788.5926 | 6.4329 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-09 14:30 | 11.9 | 6.7 | 20 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 110278.5926 | 6.4616 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-09 15:30 | 11.9 | 6.1 | 20 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 110588.5926 | 6.4798 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-09 16:30 | 11.7 | 5.8 | 20 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 110743.5926 | 6.4889 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-09 17:30 | 11.5 | 5.5 | 17.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 110833.5926 | 6.4942 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-09 18:30 | 11.6 | 5.2 | 15 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 110883.5926 | 6.4971 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-09 19:30 | 11.2 | 5 | 15 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 110893.5926 | 6.4977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-09 20:30 | 10.7 | 5 | 10 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 110903.5926 | 6.4983 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-08-09 21:30 | 10.4 | 4.7 | 2.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 110791.7407 | 6.4917 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-08-09 22:30 | 10.1 | 4 | 0 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 110387.2963 | 6.468 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-08-09 23:30 | 9.9 | 3.3 | 0 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 109761.3704 | 6.4313 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-08-10 00:30 | 9.7 | 2.8 | 175 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 109050.2593 | 6.3897 | 0 |  |  | 1 | 5 | 1 | 1
Lerwick | 1978-08-10 01:30 | 9.5 | 2.6 | 345 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 108339.1481 | 6.348 | 0 |  |  | 1 | 6 | 1 | 2
Lerwick | 1978-08-10 02:30 | 9.5 | 3.1 | 340 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 107628.037 | 6.3063 | 0 |  |  | 1 | 7 | 1 | 3
Lerwick | 1978-08-10 03:30 | 9.5 | 3.4 | 342.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 106916.9259 | 6.2647 | 0 |  |  | 1 | 8 | 1 | 4
Lerwick | 1978-08-10 04:30 | 9.5 | 3.2 | 347.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 106205.8148 | 6.223 | 0 |  |  | 1 | 9 | 1 | 5
Lerwick | 1978-08-10 05:30 | 9.5 | 3.1 | 347.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 105494.7037 | 6.1813 | 0 |  |  | 1 | 10 | 1 | 6
Lerwick | 1978-08-10 06:30 | 9.4 | 3.2 | 340 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 104783.5926 | 6.1397 | 0 |  |  | 1 | 11 | 1 | 7
Lerwick | 1978-08-10 07:30 | 9.5 | 3.6 | 330 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 104072.4815 | 6.098 | 0 |  |  | 1 | 12 | 1 | 8
Lerwick | 1978-08-10 08:30 | 9.7 | 4.2 | 325 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 103446.5556 | 6.0613 | 1 |  |  | 1 | 13 | 0 | 0
Lerwick | 1978-08-10 09:30 | 10 | 4.4 | 327.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 102905.8148 | 6.0296 | 1 |  |  | 1 | 14 | 0 | 0
Lerwick | 1978-08-10 10:30 | 10.2 | 4.2 | 332.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 102365.0741 | 5.998 | 1 |  |  | 1 | 15 | 0 | 0
Lerwick | 1978-08-10 11:30 | 10.4 | 4 | 170 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 101824.3333 | 5.9663 | 1 |  |  | 1 | 16 | 0 | 0
Lerwick | 1978-08-10 12:30 | 10.6 | 4 | 17.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 101283.5926 | 5.9346 | 1 |  |  | 1 | 17 | 0 | 0
Lerwick | 1978-08-10 13:30 | 10.6 | 4 | 27.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 100742.8519 | 5.9029 | 1 |  |  | 1 | 18 | 0 | 0
Lerwick | 1978-08-10 14:30 | 10.7 | 4 | 187.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 100202.1111 | 5.8712 | 1 |  |  | 1 | 19 | 0 | 0
Lerwick | 1978-08-10 15:30 | 10.8 | 4.2 | 345 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 99661.3704 | 5.8395 | 1 |  |  | 1 | 20 | 0 | 0
Lerwick | 1978-08-10 16:30 | 11.1 | 4.6 | 345 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 99256.9259 | 5.8158 | 1 |  |  | 1 | 21 | 0 | 0
Lerwick | 1978-08-10 17:30 | 11.2 | 4.9 | 342.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 98988.7778 | 5.8001 | 1 |  |  | 1 | 22 | 0 | 0
Lerwick | 1978-08-10 18:30 | 11.1 | 4.7 | 330 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 98720.6296 | 5.7844 | 1 |  |  | 1 | 23 | 0 | 0
Lerwick | 1978-08-10 19:30 | 10.8 | 4 | 322.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 98316.1852 | 5.7607 | 1 |  |  | 1 | 24 | 0 | 0
Lerwick | 1978-08-10 20:30 | 10.1 | 3.6 | 320 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 97690.2593 | 5.724 | 1 |  |  | 1 | 25 | 0 | 0
Lerwick | 1978-08-10 21:30 | 10 | 4 | 317.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 97064.3333 | 5.6874 | 1 |  |  | 1 | 26 | 0 | 0
Lerwick | 1978-08-10 22:30 | 10 | 4.9 | 312.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 96659.8889 | 5.6637 | 1 |  |  | 1 | 27 | 0 | 0
Lerwick | 1978-08-10 23:30 | 10 | 5.4 | 310 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 96548.037 | 5.6571 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-11 00:30 | 10.1 | 5.1 | 312.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 96558.037 | 5.6577 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-08-11 01:30 | 10.1 | 4.7 | 320 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 96446.1852 | 5.6511 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-08-11 02:30 | 10.1 | 4.7 | 330 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 96178.037 | 5.6354 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-08-11 03:30 | 10.1 | 4.7 | 337.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 95909.8889 | 5.6197 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-08-11 04:30 | 10.2 | 4.5 | 342.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 95641.7407 | 5.604 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-08-11 05:30 | 10.3 | 4.9 | 172.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 95373.5926 | 5.5883 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-08-11 06:30 | 10.4 | 5.2 | 2.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 95261.7407 | 5.5817 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-08-11 07:30 | 10.7 | 4.7 | 7.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 95149.8889 | 5.5752 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-08-11 08:30 | 11.2 | 4.7 | 17.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 94881.7407 | 5.5595 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-08-11 09:30 | 11.3 | 4.9 | 27.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 94613.5926 | 5.5438 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-08-11 10:30 | 11.5 | 5 | 30 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 94501.7407 | 5.5372 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-11 11:30 | 11.9 | 5 | 30 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 94511.7407 | 5.5378 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-08-11 12:30 | 12.3 | 4.7 | 30 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 94399.8889 | 5.5312 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-08-11 13:30 | 12.2 | 4.5 | 30 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 94131.7407 | 5.5155 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-08-11 14:30 | 12.3 | 4.7 | 30 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 93863.5926 | 5.4998 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-08-11 15:30 | 12.3 | 5.2 | 32.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 93751.7407 | 5.4933 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-11 16:30 | 11.7 | 5.5 | 37.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 93801.7407 | 5.4962 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-11 17:30 | 11.4 | 5.7 | 37.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 93891.7407 | 5.5015 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-11 18:30 | 11 | 5.3 | 32.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 93941.7407 | 5.5044 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-08-11 19:30 | 10.4 | 4.9 | 27.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 93829.8889 | 5.4978 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-08-11 20:30 | 9.8 | 4.7 | 25 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 93561.7407 | 5.4821 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-08-11 21:30 | 9.3 | 4.2 | 25 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 93157.2963 | 5.4584 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-08-11 22:30 | 9.2 | 3.6 | 30 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 92531.3704 | 5.4218 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-08-11 23:30 | 9.2 | 3 | 45 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 91820.2593 | 5.3801 | 0 |  |  | 1 | 6 | 1 | 1
Lerwick | 1978-08-12 00:30 | 9.4 | 2.6 | 52.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 91109.1481 | 5.3384 | 0 |  |  | 1 | 7 | 1 | 2
Lerwick | 1978-08-12 01:30 | 9.8 | 2.6 | 40 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 90398.037 | 5.2968 | 0 |  |  | 1 | 8 | 1 | 3
Lerwick | 1978-08-12 02:30 | 9.6 | 2.4 | 25 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 89686.9259 | 5.2551 | 0 |  |  | 1 | 9 | 1 | 4
Lerwick | 1978-08-12 03:30 | 9.2 | 1.8 | 20 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 88975.8148 | 5.2134 | 0 |  |  | 1 | 10 | 1 | 5
Lerwick | 1978-08-12 04:30 | 9.2 | 1.5 | 27.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 88264.7037 | 5.1718 | 0 |  |  | 1 | 11 | 1 | 6
Lerwick | 1978-08-12 05:30 | 9.5 | 1.8 | 45 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 87553.5926 | 5.1301 | 0 |  |  | 1 | 12 | 1 | 7
Lerwick | 1978-08-12 06:30 | 9.8 | 2.4 | 55 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 86842.4815 | 5.0884 | 0 |  |  | 1 | 13 | 1 | 8
Lerwick | 1978-08-12 07:30 | 10.1 | 2.7 | 55 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 86131.3704 | 5.0468 | 0 |  |  | 1 | 14 | 1 | 9
Lerwick | 1978-08-12 08:30 | 10.5 | 3 | 57.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 85420.2593 | 5.0051 | 0 |  |  | 1 | 15 | 1 | 10
Lerwick | 1978-08-12 09:30 | 10.9 | 3.2 | 65 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 84709.1481 | 4.9634 | 0 |  |  | 1 | 16 | 1 | 11
Lerwick | 1978-08-12 10:30 | 11.2 | 2.9 | 77.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 83998.037 | 4.9218 | 0 |  |  | 1 | 17 | 1 | 12
Lerwick | 1978-08-12 11:30 | 11.3 | 2.6 | 95 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 83286.9259 | 4.8801 | 0 |  |  | 1 | 18 | 1 | 13
Lerwick | 1978-08-12 12:30 | 11.6 | 2 | 112.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 82575.8148 | 4.8384 | 0 |  |  | 1 | 19 | 1 | 14
Lerwick | 1978-08-12 13:30 | 11.9 | 1.4 | 135 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 81864.7037 | 4.7968 | 0 |  |  | 1 | 20 | 1 | 15
Lerwick | 1978-08-12 14:30 | 11.9 | 1.7 | 135 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 81153.5926 | 4.7551 | 0 |  |  | 1 | 21 | 1 | 16
Lerwick | 1978-08-12 15:30 | 12 | 2.4 | 97.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 80442.4815 | 4.7134 | 0 |  |  | 1 | 22 | 1 | 17
Lerwick | 1978-08-12 16:30 | 12.1 | 2.4 | 87.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 79731.3704 | 4.6718 | 0 |  |  | 1 | 23 | 1 | 18
Lerwick | 1978-08-12 17:30 | 12 | 2.1 | 105 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 79020.2593 | 4.6301 | 0 |  |  | 1 | 24 | 1 | 19
Lerwick | 1978-08-12 18:30 | 11.8 | 1.9 | 97.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 78309.1481 | 4.5884 | 0 |  |  | 1 | 25 | 1 | 20
Lerwick | 1978-08-12 19:30 | 11.4 | 1.6 | 67.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 77598.037 | 4.5468 | 0 |  |  | 1 | 26 | 1 | 21
Lerwick | 1978-08-12 20:30 | 10.9 | 1.2 | 42.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 76886.9259 | 4.5051 | 0 |  |  | 1 | 27 | 1 | 22
Lerwick | 1978-08-12 21:30 | 10.2 | 1 | 20 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 76175.8148 | 4.4634 | 0 |  |  | 1 | 28 | 1 | 23
Lerwick | 1978-08-12 22:30 | 9.7 | 1 | 170 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 75464.7037 | 4.4218 | 0 |  |  | 1 | 29 | 1 | 24
Lerwick | 1978-08-12 23:30 | 9.4 | 1 | 170 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 74753.5926 | 4.3801 | 0 |  |  | 1 | 30 | 1 | 25
Lerwick | 1978-08-13 00:30 | 9.7 | 1 | 25 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 74042.4815 | 4.3384 | 0 |  |  | 1 | 31 | 1 | 26
Lerwick | 1978-08-13 01:30 | 10 | 1 | 55 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 73331.3704 | 4.2968 | 0 |  |  | 1 | 32 | 1 | 27
Lerwick | 1978-08-13 02:30 | 10 | 1 | 75 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 72620.2593 | 4.2551 | 0 |  |  | 1 | 33 | 1 | 28
Lerwick | 1978-08-13 03:30 | 10.1 | 1.1 | 85 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 71909.1481 | 4.2134 | 0 |  |  | 1 | 34 | 1 | 29
Lerwick | 1978-08-13 04:30 | 10.1 | 1.5 | 87.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 71198.037 | 4.1718 | 0 |  |  | 1 | 35 | 1 | 30
Lerwick | 1978-08-13 05:30 | 10.2 | 2 | 95 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 70486.9259 | 4.1301 | 0 |  |  | 1 | 36 | 1 | 31
Lerwick | 1978-08-13 06:30 | 10.4 | 2.6 | 102.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 69775.8148 | 4.0884 | 0 |  |  | 1 | 37 | 1 | 32
Lerwick | 1978-08-13 07:30 | 10.7 | 3.5 | 110 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 69064.7037 | 4.0468 | 0 |  |  | 1 | 38 | 1 | 33
Lerwick | 1978-08-13 08:30 | 11.1 | 3.9 | 120 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 68353.5926 | 4.0051 | 0 |  |  | 1 | 39 | 1 | 34
Lerwick | 1978-08-13 09:30 | 11.3 | 4 | 127.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 67727.6667 | 3.9684 | 1 |  |  | 1 | 40 | 0 | 0
Lerwick | 1978-08-13 10:30 | 11.5 | 3.9 | 132.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 67101.7407 | 3.9317 | 1 |  |  | 1 | 41 | 0 | 0
Lerwick | 1978-08-13 11:30 | 11.4 | 3.7 | 137.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 66390.6296 | 3.8901 | 0 |  |  | 1 | 42 | 1 | 1
Lerwick | 1978-08-13 12:30 | 11.3 | 3.7 | 142.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 65679.5185 | 3.8484 | 0 |  |  | 1 | 43 | 1 | 2
Lerwick | 1978-08-13 13:30 | 11.5 | 3.9 | 150 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 64968.4074 | 3.8067 | 0 |  |  | 1 | 44 | 1 | 3
Lerwick | 1978-08-13 14:30 | 12 | 3.9 | 157.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 64257.2963 | 3.7651 | 0 |  |  | 1 | 45 | 1 | 4
Lerwick | 1978-08-13 15:30 | 12.4 | 3.3 | 157.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 63546.1852 | 3.7234 | 0 |  |  | 1 | 46 | 1 | 5
Lerwick | 1978-08-13 16:30 | 12.4 | 2.4 | 150 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 62835.0741 | 3.6817 | 0 |  |  | 1 | 47 | 1 | 6
Lerwick | 1978-08-13 17:30 | 12.2 | 2.4 | 140 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 62123.963 | 3.6401 | 0 |  |  | 1 | 48 | 1 | 7
Lerwick | 1978-08-13 18:30 | 12.3 | 2.4 | 135 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 61412.8519 | 3.5984 | 0 |  |  | 1 | 49 | 1 | 8
Lerwick | 1978-08-13 19:30 | 12.2 | 2 | 137.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 60701.7407 | 3.5567 | 0 |  |  | 1 | 50 | 1 | 9
Lerwick | 1978-08-13 20:30 | 11.8 | 1.9 | 142.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 59990.6296 | 3.5151 | 0 |  |  | 1 | 51 | 1 | 10
Lerwick | 1978-08-13 21:30 | 11.5 | 2.6 | 150 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 59279.5185 | 3.4734 | 0 |  |  | 1 | 52 | 1 | 11
Lerwick | 1978-08-13 22:30 | 11.5 | 3.5 | 155 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 58568.4074 | 3.4317 | 0 |  |  | 1 | 53 | 1 | 12
Lerwick | 1978-08-13 23:30 | 11.4 | 3.7 | 150 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 57857.2963 | 3.3901 | 0 |  |  | 1 | 54 | 1 | 13
Lerwick | 1978-08-14 00:30 | 11.4 | 3.1 | 142.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 57146.1852 | 3.3484 | 0 |  |  | 1 | 55 | 1 | 14
Lerwick | 1978-08-14 01:30 | 11.5 | 2.9 | 137.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 56435.0741 | 3.3067 | 0 |  |  | 1 | 56 | 1 | 15
Lerwick | 1978-08-14 02:30 | 11.5 | 3.3 | 130 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 55723.963 | 3.2651 | 0 |  |  | 1 | 57 | 1 | 16
Lerwick | 1978-08-14 03:30 | 11.5 | 3.6 | 122.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 55012.8519 | 3.2234 | 0 |  |  | 1 | 58 | 1 | 17
Lerwick | 1978-08-14 04:30 | 11.8 | 3.6 | 122.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 54301.7407 | 3.1817 | 0 |  |  | 1 | 59 | 1 | 18
Lerwick | 1978-08-14 05:30 | 11.7 | 3.7 | 127.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 53590.6296 | 3.1401 | 0 |  |  | 1 | 60 | 1 | 19
Lerwick | 1978-08-14 06:30 | 11.9 | 4.2 | 130 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 52964.7037 | 3.1034 | 1 |  |  | 1 | 61 | 0 | 0
Lerwick | 1978-08-14 07:30 | 12.2 | 4.9 | 130 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 52560.2593 | 3.0797 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-14 08:30 | 12.8 | 5.6 | 130 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 52575.0926 | 3.0806 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-14 09:30 | 13.3 | 6 | 130 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 52730.0926 | 3.0897 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-14 10:30 | 13.1 | 6.2 | 130 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 52950.0926 | 3.1025 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-14 11:30 | 12.7 | 6.2 | 130 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 53170.0926 | 3.1154 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-14 12:30 | 12.5 | 6.2 | 130 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 53390.0926 | 3.1283 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-14 13:30 | 12.6 | 6.2 | 130 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 53610.0926 | 3.1412 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-14 14:30 | 12.5 | 6.3 | 130 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 53830.0926 | 3.1541 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-14 15:30 | 12.5 | 6.4 | 132.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 54050.0926 | 3.167 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-14 16:30 | 12.3 | 6.4 | 145 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 54270.0926 | 3.1799 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-14 17:30 | 12.2 | 6.1 | 165 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 54490.0926 | 3.1928 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-14 18:30 | 12.4 | 5.4 | 177.5 | 340 | 550 | 230 | 0 | 230 | 115 | 0 | 54605.0926 | 3.1995 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-08-14 19:30 | 12.4 | 4.4 | 182.5 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 54356.9444 | 3.185 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-08-14 20:30 | 12.2 | 3.5 | 192.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 53731.0185 | 3.1483 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-08-14 21:30 | 12.1 | 3.7 | 212.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 53019.9074 | 3.1066 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-08-14 22:30 | 12 | 4.9 | 235 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 52530.2778 | 3.0779 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-14 23:30 | 11.6 | 5.5 | 250 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 52545.1111 | 3.0788 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-15 00:30 | 11.3 | 5.7 | 257.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 52635.1111 | 3.0841 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-15 01:30 | 11 | 5 | 255 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 52685.1111 | 3.087 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-08-15 02:30 | 10.7 | 3.5 | 242.5 | 0 | 170 | 0 | 150 | 0 | 0 | 333.3333 | 52351.7778 | 3.0675 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-08-15 03:30 | 10.4 | 2.9 | 230 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 51640.6667 | 3.0258 | 0 |  |  | 1 | 3 | 1 | 1
Lerwick | 1978-08-15 04:30 | 10.5 | 3.5 | 222.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 50929.5556 | 2.9842 | 0 |  |  | 1 | 4 | 1 | 2
Lerwick | 1978-08-15 05:30 | 10.5 | 4.2 | 222.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 50303.6296 | 2.9475 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-08-15 06:30 | 10.7 | 4.2 | 220 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 49762.8889 | 2.9158 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-08-15 07:30 | 11 | 3.8 | 202.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 49136.963 | 2.8791 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-08-15 08:30 | 11.3 | 3.4 | 185 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 48425.8519 | 2.8375 | 0 |  |  | 1 | 8 | 1 | 1
Lerwick | 1978-08-15 09:30 | 11.5 | 3.2 | 175 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 47714.7407 | 2.7958 | 0 |  |  | 1 | 9 | 1 | 2
Lerwick | 1978-08-15 10:30 | 11.8 | 3.1 | 165 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 47003.6296 | 2.7541 | 0 |  |  | 1 | 10 | 1 | 3
Lerwick | 1978-08-15 11:30 | 12.2 | 2.8 | 162.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 46292.5185 | 2.7125 | 0 |  |  | 1 | 11 | 1 | 4
Lerwick | 1978-08-15 12:30 | 12.4 | 2.8 | 175 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 45581.4074 | 2.6708 | 0 |  |  | 1 | 12 | 1 | 5
Lerwick | 1978-08-15 13:30 | 12.2 | 3.3 | 197.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 44870.2963 | 2.6291 | 0 |  |  | 1 | 13 | 1 | 6
Lerwick | 1978-08-15 14:30 | 12.2 | 2.9 | 212.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 44159.1852 | 2.5875 | 0 |  |  | 1 | 14 | 1 | 7
Lerwick | 1978-08-15 15:30 | 12.6 | 2.1 | 205 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 43448.0741 | 2.5458 | 0 |  |  | 1 | 15 | 1 | 8
Lerwick | 1978-08-15 16:30 | 13 | 2.4 | 200 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 42736.963 | 2.5041 | 0 |  |  | 1 | 16 | 1 | 9
Lerwick | 1978-08-15 17:30 | 13.1 | 2.7 | 215 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 42025.8519 | 2.4625 | 0 |  |  | 1 | 17 | 1 | 10
Lerwick | 1978-08-15 18:30 | 12.6 | 2.6 | 222.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 41314.7407 | 2.4208 | 0 |  |  | 1 | 18 | 1 | 11
Lerwick | 1978-08-15 19:30 | 12.1 | 2.6 | 225 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 40603.6296 | 2.3791 | 0 |  |  | 1 | 19 | 1 | 12
Lerwick | 1978-08-15 20:30 | 11.1 | 2.2 | 227.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 39892.5185 | 2.3375 | 0 |  |  | 1 | 20 | 1 | 13
Lerwick | 1978-08-15 21:30 | 9.6 | 1.6 | 212.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 39181.4074 | 2.2958 | 0 |  |  | 1 | 21 | 1 | 14
Lerwick | 1978-08-15 22:30 | 9.1 | 1.6 | 197.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 38470.2963 | 2.2541 | 0 |  |  | 1 | 22 | 1 | 15
Lerwick | 1978-08-15 23:30 | 9.9 | 1.8 | 200 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 37759.1852 | 2.2125 | 0 |  |  | 1 | 23 | 1 | 16
Lerwick | 1978-08-16 00:30 | 10.5 | 1.6 | 202.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 37048.0741 | 2.1708 | 0 |  |  | 1 | 24 | 1 | 17
Lerwick | 1978-08-16 01:30 | 10.7 | 1.5 | 192.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 36336.963 | 2.1291 | 0 |  |  | 1 | 25 | 1 | 18
Lerwick | 1978-08-16 02:30 | 10.9 | 1.8 | 185 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 35625.8519 | 2.0875 | 0 |  |  | 1 | 26 | 1 | 19
Lerwick | 1978-08-16 03:30 | 11 | 2.4 | 190 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 34914.7407 | 2.0458 | 0 |  |  | 1 | 27 | 1 | 20
Lerwick | 1978-08-16 04:30 | 11 | 2.7 | 202.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 34203.6296 | 2.0041 | 0 |  |  | 1 | 28 | 1 | 21
Lerwick | 1978-08-16 05:30 | 11 | 2.9 | 217.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 33492.5185 | 1.9625 | 0 |  |  | 1 | 29 | 1 | 22
Lerwick | 1978-08-16 06:30 | 11.1 | 3.8 | 230 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 32781.4074 | 1.9208 | 0 |  |  | 1 | 30 | 1 | 23
Lerwick | 1978-08-16 07:30 | 11.3 | 5.1 | 237.5 | 340 | 170 | 0 | 150 | 0 | 0 | 333.3333 | 32448.0741 | 1.9013 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-16 08:30 | 11.8 | 5.7 | 240 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 32498.0741 | 1.9042 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-16 09:30 | 12.5 | 5.5 | 242.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 32588.0741 | 1.9095 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-16 10:30 | 13 | 5.2 | 250 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 32638.0741 | 1.9124 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-16 11:30 | 13.6 | 5.2 | 257.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 32648.0741 | 1.913 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-16 12:30 | 13.7 | 5.4 | 272.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 32658.0741 | 1.9136 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-16 13:30 | 13.2 | 5.1 | 300 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 32668.0741 | 1.9141 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-08-16 14:30 | 12.7 | 4.9 | 317.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 32556.2222 | 1.9076 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-08-16 15:30 | 11.9 | 5.4 | 317.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 32444.3704 | 1.901 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-16 16:30 | 10.9 | 5.6 | 310 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 32494.3704 | 1.904 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-16 17:30 | 9.5 | 4.9 | 305 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 32509.2037 | 1.9048 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-08-16 18:30 | 8.6 | 4.1 | 307.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 32104.7593 | 1.8811 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-08-16 19:30 | 8.3 | 3.5 | 307.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 31478.8333 | 1.8445 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-08-16 20:30 | 8.3 | 3.1 | 297.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 30767.7222 | 1.8028 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-08-16 21:30 | 8.7 | 3.5 | 282.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 30056.6111 | 1.7611 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-08-16 22:30 | 8.8 | 3.9 | 272.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 29345.5 | 1.7195 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-08-16 23:30 | 8.8 | 3.7 | 277.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 28634.3889 | 1.6778 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-08-17 00:30 | 9 | 3.7 | 290 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 27923.2778 | 1.6361 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-08-17 01:30 | 9.2 | 3.9 | 292.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 27212.1667 | 1.5945 | 0 |  |  | 1 | 9 | 1 | 6
Lerwick | 1978-08-17 02:30 | 9.1 | 3.5 | 290 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 26501.0556 | 1.5528 | 0 |  |  | 1 | 10 | 1 | 7
Lerwick | 1978-08-17 03:30 | 9 | 2.9 | 287.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 25789.9444 | 1.5111 | 0 |  |  | 1 | 11 | 1 | 8
Lerwick | 1978-08-17 04:30 | 8.8 | 2.7 | 282.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 25078.8333 | 1.4695 | 0 |  |  | 1 | 12 | 1 | 9
Lerwick | 1978-08-17 05:30 | 9 | 2.7 | 280 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 24367.7222 | 1.4278 | 0 |  |  | 1 | 13 | 1 | 10
Lerwick | 1978-08-17 06:30 | 9.5 | 3.1 | 280 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 23656.6111 | 1.3861 | 0 |  |  | 1 | 14 | 1 | 11
Lerwick | 1978-08-17 07:30 | 10.1 | 4 | 277.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 23030.6852 | 1.3495 | 1 |  |  | 1 | 15 | 0 | 0
Lerwick | 1978-08-17 08:30 | 10.7 | 4.6 | 270 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 22626.2407 | 1.3258 | 1 |  |  | 1 | 16 | 0 | 0
Lerwick | 1978-08-17 09:30 | 11.2 | 5.1 | 265 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 22514.3889 | 1.3192 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-17 10:30 | 11.8 | 5.5 | 265 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 22564.3889 | 1.3221 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-17 11:30 | 12.2 | 5.7 | 262.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 22654.3889 | 1.3274 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-17 12:30 | 12.6 | 5.8 | 257.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 22744.3889 | 1.3327 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-17 13:30 | 13.1 | 5.9 | 252.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 22834.3889 | 1.338 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-17 14:30 | 13.3 | 5.8 | 250 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 22924.3889 | 1.3432 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-17 15:30 | 13.6 | 5.5 | 247.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 23014.3889 | 1.3485 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-17 16:30 | 13.4 | 5.1 | 242.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 23064.3889 | 1.3514 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-08-17 17:30 | 13.1 | 4.4 | 237.5 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 22816.2407 | 1.3369 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-08-17 18:30 | 12.6 | 3.6 | 232.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 22190.3148 | 1.3002 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-08-17 19:30 | 11.6 | 3.2 | 230 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 21479.2037 | 1.2585 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-08-17 20:30 | 10.4 | 3.2 | 227.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 20768.0926 | 1.2169 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-08-17 21:30 | 9.8 | 3.2 | 217.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 20056.9815 | 1.1752 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-08-17 22:30 | 9.6 | 3.2 | 207.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 19345.8704 | 1.1335 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-08-17 23:30 | 9.6 | 3.6 | 205 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 18634.7593 | 1.0919 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-08-18 00:30 | 9.5 | 4.2 | 202.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 18008.8333 | 1.0552 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-08-18 01:30 | 10 | 4.4 | 197.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 17468.0926 | 1.0235 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-08-18 02:30 | 10.5 | 4.1 | 190 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 16927.3519 | 0.99184 | 1 |  |  | 1 | 11 | 0 | 0
Lerwick | 1978-08-18 03:30 | 10.6 | 3.9 | 182.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 16301.4259 | 0.95516 | 1 |  |  | 1 | 12 | 0 | 0
Lerwick | 1978-08-18 04:30 | 10.9 | 4.2 | 177.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 15675.5 | 0.91849 | 1 |  |  | 1 | 13 | 0 | 0
Lerwick | 1978-08-18 05:30 | 11 | 4.9 | 172.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 15271.0556 | 0.89479 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-18 06:30 | 11.2 | 5.5 | 170 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 15285.8889 | 0.89566 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-18 07:30 | 11.5 | 5.8 | 170 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 15375.8889 | 0.90093 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-18 08:30 | 12 | 6 | 167.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 15530.8889 | 0.91001 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-18 09:30 | 12.7 | 6 | 160 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 15750.8889 | 0.9229 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-18 10:30 | 13.4 | 6 | 155 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 15970.8889 | 0.93579 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-18 11:30 | 14.2 | 6.7 | 157.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 16280.8889 | 0.95396 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-18 12:30 | 14.7 | 7.6 | 160 | 1840 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 16860.8889 | 0.98794 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-18 13:30 | 14.5 | 8 | 160 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 17505.8889 | 1.0257 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-18 14:30 | 14.5 | 7.6 | 160 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 18150.8889 | 1.0635 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-18 15:30 | 14.6 | 7.2 | 160 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 18795.8889 | 1.1013 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-18 16:30 | 14.2 | 7.6 | 160 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 19440.8889 | 1.1391 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-18 17:30 | 13.8 | 8.2 | 162.5 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 20085.8889 | 1.1769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-18 18:30 | 13.2 | 8.5 | 167.5 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 20730.8889 | 1.2147 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-18 19:30 | 12.6 | 8.2 | 172.5 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 21375.8889 | 1.2525 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-18 20:30 | 12.2 | 7.8 | 177.5 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 22020.8889 | 1.2903 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-18 21:30 | 12.1 | 7.7 | 180 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 22665.8889 | 1.3281 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-18 22:30 | 12.3 | 7.4 | 180 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 23310.8889 | 1.3659 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-18 23:30 | 12.3 | 7.1 | 180 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 23890.8889 | 1.3999 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-19 00:30 | 12.1 | 7 | 180 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 24470.8889 | 1.4338 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-19 01:30 | 12 | 6.7 | 180 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 24960.8889 | 1.4626 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-19 02:30 | 11.9 | 6.3 | 180 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 25270.8889 | 1.4807 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-19 03:30 | 11.8 | 6.2 | 182.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 25490.8889 | 1.4936 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-19 04:30 | 11.7 | 6.2 | 187.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 25710.8889 | 1.5065 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-19 05:30 | 11.7 | 6 | 187.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 25930.8889 | 1.5194 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-19 06:30 | 11.9 | 5.9 | 180 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 26085.8889 | 1.5285 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-19 07:30 | 12.2 | 6 | 175 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 26240.8889 | 1.5376 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-19 08:30 | 12.3 | 6 | 177.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 26460.8889 | 1.5504 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-19 09:30 | 12.3 | 6.1 | 180 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 26680.8889 | 1.5633 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-19 10:30 | 12.4 | 6.7 | 180 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 26990.8889 | 1.5815 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-19 11:30 | 13.2 | 6.7 | 180 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 27390.8889 | 1.6049 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-19 12:30 | 13.5 | 6.1 | 180 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 27700.8889 | 1.6231 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-19 13:30 | 12.9 | 5.8 | 180 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 27855.8889 | 1.6322 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-19 14:30 | 13 | 5.9 | 180 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 27945.8889 | 1.6375 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-19 15:30 | 13.1 | 6.2 | 182.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 28100.8889 | 1.6465 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-19 16:30 | 13.2 | 5.9 | 187.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 28255.8889 | 1.6556 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-19 17:30 | 12.9 | 5.7 | 190 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 28345.8889 | 1.6609 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-19 18:30 | 12.5 | 5.5 | 190 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 28435.8889 | 1.6662 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-19 19:30 | 12.3 | 5.4 | 190 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 28485.8889 | 1.6691 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-19 20:30 | 12.1 | 5.4 | 187.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 28495.8889 | 1.6697 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-19 21:30 | 12 | 5.4 | 180 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 28505.8889 | 1.6703 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-19 22:30 | 11.9 | 5.2 | 175 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 28515.8889 | 1.6709 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-08-19 23:30 | 11.7 | 4.3 | 180 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 28267.7407 | 1.6563 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-08-20 00:30 | 11.5 | 3.1 | 187.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 27641.8148 | 1.6196 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-08-20 01:30 | 11.7 | 2.4 | 195 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 26930.7037 | 1.578 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-08-20 02:30 | 11.6 | 1.5 | 197.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 26219.5926 | 1.5363 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-08-20 03:30 | 11.7 | 1 | 185 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 25508.4815 | 1.4946 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-08-20 04:30 | 11.7 | 1.2 | 170 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 24797.3704 | 1.453 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-08-20 05:30 | 11.3 | 2 | 165 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 24086.2593 | 1.4113 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-08-20 06:30 | 11 | 2.6 | 167.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 23375.1481 | 1.3696 | 0 |  |  | 1 | 9 | 1 | 6
Lerwick | 1978-08-20 07:30 | 11.1 | 2.6 | 172.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 22664.037 | 1.328 | 0 |  |  | 1 | 10 | 1 | 7
Lerwick | 1978-08-20 08:30 | 11.5 | 3.1 | 175 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 21952.9259 | 1.2863 | 0 |  |  | 1 | 11 | 1 | 8
Lerwick | 1978-08-20 09:30 | 11.9 | 4 | 175 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 21327 | 1.2496 | 1 |  |  | 1 | 12 | 0 | 0
Lerwick | 1978-08-20 10:30 | 12 | 4.1 | 177.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 20786.2593 | 1.2179 | 1 |  |  | 1 | 13 | 0 | 0
Lerwick | 1978-08-20 11:30 | 12 | 3.9 | 177.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 20160.3333 | 1.1813 | 1 |  |  | 1 | 14 | 0 | 0
Lerwick | 1978-08-20 12:30 | 12.6 | 4.1 | 175 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 19534.4074 | 1.1446 | 1 |  |  | 1 | 15 | 0 | 0
Lerwick | 1978-08-20 13:30 | 13.7 | 4.6 | 177.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 19129.963 | 1.1209 | 1 |  |  | 1 | 16 | 0 | 0
Lerwick | 1978-08-20 14:30 | 14.7 | 4.7 | 175 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 18861.8148 | 1.1052 | 1 |  |  | 1 | 17 | 0 | 0
Lerwick | 1978-08-20 15:30 | 15.3 | 4.2 | 165 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 18457.3704 | 1.0815 | 1 |  |  | 1 | 18 | 0 | 0
Lerwick | 1978-08-20 16:30 | 14.9 | 3.7 | 160 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 17831.4444 | 1.0448 | 1 |  |  | 1 | 19 | 0 | 0
Lerwick | 1978-08-20 17:30 | 14 | 3.8 | 165 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 17120.3333 | 1.0031 | 0 |  |  | 1 | 20 | 1 | 1
Lerwick | 1978-08-20 18:30 | 13.1 | 4.2 | 175 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 16494.4074 | 0.96647 | 1 |  |  | 1 | 21 | 0 | 0
Lerwick | 1978-08-20 19:30 | 12.3 | 4.7 | 177.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 16089.963 | 0.94277 | 1 |  |  | 1 | 22 | 0 | 0
Lerwick | 1978-08-20 20:30 | 12.1 | 4.7 | 172.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 15821.8148 | 0.92706 | 1 |  |  | 1 | 23 | 0 | 0
Lerwick | 1978-08-20 21:30 | 12 | 4.5 | 172.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 15553.6667 | 0.91135 | 1 |  |  | 1 | 24 | 0 | 0
Lerwick | 1978-08-20 22:30 | 12 | 4.5 | 182.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 15285.5185 | 0.89564 | 1 |  |  | 1 | 25 | 0 | 0
Lerwick | 1978-08-20 23:30 | 12 | 4.5 | 197.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 15017.3704 | 0.87992 | 1 |  |  | 1 | 26 | 0 | 0
Lerwick | 1978-08-21 00:30 | 12 | 4.9 | 212.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 14749.2222 | 0.86421 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-21 01:30 | 12 | 5.5 | 220 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 14764.0556 | 0.86508 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-21 02:30 | 12 | 5.5 | 210 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 14854.0556 | 0.87035 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-21 03:30 | 12 | 5.4 | 195 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 14904.0556 | 0.87328 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-21 04:30 | 11.8 | 5.9 | 197.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 14954.0556 | 0.87621 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-21 05:30 | 11.6 | 6.5 | 215 | 1120 | 810 | 490 | 0 | 490 | 245 | 0 | 15199.0556 | 0.89057 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-21 06:30 | 11.8 | 6.5 | 230 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 15599.0556 | 0.91401 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-21 07:30 | 11.6 | 6.4 | 235 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 15909.0556 | 0.93217 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-21 08:30 | 11.4 | 6.8 | 235 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 16219.0556 | 0.95034 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-21 09:30 | 11.6 | 7.6 | 235 | 1840 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 16799.0556 | 0.98432 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-21 10:30 | 12.6 | 8 | 235 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 17444.0556 | 1.0221 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-21 11:30 | 12.9 | 8.2 | 237.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 18089.0556 | 1.0599 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-21 12:30 | 13.2 | 8.5 | 237.5 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 18734.0556 | 1.0977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-21 13:30 | 13.9 | 8.3 | 230 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 19379.0556 | 1.1355 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-21 14:30 | 13.7 | 7.8 | 222.5 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 20024.0556 | 1.1733 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-21 15:30 | 13.3 | 6.8 | 215 | 1120 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 20604.0556 | 1.2073 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-21 16:30 | 12.5 | 5.6 | 205 | 500 | 810 | 490 | 0 | 490 | 245 | 0 | 20849.0556 | 1.2216 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-21 17:30 | 11.9 | 4.5 | 200 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 20863.8889 | 1.2225 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-08-21 18:30 | 11.6 | 3.8 | 202.5 | 0 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 20374.2593 | 1.1938 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-08-21 19:30 | 11.5 | 4 | 210 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 19748.3333 | 1.1571 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-08-21 20:30 | 11.5 | 4.7 | 215 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 19343.8889 | 1.1334 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-08-21 21:30 | 11.4 | 5 | 212.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 19232.037 | 1.1269 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-21 22:30 | 11.1 | 5.6 | 212.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 19282.037 | 1.1298 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-21 23:30 | 10.5 | 6.6 | 220 | 1120 | 810 | 490 | 0 | 490 | 245 | 0 | 19527.037 | 1.1442 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-22 00:30 | 10.1 | 6.8 | 230 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 19927.037 | 1.1676 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-22 01:30 | 10.1 | 6.9 | 237.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 20327.037 | 1.191 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-22 02:30 | 10.1 | 7.4 | 240 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 20817.037 | 1.2197 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-22 03:30 | 10.2 | 7.9 | 240 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 21462.037 | 1.2575 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-22 04:30 | 10.4 | 8.5 | 240 | 2560 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 22107.037 | 1.2953 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-22 05:30 | 10.5 | 9.4 | 237.5 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 22752.037 | 1.3331 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-22 06:30 | 10.8 | 10.4 | 232.5 | 3640 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 23397.037 | 1.3709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-22 07:30 | 11 | 11.2 | 230 | 4300 | 3970 | 3650 | 0 | 1290 | 645 | 0 | 24042.037 | 1.4087 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-22 08:30 | 11.1 | 11.1 | 232.5 | 4300 | 4300 | 3980 | 0 | 1290 | 645 | 0 | 24687.037 | 1.4465 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-22 09:30 | 11.3 | 10.3 | 240 | 3640 | 3970 | 3650 | 0 | 1290 | 645 | 0 | 25332.037 | 1.4843 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-22 10:30 | 11.4 | 9.3 | 247.5 | 2920 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 25977.037 | 1.5221 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-22 11:30 | 11.7 | 8.4 | 250 | 2200 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 26622.037 | 1.5599 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-22 12:30 | 11.9 | 7.7 | 250 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 27267.037 | 1.5977 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-22 13:30 | 11.7 | 7.6 | 250 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 27912.037 | 1.6355 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-22 14:30 | 11.5 | 7.9 | 255 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 28557.037 | 1.6733 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-22 15:30 | 11.5 | 8 | 267.5 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 29202.037 | 1.7111 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-22 16:30 | 11.2 | 7.6 | 280 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 29847.037 | 1.7488 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-22 17:30 | 11.2 | 7.3 | 285 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 30492.037 | 1.7866 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-22 18:30 | 11.4 | 8.1 | 282.5 | 2200 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 31137.037 | 1.8244 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-22 19:30 | 11.1 | 8.9 | 280 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 31782.037 | 1.8622 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-22 20:30 | 10.8 | 8.5 | 280 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 32427.037 | 1.9 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-22 21:30 | 10.7 | 8 | 277.5 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 33072.037 | 1.9378 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-22 22:30 | 10.5 | 8.2 | 272.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 33717.037 | 1.9756 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-22 23:30 | 10.5 | 8.6 | 270 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 34362.037 | 2.0134 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-23 00:30 | 10.4 | 8.9 | 270 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 35007.037 | 2.0512 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-23 01:30 | 10.4 | 9.1 | 270 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 35652.037 | 2.089 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-23 02:30 | 10.4 | 9.1 | 270 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 36297.037 | 2.1268 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-23 03:30 | 10.2 | 8.9 | 270 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 36942.037 | 2.1646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-23 04:30 | 10.2 | 8.6 | 270 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 37587.037 | 2.2024 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-23 05:30 | 10.3 | 8.5 | 270 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 38232.037 | 2.2402 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-23 06:30 | 10.2 | 8.9 | 272.5 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 38877.037 | 2.278 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-23 07:30 | 10.2 | 9.8 | 275 | 3280 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 39522.037 | 2.3157 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-23 08:30 | 10.4 | 10.8 | 272.5 | 4000 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 40167.037 | 2.3535 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-23 09:30 | 10.6 | 11.5 | 270 | 4472.2222 | 4236.1111 | 3916.1111 | 0 | 1290 | 645 | 0 | 40812.037 | 2.3913 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-23 10:30 | 11.4 | 11.6 | 270 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 645 | 0 | 41457.037 | 2.4291 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-23 11:30 | 12.1 | 11.1 | 267.5 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 42102.037 | 2.4669 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-23 12:30 | 12.2 | 10.6 | 262.5 | 4000 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 42747.037 | 2.5047 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-23 13:30 | 12.3 | 10.2 | 260 | 3640 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 43392.037 | 2.5425 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-23 14:30 | 12.4 | 9.4 | 260 | 2920 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 44037.037 | 2.5803 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-23 15:30 | 11.8 | 8.4 | 260 | 2200 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 44682.037 | 2.6181 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-23 16:30 | 11.2 | 7.8 | 257.5 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 45327.037 | 2.6559 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-23 17:30 | 11.1 | 7.9 | 252.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 45972.037 | 2.6937 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-23 18:30 | 11.3 | 8.7 | 250 | 2560 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 46617.037 | 2.7315 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-23 19:30 | 11 | 9.4 | 250 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 47262.037 | 2.7693 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-23 20:30 | 10.5 | 9.5 | 250 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 47907.037 | 2.8071 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-23 21:30 | 10.5 | 9.7 | 247.5 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 48552.037 | 2.8448 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-23 22:30 | 10.4 | 10.1 | 245 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 49197.037 | 2.8826 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-23 23:30 | 10.4 | 10 | 245 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 49842.037 | 2.9204 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-24 00:30 | 10.3 | 9.5 | 245 | 3280 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 50487.037 | 2.9582 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-24 01:30 | 10 | 9.1 | 247.5 | 2920 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 51132.037 | 2.996 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-24 02:30 | 10 | 9.1 | 252.5 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 51777.037 | 3.0338 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-24 03:30 | 10.2 | 9.3 | 257.5 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 52422.037 | 3.0716 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-24 04:30 | 10.2 | 9.4 | 262.5 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 53067.037 | 3.1094 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-24 05:30 | 10 | 9.9 | 270 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 53712.037 | 3.1472 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-24 06:30 | 10 | 10.3 | 272.5 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 54357.037 | 3.185 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-24 07:30 | 10.5 | 10.3 | 265 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 55002.037 | 3.2228 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-24 08:30 | 11.2 | 10.3 | 260 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 55647.037 | 3.2606 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-24 09:30 | 11.5 | 10.5 | 260 | 4000 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 56292.037 | 3.2984 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-24 10:30 | 11.3 | 11 | 260 | 4300 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 56937.037 | 3.3362 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-24 11:30 | 11.8 | 11.3 | 260 | 4300 | 4300 | 3980 | 0 | 1290 | 645 | 0 | 57582.037 | 3.3739 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-24 12:30 | 12.2 | 11.4 | 262.5 | 4300 | 4300 | 3980 | 0 | 1290 | 645 | 0 | 58227.037 | 3.4117 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-24 13:30 | 12 | 11.7 | 270 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 58872.037 | 3.4495 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-24 14:30 | 12 | 11.7 | 277.5 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 645 | 0 | 59517.037 | 3.4873 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-24 15:30 | 11.9 | 11.1 | 280 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 60162.037 | 3.5251 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-24 16:30 | 11.7 | 10.6 | 282.5 | 4000 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 60807.037 | 3.5629 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-24 17:30 | 11.4 | 10.1 | 285 | 3640 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 61452.037 | 3.6007 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-24 18:30 | 11.4 | 9.4 | 285 | 2920 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 62097.037 | 3.6385 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-24 19:30 | 11.2 | 8.5 | 287.5 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 62742.037 | 3.6763 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-24 20:30 | 10.7 | 7.9 | 292.5 | 1840 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 63387.037 | 3.7141 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-24 21:30 | 10.4 | 7.7 | 297.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 64032.037 | 3.7519 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-24 22:30 | 10.2 | 7.6 | 300 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 64677.037 | 3.7897 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-24 23:30 | 10 | 7.1 | 300 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 65322.037 | 3.8275 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-25 00:30 | 9.9 | 6.4 | 300 | 760 | 1120 | 800 | 0 | 800 | 400 | 0 | 65722.037 | 3.8509 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-25 01:30 | 9.7 | 6.2 | 302.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 65942.037 | 3.8638 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-25 02:30 | 9.5 | 6.4 | 307.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 66162.037 | 3.8767 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-25 03:30 | 9.3 | 7.1 | 310 | 1480 | 1120 | 800 | 0 | 800 | 400 | 0 | 66562.037 | 3.9001 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-25 04:30 | 9.4 | 7.6 | 310 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 67207.037 | 3.9379 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-25 05:30 | 9.3 | 7.8 | 310 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 67852.037 | 3.9757 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-25 06:30 | 9 | 8 | 307.5 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 68497.037 | 4.0135 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-25 07:30 | 9 | 8.3 | 305 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 69142.037 | 4.0513 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-25 08:30 | 9.2 | 8.6 | 310 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 69787.037 | 4.0891 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-25 09:30 | 9.3 | 9 | 317.5 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 70432.037 | 4.1269 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-25 10:30 | 9.3 | 9.4 | 320 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 71077.037 | 4.1647 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-25 11:30 | 9.3 | 9.2 | 320 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 71722.037 | 4.2025 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-25 12:30 | 9.7 | 9 | 320 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 72367.037 | 4.2403 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-25 13:30 | 9.6 | 8.7 | 320 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 73012.037 | 4.278 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-25 14:30 | 9.9 | 8.2 | 322.5 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 73657.037 | 4.3158 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-25 15:30 | 9.9 | 8 | 325 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 74302.037 | 4.3536 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-25 16:30 | 9.1 | 8 | 322.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 74947.037 | 4.3914 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-25 17:30 | 8.8 | 7.5 | 322.5 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 75592.037 | 4.4292 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-25 18:30 | 8.5 | 6 | 327.5 | 760 | 1300 | 980 | 0 | 980 | 490 | 0 | 76082.037 | 4.4579 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-25 19:30 | 8 | 4.5 | 327.5 | 199.3333 | 479.6667 | 159.6667 | 0 | 159.6667 | 79.8333 | 0 | 76161.8704 | 4.4626 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-08-25 20:30 | 7.7 | 4.2 | 322.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 75757.4259 | 4.4389 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-08-25 21:30 | 7.9 | 4.4 | 317.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 75216.6852 | 4.4072 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-08-25 22:30 | 7.7 | 4.2 | 312.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 74675.9444 | 4.3755 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-08-25 23:30 | 7.6 | 3.9 | 310 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 74050.0185 | 4.3389 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-08-26 00:30 | 7.9 | 4.1 | 307.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 73424.0926 | 4.3022 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-08-26 01:30 | 8.1 | 4.4 | 302.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 72883.3519 | 4.2705 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-08-26 02:30 | 7.8 | 4.5 | 300 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 72478.9074 | 4.2468 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-08-26 03:30 | 7.8 | 4.2 | 297.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 72074.463 | 4.2231 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-08-26 04:30 | 8.3 | 3.9 | 292.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 71448.537 | 4.1864 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-08-26 05:30 | 8.5 | 3.9 | 287.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 70737.4259 | 4.1448 | 0 |  |  | 1 | 11 | 1 | 1
Lerwick | 1978-08-26 06:30 | 8.7 | 4.4 | 282.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 70111.5 | 4.1081 | 1 |  |  | 1 | 12 | 0 | 0
Lerwick | 1978-08-26 07:30 | 9.2 | 5.4 | 282.5 | 340 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 69863.3519 | 4.0936 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-26 08:30 | 9.9 | 6.3 | 290 | 760 | 550 | 230 | 0 | 230 | 115 | 0 | 69978.3519 | 4.1003 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-26 09:30 | 10.1 | 7.2 | 297.5 | 1480 | 1120 | 800 | 0 | 800 | 400 | 0 | 70378.3519 | 4.1237 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-26 10:30 | 10.5 | 7.9 | 300 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 71023.3519 | 4.1615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-26 11:30 | 11.3 | 8 | 300 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 71668.3519 | 4.1993 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-26 12:30 | 11.8 | 8 | 300 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 72313.3519 | 4.2371 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-26 13:30 | 11.7 | 8.4 | 305 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 72958.3519 | 4.2749 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-26 14:30 | 11.7 | 9 | 315 | 2920 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 73603.3519 | 4.3127 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-26 15:30 | 11.7 | 9.6 | 322.5 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 74248.3519 | 4.3505 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-26 16:30 | 11.2 | 10 | 327.5 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 74893.3519 | 4.3883 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-26 17:30 | 10.7 | 9.6 | 330 | 3280 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 75538.3519 | 4.4261 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-26 18:30 | 10 | 8.7 | 330 | 2560 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 76183.3519 | 4.4639 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-26 19:30 | 9.1 | 7.9 | 332.5 | 1840 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 76828.3519 | 4.5017 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-26 20:30 | 8.5 | 7.7 | 335 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 77473.3519 | 4.5395 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-26 21:30 | 8.2 | 7.7 | 332.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 78118.3519 | 4.5772 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-26 22:30 | 8.1 | 7.7 | 330 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 78763.3519 | 4.615 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-26 23:30 | 8 | 7.3 | 330 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 79408.3519 | 4.6528 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-27 00:30 | 7.9 | 6.6 | 330 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 79898.3519 | 4.6815 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-27 01:30 | 7.8 | 6.2 | 332.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 80208.3519 | 4.6997 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-27 02:30 | 7.8 | 6.2 | 337.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 80428.3519 | 4.7126 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-27 03:30 | 7.8 | 6.3 | 340 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 80648.3519 | 4.7255 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-27 04:30 | 7.8 | 6.4 | 340 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 80868.3519 | 4.7384 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-27 05:30 | 7.8 | 6.4 | 337.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 81088.3519 | 4.7513 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-27 06:30 | 7.7 | 6.5 | 335 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 81398.3519 | 4.7694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-27 07:30 | 8.2 | 6.8 | 337.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 81798.3519 | 4.7929 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-27 08:30 | 9 | 7.1 | 337.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 82288.3519 | 4.8216 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-27 09:30 | 9.6 | 7.2 | 332.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 82868.3519 | 4.8556 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-27 10:30 | 10 | 6.9 | 330 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 83358.3519 | 4.8843 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-27 11:30 | 10.4 | 6.4 | 327.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 83668.3519 | 4.9024 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-27 12:30 | 10.9 | 6.2 | 320 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 83888.3519 | 4.9153 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-27 13:30 | 10.7 | 6 | 310 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 84108.3519 | 4.9282 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-27 14:30 | 10.7 | 5.9 | 302.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 84263.3519 | 4.9373 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-27 15:30 | 10.7 | 5.9 | 302.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 84353.3519 | 4.9426 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-27 16:30 | 10.1 | 5.6 | 310 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 84443.3519 | 4.9479 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-27 17:30 | 9.5 | 5.1 | 315 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 84493.3519 | 4.9508 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-08-27 18:30 | 9.1 | 4.4 | 312.5 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 84245.2037 | 4.9362 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-08-27 19:30 | 8.6 | 3.6 | 310 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 83619.2778 | 4.8996 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-08-27 20:30 | 8.2 | 3 | 305 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 82908.1667 | 4.8579 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-08-27 21:30 | 8 | 2.6 | 292.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 82197.0556 | 4.8162 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-08-27 22:30 | 7.9 | 2.6 | 282.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 81485.9444 | 4.7746 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-08-27 23:30 | 7.9 | 2.3 | 270 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 80774.8333 | 4.7329 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-08-28 00:30 | 7.8 | 1.9 | 237.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 80063.7222 | 4.6912 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-08-28 01:30 | 7.4 | 2.2 | 197.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 79352.6111 | 4.6496 | 0 |  |  | 1 | 9 | 1 | 6
Lerwick | 1978-08-28 02:30 | 7.3 | 3.3 | 175 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 78641.5 | 4.6079 | 0 |  |  | 1 | 10 | 1 | 7
Lerwick | 1978-08-28 03:30 | 7.5 | 3.9 | 170 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 77930.3889 | 4.5662 | 0 |  |  | 1 | 11 | 1 | 8
Lerwick | 1978-08-28 04:30 | 7.8 | 3.3 | 162.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 77219.2778 | 4.5246 | 0 |  |  | 1 | 12 | 1 | 9
Lerwick | 1978-08-28 05:30 | 8.4 | 1.8 | 112.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 76508.1667 | 4.4829 | 0 |  |  | 1 | 13 | 1 | 10
Lerwick | 1978-08-28 06:30 | 9.2 | 1.5 | 200 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 75797.0556 | 4.4412 | 0 |  |  | 1 | 14 | 1 | 11
Lerwick | 1978-08-28 07:30 | 9.7 | 3.3 | 317.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 75085.9444 | 4.3996 | 0 |  |  | 1 | 15 | 1 | 12
Lerwick | 1978-08-28 08:30 | 10.1 | 4.7 | 302.5 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 74596.3148 | 4.3709 | 1 |  |  | 1 | 16 | 0 | 0
Lerwick | 1978-08-28 09:30 | 10.5 | 4.7 | 290 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 74328.1667 | 4.3552 | 1 |  |  | 1 | 17 | 0 | 0
Lerwick | 1978-08-28 10:30 | 11 | 4.7 | 272.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 74060.0185 | 4.3395 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-28 11:30 | 11.3 | 5.6 | 265 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 74074.8519 | 4.3403 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-28 12:30 | 11.2 | 6.6 | 267.5 | 1120 | 810 | 490 | 0 | 490 | 245 | 0 | 74319.8519 | 4.3547 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-28 13:30 | 11.1 | 7 | 272.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 74809.8519 | 4.3834 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-28 14:30 | 11 | 6.7 | 280 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 75299.8519 | 4.4121 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-28 15:30 | 11 | 6.3 | 290 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 75609.8519 | 4.4303 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-28 16:30 | 11 | 5.9 | 297.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 75764.8519 | 4.4393 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-28 17:30 | 11.2 | 5.7 | 300 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 75854.8519 | 4.4446 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-28 18:30 | 11.4 | 6 | 300 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 76009.8519 | 4.4537 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-28 19:30 | 11.2 | 6.7 | 300 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 76319.8519 | 4.4719 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-28 20:30 | 10.8 | 7 | 300 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 76809.8519 | 4.5006 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-28 21:30 | 10 | 6.6 | 300 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 77299.8519 | 4.5293 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-28 22:30 | 9.2 | 5.9 | 300 | 500 | 810 | 490 | 0 | 490 | 245 | 0 | 77544.8519 | 4.5436 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-28 23:30 | 8.8 | 6 | 300 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 77699.8519 | 4.5527 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-29 00:30 | 8.7 | 6.5 | 302.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 78009.8519 | 4.5709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-29 01:30 | 8.8 | 6.3 | 312.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 78319.8519 | 4.5891 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-29 02:30 | 8.7 | 6.5 | 332.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 78629.8519 | 4.6072 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-29 03:30 | 9 | 7.4 | 172.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 79119.8519 | 4.6359 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-29 04:30 | 9.2 | 7 | 0 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 79699.8519 | 4.6699 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-29 05:30 | 8.6 | 6 | 177.5 | 760 | 1120 | 800 | 0 | 800 | 400 | 0 | 80099.8519 | 4.6934 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-29 06:30 | 8.2 | 5.1 | 347.5 | 340 | 550 | 230 | 0 | 230 | 115 | 0 | 80214.8519 | 4.7001 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-08-29 07:30 | 8.5 | 4.2 | 332.5 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 79966.7037 | 4.6855 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-08-29 08:30 | 9.5 | 4.2 | 317.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 79425.963 | 4.6539 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-08-29 09:30 | 10.3 | 5.1 | 305 | 340 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 79177.8148 | 4.6393 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-29 10:30 | 10.6 | 5.9 | 305 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 79227.8148 | 4.6423 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-29 11:30 | 11 | 6.2 | 322.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 79382.8148 | 4.6513 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-29 12:30 | 11 | 6.4 | 170 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 79602.8148 | 4.6642 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-29 13:30 | 10.9 | 6.9 | 12.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 79912.8148 | 4.6824 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-29 14:30 | 10.1 | 7.3 | 17.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 80402.8148 | 4.7111 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-29 15:30 | 9.7 | 7.6 | 7.5 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 81047.8148 | 4.7489 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-29 16:30 | 10.2 | 7.6 | 175 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 81692.8148 | 4.7867 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-29 17:30 | 9.7 | 7.3 | 350 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 82337.8148 | 4.8245 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-29 18:30 | 9.6 | 6.9 | 347.5 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 82827.8148 | 4.8532 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-29 19:30 | 9.1 | 6.5 | 342.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 83227.8148 | 4.8766 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-29 20:30 | 8 | 7 | 340 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 83717.8148 | 4.9053 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-29 21:30 | 7.8 | 7.7 | 337.5 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 84362.8148 | 4.9431 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-29 22:30 | 7.8 | 7.2 | 330 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 85007.8148 | 4.9809 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-29 23:30 | 7.5 | 6.5 | 325 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 85497.8148 | 5.0096 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-30 00:30 | 7.6 | 6.4 | 327.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 85807.8148 | 5.0278 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-30 01:30 | 8 | 6.7 | 332.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 86117.8148 | 5.046 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-30 02:30 | 7.7 | 7 | 335 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 86607.8148 | 5.0747 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-30 03:30 | 7.3 | 7 | 335 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 87187.8148 | 5.1087 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-30 04:30 | 7.1 | 7 | 332.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 87767.8148 | 5.1426 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-30 05:30 | 7.1 | 7 | 327.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 88347.8148 | 5.1766 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-30 06:30 | 7.6 | 7.2 | 327.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 88927.8148 | 5.2106 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-30 07:30 | 8 | 7.7 | 332.5 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 89572.8148 | 5.2484 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-30 08:30 | 8 | 8 | 337.5 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 90217.8148 | 5.2862 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-30 09:30 | 8.2 | 7.9 | 337.5 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 90862.8148 | 5.324 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-30 10:30 | 8.7 | 7.6 | 332.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 91507.8148 | 5.3618 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-30 11:30 | 9.1 | 7.5 | 330 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 92152.8148 | 5.3996 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-30 12:30 | 9.6 | 7.5 | 332.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 92797.8148 | 5.4374 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-30 13:30 | 9.8 | 7.5 | 335 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 93442.8148 | 5.4752 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-30 14:30 | 10 | 7.5 | 330 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 94087.8148 | 5.513 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-30 15:30 | 10.2 | 7.5 | 325 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 94732.8148 | 5.5508 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-30 16:30 | 9.9 | 7.1 | 325 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 95377.8148 | 5.5885 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-30 17:30 | 9.7 | 6.3 | 322.5 | 760 | 1120 | 800 | 0 | 800 | 400 | 0 | 95777.8148 | 5.612 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-08-30 18:30 | 9.4 | 5.4 | 320 | 340 | 550 | 230 | 0 | 230 | 115 | 0 | 95892.8148 | 5.6187 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-08-30 19:30 | 9.1 | 4.9 | 320 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 95780.963 | 5.6122 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-08-30 20:30 | 8.7 | 4.7 | 322.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 95512.8148 | 5.5965 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-08-30 21:30 | 8.3 | 4.2 | 327.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 95108.3704 | 5.5728 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-08-30 22:30 | 8.2 | 3.6 | 325 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 94482.4444 | 5.5361 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-08-30 23:30 | 8 | 2.7 | 317.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 93771.3333 | 5.4944 | 0 |  |  | 1 | 6 | 1 | 1
Lerwick | 1978-08-31 00:30 | 7.8 | 2.2 | 310 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 93060.2222 | 5.4527 | 0 |  |  | 1 | 7 | 1 | 2
Lerwick | 1978-08-31 01:30 | 7.8 | 2.7 | 297.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 92349.1111 | 5.4111 | 0 |  |  | 1 | 8 | 1 | 3
Lerwick | 1978-08-31 02:30 | 7.8 | 3 | 290 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 91638 | 5.3694 | 0 |  |  | 1 | 9 | 1 | 4
Lerwick | 1978-08-31 03:30 | 7.8 | 2.2 | 292.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 90926.8889 | 5.3277 | 0 |  |  | 1 | 10 | 1 | 5
Lerwick | 1978-08-31 04:30 | 7.5 | 1.3 | 312.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 90215.7778 | 5.2861 | 0 |  |  | 1 | 11 | 1 | 6
Lerwick | 1978-08-31 05:30 | 7.3 | 0.4 | 165 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 89504.6667 | 5.2444 | 0 |  |  | 1 | 12 | 1 | 7
Lerwick | 1978-08-31 06:30 | 7.1 | 0.2 | 140 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 88793.5556 | 5.2027 | 0 |  |  | 1 | 13 | 1 | 8
Lerwick | 1978-08-31 07:30 | 7.3 | 0.9 | 240 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 88082.4444 | 5.1611 | 0 |  |  | 1 | 14 | 1 | 9
Lerwick | 1978-08-31 08:30 | 7.9 | 1.5 | 192.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 87371.3333 | 5.1194 | 0 |  |  | 1 | 15 | 1 | 10
Lerwick | 1978-08-31 09:30 | 8.8 | 2 | 170 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 86660.2222 | 5.0777 | 0 |  |  | 1 | 16 | 1 | 11
Lerwick | 1978-08-31 10:30 | 9.6 | 2.4 | 147.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 85949.1111 | 5.0361 | 0 |  |  | 1 | 17 | 1 | 12
Lerwick | 1978-08-31 11:30 | 9.7 | 2.9 | 142.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 85238 | 4.9944 | 0 |  |  | 1 | 18 | 1 | 13
Lerwick | 1978-08-31 12:30 | 10.2 | 2.9 | 147.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 84526.8889 | 4.9527 | 0 |  |  | 1 | 19 | 1 | 14
Lerwick | 1978-08-31 13:30 | 10.4 | 2.7 | 152.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 83815.7778 | 4.9111 | 0 |  |  | 1 | 20 | 1 | 15
Lerwick | 1978-08-31 14:30 | 10 | 2.9 | 155 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 83104.6667 | 4.8694 | 0 |  |  | 1 | 21 | 1 | 16
Lerwick | 1978-08-31 15:30 | 9.6 | 2.9 | 147.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 82393.5556 | 4.8277 | 0 |  |  | 1 | 22 | 1 | 17
Lerwick | 1978-08-31 16:30 | 9.3 | 2.6 | 135 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 81682.4444 | 4.7861 | 0 |  |  | 1 | 23 | 1 | 18
Lerwick | 1978-08-31 17:30 | 9 | 2.6 | 125 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 80971.3333 | 4.7444 | 0 |  |  | 1 | 24 | 1 | 19
Lerwick | 1978-08-31 18:30 | 9 | 3 | 115 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 80260.2222 | 4.7027 | 0 |  |  | 1 | 25 | 1 | 20
Lerwick | 1978-08-31 19:30 | 8.9 | 3.3 | 100 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 79549.1111 | 4.6611 | 0 |  |  | 1 | 26 | 1 | 21
Lerwick | 1978-08-31 20:30 | 8.9 | 3.4 | 75 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 78838 | 4.6194 | 0 |  |  | 1 | 27 | 1 | 22
Lerwick | 1978-08-31 21:30 | 8.9 | 3.7 | 55 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 78126.8889 | 4.5777 | 0 |  |  | 1 | 28 | 1 | 23
Lerwick | 1978-08-31 22:30 | 8.6 | 3.3 | 45 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 77415.7778 | 4.5361 | 0 |  |  | 1 | 29 | 1 | 24
Lerwick | 1978-08-31 23:30 | 8.4 | 2.4 | 25 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 76704.6667 | 4.4944 | 0 |  |  | 1 | 30 | 1 | 25
Lerwick | 1978-09-01 00:30 | 8.3 | 2.4 | 180 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 75993.5556 | 4.4527 | 0 |  |  | 1 | 31 | 1 | 26
Lerwick | 1978-09-01 01:30 | 8.1 | 2.6 | 347.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 75282.4444 | 4.4111 | 0 |  |  | 1 | 32 | 1 | 27
Lerwick | 1978-09-01 02:30 | 7.9 | 2.4 | 340 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 74571.3333 | 4.3694 | 0 |  |  | 1 | 33 | 1 | 28
Lerwick | 1978-09-01 03:30 | 8 | 2.1 | 335 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 73860.2222 | 4.3277 | 0 |  |  | 1 | 34 | 1 | 29
Lerwick | 1978-09-01 04:30 | 8.1 | 2.1 | 337.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 73149.1111 | 4.2861 | 0 |  |  | 1 | 35 | 1 | 30
Lerwick | 1978-09-01 05:30 | 8 | 1.9 | 335 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 72438 | 4.2444 | 0 |  |  | 1 | 36 | 1 | 31
Lerwick | 1978-09-01 06:30 | 7.9 | 1.8 | 325 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 71726.8889 | 4.2027 | 0 |  |  | 1 | 37 | 1 | 32
Lerwick | 1978-09-01 07:30 | 8.3 | 2 | 325 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 71015.7778 | 4.1611 | 0 |  |  | 1 | 38 | 1 | 33
Lerwick | 1978-09-01 08:30 | 9 | 2.4 | 165 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 70304.6667 | 4.1194 | 0 |  |  | 1 | 39 | 1 | 34
Lerwick | 1978-09-01 09:30 | 9.4 | 2.4 | 15 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 69593.5556 | 4.0777 | 0 |  |  | 1 | 40 | 1 | 35
Lerwick | 1978-09-01 10:30 | 9.5 | 2.2 | 32.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 68882.4444 | 4.0361 | 0 |  |  | 1 | 41 | 1 | 36
Lerwick | 1978-09-01 11:30 | 9.8 | 2.4 | 35 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 68171.3333 | 3.9944 | 0 |  |  | 1 | 42 | 1 | 37
Lerwick | 1978-09-01 12:30 | 10.2 | 3.3 | 35 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 67460.2222 | 3.9527 | 0 |  |  | 1 | 43 | 1 | 38
Lerwick | 1978-09-01 13:30 | 11 | 4.4 | 22.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 66834.2963 | 3.9161 | 1 |  |  | 1 | 44 | 0 | 0
Lerwick | 1978-09-01 14:30 | 11.5 | 5.1 | 180 | 340 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 66586.1481 | 3.9015 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-01 15:30 | 11.7 | 5.4 | 347.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 66596.1481 | 3.9021 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-01 16:30 | 11.5 | 5.4 | 340 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 66606.1481 | 3.9027 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-01 17:30 | 11 | 5.5 | 330 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 66656.1481 | 3.9056 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-01 18:30 | 10.4 | 5.7 | 322.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 66746.1481 | 3.9109 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-01 19:30 | 9.6 | 5.7 | 322.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 66836.1481 | 3.9162 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-01 20:30 | 9.1 | 5.8 | 327.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 66926.1481 | 3.9215 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-01 21:30 | 8.8 | 6.1 | 327.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 67081.1481 | 3.9305 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-01 22:30 | 8.4 | 6.1 | 322.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 67301.1481 | 3.9434 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-01 23:30 | 7.7 | 5.2 | 320 | 340 | 550 | 230 | 0 | 230 | 115 | 0 | 67416.1481 | 3.9502 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-09-02 00:30 | 7.4 | 4.5 | 322.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 67304.2963 | 3.9436 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-09-02 01:30 | 7.6 | 5.1 | 325 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 67192.4444 | 3.9371 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-02 02:30 | 7.8 | 5.8 | 322.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 67242.4444 | 3.94 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-02 03:30 | 7.5 | 5.8 | 320 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 67332.4444 | 3.9453 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-02 04:30 | 7.5 | 5.7 | 320 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 67422.4444 | 3.9505 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-02 05:30 | 7.4 | 5.7 | 320 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 67512.4444 | 3.9558 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-02 06:30 | 7.3 | 5.7 | 320 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 67602.4444 | 3.9611 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-02 07:30 | 8.2 | 5.9 | 320 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 67692.4444 | 3.9664 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-02 08:30 | 9 | 6.4 | 322.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 67847.4444 | 3.9754 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-02 09:30 | 9.3 | 6.8 | 325 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 68157.4444 | 3.9936 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-02 10:30 | 9.7 | 7 | 322.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 68647.4444 | 4.0223 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-02 11:30 | 10.3 | 7 | 320 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 69227.4444 | 4.0563 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-02 12:30 | 10.9 | 7.1 | 320 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 69807.4444 | 4.0903 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-02 13:30 | 11 | 7.3 | 320 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 70387.4444 | 4.1243 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-02 14:30 | 10.5 | 7.5 | 317.5 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 71032.4444 | 4.1621 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-02 15:30 | 10.3 | 7.2 | 315 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 71677.4444 | 4.1999 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-02 16:30 | 9.9 | 6.8 | 317.5 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 72167.4444 | 4.2286 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-02 17:30 | 9.6 | 6.5 | 322.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 72567.4444 | 4.252 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-02 18:30 | 9.9 | 6.1 | 327.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 72877.4444 | 4.2702 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-02 19:30 | 9.5 | 5.6 | 327.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 73032.4444 | 4.2792 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-02 20:30 | 9.3 | 5.1 | 322.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 73082.4444 | 4.2822 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-09-02 21:30 | 9.3 | 4.9 | 322.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 72970.5926 | 4.2756 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-09-02 22:30 | 9.2 | 4.9 | 320 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 72702.4444 | 4.2599 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-09-02 23:30 | 9.4 | 4.7 | 310 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 72434.2963 | 4.2442 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-09-03 00:30 | 9.6 | 4.5 | 310 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 72166.1481 | 4.2285 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-09-03 01:30 | 9.3 | 4.5 | 315 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 71898 | 4.2128 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-09-03 02:30 | 8.7 | 4.5 | 310 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 71629.8519 | 4.1971 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-09-03 03:30 | 8.5 | 4.7 | 302.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 71361.7037 | 4.1813 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-09-03 04:30 | 8.5 | 4.9 | 300 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 71093.5556 | 4.1656 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-09-03 05:30 | 8.2 | 4.9 | 302.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 70825.4074 | 4.1499 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-09-03 06:30 | 7.9 | 5.2 | 307.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 70713.5556 | 4.1434 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-03 07:30 | 8.5 | 5.5 | 312.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 70763.5556 | 4.1463 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-03 08:30 | 9 | 6 | 317.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 70918.5556 | 4.1554 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-03 09:30 | 9.3 | 6.7 | 317.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 71228.5556 | 4.1735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-03 10:30 | 9.9 | 7 | 312.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 71718.5556 | 4.2023 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-03 11:30 | 10.5 | 6.6 | 315 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 72208.5556 | 4.231 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-03 12:30 | 10.4 | 6 | 322.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 72518.5556 | 4.2491 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-03 13:30 | 10 | 5.9 | 322.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 72673.5556 | 4.2582 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-03 14:30 | 10 | 6 | 322.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 72828.5556 | 4.2673 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-03 15:30 | 9.9 | 6.3 | 325 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 73048.5556 | 4.2802 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-03 16:30 | 9.6 | 6.1 | 325 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 73268.5556 | 4.2931 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-03 17:30 | 9.5 | 5.8 | 327.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 73423.5556 | 4.3022 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-03 18:30 | 9.1 | 5.3 | 327.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 73473.5556 | 4.3051 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-09-03 19:30 | 8.7 | 4.4 | 320 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 73225.4074 | 4.2906 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-09-03 20:30 | 8.6 | 3.7 | 315 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 72599.4815 | 4.2539 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-09-03 21:30 | 8.3 | 3.7 | 320 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 71888.3704 | 4.2122 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-09-03 22:30 | 7.7 | 4.1 | 325 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 71262.4444 | 4.1755 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-09-03 23:30 | 7.5 | 4.4 | 325 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 70721.7037 | 4.1438 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-09-04 00:30 | 7.5 | 4.1 | 327.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 70180.963 | 4.1122 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-09-04 01:30 | 7.6 | 3.9 | 335 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 69555.037 | 4.0755 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-09-04 02:30 | 7.5 | 4 | 342.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 68929.1111 | 4.0388 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-09-04 03:30 | 7.1 | 4 | 345 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 68388.3704 | 4.0071 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-09-04 04:30 | 6.9 | 4.4 | 347.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 67847.6296 | 3.9754 | 1 |  |  | 1 | 11 | 0 | 0
Lerwick | 1978-09-04 05:30 | 6.9 | 4.9 | 350 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 67443.1852 | 3.9517 | 1 |  |  | 1 | 12 | 0 | 0
Lerwick | 1978-09-04 06:30 | 7 | 5.3 | 350 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 67331.3333 | 3.9452 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-04 07:30 | 7.8 | 6.2 | 352.5 | 760 | 550 | 230 | 0 | 230 | 115 | 0 | 67446.3333 | 3.9519 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-04 08:30 | 9.2 | 6.9 | 180 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 67756.3333 | 3.9701 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-04 09:30 | 10 | 7.3 | 10 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 68246.3333 | 3.9988 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-04 10:30 | 10.5 | 7.7 | 17.5 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 68891.3333 | 4.0366 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-04 11:30 | 11 | 8.2 | 20 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 69536.3333 | 4.0744 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-04 12:30 | 11.6 | 8.5 | 20 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 70181.3333 | 4.1122 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-04 13:30 | 11.9 | 8.2 | 17.5 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 70826.3333 | 4.15 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-04 14:30 | 11.3 | 7.8 | 15 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 71471.3333 | 4.1878 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-04 15:30 | 11 | 7.8 | 15 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 72116.3333 | 4.2256 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-04 16:30 | 11 | 8 | 12.5 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 72761.3333 | 4.2634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-04 17:30 | 10.6 | 7.7 | 10 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 73406.3333 | 4.3012 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-04 18:30 | 10.3 | 7.2 | 10 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 74051.3333 | 4.3389 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-04 19:30 | 10 | 7 | 10 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 74631.3333 | 4.3729 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-04 20:30 | 9.8 | 7 | 10 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 75211.3333 | 4.4069 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-04 21:30 | 9.8 | 6.8 | 7.5 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 75701.3333 | 4.4356 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-04 22:30 | 9.8 | 6.4 | 2.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 76011.3333 | 4.4538 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-04 23:30 | 9.5 | 5.9 | 0 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 76166.3333 | 4.4629 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-05 00:30 | 9.4 | 5.7 | 0 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 76256.3333 | 4.4681 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-05 01:30 | 9.6 | 5.8 | 2.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 76346.3333 | 4.4734 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-05 02:30 | 9.8 | 5.9 | 5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 76436.3333 | 4.4787 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-05 03:30 | 10 | 5.4 | 2.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 76486.3333 | 4.4816 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-09-05 04:30 | 10 | 4.9 | 2.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 76374.4815 | 4.4751 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-09-05 05:30 | 10 | 4.9 | 10 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 76106.3333 | 4.4594 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-09-05 06:30 | 10 | 4.9 | 20 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 75838.1852 | 4.4436 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-09-05 07:30 | 10.3 | 4.4 | 27.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 75433.7407 | 4.4199 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-09-05 08:30 | 10.7 | 3.9 | 37.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 74807.8148 | 4.3833 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-09-05 09:30 | 11.1 | 3.9 | 60 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 74096.7037 | 4.3416 | 0 |  |  | 1 | 7 | 1 | 1
Lerwick | 1978-09-05 10:30 | 11.9 | 3.9 | 82.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 73385.5926 | 4.2999 | 0 |  |  | 1 | 8 | 1 | 2
Lerwick | 1978-09-05 11:30 | 12.5 | 3.9 | 95 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 72674.4815 | 4.2583 | 0 |  |  | 1 | 9 | 1 | 3
Lerwick | 1978-09-05 12:30 | 12.9 | 3.7 | 107.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 71963.3704 | 4.2166 | 0 |  |  | 1 | 10 | 1 | 4
Lerwick | 1978-09-05 13:30 | 12.7 | 3.6 | 115 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 71252.2593 | 4.1749 | 0 |  |  | 1 | 11 | 1 | 5
Lerwick | 1978-09-05 14:30 | 12.4 | 3.4 | 112.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 70541.1481 | 4.1333 | 0 |  |  | 1 | 12 | 1 | 6
Lerwick | 1978-09-05 15:30 | 12.4 | 3.3 | 112.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 69830.037 | 4.0916 | 0 |  |  | 1 | 13 | 1 | 7
Lerwick | 1978-09-05 16:30 | 12.2 | 3.3 | 115 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 69118.9259 | 4.0499 | 0 |  |  | 1 | 14 | 1 | 8
Lerwick | 1978-09-05 17:30 | 11.9 | 3.4 | 112.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 68407.8148 | 4.0083 | 0 |  |  | 1 | 15 | 1 | 9
Lerwick | 1978-09-05 18:30 | 11.8 | 4 | 112.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 67781.8889 | 3.9716 | 1 |  |  | 1 | 16 | 0 | 0
Lerwick | 1978-09-05 19:30 | 11.4 | 4.6 | 115 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 67377.4444 | 3.9479 | 1 |  |  | 1 | 17 | 0 | 0
Lerwick | 1978-09-05 20:30 | 11.2 | 5.1 | 112.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 67265.5926 | 3.9413 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-05 21:30 | 11.3 | 5.5 | 110 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 67315.5926 | 3.9443 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-05 22:30 | 11.3 | 5.8 | 110 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 67405.5926 | 3.9495 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-05 23:30 | 11.3 | 5.9 | 110 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 67495.5926 | 3.9548 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-06 00:30 | 11.2 | 5.8 | 112.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 67585.5926 | 3.9601 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-06 01:30 | 11 | 5.7 | 112.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 67675.5926 | 3.9654 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-06 02:30 | 10.7 | 5.7 | 105 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 67765.5926 | 3.9706 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-06 03:30 | 10.7 | 5.9 | 100 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 67855.5926 | 3.9759 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-06 04:30 | 11 | 6.3 | 100 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 68010.5926 | 3.985 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-06 05:30 | 11 | 6.3 | 100 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 68230.5926 | 3.9979 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-06 06:30 | 11 | 6.3 | 102.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 68450.5926 | 4.0108 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-06 07:30 | 11.4 | 6.7 | 107.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 68760.5926 | 4.0289 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-06 08:30 | 12.1 | 7 | 110 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 69250.5926 | 4.0577 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-06 09:30 | 12.7 | 6.8 | 110 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 69740.5926 | 4.0864 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-06 10:30 | 13.3 | 6.7 | 110 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 70140.5926 | 4.1098 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-06 11:30 | 13.8 | 6.8 | 107.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 70540.5926 | 4.1332 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-06 12:30 | 13.8 | 6.8 | 105 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 70940.5926 | 4.1567 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-06 13:30 | 13.8 | 6.7 | 107.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 71340.5926 | 4.1801 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-06 14:30 | 13.4 | 6.8 | 110 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 71740.5926 | 4.2036 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-06 15:30 | 12.6 | 6.7 | 110 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 72140.5926 | 4.227 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-06 16:30 | 12.3 | 6.3 | 110 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 72450.5926 | 4.2452 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-06 17:30 | 12.1 | 6.2 | 110 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 72670.5926 | 4.258 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-06 18:30 | 11.7 | 6.2 | 110 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 72890.5926 | 4.2709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-06 19:30 | 11.4 | 6.4 | 110 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 73110.5926 | 4.2838 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-06 20:30 | 11.2 | 6.8 | 110 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 73420.5926 | 4.302 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-06 21:30 | 11.3 | 7 | 110 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 73910.5926 | 4.3307 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-06 22:30 | 11.4 | 7 | 110 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 74490.5926 | 4.3647 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-06 23:30 | 11.3 | 6.7 | 110 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 74980.5926 | 4.3934 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-07 00:30 | 11.3 | 6.3 | 110 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 75290.5926 | 4.4116 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-07 01:30 | 11.3 | 6.4 | 110 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 75510.5926 | 4.4244 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-07 02:30 | 11.3 | 7.2 | 110 | 1480 | 1120 | 800 | 0 | 800 | 400 | 0 | 75910.5926 | 4.4479 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-07 03:30 | 11.4 | 7.9 | 110 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 76555.5926 | 4.4857 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-07 04:30 | 11.5 | 8.1 | 110 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 77200.5926 | 4.5235 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-07 05:30 | 11.2 | 8.3 | 110 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 77845.5926 | 4.5613 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-07 06:30 | 11.2 | 8.3 | 110 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 78490.5926 | 4.5991 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-07 07:30 | 11.5 | 7.8 | 110 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 79135.5926 | 4.6369 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-07 08:30 | 11.5 | 7.2 | 115 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 79780.5926 | 4.6746 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-07 09:30 | 11.5 | 6.8 | 125 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 80270.5926 | 4.7034 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-07 10:30 | 11 | 6.9 | 130 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 80670.5926 | 4.7268 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-07 11:30 | 10.9 | 7.6 | 127.5 | 1840 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 81250.5926 | 4.7608 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-07 12:30 | 11.1 | 8.3 | 122.5 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 81895.5926 | 4.7986 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-07 13:30 | 11.2 | 8.5 | 120 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 82540.5926 | 4.8364 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-07 14:30 | 11.6 | 8.5 | 122.5 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 83185.5926 | 4.8742 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-07 15:30 | 11.5 | 8.5 | 127.5 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 83830.5926 | 4.9119 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-07 16:30 | 11.3 | 9 | 125 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 84475.5926 | 4.9497 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-07 17:30 | 11 | 9.4 | 125 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 85120.5926 | 4.9875 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-07 18:30 | 11 | 8.4 | 145 | 2200 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 85765.5926 | 5.0253 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-07 19:30 | 11.2 | 6.7 | 165 | 1120 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 86410.5926 | 5.0631 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-07 20:30 | 11.3 | 5.4 | 172.5 | 340 | 730 | 410 | 0 | 410 | 205 | 0 | 86615.5926 | 5.0751 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-09-07 21:30 | 11 | 4.7 | 180 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 86503.7407 | 5.0686 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-09-07 22:30 | 11 | 5.1 | 190 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 86391.8889 | 5.062 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-07 23:30 | 11.1 | 6.3 | 197.5 | 760 | 550 | 230 | 0 | 230 | 115 | 0 | 86506.8889 | 5.0688 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-08 00:30 | 11.3 | 6.7 | 200 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 86816.8889 | 5.0869 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-08 01:30 | 11.2 | 6.5 | 202.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 87216.8889 | 5.1104 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-08 02:30 | 11 | 7.2 | 212.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 87706.8889 | 5.1391 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-08 03:30 | 10.9 | 7.7 | 225 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 88351.8889 | 5.1769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-08 04:30 | 10.9 | 7.4 | 225 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 88996.8889 | 5.2147 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-08 05:30 | 10.7 | 7.3 | 215 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 89576.8889 | 5.2486 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-08 06:30 | 10.6 | 7.5 | 210 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 90221.8889 | 5.2864 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-08 07:30 | 10.9 | 7.5 | 210 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 90866.8889 | 5.3242 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-08 08:30 | 11.1 | 7.3 | 202.5 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 91511.8889 | 5.362 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-08 09:30 | 11.5 | 6.9 | 187.5 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 92001.8889 | 5.3907 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-08 10:30 | 11.8 | 6.7 | 177.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 92401.8889 | 5.4142 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-08 11:30 | 11.6 | 6.5 | 172.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 92801.8889 | 5.4376 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-08 12:30 | 11.6 | 6 | 167.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 93111.8889 | 5.4558 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-08 13:30 | 11.9 | 6.3 | 162.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 93331.8889 | 5.4687 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-08 14:30 | 12 | 8 | 162.5 | 2200 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 93911.8889 | 5.5026 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-08 15:30 | 11.7 | 9.2 | 165 | 2920 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 94556.8889 | 5.5404 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-08 16:30 | 11.4 | 9.5 | 165 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 95201.8889 | 5.5782 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-08 17:30 | 11.2 | 9.2 | 167.5 | 2920 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 95846.8889 | 5.616 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-08 18:30 | 11 | 8.5 | 172.5 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 96491.8889 | 5.6538 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-08 19:30 | 11 | 8.4 | 180 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 97136.8889 | 5.6916 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-08 20:30 | 11 | 9.8 | 192.5 | 3280 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 97781.8889 | 5.7294 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-08 21:30 | 11.4 | 10.6 | 207.5 | 4000 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 98426.8889 | 5.7672 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-08 22:30 | 11.4 | 9.6 | 215 | 3280 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 99071.8889 | 5.805 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-08 23:30 | 10.9 | 8.1 | 210 | 2200 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 99716.8889 | 5.8428 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-09 00:30 | 10.9 | 7.1 | 197.5 | 1480 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 100361.8889 | 5.8806 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-09 01:30 | 11 | 7.2 | 187.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 100941.8889 | 5.9146 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-09 02:30 | 10.9 | 8.2 | 190 | 2200 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 101586.8889 | 5.9524 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-09 03:30 | 10.9 | 8.6 | 197.5 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 102231.8889 | 5.9901 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-09 04:30 | 10.9 | 8.5 | 202.5 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 102876.8889 | 6.0279 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-09 05:30 | 10.6 | 9 | 205 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 103521.8889 | 6.0657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-09 06:30 | 10.2 | 10.1 | 202.5 | 3640 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 104166.8889 | 6.1035 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-09 07:30 | 10.3 | 11 | 202.5 | 4300 | 3970 | 3650 | 0 | 1290 | 645 | 0 | 104811.8889 | 6.1413 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-09 08:30 | 10.8 | 11.1 | 210 | 4300 | 4300 | 3980 | 0 | 1290 | 645 | 0 | 105456.8889 | 6.1791 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-09 09:30 | 11 | 10.6 | 220 | 4000 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 106101.8889 | 6.2169 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-09 10:30 | 11.3 | 10 | 227.5 | 3640 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 106746.8889 | 6.2547 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-09 11:30 | 11.7 | 9.8 | 230 | 3280 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 107391.8889 | 6.2925 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-09 12:30 | 12.2 | 9.9 | 230 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 108036.8889 | 6.3303 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-09 13:30 | 12.4 | 10.1 | 230 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 108681.8889 | 6.3681 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-09 14:30 | 12.4 | 10.3 | 230 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 109326.8889 | 6.4059 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-09 15:30 | 12.3 | 10.1 | 230 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 109971.8889 | 6.4437 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-09 16:30 | 12.1 | 10 | 230 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 110616.8889 | 6.4815 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-09 17:30 | 11.5 | 9.7 | 230 | 3280 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 111261.8889 | 6.5193 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-09 18:30 | 10.9 | 9.1 | 230 | 2920 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 111906.8889 | 6.557 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-09 19:30 | 10.4 | 8.9 | 230 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 112551.8889 | 6.5948 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-09 20:30 | 10.3 | 9 | 227.5 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 113196.8889 | 6.6326 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-09 21:30 | 10.1 | 9.1 | 222.5 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 113841.8889 | 6.6704 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-09 22:30 | 9.9 | 9.3 | 220 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 114486.8889 | 6.7082 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-09 23:30 | 10 | 8.9 | 220 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 115131.8889 | 6.746 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-10 00:30 | 10.2 | 8.5 | 220 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 115776.8889 | 6.7838 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-10 01:30 | 10.4 | 8.3 | 217.5 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 116421.8889 | 6.8216 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-10 02:30 | 10.5 | 7.5 | 212.5 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 117066.8889 | 6.8594 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-10 03:30 | 10.5 | 6.6 | 217.5 | 1120 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 117646.8889 | 6.8934 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-10 04:30 | 10.2 | 6 | 237.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 117956.8889 | 6.9115 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-10 05:30 | 9.9 | 5.8 | 260 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 118111.8889 | 6.9206 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-10 06:30 | 9.7 | 5.9 | 275 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 118201.8889 | 6.9259 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-10 07:30 | 9.7 | 6.6 | 282.5 | 1120 | 810 | 490 | 0 | 490 | 245 | 0 | 118446.8889 | 6.9402 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-10 08:30 | 9.8 | 7.1 | 285 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 118936.8889 | 6.969 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-10 09:30 | 9.8 | 7.3 | 282.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 119516.8889 | 7.0029 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-10 10:30 | 10.3 | 7.7 | 277.5 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 120161.8889 | 7.0407 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-10 11:30 | 11.1 | 8 | 275 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 120806.8889 | 7.0785 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-10 12:30 | 11.6 | 7.7 | 275 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 121451.8889 | 7.1163 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-10 13:30 | 11.6 | 7.2 | 272.5 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 122096.8889 | 7.1541 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-10 14:30 | 11.2 | 6.8 | 270 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 122586.8889 | 7.1828 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-10 15:30 | 10.7 | 6.7 | 270 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 122986.8889 | 7.2063 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-10 16:30 | 10.2 | 6.7 | 270 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 123386.8889 | 7.2297 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-10 17:30 | 9.7 | 6.4 | 267.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 123696.8889 | 7.2479 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-10 18:30 | 9.5 | 5.9 | 262.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 123851.8889 | 7.2569 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-10 19:30 | 9.4 | 5.3 | 257.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 123901.8889 | 7.2599 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-09-10 20:30 | 9.3 | 4.6 | 252.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 123790.037 | 7.2533 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-09-10 21:30 | 9.4 | 4 | 245 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 123385.5926 | 7.2296 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-09-10 22:30 | 9.4 | 2.9 | 237.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 122759.6667 | 7.1929 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-09-10 23:30 | 9 | 1.8 | 225 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 122048.5556 | 7.1513 | 0 |  |  | 1 | 5 | 1 | 1
Lerwick | 1978-09-11 00:30 | 8.7 | 1.5 | 207.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 121337.4444 | 7.1096 | 0 |  |  | 1 | 6 | 1 | 2
Lerwick | 1978-09-11 01:30 | 8.7 | 1.2 | 242.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 120626.3333 | 7.0679 | 0 |  |  | 1 | 7 | 1 | 3
Lerwick | 1978-09-11 02:30 | 8.5 | 0.5 | 142.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 119915.2222 | 7.0263 | 0 |  |  | 1 | 8 | 1 | 4
Lerwick | 1978-09-11 03:30 | 8.3 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 119204.1111 | 6.9846 | 0 |  |  | 1 | 9 | 1 | 5
Lerwick | 1978-09-11 04:30 | 8.2 | 0.6 | 175 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 118493 | 6.9429 | 0 |  |  | 1 | 10 | 1 | 6
Lerwick | 1978-09-11 05:30 | 7.9 | 2.3 | 347.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 117781.8889 | 6.9013 | 0 |  |  | 1 | 11 | 1 | 7
Lerwick | 1978-09-11 06:30 | 7.8 | 3.8 | 345 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 117070.7778 | 6.8596 | 0 |  |  | 1 | 12 | 1 | 8
Lerwick | 1978-09-11 07:30 | 7.9 | 4.6 | 340 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 116581.1481 | 6.8309 | 1 |  |  | 1 | 13 | 0 | 0
Lerwick | 1978-09-11 08:30 | 8.8 | 5.4 | 332.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 116469.2963 | 6.8244 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-11 09:30 | 9.5 | 6.7 | 327.5 | 1120 | 730 | 410 | 0 | 410 | 205 | 0 | 116674.2963 | 6.8364 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-11 10:30 | 10 | 7.8 | 322.5 | 1840 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 117254.2963 | 6.8704 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-11 11:30 | 10.7 | 8.7 | 320 | 2560 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 117899.2963 | 6.9082 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-11 12:30 | 10.8 | 9.8 | 320 | 3280 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 118544.2963 | 6.946 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-11 13:30 | 10.6 | 10.3 | 320 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 119189.2963 | 6.9837 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-11 14:30 | 10.9 | 10.3 | 320 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 119834.2963 | 7.0215 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-11 15:30 | 11.1 | 10.3 | 320 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 120479.2963 | 7.0593 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-11 16:30 | 10.7 | 10.5 | 320 | 4000 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 121124.2963 | 7.0971 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-11 17:30 | 10.1 | 11 | 320 | 4300 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 121769.2963 | 7.1349 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-11 18:30 | 9.9 | 11.1 | 320 | 4300 | 4300 | 3980 | 0 | 1290 | 645 | 0 | 122414.2963 | 7.1727 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-11 19:30 | 9.7 | 10.7 | 320 | 4000 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 123059.2963 | 7.2105 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-11 20:30 | 9.3 | 10.4 | 320 | 3640 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 123704.2963 | 7.2483 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-11 21:30 | 9.2 | 10.3 | 320 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 124349.2963 | 7.2861 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-11 22:30 | 9.4 | 9.9 | 320 | 3280 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 124994.2963 | 7.3239 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-11 23:30 | 9.3 | 9 | 317.5 | 2920 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 125639.2963 | 7.3617 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-12 00:30 | 9.1 | 8.3 | 312.5 | 2200 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 126284.2963 | 7.3995 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-12 01:30 | 8.8 | 8.3 | 312.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 126929.2963 | 7.4373 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-12 02:30 | 8.3 | 8.5 | 317.5 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 127574.2963 | 7.4751 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-12 03:30 | 8.1 | 8.5 | 320 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 128219.2963 | 7.5128 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-12 04:30 | 8 | 8.5 | 320 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 128864.2963 | 7.5506 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-12 05:30 | 7.9 | 8 | 320 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 129509.2963 | 7.5884 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-12 06:30 | 7.6 | 6.9 | 320 | 1120 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 130154.2963 | 7.6262 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-12 07:30 | 7.8 | 6.4 | 320 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 130464.2963 | 7.6444 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-12 08:30 | 8.5 | 6.5 | 317.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 130774.2963 | 7.6626 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-12 09:30 | 9 | 6.4 | 312.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 131084.2963 | 7.6807 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-12 10:30 | 9.3 | 5.9 | 305 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 131239.2963 | 7.6898 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-12 11:30 | 9.3 | 5.5 | 292.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 131329.2963 | 7.6951 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-12 12:30 | 9.3 | 5.4 | 277.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 131379.2963 | 7.698 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-12 13:30 | 9.5 | 5.1 | 265 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 131389.2963 | 7.6986 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-09-12 14:30 | 9.7 | 4.4 | 257.5 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 131141.1481 | 7.6841 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-09-12 15:30 | 9.4 | 3.5 | 247.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 130515.2222 | 7.6474 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-09-12 16:30 | 9 | 2.6 | 225 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 129804.1111 | 7.6057 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-09-12 17:30 | 8.5 | 2.3 | 192.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 129093 | 7.564 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-09-12 18:30 | 8.3 | 3.3 | 165 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 128381.8889 | 7.5224 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-09-12 19:30 | 8.1 | 4.8 | 155 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 127892.2593 | 7.4937 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-12 20:30 | 8.2 | 6.3 | 160 | 760 | 479.6667 | 159.6667 | 0 | 159.6667 | 79.8333 | 0 | 127972.0926 | 7.4984 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-12 21:30 | 8.8 | 7.5 | 165 | 1840 | 1300 | 980 | 0 | 980 | 490 | 0 | 128462.0926 | 7.5271 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-12 22:30 | 8.4 | 8.4 | 162.5 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 129107.0926 | 7.5649 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-12 23:30 | 7.9 | 8.9 | 157.5 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 129752.0926 | 7.6027 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-13 00:30 | 8 | 8.9 | 157.5 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 130397.0926 | 7.6405 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-13 01:30 | 8.4 | 8.1 | 175 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 131042.0926 | 7.6782 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-13 02:30 | 9.4 | 7.2 | 205 | 1480 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 131687.0926 | 7.716 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-13 03:30 | 10 | 7.1 | 227.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 132267.0926 | 7.75 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-13 04:30 | 10.3 | 7.3 | 237.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 132847.0926 | 7.784 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-13 05:30 | 10.5 | 7.5 | 237.5 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 133492.0926 | 7.8218 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-13 06:30 | 10.4 | 7.7 | 232.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 134137.0926 | 7.8596 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-13 07:30 | 10.7 | 8.5 | 230 | 2560 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 134782.0926 | 7.8974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-13 08:30 | 10.9 | 9.2 | 227.5 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 135427.0926 | 7.9352 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-13 09:30 | 11.2 | 9.9 | 222.5 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 136072.0926 | 7.973 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-13 10:30 | 11.8 | 10.6 | 220 | 4000 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 136717.0926 | 8.0108 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-13 11:30 | 12.4 | 10.9 | 220 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 137362.0926 | 8.0486 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-13 12:30 | 12.7 | 10.5 | 220 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 138007.0926 | 8.0864 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-13 13:30 | 12.8 | 10.4 | 220 | 3640 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 138652.0926 | 8.1241 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-13 14:30 | 12.6 | 10.4 | 220 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 139297.0926 | 8.1619 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-13 15:30 | 12.7 | 10.1 | 217.5 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 139942.0926 | 8.1997 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-13 16:30 | 12.2 | 10.2 | 212.5 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 140587.0926 | 8.2375 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-13 17:30 | 11.5 | 10.5 | 210 | 4000 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 141232.0926 | 8.2753 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-13 18:30 | 11.5 | 10.1 | 210 | 3640 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 141877.0926 | 8.3131 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-13 19:30 | 11.1 | 9.6 | 210 | 3280 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 142522.0926 | 8.3509 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-13 20:30 | 10.9 | 9.7 | 210 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 143167.0926 | 8.3887 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-13 21:30 | 11 | 10.1 | 210 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 143812.0926 | 8.4265 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-13 22:30 | 10.9 | 10.3 | 210 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 144457.0926 | 8.4643 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-13 23:30 | 10.7 | 10.5 | 210 | 4000 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 145102.0926 | 8.5021 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-14 00:30 | 10.4 | 11.6 | 210 | 4472.2222 | 4236.1111 | 3916.1111 | 0 | 1290 | 645 | 0 | 145747.0926 | 8.5399 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-14 01:30 | 10.2 | 12.7 | 210 | 4600 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 146392.0926 | 8.5777 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-14 02:30 | 10.1 | 12.8 | 210 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 147037.0926 | 8.6155 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-14 03:30 | 10 | 12.4 | 212.5 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 645 | 0 | 147682.0926 | 8.6532 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-14 04:30 | 10 | 12.4 | 217.5 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 148327.0926 | 8.691 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-14 05:30 | 10.2 | 12.4 | 220 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 148972.0926 | 8.7288 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-14 06:30 | 10.4 | 12.1 | 220 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 149617.0926 | 8.7666 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-14 07:30 | 10.5 | 12.1 | 220 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 150262.0926 | 8.8044 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-14 08:30 | 10.6 | 12.6 | 222.5 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 645 | 0 | 150907.0926 | 8.8422 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-14 09:30 | 10.9 | 13 | 227.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 151552.0926 | 8.88 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-14 10:30 | 11.1 | 13.2 | 232.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 152197.0926 | 8.9178 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-14 11:30 | 10.8 | 13.4 | 237.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 152842.0926 | 8.9556 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-14 12:30 | 10.6 | 13.9 | 242.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 153487.0926 | 8.9934 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-14 13:30 | 10.6 | 14.6 | 247.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 154132.0926 | 9.0312 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-14 14:30 | 10.3 | 14.5 | 250 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 154777.0926 | 9.069 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-14 15:30 | 10 | 14.3 | 250 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 155422.0926 | 9.1068 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-14 16:30 | 10.1 | 14.6 | 250 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 156067.0926 | 9.1446 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-14 17:30 | 10.3 | 14.8 | 252.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 156712.0926 | 9.1823 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-14 18:30 | 10.4 | 14.3 | 257.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 157357.0926 | 9.2201 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-14 19:30 | 10.1 | 13.5 | 260 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 158002.0926 | 9.2579 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-14 20:30 | 9.7 | 12.7 | 257.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 158647.0926 | 9.2957 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-14 21:30 | 9.5 | 11.3 | 252.5 | 4300 | 4450 | 4130 | 0 | 1290 | 645 | 0 | 159292.0926 | 9.3335 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-14 22:30 | 9.3 | 8.9 | 247.5 | 2560 | 3430 | 3110 | 0 | 1290 | 645 | 0 | 159937.0926 | 9.3713 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-14 23:30 | 9.1 | 6.7 | 237.5 | 1120 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 160582.0926 | 9.4091 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-15 00:30 | 8.8 | 5.4 | 220 | 340 | 730 | 410 | 0 | 410 | 205 | 0 | 160787.0926 | 9.4211 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-09-15 01:30 | 8.7 | 4.4 | 200 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 160538.9444 | 9.4066 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-09-15 02:30 | 8.7 | 3.6 | 170 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 159913.0185 | 9.3699 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-09-15 03:30 | 8.5 | 3 | 112.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 159201.9074 | 9.3282 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-09-15 04:30 | 8.1 | 3.8 | 52.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 158490.7963 | 9.2866 | 0 |  |  | 0 | 0 | 1 | 2
Lerwick | 1978-09-15 05:30 | 7.6 | 6.3 | 22.5 | 760 | 380 | 60 | 0 | 60 | 30 | 0 | 158520.7963 | 9.2883 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-15 06:30 | 7.6 | 7.9 | 182.5 | 1840 | 1300 | 980 | 0 | 980 | 490 | 0 | 159010.7963 | 9.317 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-15 07:30 | 7.6 | 7.9 | 340 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 159655.7963 | 9.3548 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-15 08:30 | 7.6 | 7.9 | 320 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 160300.7963 | 9.3926 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-15 09:30 | 8.5 | 8.7 | 302.5 | 2560 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 160945.7963 | 9.4304 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-15 10:30 | 9.5 | 9.5 | 292.5 | 3280 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 161590.7963 | 9.4682 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-15 11:30 | 10 | 9.8 | 290 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 162235.7963 | 9.506 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-15 12:30 | 10.4 | 9.8 | 290 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 162880.7963 | 9.5438 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-15 13:30 | 10.8 | 9.8 | 287.5 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 163525.7963 | 9.5816 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-15 14:30 | 10.7 | 10 | 280 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 164170.7963 | 9.6194 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-15 15:30 | 10.6 | 9.9 | 275 | 3280 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 164815.7963 | 9.6572 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-15 16:30 | 10.7 | 8.5 | 272.5 | 2560 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 165460.7963 | 9.695 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-15 17:30 | 10.5 | 7.2 | 262.5 | 1480 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 166105.7963 | 9.7328 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-15 18:30 | 10.2 | 7 | 255 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 166685.7963 | 9.7667 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-15 19:30 | 9.8 | 6.7 | 252.5 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 167175.7963 | 9.7955 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-15 20:30 | 9.6 | 6.3 | 242.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 167485.7963 | 9.8136 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-15 21:30 | 9.4 | 6.2 | 232.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 167705.7963 | 9.8265 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-15 22:30 | 9.2 | 6.3 | 227.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 167925.7963 | 9.8394 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-15 23:30 | 9.2 | 7 | 220 | 1480 | 1120 | 800 | 0 | 800 | 400 | 0 | 168325.7963 | 9.8628 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-16 00:30 | 9.4 | 7.9 | 207.5 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 168970.7963 | 9.9006 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-16 01:30 | 9.2 | 8.1 | 192.5 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 169615.7963 | 9.9384 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-16 02:30 | 9 | 9 | 180 | 2920 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 170260.7963 | 9.9762 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-16 03:30 | 8.9 | 10.7 | 175 | 4000 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170260.7963 | 9.9762 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-16 04:30 | 9.2 | 11.7 | 182.5 | 4472.2222 | 4236.1111 | 3916.1111 | 0 | 1290 | 0 | 0 | 170260.7963 | 9.9762 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-16 05:30 | 9.5 | 12.5 | 197.5 | 4600 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170260.7963 | 9.9762 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-16 06:30 | 10.3 | 13.2 | 210 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170260.7963 | 9.9762 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-16 07:30 | 11.2 | 13.1 | 217.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170260.7963 | 9.9762 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-16 08:30 | 11.7 | 12.9 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170260.7963 | 9.9762 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-16 09:30 | 12 | 12.9 | 217.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170260.7963 | 9.9762 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-16 10:30 | 12 | 12.7 | 212.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170260.7963 | 9.9762 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-16 11:30 | 12.2 | 11.7 | 202.5 | 4472.2222 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170260.7963 | 9.9762 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-16 12:30 | 12.7 | 10.5 | 187.5 | 4000 | 4236.1111 | 3916.1111 | 0 | 1290 | 0 | 0 | 170260.7963 | 9.9762 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-16 13:30 | 12.3 | 10.9 | 180 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170260.7963 | 9.9762 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-16 14:30 | 11.8 | 13.3 | 182.5 | 4600 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170260.7963 | 9.9762 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-16 15:30 | 12.2 | 16.3 | 190 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170260.7963 | 9.9762 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-16 16:30 | 12.3 | 20.7 | 200 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170260.7963 | 9.9762 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-16 17:30 | 11.8 | 26.5 | 207.5 | 0 | 2300 | 1980 | 0 | 1290 | 0 | 0 | 170260.7963 | 9.9762 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-09-16 18:30 | 10.6 | 29.2 | 215 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 169549.6852 | 9.9346 | 0 |  |  | 1 | 2 | 1 | 1
Lerwick | 1978-09-16 19:30 | 10.1 | 27.9 | 227.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168838.5741 | 9.8929 | 0 |  |  | 1 | 3 | 1 | 2
Lerwick | 1978-09-16 20:30 | 10.4 | 25.7 | 242.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168127.463 | 9.8512 | 0 |  |  | 0 | 0 | 1 | 3
Lerwick | 1978-09-16 21:30 | 10.4 | 24.1 | 257.5 | 4600 | 2300 | 1980 | 0 | 1290 | 645 | 0 | 168772.463 | 9.889 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-16 22:30 | 9.8 | 23.3 | 267.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 169417.463 | 9.9268 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-16 23:30 | 9.3 | 22.3 | 270 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-17 00:30 | 9.4 | 20.8 | 270 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-17 01:30 | 9.3 | 19 | 272.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-17 02:30 | 8.6 | 17.3 | 277.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-17 03:30 | 8.2 | 16.4 | 280 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-17 04:30 | 8.2 | 15.7 | 280 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-17 05:30 | 8 | 15 | 280 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-17 06:30 | 8 | 14.1 | 280 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-17 07:30 | 7.4 | 12.9 | 280 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-17 08:30 | 6.7 | 12.7 | 280 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-17 09:30 | 7.3 | 13.5 | 280 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-17 10:30 | 8.4 | 14.3 | 280 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-17 11:30 | 9 | 14.8 | 277.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-17 12:30 | 9.3 | 14.9 | 272.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-17 13:30 | 9.6 | 14.8 | 270 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-17 14:30 | 10 | 14.5 | 270 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-17 15:30 | 10.4 | 14.3 | 270 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-17 16:30 | 10 | 13.8 | 270 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-17 17:30 | 9.4 | 13.1 | 270 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-17 18:30 | 9.2 | 12.7 | 270 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-17 19:30 | 9 | 12.4 | 270 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-17 20:30 | 9 | 12.2 | 270 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-17 21:30 | 9.2 | 11.9 | 270 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-17 22:30 | 9.4 | 11.5 | 270 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-17 23:30 | 9.6 | 10.9 | 270 | 4000 | 4236.1111 | 3916.1111 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-18 00:30 | 9.6 | 10.5 | 270 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-18 01:30 | 9.5 | 10.9 | 270 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-18 02:30 | 9.4 | 11 | 267.5 | 4300 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-18 03:30 | 9.4 | 10.8 | 262.5 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-18 04:30 | 9.6 | 11.4 | 260 | 4300 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-18 05:30 | 9.6 | 11.7 | 260 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-18 06:30 | 9.3 | 11 | 260 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-18 07:30 | 9.3 | 10.4 | 260 | 3640 | 3970 | 3650 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-18 08:30 | 9.5 | 10.8 | 260 | 4000 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-18 09:30 | 9.8 | 11.5 | 262.5 | 4472.2222 | 4236.1111 | 3916.1111 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-18 10:30 | 9.9 | 10.4 | 272.5 | 3640 | 4056.1111 | 3736.1111 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-18 11:30 | 9.9 | 7.6 | 292.5 | 1840 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-18 12:30 | 9.9 | 6 | 315 | 760 | 1300 | 980 | 0 | 980 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-18 13:30 | 9.5 | 5.9 | 327.5 | 500 | 630 | 310 | 0 | 310 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-18 14:30 | 9 | 5.9 | 325 | 500 | 500 | 180 | 0 | 180 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-18 15:30 | 8.8 | 5.9 | 315 | 500 | 500 | 180 | 0 | 180 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-18 16:30 | 8.7 | 5.4 | 310 | 340 | 420 | 100 | 0 | 100 | 0 | 0 | 170062.463 | 9.9646 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-09-18 17:30 | 8.3 | 4.7 | 310 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 169950.6111 | 9.958 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-09-18 18:30 | 7.9 | 4.7 | 307.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 169682.463 | 9.9423 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-18 19:30 | 7.1 | 6 | 305 | 760 | 479.6667 | 159.6667 | 0 | 159.6667 | 79.8333 | 0 | 169762.2963 | 9.947 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-18 20:30 | 6.6 | 7.1 | 310 | 1480 | 1120 | 800 | 0 | 800 | 400 | 0 | 170162.2963 | 9.9704 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-18 21:30 | 6.7 | 6.5 | 315 | 1120 | 1300 | 980 | 0 | 980 | 0 | 0 | 170162.2963 | 9.9704 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-18 22:30 | 6.4 | 5.8 | 312.5 | 500 | 810 | 490 | 0 | 490 | 0 | 0 | 170162.2963 | 9.9704 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-18 23:30 | 6.3 | 5.8 | 312.5 | 500 | 500 | 180 | 0 | 180 | 0 | 0 | 170162.2963 | 9.9704 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-19 00:30 | 6.8 | 6 | 317.5 | 760 | 630 | 310 | 0 | 310 | 0 | 0 | 170162.2963 | 9.9704 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-19 01:30 | 7 | 5.9 | 320 | 500 | 630 | 310 | 0 | 310 | 0 | 0 | 170162.2963 | 9.9704 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-19 02:30 | 6.5 | 4.8 | 317.5 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 0 | 0 | 170162.2963 | 9.9704 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-09-19 03:30 | 6.2 | 3.8 | 312.5 | 0 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 169672.6667 | 9.9418 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-09-19 04:30 | 6.2 | 3.4 | 315 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168961.5556 | 9.9001 | 0 |  |  | 1 | 3 | 1 | 1
Lerwick | 1978-09-19 05:30 | 6.1 | 3.2 | 325 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168250.4444 | 9.8584 | 0 |  |  | 1 | 4 | 1 | 2
Lerwick | 1978-09-19 06:30 | 5.8 | 3.1 | 330 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167539.3333 | 9.8168 | 0 |  |  | 1 | 5 | 1 | 3
Lerwick | 1978-09-19 07:30 | 6 | 3.2 | 325 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166828.2222 | 9.7751 | 0 |  |  | 1 | 6 | 1 | 4
Lerwick | 1978-09-19 08:30 | 6.9 | 3.6 | 320 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166117.1111 | 9.7334 | 0 |  |  | 1 | 7 | 1 | 5
Lerwick | 1978-09-19 09:30 | 7.9 | 3.9 | 327.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165406 | 9.6918 | 0 |  |  | 1 | 8 | 1 | 6
Lerwick | 1978-09-19 10:30 | 8.7 | 4 | 335 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 164780.0741 | 9.6551 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-09-19 11:30 | 8.9 | 4 | 330 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 164239.3333 | 9.6234 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-09-19 12:30 | 8.8 | 4.2 | 320 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 163698.5926 | 9.5917 | 1 |  |  | 1 | 11 | 0 | 0
Lerwick | 1978-09-19 13:30 | 9.2 | 4.4 | 312.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 163157.8519 | 9.56 | 1 |  |  | 1 | 12 | 0 | 0
Lerwick | 1978-09-19 14:30 | 9.2 | 4.4 | 307.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 162617.1111 | 9.5283 | 1 |  |  | 1 | 13 | 0 | 0
Lerwick | 1978-09-19 15:30 | 8.1 | 4.1 | 300 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 162076.3704 | 9.4967 | 1 |  |  | 1 | 14 | 0 | 0
Lerwick | 1978-09-19 16:30 | 7.5 | 3.7 | 297.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 161450.4444 | 9.46 | 1 |  |  | 1 | 15 | 0 | 0
Lerwick | 1978-09-19 17:30 | 7.6 | 3.4 | 300 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160739.3333 | 9.4183 | 0 |  |  | 1 | 16 | 1 | 1
Lerwick | 1978-09-19 18:30 | 7 | 3 | 290 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160028.2222 | 9.3767 | 0 |  |  | 1 | 17 | 1 | 2
Lerwick | 1978-09-19 19:30 | 6.3 | 2.7 | 270 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 159317.1111 | 9.335 | 0 |  |  | 1 | 18 | 1 | 3
Lerwick | 1978-09-19 20:30 | 5.8 | 3 | 250 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 158606 | 9.2933 | 0 |  |  | 1 | 19 | 1 | 4
Lerwick | 1978-09-19 21:30 | 5.3 | 3.6 | 232.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 157894.8889 | 9.2517 | 0 |  |  | 1 | 20 | 1 | 5
Lerwick | 1978-09-19 22:30 | 5.7 | 4.7 | 225 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 157405.2593 | 9.223 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-19 23:30 | 7.1 | 6 | 225 | 760 | 479.6667 | 159.6667 | 0 | 159.6667 | 79.8333 | 0 | 157485.0926 | 9.2276 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-20 00:30 | 8.4 | 6.9 | 225 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 157795.0926 | 9.2458 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-20 01:30 | 9 | 7.2 | 227.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 158285.0926 | 9.2745 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-20 02:30 | 9.4 | 7.6 | 230 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 158930.0926 | 9.3123 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-20 03:30 | 9.7 | 9.4 | 227.5 | 2920 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 159575.0926 | 9.3501 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-20 04:30 | 9.8 | 11.6 | 225 | 4472.2222 | 3696.1111 | 3376.1111 | 0 | 1290 | 645 | 0 | 160220.0926 | 9.3879 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-20 05:30 | 9.8 | 12.4 | 225 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 645 | 0 | 160865.0926 | 9.4257 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-20 06:30 | 9.6 | 12.4 | 225 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 161510.0926 | 9.4635 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-20 07:30 | 9.7 | 12.4 | 227.5 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 162155.0926 | 9.5013 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-20 08:30 | 10.1 | 12.5 | 235 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 645 | 0 | 162800.0926 | 9.5391 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-20 09:30 | 10.7 | 12.7 | 250 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 163445.0926 | 9.5769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-20 10:30 | 11 | 12.7 | 267.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 164090.0926 | 9.6147 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-20 11:30 | 10.8 | 11.7 | 280 | 4472.2222 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 164735.0926 | 9.6524 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-20 12:30 | 10.5 | 10.6 | 287.5 | 4000 | 4236.1111 | 3916.1111 | 0 | 1290 | 645 | 0 | 165380.0926 | 9.6902 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-20 13:30 | 10.5 | 10.3 | 287.5 | 3640 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 166025.0926 | 9.728 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-20 14:30 | 10.4 | 10 | 282.5 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 166670.0926 | 9.7658 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-20 15:30 | 10.3 | 9.6 | 280 | 3280 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 167315.0926 | 9.8036 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-20 16:30 | 10.4 | 9.4 | 282.5 | 2920 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 167960.0926 | 9.8414 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-20 17:30 | 10.3 | 9 | 287.5 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 168605.0926 | 9.8792 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-20 18:30 | 9.8 | 8.8 | 290 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 169250.0926 | 9.917 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-20 19:30 | 9.6 | 8.6 | 287.5 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 169895.0926 | 9.9548 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-20 20:30 | 9.6 | 8.3 | 285 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 170540.0926 | 9.9926 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-20 21:30 | 9.7 | 8.4 | 290 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170540.0926 | 9.9926 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-20 22:30 | 9.6 | 8.6 | 297.5 | 2560 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170540.0926 | 9.9926 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-20 23:30 | 9.2 | 7.8 | 300 | 1840 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170540.0926 | 9.9926 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-21 00:30 | 9 | 6.8 | 300 | 1120 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170540.0926 | 9.9926 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-21 01:30 | 8.8 | 5.9 | 300 | 500 | 810 | 490 | 0 | 490 | 0 | 0 | 170540.0926 | 9.9926 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-21 02:30 | 8.2 | 4.9 | 302.5 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 0 | 0 | 170540.0926 | 9.9926 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-09-21 03:30 | 7.8 | 4.2 | 310 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 170135.6481 | 9.9689 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-09-21 04:30 | 7.7 | 3.5 | 315 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 169509.7222 | 9.9322 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-09-21 05:30 | 7.7 | 2.9 | 307.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168798.6111 | 9.8905 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-09-21 06:30 | 7.7 | 2.4 | 297.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168087.5 | 9.8489 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-09-21 07:30 | 7.8 | 1.4 | 312.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167376.3889 | 9.8072 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-09-21 08:30 | 8 | 0.6 | 202.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166665.2778 | 9.7655 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-09-21 09:30 | 8.2 | 1 | 115 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165954.1667 | 9.7239 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-09-21 10:30 | 8.4 | 2.1 | 157.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165243.0556 | 9.6822 | 0 |  |  | 1 | 9 | 1 | 6
Lerwick | 1978-09-21 11:30 | 8.5 | 3.5 | 162.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164531.9444 | 9.6405 | 0 |  |  | 1 | 10 | 1 | 7
Lerwick | 1978-09-21 12:30 | 8.5 | 4.9 | 172.5 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 164042.3148 | 9.6119 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-21 13:30 | 8.8 | 6 | 192.5 | 760 | 479.6667 | 159.6667 | 0 | 159.6667 | 79.8333 | 0 | 164122.1481 | 9.6165 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-21 14:30 | 9.8 | 7.4 | 215 | 1480 | 1120 | 800 | 0 | 800 | 400 | 0 | 164522.1481 | 9.64 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-21 15:30 | 11 | 8.4 | 227.5 | 2200 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 165167.1481 | 9.6778 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-21 16:30 | 11.4 | 8.9 | 227.5 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 165812.1481 | 9.7156 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-21 17:30 | 11.4 | 9.2 | 220 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 166457.1481 | 9.7533 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-21 18:30 | 11.4 | 9.7 | 212.5 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 167102.1481 | 9.7911 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-21 19:30 | 11.4 | 10.4 | 210 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 167747.1481 | 9.8289 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-21 20:30 | 11.7 | 11 | 212.5 | 4300 | 3970 | 3650 | 0 | 1290 | 645 | 0 | 168392.1481 | 9.8667 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-21 21:30 | 11.7 | 11.1 | 217.5 | 4300 | 4300 | 3980 | 0 | 1290 | 645 | 0 | 169037.1481 | 9.9045 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-21 22:30 | 11.5 | 11.4 | 222.5 | 4300 | 4300 | 3980 | 0 | 1290 | 645 | 0 | 169682.1481 | 9.9423 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-21 23:30 | 11.5 | 12.1 | 230 | 4536.1111 | 4418.0556 | 4098.0556 | 0 | 1290 | 645 | 0 | 170327.1481 | 9.9801 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-22 00:30 | 11.7 | 12.5 | 237.5 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170327.1481 | 9.9801 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-22 01:30 | 11.6 | 12.8 | 237.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170327.1481 | 9.9801 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-22 02:30 | 11.3 | 13.1 | 232.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170327.1481 | 9.9801 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-22 03:30 | 11.1 | 12.7 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170327.1481 | 9.9801 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-22 04:30 | 11 | 12.2 | 232.5 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170327.1481 | 9.9801 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-22 05:30 | 11 | 12 | 237.5 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170327.1481 | 9.9801 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-22 06:30 | 11 | 11.7 | 240 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170327.1481 | 9.9801 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-22 07:30 | 10.8 | 11.2 | 242.5 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170327.1481 | 9.9801 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-22 08:30 | 10.7 | 10.5 | 250 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170327.1481 | 9.9801 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-22 09:30 | 10.9 | 9 | 265 | 2920 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170327.1481 | 9.9801 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-22 10:30 | 11 | 7.3 | 290 | 1480 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170327.1481 | 9.9801 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-22 11:30 | 11.1 | 6.4 | 317.5 | 760 | 1120 | 800 | 0 | 800 | 0 | 0 | 170327.1481 | 9.9801 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-22 12:30 | 11.5 | 5.9 | 335 | 500 | 630 | 310 | 0 | 310 | 0 | 0 | 170327.1481 | 9.9801 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-22 13:30 | 12 | 5.9 | 330 | 500 | 500 | 180 | 0 | 180 | 0 | 0 | 170327.1481 | 9.9801 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-22 14:30 | 12.1 | 6.3 | 315 | 760 | 630 | 310 | 0 | 310 | 0 | 0 | 170327.1481 | 9.9801 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-22 15:30 | 11.5 | 6.1 | 320 | 760 | 760 | 440 | 0 | 440 | 0 | 0 | 170327.1481 | 9.9801 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-22 16:30 | 10.7 | 5.4 | 332.5 | 340 | 550 | 230 | 0 | 230 | 0 | 0 | 170327.1481 | 9.9801 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-09-22 17:30 | 10.2 | 4.2 | 337.5 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 170079 | 9.9656 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-09-22 18:30 | 10 | 3.3 | 170 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 169453.0741 | 9.9289 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-09-22 19:30 | 9.9 | 3.1 | 10 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168741.963 | 9.8872 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-09-22 20:30 | 9.7 | 3.1 | 35 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168030.8519 | 9.8456 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-09-22 21:30 | 9.4 | 2.6 | 77.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167319.7407 | 9.8039 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-09-22 22:30 | 9.3 | 1.5 | 125 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166608.6296 | 9.7622 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-09-22 23:30 | 9.2 | 1.2 | 157.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165897.5185 | 9.7206 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-09-23 00:30 | 9.1 | 1.6 | 180 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165186.4074 | 9.6789 | 0 |  |  | 1 | 9 | 1 | 6
Lerwick | 1978-09-23 01:30 | 9 | 1.9 | 177.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164475.2963 | 9.6372 | 0 |  |  | 1 | 10 | 1 | 7
Lerwick | 1978-09-23 02:30 | 8.7 | 2.6 | 160 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163764.1852 | 9.5956 | 0 |  |  | 1 | 11 | 1 | 8
Lerwick | 1978-09-23 03:30 | 8.6 | 3.7 | 162.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163053.0741 | 9.5539 | 0 |  |  | 1 | 12 | 1 | 9
Lerwick | 1978-09-23 04:30 | 8.7 | 5 | 170 | 340 | 170 | 0 | 150 | 0 | 0 | 333.3333 | 162719.7407 | 9.5344 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-23 05:30 | 8.9 | 5.9 | 172.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 162769.7407 | 9.5373 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-23 06:30 | 9.2 | 6.7 | 182.5 | 1120 | 810 | 490 | 0 | 490 | 245 | 0 | 163014.7407 | 9.5516 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-23 07:30 | 9.7 | 7.6 | 205 | 1840 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 163594.7407 | 9.5856 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-23 08:30 | 10.6 | 7.9 | 230 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 164239.7407 | 9.6234 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-23 09:30 | 11.4 | 7.2 | 237.5 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 164884.7407 | 9.6612 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-23 10:30 | 11.3 | 6.4 | 232.5 | 760 | 1120 | 800 | 0 | 800 | 400 | 0 | 165284.7407 | 9.6847 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-23 11:30 | 11.1 | 6.2 | 232.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 165504.7407 | 9.6975 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-23 12:30 | 11 | 6 | 237.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 165724.7407 | 9.7104 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-23 13:30 | 11 | 5.9 | 237.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 165879.7407 | 9.7195 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-23 14:30 | 11 | 6.3 | 230 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 166034.7407 | 9.7286 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-23 15:30 | 11 | 6.7 | 222.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 166344.7407 | 9.7468 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-23 16:30 | 10.9 | 6.7 | 217.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 166744.7407 | 9.7702 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-23 17:30 | 10.8 | 6.8 | 207.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 167144.7407 | 9.7936 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-23 18:30 | 10.8 | 7 | 192.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 167634.7407 | 9.8223 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-23 19:30 | 10.6 | 7.5 | 182.5 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 168279.7407 | 9.8601 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-23 20:30 | 10.2 | 8.6 | 180 | 2560 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 168924.7407 | 9.8979 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-23 21:30 | 10 | 9.8 | 180 | 3280 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 169569.7407 | 9.9357 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-23 22:30 | 10.2 | 10.8 | 182.5 | 4000 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-23 23:30 | 10.4 | 12.2 | 195 | 4536.1111 | 4268.0556 | 3948.0556 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-24 00:30 | 10.6 | 13.2 | 215 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-24 01:30 | 10.9 | 11.9 | 232.5 | 4472.2222 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-24 02:30 | 10.9 | 9.6 | 242.5 | 3280 | 3876.1111 | 3556.1111 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-24 03:30 | 10.4 | 8.9 | 245 | 2560 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-24 04:30 | 10 | 9 | 245 | 2920 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-24 05:30 | 9.7 | 8.9 | 245 | 2560 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-24 06:30 | 9.2 | 8.8 | 247.5 | 2560 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-24 07:30 | 9.4 | 9 | 247.5 | 2920 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-24 08:30 | 10.1 | 9.5 | 242.5 | 3280 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-24 09:30 | 10.6 | 9.8 | 240 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-24 10:30 | 11.4 | 10.1 | 240 | 3640 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-24 11:30 | 12 | 10.7 | 237.5 | 4000 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-24 12:30 | 12.1 | 10.6 | 232.5 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-24 13:30 | 11.9 | 10.3 | 232.5 | 3640 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-24 14:30 | 11.3 | 10.3 | 237.5 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-24 15:30 | 11.2 | 9.8 | 240 | 3280 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-24 16:30 | 11.2 | 8.9 | 237.5 | 2560 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-24 17:30 | 10.6 | 8.2 | 232.5 | 2200 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-24 18:30 | 10 | 8 | 232.5 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-24 19:30 | 9.5 | 8 | 235 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-24 20:30 | 9.1 | 8.1 | 235 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-24 21:30 | 9 | 8.4 | 237.5 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-24 22:30 | 9 | 9 | 240 | 2920 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-24 23:30 | 8.8 | 8.9 | 237.5 | 2560 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-25 00:30 | 8.7 | 8.2 | 235 | 2200 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-25 01:30 | 8.5 | 7.8 | 237.5 | 1840 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-25 02:30 | 8.6 | 7.4 | 240 | 1480 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-25 03:30 | 8.4 | 7.4 | 240 | 1480 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-25 04:30 | 8.3 | 7.8 | 237.5 | 1840 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-25 05:30 | 8.6 | 7.8 | 235 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-25 06:30 | 8.4 | 7.8 | 237.5 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-25 07:30 | 8.3 | 8 | 237.5 | 2200 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-25 08:30 | 8.8 | 8 | 235 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-25 09:30 | 9.8 | 8 | 235 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-25 10:30 | 9.3 | 7.8 | 230 | 1840 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-25 11:30 | 8.1 | 7.9 | 232.5 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-25 12:30 | 7.9 | 8.8 | 245 | 2560 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-25 13:30 | 7.3 | 10.1 | 247.5 | 3640 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-25 14:30 | 8.2 | 10.5 | 245 | 4000 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-25 15:30 | 9.7 | 9.8 | 240 | 3280 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-25 16:30 | 9.3 | 9.4 | 232.5 | 2920 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-25 17:30 | 8.6 | 9.4 | 230 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-25 18:30 | 8.3 | 9 | 230 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-25 19:30 | 8.4 | 8.9 | 235 | 2560 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-25 20:30 | 8.4 | 8.9 | 242.5 | 2560 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-25 21:30 | 8.3 | 8.9 | 245 | 2560 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-25 22:30 | 8.2 | 9 | 247.5 | 2920 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-25 23:30 | 7.9 | 8.7 | 250 | 2560 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-26 00:30 | 7.7 | 7.8 | 247.5 | 1840 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-26 01:30 | 8.1 | 6.8 | 242.5 | 1120 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-26 02:30 | 8.6 | 6.8 | 240 | 1120 | 1120 | 800 | 0 | 800 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-26 03:30 | 8.7 | 6.8 | 237.5 | 1120 | 1120 | 800 | 0 | 800 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-26 04:30 | 8.4 | 5.7 | 230 | 500 | 810 | 490 | 0 | 490 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-26 05:30 | 8.2 | 5.2 | 222.5 | 340 | 420 | 100 | 0 | 100 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-26 06:30 | 8.2 | 5.1 | 222.5 | 340 | 340 | 20 | 0 | 20 | 0 | 0 | 170214.7407 | 9.9735 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-09-26 07:30 | 7.5 | 4.6 | 235 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 170102.8889 | 9.967 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-09-26 08:30 | 7.3 | 4.6 | 245 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 169834.7407 | 9.9513 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-09-26 09:30 | 7.7 | 5.1 | 237.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 169722.8889 | 9.9447 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-26 10:30 | 8.6 | 5.6 | 232.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 169772.8889 | 9.9476 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-26 11:30 | 10.2 | 6.3 | 235 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 169927.8889 | 9.9567 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-26 12:30 | 10.8 | 6.9 | 230 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 170237.8889 | 9.9749 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-26 13:30 | 10.6 | 7.1 | 220 | 1480 | 1300 | 980 | 0 | 980 | 0 | 0 | 170237.8889 | 9.9749 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-26 14:30 | 10.5 | 6.7 | 212.5 | 1120 | 1300 | 980 | 0 | 980 | 0 | 0 | 170237.8889 | 9.9749 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-26 15:30 | 10 | 5.7 | 210 | 500 | 810 | 490 | 0 | 490 | 0 | 0 | 170237.8889 | 9.9749 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-09-26 16:30 | 9.5 | 4 | 210 | 76.6667 | 288.3333 | 0 | 31.6667 | 0 | 0 | 70.3704 | 170167.5185 | 9.9708 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-09-26 17:30 | 9.2 | 2.6 | 217.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 169541.5926 | 9.9341 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-09-26 18:30 | 8.4 | 2.7 | 240 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168830.4815 | 9.8924 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-09-26 19:30 | 8 | 3.6 | 265 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168119.3704 | 9.8507 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-09-26 20:30 | 8 | 3.7 | 275 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167408.2593 | 9.8091 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-09-26 21:30 | 8.1 | 3.4 | 270 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166697.1481 | 9.7674 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-09-26 22:30 | 8.1 | 3.2 | 260 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165986.037 | 9.7257 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-09-26 23:30 | 7.5 | 3.2 | 252.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165274.9259 | 9.6841 | 0 |  |  | 1 | 9 | 1 | 6
Lerwick | 1978-09-27 00:30 | 7 | 3.6 | 250 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164563.8148 | 9.6424 | 0 |  |  | 1 | 10 | 1 | 7
Lerwick | 1978-09-27 01:30 | 7 | 3.9 | 252.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163852.7037 | 9.6007 | 0 |  |  | 1 | 11 | 1 | 8
Lerwick | 1978-09-27 02:30 | 7 | 3.7 | 260 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163141.5926 | 9.5591 | 0 |  |  | 1 | 12 | 1 | 9
Lerwick | 1978-09-27 03:30 | 7.3 | 3.3 | 265 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162430.4815 | 9.5174 | 0 |  |  | 1 | 13 | 1 | 10
Lerwick | 1978-09-27 04:30 | 7.4 | 2.6 | 262.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161719.3704 | 9.4757 | 0 |  |  | 1 | 14 | 1 | 11
Lerwick | 1978-09-27 05:30 | 6.7 | 1.9 | 262.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161008.2593 | 9.4341 | 0 |  |  | 1 | 15 | 1 | 12
Lerwick | 1978-09-27 06:30 | 6.5 | 2 | 267.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160297.1481 | 9.3924 | 0 |  |  | 1 | 16 | 1 | 13
Lerwick | 1978-09-27 07:30 | 7 | 2.6 | 275 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 159586.037 | 9.3507 | 0 |  |  | 1 | 17 | 1 | 14
Lerwick | 1978-09-27 08:30 | 7.6 | 3.7 | 290 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 158874.9259 | 9.3091 | 0 |  |  | 1 | 18 | 1 | 15
Lerwick | 1978-09-27 09:30 | 8.5 | 4.7 | 305 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 158385.2963 | 9.2804 | 1 |  |  | 1 | 19 | 0 | 0
Lerwick | 1978-09-27 10:30 | 9.2 | 5 | 307.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 158273.4444 | 9.2738 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-27 11:30 | 9.3 | 5.2 | 302.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 158283.4444 | 9.2744 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-27 12:30 | 9.3 | 5.8 | 302.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 158333.4444 | 9.2774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-27 13:30 | 9.6 | 6.6 | 305 | 1120 | 810 | 490 | 0 | 490 | 245 | 0 | 158578.4444 | 9.2917 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-27 14:30 | 9.9 | 7.1 | 302.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 159068.4444 | 9.3204 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-27 15:30 | 9.6 | 7.4 | 300 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 159648.4444 | 9.3544 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-27 16:30 | 8.9 | 7.8 | 302.5 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 160293.4444 | 9.3922 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-27 17:30 | 8.4 | 7.8 | 302.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 160938.4444 | 9.43 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-27 18:30 | 7.8 | 7.4 | 295 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 161583.4444 | 9.4678 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-27 19:30 | 7.6 | 6.9 | 290 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 162073.4444 | 9.4965 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-27 20:30 | 7.5 | 6.5 | 290 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 162473.4444 | 9.5199 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-27 21:30 | 7.3 | 5.9 | 290 | 500 | 810 | 490 | 0 | 490 | 245 | 0 | 162718.4444 | 9.5343 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-27 22:30 | 7.3 | 4.9 | 290 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 162733.2778 | 9.5352 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-09-27 23:30 | 6.7 | 4 | 290 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 162328.8333 | 9.5115 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-09-28 00:30 | 6 | 3.3 | 290 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 161702.9074 | 9.4748 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-09-28 01:30 | 6.1 | 3.1 | 290 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160991.7963 | 9.4331 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-09-28 02:30 | 6.1 | 3.1 | 290 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160280.6852 | 9.3914 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-09-28 03:30 | 5.7 | 3.1 | 290 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 159569.5741 | 9.3498 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-09-28 04:30 | 6 | 3.1 | 292.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 158858.463 | 9.3081 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-09-28 05:30 | 6.2 | 2.6 | 300 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 158147.3519 | 9.2664 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-09-28 06:30 | 6 | 1.5 | 320 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 157436.2407 | 9.2248 | 0 |  |  | 1 | 9 | 1 | 6
Lerwick | 1978-09-28 07:30 | 5.6 | 0.6 | 200 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 156725.1296 | 9.1831 | 0 |  |  | 1 | 10 | 1 | 7
Lerwick | 1978-09-28 08:30 | 6.2 | 1.3 | 100 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 156014.0185 | 9.1414 | 0 |  |  | 1 | 11 | 1 | 8
Lerwick | 1978-09-28 09:30 | 8.2 | 2.8 | 140 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 155302.9074 | 9.0998 | 0 |  |  | 1 | 12 | 1 | 9
Lerwick | 1978-09-28 10:30 | 9.1 | 4 | 147.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 154676.9815 | 9.0631 | 1 |  |  | 1 | 13 | 0 | 0
Lerwick | 1978-09-28 11:30 | 9.1 | 5.1 | 147.5 | 340 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 154428.8333 | 9.0486 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-28 12:30 | 9.4 | 6.2 | 142.5 | 760 | 550 | 230 | 0 | 230 | 115 | 0 | 154543.8333 | 9.0553 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-28 13:30 | 9.5 | 7.2 | 140 | 1480 | 1120 | 800 | 0 | 800 | 400 | 0 | 154943.8333 | 9.0787 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-28 14:30 | 9 | 8.1 | 140 | 2200 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 155588.8333 | 9.1165 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-28 15:30 | 8.7 | 8.9 | 142.5 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 156233.8333 | 9.1543 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-28 16:30 | 8.5 | 9.6 | 145 | 3280 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 156878.8333 | 9.1921 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-28 17:30 | 8.4 | 10.4 | 142.5 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 157523.8333 | 9.2299 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-28 18:30 | 8.4 | 11 | 140 | 4300 | 3970 | 3650 | 0 | 1290 | 645 | 0 | 158168.8333 | 9.2677 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-28 19:30 | 8.5 | 11.4 | 140 | 4300 | 4300 | 3980 | 0 | 1290 | 645 | 0 | 158813.8333 | 9.3055 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-28 20:30 | 8.5 | 11.7 | 137.5 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 159458.8333 | 9.3433 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-28 21:30 | 8.4 | 12.2 | 132.5 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 645 | 0 | 160103.8333 | 9.3811 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-28 22:30 | 8.2 | 12.7 | 130 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 645 | 0 | 160748.8333 | 9.4189 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-28 23:30 | 8.1 | 13 | 127.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 161393.8333 | 9.4567 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-29 00:30 | 8.1 | 13.5 | 125 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 162038.8333 | 9.4945 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-29 01:30 | 8.1 | 14.1 | 127.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 162683.8333 | 9.5323 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-29 02:30 | 7.8 | 14.5 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 163328.8333 | 9.57 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-29 03:30 | 7.4 | 14.7 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 163973.8333 | 9.6078 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-29 04:30 | 7.3 | 14.4 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 164618.8333 | 9.6456 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-29 05:30 | 7.5 | 13.9 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 165263.8333 | 9.6834 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-29 06:30 | 7.7 | 13.3 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 165908.8333 | 9.7212 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-29 07:30 | 7.9 | 13.2 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 166553.8333 | 9.759 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-29 08:30 | 8 | 13.8 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 167198.8333 | 9.7968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-29 09:30 | 8.2 | 14.3 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 167843.8333 | 9.8346 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-29 10:30 | 8.3 | 14.3 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 168488.8333 | 9.8724 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-29 11:30 | 8.3 | 14.3 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 169133.8333 | 9.9102 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-29 12:30 | 8.4 | 14.6 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 169778.8333 | 9.948 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-29 13:30 | 8.6 | 14.5 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 170423.8333 | 9.9858 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-29 14:30 | 8.6 | 13.8 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170423.8333 | 9.9858 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-29 15:30 | 8.7 | 13.5 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170423.8333 | 9.9858 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-29 16:30 | 8.9 | 12.8 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170423.8333 | 9.9858 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-29 17:30 | 9.1 | 11.1 | 130 | 4300 | 4450 | 4130 | 0 | 1290 | 0 | 0 | 170423.8333 | 9.9858 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-29 18:30 | 9.4 | 10.4 | 130 | 3640 | 3970 | 3650 | 0 | 1290 | 0 | 0 | 170423.8333 | 9.9858 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-29 19:30 | 9.7 | 10.7 | 130 | 4000 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170423.8333 | 9.9858 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-29 20:30 | 9.7 | 11.2 | 130 | 4300 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170423.8333 | 9.9858 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-29 21:30 | 9.4 | 11.1 | 130 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170423.8333 | 9.9858 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-29 22:30 | 9.3 | 9.9 | 130 | 3280 | 3790 | 3470 | 0 | 1290 | 0 | 0 | 170423.8333 | 9.9858 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-29 23:30 | 9.3 | 8.1 | 125 | 2200 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170423.8333 | 9.9858 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-30 00:30 | 9.3 | 6.5 | 122.5 | 1120 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170423.8333 | 9.9858 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-30 01:30 | 9.2 | 5.9 | 130 | 500 | 810 | 490 | 0 | 490 | 0 | 0 | 170423.8333 | 9.9858 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-30 02:30 | 9.2 | 6.7 | 130 | 1120 | 810 | 490 | 0 | 490 | 0 | 0 | 170423.8333 | 9.9858 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-30 03:30 | 9.5 | 8.1 | 125 | 2200 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170423.8333 | 9.9858 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-30 04:30 | 9.4 | 8.6 | 125 | 2560 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170423.8333 | 9.9858 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-30 05:30 | 9.3 | 8.7 | 122.5 | 2560 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170423.8333 | 9.9858 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-30 06:30 | 9.5 | 9.4 | 120 | 2920 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170423.8333 | 9.9858 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-30 07:30 | 9.5 | 9.5 | 120 | 3280 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170423.8333 | 9.9858 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-30 08:30 | 9.5 | 8.9 | 120 | 2560 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170423.8333 | 9.9858 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-30 09:30 | 9.8 | 8.2 | 120 | 2200 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170423.8333 | 9.9858 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-30 10:30 | 10 | 7.7 | 120 | 1840 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170423.8333 | 9.9858 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-30 11:30 | 10.4 | 7.2 | 120 | 1480 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170423.8333 | 9.9858 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-30 12:30 | 10.9 | 6.7 | 120 | 1120 | 1300 | 980 | 0 | 980 | 0 | 0 | 170423.8333 | 9.9858 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-30 13:30 | 11.2 | 5.9 | 122.5 | 500 | 810 | 490 | 0 | 490 | 0 | 0 | 170423.8333 | 9.9858 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-09-30 14:30 | 11.2 | 4.6 | 122.5 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 0 | 0 | 170423.8333 | 9.9858 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-09-30 15:30 | 11 | 3 | 102.5 | 0 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 169934.2037 | 9.9571 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-09-30 16:30 | 10.7 | 1.7 | 60 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 169223.0926 | 9.9154 | 0 |  |  | 1 | 3 | 1 | 1
Lerwick | 1978-09-30 17:30 | 10 | 1.1 | 195 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168511.9815 | 9.8737 | 0 |  |  | 1 | 4 | 1 | 2
Lerwick | 1978-09-30 18:30 | 9.1 | 0.7 | 352.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167800.8704 | 9.8321 | 0 |  |  | 1 | 5 | 1 | 3
Lerwick | 1978-09-30 19:30 | 7.9 | 0.2 | 175 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167089.7593 | 9.7904 | 0 |  |  | 1 | 6 | 1 | 4
Lerwick | 1978-09-30 20:30 | 7.8 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166378.6481 | 9.7487 | 0 |  |  | 1 | 7 | 1 | 5
Lerwick | 1978-09-30 21:30 | 7 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165667.537 | 9.7071 | 0 |  |  | 1 | 8 | 1 | 6
Lerwick | 1978-09-30 22:30 | 5.8 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164956.4259 | 9.6654 | 0 |  |  | 1 | 9 | 1 | 7
Lerwick | 1978-09-30 23:30 | 5.7 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164245.3148 | 9.6237 | 0 |  |  | 1 | 10 | 1 | 8
Lerwick | 1978-10-01 00:30 | 5.2 | 0.2 | 142.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163534.2037 | 9.5821 | 0 |  |  | 1 | 11 | 1 | 9
Lerwick | 1978-10-01 01:30 | 4.6 | 0.7 | 247.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162823.0926 | 9.5404 | 0 |  |  | 1 | 12 | 1 | 10
Lerwick | 1978-10-01 02:30 | 5 | 1 | 207.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162111.9815 | 9.4987 | 0 |  |  | 1 | 13 | 1 | 11
Lerwick | 1978-10-01 03:30 | 5.3 | 1 | 202.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161400.8704 | 9.4571 | 0 |  |  | 1 | 14 | 1 | 12
Lerwick | 1978-10-01 04:30 | 5.2 | 1.1 | 202.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160689.7593 | 9.4154 | 0 |  |  | 1 | 15 | 1 | 13
Lerwick | 1978-10-01 05:30 | 5.2 | 1.5 | 205 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 159978.6481 | 9.3737 | 0 |  |  | 1 | 16 | 1 | 14
Lerwick | 1978-10-01 06:30 | 4.9 | 2.2 | 202.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 159267.537 | 9.3321 | 0 |  |  | 1 | 17 | 1 | 15
Lerwick | 1978-10-01 07:30 | 5.8 | 3.3 | 202.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 158556.4259 | 9.2904 | 0 |  |  | 1 | 18 | 1 | 16
Lerwick | 1978-10-01 08:30 | 7.5 | 4.9 | 207.5 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 158066.7963 | 9.2617 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-01 09:30 | 9.2 | 6.5 | 207.5 | 1120 | 659.6667 | 339.6667 | 0 | 339.6667 | 169.8333 | 0 | 158236.6296 | 9.2717 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-01 10:30 | 10.4 | 7.8 | 202.5 | 1840 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 158816.6296 | 9.3057 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-01 11:30 | 10.8 | 9.2 | 200 | 2920 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 159461.6296 | 9.3435 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-01 12:30 | 10.9 | 10.4 | 200 | 3640 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 160106.6296 | 9.3812 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-01 13:30 | 11.1 | 10.8 | 200 | 4000 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 160751.6296 | 9.419 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-01 14:30 | 10.9 | 10.8 | 200 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 161396.6296 | 9.4568 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-01 15:30 | 10.2 | 10.8 | 200 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 162041.6296 | 9.4946 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-01 16:30 | 9.9 | 11 | 197.5 | 4300 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 162686.6296 | 9.5324 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-01 17:30 | 9.7 | 11.9 | 192.5 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 163331.6296 | 9.5702 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-01 18:30 | 9.6 | 13 | 192.5 | 4600 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 163976.6296 | 9.608 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-01 19:30 | 9.5 | 14.1 | 200 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 164621.6296 | 9.6458 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-01 20:30 | 9.5 | 15 | 207.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 165266.6296 | 9.6836 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-01 21:30 | 9.4 | 15.1 | 210 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 165911.6296 | 9.7214 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-01 22:30 | 9.4 | 14.5 | 212.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 166556.6296 | 9.7592 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-01 23:30 | 9.7 | 13 | 227.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 167201.6296 | 9.797 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-02 00:30 | 9.8 | 10.4 | 247.5 | 3640 | 4120 | 3800 | 0 | 1290 | 645 | 0 | 167846.6296 | 9.8348 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-02 01:30 | 9.5 | 8.5 | 255 | 2560 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 168491.6296 | 9.8726 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-02 02:30 | 9.1 | 7.9 | 257.5 | 1840 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 169136.6296 | 9.9103 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-02 03:30 | 8.9 | 7.3 | 257.5 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 169781.6296 | 9.9481 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-02 04:30 | 8.5 | 6.8 | 252.5 | 1120 | 1300 | 980 | 0 | 980 | 490 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-02 05:30 | 8.3 | 6.7 | 252.5 | 1120 | 1120 | 800 | 0 | 800 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-02 06:30 | 8.4 | 6.7 | 255 | 1120 | 1120 | 800 | 0 | 800 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-02 07:30 | 8.4 | 6.7 | 250 | 1120 | 1120 | 800 | 0 | 800 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-02 08:30 | 8.7 | 7.1 | 247.5 | 1480 | 1300 | 980 | 0 | 980 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-02 09:30 | 8.9 | 7.7 | 255 | 1840 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-02 10:30 | 9.4 | 7.7 | 257.5 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-02 11:30 | 10 | 7.5 | 250 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-02 12:30 | 10.5 | 7.5 | 240 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-02 13:30 | 11.1 | 7.3 | 230 | 1480 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-02 14:30 | 11 | 7.2 | 220 | 1480 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-02 15:30 | 10.7 | 6.8 | 210 | 1120 | 1300 | 980 | 0 | 980 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-02 16:30 | 10.1 | 6 | 200 | 760 | 940 | 620 | 0 | 620 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-02 17:30 | 9.2 | 6 | 192.5 | 760 | 760 | 440 | 0 | 440 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-02 18:30 | 8.9 | 7.2 | 187.5 | 1480 | 1120 | 800 | 0 | 800 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-02 19:30 | 9 | 8.5 | 185 | 2560 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-02 20:30 | 9.1 | 9.4 | 187.5 | 2920 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-02 21:30 | 8.9 | 9.4 | 190 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-02 22:30 | 8.5 | 8.9 | 192.5 | 2560 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-02 23:30 | 8.6 | 9.5 | 197.5 | 3280 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-03 00:30 | 8.8 | 10.6 | 200 | 4000 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-03 01:30 | 8.9 | 11.4 | 202.5 | 4300 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-03 02:30 | 9.1 | 11.8 | 210 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-03 03:30 | 8.9 | 11.5 | 217.5 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-03 04:30 | 8.4 | 10.9 | 220 | 4000 | 4236.1111 | 3916.1111 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-03 05:30 | 7.8 | 10 | 222.5 | 3640 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-03 06:30 | 7.5 | 9.6 | 227.5 | 3280 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-03 07:30 | 7.3 | 10.6 | 227.5 | 4000 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-03 08:30 | 8 | 12 | 222.5 | 4536.1111 | 4268.0556 | 3948.0556 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-03 09:30 | 8.9 | 12.7 | 220 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-03 10:30 | 9 | 13.4 | 222.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-03 11:30 | 9.6 | 13.6 | 227.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-03 12:30 | 9.9 | 13.4 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-03 13:30 | 9.2 | 13.4 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-03 14:30 | 8.5 | 12.6 | 227.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-03 15:30 | 8.4 | 11.8 | 225 | 4472.2222 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-03 16:30 | 8.3 | 11.9 | 227.5 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-03 17:30 | 8.3 | 11.7 | 232.5 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-03 18:30 | 8 | 11.4 | 237.5 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-03 19:30 | 7.4 | 11.4 | 237.5 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-03 20:30 | 7.3 | 11.6 | 232.5 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-03 21:30 | 7.6 | 11.9 | 232.5 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-03 22:30 | 7.7 | 12.2 | 237.5 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-03 23:30 | 7.9 | 12.4 | 242.5 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-04 00:30 | 8 | 12.2 | 247.5 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-04 01:30 | 7.9 | 11.5 | 247.5 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-04 02:30 | 8.1 | 10.6 | 245 | 4000 | 4236.1111 | 3916.1111 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-04 03:30 | 7.4 | 10.4 | 247.5 | 3640 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-04 04:30 | 7 | 10.7 | 250 | 4000 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-04 05:30 | 7.1 | 11.1 | 250 | 4300 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-04 06:30 | 7 | 11.4 | 250 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-04 07:30 | 7.5 | 11.7 | 250 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-04 08:30 | 8 | 12.2 | 252.5 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-04 09:30 | 8.2 | 12.8 | 257.5 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-04 10:30 | 8.9 | 13.5 | 260 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-04 11:30 | 9.1 | 14 | 260 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-04 12:30 | 9.1 | 13.9 | 262.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-04 13:30 | 9.4 | 13.2 | 265 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-04 14:30 | 8.8 | 12.7 | 262.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-04 15:30 | 8.2 | 12.5 | 260 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-04 16:30 | 8.2 | 12.4 | 260 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-04 17:30 | 8.1 | 12.4 | 262.5 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-04 18:30 | 8 | 12.1 | 265 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-04 19:30 | 8 | 11.4 | 262.5 | 4300 | 4418.0556 | 4098.0556 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-04 20:30 | 8 | 10.7 | 260 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-04 21:30 | 8 | 10.1 | 260 | 3640 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-04 22:30 | 8 | 9.1 | 260 | 2920 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-04 23:30 | 7.9 | 7.7 | 257.5 | 1840 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-05 00:30 | 7.9 | 6.3 | 252.5 | 760 | 1300 | 980 | 0 | 980 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-05 01:30 | 7.6 | 4.5 | 247.5 | 199.3333 | 479.6667 | 159.6667 | 0 | 159.6667 | 0 | 0 | 170271.6296 | 9.9769 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-10-05 02:30 | 7.1 | 2 | 272.5 | 0 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 169782 | 9.9482 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-10-05 03:30 | 6.6 | 1.3 | 162.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 169070.8889 | 9.9065 | 0 |  |  | 1 | 3 | 1 | 1
Lerwick | 1978-10-05 04:30 | 6.3 | 2.8 | 47.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168359.7778 | 9.8648 | 0 |  |  | 1 | 4 | 1 | 2
Lerwick | 1978-10-05 05:30 | 6.1 | 4.4 | 77.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 167733.8519 | 9.8282 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-10-05 06:30 | 6.2 | 5.5 | 82.5 | 500 | 288.3333 | 0 | 31.6667 | 0 | 0 | 70.3704 | 167663.4815 | 9.824 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-05 07:30 | 6.6 | 6.3 | 80 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 167818.4815 | 9.8331 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-05 08:30 | 6.7 | 6.1 | 82.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 168038.4815 | 9.846 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-05 09:30 | 6.9 | 5.6 | 87.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 168193.4815 | 9.8551 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-05 10:30 | 7.1 | 5.2 | 92.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 168243.4815 | 9.858 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-10-05 11:30 | 7.3 | 4.9 | 100 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 168131.6296 | 9.8515 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-10-05 12:30 | 7.7 | 4.7 | 107.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 167863.4815 | 9.8358 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-10-05 13:30 | 8 | 4.4 | 110 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 167459.037 | 9.8121 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-10-05 14:30 | 8 | 4.2 | 110 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 166918.2963 | 9.7804 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-10-05 15:30 | 8 | 4.2 | 107.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 166377.5556 | 9.7487 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-10-05 16:30 | 8 | 4.9 | 102.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 165973.1111 | 9.725 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-10-05 17:30 | 7.9 | 5.2 | 105 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 165861.2593 | 9.7184 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-10-05 18:30 | 7.8 | 4.7 | 117.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 165749.4074 | 9.7119 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-10-05 19:30 | 7.9 | 4.1 | 130 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 165344.963 | 9.6882 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-10-05 20:30 | 8 | 3.3 | 137.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 164719.037 | 9.6515 | 1 |  |  | 1 | 11 | 0 | 0
Lerwick | 1978-10-05 21:30 | 8.3 | 3.3 | 170 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164007.9259 | 9.6098 | 0 |  |  | 1 | 12 | 1 | 1
Lerwick | 1978-10-05 22:30 | 8.5 | 5.4 | 230 | 340 | 170 | 0 | 150 | 0 | 0 | 333.3333 | 163674.5926 | 9.5903 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-05 23:30 | 9.3 | 7.7 | 262.5 | 1840 | 1090 | 770 | 0 | 770 | 385 | 0 | 164059.5926 | 9.6129 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-06 00:30 | 10.2 | 8.7 | 267.5 | 2560 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 164704.5926 | 9.6507 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-06 01:30 | 10.4 | 9.4 | 270 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 165349.5926 | 9.6885 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-06 02:30 | 10.1 | 10 | 270 | 3640 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 165994.5926 | 9.7262 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-06 03:30 | 9.7 | 10.1 | 267.5 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 166639.5926 | 9.764 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-06 04:30 | 9.6 | 9.5 | 262.5 | 3280 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 167284.5926 | 9.8018 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-06 05:30 | 9.7 | 8.3 | 257.5 | 2200 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 167929.5926 | 9.8396 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-06 06:30 | 9.9 | 7.3 | 252.5 | 1480 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 168574.5926 | 9.8774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-06 07:30 | 9.9 | 7.5 | 245 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 169219.5926 | 9.9152 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-06 08:30 | 10.2 | 9.7 | 235 | 3280 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 169864.5926 | 9.953 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-06 09:30 | 10.8 | 12.7 | 230 | 4600 | 3940 | 3620 | 0 | 1290 | 645 | 0 | 170509.5926 | 9.9908 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-06 10:30 | 11.2 | 14.4 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170509.5926 | 9.9908 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-06 11:30 | 11.4 | 14.4 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170509.5926 | 9.9908 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-06 12:30 | 11.4 | 14.4 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170509.5926 | 9.9908 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-06 13:30 | 11.9 | 14.9 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170509.5926 | 9.9908 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-06 14:30 | 12.3 | 15 | 232.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170509.5926 | 9.9908 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-06 15:30 | 12.1 | 14.5 | 237.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170509.5926 | 9.9908 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-06 16:30 | 11.6 | 13.8 | 240 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170509.5926 | 9.9908 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-06 17:30 | 11.5 | 13.1 | 240 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170509.5926 | 9.9908 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-06 18:30 | 11.5 | 12.9 | 237.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170509.5926 | 9.9908 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-06 19:30 | 11.4 | 13 | 232.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170509.5926 | 9.9908 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-06 20:30 | 11.2 | 13.2 | 227.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170509.5926 | 9.9908 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-06 21:30 | 11.2 | 13.2 | 222.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170509.5926 | 9.9908 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-06 22:30 | 11.4 | 13.3 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170509.5926 | 9.9908 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-06 23:30 | 11.4 | 13.7 | 217.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170509.5926 | 9.9908 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-07 00:30 | 11.5 | 13.2 | 212.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170509.5926 | 9.9908 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-07 01:30 | 11.7 | 12 | 212.5 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170509.5926 | 9.9908 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-07 02:30 | 11.9 | 11.2 | 217.5 | 4300 | 4418.0556 | 4098.0556 | 0 | 1290 | 0 | 0 | 170509.5926 | 9.9908 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-07 03:30 | 12 | 11.1 | 220 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170509.5926 | 9.9908 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-07 04:30 | 12 | 11.4 | 220 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170509.5926 | 9.9908 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-07 05:30 | 11.8 | 11.2 | 217.5 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170509.5926 | 9.9908 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-07 06:30 | 11.6 | 10.9 | 215 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170509.5926 | 9.9908 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-07 07:30 | 11.6 | 10.6 | 215 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170509.5926 | 9.9908 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-07 08:30 | 11.8 | 10 | 212.5 | 3640 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170509.5926 | 9.9908 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-07 09:30 | 12 | 9 | 210 | 2920 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170509.5926 | 9.9908 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-07 10:30 | 12.1 | 8.3 | 217.5 | 2200 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170509.5926 | 9.9908 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-07 11:30 | 12.4 | 7.8 | 235 | 1840 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170509.5926 | 9.9908 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-07 12:30 | 12.7 | 6.8 | 247.5 | 1120 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170509.5926 | 9.9908 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-07 13:30 | 12.9 | 5.8 | 250 | 500 | 810 | 490 | 0 | 490 | 0 | 0 | 170509.5926 | 9.9908 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-07 14:30 | 12.5 | 5.2 | 252.5 | 340 | 420 | 100 | 0 | 100 | 0 | 0 | 170509.5926 | 9.9908 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-10-07 15:30 | 12.1 | 4.9 | 255 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 170397.7407 | 9.9842 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-10-07 16:30 | 11.5 | 4.4 | 250 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 169993.2963 | 9.9605 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-10-07 17:30 | 10.5 | 3.3 | 227.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 169367.3704 | 9.9239 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-10-07 18:30 | 9.4 | 2.4 | 195 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168656.2593 | 9.8822 | 0 |  |  | 1 | 5 | 1 | 1
Lerwick | 1978-10-07 19:30 | 8.3 | 2.9 | 180 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167945.1481 | 9.8405 | 0 |  |  | 1 | 6 | 1 | 2
Lerwick | 1978-10-07 20:30 | 8 | 3.6 | 180 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167234.037 | 9.7989 | 0 |  |  | 1 | 7 | 1 | 3
Lerwick | 1978-10-07 21:30 | 8.4 | 3.6 | 180 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166522.9259 | 9.7572 | 0 |  |  | 1 | 8 | 1 | 4
Lerwick | 1978-10-07 22:30 | 8.7 | 3.6 | 180 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165811.8148 | 9.7155 | 0 |  |  | 1 | 9 | 1 | 5
Lerwick | 1978-10-07 23:30 | 8.9 | 3.3 | 172.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165100.7037 | 9.6739 | 0 |  |  | 1 | 10 | 1 | 6
Lerwick | 1978-10-08 00:30 | 8.7 | 2.9 | 160 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164389.5926 | 9.6322 | 0 |  |  | 1 | 11 | 1 | 7
Lerwick | 1978-10-08 01:30 | 8.5 | 2.9 | 160 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163678.4815 | 9.5905 | 0 |  |  | 1 | 12 | 1 | 8
Lerwick | 1978-10-08 02:30 | 8.6 | 3.7 | 172.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162967.3704 | 9.5489 | 0 |  |  | 1 | 13 | 1 | 9
Lerwick | 1978-10-08 03:30 | 8.9 | 4.6 | 182.5 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 162477.7407 | 9.5202 | 1 |  |  | 1 | 14 | 0 | 0
Lerwick | 1978-10-08 04:30 | 9 | 4.7 | 175 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 162209.5926 | 9.5045 | 1 |  |  | 1 | 15 | 0 | 0
Lerwick | 1978-10-08 05:30 | 9.1 | 4.7 | 162.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 161941.4444 | 9.4888 | 1 |  |  | 1 | 16 | 0 | 0
Lerwick | 1978-10-08 06:30 | 9.1 | 5.1 | 165 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 161829.5926 | 9.4822 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-08 07:30 | 9.3 | 5.4 | 170 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 161839.5926 | 9.4828 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-08 08:30 | 9.7 | 5.5 | 172.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 161889.5926 | 9.4857 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-08 09:30 | 9.9 | 6 | 177.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 162044.5926 | 9.4948 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-08 10:30 | 10.4 | 6.5 | 180 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 162354.5926 | 9.513 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-08 11:30 | 11.5 | 6.5 | 177.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 162754.5926 | 9.5364 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-08 12:30 | 12.1 | 6.1 | 170 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 163064.5926 | 9.5546 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-08 13:30 | 12.3 | 5.6 | 162.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 163219.5926 | 9.5636 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-08 14:30 | 11.8 | 5.4 | 162.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 163269.5926 | 9.5666 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-08 15:30 | 11.6 | 5.6 | 167.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 163319.5926 | 9.5695 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-08 16:30 | 11.9 | 5.9 | 172.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 163409.5926 | 9.5748 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-08 17:30 | 11 | 5.6 | 175 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 163499.5926 | 9.5801 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-08 18:30 | 10.4 | 5.5 | 175 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 163589.5926 | 9.5853 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-08 19:30 | 10.4 | 6.9 | 182.5 | 1120 | 810 | 490 | 0 | 490 | 245 | 0 | 163834.5926 | 9.5997 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-08 20:30 | 10.7 | 9.5 | 200 | 3280 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 164479.5926 | 9.6375 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-08 21:30 | 11.8 | 11 | 215 | 4300 | 3790 | 3470 | 0 | 1290 | 645 | 0 | 165124.5926 | 9.6753 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-08 22:30 | 12.3 | 10.4 | 222.5 | 3640 | 3970 | 3650 | 0 | 1290 | 645 | 0 | 165769.5926 | 9.7131 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-08 23:30 | 12 | 9.3 | 227.5 | 2920 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 166414.5926 | 9.7509 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-09 00:30 | 11.7 | 8.2 | 230 | 2200 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 167059.5926 | 9.7886 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-09 01:30 | 11.5 | 6.9 | 230 | 1120 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 167704.5926 | 9.8264 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-09 02:30 | 11.1 | 4.9 | 217.5 | 199.3333 | 659.6667 | 339.6667 | 0 | 339.6667 | 169.8333 | 0 | 167874.4259 | 9.8364 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-10-09 03:30 | 10.8 | 3.1 | 187.5 | 0 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 167384.7963 | 9.8077 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-10-09 04:30 | 10.9 | 2.6 | 170 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166673.6852 | 9.766 | 0 |  |  | 1 | 3 | 1 | 1
Lerwick | 1978-10-09 05:30 | 10.5 | 2.7 | 175 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165962.5741 | 9.7244 | 0 |  |  | 1 | 4 | 1 | 2
Lerwick | 1978-10-09 06:30 | 9.7 | 3 | 175 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165251.463 | 9.6827 | 0 |  |  | 1 | 5 | 1 | 3
Lerwick | 1978-10-09 07:30 | 9.7 | 3 | 160 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164540.3519 | 9.641 | 0 |  |  | 1 | 6 | 1 | 4
Lerwick | 1978-10-09 08:30 | 10.1 | 2.2 | 145 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163829.2407 | 9.5994 | 0 |  |  | 1 | 7 | 1 | 5
Lerwick | 1978-10-09 09:30 | 10.4 | 2.2 | 125 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163118.1296 | 9.5577 | 0 |  |  | 1 | 8 | 1 | 6
Lerwick | 1978-10-09 10:30 | 10.5 | 3.3 | 82.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162407.0185 | 9.516 | 0 |  |  | 1 | 9 | 1 | 7
Lerwick | 1978-10-09 11:30 | 10 | 3.6 | 40 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161695.9074 | 9.4744 | 0 |  |  | 1 | 10 | 1 | 8
Lerwick | 1978-10-09 12:30 | 9.1 | 2.9 | 25 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160984.7963 | 9.4327 | 0 |  |  | 1 | 11 | 1 | 9
Lerwick | 1978-10-09 13:30 | 9.1 | 2.3 | 25 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160273.6852 | 9.391 | 0 |  |  | 1 | 12 | 1 | 10
Lerwick | 1978-10-09 14:30 | 9.4 | 2.1 | 185 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 159562.5741 | 9.3494 | 0 |  |  | 1 | 13 | 1 | 11
Lerwick | 1978-10-09 15:30 | 9.5 | 2.4 | 315 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 158851.463 | 9.3077 | 0 |  |  | 1 | 14 | 1 | 12
Lerwick | 1978-10-09 16:30 | 9.1 | 2.4 | 277.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 158140.3519 | 9.266 | 0 |  |  | 1 | 15 | 1 | 13
Lerwick | 1978-10-09 17:30 | 8.4 | 1.8 | 277.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 157429.2407 | 9.2244 | 0 |  |  | 1 | 16 | 1 | 14
Lerwick | 1978-10-09 18:30 | 7.8 | 1.5 | 280 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 156718.1296 | 9.1827 | 0 |  |  | 1 | 17 | 1 | 15
Lerwick | 1978-10-09 19:30 | 7.1 | 1.5 | 262.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 156007.0185 | 9.141 | 0 |  |  | 1 | 18 | 1 | 16
Lerwick | 1978-10-09 20:30 | 6.9 | 1.6 | 240 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 155295.9074 | 9.0994 | 0 |  |  | 1 | 19 | 1 | 17
Lerwick | 1978-10-09 21:30 | 7 | 2.2 | 225 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 154584.7963 | 9.0577 | 0 |  |  | 1 | 20 | 1 | 18
Lerwick | 1978-10-09 22:30 | 6.7 | 3.1 | 217.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 153873.6852 | 9.016 | 0 |  |  | 1 | 21 | 1 | 19
Lerwick | 1978-10-09 23:30 | 6.7 | 3.7 | 215 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 153162.5741 | 8.9744 | 0 |  |  | 1 | 22 | 1 | 20
Lerwick | 1978-10-10 00:30 | 7.2 | 3.9 | 217.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 152451.463 | 8.9327 | 0 |  |  | 1 | 23 | 1 | 21
Lerwick | 1978-10-10 01:30 | 7.4 | 4.2 | 217.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 151825.537 | 8.896 | 1 |  |  | 1 | 24 | 0 | 0
Lerwick | 1978-10-10 02:30 | 7.5 | 4.9 | 215 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 151421.0926 | 8.8723 | 1 |  |  | 1 | 25 | 0 | 0
Lerwick | 1978-10-10 03:30 | 7.5 | 5.4 | 220 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 151309.2407 | 8.8658 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-10 04:30 | 7.6 | 5.1 | 227.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 151319.2407 | 8.8664 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-10-10 05:30 | 7.5 | 4.7 | 232.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 151207.3889 | 8.8598 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-10-10 06:30 | 7.5 | 4.4 | 235 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 150802.9444 | 8.8361 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-10-10 07:30 | 7.8 | 4.4 | 230 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 150262.2037 | 8.8044 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-10-10 08:30 | 8.1 | 4.9 | 220 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 149857.7593 | 8.7807 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-10 09:30 | 8.6 | 5.8 | 212.5 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 149872.5926 | 8.7816 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-10 10:30 | 9 | 6.4 | 212.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 150027.5926 | 8.7907 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-10 11:30 | 9.3 | 6.7 | 220 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 150337.5926 | 8.8088 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-10 12:30 | 9.7 | 6.8 | 225 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 150737.5926 | 8.8323 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-10 13:30 | 10 | 7.1 | 220 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 151227.5926 | 8.861 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-10 14:30 | 10 | 7.1 | 212.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 151807.5926 | 8.895 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-10 15:30 | 9.9 | 6.4 | 212.5 | 760 | 1120 | 800 | 0 | 800 | 400 | 0 | 152207.5926 | 8.9184 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-10 16:30 | 9.8 | 4.9 | 217.5 | 199.3333 | 479.6667 | 159.6667 | 0 | 159.6667 | 79.8333 | 0 | 152287.4259 | 8.9231 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-10-10 17:30 | 9.3 | 3.1 | 212.5 | 0 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 151797.7963 | 8.8944 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-10-10 18:30 | 8.4 | 1.8 | 200 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 151086.6852 | 8.8527 | 0 |  |  | 1 | 3 | 1 | 1
Lerwick | 1978-10-10 19:30 | 7.7 | 1.5 | 192.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 150375.5741 | 8.8111 | 0 |  |  | 1 | 4 | 1 | 2
Lerwick | 1978-10-10 20:30 | 8 | 1.8 | 177.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 149664.463 | 8.7694 | 0 |  |  | 1 | 5 | 1 | 3
Lerwick | 1978-10-10 21:30 | 8.4 | 3 | 157.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 148953.3519 | 8.7277 | 0 |  |  | 1 | 6 | 1 | 4
Lerwick | 1978-10-10 22:30 | 8.1 | 3.9 | 150 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 148242.2407 | 8.6861 | 0 |  |  | 1 | 7 | 1 | 5
Lerwick | 1978-10-10 23:30 | 8.1 | 4.2 | 147.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 147616.3148 | 8.6494 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-10-11 00:30 | 8.3 | 4.7 | 137.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 147211.8704 | 8.6257 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-10-11 01:30 | 8.4 | 5 | 122.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 147100.0185 | 8.6191 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-11 02:30 | 8.8 | 5 | 107.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 147110.0185 | 8.6197 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-11 03:30 | 9 | 5.2 | 95 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 147120.0185 | 8.6203 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-11 04:30 | 9 | 5.8 | 92.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 147170.0185 | 8.6232 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-11 05:30 | 9.2 | 6.7 | 100 | 1120 | 810 | 490 | 0 | 490 | 245 | 0 | 147415.0185 | 8.6376 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-11 06:30 | 9.6 | 7.8 | 110 | 1840 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 147995.0185 | 8.6716 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-11 07:30 | 9.9 | 8.9 | 120 | 2560 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 148640.0185 | 8.7094 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-11 08:30 | 10.2 | 8.9 | 132.5 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 149285.0185 | 8.7472 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-11 09:30 | 10.5 | 8 | 145 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 149930.0185 | 8.785 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-11 10:30 | 10.5 | 7.8 | 152.5 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 150575.0185 | 8.8228 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-11 11:30 | 10.5 | 8.4 | 160 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 151220.0185 | 8.8605 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-11 12:30 | 10.5 | 8.4 | 167.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 151865.0185 | 8.8983 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-11 13:30 | 10.5 | 8.4 | 170 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 152510.0185 | 8.9361 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-11 14:30 | 10.2 | 9 | 172.5 | 2920 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 153155.0185 | 8.9739 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-11 15:30 | 10 | 8.9 | 175 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 153800.0185 | 9.0117 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-11 16:30 | 10 | 8.5 | 175 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 154445.0185 | 9.0495 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-11 17:30 | 10.2 | 9.1 | 177.5 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 155090.0185 | 9.0873 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-11 18:30 | 10.7 | 9.4 | 180 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 155735.0185 | 9.1251 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-11 19:30 | 11.4 | 8.3 | 180 | 2200 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 156380.0185 | 9.1629 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-11 20:30 | 11.8 | 7.3 | 177.5 | 1480 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 157025.0185 | 9.2007 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-11 21:30 | 11.7 | 6.4 | 175 | 760 | 1120 | 800 | 0 | 800 | 400 | 0 | 157425.0185 | 9.2241 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-11 22:30 | 11.3 | 5.8 | 175 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 157580.0185 | 9.2332 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-11 23:30 | 11 | 5.1 | 175 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 157630.0185 | 9.2361 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-10-12 00:30 | 11 | 4 | 172.5 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 157381.8704 | 9.2216 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-10-12 01:30 | 11.1 | 4 | 167.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 156841.1296 | 9.1899 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-10-12 02:30 | 11.1 | 4.4 | 167.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 156300.3889 | 9.1582 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-10-12 03:30 | 11 | 4.2 | 170 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 155759.6481 | 9.1265 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-10-12 04:30 | 10.9 | 3.9 | 170 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 155133.7222 | 9.0899 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-10-12 05:30 | 10.4 | 4.1 | 167.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 154507.7963 | 9.0532 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-10-12 06:30 | 10 | 4.4 | 162.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 153967.0556 | 9.0215 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-10-12 07:30 | 10.2 | 4.6 | 160 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 153562.6111 | 8.9978 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-12 08:30 | 10.4 | 5.8 | 165 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 153577.4444 | 8.9987 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-12 09:30 | 10.4 | 8.3 | 187.5 | 2200 | 1350 | 1030 | 0 | 1030 | 515 | 0 | 154092.4444 | 9.0289 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-12 10:30 | 10.5 | 11.2 | 217.5 | 4300 | 3250 | 2930 | 0 | 1290 | 645 | 0 | 154737.4444 | 9.0666 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-12 11:30 | 11.2 | 13 | 230 | 4600 | 4450 | 4130 | 0 | 1290 | 645 | 0 | 155382.4444 | 9.1044 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-12 12:30 | 12.5 | 14.1 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 156027.4444 | 9.1422 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-12 13:30 | 12.7 | 14.5 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 156672.4444 | 9.18 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-12 14:30 | 12 | 13.9 | 232.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 157317.4444 | 9.2178 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-12 15:30 | 11.3 | 13.5 | 235 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 157962.4444 | 9.2556 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-12 16:30 | 10.9 | 13.6 | 237.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 158607.4444 | 9.2934 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-12 17:30 | 10.3 | 12.7 | 245 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 159252.4444 | 9.3312 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-12 18:30 | 9.9 | 10.6 | 247.5 | 4000 | 4300 | 3980 | 0 | 1290 | 645 | 0 | 159897.4444 | 9.369 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-12 19:30 | 10 | 8.7 | 242.5 | 2560 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 160542.4444 | 9.4068 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-12 20:30 | 10 | 7.6 | 240 | 1840 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 161187.4444 | 9.4446 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-12 21:30 | 9.7 | 6.8 | 240 | 1120 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 161767.4444 | 9.4786 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-12 22:30 | 9.7 | 6.3 | 240 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 162077.4444 | 9.4967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-12 23:30 | 9.6 | 5.9 | 240 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 162232.4444 | 9.5058 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-13 00:30 | 9 | 5.1 | 240 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 162282.4444 | 9.5087 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-10-13 01:30 | 8.6 | 4.2 | 235 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 162034.2963 | 9.4942 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-10-13 02:30 | 8.3 | 3.7 | 225 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 161408.3704 | 9.4575 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-10-13 03:30 | 8 | 3.4 | 222.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160697.2593 | 9.4159 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-10-13 04:30 | 7.9 | 3.3 | 222.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 159986.1481 | 9.3742 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-10-13 05:30 | 7.3 | 3.3 | 212.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 159275.037 | 9.3325 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-10-13 06:30 | 6.5 | 3 | 200 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 158563.9259 | 9.2909 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-10-13 07:30 | 6.8 | 2.7 | 192.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 157852.8148 | 9.2492 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-10-13 08:30 | 7.9 | 3 | 187.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 157141.7037 | 9.2075 | 0 |  |  | 1 | 9 | 1 | 6
Lerwick | 1978-10-13 09:30 | 8.7 | 3.4 | 182.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 156430.5926 | 9.1659 | 0 |  |  | 1 | 10 | 1 | 7
Lerwick | 1978-10-13 10:30 | 9.7 | 4 | 177.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 155804.6667 | 9.1292 | 1 |  |  | 1 | 11 | 0 | 0
Lerwick | 1978-10-13 11:30 | 10.7 | 4.7 | 172.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 155400.2222 | 9.1055 | 1 |  |  | 1 | 12 | 0 | 0
Lerwick | 1978-10-13 12:30 | 10.8 | 5 | 170 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 155288.3704 | 9.0989 | 1 |  |  | 1 | 13 | 0 | 0
Lerwick | 1978-10-13 13:30 | 10.8 | 4.7 | 167.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 155176.5185 | 9.0924 | 1 |  |  | 1 | 14 | 0 | 0
Lerwick | 1978-10-13 14:30 | 10.5 | 4.2 | 162.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 154772.0741 | 9.0687 | 1 |  |  | 1 | 15 | 0 | 0
Lerwick | 1978-10-13 15:30 | 10.5 | 4 | 162.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 154231.3333 | 9.037 | 1 |  |  | 1 | 16 | 0 | 0
Lerwick | 1978-10-13 16:30 | 10.2 | 4.2 | 167.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 153690.5926 | 9.0053 | 1 |  |  | 1 | 17 | 0 | 0
Lerwick | 1978-10-13 17:30 | 9.5 | 4.9 | 170 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 153286.1481 | 8.9816 | 1 |  |  | 1 | 18 | 0 | 0
Lerwick | 1978-10-13 18:30 | 9.5 | 5.2 | 172.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 153174.2963 | 8.9751 | 1 |  |  | 1 | 19 | 0 | 0
Lerwick | 1978-10-13 19:30 | 9.5 | 4.7 | 180 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 153062.4444 | 8.9685 | 1 |  |  | 1 | 20 | 0 | 0
Lerwick | 1978-10-13 20:30 | 9.5 | 4.4 | 187.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 152658 | 8.9448 | 1 |  |  | 1 | 21 | 0 | 0
Lerwick | 1978-10-13 21:30 | 9.5 | 4.2 | 195 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 152117.2593 | 8.9131 | 1 |  |  | 1 | 22 | 0 | 0
Lerwick | 1978-10-13 22:30 | 9.5 | 3.8 | 210 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 151491.3333 | 8.8764 | 1 |  |  | 1 | 23 | 0 | 0
Lerwick | 1978-10-13 23:30 | 9.4 | 3.4 | 230 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 150780.2222 | 8.8348 | 0 |  |  | 1 | 24 | 1 | 1
Lerwick | 1978-10-14 00:30 | 8.8 | 3.6 | 250 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 150069.1111 | 8.7931 | 0 |  |  | 1 | 25 | 1 | 2
Lerwick | 1978-10-14 01:30 | 8.2 | 3.9 | 267.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 149358 | 8.7514 | 0 |  |  | 1 | 26 | 1 | 3
Lerwick | 1978-10-14 02:30 | 8.2 | 4 | 275 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 148732.0741 | 8.7148 | 1 |  |  | 1 | 27 | 0 | 0
Lerwick | 1978-10-14 03:30 | 8.1 | 3.8 | 270 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 148106.1481 | 8.6781 | 1 |  |  | 1 | 28 | 0 | 0
Lerwick | 1978-10-14 04:30 | 8.2 | 3.1 | 262.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 147395.037 | 8.6364 | 0 |  |  | 1 | 29 | 1 | 1
Lerwick | 1978-10-14 05:30 | 8.3 | 2.6 | 255 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 146683.9259 | 8.5948 | 0 |  |  | 1 | 30 | 1 | 2
Lerwick | 1978-10-14 06:30 | 8 | 2.6 | 247.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 145972.8148 | 8.5531 | 0 |  |  | 1 | 31 | 1 | 3
Lerwick | 1978-10-14 07:30 | 8.4 | 2.8 | 260 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 145261.7037 | 8.5114 | 0 |  |  | 1 | 32 | 1 | 4
Lerwick | 1978-10-14 08:30 | 8.6 | 4 | 302.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 144635.7778 | 8.4748 | 1 |  |  | 1 | 33 | 0 | 0
Lerwick | 1978-10-14 09:30 | 9 | 5.8 | 167.5 | 500 | 288.3333 | 0 | 31.6667 | 0 | 0 | 70.3704 | 144565.4074 | 8.4706 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-14 10:30 | 9.4 | 6.5 | 7.5 | 1120 | 810 | 490 | 0 | 490 | 245 | 0 | 144810.4074 | 8.485 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-14 11:30 | 9.3 | 6.1 | 12.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 145120.4074 | 8.5031 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-14 12:30 | 9.2 | 5.8 | 17.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 145275.4074 | 8.5122 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-14 13:30 | 9.2 | 5.7 | 20 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 145365.4074 | 8.5175 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-14 14:30 | 9.4 | 5.7 | 20 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 145455.4074 | 8.5228 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-14 15:30 | 9.3 | 5.5 | 20 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 145545.4074 | 8.5281 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-14 16:30 | 8.7 | 5.2 | 20 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 145595.4074 | 8.531 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-14 17:30 | 8.2 | 5.2 | 22.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 145605.4074 | 8.5316 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-14 18:30 | 8 | 5.5 | 27.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 145655.4074 | 8.5345 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-14 19:30 | 8 | 5.5 | 30 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 145745.4074 | 8.5398 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-14 20:30 | 8 | 4.9 | 30 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 145760.2407 | 8.5406 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-10-14 21:30 | 8 | 4.4 | 32.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 145355.7963 | 8.5169 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-10-14 22:30 | 7.9 | 4.6 | 37.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 144951.3519 | 8.4932 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-10-14 23:30 | 7.9 | 4.9 | 40 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 144683.2037 | 8.4775 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-10-15 00:30 | 7.8 | 4.7 | 42.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 144415.0556 | 8.4618 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-10-15 01:30 | 7.7 | 4.5 | 50 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 144146.9074 | 8.4461 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-10-15 02:30 | 7.7 | 4.4 | 55 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 143742.463 | 8.4224 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-10-15 03:30 | 7.5 | 4.4 | 55 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 143201.7222 | 8.3907 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-10-15 04:30 | 7.3 | 4.5 | 55 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 142797.2778 | 8.367 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-10-15 05:30 | 7.3 | 4.2 | 52.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 142392.8333 | 8.3433 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-10-15 06:30 | 7.4 | 4 | 55 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 141852.0926 | 8.3116 | 1 |  |  | 1 | 11 | 0 | 0
Lerwick | 1978-10-15 07:30 | 7.3 | 4 | 65 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 141311.3519 | 8.28 | 1 |  |  | 1 | 12 | 0 | 0
Lerwick | 1978-10-15 08:30 | 7.3 | 4 | 65 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 140770.6111 | 8.2483 | 1 |  |  | 1 | 13 | 0 | 0
Lerwick | 1978-10-15 09:30 | 7.4 | 4 | 60 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 140229.8704 | 8.2166 | 1 |  |  | 1 | 14 | 0 | 0
Lerwick | 1978-10-15 10:30 | 7.6 | 3.9 | 70 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 139603.9444 | 8.1799 | 1 |  |  | 1 | 15 | 0 | 0
Lerwick | 1978-10-15 11:30 | 7.8 | 3.9 | 85 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 138892.8333 | 8.1383 | 0 |  |  | 1 | 16 | 1 | 1
Lerwick | 1978-10-15 12:30 | 7.7 | 3.9 | 90 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 138181.7222 | 8.0966 | 0 |  |  | 1 | 17 | 1 | 2
Lerwick | 1978-10-15 13:30 | 7.7 | 3.8 | 92.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 137470.6111 | 8.0549 | 0 |  |  | 1 | 18 | 1 | 3
Lerwick | 1978-10-15 14:30 | 7.7 | 3.1 | 97.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 136759.5 | 8.0133 | 0 |  |  | 1 | 19 | 1 | 4
Lerwick | 1978-10-15 15:30 | 7.5 | 2.2 | 107.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 136048.3889 | 7.9716 | 0 |  |  | 1 | 20 | 1 | 5
Lerwick | 1978-10-15 16:30 | 7.7 | 1.8 | 140 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 135337.2778 | 7.9299 | 0 |  |  | 1 | 21 | 1 | 6
Lerwick | 1978-10-15 17:30 | 7.4 | 2.2 | 180 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 134626.1667 | 7.8883 | 0 |  |  | 1 | 22 | 1 | 7
Lerwick | 1978-10-15 18:30 | 6.5 | 2.4 | 187.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 133915.0556 | 7.8466 | 0 |  |  | 1 | 23 | 1 | 8
Lerwick | 1978-10-15 19:30 | 6 | 1.5 | 162.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 133203.9444 | 7.8049 | 0 |  |  | 1 | 24 | 1 | 9
Lerwick | 1978-10-15 20:30 | 5.7 | 1.1 | 147.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 132492.8333 | 7.7633 | 0 |  |  | 1 | 25 | 1 | 10
Lerwick | 1978-10-15 21:30 | 5.7 | 1.9 | 162.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 131781.7222 | 7.7216 | 0 |  |  | 1 | 26 | 1 | 11
Lerwick | 1978-10-15 22:30 | 6.4 | 3.1 | 165 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 131070.6111 | 7.6799 | 0 |  |  | 1 | 27 | 1 | 12
Lerwick | 1978-10-15 23:30 | 6.8 | 4.9 | 180 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 130580.9815 | 7.6512 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-16 00:30 | 7.1 | 7.5 | 237.5 | 1840 | 1019.6667 | 699.6667 | 0 | 699.6667 | 349.8333 | 0 | 130930.8148 | 7.6717 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-16 01:30 | 7.1 | 8.4 | 267.5 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 131575.8148 | 7.7095 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-16 02:30 | 6.9 | 7.3 | 262.5 | 1480 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 132220.8148 | 7.7473 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-16 03:30 | 7 | 6.2 | 255 | 760 | 1120 | 800 | 0 | 800 | 400 | 0 | 132620.8148 | 7.7708 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-16 04:30 | 6.9 | 5.3 | 237.5 | 340 | 550 | 230 | 0 | 230 | 115 | 0 | 132735.8148 | 7.7775 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-16 05:30 | 6.8 | 5 | 215 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 132745.8148 | 7.7781 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-16 06:30 | 6.7 | 5.2 | 207.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 132755.8148 | 7.7787 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-16 07:30 | 6.7 | 5.4 | 217.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 132765.8148 | 7.7792 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-16 08:30 | 6.6 | 5.1 | 237.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 132775.8148 | 7.7798 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-16 09:30 | 7.1 | 5.3 | 262.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 132785.8148 | 7.7804 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-16 10:30 | 7.7 | 6.7 | 280 | 1120 | 730 | 410 | 0 | 410 | 205 | 0 | 132990.8148 | 7.7924 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-16 11:30 | 8.1 | 8.5 | 290 | 2560 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 133635.8148 | 7.8302 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-16 12:30 | 8.4 | 9.5 | 297.5 | 3280 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 134280.8148 | 7.868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-16 13:30 | 8.1 | 9.5 | 300 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 134925.8148 | 7.9058 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-16 14:30 | 7.4 | 8.6 | 300 | 2560 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 135570.8148 | 7.9436 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-16 15:30 | 7.2 | 7.5 | 297.5 | 1840 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 136215.8148 | 7.9814 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-16 16:30 | 7.3 | 6.8 | 292.5 | 1120 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 136795.8148 | 8.0154 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-16 17:30 | 6.9 | 6.5 | 290 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 137195.8148 | 8.0388 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-16 18:30 | 6.6 | 6.1 | 287.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 137505.8148 | 8.057 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-16 19:30 | 6.2 | 5.6 | 282.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 137660.8148 | 8.0661 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-16 20:30 | 5.9 | 5.1 | 280 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 137710.8148 | 8.069 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-10-16 21:30 | 5.8 | 4.6 | 277.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 137598.963 | 8.0624 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-10-16 22:30 | 5.3 | 4.1 | 277.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 137194.5185 | 8.0387 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-10-16 23:30 | 5.1 | 3.5 | 287.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 136568.5926 | 8.0021 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-10-17 00:30 | 5 | 3.3 | 300 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 135857.4815 | 7.9604 | 0 |  |  | 1 | 5 | 1 | 1
Lerwick | 1978-10-17 01:30 | 4.6 | 4.2 | 315 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 135231.5556 | 7.9237 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-10-17 02:30 | 4.6 | 5.3 | 330 | 340 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 134983.4074 | 7.9092 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-17 03:30 | 4.1 | 6 | 335 | 760 | 550 | 230 | 0 | 230 | 115 | 0 | 135098.4074 | 7.9159 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-17 04:30 | 3.9 | 6.7 | 335 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 135408.4074 | 7.9341 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-17 05:30 | 4.3 | 6.8 | 332.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 135808.4074 | 7.9575 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-17 06:30 | 4.6 | 6.7 | 330 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 136208.4074 | 7.981 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-17 07:30 | 5.1 | 7.2 | 330 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 136698.4074 | 8.0097 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-17 08:30 | 5.6 | 7.9 | 330 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 137343.4074 | 8.0475 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-17 09:30 | 6.2 | 8.1 | 330 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 137988.4074 | 8.0853 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-17 10:30 | 6.8 | 8.1 | 327.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 138633.4074 | 8.1231 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-17 11:30 | 7 | 8.1 | 322.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 139278.4074 | 8.1608 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-17 12:30 | 7.2 | 8 | 320 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 139923.4074 | 8.1986 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-17 13:30 | 7.7 | 7.7 | 317.5 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 140568.4074 | 8.2364 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-17 14:30 | 6.9 | 6.8 | 310 | 1120 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 141148.4074 | 8.2704 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-17 15:30 | 6.1 | 5.8 | 300 | 500 | 810 | 490 | 0 | 490 | 245 | 0 | 141393.4074 | 8.2848 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-17 16:30 | 5.9 | 5.2 | 292.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 141443.4074 | 8.2877 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-17 17:30 | 5.4 | 5 | 287.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 141453.4074 | 8.2883 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-17 18:30 | 5.1 | 5.4 | 280 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 141463.4074 | 8.2889 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-17 19:30 | 5.4 | 5.8 | 265 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 141513.4074 | 8.2918 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-17 20:30 | 6 | 6.2 | 247.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 141668.4074 | 8.3009 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-17 21:30 | 6.6 | 7.7 | 240 | 1840 | 1300 | 980 | 0 | 980 | 490 | 0 | 142158.4074 | 8.3296 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-17 22:30 | 7.3 | 9.3 | 240 | 2920 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 142803.4074 | 8.3674 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-17 23:30 | 7.8 | 9.8 | 240 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 143448.4074 | 8.4052 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-18 00:30 | 7.8 | 10.1 | 242.5 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 144093.4074 | 8.443 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-18 01:30 | 7.9 | 11.5 | 247.5 | 4472.2222 | 4056.1111 | 3736.1111 | 0 | 1290 | 645 | 0 | 144738.4074 | 8.4808 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-18 02:30 | 8.4 | 12.5 | 250 | 4600 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 145383.4074 | 8.5186 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-18 03:30 | 8.7 | 12.5 | 252.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 146028.4074 | 8.5564 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-18 04:30 | 8.7 | 12.9 | 260 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 146673.4074 | 8.5941 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-18 05:30 | 8.8 | 13.1 | 267.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 147318.4074 | 8.6319 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-18 06:30 | 8.9 | 12.9 | 267.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 147963.4074 | 8.6697 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-18 07:30 | 8.9 | 13 | 262.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 148608.4074 | 8.7075 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-18 08:30 | 9.2 | 13.3 | 262.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 149253.4074 | 8.7453 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-18 09:30 | 9.4 | 13.9 | 270 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 149898.4074 | 8.7831 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-18 10:30 | 9.5 | 14.2 | 275 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 150543.4074 | 8.8209 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-18 11:30 | 9.8 | 14.3 | 272.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 151188.4074 | 8.8587 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-18 12:30 | 10.1 | 14 | 272.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 151833.4074 | 8.8965 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-18 13:30 | 10.3 | 13.2 | 275 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 152478.4074 | 8.9343 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-18 14:30 | 10.3 | 12.6 | 272.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 153123.4074 | 8.9721 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-18 15:30 | 10.2 | 11.9 | 270 | 4472.2222 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 153768.4074 | 9.0099 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-18 16:30 | 10 | 11.4 | 270 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 154413.4074 | 9.0477 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-18 17:30 | 10 | 11.1 | 270 | 4300 | 4300 | 3980 | 0 | 1290 | 645 | 0 | 155058.4074 | 9.0855 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-18 18:30 | 10 | 10.6 | 267.5 | 4000 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 155703.4074 | 9.1232 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-18 19:30 | 10 | 9.8 | 262.5 | 3280 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 156348.4074 | 9.161 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-18 20:30 | 10 | 8.9 | 260 | 2560 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 156993.4074 | 9.1988 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-18 21:30 | 10 | 8.5 | 260 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 157638.4074 | 9.2366 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-18 22:30 | 9.9 | 8.5 | 257.5 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 158283.4074 | 9.2744 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-18 23:30 | 9.7 | 8.2 | 252.5 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 158928.4074 | 9.3122 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-19 00:30 | 9.3 | 7.8 | 250 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 159573.4074 | 9.35 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-19 01:30 | 9.3 | 7.8 | 245 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 160218.4074 | 9.3878 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-19 02:30 | 9.4 | 8.4 | 237.5 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 160863.4074 | 9.4256 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-19 03:30 | 9.4 | 8.8 | 232.5 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 161508.4074 | 9.4634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-19 04:30 | 9 | 9 | 227.5 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 162153.4074 | 9.5012 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-19 05:30 | 8.8 | 10 | 227.5 | 3640 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 162798.4074 | 9.539 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-19 06:30 | 9.2 | 10.8 | 230 | 4000 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 163443.4074 | 9.5768 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-19 07:30 | 9.3 | 10.8 | 230 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 164088.4074 | 9.6146 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-19 08:30 | 9.4 | 11.1 | 227.5 | 4300 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 164733.4074 | 9.6523 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-19 09:30 | 9.5 | 12 | 222.5 | 4536.1111 | 4418.0556 | 4098.0556 | 0 | 1290 | 645 | 0 | 165378.4074 | 9.6901 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-19 10:30 | 9.7 | 12.8 | 220 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 645 | 0 | 166023.4074 | 9.7279 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-19 11:30 | 9.9 | 13.6 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 166668.4074 | 9.7657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-19 12:30 | 10 | 14.8 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 167313.4074 | 9.8035 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-19 13:30 | 9.7 | 15.1 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 167958.4074 | 9.8413 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-19 14:30 | 9.4 | 14.9 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 168603.4074 | 9.8791 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-19 15:30 | 9.7 | 15.4 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 169248.4074 | 9.9169 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-19 16:30 | 10 | 16.5 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 169893.4074 | 9.9547 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-19 17:30 | 10.1 | 17.2 | 222.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 170538.4074 | 9.9925 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-19 18:30 | 10.3 | 17 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170538.4074 | 9.9925 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-19 19:30 | 10.4 | 15.4 | 242.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170538.4074 | 9.9925 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-19 20:30 | 9.6 | 13.7 | 255 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170538.4074 | 9.9925 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-19 21:30 | 8.9 | 13.6 | 260 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170538.4074 | 9.9925 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-19 22:30 | 8.8 | 14.8 | 260 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170538.4074 | 9.9925 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-19 23:30 | 8.3 | 15.8 | 260 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170538.4074 | 9.9925 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-20 00:30 | 8 | 16.6 | 260 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170538.4074 | 9.9925 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-20 01:30 | 7.7 | 17 | 262.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170538.4074 | 9.9925 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-20 02:30 | 7.4 | 16.6 | 265 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170538.4074 | 9.9925 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-20 03:30 | 7 | 15.7 | 265 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170538.4074 | 9.9925 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-20 04:30 | 6.9 | 13.8 | 275 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170538.4074 | 9.9925 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-20 05:30 | 6.4 | 11.5 | 297.5 | 4472.2222 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170538.4074 | 9.9925 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-20 06:30 | 5.3 | 10.4 | 312.5 | 3640 | 4056.1111 | 3736.1111 | 0 | 1290 | 0 | 0 | 170538.4074 | 9.9925 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-20 07:30 | 4.7 | 10 | 310 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170538.4074 | 9.9925 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-20 08:30 | 4.6 | 9.9 | 305 | 3280 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170538.4074 | 9.9925 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-20 09:30 | 4.6 | 10.1 | 307.5 | 3640 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170538.4074 | 9.9925 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-20 10:30 | 4.1 | 10 | 310 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170538.4074 | 9.9925 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-20 11:30 | 4.2 | 9.8 | 310 | 3280 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170538.4074 | 9.9925 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-20 12:30 | 4.8 | 9.9 | 310 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170538.4074 | 9.9925 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-20 13:30 | 4.4 | 10 | 312.5 | 3640 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170538.4074 | 9.9925 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-20 14:30 | 4.1 | 9.9 | 315 | 3280 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170538.4074 | 9.9925 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-20 15:30 | 4 | 9.4 | 312.5 | 2920 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170538.4074 | 9.9925 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-20 16:30 | 3.2 | 9 | 312.5 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170538.4074 | 9.9925 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-20 17:30 | 3 | 8.9 | 315 | 2560 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170538.4074 | 9.9925 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-20 18:30 | 3.4 | 8 | 315 | 2200 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170538.4074 | 9.9925 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-20 19:30 | 3.1 | 6.4 | 320 | 760 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170538.4074 | 9.9925 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-20 20:30 | 2.8 | 5.5 | 325 | 500 | 630 | 310 | 0 | 310 | 0 | 0 | 170538.4074 | 9.9925 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-20 21:30 | 2.7 | 5.5 | 320 | 500 | 500 | 180 | 0 | 180 | 0 | 0 | 170538.4074 | 9.9925 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-20 22:30 | 3.1 | 5.3 | 312.5 | 340 | 420 | 100 | 0 | 100 | 0 | 0 | 170538.4074 | 9.9925 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-10-20 23:30 | 3.3 | 4.9 | 307.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 170426.5556 | 9.9859 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-10-21 00:30 | 3 | 4.9 | 300 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 170158.4074 | 9.9702 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-10-21 01:30 | 3.1 | 4.9 | 290 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 169890.2593 | 9.9545 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-10-21 02:30 | 3.2 | 4.9 | 285 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 169622.1111 | 9.9388 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-10-21 03:30 | 3.4 | 4.9 | 287.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 169353.963 | 9.9231 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-10-21 04:30 | 3.6 | 4.4 | 287.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 168949.5185 | 9.8994 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-10-21 05:30 | 3.7 | 3.5 | 285 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 168323.5926 | 9.8627 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-10-21 06:30 | 3.6 | 2.8 | 285 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167612.4815 | 9.821 | 0 |  |  | 1 | 9 | 1 | 1
Lerwick | 1978-10-21 07:30 | 3.7 | 2.3 | 280 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166901.3704 | 9.7794 | 0 |  |  | 1 | 10 | 1 | 2
Lerwick | 1978-10-21 08:30 | 3.8 | 1.9 | 270 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166190.2593 | 9.7377 | 0 |  |  | 1 | 11 | 1 | 3
Lerwick | 1978-10-21 09:30 | 4.2 | 2.2 | 255 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165479.1481 | 9.696 | 0 |  |  | 1 | 12 | 1 | 4
Lerwick | 1978-10-21 10:30 | 4.6 | 2.9 | 240 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164768.037 | 9.6544 | 0 |  |  | 1 | 13 | 1 | 5
Lerwick | 1978-10-21 11:30 | 4.7 | 3.4 | 230 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164056.9259 | 9.6127 | 0 |  |  | 1 | 14 | 1 | 6
Lerwick | 1978-10-21 12:30 | 4.5 | 3.4 | 210 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163345.8148 | 9.571 | 0 |  |  | 1 | 15 | 1 | 7
Lerwick | 1978-10-21 13:30 | 4.3 | 3.3 | 182.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162634.7037 | 9.5294 | 0 |  |  | 1 | 16 | 1 | 8
Lerwick | 1978-10-21 14:30 | 4.4 | 4.1 | 165 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 162008.7778 | 9.4927 | 1 |  |  | 1 | 17 | 0 | 0
Lerwick | 1978-10-21 15:30 | 4.6 | 5.9 | 157.5 | 500 | 288.3333 | 0 | 31.6667 | 0 | 0 | 70.3704 | 161938.4074 | 9.4886 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-21 16:30 | 4.9 | 7.5 | 155 | 1840 | 1170 | 850 | 0 | 850 | 425 | 0 | 162363.4074 | 9.5135 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-21 17:30 | 5.4 | 8.2 | 155 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 163008.4074 | 9.5513 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-21 18:30 | 5.6 | 8.9 | 155 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 163653.4074 | 9.5891 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-21 19:30 | 5.8 | 9.3 | 157.5 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 164298.4074 | 9.6269 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-21 20:30 | 6.2 | 8.7 | 162.5 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 164943.4074 | 9.6647 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-21 21:30 | 6.1 | 8.3 | 192.5 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 165588.4074 | 9.7024 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-21 22:30 | 6.9 | 9 | 247.5 | 2920 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 166233.4074 | 9.7402 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-21 23:30 | 8.3 | 9.5 | 277.5 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 166878.4074 | 9.778 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-22 00:30 | 8.1 | 9.9 | 280 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 167523.4074 | 9.8158 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-22 01:30 | 7.7 | 10.5 | 280 | 4000 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 168168.4074 | 9.8536 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-22 02:30 | 7.9 | 10.5 | 282.5 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 168813.4074 | 9.8914 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-22 03:30 | 7.6 | 10.1 | 287.5 | 3640 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 169458.4074 | 9.9292 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-22 04:30 | 7.6 | 10 | 290 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-22 05:30 | 7.2 | 10 | 287.5 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-22 06:30 | 6.9 | 9.9 | 282.5 | 3280 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-22 07:30 | 6.7 | 9.8 | 282.5 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-22 08:30 | 6.7 | 9.8 | 287.5 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-22 09:30 | 6.9 | 9.8 | 287.5 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-22 10:30 | 7.2 | 9.9 | 285 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-22 11:30 | 7.8 | 10 | 287.5 | 3640 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-22 12:30 | 7.7 | 10.1 | 287.5 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-22 13:30 | 7.7 | 10.3 | 282.5 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-22 14:30 | 7.9 | 9.8 | 282.5 | 3280 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-22 15:30 | 8 | 8.7 | 285 | 2560 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-22 16:30 | 7.3 | 7.9 | 282.5 | 1840 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-22 17:30 | 6.9 | 7.7 | 280 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-22 18:30 | 7.1 | 7.6 | 277.5 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-22 19:30 | 7.1 | 7.5 | 272.5 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-22 20:30 | 7.1 | 7.8 | 267.5 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-22 21:30 | 7.1 | 8.1 | 260 | 2200 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-22 22:30 | 7.3 | 7.9 | 250 | 1840 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-22 23:30 | 7.4 | 8.2 | 240 | 2200 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-23 00:30 | 7.9 | 9.4 | 232.5 | 2920 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-23 01:30 | 8.6 | 10.6 | 230 | 4000 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-23 02:30 | 8.8 | 11.8 | 230 | 4472.2222 | 4236.1111 | 3916.1111 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-23 03:30 | 9.1 | 12.4 | 230 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-23 04:30 | 9.5 | 12.8 | 230 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-23 05:30 | 9.7 | 13 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-23 06:30 | 9.9 | 12.2 | 230 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-23 07:30 | 10 | 11.2 | 230 | 4300 | 4418.0556 | 4098.0556 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-23 08:30 | 10 | 11.2 | 230 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-23 09:30 | 10.1 | 11.5 | 230 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-23 10:30 | 10.3 | 11.4 | 230 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-23 11:30 | 10.2 | 11.5 | 227.5 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-23 12:30 | 9.6 | 11.5 | 225 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-23 13:30 | 9.3 | 10.8 | 230 | 4000 | 4236.1111 | 3916.1111 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-23 14:30 | 9.5 | 10.4 | 237.5 | 3640 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-23 15:30 | 9.3 | 10.7 | 235 | 4000 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-23 16:30 | 8.8 | 11.2 | 230 | 4300 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-23 17:30 | 8.8 | 11.5 | 237.5 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-23 18:30 | 9.1 | 11.4 | 247.5 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-23 19:30 | 9.1 | 11.4 | 247.5 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-23 20:30 | 8.7 | 11.7 | 242.5 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-23 21:30 | 8.6 | 12 | 242.5 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-23 22:30 | 8.2 | 12 | 247.5 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-23 23:30 | 7.8 | 11.9 | 250 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-24 00:30 | 7.7 | 11.1 | 252.5 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-24 01:30 | 6.8 | 11 | 255 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-24 02:30 | 6.1 | 12.7 | 252.5 | 4600 | 4450 | 4130 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-24 03:30 | 5.8 | 14.1 | 250 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-24 04:30 | 5.6 | 14.1 | 252.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-24 05:30 | 6.2 | 14.4 | 255 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-24 06:30 | 6.3 | 15.7 | 252.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-24 07:30 | 6.3 | 16.3 | 250 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-24 08:30 | 7.1 | 16.1 | 252.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-24 09:30 | 7.3 | 15.8 | 257.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-24 10:30 | 7.3 | 15.8 | 260 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-24 11:30 | 7.4 | 16.2 | 257.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-24 12:30 | 6.6 | 16.7 | 255 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-24 13:30 | 6.7 | 17.9 | 257.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-24 14:30 | 8 | 19.3 | 262.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-24 15:30 | 8.1 | 19 | 267.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-24 16:30 | 6.2 | 17.6 | 270 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-24 17:30 | 5.8 | 16.7 | 270 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-24 18:30 | 7.2 | 15.9 | 270 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-24 19:30 | 7.2 | 14.6 | 272.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-24 20:30 | 6.8 | 13.4 | 277.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-24 21:30 | 6.9 | 12.9 | 280 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-24 22:30 | 6.9 | 12.9 | 280 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-24 23:30 | 6.8 | 13 | 280 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-25 00:30 | 6.9 | 13.2 | 280 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-25 01:30 | 6.6 | 12.9 | 282.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-25 02:30 | 6.6 | 12 | 287.5 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-25 03:30 | 6.6 | 11.2 | 290 | 4300 | 4418.0556 | 4098.0556 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-25 04:30 | 6.5 | 10.6 | 290 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-25 05:30 | 6.2 | 10 | 290 | 3640 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-25 06:30 | 5.5 | 9.6 | 290 | 3280 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-25 07:30 | 5.4 | 9 | 292.5 | 2920 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-25 08:30 | 5.4 | 8.1 | 295 | 2200 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-25 09:30 | 5.5 | 8.2 | 292.5 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-25 10:30 | 6.3 | 9 | 290 | 2920 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-25 11:30 | 6.6 | 8.5 | 290 | 2560 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-25 12:30 | 6.5 | 7.2 | 290 | 1480 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-25 13:30 | 6.6 | 6.7 | 290 | 1120 | 1300 | 980 | 0 | 980 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-25 14:30 | 6.7 | 6.4 | 292.5 | 760 | 940 | 620 | 0 | 620 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-25 15:30 | 6.7 | 5.6 | 300 | 500 | 630 | 310 | 0 | 310 | 0 | 0 | 170103.4074 | 9.967 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-10-25 16:30 | 6.5 | 4.4 | 307.5 | 76.6667 | 288.3333 | 0 | 31.6667 | 0 | 0 | 70.3704 | 170033.037 | 9.9629 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-10-25 17:30 | 6.2 | 3.3 | 305 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 169407.1111 | 9.9262 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-10-25 18:30 | 5.8 | 2.4 | 295 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168696 | 9.8845 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-10-25 19:30 | 5.8 | 2.2 | 290 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167984.8889 | 9.8429 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-10-25 20:30 | 5.7 | 2.4 | 290 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167273.7778 | 9.8012 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-10-25 21:30 | 5.5 | 2.6 | 290 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166562.6667 | 9.7595 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-10-25 22:30 | 5.5 | 2.6 | 290 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165851.5556 | 9.7179 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-10-25 23:30 | 5.2 | 2.6 | 290 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165140.4444 | 9.6762 | 0 |  |  | 1 | 9 | 1 | 6
Lerwick | 1978-10-26 00:30 | 5 | 2.7 | 292.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164429.3333 | 9.6345 | 0 |  |  | 1 | 10 | 1 | 7
Lerwick | 1978-10-26 01:30 | 4.9 | 2.4 | 297.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163718.2222 | 9.5929 | 0 |  |  | 1 | 11 | 1 | 8
Lerwick | 1978-10-26 02:30 | 4.3 | 2 | 295 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163007.1111 | 9.5512 | 0 |  |  | 1 | 12 | 1 | 9
Lerwick | 1978-10-26 03:30 | 4.7 | 1.5 | 270 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162296 | 9.5095 | 0 |  |  | 1 | 13 | 1 | 10
Lerwick | 1978-10-26 04:30 | 5.2 | 1.1 | 230 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161584.8889 | 9.4679 | 0 |  |  | 1 | 14 | 1 | 11
Lerwick | 1978-10-26 05:30 | 4.1 | 1.2 | 202.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160873.7778 | 9.4262 | 0 |  |  | 1 | 15 | 1 | 12
Lerwick | 1978-10-26 06:30 | 3.2 | 1.6 | 192.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160162.6667 | 9.3845 | 0 |  |  | 1 | 16 | 1 | 13
Lerwick | 1978-10-26 07:30 | 3.1 | 1.9 | 190 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 159451.5556 | 9.3429 | 0 |  |  | 1 | 17 | 1 | 14
Lerwick | 1978-10-26 08:30 | 4.2 | 3 | 187.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 158740.4444 | 9.3012 | 0 |  |  | 1 | 18 | 1 | 15
Lerwick | 1978-10-26 09:30 | 5.7 | 5.1 | 182.5 | 340 | 170 | 0 | 150 | 0 | 0 | 333.3333 | 158407.1111 | 9.2817 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-26 10:30 | 6.9 | 7.4 | 180 | 1480 | 910 | 590 | 0 | 590 | 295 | 0 | 158702.1111 | 9.299 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-26 11:30 | 7.9 | 8.9 | 180 | 2560 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 159347.1111 | 9.3367 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-26 12:30 | 8.1 | 9 | 182.5 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 159992.1111 | 9.3745 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-26 13:30 | 8.1 | 8.8 | 195 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 160637.1111 | 9.4123 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-26 14:30 | 8.4 | 9.1 | 217.5 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 161282.1111 | 9.4501 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-26 15:30 | 9.3 | 9.7 | 237.5 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 161927.1111 | 9.4879 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-26 16:30 | 9.9 | 10.4 | 247.5 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 162572.1111 | 9.5257 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-26 17:30 | 10 | 10.9 | 250 | 4000 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 163217.1111 | 9.5635 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-26 18:30 | 10 | 10.7 | 252.5 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 163862.1111 | 9.6013 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-26 19:30 | 10 | 10.4 | 255 | 3640 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 164507.1111 | 9.6391 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-26 20:30 | 9.9 | 10 | 255 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 165152.1111 | 9.6769 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-26 21:30 | 9.9 | 9.4 | 250 | 2920 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 165797.1111 | 9.7147 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-26 22:30 | 10 | 9 | 240 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 166442.1111 | 9.7525 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-26 23:30 | 10.1 | 9.4 | 237.5 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 167087.1111 | 9.7903 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-27 00:30 | 10.2 | 10 | 240 | 3640 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 167732.1111 | 9.8281 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-27 01:30 | 10.3 | 10.6 | 237.5 | 4000 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 168377.1111 | 9.8658 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-27 02:30 | 10.2 | 11.4 | 232.5 | 4300 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 169022.1111 | 9.9036 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-27 03:30 | 10.2 | 12.1 | 230 | 4536.1111 | 4418.0556 | 4098.0556 | 0 | 1290 | 645 | 0 | 169667.1111 | 9.9414 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-27 04:30 | 10.4 | 13 | 230 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 645 | 0 | 170312.1111 | 9.9792 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-27 05:30 | 10.4 | 14 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170312.1111 | 9.9792 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-27 06:30 | 10.5 | 14.6 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170312.1111 | 9.9792 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-27 07:30 | 10.6 | 14.9 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170312.1111 | 9.9792 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-27 08:30 | 10.8 | 14.8 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170312.1111 | 9.9792 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-27 09:30 | 10.6 | 14.5 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170312.1111 | 9.9792 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-27 10:30 | 10.5 | 14.1 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170312.1111 | 9.9792 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-27 11:30 | 10.7 | 13.4 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170312.1111 | 9.9792 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-27 12:30 | 10.9 | 12.7 | 232.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170312.1111 | 9.9792 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-27 13:30 | 10.9 | 12.8 | 237.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170312.1111 | 9.9792 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-27 14:30 | 10.9 | 13.5 | 237.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170312.1111 | 9.9792 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-27 15:30 | 10.9 | 14.1 | 232.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170312.1111 | 9.9792 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-27 16:30 | 10.9 | 14.5 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170312.1111 | 9.9792 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-27 17:30 | 10.9 | 14.5 | 232.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170312.1111 | 9.9792 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-27 18:30 | 10.9 | 14.5 | 237.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170312.1111 | 9.9792 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-27 19:30 | 11 | 15 | 240 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170312.1111 | 9.9792 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-27 20:30 | 11 | 15.1 | 242.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170312.1111 | 9.9792 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-27 21:30 | 10.9 | 14.5 | 247.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170312.1111 | 9.9792 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-27 22:30 | 10.8 | 13.5 | 250 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170312.1111 | 9.9792 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-27 23:30 | 10.6 | 11.9 | 252.5 | 4472.2222 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170312.1111 | 9.9792 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-28 00:30 | 10.4 | 10.6 | 260 | 4000 | 4236.1111 | 3916.1111 | 0 | 1290 | 0 | 0 | 170312.1111 | 9.9792 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-28 01:30 | 10.3 | 9.9 | 270 | 3280 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170312.1111 | 9.9792 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-28 02:30 | 10.1 | 8.8 | 275 | 2560 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170312.1111 | 9.9792 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-28 03:30 | 9.8 | 7.5 | 272.5 | 1840 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170312.1111 | 9.9792 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-28 04:30 | 9.3 | 6 | 270 | 760 | 1300 | 980 | 0 | 980 | 0 | 0 | 170312.1111 | 9.9792 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-28 05:30 | 9 | 4.5 | 275 | 199.3333 | 479.6667 | 159.6667 | 0 | 159.6667 | 0 | 0 | 170312.1111 | 9.9792 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-10-28 06:30 | 8.9 | 3.9 | 277.5 | 0 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 169822.4815 | 9.9505 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-10-28 07:30 | 8.5 | 3.9 | 265 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 169111.3704 | 9.9089 | 0 |  |  | 1 | 3 | 1 | 1
Lerwick | 1978-10-28 08:30 | 8.1 | 3.9 | 252.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168400.2593 | 9.8672 | 0 |  |  | 1 | 4 | 1 | 2
Lerwick | 1978-10-28 09:30 | 8.4 | 4.1 | 247.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 167774.3333 | 9.8305 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-10-28 10:30 | 8.9 | 4.7 | 242.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 167369.8889 | 9.8068 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-10-28 11:30 | 9.1 | 5.2 | 240 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 167258.037 | 9.8003 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-28 12:30 | 9.3 | 5.8 | 237.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 167308.037 | 9.8032 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-28 13:30 | 9.8 | 6.6 | 235 | 1120 | 810 | 490 | 0 | 490 | 245 | 0 | 167553.037 | 9.8176 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-28 14:30 | 10.1 | 7.3 | 237.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 168043.037 | 9.8463 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-28 15:30 | 10.2 | 8.5 | 240 | 2560 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 168688.037 | 9.8841 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-28 16:30 | 10.1 | 9.8 | 240 | 3280 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 169333.037 | 9.9219 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-28 17:30 | 10.2 | 10.6 | 240 | 4000 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 169978.037 | 9.9597 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-28 18:30 | 10.3 | 11.7 | 240 | 4472.2222 | 4236.1111 | 3916.1111 | 0 | 1290 | 645 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-28 19:30 | 10.3 | 12.9 | 242.5 | 4600 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-28 20:30 | 10.3 | 13.6 | 247.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-28 21:30 | 10.4 | 14 | 250 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-28 22:30 | 10.5 | 13.9 | 250 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-28 23:30 | 10.3 | 13 | 250 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-29 00:30 | 10.1 | 11.9 | 250 | 4472.2222 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-29 01:30 | 10.2 | 10.9 | 250 | 4000 | 4236.1111 | 3916.1111 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-29 02:30 | 10.2 | 10.1 | 250 | 3640 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-29 03:30 | 10.1 | 9.8 | 247.5 | 3280 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-29 04:30 | 10.1 | 9.6 | 242.5 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-29 05:30 | 10.1 | 8.7 | 240 | 2560 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-29 06:30 | 10.2 | 7.6 | 237.5 | 1840 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-29 07:30 | 10.2 | 7.6 | 232.5 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-29 08:30 | 10.1 | 8.2 | 230 | 2200 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-29 09:30 | 10.3 | 8.6 | 230 | 2560 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-29 10:30 | 10.6 | 9.1 | 227.5 | 2920 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-29 11:30 | 10.8 | 9.6 | 222.5 | 3280 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-29 12:30 | 10.6 | 10 | 220 | 3640 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-29 13:30 | 10.5 | 10.8 | 222.5 | 4000 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-29 14:30 | 10.5 | 11.3 | 227.5 | 4300 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-29 15:30 | 10.6 | 11 | 230 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-29 16:30 | 10.8 | 10.6 | 230 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-29 17:30 | 10.7 | 10.1 | 230 | 3640 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-29 18:30 | 10.5 | 9.8 | 230 | 3280 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-29 19:30 | 10.5 | 10.1 | 230 | 3640 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-29 20:30 | 10.6 | 10.5 | 230 | 4000 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-29 21:30 | 10.7 | 10.5 | 232.5 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-29 22:30 | 10.7 | 11 | 237.5 | 4300 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-29 23:30 | 10.5 | 11.5 | 240 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-30 00:30 | 10.5 | 10.6 | 237.5 | 4000 | 4236.1111 | 3916.1111 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-30 01:30 | 10.5 | 9.6 | 232.5 | 3280 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-30 02:30 | 10.5 | 9.7 | 230 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-30 03:30 | 10.5 | 9.9 | 230 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-30 04:30 | 10.5 | 9.5 | 230 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-30 05:30 | 10.6 | 9 | 230 | 2920 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-30 06:30 | 10.7 | 8.4 | 230 | 2200 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-30 07:30 | 10.9 | 7.9 | 227.5 | 1840 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-30 08:30 | 10.9 | 7.8 | 222.5 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-30 09:30 | 10.9 | 8 | 217.5 | 2200 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-30 10:30 | 11.5 | 8 | 212.5 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-30 11:30 | 12 | 8.1 | 210 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-30 12:30 | 11.8 | 7.9 | 210 | 1840 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-30 13:30 | 11.8 | 7.9 | 210 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-30 14:30 | 11.5 | 8.3 | 210 | 2200 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-30 15:30 | 11 | 8.9 | 210 | 2560 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-30 16:30 | 11.2 | 9.9 | 212.5 | 3280 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-30 17:30 | 11.2 | 10.4 | 217.5 | 3640 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-30 18:30 | 11.2 | 9.8 | 220 | 3280 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-30 19:30 | 11.3 | 8.7 | 220 | 2560 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-30 20:30 | 11.3 | 7.8 | 220 | 1840 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-30 21:30 | 11.3 | 7.1 | 220 | 1480 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-30 22:30 | 11.1 | 6 | 217.5 | 760 | 1120 | 800 | 0 | 800 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-30 23:30 | 10.9 | 4.7 | 212.5 | 199.3333 | 479.6667 | 159.6667 | 0 | 159.6667 | 0 | 0 | 170623.037 | 9.9974 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-10-31 00:30 | 10.8 | 3.5 | 205 | 0 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 170133.4074 | 9.9688 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-10-31 01:30 | 10.6 | 2.9 | 190 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 169422.2963 | 9.9271 | 0 |  |  | 1 | 3 | 1 | 1
Lerwick | 1978-10-31 02:30 | 10.3 | 3.1 | 175 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168711.1852 | 9.8854 | 0 |  |  | 1 | 4 | 1 | 2
Lerwick | 1978-10-31 03:30 | 10.1 | 4.9 | 175 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 168221.5556 | 9.8567 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-31 04:30 | 10 | 7.3 | 192.5 | 1480 | 839.6667 | 519.6667 | 0 | 519.6667 | 259.8333 | 0 | 168481.3889 | 9.872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-31 05:30 | 10.5 | 8.2 | 232.5 | 2200 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 169126.3889 | 9.9097 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-31 06:30 | 10.4 | 6.8 | 280 | 1120 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 169771.3889 | 9.9475 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-31 07:30 | 8.6 | 5.1 | 292.5 | 340 | 730 | 410 | 0 | 410 | 205 | 0 | 169976.3889 | 9.9596 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-10-31 08:30 | 7.5 | 4.7 | 272.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 169864.537 | 9.953 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-10-31 09:30 | 7.6 | 5.4 | 252.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 169752.6852 | 9.9464 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-31 10:30 | 7.8 | 6.5 | 242.5 | 1120 | 730 | 410 | 0 | 410 | 205 | 0 | 169957.6852 | 9.9585 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-31 11:30 | 8.3 | 7.4 | 237.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-31 12:30 | 9.2 | 7.6 | 232.5 | 1840 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-31 13:30 | 9.9 | 7.3 | 230 | 1480 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-31 14:30 | 9.8 | 7.1 | 230 | 1480 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-31 15:30 | 9 | 6.8 | 230 | 1120 | 1300 | 980 | 0 | 980 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-31 16:30 | 8.4 | 6.7 | 232.5 | 1120 | 1120 | 800 | 0 | 800 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-31 17:30 | 8.4 | 6.5 | 235 | 1120 | 1120 | 800 | 0 | 800 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-31 18:30 | 7.7 | 6.7 | 235 | 1120 | 1120 | 800 | 0 | 800 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-31 19:30 | 7.3 | 7.9 | 235 | 1840 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-31 20:30 | 7.6 | 9.3 | 232.5 | 2920 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-31 21:30 | 7.7 | 10 | 230 | 3640 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-31 22:30 | 7.9 | 10.8 | 230 | 4000 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-10-31 23:30 | 8.2 | 11.4 | 227.5 | 4300 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-01 00:30 | 8.5 | 11.6 | 222.5 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-01 01:30 | 8.7 | 12.1 | 220 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-01 02:30 | 8.8 | 12.2 | 222.5 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-01 03:30 | 8.7 | 11.7 | 225 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-01 04:30 | 8.7 | 11.2 | 222.5 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-01 05:30 | 8.9 | 10.1 | 215 | 3640 | 3970 | 3650 | 0 | 1290 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-01 06:30 | 8.9 | 8.2 | 205 | 2200 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-01 07:30 | 8.7 | 6.9 | 197.5 | 1120 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-01 08:30 | 8.5 | 7.3 | 190 | 1480 | 1300 | 980 | 0 | 980 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-01 09:30 | 8.8 | 9.1 | 180 | 2920 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-01 10:30 | 8.8 | 11.3 | 172.5 | 4300 | 3610 | 3290 | 0 | 1290 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-01 11:30 | 8.9 | 13 | 170 | 4600 | 4450 | 4130 | 0 | 1290 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-01 12:30 | 9.4 | 14.1 | 170 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-01 13:30 | 9.5 | 15 | 172.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-01 14:30 | 9.5 | 15.5 | 177.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-01 15:30 | 9.3 | 15.7 | 180 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-01 16:30 | 9.3 | 15.4 | 182.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-01 17:30 | 9.3 | 15.2 | 187.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-01 18:30 | 9.3 | 15.4 | 190 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-01 19:30 | 9.3 | 15.5 | 192.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-01 20:30 | 9.5 | 15.7 | 197.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-01 21:30 | 10 | 16.3 | 202.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-01 22:30 | 10.5 | 16.4 | 207.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-01 23:30 | 10.5 | 15.8 | 210 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-02 00:30 | 10.4 | 14.8 | 217.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-02 01:30 | 10.4 | 12.5 | 237.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-02 02:30 | 9.5 | 9.4 | 257.5 | 2920 | 3760 | 3440 | 0 | 1290 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-02 03:30 | 8.2 | 7.7 | 267.5 | 1840 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-02 04:30 | 7.7 | 6.9 | 272.5 | 1120 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-02 05:30 | 7.8 | 5.7 | 277.5 | 500 | 810 | 490 | 0 | 490 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-02 06:30 | 7.7 | 4.7 | 280 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 0 | 0 | 170447.6852 | 9.9872 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-11-02 07:30 | 7.5 | 4.5 | 280 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 170179.537 | 9.9715 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-11-02 08:30 | 7.3 | 4.9 | 277.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 169911.3889 | 9.9557 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-02 09:30 | 7.1 | 5.8 | 272.5 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 169926.2222 | 9.9566 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-02 10:30 | 7.4 | 6 | 270 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-02 11:30 | 7.7 | 5.8 | 272.5 | 500 | 630 | 310 | 0 | 310 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-02 12:30 | 7.8 | 5.5 | 272.5 | 500 | 500 | 180 | 0 | 180 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-02 13:30 | 8.3 | 5.4 | 255 | 340 | 420 | 100 | 0 | 100 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-02 14:30 | 8.5 | 5.6 | 230 | 500 | 420 | 100 | 0 | 100 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-02 15:30 | 7.7 | 5.9 | 217.5 | 500 | 500 | 180 | 0 | 180 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-02 16:30 | 6.7 | 5.9 | 210 | 500 | 500 | 180 | 0 | 180 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-02 17:30 | 5.9 | 6.7 | 200 | 1120 | 810 | 490 | 0 | 490 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-02 18:30 | 6 | 9 | 195 | 2920 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-02 19:30 | 7.1 | 11.4 | 202.5 | 4300 | 3610 | 3290 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-02 20:30 | 8 | 11.7 | 215 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-02 21:30 | 8.6 | 10.2 | 217.5 | 3640 | 4056.1111 | 3736.1111 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-02 22:30 | 8.4 | 9.2 | 210 | 2920 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-02 23:30 | 8.3 | 9.5 | 202.5 | 3280 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-03 00:30 | 8.4 | 10.7 | 200 | 4000 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-03 01:30 | 8.5 | 11.4 | 197.5 | 4300 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-03 02:30 | 8.5 | 11 | 192.5 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-03 03:30 | 8.5 | 10.9 | 190 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-03 04:30 | 8.7 | 11.1 | 192.5 | 4300 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-03 05:30 | 8.8 | 11.1 | 200 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-03 06:30 | 8.6 | 9.9 | 225 | 3280 | 3790 | 3470 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-03 07:30 | 7.7 | 6.9 | 275 | 1120 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-03 08:30 | 6.2 | 5.6 | 295 | 500 | 810 | 490 | 0 | 490 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-03 09:30 | 5.3 | 8.2 | 257.5 | 2200 | 1350 | 1030 | 0 | 1030 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-03 10:30 | 6 | 11.3 | 220 | 4300 | 3250 | 2930 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-03 11:30 | 7.3 | 13.3 | 212.5 | 4600 | 4450 | 4130 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-03 12:30 | 8 | 15.1 | 225 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-03 13:30 | 7.6 | 16.6 | 240 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-03 14:30 | 6.2 | 18 | 247.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-03 15:30 | 5.8 | 18.6 | 252.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-03 16:30 | 6.3 | 17.9 | 260 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-03 17:30 | 6.3 | 16.6 | 267.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-03 18:30 | 6.2 | 14.9 | 267.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-03 19:30 | 6.4 | 13.2 | 260 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-03 20:30 | 6.8 | 12.5 | 250 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-03 21:30 | 7 | 12.5 | 242.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-03 22:30 | 7.2 | 12.8 | 240 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-03 23:30 | 7.6 | 13.2 | 237.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-04 00:30 | 7.9 | 13.1 | 235 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-04 01:30 | 7.9 | 13 | 240 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-04 02:30 | 7.3 | 12.7 | 247.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-04 03:30 | 6.8 | 11.7 | 247.5 | 4472.2222 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-04 04:30 | 6.6 | 10.7 | 242.5 | 4000 | 4236.1111 | 3916.1111 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-04 05:30 | 6.8 | 9.7 | 242.5 | 3280 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-04 06:30 | 7.3 | 7.8 | 252.5 | 1840 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-04 07:30 | 7.3 | 5.6 | 262.5 | 500 | 1170 | 850 | 0 | 850 | 0 | 0 | 170081.2222 | 9.9657 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-11-04 08:30 | 7.1 | 3.6 | 252.5 | 0 | 250 | 0 | 70 | 0 | 0 | 155.5556 | 169925.6667 | 9.9566 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-11-04 09:30 | 6.8 | 2.4 | 225 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 169214.5556 | 9.9149 | 0 |  |  | 1 | 3 | 1 | 1
Lerwick | 1978-11-04 10:30 | 7.1 | 2.1 | 200 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168503.4444 | 9.8732 | 0 |  |  | 1 | 4 | 1 | 2
Lerwick | 1978-11-04 11:30 | 7.3 | 2.2 | 182.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167792.3333 | 9.8316 | 0 |  |  | 1 | 5 | 1 | 3
Lerwick | 1978-11-04 12:30 | 7.5 | 2.4 | 170 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167081.2222 | 9.7899 | 0 |  |  | 1 | 6 | 1 | 4
Lerwick | 1978-11-04 13:30 | 7.7 | 3.3 | 162.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166370.1111 | 9.7482 | 0 |  |  | 1 | 7 | 1 | 5
Lerwick | 1978-11-04 14:30 | 7.7 | 4.4 | 155 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 165744.1852 | 9.7116 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-11-04 15:30 | 7 | 5.1 | 142.5 | 340 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 165496.037 | 9.697 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-04 16:30 | 6.4 | 5.6 | 132.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 165546.037 | 9.7 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-04 17:30 | 6.5 | 6.1 | 130 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 165701.037 | 9.709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-04 18:30 | 6.9 | 6.5 | 130 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 166011.037 | 9.7272 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-04 19:30 | 7.3 | 6.7 | 130 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 166411.037 | 9.7506 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-04 20:30 | 7.6 | 6.9 | 127.5 | 1120 | 1120 | 800 | 0 | 800 | 400 | 0 | 166811.037 | 9.7741 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-04 21:30 | 7.7 | 7.4 | 125 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 167301.037 | 9.8028 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-04 22:30 | 7.7 | 7.3 | 132.5 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 167881.037 | 9.8368 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-04 23:30 | 7.8 | 6.4 | 150 | 760 | 1120 | 800 | 0 | 800 | 400 | 0 | 168281.037 | 9.8602 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-05 00:30 | 8.4 | 6.3 | 177.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 168501.037 | 9.8731 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-05 01:30 | 8.9 | 7.8 | 207.5 | 1840 | 1300 | 980 | 0 | 980 | 490 | 0 | 168991.037 | 9.9018 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-05 02:30 | 9.8 | 9.6 | 217.5 | 3280 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 169636.037 | 9.9396 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-05 03:30 | 10.6 | 10.1 | 210 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-05 04:30 | 10.6 | 10.6 | 205 | 4000 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-05 05:30 | 10.7 | 12.8 | 207.5 | 4600 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-05 06:30 | 11.2 | 15.2 | 212.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-05 07:30 | 11.5 | 16.1 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-05 08:30 | 11.6 | 16.4 | 225 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-05 09:30 | 11.7 | 16.7 | 225 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-05 10:30 | 11.6 | 16.8 | 227.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-05 11:30 | 11.8 | 17 | 227.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-05 12:30 | 12 | 16.6 | 222.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-05 13:30 | 11.7 | 15.9 | 222.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-05 14:30 | 11.6 | 15.4 | 227.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-05 15:30 | 11.6 | 15 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-05 16:30 | 11.5 | 14.5 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-05 17:30 | 11.5 | 13.5 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-05 18:30 | 11.4 | 12.3 | 230 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-05 19:30 | 11.2 | 11.4 | 230 | 4300 | 4418.0556 | 4098.0556 | 0 | 1290 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-05 20:30 | 11 | 10.9 | 230 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-05 21:30 | 11 | 10.8 | 230 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-05 22:30 | 10.9 | 10.6 | 230 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-05 23:30 | 10.9 | 10.4 | 232.5 | 3640 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-06 00:30 | 10.9 | 10.1 | 237.5 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-06 01:30 | 10.6 | 9.7 | 237.5 | 3280 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-06 02:30 | 10.7 | 9.4 | 232.5 | 2920 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-06 03:30 | 11 | 9.3 | 227.5 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-06 04:30 | 11.4 | 8.9 | 222.5 | 2560 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-06 05:30 | 11.9 | 7.7 | 220 | 1840 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-06 06:30 | 12 | 6.4 | 215 | 760 | 1300 | 980 | 0 | 980 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-06 07:30 | 11.6 | 5.9 | 205 | 500 | 630 | 310 | 0 | 310 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-06 08:30 | 10.4 | 6 | 200 | 760 | 630 | 310 | 0 | 310 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-06 09:30 | 9.5 | 6.2 | 200 | 760 | 760 | 440 | 0 | 440 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-06 10:30 | 9.8 | 6.3 | 197.5 | 760 | 760 | 440 | 0 | 440 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-06 11:30 | 10.3 | 6.5 | 192.5 | 1120 | 940 | 620 | 0 | 620 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-06 12:30 | 10.3 | 6.5 | 187.5 | 1120 | 1120 | 800 | 0 | 800 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-06 13:30 | 10.4 | 6.3 | 182.5 | 760 | 940 | 620 | 0 | 620 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-06 14:30 | 10.6 | 5.9 | 182.5 | 500 | 630 | 310 | 0 | 310 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-06 15:30 | 10.2 | 5.7 | 185 | 500 | 500 | 180 | 0 | 180 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-06 16:30 | 10 | 5.9 | 185 | 500 | 500 | 180 | 0 | 180 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-06 17:30 | 9.5 | 5.6 | 187.5 | 500 | 500 | 180 | 0 | 180 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-06 18:30 | 9.2 | 4.9 | 192.5 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 0 | 0 | 170281.037 | 9.9774 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-11-06 19:30 | 9.2 | 5.4 | 197.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 170169.1852 | 9.9709 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-06 20:30 | 9.3 | 6.5 | 200 | 1120 | 730 | 410 | 0 | 410 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-06 21:30 | 9.9 | 8.2 | 197.5 | 2200 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-06 22:30 | 10.1 | 9.8 | 192.5 | 3280 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-06 23:30 | 9.7 | 10.8 | 190 | 4000 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-07 00:30 | 9.4 | 11.8 | 190 | 4472.2222 | 4236.1111 | 3916.1111 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-07 01:30 | 9.3 | 12.1 | 190 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-07 02:30 | 9.2 | 11.6 | 190 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-07 03:30 | 9 | 11.6 | 190 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-07 04:30 | 9 | 11.3 | 187.5 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-07 05:30 | 9.1 | 10.5 | 185 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-07 06:30 | 9.2 | 10.4 | 187.5 | 3640 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-07 07:30 | 9.4 | 10.5 | 190 | 4000 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-07 08:30 | 9.4 | 10.9 | 190 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-07 09:30 | 9.3 | 11.3 | 190 | 4300 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-07 10:30 | 9.3 | 10.9 | 190 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-07 11:30 | 9.4 | 10.5 | 190 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-07 12:30 | 9.5 | 10.6 | 190 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-07 13:30 | 9.5 | 10.8 | 190 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-07 14:30 | 9.4 | 10.9 | 187.5 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-07 15:30 | 9.3 | 11.4 | 182.5 | 4300 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-07 16:30 | 9.3 | 12.1 | 180 | 4536.1111 | 4418.0556 | 4098.0556 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-07 17:30 | 9.3 | 12.8 | 180 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-07 18:30 | 9.3 | 13.5 | 180 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-07 19:30 | 9.4 | 14.1 | 180 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-07 20:30 | 9.6 | 14.4 | 180 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-07 21:30 | 9.7 | 14.4 | 180 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-07 22:30 | 9.8 | 14.1 | 180 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-07 23:30 | 9.8 | 13.6 | 180 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-08 00:30 | 9.8 | 13.4 | 180 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-08 01:30 | 9.8 | 13.4 | 180 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-08 02:30 | 9.9 | 13.4 | 180 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-08 03:30 | 10 | 13.5 | 180 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-08 04:30 | 10 | 14 | 182.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-08 05:30 | 10 | 14.8 | 190 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-08 06:30 | 10.3 | 15.4 | 207.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-08 07:30 | 10.7 | 15 | 237.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-08 08:30 | 9.7 | 13.4 | 260 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-08 09:30 | 8 | 12.4 | 260 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-08 10:30 | 7.9 | 12.4 | 250 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-08 11:30 | 8.5 | 12.8 | 242.5 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-08 12:30 | 9 | 13.2 | 240 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-08 13:30 | 9.2 | 13.4 | 237.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-08 14:30 | 8.9 | 13.4 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-08 15:30 | 8.7 | 13.9 | 222.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-08 16:30 | 8.9 | 14.8 | 222.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-08 17:30 | 9.1 | 14.9 | 227.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-08 18:30 | 9.1 | 14.7 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-08 19:30 | 9 | 14.8 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-08 20:30 | 9.1 | 14.5 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-08 21:30 | 9.4 | 13.6 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-08 22:30 | 9.6 | 13.2 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-08 23:30 | 9.6 | 13.5 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-09 00:30 | 9.6 | 13.6 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-09 01:30 | 9.7 | 13.9 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-09 02:30 | 9.8 | 14.3 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-09 03:30 | 9.9 | 14.3 | 227.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-09 04:30 | 10 | 13.9 | 222.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-09 05:30 | 9.9 | 13.7 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-09 06:30 | 9.9 | 14 | 217.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-09 07:30 | 10.1 | 14.5 | 215 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-09 08:30 | 10.1 | 15.4 | 217.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-09 09:30 | 10 | 16 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-09 10:30 | 10.1 | 16 | 222.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-09 11:30 | 10.4 | 15.6 | 225 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-09 12:30 | 10.5 | 14.5 | 222.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-09 13:30 | 10.5 | 14 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-09 14:30 | 10.5 | 14.7 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-09 15:30 | 10.7 | 15.6 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-09 16:30 | 11 | 16.2 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-09 17:30 | 11 | 16.6 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-09 18:30 | 11.1 | 17 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-09 19:30 | 11.3 | 17.4 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-09 20:30 | 11.3 | 17.4 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-09 21:30 | 11.3 | 17.1 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-09 22:30 | 11.1 | 17 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-09 23:30 | 10.8 | 16.7 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-10 00:30 | 10.8 | 15.8 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-10 01:30 | 10.5 | 15 | 222.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-10 02:30 | 10.2 | 13.2 | 245 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-10 03:30 | 10.4 | 8.6 | 280 | 2560 | 3580 | 3260 | 0 | 1290 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-10 04:30 | 9 | 4.5 | 292.5 | 199.3333 | 1379.6667 | 1059.6667 | 0 | 1059.6667 | 0 | 0 | 170169.1852 | 9.9709 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-11-10 05:30 | 7.3 | 3.6 | 290 | 0 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 169679.5556 | 9.9422 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-11-10 06:30 | 7.1 | 4.2 | 295 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 169053.6296 | 9.9055 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-11-10 07:30 | 7 | 4.2 | 302.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 168512.8889 | 9.8738 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-11-10 08:30 | 6.8 | 4 | 302.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 167972.1481 | 9.8421 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-11-10 09:30 | 6.3 | 4.2 | 297.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 167431.4074 | 9.8104 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-11-10 10:30 | 6 | 4.9 | 290 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 167026.963 | 9.7867 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-10 11:30 | 6.4 | 5.6 | 282.5 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 167041.7963 | 9.7876 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-10 12:30 | 6.9 | 6 | 280 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 167196.7963 | 9.7967 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-10 13:30 | 7.1 | 5.9 | 282.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 167351.7963 | 9.8058 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-10 14:30 | 7 | 5.1 | 287.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 167401.7963 | 9.8087 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-11-10 15:30 | 6.7 | 4.5 | 290 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 167289.9444 | 9.8021 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-11-10 16:30 | 6.8 | 4.7 | 287.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 167021.7963 | 9.7864 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-11-10 17:30 | 6.8 | 5 | 282.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 166909.9444 | 9.7799 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-10 18:30 | 6.6 | 5.2 | 280 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 166919.9444 | 9.7805 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-10 19:30 | 6.2 | 5.2 | 282.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 166929.9444 | 9.7811 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-11-10 20:30 | 5.7 | 4.7 | 285 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 166818.0926 | 9.7745 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-11-10 21:30 | 5.7 | 4.4 | 282.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 166413.6481 | 9.7508 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-11-10 22:30 | 6.1 | 4.4 | 275 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 165872.9074 | 9.7191 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-11-10 23:30 | 5.9 | 4.7 | 265 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 165468.463 | 9.6954 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-11-11 00:30 | 5.7 | 4.9 | 257.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 165200.3148 | 9.6797 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-11-11 01:30 | 5.6 | 4.7 | 250 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 164932.1667 | 9.664 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-11-11 02:30 | 5.3 | 4.2 | 240 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 164527.7222 | 9.6403 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-11-11 03:30 | 4.9 | 3.6 | 230 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 163901.7963 | 9.6036 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-11-11 04:30 | 4.6 | 3.3 | 220 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163190.6852 | 9.562 | 0 |  |  | 1 | 10 | 1 | 1
Lerwick | 1978-11-11 05:30 | 4.4 | 3.9 | 215 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162479.5741 | 9.5203 | 0 |  |  | 1 | 11 | 1 | 2
Lerwick | 1978-11-11 06:30 | 4.4 | 5.1 | 220 | 340 | 170 | 0 | 150 | 0 | 0 | 333.3333 | 162146.2407 | 9.5008 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-11 07:30 | 5.2 | 5.9 | 225 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 162196.2407 | 9.5037 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-11 08:30 | 6 | 6.6 | 220 | 1120 | 810 | 490 | 0 | 490 | 245 | 0 | 162441.2407 | 9.518 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-11 09:30 | 6.1 | 7.3 | 210 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 162931.2407 | 9.5468 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-11 10:30 | 6.5 | 8.2 | 202.5 | 2200 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 163576.2407 | 9.5845 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-11 11:30 | 7.4 | 9 | 200 | 2920 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 164221.2407 | 9.6223 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-11 12:30 | 8.2 | 9.3 | 202.5 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 164866.2407 | 9.6601 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-11 13:30 | 8.5 | 9.1 | 207.5 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 165511.2407 | 9.6979 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-11 14:30 | 8.2 | 8.7 | 207.5 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 166156.2407 | 9.7357 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-11 15:30 | 7.8 | 8.5 | 205 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 166801.2407 | 9.7735 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-11 16:30 | 7.3 | 8.2 | 205 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 167446.2407 | 9.8113 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-11 17:30 | 7.1 | 8.2 | 202.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 168091.2407 | 9.8491 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-11 18:30 | 7.3 | 9.1 | 200 | 2920 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 168736.2407 | 9.8869 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-11 19:30 | 7.8 | 9.6 | 200 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 169381.2407 | 9.9247 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-11 20:30 | 8.6 | 9.1 | 200 | 2920 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-11 21:30 | 9.4 | 9 | 200 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-11 22:30 | 9.8 | 9.6 | 200 | 3280 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-11 23:30 | 10.2 | 9.6 | 197.5 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-12 00:30 | 10.2 | 8.9 | 195 | 2560 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-12 01:30 | 9.9 | 8.2 | 195 | 2200 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-12 02:30 | 9.7 | 8 | 195 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-12 03:30 | 9.6 | 8.6 | 197.5 | 2560 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-12 04:30 | 9.5 | 9.9 | 200 | 3280 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-12 05:30 | 9.7 | 10.7 | 197.5 | 4000 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-12 06:30 | 9.8 | 11.4 | 192.5 | 4300 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-12 07:30 | 9.6 | 12.3 | 190 | 4536.1111 | 4418.0556 | 4098.0556 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-12 08:30 | 9.6 | 13.2 | 190 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-12 09:30 | 9.6 | 13.7 | 187.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-12 10:30 | 9.5 | 13.9 | 182.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-12 11:30 | 9.5 | 14.1 | 180 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-12 12:30 | 9.3 | 14.8 | 180 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-12 13:30 | 9 | 15.6 | 180 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-12 14:30 | 8.9 | 16.3 | 180 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-12 15:30 | 8.8 | 17 | 177.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-12 16:30 | 9 | 17.5 | 172.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-12 17:30 | 9.1 | 17.9 | 172.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-12 18:30 | 9 | 17.7 | 175 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-12 19:30 | 8.6 | 16.4 | 197.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-12 20:30 | 6.7 | 14.5 | 245 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-12 21:30 | 5.9 | 13.6 | 270 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-12 22:30 | 6.3 | 13 | 267.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-12 23:30 | 6.2 | 11.7 | 260 | 4472.2222 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-13 00:30 | 6 | 11.1 | 255 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-13 01:30 | 5.7 | 11.3 | 252.5 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-13 02:30 | 4.5 | 10.9 | 245 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-13 03:30 | 3.2 | 11.7 | 242.5 | 4472.2222 | 4236.1111 | 3916.1111 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-13 04:30 | 4.1 | 13.8 | 247.5 | 4600 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-13 05:30 | 4.5 | 14.5 | 250 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-13 06:30 | 4.4 | 13.9 | 252.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-13 07:30 | 5.2 | 12.4 | 255 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-13 08:30 | 4.9 | 12 | 247.5 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-13 09:30 | 4.6 | 13.4 | 232.5 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-13 10:30 | 4.9 | 14.5 | 225 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-13 11:30 | 5.2 | 13.9 | 225 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-13 12:30 | 4.7 | 13 | 222.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-13 13:30 | 4.6 | 12.7 | 225 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-13 14:30 | 4.8 | 12.7 | 237.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-13 15:30 | 4.5 | 12.9 | 252.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-13 16:30 | 4.4 | 11.9 | 262.5 | 4472.2222 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-13 17:30 | 4.4 | 11.5 | 260 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-13 18:30 | 4.3 | 11.7 | 255 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-13 19:30 | 4 | 11.1 | 257.5 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-13 20:30 | 3.9 | 11.1 | 257.5 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-13 21:30 | 3.3 | 11.9 | 250 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-13 22:30 | 3.9 | 12.4 | 242.5 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-13 23:30 | 5.4 | 12.2 | 242.5 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-14 00:30 | 5.7 | 12.2 | 247.5 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-14 01:30 | 5.4 | 11.6 | 247.5 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-14 02:30 | 5.7 | 10.1 | 237.5 | 3640 | 4056.1111 | 3736.1111 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-14 03:30 | 6.3 | 9.1 | 220 | 2920 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-14 04:30 | 6 | 9.6 | 202.5 | 3280 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-14 05:30 | 5.6 | 12.2 | 187.5 | 4536.1111 | 3908.0556 | 3588.0556 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-14 06:30 | 5.7 | 15.2 | 180 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-14 07:30 | 7 | 17.4 | 187.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-14 08:30 | 8.3 | 18.8 | 200 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-14 09:30 | 8.6 | 19.4 | 210 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-14 10:30 | 9.1 | 19.9 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-14 11:30 | 10 | 20.7 | 227.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-14 12:30 | 10.4 | 22.1 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-14 13:30 | 9.5 | 24 | 232.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-14 14:30 | 8.8 | 23.8 | 237.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-14 15:30 | 8.9 | 21.3 | 242.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-14 16:30 | 8.7 | 18.8 | 255 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-14 17:30 | 8.7 | 15.7 | 277.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-14 18:30 | 7.8 | 12.3 | 300 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-14 19:30 | 5.6 | 9.8 | 312.5 | 3280 | 3908.0556 | 3588.0556 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-14 20:30 | 4.5 | 8 | 310 | 2200 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-14 21:30 | 4.6 | 6.4 | 300 | 760 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-14 22:30 | 4.6 | 4.8 | 290 | 199.3333 | 479.6667 | 159.6667 | 0 | 159.6667 | 0 | 0 | 170026.2407 | 9.9625 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-11-14 23:30 | 4.5 | 3.8 | 277.5 | 0 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 169536.6111 | 9.9338 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-11-15 00:30 | 4.2 | 3.1 | 260 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168825.5 | 9.8921 | 0 |  |  | 1 | 3 | 1 | 1
Lerwick | 1978-11-15 01:30 | 4 | 2.4 | 237.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168114.3889 | 9.8505 | 0 |  |  | 1 | 4 | 1 | 2
Lerwick | 1978-11-15 02:30 | 3.8 | 2.1 | 220 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167403.2778 | 9.8088 | 0 |  |  | 1 | 5 | 1 | 3
Lerwick | 1978-11-15 03:30 | 3.8 | 2.7 | 212.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166692.1667 | 9.7671 | 0 |  |  | 1 | 6 | 1 | 4
Lerwick | 1978-11-15 04:30 | 3.9 | 3.4 | 207.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165981.0556 | 9.7255 | 0 |  |  | 1 | 7 | 1 | 5
Lerwick | 1978-11-15 05:30 | 4.2 | 3.4 | 200 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165269.9444 | 9.6838 | 0 |  |  | 1 | 8 | 1 | 6
Lerwick | 1978-11-15 06:30 | 4.2 | 3.2 | 192.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164558.8333 | 9.6421 | 0 |  |  | 1 | 9 | 1 | 7
Lerwick | 1978-11-15 07:30 | 4.5 | 2.9 | 192.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163847.7222 | 9.6005 | 0 |  |  | 1 | 10 | 1 | 8
Lerwick | 1978-11-15 08:30 | 4.7 | 3.1 | 182.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163136.6111 | 9.5588 | 0 |  |  | 1 | 11 | 1 | 9
Lerwick | 1978-11-15 09:30 | 4.6 | 4 | 150 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 162510.6852 | 9.5221 | 1 |  |  | 1 | 12 | 0 | 0
Lerwick | 1978-11-15 10:30 | 4.4 | 4.6 | 112.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 162106.2407 | 9.4984 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-15 11:30 | 4.2 | 5.5 | 87.5 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 162121.0741 | 9.4993 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-15 12:30 | 4.1 | 6.9 | 77.5 | 1120 | 810 | 490 | 0 | 490 | 245 | 0 | 162366.0741 | 9.5136 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-15 13:30 | 4 | 8.1 | 65 | 2200 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 163011.0741 | 9.5514 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-15 14:30 | 3.9 | 8.6 | 40 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 163656.0741 | 9.5892 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-15 15:30 | 3.9 | 8.9 | 190 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 164301.0741 | 9.627 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-15 16:30 | 4 | 9 | 345 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 164946.0741 | 9.6648 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-15 17:30 | 3.7 | 8.5 | 330 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 165591.0741 | 9.7026 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-15 18:30 | 3.3 | 8.1 | 320 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 166236.0741 | 9.7404 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-15 19:30 | 3.5 | 8.3 | 310 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 166881.0741 | 9.7782 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-15 20:30 | 3.8 | 7.8 | 300 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 167526.0741 | 9.816 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-15 21:30 | 3.9 | 6.5 | 290 | 1120 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 168106.0741 | 9.85 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-15 22:30 | 3.8 | 5.2 | 282.5 | 340 | 730 | 410 | 0 | 410 | 205 | 0 | 168311.0741 | 9.862 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-11-15 23:30 | 3.5 | 3.1 | 300 | 0 | 170 | 0 | 150 | 0 | 0 | 333.3333 | 167977.7407 | 9.8424 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-11-16 00:30 | 3.5 | 2.8 | 310 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167266.6296 | 9.8008 | 0 |  |  | 0 | 0 | 1 | 1
Lerwick | 1978-11-16 01:30 | 3.1 | 6.7 | 275 | 1120 | 560 | 240 | 0 | 240 | 120 | 0 | 167386.6296 | 9.8078 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-16 02:30 | 2.6 | 11.4 | 255 | 4300 | 2710 | 2390 | 0 | 1290 | 645 | 0 | 168031.6296 | 9.8456 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-16 03:30 | 3.2 | 14.7 | 262.5 | 4600 | 4450 | 4130 | 0 | 1290 | 645 | 0 | 168676.6296 | 9.8834 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-16 04:30 | 3.9 | 14.9 | 270 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 169321.6296 | 9.9212 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-16 05:30 | 3.3 | 12.6 | 275 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 169966.6296 | 9.959 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-16 06:30 | 2.5 | 11 | 272.5 | 4300 | 4450 | 4130 | 0 | 1290 | 645 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-16 07:30 | 3.2 | 10.3 | 265 | 3640 | 3970 | 3650 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-16 08:30 | 3.7 | 9.5 | 252.5 | 3280 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-16 09:30 | 4.2 | 9.3 | 245 | 2920 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-16 10:30 | 4.3 | 10.3 | 245 | 3640 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-16 11:30 | 4.7 | 12.1 | 242.5 | 4536.1111 | 4088.0556 | 3768.0556 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-16 12:30 | 5.3 | 12.6 | 240 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-16 13:30 | 4.8 | 12.1 | 242.5 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-16 14:30 | 4.8 | 10.6 | 242.5 | 4000 | 4268.0556 | 3948.0556 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-16 15:30 | 4.1 | 9.2 | 235 | 2920 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-16 16:30 | 3.7 | 9.4 | 230 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-16 17:30 | 5 | 9.1 | 230 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-16 18:30 | 4.7 | 7.7 | 230 | 1840 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-16 19:30 | 3.7 | 7.1 | 235 | 1480 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-16 20:30 | 3.7 | 8 | 250 | 2200 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-16 21:30 | 4.2 | 9.5 | 262.5 | 3280 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-16 22:30 | 4.9 | 11 | 262.5 | 4300 | 3790 | 3470 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-16 23:30 | 5.3 | 12.1 | 260 | 4536.1111 | 4418.0556 | 4098.0556 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-17 00:30 | 5.7 | 12.2 | 262.5 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-17 01:30 | 5.7 | 12.2 | 265 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-17 02:30 | 5.3 | 12.4 | 262.5 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-17 03:30 | 5.3 | 11.4 | 257.5 | 4300 | 4418.0556 | 4098.0556 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-17 04:30 | 5.5 | 10 | 252.5 | 3640 | 3970 | 3650 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-17 05:30 | 5.9 | 9.1 | 247.5 | 2920 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-17 06:30 | 6.5 | 7.9 | 237.5 | 1840 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-17 07:30 | 6.7 | 6.4 | 217.5 | 760 | 1300 | 980 | 0 | 980 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-17 08:30 | 6.8 | 5.6 | 202.5 | 500 | 630 | 310 | 0 | 310 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-17 09:30 | 6.6 | 6.7 | 207.5 | 1120 | 810 | 490 | 0 | 490 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-17 10:30 | 7 | 10 | 217.5 | 3640 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-17 11:30 | 8.4 | 12.5 | 220 | 4600 | 4120 | 3800 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-17 12:30 | 9.6 | 13.2 | 220 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-17 13:30 | 9.6 | 13.4 | 217.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-17 14:30 | 9.3 | 13.4 | 212.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-17 15:30 | 9.2 | 13.2 | 210 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-17 16:30 | 9.2 | 12.8 | 210 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-17 17:30 | 8.8 | 12.8 | 210 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-17 18:30 | 8.6 | 12.8 | 210 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-17 19:30 | 8.3 | 11.7 | 210 | 4472.2222 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-17 20:30 | 8.3 | 11 | 210 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-17 21:30 | 8.4 | 11.1 | 210 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-17 22:30 | 8.3 | 11.3 | 210 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-17 23:30 | 8.2 | 11 | 215 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-18 00:30 | 8 | 11.3 | 225 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-18 01:30 | 8 | 12.1 | 235 | 4536.1111 | 4418.0556 | 4098.0556 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-18 02:30 | 8.2 | 12.2 | 247.5 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-18 03:30 | 8.3 | 11.7 | 257.5 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-18 04:30 | 7.8 | 11 | 260 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-18 05:30 | 7.5 | 10.4 | 257.5 | 3640 | 3970 | 3650 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-18 06:30 | 7.5 | 10.3 | 250 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-18 07:30 | 7.4 | 10.3 | 242.5 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-18 08:30 | 7.4 | 10.3 | 240 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-18 09:30 | 7.6 | 10.3 | 240 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-18 10:30 | 7.8 | 9.8 | 240 | 3280 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-18 11:30 | 7 | 8.2 | 240 | 2200 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-18 12:30 | 6.7 | 6.7 | 237.5 | 1120 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-18 13:30 | 7.2 | 6.2 | 230 | 760 | 940 | 620 | 0 | 620 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-18 14:30 | 7.3 | 6.2 | 220 | 760 | 760 | 440 | 0 | 440 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-18 15:30 | 7.4 | 6.2 | 210 | 760 | 760 | 440 | 0 | 440 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-18 16:30 | 7.1 | 6.7 | 200 | 1120 | 940 | 620 | 0 | 620 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-18 17:30 | 7 | 8.2 | 190 | 2200 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-18 18:30 | 7.4 | 10.1 | 182.5 | 3640 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-18 19:30 | 7.9 | 11.5 | 187.5 | 4472.2222 | 4056.1111 | 3736.1111 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-18 20:30 | 8.1 | 12.7 | 207.5 | 4600 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-18 21:30 | 8.4 | 13.6 | 225 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-18 22:30 | 7.6 | 13.7 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-18 23:30 | 6.4 | 13.7 | 232.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-19 00:30 | 6.7 | 14 | 237.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-19 01:30 | 7.1 | 14 | 242.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-19 02:30 | 7.1 | 13.7 | 247.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-19 03:30 | 7.1 | 13.3 | 250 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-19 04:30 | 6.7 | 12.4 | 250 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-19 05:30 | 6.5 | 10.9 | 252.5 | 4000 | 4268.0556 | 3948.0556 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-19 06:30 | 6.2 | 9.2 | 255 | 2920 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-19 07:30 | 5.5 | 8.1 | 252.5 | 2200 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-19 08:30 | 5.4 | 7.4 | 250 | 1480 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-19 09:30 | 5.9 | 6.9 | 252.5 | 1120 | 1300 | 980 | 0 | 980 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-19 10:30 | 6.5 | 6.5 | 255 | 1120 | 1120 | 800 | 0 | 800 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-19 11:30 | 6 | 6.7 | 250 | 1120 | 1120 | 800 | 0 | 800 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-19 12:30 | 4.8 | 6.8 | 252.5 | 1120 | 1120 | 800 | 0 | 800 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-19 13:30 | 5.3 | 5.8 | 260 | 500 | 810 | 490 | 0 | 490 | 0 | 0 | 170611.6296 | 9.9968 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-11-19 14:30 | 5.1 | 4.1 | 257.5 | 76.6667 | 288.3333 | 0 | 31.6667 | 0 | 0 | 70.3704 | 170541.2593 | 9.9927 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-11-19 15:30 | 4.1 | 3.2 | 245 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 169915.3333 | 9.956 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-11-19 16:30 | 4 | 3.5 | 220 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 169204.2222 | 9.9143 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-11-19 17:30 | 4 | 4.2 | 230 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 168578.2963 | 9.8776 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-11-19 18:30 | 3.9 | 4.4 | 265 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 168037.5556 | 9.846 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-11-19 19:30 | 3.3 | 4 | 260 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 167496.8148 | 9.8143 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-11-19 20:30 | 3.1 | 3.7 | 247.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 166870.8889 | 9.7776 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-11-19 21:30 | 3.2 | 4.2 | 257.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 166244.963 | 9.7409 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-11-19 22:30 | 3.6 | 4.7 | 270 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 165840.5185 | 9.7172 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-11-19 23:30 | 4.2 | 5.2 | 275 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 165728.6667 | 9.7107 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-20 00:30 | 4.1 | 5.5 | 272.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 165778.6667 | 9.7136 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-20 01:30 | 4.2 | 5.8 | 270 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 165868.6667 | 9.7189 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-20 02:30 | 4.7 | 5.9 | 267.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 165958.6667 | 9.7241 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-20 03:30 | 4 | 6 | 255 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 166113.6667 | 9.7332 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-20 04:30 | 4 | 6.2 | 247.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 166333.6667 | 9.7461 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-20 05:30 | 4.1 | 6.6 | 252.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 166643.6667 | 9.7643 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-20 06:30 | 3.5 | 6.2 | 247.5 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 166953.6667 | 9.7824 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-20 07:30 | 2.8 | 4.9 | 237.5 | 199.3333 | 479.6667 | 159.6667 | 0 | 159.6667 | 79.8333 | 0 | 167033.5 | 9.7871 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-11-20 08:30 | 1.8 | 5.4 | 230 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 166921.6481 | 9.7806 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-20 09:30 | 2.3 | 7 | 222.5 | 1480 | 910 | 590 | 0 | 590 | 295 | 0 | 167216.6481 | 9.7979 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-20 10:30 | 4.1 | 8.2 | 220 | 2200 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 167861.6481 | 9.8356 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-20 11:30 | 5.2 | 9.1 | 217.5 | 2920 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 168506.6481 | 9.8734 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-20 12:30 | 5.5 | 9.7 | 210 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 169151.6481 | 9.9112 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-20 13:30 | 5.3 | 9.9 | 202.5 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 169796.6481 | 9.949 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-20 14:30 | 5.2 | 9.9 | 197.5 | 3280 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-20 15:30 | 5.6 | 10.5 | 190 | 4000 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-20 16:30 | 5.7 | 11.9 | 182.5 | 4472.2222 | 4236.1111 | 3916.1111 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-20 17:30 | 6.3 | 13.6 | 180 | 4600 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-20 18:30 | 6.2 | 14.6 | 180 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-20 19:30 | 5.8 | 15 | 185 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-20 20:30 | 6.2 | 14.9 | 197.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-20 21:30 | 6.9 | 14.1 | 215 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-20 22:30 | 7.2 | 13.9 | 232.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-20 23:30 | 7.5 | 14.5 | 240 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-21 00:30 | 7.9 | 15.3 | 240 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-21 01:30 | 7.8 | 15.9 | 242.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-21 02:30 | 7.6 | 16.1 | 245 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-21 03:30 | 7.6 | 16.1 | 242.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-21 04:30 | 7.8 | 16.1 | 237.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-21 05:30 | 8.1 | 15.8 | 232.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-21 06:30 | 7.9 | 15.8 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-21 07:30 | 7.9 | 15.7 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-21 08:30 | 7.8 | 15.4 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-21 09:30 | 7.9 | 15.9 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-21 10:30 | 8.4 | 16.9 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-21 11:30 | 8.6 | 17.1 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-21 12:30 | 8.3 | 16.5 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-21 13:30 | 7.6 | 15.3 | 232.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-21 14:30 | 7.7 | 14 | 235 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-21 15:30 | 7.6 | 12.9 | 232.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-21 16:30 | 7.4 | 12.4 | 230 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-21 17:30 | 7.8 | 12.4 | 230 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-21 18:30 | 8.1 | 12.7 | 230 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-21 19:30 | 8.4 | 13.6 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-21 20:30 | 8.3 | 14.2 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-21 21:30 | 8.3 | 13.8 | 235 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-21 22:30 | 7.4 | 13.5 | 247.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-21 23:30 | 6.8 | 13.9 | 260 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-22 00:30 | 7.2 | 13.8 | 265 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-22 01:30 | 6.8 | 12.9 | 262.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-22 02:30 | 6.8 | 12 | 260 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-22 03:30 | 6.8 | 10.4 | 257.5 | 3640 | 4088.0556 | 3768.0556 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-22 04:30 | 6.7 | 8.5 | 247.5 | 2560 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-22 05:30 | 6.8 | 7.3 | 232.5 | 1480 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-22 06:30 | 7 | 6.7 | 217.5 | 1120 | 1300 | 980 | 0 | 980 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-22 07:30 | 6.8 | 7.4 | 200 | 1480 | 1300 | 980 | 0 | 980 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-22 08:30 | 6.4 | 10.1 | 187.5 | 3640 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-22 09:30 | 6.4 | 13.6 | 190 | 4600 | 4120 | 3800 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-22 10:30 | 7.2 | 16.7 | 202.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-22 11:30 | 8.3 | 18.4 | 217.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-22 12:30 | 8.9 | 19.4 | 230 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-22 13:30 | 8.8 | 20.9 | 237.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-22 14:30 | 8.4 | 22.3 | 240 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-22 15:30 | 8.1 | 21.3 | 247.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-22 16:30 | 7.4 | 16.7 | 270 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-22 17:30 | 6.2 | 11.7 | 290 | 4472.2222 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-22 18:30 | 5 | 8.9 | 290 | 2560 | 3516.1111 | 3196.1111 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-22 19:30 | 4.2 | 7.7 | 277.5 | 1840 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-22 20:30 | 3.9 | 8.2 | 265 | 2200 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-22 21:30 | 4.6 | 9.5 | 262.5 | 3280 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-22 22:30 | 4.6 | 9.5 | 270 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-22 23:30 | 3.1 | 8.2 | 277.5 | 2200 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-23 00:30 | 2.5 | 7.7 | 275 | 1840 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-23 01:30 | 3.1 | 8 | 265 | 2200 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-23 02:30 | 3.9 | 7.6 | 255 | 1840 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-23 03:30 | 4.1 | 7.1 | 240 | 1480 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-23 04:30 | 4.2 | 8 | 222.5 | 2200 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-23 05:30 | 4.1 | 10 | 215 | 3640 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-23 06:30 | 4.1 | 10.9 | 222.5 | 4000 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-23 07:30 | 3.6 | 11.6 | 235 | 4472.2222 | 4236.1111 | 3916.1111 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-23 08:30 | 3.9 | 13 | 240 | 4600 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-23 09:30 | 5.3 | 13.3 | 240 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-23 10:30 | 5.1 | 13 | 240 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-23 11:30 | 5.5 | 12.3 | 240 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-23 12:30 | 5.9 | 11.4 | 240 | 4300 | 4418.0556 | 4098.0556 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-23 13:30 | 5.7 | 10.7 | 242.5 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-23 14:30 | 5.8 | 10.2 | 247.5 | 3640 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-23 15:30 | 5.5 | 9.7 | 250 | 3280 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-23 16:30 | 4.7 | 9 | 252.5 | 2920 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-23 17:30 | 4.5 | 8.3 | 257.5 | 2200 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-23 18:30 | 4.5 | 8.1 | 257.5 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-23 19:30 | 4.5 | 8 | 255 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-23 20:30 | 4.6 | 7.3 | 265 | 1480 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-23 21:30 | 4.5 | 6 | 272.5 | 760 | 1120 | 800 | 0 | 800 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-23 22:30 | 2.9 | 5.4 | 265 | 340 | 550 | 230 | 0 | 230 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-23 23:30 | 2.1 | 5.8 | 265 | 500 | 420 | 100 | 0 | 100 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-24 00:30 | 3 | 6.6 | 270 | 1120 | 810 | 490 | 0 | 490 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-24 01:30 | 2.7 | 7.1 | 267.5 | 1480 | 1300 | 980 | 0 | 980 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-24 02:30 | 2.8 | 7.2 | 260 | 1480 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-24 03:30 | 2.5 | 7.6 | 252.5 | 1840 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-24 04:30 | 2.9 | 8.5 | 250 | 2560 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-24 05:30 | 4 | 8.5 | 255 | 2560 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-24 06:30 | 3.4 | 7.9 | 257.5 | 1840 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-24 07:30 | 3 | 7.8 | 250 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-24 08:30 | 3 | 8 | 250 | 2200 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-24 09:30 | 3.5 | 8.4 | 257.5 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-24 10:30 | 4.3 | 8.9 | 260 | 2560 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-24 11:30 | 4.6 | 9 | 257.5 | 2920 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-24 12:30 | 4.5 | 8.9 | 252.5 | 2560 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-24 13:30 | 4.2 | 8.2 | 252.5 | 2200 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-24 14:30 | 3.9 | 7.3 | 260 | 1480 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-24 15:30 | 3.9 | 7 | 267.5 | 1480 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-24 16:30 | 3.7 | 7.1 | 265 | 1480 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-24 17:30 | 3.1 | 7.2 | 250 | 1480 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-24 18:30 | 2.2 | 6.8 | 237.5 | 1120 | 1300 | 980 | 0 | 980 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-24 19:30 | 1.9 | 6 | 242.5 | 760 | 940 | 620 | 0 | 620 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-24 20:30 | 2 | 5.8 | 252.5 | 500 | 630 | 310 | 0 | 310 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-24 21:30 | 2.4 | 6 | 257.5 | 760 | 630 | 310 | 0 | 310 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-24 22:30 | 2.3 | 6.2 | 260 | 760 | 760 | 440 | 0 | 440 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-24 23:30 | 2.1 | 6 | 255 | 760 | 760 | 440 | 0 | 440 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-25 00:30 | 1.9 | 5.4 | 250 | 340 | 550 | 230 | 0 | 230 | 0 | 0 | 170441.6481 | 9.9868 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-11-25 01:30 | 1.4 | 4.4 | 265 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 170193.5 | 9.9723 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-11-25 02:30 | 2 | 4.2 | 292.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 169652.7593 | 9.9406 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-11-25 03:30 | 2 | 4.1 | 290 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 169112.0185 | 9.9089 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-11-25 04:30 | 1.1 | 3 | 252.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 168486.0926 | 9.8722 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-11-25 05:30 | 0.8 | 2.2 | 237.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167774.9815 | 9.8306 | 0 |  |  | 1 | 6 | 1 | 1
Lerwick | 1978-11-25 06:30 | 0.4 | 2.4 | 260 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167063.8704 | 9.7889 | 0 |  |  | 1 | 7 | 1 | 2
Lerwick | 1978-11-25 07:30 | 1.1 | 2.9 | 275 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166352.7593 | 9.7472 | 0 |  |  | 1 | 8 | 1 | 3
Lerwick | 1978-11-25 08:30 | 1.7 | 3.9 | 265 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165641.6481 | 9.7056 | 0 |  |  | 1 | 9 | 1 | 4
Lerwick | 1978-11-25 09:30 | 1.8 | 4.7 | 252.5 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 165152.0185 | 9.6769 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-25 10:30 | 2.2 | 5.8 | 247.5 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 165166.8519 | 9.6777 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-25 11:30 | 2.2 | 6.9 | 235 | 1120 | 810 | 490 | 0 | 490 | 245 | 0 | 165411.8519 | 9.6921 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-25 12:30 | 2.2 | 7.3 | 232.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 165901.8519 | 9.7208 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-25 13:30 | 2.4 | 7.8 | 245 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 166546.8519 | 9.7586 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-25 14:30 | 3 | 8.1 | 250 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 167191.8519 | 9.7964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-25 15:30 | 3.4 | 8.4 | 250 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 167836.8519 | 9.8342 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-25 16:30 | 3.4 | 9 | 247.5 | 2920 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 168481.8519 | 9.872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-25 17:30 | 3.5 | 9 | 240 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 169126.8519 | 9.9098 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-25 18:30 | 3.1 | 8.2 | 240 | 2200 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 169771.8519 | 9.9476 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-25 19:30 | 2.4 | 7.4 | 252.5 | 1480 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 170416.8519 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-25 20:30 | 2.4 | 7.3 | 290 | 1480 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170416.8519 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-25 21:30 | 2.5 | 8.7 | 167.5 | 2560 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170416.8519 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-25 22:30 | 2.7 | 10.6 | 10 | 4000 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170416.8519 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-25 23:30 | 3.1 | 10.3 | 5 | 3640 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170416.8519 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-26 00:30 | 3 | 9.5 | 2.5 | 3280 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170416.8519 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-26 01:30 | 2.2 | 11.3 | 177.5 | 4300 | 3790 | 3470 | 0 | 1290 | 0 | 0 | 170416.8519 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-26 02:30 | 1.5 | 13.9 | 180 | 4600 | 4450 | 4130 | 0 | 1290 | 0 | 0 | 170416.8519 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-26 03:30 | 1.5 | 14.2 | 5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170416.8519 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-26 04:30 | 2 | 12.5 | 180 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170416.8519 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-26 05:30 | 2.3 | 11.4 | 352.5 | 4300 | 4450 | 4130 | 0 | 1290 | 0 | 0 | 170416.8519 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-26 06:30 | 2.2 | 10.9 | 350 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170416.8519 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-26 07:30 | 1.7 | 9.5 | 347.5 | 3280 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170416.8519 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-26 08:30 | 1.3 | 7.3 | 340 | 1480 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170416.8519 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-26 09:30 | 0.6 | 5.6 | 335 | 500 | 990 | 670 | 0 | 670 | 0 | 0 | 170416.8519 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-26 10:30 | 0.2 | 4.9 | 332.5 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 0 | 0 | 170416.8519 | 9.9854 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-11-26 11:30 | 1 | 4.6 | 330 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 170148.7037 | 9.9697 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-11-26 12:30 | 1.2 | 3.5 | 325 | 0 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 169659.0741 | 9.941 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-11-26 13:30 | 0.8 | 2.1 | 300 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168947.963 | 9.8993 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-11-26 14:30 | 0.8 | 2.5 | 267.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168236.8519 | 9.8576 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-11-26 15:30 | 0.5 | 4.7 | 252.5 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 167747.2222 | 9.8289 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-11-26 16:30 | 0.1 | 5.4 | 260 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 167635.3704 | 9.8224 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-11-26 17:30 | 0.1 | 4.9 | 282.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 167523.5185 | 9.8158 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-11-26 18:30 | 0.1 | 5.4 | 297.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 167411.6667 | 9.8093 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-26 19:30 | -0.1 | 6 | 300 | 760 | 550 | 230 | 0 | 230 | 115 | 0 | 167526.6667 | 9.816 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-26 20:30 | 0 | 6.7 | 307.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 167836.6667 | 9.8342 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-26 21:30 | 0.7 | 8.5 | 322.5 | 2560 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 168481.6667 | 9.872 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-26 22:30 | 0.6 | 10.6 | 330 | 4000 | 3280 | 2960 | 0 | 1290 | 645 | 0 | 169126.6667 | 9.9098 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-26 23:30 | -0.1 | 11.6 | 332.5 | 4472.2222 | 4236.1111 | 3916.1111 | 0 | 1290 | 645 | 0 | 169771.6667 | 9.9476 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-27 00:30 | -0.4 | 11.9 | 335 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 645 | 0 | 170416.6667 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-27 01:30 | -0.6 | 12.2 | 335 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170416.6667 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-27 02:30 | -0.9 | 12.2 | 335 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170416.6667 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-27 03:30 | -1.1 | 12 | 335 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170416.6667 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-27 04:30 | -1.4 | 11.7 | 335 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170416.6667 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-27 05:30 | -2.2 | 10.9 | 335 | 4000 | 4236.1111 | 3916.1111 | 0 | 1290 | 0 | 0 | 170416.6667 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-27 06:30 | -2.6 | 10 | 335 | 3640 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170416.6667 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-27 07:30 | -2.7 | 9.8 | 335 | 3280 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170416.6667 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-27 08:30 | -2.7 | 9.6 | 335 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170416.6667 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-27 09:30 | -2.7 | 9.5 | 332.5 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170416.6667 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-27 10:30 | -2.7 | 9.6 | 332.5 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170416.6667 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-27 11:30 | -2.6 | 9.6 | 335 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170416.6667 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-27 12:30 | -2.7 | 9.5 | 332.5 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170416.6667 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-27 13:30 | -2.4 | 9.4 | 330 | 2920 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170416.6667 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-27 14:30 | -2.3 | 9 | 330 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170416.6667 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-27 15:30 | -2.5 | 8.2 | 332.5 | 2200 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170416.6667 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-27 16:30 | -2 | 7.2 | 335 | 1480 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170416.6667 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-27 17:30 | -1.6 | 6.4 | 335 | 760 | 1120 | 800 | 0 | 800 | 0 | 0 | 170416.6667 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-27 18:30 | -1.5 | 6.2 | 335 | 760 | 760 | 440 | 0 | 440 | 0 | 0 | 170416.6667 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-27 19:30 | -1.5 | 6.3 | 330 | 760 | 760 | 440 | 0 | 440 | 0 | 0 | 170416.6667 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-27 20:30 | -1.5 | 6.1 | 327.5 | 760 | 760 | 440 | 0 | 440 | 0 | 0 | 170416.6667 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-27 21:30 | -1.1 | 5.8 | 335 | 500 | 630 | 310 | 0 | 310 | 0 | 0 | 170416.6667 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-27 22:30 | -1.5 | 5.8 | 340 | 500 | 500 | 180 | 0 | 180 | 0 | 0 | 170416.6667 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-27 23:30 | -1.8 | 6 | 335 | 760 | 630 | 310 | 0 | 310 | 0 | 0 | 170416.6667 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-28 00:30 | -1.3 | 6 | 327.5 | 760 | 760 | 440 | 0 | 440 | 0 | 0 | 170416.6667 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-28 01:30 | -1.4 | 5.8 | 325 | 500 | 630 | 310 | 0 | 310 | 0 | 0 | 170416.6667 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-28 02:30 | -1.4 | 5.8 | 322.5 | 500 | 500 | 180 | 0 | 180 | 0 | 0 | 170416.6667 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-28 03:30 | -0.9 | 5.9 | 322.5 | 500 | 500 | 180 | 0 | 180 | 0 | 0 | 170416.6667 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-28 04:30 | -0.6 | 5.9 | 330 | 500 | 500 | 180 | 0 | 180 | 0 | 0 | 170416.6667 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-28 05:30 | -1.1 | 5.9 | 337.5 | 500 | 500 | 180 | 0 | 180 | 0 | 0 | 170416.6667 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-28 06:30 | -1.3 | 5.8 | 337.5 | 500 | 500 | 180 | 0 | 180 | 0 | 0 | 170416.6667 | 9.9854 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-28 07:30 | -0.8 | 5.3 | 332.5 | 340 | 420 | 100 | 0 | 100 | 0 | 0 | 170416.6667 | 9.9854 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-11-28 08:30 | -1.2 | 4.7 | 330 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 170304.8148 | 9.9788 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-11-28 09:30 | -1.3 | 4.5 | 330 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 170036.6667 | 9.9631 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-11-28 10:30 | -0.5 | 4.2 | 330 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 169632.2222 | 9.9394 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-11-28 11:30 | -0.1 | 3.6 | 330 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 169006.2963 | 9.9027 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-11-28 12:30 | 0.1 | 2.9 | 327.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168295.1852 | 9.861 | 0 |  |  | 1 | 6 | 1 | 1
Lerwick | 1978-11-28 13:30 | 0.5 | 2 | 322.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167584.0741 | 9.8194 | 0 |  |  | 1 | 7 | 1 | 2
Lerwick | 1978-11-28 14:30 | 0.9 | 1 | 330 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166872.963 | 9.7777 | 0 |  |  | 1 | 8 | 1 | 3
Lerwick | 1978-11-28 15:30 | 0.8 | 0.2 | 170 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166161.8519 | 9.736 | 0 |  |  | 1 | 9 | 1 | 4
Lerwick | 1978-11-28 16:30 | -0.3 | 0.2 | 147.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165450.7407 | 9.6944 | 0 |  |  | 1 | 10 | 1 | 5
Lerwick | 1978-11-28 17:30 | -0.9 | 0.9 | 255 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164739.6296 | 9.6527 | 0 |  |  | 1 | 11 | 1 | 6
Lerwick | 1978-11-28 18:30 | -0.5 | 1.4 | 207.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164028.5185 | 9.611 | 0 |  |  | 1 | 12 | 1 | 7
Lerwick | 1978-11-28 19:30 | 0.3 | 1.8 | 197.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163317.4074 | 9.5694 | 0 |  |  | 1 | 13 | 1 | 8
Lerwick | 1978-11-28 20:30 | 1.1 | 2.7 | 190 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162606.2963 | 9.5277 | 0 |  |  | 1 | 14 | 1 | 9
Lerwick | 1978-11-28 21:30 | 1.5 | 3.6 | 185 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161895.1852 | 9.486 | 0 |  |  | 1 | 15 | 1 | 10
Lerwick | 1978-11-28 22:30 | 2.2 | 4.9 | 180 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 161405.5556 | 9.4574 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-28 23:30 | 2.6 | 6.9 | 170 | 1120 | 659.6667 | 339.6667 | 0 | 339.6667 | 169.8333 | 0 | 161575.3889 | 9.4673 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-29 00:30 | 2.9 | 8 | 170 | 2200 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 162220.3889 | 9.5051 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-29 01:30 | 3.4 | 7.6 | 180 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 162865.3889 | 9.5429 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-29 02:30 | 3.5 | 7.3 | 185 | 1480 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 163510.3889 | 9.5807 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-29 03:30 | 3.5 | 7.7 | 182.5 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 164155.3889 | 9.6185 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-29 04:30 | 3.8 | 8 | 180 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 164800.3889 | 9.6563 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-29 05:30 | 4 | 8.8 | 180 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 165445.3889 | 9.6941 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-29 06:30 | 4.2 | 9.2 | 180 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 166090.3889 | 9.7319 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-29 07:30 | 4.2 | 8.5 | 182.5 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 166735.3889 | 9.7697 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-29 08:30 | 4.2 | 8.4 | 185 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 167380.3889 | 9.8074 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-29 09:30 | 4.7 | 9 | 180 | 2920 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 168025.3889 | 9.8452 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-29 10:30 | 5 | 9.6 | 170 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 168670.3889 | 9.883 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-29 11:30 | 5 | 10.2 | 165 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 169315.3889 | 9.9208 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-29 12:30 | 5.1 | 10.4 | 165 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 169960.3889 | 9.9586 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-29 13:30 | 5.1 | 10.1 | 165 | 3640 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-29 14:30 | 5.2 | 10.4 | 167.5 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-29 15:30 | 5.6 | 10.9 | 170 | 4000 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-29 16:30 | 5.9 | 11.1 | 170 | 4300 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-29 17:30 | 5.8 | 11.1 | 167.5 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-29 18:30 | 5.8 | 10.9 | 162.5 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-29 19:30 | 5.8 | 11 | 162.5 | 4300 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-29 20:30 | 5.7 | 11.1 | 167.5 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-29 21:30 | 5.8 | 10.1 | 170 | 3640 | 3970 | 3650 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-29 22:30 | 6.1 | 8.4 | 170 | 2200 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-29 23:30 | 5.6 | 7.8 | 167.5 | 1840 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-30 00:30 | 4.7 | 8.7 | 162.5 | 2560 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-30 01:30 | 4.9 | 9.5 | 157.5 | 3280 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-30 02:30 | 5.2 | 9.9 | 152.5 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-30 03:30 | 5.2 | 10 | 152.5 | 3640 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-30 04:30 | 5.5 | 10.1 | 155 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-30 05:30 | 5.5 | 10.3 | 152.5 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-30 06:30 | 5.3 | 10 | 147.5 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-30 07:30 | 5.2 | 9.5 | 145 | 3280 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-30 08:30 | 4.9 | 9.4 | 150 | 2920 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-30 09:30 | 4.5 | 9.7 | 157.5 | 3280 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-30 10:30 | 4.3 | 10.4 | 157.5 | 3640 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-30 11:30 | 4.3 | 10.9 | 152.5 | 4000 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-30 12:30 | 4.4 | 10.5 | 152.5 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-30 13:30 | 4.7 | 9.7 | 157.5 | 3280 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-30 14:30 | 4.5 | 9.4 | 160 | 2920 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-30 15:30 | 4.1 | 9 | 157.5 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-30 16:30 | 3.8 | 8.8 | 150 | 2560 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-30 17:30 | 3.4 | 8.9 | 142.5 | 2560 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-30 18:30 | 3.6 | 9.4 | 140 | 2920 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-30 19:30 | 3.9 | 9.9 | 140 | 3280 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-30 20:30 | 3.9 | 9.5 | 137.5 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-30 21:30 | 4 | 8.5 | 135 | 2560 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-30 22:30 | 3.9 | 8.3 | 140 | 2200 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-11-30 23:30 | 3.6 | 8.6 | 145 | 2560 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-01 00:30 | 3.7 | 8.9 | 142.5 | 2560 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-01 01:30 | 3.9 | 9 | 140 | 2920 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-01 02:30 | 3.7 | 9 | 137.5 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-01 03:30 | 3.6 | 9.4 | 132.5 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-01 04:30 | 3.6 | 9.8 | 135 | 3280 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-01 05:30 | 3.6 | 9.6 | 142.5 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-01 06:30 | 3 | 9.5 | 140 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-01 07:30 | 2.4 | 9.6 | 132.5 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-01 08:30 | 3 | 9.9 | 135 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-01 09:30 | 3.4 | 9.7 | 142.5 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-01 10:30 | 3.4 | 9.6 | 142.5 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-01 11:30 | 3.8 | 9.9 | 137.5 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-01 12:30 | 3.8 | 9.7 | 132.5 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-01 13:30 | 3.7 | 9.4 | 132.5 | 2920 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-01 14:30 | 3.5 | 9.3 | 137.5 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-01 15:30 | 3.6 | 9.3 | 137.5 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-01 16:30 | 3.3 | 9.3 | 132.5 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-01 17:30 | 3.4 | 9.4 | 132.5 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-01 18:30 | 4.1 | 9.6 | 135 | 3280 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-01 19:30 | 3.7 | 9.6 | 132.5 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-01 20:30 | 3.8 | 9.5 | 130 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-01 21:30 | 4.3 | 9.5 | 127.5 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-01 22:30 | 4.1 | 9 | 125 | 2920 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-01 23:30 | 4.1 | 8.2 | 125 | 2200 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-02 00:30 | 4 | 8 | 125 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-02 01:30 | 3.8 | 8.4 | 125 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-02 02:30 | 4.1 | 8.8 | 127.5 | 2560 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-02 03:30 | 4.5 | 8.9 | 132.5 | 2560 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-02 04:30 | 4.2 | 9.4 | 135 | 2920 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-02 05:30 | 4.6 | 10 | 137.5 | 3640 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-02 06:30 | 5.1 | 10.6 | 140 | 4000 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-02 07:30 | 5.1 | 11.4 | 140 | 4300 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-02 08:30 | 5.3 | 11.9 | 140 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-02 09:30 | 5.7 | 12 | 140 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-02 10:30 | 6 | 12.2 | 140 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-02 11:30 | 5.6 | 12.4 | 140 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-02 12:30 | 5.4 | 12.1 | 140 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-02 13:30 | 5.8 | 11.8 | 140 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-02 14:30 | 6.1 | 11.9 | 140 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-02 15:30 | 6.1 | 12.2 | 140 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-02 16:30 | 6.2 | 12.8 | 140 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-02 17:30 | 6.4 | 13.2 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-02 18:30 | 6.3 | 13.4 | 137.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-02 19:30 | 6.2 | 13.4 | 132.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-02 20:30 | 6.2 | 13.5 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-02 21:30 | 6.1 | 13.6 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-02 22:30 | 6.1 | 13.5 | 132.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-02 23:30 | 6.1 | 13.2 | 137.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-03 00:30 | 5.7 | 12.8 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-03 01:30 | 5.7 | 12.4 | 140 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-03 02:30 | 5.9 | 12.1 | 140 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-03 03:30 | 6.2 | 11.6 | 140 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-03 04:30 | 6.6 | 11.6 | 140 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-03 05:30 | 6.8 | 11.9 | 140 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-03 06:30 | 6.8 | 12 | 140 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-03 07:30 | 6.8 | 12 | 140 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-03 08:30 | 6.8 | 11.7 | 142.5 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-03 09:30 | 6.6 | 11.2 | 150 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-03 10:30 | 6.7 | 11.4 | 155 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-03 11:30 | 7 | 11.9 | 152.5 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-03 12:30 | 7.2 | 11.9 | 150 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-03 13:30 | 7.1 | 11.8 | 147.5 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-03 14:30 | 6.9 | 11.8 | 142.5 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-03 15:30 | 7 | 11.6 | 140 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-03 16:30 | 6.9 | 11.6 | 140 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-03 17:30 | 6.7 | 12.1 | 140 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-03 18:30 | 6.7 | 12.5 | 140 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-03 19:30 | 6.8 | 12.5 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-03 20:30 | 6.7 | 12.4 | 137.5 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-03 21:30 | 6.7 | 12.4 | 132.5 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-03 22:30 | 6.8 | 13 | 130 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-03 23:30 | 6.4 | 14.1 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-04 00:30 | 6.1 | 14.8 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-04 01:30 | 5.8 | 15 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-04 02:30 | 5.8 | 15 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-04 03:30 | 6 | 14.8 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-04 04:30 | 6.1 | 14.8 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-04 05:30 | 6.3 | 14.8 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-04 06:30 | 6.2 | 14.7 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-04 07:30 | 6.1 | 14.8 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-04 08:30 | 6.4 | 14.8 | 132.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-04 09:30 | 6.1 | 14.4 | 135 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-04 10:30 | 5.8 | 14.3 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-04 11:30 | 5.5 | 14.3 | 122.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-04 12:30 | 5.3 | 14 | 122.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-04 13:30 | 5 | 14.1 | 127.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-04 14:30 | 4.4 | 14.4 | 127.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-04 15:30 | 4.6 | 14.4 | 122.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-04 16:30 | 4.9 | 14.3 | 120 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-04 17:30 | 5 | 13.9 | 120 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-04 18:30 | 5 | 13.6 | 120 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-04 19:30 | 5 | 13.9 | 120 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-04 20:30 | 5.1 | 14.3 | 120 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-04 21:30 | 5.1 | 14.5 | 120 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-04 22:30 | 5.1 | 14.5 | 122.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-04 23:30 | 5 | 14 | 127.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-05 00:30 | 5 | 13.7 | 127.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-05 01:30 | 5 | 14.1 | 125 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-05 02:30 | 5 | 14.4 | 125 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-05 03:30 | 5.2 | 14.3 | 125 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-05 04:30 | 5.2 | 13.9 | 127.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-05 05:30 | 5.4 | 13.3 | 132.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-05 06:30 | 5.8 | 12.8 | 135 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-05 07:30 | 6.1 | 12.4 | 132.5 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-05 08:30 | 6.3 | 12.4 | 130 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-05 09:30 | 6.5 | 12.7 | 130 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-05 10:30 | 6.5 | 12.7 | 132.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-05 11:30 | 6.2 | 12.4 | 140 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-05 12:30 | 6.1 | 12.4 | 150 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-05 13:30 | 6.5 | 12.2 | 157.5 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-05 14:30 | 6.9 | 11.6 | 160 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-05 15:30 | 7.2 | 11.3 | 160 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-05 16:30 | 7.3 | 11.3 | 160 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-05 17:30 | 7.2 | 11.1 | 160 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-05 18:30 | 7.2 | 11 | 157.5 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-05 19:30 | 7.2 | 11 | 152.5 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-05 20:30 | 7.1 | 10.9 | 150 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-05 21:30 | 7 | 10.8 | 150 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-05 22:30 | 6.8 | 10.6 | 150 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-05 23:30 | 6.6 | 10.4 | 150 | 3640 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-06 00:30 | 6.6 | 10.3 | 150 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-06 01:30 | 6.5 | 10.3 | 150 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-06 02:30 | 6.3 | 10.3 | 147.5 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-06 03:30 | 6.2 | 10.3 | 142.5 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-06 04:30 | 6.1 | 10.3 | 140 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-06 05:30 | 6 | 10.4 | 140 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-06 06:30 | 6.2 | 10.7 | 140 | 4000 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-06 07:30 | 6.3 | 11.1 | 140 | 4300 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-06 08:30 | 6.2 | 11.3 | 140 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-06 09:30 | 6.2 | 11.3 | 140 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-06 10:30 | 6.2 | 11.3 | 140 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-06 11:30 | 6.1 | 11.4 | 140 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-06 12:30 | 6 | 11.6 | 140 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-06 13:30 | 6 | 11.8 | 140 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-06 14:30 | 6 | 11.9 | 140 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-06 15:30 | 6 | 12.2 | 140 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-06 16:30 | 6 | 12.7 | 140 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-06 17:30 | 6 | 13 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-06 18:30 | 5.9 | 13.2 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-06 19:30 | 5.9 | 13.4 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-06 20:30 | 5.9 | 13.4 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-06 21:30 | 5.9 | 13.5 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-06 22:30 | 5.7 | 13.6 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-06 23:30 | 5.3 | 13.3 | 137.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-07 00:30 | 5.3 | 13.1 | 135 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-07 01:30 | 5.4 | 13.1 | 137.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-07 02:30 | 5.5 | 13.1 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-07 03:30 | 5.6 | 13.5 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-07 04:30 | 5.5 | 14 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-07 05:30 | 5.4 | 14 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-07 06:30 | 5.4 | 13.9 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-07 07:30 | 5.4 | 13.7 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-07 08:30 | 5.3 | 13.3 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-07 09:30 | 5.3 | 13.2 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-07 10:30 | 5.4 | 13.6 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-07 11:30 | 5.4 | 13.7 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-07 12:30 | 5.4 | 13.6 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-07 13:30 | 5.4 | 13.7 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-07 14:30 | 5.2 | 14 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-07 15:30 | 5.1 | 14 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-07 16:30 | 5.3 | 13.7 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-07 17:30 | 5.3 | 14.1 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-07 18:30 | 5.2 | 15.2 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-07 19:30 | 5.2 | 15.7 | 140 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-07 20:30 | 5.2 | 15.7 | 137.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-07 21:30 | 5.1 | 15.8 | 132.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-07 22:30 | 5 | 16.1 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-07 23:30 | 4.9 | 16.3 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-08 00:30 | 4.9 | 16.6 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-08 01:30 | 5 | 17 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-08 02:30 | 4.9 | 17.3 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-08 03:30 | 4.9 | 17.1 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-08 04:30 | 4.8 | 17 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-08 05:30 | 4.8 | 16.8 | 127.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-08 06:30 | 4.7 | 16.6 | 122.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-08 07:30 | 4.5 | 16.5 | 120 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-08 08:30 | 4.6 | 16.5 | 120 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-08 09:30 | 4.7 | 16.2 | 120 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-08 10:30 | 4.7 | 15.8 | 120 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-08 11:30 | 4.7 | 15.7 | 120 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-08 12:30 | 4.7 | 15.5 | 120 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-08 13:30 | 4.6 | 15.4 | 120 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-08 14:30 | 4.5 | 15.4 | 117.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-08 15:30 | 4.5 | 15.5 | 112.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-08 16:30 | 4.5 | 15.5 | 110 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-08 17:30 | 4.5 | 15.1 | 110 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-08 18:30 | 4.4 | 14.8 | 110 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-08 19:30 | 4.1 | 14.4 | 110 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-08 20:30 | 3.9 | 13.8 | 110 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-08 21:30 | 3.9 | 13.1 | 110 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-08 22:30 | 3.8 | 12.7 | 110 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-08 23:30 | 3.6 | 12.2 | 107.5 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-09 00:30 | 3.6 | 11.7 | 105 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-09 01:30 | 3.7 | 11.1 | 107.5 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-09 02:30 | 3.7 | 10.5 | 107.5 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-09 03:30 | 3.6 | 10.3 | 105 | 3640 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-09 04:30 | 3.4 | 10.3 | 105 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-09 05:30 | 3.3 | 10.1 | 102.5 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-09 06:30 | 3.3 | 9.6 | 100 | 3280 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-09 07:30 | 3.3 | 8.9 | 100 | 2560 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-09 08:30 | 3.4 | 8.2 | 102.5 | 2200 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-09 09:30 | 3.2 | 8 | 107.5 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-09 10:30 | 3.3 | 8 | 110 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-09 11:30 | 3.6 | 8 | 107.5 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-09 12:30 | 3.6 | 8.2 | 102.5 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-09 13:30 | 3.6 | 8.6 | 100 | 2560 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-09 14:30 | 3.7 | 8.9 | 102.5 | 2560 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-09 15:30 | 3.7 | 9 | 105 | 2920 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-09 16:30 | 3.7 | 8.9 | 105 | 2560 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-09 17:30 | 3.7 | 8.6 | 107.5 | 2560 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-09 18:30 | 3.9 | 8.3 | 110 | 2200 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-09 19:30 | 4.1 | 8 | 110 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-09 20:30 | 4.3 | 7.8 | 110 | 1840 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-09 21:30 | 4.4 | 7.7 | 110 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-09 22:30 | 4.4 | 7.7 | 110 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-09 23:30 | 4.4 | 7.6 | 110 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-10 00:30 | 4.6 | 7.3 | 112.5 | 1480 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-10 01:30 | 4.8 | 7.3 | 117.5 | 1480 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-10 02:30 | 4.8 | 7.6 | 120 | 1840 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-10 03:30 | 4.9 | 7.7 | 120 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-10 04:30 | 5 | 7.6 | 120 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-10 05:30 | 5.1 | 7.6 | 120 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-10 06:30 | 5.2 | 7.9 | 120 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-10 07:30 | 5.3 | 8.3 | 117.5 | 2200 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-10 08:30 | 5.4 | 8.9 | 115 | 2560 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-10 09:30 | 5.4 | 9.5 | 115 | 3280 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-10 10:30 | 5.5 | 10.1 | 117.5 | 3640 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-10 11:30 | 5.7 | 11 | 125 | 4300 | 3970 | 3650 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-10 12:30 | 5.9 | 11.7 | 130 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-10 13:30 | 6 | 12.2 | 130 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-10 14:30 | 6.2 | 12.7 | 127.5 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-10 15:30 | 6.3 | 12.7 | 122.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-10 16:30 | 6.5 | 12.5 | 120 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-10 17:30 | 6.7 | 12.7 | 122.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-10 18:30 | 6.8 | 12.9 | 127.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-10 19:30 | 7.1 | 12.9 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-10 20:30 | 7.1 | 13 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-10 21:30 | 6.8 | 13.1 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-10 22:30 | 6.7 | 12.8 | 132.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-10 23:30 | 6.6 | 12.4 | 137.5 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-11 00:30 | 6.8 | 12.4 | 140 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-11 01:30 | 7.1 | 11.9 | 140 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-11 02:30 | 7.2 | 11.1 | 140 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-11 03:30 | 7.3 | 10.3 | 142.5 | 3640 | 3970 | 3650 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-11 04:30 | 7.4 | 9.5 | 147.5 | 3280 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-11 05:30 | 7.7 | 9.5 | 150 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-11 06:30 | 7.9 | 9.6 | 150 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-11 07:30 | 8 | 9 | 147.5 | 2920 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-11 08:30 | 8 | 8.6 | 142.5 | 2560 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-11 09:30 | 8 | 9.5 | 140 | 3280 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-11 10:30 | 7.8 | 10.4 | 140 | 3640 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-11 11:30 | 7.6 | 10.5 | 140 | 4000 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-11 12:30 | 7.5 | 10.4 | 137.5 | 3640 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-11 13:30 | 7.5 | 9.9 | 132.5 | 3280 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-11 14:30 | 7.5 | 9.4 | 130 | 2920 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-11 15:30 | 7.6 | 9.5 | 130 | 3280 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-11 16:30 | 7.7 | 10.3 | 130 | 3640 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-11 17:30 | 7.8 | 11 | 130 | 4300 | 3970 | 3650 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-11 18:30 | 7.8 | 11.6 | 130 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-11 19:30 | 7.8 | 12.4 | 130 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-11 20:30 | 7.7 | 13 | 130 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-11 21:30 | 7.6 | 13.2 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-11 22:30 | 7.5 | 13.8 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-11 23:30 | 7.3 | 14.7 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-12 00:30 | 7 | 15.2 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-12 01:30 | 6.8 | 15 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-12 02:30 | 6.7 | 14.8 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-12 03:30 | 6.7 | 14.5 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-12 04:30 | 6.7 | 14.5 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-12 05:30 | 6.6 | 14.8 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-12 06:30 | 6.6 | 14.9 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-12 07:30 | 6.6 | 14.9 | 130 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-12 08:30 | 6.6 | 14.8 | 127.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-12 09:30 | 6.4 | 14.7 | 122.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-12 10:30 | 6.2 | 14.7 | 120 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-12 11:30 | 6.3 | 14.7 | 117.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-12 12:30 | 6.5 | 14.9 | 112.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-12 13:30 | 6.5 | 15.4 | 110 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-12 14:30 | 6.5 | 16.1 | 110 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-12 15:30 | 6.6 | 16.2 | 110 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-12 16:30 | 6.6 | 14.9 | 112.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-12 17:30 | 6.6 | 13.4 | 117.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-12 18:30 | 6.8 | 12.7 | 120 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-12 19:30 | 7 | 12.2 | 120 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-12 20:30 | 6.9 | 11.7 | 117.5 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-12 21:30 | 6.8 | 11.7 | 112.5 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-12 22:30 | 6.8 | 12.2 | 110 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-12 23:30 | 6.9 | 12.4 | 107.5 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-13 00:30 | 6.7 | 12.7 | 102.5 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-13 01:30 | 6.3 | 13.1 | 100 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-13 02:30 | 6.2 | 12.8 | 100 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-13 03:30 | 6.2 | 12.2 | 102.5 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-13 04:30 | 6 | 11.9 | 105 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-13 05:30 | 6 | 11.8 | 102.5 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-13 06:30 | 6.2 | 11.9 | 100 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-13 07:30 | 6.4 | 12 | 97.5 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-13 08:30 | 6.2 | 11.7 | 92.5 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-13 09:30 | 5.8 | 11.2 | 90 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-13 10:30 | 5.7 | 10.9 | 90 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-13 11:30 | 5.6 | 10.8 | 90 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-13 12:30 | 5.5 | 10.6 | 90 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-13 13:30 | 5.6 | 10.4 | 90 | 3640 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-13 14:30 | 5.6 | 10.1 | 90 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-13 15:30 | 5.6 | 9.7 | 90 | 3280 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-13 16:30 | 5.7 | 9.2 | 87.5 | 2920 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-13 17:30 | 5.7 | 8.7 | 82.5 | 2560 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-13 18:30 | 5.8 | 8.3 | 80 | 2200 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-13 19:30 | 5.8 | 8 | 80 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-13 20:30 | 5.8 | 7.8 | 80 | 1840 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-13 21:30 | 5.8 | 7.6 | 82.5 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-13 22:30 | 5.6 | 7.2 | 87.5 | 1480 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-13 23:30 | 5.5 | 6.7 | 90 | 1120 | 1300 | 980 | 0 | 980 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-14 00:30 | 5.5 | 6.1 | 90 | 760 | 940 | 620 | 0 | 620 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-14 01:30 | 5.3 | 5.9 | 90 | 500 | 630 | 310 | 0 | 310 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-14 02:30 | 5.2 | 5.6 | 87.5 | 500 | 500 | 180 | 0 | 180 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-14 03:30 | 5 | 4.9 | 80 | 199.3333 | 349.6667 | 29.6667 | 0 | 29.6667 | 0 | 0 | 170605.3889 | 9.9964 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-12-14 04:30 | 4.6 | 4.4 | 77.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 170200.9444 | 9.9727 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-12-14 05:30 | 4.5 | 4.2 | 85 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 169660.2037 | 9.941 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-12-14 06:30 | 4.5 | 3.8 | 87.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 169034.2778 | 9.9044 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-12-14 07:30 | 4.4 | 3.6 | 82.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168323.1667 | 9.8627 | 0 |  |  | 1 | 5 | 1 | 1
Lerwick | 1978-12-14 08:30 | 4.5 | 4 | 85 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 167697.2407 | 9.826 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-12-14 09:30 | 4.7 | 4.4 | 95 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 167156.5 | 9.7943 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-12-14 10:30 | 4.6 | 4.5 | 95 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 166752.0556 | 9.7706 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-12-14 11:30 | 4.5 | 4.5 | 87.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 166483.9074 | 9.7549 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-12-14 12:30 | 4.5 | 4.5 | 90 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 166215.7593 | 9.7392 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-12-14 13:30 | 4.6 | 4.5 | 95 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 165947.6111 | 9.7235 | 1 |  |  | 1 | 11 | 0 | 0
Lerwick | 1978-12-14 14:30 | 4.8 | 4.5 | 90 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 165679.463 | 9.7078 | 1 |  |  | 1 | 12 | 0 | 0
Lerwick | 1978-12-14 15:30 | 4.8 | 4.4 | 85 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 165275.0185 | 9.6841 | 1 |  |  | 1 | 13 | 0 | 0
Lerwick | 1978-12-14 16:30 | 4.5 | 4.2 | 87.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 164734.2778 | 9.6524 | 1 |  |  | 1 | 14 | 0 | 0
Lerwick | 1978-12-14 17:30 | 4.3 | 3.9 | 87.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 164108.3519 | 9.6157 | 1 |  |  | 1 | 15 | 0 | 0
Lerwick | 1978-12-14 18:30 | 4.3 | 3.7 | 82.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163397.2407 | 9.5741 | 0 |  |  | 1 | 16 | 1 | 1
Lerwick | 1978-12-14 19:30 | 4.3 | 3.4 | 82.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162686.1296 | 9.5324 | 0 |  |  | 1 | 17 | 1 | 2
Lerwick | 1978-12-14 20:30 | 4.4 | 2.9 | 80 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161975.0185 | 9.4907 | 0 |  |  | 1 | 18 | 1 | 3
Lerwick | 1978-12-14 21:30 | 4.5 | 2 | 55 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161263.9074 | 9.4491 | 0 |  |  | 1 | 19 | 1 | 4
Lerwick | 1978-12-14 22:30 | 4.4 | 1.6 | 25 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 160552.7963 | 9.4074 | 0 |  |  | 1 | 20 | 1 | 5
Lerwick | 1978-12-14 23:30 | 4.4 | 2.9 | 17.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 159841.6852 | 9.3657 | 0 |  |  | 1 | 21 | 1 | 6
Lerwick | 1978-12-15 00:30 | 4.3 | 4.9 | 22.5 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 159352.0556 | 9.337 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-15 01:30 | 3.9 | 6.1 | 27.5 | 760 | 479.6667 | 159.6667 | 0 | 159.6667 | 79.8333 | 0 | 159431.8889 | 9.3417 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-15 02:30 | 3.9 | 6.8 | 27.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 159741.8889 | 9.3599 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-15 03:30 | 4.3 | 7.3 | 22.5 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 160231.8889 | 9.3886 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-15 04:30 | 4.5 | 7.6 | 20 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 160876.8889 | 9.4264 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-15 05:30 | 4.4 | 7.9 | 17.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 161521.8889 | 9.4642 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-15 06:30 | 4.2 | 8.1 | 15 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 162166.8889 | 9.502 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-15 07:30 | 3.8 | 8.4 | 15 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 162811.8889 | 9.5398 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-15 08:30 | 3.3 | 9 | 12.5 | 2920 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 163456.8889 | 9.5776 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-15 09:30 | 3.1 | 9.3 | 10 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 164101.8889 | 9.6153 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-15 10:30 | 3.3 | 9.1 | 7.5 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 164746.8889 | 9.6531 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-15 11:30 | 3 | 8.7 | 2.5 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 165391.8889 | 9.6909 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-15 12:30 | 2.7 | 8.2 | 0 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 166036.8889 | 9.7287 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-15 13:30 | 2.4 | 8 | 177.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 166681.8889 | 9.7665 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-15 14:30 | 2.4 | 8 | 355 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 167326.8889 | 9.8043 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-15 15:30 | 2.1 | 7.8 | 177.5 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 167971.8889 | 9.8421 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-15 16:30 | 1.9 | 7.8 | 0 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 168616.8889 | 9.8799 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-15 17:30 | 2.3 | 7.6 | 0 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 169261.8889 | 9.9177 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-15 18:30 | 2.3 | 6.7 | 0 | 1120 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 169841.8889 | 9.9517 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-15 19:30 | 2.5 | 6.2 | 0 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 170151.8889 | 9.9698 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-15 20:30 | 2.6 | 6.3 | 177.5 | 760 | 760 | 440 | 0 | 440 | 0 | 0 | 170151.8889 | 9.9698 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-15 21:30 | 2.2 | 6.5 | 352.5 | 1120 | 940 | 620 | 0 | 620 | 0 | 0 | 170151.8889 | 9.9698 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-15 22:30 | 1.4 | 6.3 | 352.5 | 760 | 940 | 620 | 0 | 620 | 0 | 0 | 170151.8889 | 9.9698 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-15 23:30 | 1.7 | 5.6 | 352.5 | 500 | 630 | 310 | 0 | 310 | 0 | 0 | 170151.8889 | 9.9698 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-16 00:30 | 2.5 | 5.2 | 347.5 | 340 | 420 | 100 | 0 | 100 | 0 | 0 | 170151.8889 | 9.9698 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-12-16 01:30 | 2.3 | 4.4 | 342.5 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 169903.7407 | 9.9553 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-12-16 02:30 | 2.1 | 3.5 | 327.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 169277.8148 | 9.9186 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-12-16 03:30 | 2 | 3.2 | 307.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168566.7037 | 9.877 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-12-16 04:30 | 2.2 | 3.6 | 297.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167855.5926 | 9.8353 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-12-16 05:30 | 2.4 | 3.9 | 295 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167144.4815 | 9.7936 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-12-16 06:30 | 2.1 | 3.9 | 297.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166433.3704 | 9.752 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-12-16 07:30 | 1.5 | 3.9 | 302.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165722.2593 | 9.7103 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-12-16 08:30 | 1.5 | 4 | 307.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 165096.3333 | 9.6736 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-12-16 09:30 | 1.5 | 4 | 307.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 164555.5926 | 9.6419 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-12-16 10:30 | 1.6 | 4 | 305 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 164014.8519 | 9.6102 | 1 |  |  | 1 | 11 | 0 | 0
Lerwick | 1978-12-16 11:30 | 2.2 | 4.2 | 312.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 163474.1111 | 9.5786 | 1 |  |  | 1 | 12 | 0 | 0
Lerwick | 1978-12-16 12:30 | 2.2 | 5.3 | 327.5 | 340 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 163225.963 | 9.564 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-16 13:30 | 1.8 | 6.9 | 340 | 1120 | 730 | 410 | 0 | 410 | 205 | 0 | 163430.963 | 9.576 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-16 14:30 | 1.4 | 7.9 | 342.5 | 1840 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 164010.963 | 9.61 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-16 15:30 | 1.4 | 8.3 | 335 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 164655.963 | 9.6478 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-16 16:30 | 1.7 | 8.6 | 330 | 2560 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 165300.963 | 9.6856 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-16 17:30 | 1.5 | 8.6 | 335 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 165945.963 | 9.7234 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-16 18:30 | 1.1 | 8.6 | 347.5 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 166590.963 | 9.7612 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-16 19:30 | 1.4 | 9.1 | 177.5 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 167235.963 | 9.799 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-16 20:30 | 1.7 | 9.4 | 0 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 167880.963 | 9.8368 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-16 21:30 | 1.5 | 8.9 | 177.5 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 168525.963 | 9.8746 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-16 22:30 | 1.4 | 8.2 | 355 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 169170.963 | 9.9124 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-16 23:30 | 0.7 | 8 | 355 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 169815.963 | 9.9502 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-17 00:30 | 0.1 | 8 | 355 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 170460.963 | 9.9879 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-17 01:30 | 0.2 | 7.3 | 355 | 1480 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170460.963 | 9.9879 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-17 02:30 | 0.7 | 6.2 | 350 | 760 | 1120 | 800 | 0 | 800 | 0 | 0 | 170460.963 | 9.9879 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-17 03:30 | 0.8 | 5.3 | 340 | 340 | 550 | 230 | 0 | 230 | 0 | 0 | 170460.963 | 9.9879 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-12-17 04:30 | 0.5 | 4.7 | 335 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 170349.1111 | 9.9814 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-12-17 05:30 | 0.5 | 4 | 335 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 169944.6667 | 9.9577 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-12-17 06:30 | 0.5 | 3.3 | 327.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 169318.7407 | 9.921 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-12-17 07:30 | 0.5 | 2.8 | 315 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168607.6296 | 9.8794 | 0 |  |  | 1 | 5 | 1 | 1
Lerwick | 1978-12-17 08:30 | 0.7 | 1.8 | 322.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167896.5185 | 9.8377 | 0 |  |  | 1 | 6 | 1 | 2
Lerwick | 1978-12-17 09:30 | 0.7 | 0.5 | 167.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167185.4074 | 9.796 | 0 |  |  | 1 | 7 | 1 | 3
Lerwick | 1978-12-17 10:30 | 0.2 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166474.2963 | 9.7544 | 0 |  |  | 1 | 8 | 1 | 4
Lerwick | 1978-12-17 11:30 | 0 | 0.5 | 137.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165763.1852 | 9.7127 | 0 |  |  | 1 | 9 | 1 | 5
Lerwick | 1978-12-17 12:30 | 1.1 | 1.8 | 235 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 165052.0741 | 9.671 | 0 |  |  | 1 | 10 | 1 | 6
Lerwick | 1978-12-17 13:30 | 1.6 | 3.3 | 197.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 164340.963 | 9.6294 | 0 |  |  | 1 | 11 | 1 | 7
Lerwick | 1978-12-17 14:30 | 1.5 | 3.9 | 200 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163629.8519 | 9.5877 | 0 |  |  | 1 | 12 | 1 | 8
Lerwick | 1978-12-17 15:30 | 1.9 | 4.2 | 202.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 163003.9259 | 9.551 | 1 |  |  | 1 | 13 | 0 | 0
Lerwick | 1978-12-17 16:30 | 2.1 | 5.2 | 212.5 | 340 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 162755.7778 | 9.5365 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-17 17:30 | 2.4 | 5.9 | 222.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 162805.7778 | 9.5394 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-17 18:30 | 2.6 | 5.6 | 222.5 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 162895.7778 | 9.5447 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-17 19:30 | 2.5 | 6 | 217.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 163050.7778 | 9.5538 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-17 20:30 | 2.9 | 7.6 | 212.5 | 1840 | 1300 | 980 | 0 | 980 | 490 | 0 | 163540.7778 | 9.5825 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-17 21:30 | 3.4 | 8.7 | 210 | 2560 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 164185.7778 | 9.6203 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-17 22:30 | 3.6 | 9.1 | 212.5 | 2920 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 164830.7778 | 9.6581 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-17 23:30 | 3.9 | 9.8 | 217.5 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 165475.7778 | 9.6958 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-18 00:30 | 4.2 | 10.6 | 220 | 4000 | 3640 | 3320 | 0 | 1290 | 645 | 0 | 166120.7778 | 9.7336 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-18 01:30 | 4.6 | 11.1 | 220 | 4300 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 166765.7778 | 9.7714 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-18 02:30 | 4.9 | 11.1 | 220 | 4300 | 4300 | 3980 | 0 | 1290 | 645 | 0 | 167410.7778 | 9.8092 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-18 03:30 | 4.9 | 10.9 | 220 | 4000 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 168055.7778 | 9.847 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-18 04:30 | 4.8 | 10.6 | 220 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 168700.7778 | 9.8848 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-18 05:30 | 5.2 | 10.5 | 220 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 169345.7778 | 9.9226 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-18 06:30 | 5.5 | 10.7 | 220 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 169990.7778 | 9.9604 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-18 07:30 | 5.6 | 11.1 | 217.5 | 4300 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 170635.7778 | 9.9982 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-18 08:30 | 5.6 | 11.4 | 212.5 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170635.7778 | 9.9982 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-18 09:30 | 5.6 | 11.5 | 210 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170635.7778 | 9.9982 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-18 10:30 | 5.8 | 11.5 | 210 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170635.7778 | 9.9982 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-18 11:30 | 6.1 | 11.6 | 212.5 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170635.7778 | 9.9982 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-18 12:30 | 6.3 | 11.8 | 215 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170635.7778 | 9.9982 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-18 13:30 | 6.5 | 11.8 | 212.5 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170635.7778 | 9.9982 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-18 14:30 | 6.6 | 11.6 | 210 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170635.7778 | 9.9982 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-18 15:30 | 6.6 | 11.5 | 210 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170635.7778 | 9.9982 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-18 16:30 | 6.6 | 11.6 | 210 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170635.7778 | 9.9982 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-18 17:30 | 6.6 | 11.9 | 210 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170635.7778 | 9.9982 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-18 18:30 | 6.6 | 12 | 210 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170635.7778 | 9.9982 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-18 19:30 | 6.6 | 11.9 | 210 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170635.7778 | 9.9982 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-18 20:30 | 6.7 | 11.4 | 210 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170635.7778 | 9.9982 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-18 21:30 | 6.7 | 9.9 | 207.5 | 3280 | 3790 | 3470 | 0 | 1290 | 0 | 0 | 170635.7778 | 9.9982 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-18 22:30 | 6.4 | 7.9 | 202.5 | 1840 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170635.7778 | 9.9982 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-18 23:30 | 6 | 6.4 | 200 | 760 | 1300 | 980 | 0 | 980 | 0 | 0 | 170635.7778 | 9.9982 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-19 00:30 | 5.9 | 5.4 | 197.5 | 340 | 550 | 230 | 0 | 230 | 0 | 0 | 170635.7778 | 9.9982 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-12-19 01:30 | 5.8 | 4.7 | 192.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 170523.9259 | 9.9916 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-12-19 02:30 | 5.3 | 4.7 | 192.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 170255.7778 | 9.9759 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-12-19 03:30 | 4.7 | 5.3 | 197.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 170143.9259 | 9.9694 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-19 04:30 | 3.9 | 5.5 | 197.5 | 500 | 420 | 100 | 0 | 100 | 0 | 0 | 170143.9259 | 9.9694 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-19 05:30 | 3.4 | 5.2 | 195 | 340 | 420 | 100 | 0 | 100 | 0 | 0 | 170143.9259 | 9.9694 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-12-19 06:30 | 3.3 | 4.7 | 195 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 170032.0741 | 9.9628 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-12-19 07:30 | 3.4 | 4 | 195 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 169627.6296 | 9.9391 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-12-19 08:30 | 3.5 | 3.8 | 200 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 169001.7037 | 9.9024 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-12-19 09:30 | 3.5 | 4.4 | 207.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 168375.7778 | 9.8658 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-12-19 10:30 | 3.6 | 4.9 | 207.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 167971.3333 | 9.8421 | 1 |  |  | 1 | 6 | 0 | 0
Lerwick | 1978-12-19 11:30 | 4.2 | 5 | 202.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 167859.4815 | 9.8355 | 1 |  |  | 1 | 7 | 0 | 0
Lerwick | 1978-12-19 12:30 | 5.2 | 4.9 | 202.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 167747.6296 | 9.829 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-12-19 13:30 | 5.4 | 4.7 | 205 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 167479.4815 | 9.8133 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-12-19 14:30 | 5.2 | 4.7 | 202.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 167211.3333 | 9.7975 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-12-19 15:30 | 4.9 | 5 | 202.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 167099.4815 | 9.791 | 1 |  |  | 1 | 11 | 0 | 0
Lerwick | 1978-12-19 16:30 | 5.2 | 4.7 | 207.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 166987.6296 | 9.7844 | 1 |  |  | 1 | 12 | 0 | 0
Lerwick | 1978-12-19 17:30 | 5.3 | 4.6 | 207.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 166719.4815 | 9.7687 | 1 |  |  | 1 | 13 | 0 | 0
Lerwick | 1978-12-19 18:30 | 5.4 | 4.9 | 205 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 166451.3333 | 9.753 | 1 |  |  | 1 | 14 | 0 | 0
Lerwick | 1978-12-19 19:30 | 5.8 | 4.7 | 200 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 166183.1852 | 9.7373 | 1 |  |  | 1 | 15 | 0 | 0
Lerwick | 1978-12-19 20:30 | 5.7 | 4.7 | 192.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 165915.037 | 9.7216 | 1 |  |  | 1 | 16 | 0 | 0
Lerwick | 1978-12-19 21:30 | 5.3 | 5 | 192.5 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 165803.1852 | 9.715 | 1 |  |  | 1 | 17 | 0 | 0
Lerwick | 1978-12-19 22:30 | 5.2 | 4.5 | 192.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 165691.3333 | 9.7085 | 1 |  |  | 1 | 18 | 0 | 0
Lerwick | 1978-12-19 23:30 | 5 | 4 | 187.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 165286.8889 | 9.6848 | 1 |  |  | 1 | 19 | 0 | 0
Lerwick | 1978-12-20 00:30 | 4.5 | 4.2 | 185 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 164746.1481 | 9.6531 | 1 |  |  | 1 | 20 | 0 | 0
Lerwick | 1978-12-20 01:30 | 4.3 | 4.6 | 182.5 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 164341.7037 | 9.6294 | 1 |  |  | 1 | 21 | 0 | 0
Lerwick | 1978-12-20 02:30 | 4.2 | 4.9 | 180 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 164073.5556 | 9.6137 | 1 |  |  | 1 | 22 | 0 | 0
Lerwick | 1978-12-20 03:30 | 4.7 | 4.9 | 180 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 163805.4074 | 9.598 | 1 |  |  | 1 | 23 | 0 | 0
Lerwick | 1978-12-20 04:30 | 5.6 | 5.1 | 175 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 163693.5556 | 9.5914 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-20 05:30 | 5.8 | 5.5 | 170 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 163743.5556 | 9.5943 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-20 06:30 | 5.8 | 5.7 | 170 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 163833.5556 | 9.5996 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-20 07:30 | 5.7 | 5.7 | 170 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 163923.5556 | 9.6049 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-20 08:30 | 5.6 | 5.8 | 170 | 500 | 500 | 180 | 0 | 180 | 90 | 0 | 164013.5556 | 9.6102 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-20 09:30 | 5.6 | 6.3 | 170 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 164168.5556 | 9.6193 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-20 10:30 | 5.5 | 6.5 | 172.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 164478.5556 | 9.6374 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-20 11:30 | 5.5 | 5.6 | 182.5 | 500 | 810 | 490 | 0 | 490 | 245 | 0 | 164723.5556 | 9.6518 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-12-20 12:30 | 5.5 | 4.1 | 195 | 76.6667 | 288.3333 | 0 | 31.6667 | 0 | 0 | 70.3704 | 164653.1852 | 9.6476 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-12-20 13:30 | 4.9 | 3.3 | 195 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 164027.2593 | 9.611 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-12-20 14:30 | 4 | 3.6 | 185 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 163316.1481 | 9.5693 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-12-20 15:30 | 4.3 | 3.6 | 185 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 162605.037 | 9.5276 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-12-20 16:30 | 5 | 3.2 | 190 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161893.9259 | 9.486 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-12-20 17:30 | 4.7 | 3.5 | 180 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 161182.8148 | 9.4443 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-12-20 18:30 | 4.7 | 4.4 | 162.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 160556.8889 | 9.4076 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-12-20 19:30 | 5 | 4.7 | 150 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 160152.4444 | 9.3839 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-12-20 20:30 | 5.2 | 4.5 | 142.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 159884.2963 | 9.3682 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-12-20 21:30 | 5.4 | 4.7 | 140 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 159616.1481 | 9.3525 | 1 |  |  | 1 | 11 | 0 | 0
Lerwick | 1978-12-20 22:30 | 5.4 | 5 | 140 | 340 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 159504.2963 | 9.346 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-20 23:30 | 5.4 | 5.3 | 137.5 | 340 | 340 | 20 | 0 | 20 | 10 | 0 | 159514.2963 | 9.3465 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-21 00:30 | 5.5 | 5.8 | 135 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 159564.2963 | 9.3495 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-21 01:30 | 5.3 | 6 | 137.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 159719.2963 | 9.3586 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-21 02:30 | 5 | 6.3 | 132.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 159939.2963 | 9.3714 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-21 03:30 | 4.7 | 6 | 117.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 160159.2963 | 9.3843 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-21 04:30 | 4.5 | 5.8 | 110 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 160314.2963 | 9.3934 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-21 05:30 | 4.5 | 6.4 | 110 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 160469.2963 | 9.4025 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-21 06:30 | 4.6 | 7.2 | 107.5 | 1480 | 1120 | 800 | 0 | 800 | 400 | 0 | 160869.2963 | 9.4259 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-21 07:30 | 4.5 | 7.6 | 100 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 161514.2963 | 9.4637 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-21 08:30 | 4.3 | 7.7 | 97.5 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 162159.2963 | 9.5015 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-21 09:30 | 4.4 | 7.8 | 105 | 1840 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 162804.2963 | 9.5393 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-21 10:30 | 4.6 | 8.2 | 110 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 163449.2963 | 9.5771 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-21 11:30 | 4.6 | 9 | 110 | 2920 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 164094.2963 | 9.6149 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-21 12:30 | 4.7 | 9.6 | 107.5 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 164739.2963 | 9.6527 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-21 13:30 | 4.7 | 9.4 | 102.5 | 2920 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 165384.2963 | 9.6905 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-21 14:30 | 4.3 | 8.9 | 100 | 2560 | 2740 | 2420 | 0 | 1290 | 645 | 0 | 166029.2963 | 9.7283 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-21 15:30 | 4.1 | 8.6 | 100 | 2560 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 166674.2963 | 9.7661 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-21 16:30 | 4.3 | 8.3 | 102.5 | 2200 | 2380 | 2060 | 0 | 1290 | 645 | 0 | 167319.2963 | 9.8039 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-21 17:30 | 4.6 | 8 | 105 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 167964.2963 | 9.8417 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-21 18:30 | 4.4 | 7.6 | 102.5 | 1840 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 168609.2963 | 9.8795 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-21 19:30 | 4.1 | 6.8 | 102.5 | 1120 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 169189.2963 | 9.9134 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-21 20:30 | 3.9 | 6.4 | 105 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 169499.2963 | 9.9316 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-21 21:30 | 3.8 | 6.4 | 97.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 169719.2963 | 9.9445 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-21 22:30 | 4 | 6.3 | 87.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 169939.2963 | 9.9574 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-21 23:30 | 4.3 | 5.9 | 87.5 | 500 | 630 | 310 | 0 | 310 | 155 | 0 | 170094.2963 | 9.9665 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-22 00:30 | 4.4 | 5.3 | 90 | 340 | 420 | 100 | 0 | 100 | 0 | 0 | 170094.2963 | 9.9665 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-12-22 01:30 | 4.4 | 4.9 | 95 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 169982.4444 | 9.9599 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-12-22 02:30 | 4.4 | 4.4 | 105 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 169578 | 9.9362 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-12-22 03:30 | 4.5 | 3.9 | 110 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 168952.0741 | 9.8995 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-12-22 04:30 | 4.2 | 3.9 | 112.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168240.963 | 9.8579 | 0 |  |  | 1 | 5 | 1 | 1
Lerwick | 1978-12-22 05:30 | 4.2 | 3.8 | 115 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167529.8519 | 9.8162 | 0 |  |  | 1 | 6 | 1 | 2
Lerwick | 1978-12-22 06:30 | 4.4 | 3.6 | 112.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166818.7407 | 9.7745 | 0 |  |  | 1 | 7 | 1 | 3
Lerwick | 1978-12-22 07:30 | 4.4 | 4 | 110 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 166192.8148 | 9.7379 | 1 |  |  | 1 | 8 | 0 | 0
Lerwick | 1978-12-22 08:30 | 4.6 | 4.4 | 112.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 165652.0741 | 9.7062 | 1 |  |  | 1 | 9 | 0 | 0
Lerwick | 1978-12-22 09:30 | 4.8 | 4.2 | 117.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 165111.3333 | 9.6745 | 1 |  |  | 1 | 10 | 0 | 0
Lerwick | 1978-12-22 10:30 | 4.7 | 4.2 | 115 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 164570.5926 | 9.6428 | 1 |  |  | 1 | 11 | 0 | 0
Lerwick | 1978-12-22 11:30 | 4.5 | 4.4 | 105 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 164029.8519 | 9.6111 | 1 |  |  | 1 | 12 | 0 | 0
Lerwick | 1978-12-22 12:30 | 4.4 | 4.4 | 100 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 163489.1111 | 9.5794 | 1 |  |  | 1 | 13 | 0 | 0
Lerwick | 1978-12-22 13:30 | 4.1 | 4.4 | 97.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 162948.3704 | 9.5478 | 1 |  |  | 1 | 14 | 0 | 0
Lerwick | 1978-12-22 14:30 | 4 | 4.6 | 95 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 162543.9259 | 9.5241 | 1 |  |  | 1 | 15 | 0 | 0
Lerwick | 1978-12-22 15:30 | 4 | 4.7 | 97.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 162275.7778 | 9.5083 | 1 |  |  | 1 | 16 | 0 | 0
Lerwick | 1978-12-22 16:30 | 3.8 | 4.2 | 100 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 161871.3333 | 9.4846 | 1 |  |  | 1 | 17 | 0 | 0
Lerwick | 1978-12-22 17:30 | 3.7 | 4.2 | 97.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 161330.5926 | 9.453 | 1 |  |  | 1 | 18 | 0 | 0
Lerwick | 1978-12-22 18:30 | 3.9 | 4.7 | 95 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 160926.1481 | 9.4293 | 1 |  |  | 1 | 19 | 0 | 0
Lerwick | 1978-12-22 19:30 | 3.6 | 4.7 | 97.5 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 160658 | 9.4136 | 1 |  |  | 1 | 20 | 0 | 0
Lerwick | 1978-12-22 20:30 | 3.6 | 4.5 | 100 | 199.3333 | 199.3333 | 0 | 120.6667 | 0 | 0 | 268.1481 | 160389.8519 | 9.3978 | 1 |  |  | 1 | 21 | 0 | 0
Lerwick | 1978-12-22 21:30 | 3.9 | 4.4 | 102.5 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 159985.4074 | 9.3741 | 1 |  |  | 1 | 22 | 0 | 0
Lerwick | 1978-12-22 22:30 | 3.9 | 4.2 | 107.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 159444.6667 | 9.3425 | 1 |  |  | 1 | 23 | 0 | 0
Lerwick | 1978-12-22 23:30 | 3.8 | 4.2 | 112.5 | 76.6667 | 76.6667 | 0 | 243.3333 | 0 | 0 | 540.7407 | 158903.9259 | 9.3108 | 1 |  |  | 1 | 24 | 0 | 0
Lerwick | 1978-12-23 00:30 | 3.7 | 3.7 | 90 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 158278 | 9.2741 | 1 |  |  | 1 | 25 | 0 | 0
Lerwick | 1978-12-23 01:30 | 3 | 2.4 | 40 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 157566.8889 | 9.2324 | 0 |  |  | 1 | 26 | 1 | 1
Lerwick | 1978-12-23 02:30 | 2 | 2.2 | 25 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 156855.7778 | 9.1908 | 0 |  |  | 1 | 27 | 1 | 2
Lerwick | 1978-12-23 03:30 | 2.1 | 3.1 | 47.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 156144.6667 | 9.1491 | 0 |  |  | 1 | 28 | 1 | 3
Lerwick | 1978-12-23 04:30 | 2.9 | 3.6 | 77.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 155433.5556 | 9.1074 | 0 |  |  | 1 | 29 | 1 | 4
Lerwick | 1978-12-23 05:30 | 3.4 | 3.4 | 110 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 154722.4444 | 9.0658 | 0 |  |  | 1 | 30 | 1 | 5
Lerwick | 1978-12-23 06:30 | 3.6 | 2.9 | 125 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 154011.3333 | 9.0241 | 0 |  |  | 1 | 31 | 1 | 6
Lerwick | 1978-12-23 07:30 | 3.4 | 2.6 | 102.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 153300.2222 | 8.9824 | 0 |  |  | 1 | 32 | 1 | 7
Lerwick | 1978-12-23 08:30 | 3.3 | 2.4 | 50 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 152589.1111 | 8.9408 | 0 |  |  | 1 | 33 | 1 | 8
Lerwick | 1978-12-23 09:30 | 3 | 1.7 | 15 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 151878 | 8.8991 | 0 |  |  | 1 | 34 | 1 | 9
Lerwick | 1978-12-23 10:30 | 2.3 | 1.3 | 15 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 151166.8889 | 8.8574 | 0 |  |  | 1 | 35 | 1 | 10
Lerwick | 1978-12-23 11:30 | 2.1 | 1.5 | 30 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 150455.7778 | 8.8158 | 0 |  |  | 1 | 36 | 1 | 11
Lerwick | 1978-12-23 12:30 | 2.1 | 2.7 | 57.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 149744.6667 | 8.7741 | 0 |  |  | 1 | 37 | 1 | 12
Lerwick | 1978-12-23 13:30 | 2.1 | 5 | 80 | 340 | 170 | 0 | 150 | 0 | 0 | 333.3333 | 149411.3333 | 8.7546 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-23 14:30 | 2.4 | 7.2 | 82.5 | 1480 | 910 | 590 | 0 | 590 | 295 | 0 | 149706.3333 | 8.7719 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-23 15:30 | 2.5 | 8.4 | 80 | 2200 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 150351.3333 | 8.8096 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-23 16:30 | 2.9 | 9.1 | 77.5 | 2920 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 150996.3333 | 8.8474 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-23 17:30 | 3.5 | 9.1 | 80 | 2920 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 151641.3333 | 8.8852 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-23 18:30 | 2.8 | 8.4 | 92.5 | 2200 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 152286.3333 | 8.923 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-23 19:30 | 2.3 | 7.3 | 102.5 | 1480 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 152931.3333 | 8.9608 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-23 20:30 | 1.9 | 5.8 | 107.5 | 500 | 990 | 670 | 0 | 670 | 335 | 0 | 153266.3333 | 8.9804 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-23 21:30 | 1.9 | 5.2 | 107.5 | 340 | 420 | 100 | 0 | 100 | 50 | 0 | 153316.3333 | 8.9834 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-23 22:30 | 2.5 | 5.9 | 102.5 | 500 | 420 | 100 | 0 | 100 | 50 | 0 | 153366.3333 | 8.9863 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-23 23:30 | 2.5 | 7 | 102.5 | 1480 | 990 | 670 | 0 | 670 | 335 | 0 | 153701.3333 | 9.0059 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-24 00:30 | 2.6 | 7.9 | 107.5 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 154346.3333 | 9.0437 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-24 01:30 | 2.7 | 8.1 | 110 | 2200 | 2020 | 1700 | 0 | 1290 | 645 | 0 | 154991.3333 | 9.0815 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-24 02:30 | 2.7 | 8.4 | 107.5 | 2200 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 155636.3333 | 9.1193 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-24 03:30 | 2.6 | 9.1 | 102.5 | 2920 | 2560 | 2240 | 0 | 1290 | 645 | 0 | 156281.3333 | 9.1571 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-24 04:30 | 2.1 | 9.7 | 100 | 3280 | 3100 | 2780 | 0 | 1290 | 645 | 0 | 156926.3333 | 9.1949 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-24 05:30 | 2.2 | 10.2 | 102.5 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 157571.3333 | 9.2327 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-24 06:30 | 2.8 | 10.7 | 107.5 | 4000 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 158216.3333 | 9.2705 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-24 07:30 | 3 | 11.2 | 110 | 4300 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 158861.3333 | 9.3083 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-24 08:30 | 3 | 11.7 | 110 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 159506.3333 | 9.3461 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-24 09:30 | 2.8 | 12.4 | 110 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 645 | 0 | 160151.3333 | 9.3839 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-24 10:30 | 2.7 | 13.4 | 107.5 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 645 | 0 | 160796.3333 | 9.4217 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-24 11:30 | 2.7 | 13.9 | 105 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 161441.3333 | 9.4595 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-24 12:30 | 2.5 | 13.5 | 107.5 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 162086.3333 | 9.4972 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-24 13:30 | 2.3 | 12.8 | 110 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 162731.3333 | 9.535 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-24 14:30 | 2.3 | 12.5 | 110 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 163376.3333 | 9.5728 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-24 15:30 | 2.1 | 12.5 | 110 | 4600 | 4600 | 4280 | 0 | 1290 | 645 | 0 | 164021.3333 | 9.6106 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-24 16:30 | 1.9 | 12.4 | 107.5 | 4536.1111 | 4568.0556 | 4248.0556 | 0 | 1290 | 645 | 0 | 164666.3333 | 9.6484 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-24 17:30 | 2.1 | 12.4 | 102.5 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 165311.3333 | 9.6862 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-24 18:30 | 2.2 | 12.4 | 100 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 165956.3333 | 9.724 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-24 19:30 | 2 | 12.2 | 100 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 645 | 0 | 166601.3333 | 9.7618 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-24 20:30 | 2 | 11.7 | 97.5 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 645 | 0 | 167246.3333 | 9.7996 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-24 21:30 | 2 | 11.4 | 92.5 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 167891.3333 | 9.8374 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-24 22:30 | 1.5 | 11.4 | 90 | 4300 | 4300 | 3980 | 0 | 1290 | 645 | 0 | 168536.3333 | 9.8752 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-24 23:30 | 1.6 | 11.5 | 90 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 169181.3333 | 9.913 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-25 00:30 | 2.2 | 11.2 | 90 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 645 | 0 | 169826.3333 | 9.9508 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-25 01:30 | 2.3 | 10.7 | 90 | 4000 | 4150 | 3830 | 0 | 1290 | 645 | 0 | 170471.3333 | 9.9886 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-25 02:30 | 2.4 | 10.1 | 90 | 3640 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170471.3333 | 9.9886 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-25 03:30 | 2.3 | 9.4 | 87.5 | 2920 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170471.3333 | 9.9886 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-25 04:30 | 2.1 | 8.5 | 82.5 | 2560 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170471.3333 | 9.9886 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-25 05:30 | 2.1 | 7.8 | 80 | 1840 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170471.3333 | 9.9886 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-25 06:30 | 2.2 | 7.2 | 80 | 1480 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170471.3333 | 9.9886 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-25 07:30 | 2.1 | 6.8 | 80 | 1120 | 1300 | 980 | 0 | 980 | 0 | 0 | 170471.3333 | 9.9886 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-25 08:30 | 2.1 | 6.4 | 82.5 | 760 | 940 | 620 | 0 | 620 | 0 | 0 | 170471.3333 | 9.9886 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-25 09:30 | 2.1 | 5.9 | 90 | 500 | 630 | 310 | 0 | 310 | 0 | 0 | 170471.3333 | 9.9886 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-25 10:30 | 2.3 | 5.7 | 100 | 500 | 500 | 180 | 0 | 180 | 0 | 0 | 170471.3333 | 9.9886 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-25 11:30 | 2.3 | 5.3 | 105 | 340 | 420 | 100 | 0 | 100 | 0 | 0 | 170471.3333 | 9.9886 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-12-25 12:30 | 2.1 | 4.4 | 105 | 76.6667 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 170223.1852 | 9.974 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-12-25 13:30 | 2 | 3.7 | 102.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 169597.2593 | 9.9373 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-12-25 14:30 | 1.6 | 3.8 | 90 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168886.1481 | 9.8957 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-12-25 15:30 | 1.5 | 4.2 | 72.5 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 168260.2222 | 9.859 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-12-25 16:30 | 1.8 | 4.7 | 65 | 199.3333 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 167855.7778 | 9.8353 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-25 17:30 | 1.8 | 5.6 | 65 | 500 | 349.6667 | 29.6667 | 0 | 29.6667 | 14.8333 | 0 | 167870.6111 | 9.8362 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-25 18:30 | 2 | 6.4 | 62.5 | 760 | 630 | 310 | 0 | 310 | 155 | 0 | 168025.6111 | 9.8453 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-25 19:30 | 1.8 | 6.5 | 62.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 168335.6111 | 9.8634 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-25 20:30 | 1.4 | 6.3 | 65 | 760 | 940 | 620 | 0 | 620 | 310 | 0 | 168645.6111 | 9.8816 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-25 21:30 | 1.2 | 6.2 | 62.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 168865.6111 | 9.8945 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-25 22:30 | 1.2 | 6.4 | 62.5 | 760 | 760 | 440 | 0 | 440 | 220 | 0 | 169085.6111 | 9.9074 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-25 23:30 | 1.5 | 6.9 | 67.5 | 1120 | 940 | 620 | 0 | 620 | 310 | 0 | 169395.6111 | 9.9255 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-26 00:30 | 1.6 | 7.2 | 70 | 1480 | 1300 | 980 | 0 | 980 | 490 | 0 | 169885.6111 | 9.9542 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-26 01:30 | 1.6 | 7.1 | 70 | 1480 | 1480 | 1160 | 0 | 1160 | 580 | 0 | 170465.6111 | 9.9882 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-26 02:30 | 1.7 | 6.8 | 67.5 | 1120 | 1300 | 980 | 0 | 980 | 0 | 0 | 170465.6111 | 9.9882 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-26 03:30 | 1.8 | 6.7 | 62.5 | 1120 | 1120 | 800 | 0 | 800 | 0 | 0 | 170465.6111 | 9.9882 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-26 04:30 | 1.9 | 6.8 | 62.5 | 1120 | 1120 | 800 | 0 | 800 | 0 | 0 | 170465.6111 | 9.9882 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-26 05:30 | 2 | 6.8 | 70 | 1120 | 1120 | 800 | 0 | 800 | 0 | 0 | 170465.6111 | 9.9882 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-26 06:30 | 2 | 6.4 | 75 | 760 | 940 | 620 | 0 | 620 | 0 | 0 | 170465.6111 | 9.9882 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-26 07:30 | 2.1 | 6.2 | 70 | 760 | 760 | 440 | 0 | 440 | 0 | 0 | 170465.6111 | 9.9882 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-26 08:30 | 2.1 | 6.3 | 62.5 | 760 | 760 | 440 | 0 | 440 | 0 | 0 | 170465.6111 | 9.9882 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-26 09:30 | 1.8 | 6.3 | 62.5 | 760 | 760 | 440 | 0 | 440 | 0 | 0 | 170465.6111 | 9.9882 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-26 10:30 | 1.9 | 5.9 | 65 | 500 | 630 | 310 | 0 | 310 | 0 | 0 | 170465.6111 | 9.9882 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-26 11:30 | 2.3 | 5.8 | 65 | 500 | 500 | 180 | 0 | 180 | 0 | 0 | 170465.6111 | 9.9882 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-26 12:30 | 2.6 | 6 | 67.5 | 760 | 630 | 310 | 0 | 310 | 0 | 0 | 170465.6111 | 9.9882 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-26 13:30 | 2.6 | 6 | 70 | 760 | 760 | 440 | 0 | 440 | 0 | 0 | 170465.6111 | 9.9882 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-26 14:30 | 2.5 | 5.8 | 67.5 | 500 | 630 | 310 | 0 | 310 | 0 | 0 | 170465.6111 | 9.9882 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-26 15:30 | 2.5 | 5.3 | 65 | 340 | 420 | 100 | 0 | 100 | 0 | 0 | 170465.6111 | 9.9882 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-12-26 16:30 | 2.4 | 4.7 | 62.5 | 199.3333 | 269.6667 | 0 | 50.3333 | 0 | 0 | 111.8519 | 170353.7593 | 9.9817 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-12-26 17:30 | 2.4 | 4.2 | 55 | 76.6667 | 138 | 0 | 182 | 0 | 0 | 404.4444 | 169949.3148 | 9.958 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-12-26 18:30 | 2.4 | 3.7 | 47.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 169323.3889 | 9.9213 | 1 |  |  | 1 | 4 | 0 | 0
Lerwick | 1978-12-26 19:30 | 2.4 | 4 | 40 | 76.6667 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 168697.463 | 9.8846 | 1 |  |  | 1 | 5 | 0 | 0
Lerwick | 1978-12-26 20:30 | 2.5 | 5.1 | 35 | 340 | 208.3333 | 0 | 111.6667 | 0 | 0 | 248.1481 | 168449.3148 | 9.8701 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-26 21:30 | 2.7 | 6.3 | 37.5 | 760 | 550 | 230 | 0 | 230 | 115 | 0 | 168564.3148 | 9.8768 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-26 22:30 | 2.7 | 7.3 | 40 | 1480 | 1120 | 800 | 0 | 800 | 400 | 0 | 168964.3148 | 9.9003 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-26 23:30 | 2.6 | 7.9 | 40 | 1840 | 1660 | 1340 | 0 | 1290 | 645 | 0 | 169609.3148 | 9.938 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-27 00:30 | 2.4 | 8.5 | 42.5 | 2560 | 2200 | 1880 | 0 | 1290 | 645 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-27 01:30 | 2.3 | 9.1 | 47.5 | 2920 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-27 02:30 | 2.4 | 9.4 | 47.5 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-27 03:30 | 2.2 | 9.7 | 42.5 | 3280 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-27 04:30 | 2.2 | 10 | 42.5 | 3640 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-27 05:30 | 2.3 | 9.6 | 47.5 | 3280 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-27 06:30 | 2.3 | 8.9 | 47.5 | 2560 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-27 07:30 | 2.3 | 8.3 | 45 | 2200 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-27 08:30 | 1.7 | 8 | 47.5 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-27 09:30 | 1.1 | 8 | 47.5 | 2200 | 2200 | 1880 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-27 10:30 | 1.2 | 7.8 | 42.5 | 1840 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-27 11:30 | 1.5 | 7.2 | 45 | 1480 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-27 12:30 | 1.5 | 6.9 | 50 | 1120 | 1300 | 980 | 0 | 980 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-27 13:30 | 1.5 | 7.4 | 45 | 1480 | 1300 | 980 | 0 | 980 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-27 14:30 | 1.4 | 7.8 | 37.5 | 1840 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-27 15:30 | 1.5 | 8.2 | 35 | 2200 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-27 16:30 | 1.6 | 8.6 | 35 | 2560 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-27 17:30 | 1.4 | 9.1 | 32.5 | 2920 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-27 18:30 | 1.4 | 9.5 | 30 | 3280 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-27 19:30 | 1 | 9.4 | 30 | 2920 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-27 20:30 | 0.9 | 9.4 | 30 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-27 21:30 | 1.4 | 9.4 | 35 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-27 22:30 | 0.7 | 9.4 | 45 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-27 23:30 | 0 | 9.4 | 50 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-28 00:30 | 0 | 9 | 50 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-28 01:30 | 0 | 8.9 | 47.5 | 2560 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-28 02:30 | 0.1 | 9 | 42.5 | 2920 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-28 03:30 | 0.4 | 9.6 | 40 | 3280 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-28 04:30 | 0.3 | 10 | 45 | 3640 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-28 05:30 | 0.2 | 8.7 | 47.5 | 2560 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-28 06:30 | 0 | 7.3 | 35 | 1480 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-28 07:30 | -0.2 | 7.2 | 27.5 | 1480 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-28 08:30 | 0.1 | 8 | 45 | 2200 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-28 09:30 | 0.4 | 8.9 | 62.5 | 2560 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-28 10:30 | 0.2 | 9.9 | 55 | 3280 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-28 11:30 | -0.1 | 10.7 | 45 | 4000 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-28 12:30 | -0.3 | 10.5 | 50 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-28 13:30 | -0.7 | 9.4 | 55 | 2920 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-28 14:30 | -0.4 | 9.4 | 50 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-28 15:30 | -0.1 | 10.1 | 40 | 3640 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-28 16:30 | -0.1 | 9.8 | 37.5 | 3280 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-28 17:30 | 0.1 | 9.4 | 45 | 2920 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-28 18:30 | 0 | 10 | 52.5 | 3640 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-28 19:30 | 0.1 | 11 | 57.5 | 4300 | 3970 | 3650 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-28 20:30 | -0.1 | 11.4 | 55 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-28 21:30 | -0.6 | 11.4 | 45 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-28 22:30 | -0.4 | 11.7 | 40 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-28 23:30 | -0.5 | 12 | 42.5 | 4536.1111 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-29 00:30 | -1.5 | 12 | 45 | 4536.1111 | 4536.1111 | 4216.1111 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-29 01:30 | -1.6 | 11.9 | 47.5 | 4472.2222 | 4504.1667 | 4184.1667 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-29 02:30 | -1.5 | 11.3 | 52.5 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-29 03:30 | -1.9 | 10.4 | 50 | 3640 | 3970 | 3650 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-29 04:30 | -1.7 | 10 | 42.5 | 3640 | 3640 | 3320 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-29 05:30 | -1.5 | 9.6 | 45 | 3280 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-29 06:30 | -2 | 8.9 | 52.5 | 2560 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-29 07:30 | -2.3 | 8.3 | 42.5 | 2200 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-29 08:30 | -2 | 7.4 | 22.5 | 1480 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-29 09:30 | -1.9 | 5.8 | 40 | 500 | 990 | 670 | 0 | 670 | 0 | 0 | 170254.3148 | 9.9758 | 0 |  |  | 1 | 1 | 0 | 0
Lerwick | 1978-12-29 10:30 | -2.1 | 4.3 | 105 | 76.6667 | 288.3333 | 0 | 31.6667 | 0 | 0 | 70.3704 | 170183.9444 | 9.9717 | 1 |  |  | 1 | 2 | 0 | 0
Lerwick | 1978-12-29 11:30 | -1.9 | 3.1 | 172.5 | 0 | 38.3333 | 0 | 281.6667 | 0 | 0 | 625.9259 | 169558.0185 | 9.935 | 1 |  |  | 1 | 3 | 0 | 0
Lerwick | 1978-12-29 12:30 | -1.9 | 2.6 | 212.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168846.9074 | 9.8934 | 0 |  |  | 1 | 4 | 1 | 1
Lerwick | 1978-12-29 13:30 | -2.5 | 2.3 | 240 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 168135.7963 | 9.8517 | 0 |  |  | 1 | 5 | 1 | 2
Lerwick | 1978-12-29 14:30 | -3.3 | 1.9 | 247.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 167424.6852 | 9.81 | 0 |  |  | 1 | 6 | 1 | 3
Lerwick | 1978-12-29 15:30 | -3.4 | 2 | 222.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166713.5741 | 9.7684 | 0 |  |  | 1 | 7 | 1 | 4
Lerwick | 1978-12-29 16:30 | -3.2 | 2.9 | 202.5 | 0 | 0 | 0 | 320 | 0 | 0 | 711.1111 | 166002.463 | 9.7267 | 0 |  |  | 1 | 8 | 1 | 5
Lerwick | 1978-12-29 17:30 | -3.2 | 4.5 | 187.5 | 199.3333 | 99.6667 | 0 | 220.3333 | 0 | 0 | 489.6296 | 165512.8333 | 9.698 | 1 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-29 18:30 | -2.6 | 6.5 | 170 | 1120 | 659.6667 | 339.6667 | 0 | 339.6667 | 169.8333 | 0 | 165682.6667 | 9.708 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-29 19:30 | -1.9 | 8.5 | 165 | 2560 | 1840 | 1520 | 0 | 1290 | 645 | 0 | 166327.6667 | 9.7458 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-29 20:30 | -1.9 | 9.5 | 162.5 | 3280 | 2920 | 2600 | 0 | 1290 | 645 | 0 | 166972.6667 | 9.7836 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-29 21:30 | -2.1 | 10 | 160 | 3640 | 3460 | 3140 | 0 | 1290 | 645 | 0 | 167617.6667 | 9.8213 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-29 22:30 | -1.7 | 10.5 | 160 | 4000 | 3820 | 3500 | 0 | 1290 | 645 | 0 | 168262.6667 | 9.8591 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-29 23:30 | -1.5 | 10.8 | 157.5 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 168907.6667 | 9.8969 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-30 00:30 | -2 | 10.8 | 152.5 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 169552.6667 | 9.9347 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-30 01:30 | -1.7 | 10.8 | 150 | 4000 | 4000 | 3680 | 0 | 1290 | 645 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-30 02:30 | -1.5 | 10.9 | 150 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-30 03:30 | -1.9 | 11.2 | 150 | 4300 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-30 04:30 | -1.6 | 11.4 | 150 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-30 05:30 | -1.2 | 11.4 | 150 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-30 06:30 | -1.2 | 11.6 | 150 | 4472.2222 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-30 07:30 | -1.2 | 11.5 | 150 | 4472.2222 | 4472.2222 | 4152.2222 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-30 08:30 | -1.3 | 11.1 | 150 | 4300 | 4386.1111 | 4066.1111 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-30 09:30 | -1.8 | 10.9 | 150 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-30 10:30 | -1.9 | 10.9 | 150 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-30 11:30 | -1.4 | 11.1 | 150 | 4300 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-30 12:30 | -1.1 | 11.1 | 150 | 4300 | 4300 | 3980 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-30 13:30 | -1.1 | 10.9 | 152.5 | 4000 | 4150 | 3830 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-30 14:30 | -1.2 | 10.8 | 157.5 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-30 15:30 | -1.4 | 10.6 | 160 | 4000 | 4000 | 3680 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-30 16:30 | -1.6 | 10.2 | 160 | 3640 | 3820 | 3500 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-30 17:30 | -1.9 | 9.9 | 157.5 | 3280 | 3460 | 3140 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-30 18:30 | -2.2 | 9.6 | 152.5 | 3280 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-30 19:30 | -2.2 | 9.4 | 150 | 2920 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-30 20:30 | -2 | 9.4 | 152.5 | 2920 | 2920 | 2600 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-30 21:30 | -2.1 | 9.5 | 157.5 | 3280 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-30 22:30 | -2.3 | 9.2 | 155 | 2920 | 3100 | 2780 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-30 23:30 | -2.5 | 8.7 | 147.5 | 2560 | 2740 | 2420 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-31 00:30 | -2.4 | 8.2 | 145 | 2200 | 2380 | 2060 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-31 01:30 | -2.2 | 7.7 | 142.5 | 1840 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-31 02:30 | -2.6 | 7.1 | 142.5 | 1480 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-31 03:30 | -3.1 | 6.5 | 147.5 | 1120 | 1300 | 980 | 0 | 980 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-31 04:30 | -3.3 | 6.7 | 152.5 | 1120 | 1120 | 800 | 0 | 800 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-31 05:30 | -3.4 | 7.1 | 157.5 | 1480 | 1300 | 980 | 0 | 980 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-31 06:30 | -3.7 | 7.1 | 157.5 | 1480 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-31 07:30 | -3.7 | 7.1 | 152.5 | 1480 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-31 08:30 | -3.5 | 7.3 | 152.5 | 1480 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-31 09:30 | -3.5 | 7.3 | 157.5 | 1480 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-31 10:30 | -3.7 | 7.4 | 160 | 1480 | 1480 | 1160 | 0 | 1160 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-31 11:30 | -3.6 | 7.8 | 160 | 1840 | 1660 | 1340 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-31 12:30 | -3.2 | 7.7 | 162.5 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-31 13:30 | -3.1 | 7.5 | 167.5 | 1840 | 1840 | 1520 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-31 14:30 | -3.1 | 8 | 170 | 2200 | 2020 | 1700 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-31 15:30 | -2.9 | 9.1 | 167.5 | 2920 | 2560 | 2240 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-31 16:30 | -3.1 | 10.3 | 162.5 | 3640 | 3280 | 2960 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-31 17:30 | -3.3 | 11.3 | 157.5 | 4300 | 3970 | 3650 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-31 18:30 | -3 | 12.1 | 155 | 4536.1111 | 4418.0556 | 4098.0556 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-31 19:30 | -2.9 | 12.6 | 155 | 4600 | 4568.0556 | 4248.0556 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-31 20:30 | -3.1 | 13.1 | 152.5 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-31 21:30 | -3.2 | 13.2 | 150 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-31 22:30 | -3.3 | 13.1 | 150 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0 |  |  | 0 | 0 | 0 | 0
Lerwick | 1978-12-31 23:30 | -2.9 | 13.2 | 150 | 4600 | 4600 | 4280 | 0 | 1290 | 0 | 0 | 170197.6667 | 9.9725 | 0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
Note on C18: Kati Svehla: manual input depending on turbine
Note on C19: Kati Svehla: manual input depending on turbine
Note on J9: Kati Svehla: Exactly 320kWh

## Wind turbine characteristics
Wind Power Calculations
Turbine characteristics
Wind speed | Vestas 2.0 MW | Vestas 112-3.0 MW | GE 3.6MW | GE 2.5MW | Siemens SWT-2.3-101 | GE 1.5MW sle
m/s | kW | kW | kW | kW | kW | kW
0 | 0 | 0 | 0 | 0 | 0 | 0
0.5 | 0 | 0 | 0 | 0 | 0 | 0
1 | 0 | 0 | 0 | 0 | 0 | 0
1.5 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0
2.5 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 50 | 0 | 34.7222 | 0 | 0
3.5 | 0 | 130 | 50 | 55.5556 | 0 | 25
4 | 50 | 200 | 80 | 104.1667 | 38.3333 | 60
4.5 | 90 | 250 | 150 | 159.7222 | 99.6667 | 80
5 | 100 | 320 | 230 | 243.0556 | 170 | 110
5.5 | 135 | 420 | 350 | 347.2222 | 250 | 150
6 | 200 | 540 | 500 | 480 | 380 | 220
6.5 | 300 | 720 | 650 | 676.25 | 560 | 300
7 | 400 | 900 | 800 | 872.5 | 740 | 400
7.5 | 516.5 | 1200 | 950 | 1068.75 | 920 | 500
8 | 633 | 1500 | 1100 | 1265 | 1100 | 635
8.5 | 749.5 | 1800 | 1300 | 1461.25 | 1280 | 770
9 | 866 | 2100 | 1500 | 1657.5 | 1460 | 900
9.5 | 982.5 | 2400 | 1800 | 1853.75 | 1640 | 1025
10 | 1099 | 2650 | 2100 | 2050 | 1820 | 1150
10.5 | 1215.5 | 2800 | 2400 | 2222.2222 | 2000 | 1270
11 | 1332 | 2870 | 2600 | 2361.1111 | 2150 | 1340
11.5 | 1448.5 | 2950 | 2900 | 2430.5556 | 2236.1111 | 1400
12 | 1565 | 3000 | 3200 | 2465.2778 | 2268.0556 | 1450
12.5 | 1681.5 | 3000 | 3400 | 2500 | 2300 | 1470
13 | 1798 | 3000 | 3500 | 2500 | 2300 | 1480
13.5 | 1860 | 3000 | 3550 | 2500 | 2300 | 1490
14 | 1920 | 3000 | 3600 | 2500 | 2300 | 1500
14.5 | 1950 | 3000 | 3600 | 2500 | 2300 | 1500
15 | 1970 | 3000 | 3600 | 2500 | 2300 | 1500
15.5 | 1985 | 3000 | 3600 | 2500 | 2300 | 1500
16 | 2000 | 3000 | 3600 | 2500 | 2300 | 1500
16.5 | 2000 | 3000 | 3600 | 2500 | 2300 | 1500
17 | 2000 | 3000 | 3600 | 2500 | 2300 | 1500
17.5 | 2000 | 3000 | 3600 | 2500 | 2300 | 1500
18 | 2000 | 3000 | 3600 | 2500 | 2300 | 1500
18.5 | 2000 | 3000 | 3600 | 2500 | 2300 | 1500
19 | 2000 | 3000 | 3600 | 2500 | 2300 | 1500
19.5 | 2000 | 3000 | 3600 | 2500 | 2300 | 1500
20 | 2000 | 3000 | 3600 | 2500 | 2300 | 1500
20.5 | 2000 | 3000 | 3600 | 2500 | 2300 | 1500
21 | 2000 | 3000 | 3600 | 2500 | 2300 | 1500
21.5 | 2000 | 3000 | 3600 | 2500 | 2300 | 1500
22 | 2000 | 3000 | 3600 | 2500 | 2300 | 1500
22.5 | 2000 | 3000 | 3600 | 2500 | 2300 | 1500
23 | 2000 | 3000 | 3600 | 2500 | 2300 | 1500
23.5 | 2000 | 3000 | 3600 | 2500 | 2300 | 1500
24 | 2000 | 3000 | 3600 | 2500 | 2300 | 1500
24.5 | 2000 | 3000 | 3600 | 2500 | 2300 | 1500
25 | 2000 | 3000 | 3600 | 2500 | 2300 | 1500
25.5 | 0 | 0 | 3600 | 0 | 0 | 0
26 | 0 | 0 | 3600 | 0 | 0 | 0
26.5 | 0 | 0 | 3600 | 0 | 0 | 0
27 | 0 | 0 | 3600 | 0 | 0 | 0
27.5 | 0 | 0 | 0 | 0 | 0 | 0
27.5 | 0 | 0 | 0 | 0 | 0 | 0
Source: | (1) | Vestas 2.0 MW |  | http://www.vestas.com/en/wind-power-solutions/wind-turbines/2.0-mw.aspx
| (2) | Vestas 112-3.0 MW |  | http://www.vestas.com/en/wind-power-solutions/wind-turbines/3.0-mw.aspx
| (3) | GE 3.6MW |  | GE brochure for 3.6MW turbine - cant find on the web again but have got downlaoded brochure from GE from somewhere
| (4) | GE 2.5MW |  | http://www.gepower.com/prod_serv/products/wind_turbines/en/downloads/GEA17007A-Wind25Brochure.pdf
| (5) | Siemens SWT-2.3-101 |  | http://www.energy.siemens.com/hq/en/power-generation/renewables/wind-power/wind-turbines/swt-2-3-101.htm
all access checked on 27 March
Note on E6: Kati Svehla: This column is deduced from GE3.6 as wind speed characteristics are not on brochure
Note on F6: Kati Svehla: This column is deduced from GE2.5 as wind speed characteristics are not on brochure