## Hot Water Demand
Hot Water Consumption Per Person Per day (l) | 3 |  | Specific Heat Capacity of Water (Wh/kgK) | 1.16
Dishwashing (l) | 20 |  | Cold Water Temp. (oC) | 10
|  |  | Hot Water Temp. (oC) | 50
| Days in Month | People/Visitors per week | People/Visitors per month | Dishwasher usage per week | Dishwasher usage per month | Hand Washing Monthly Hot Water Consumption (l) | Dishwasher Monthly Hot Water Consumption (l) | Total Monthly Hot Water Consumption (l) | Monthly Hot Water Heat Requirement (kWh)
January | 31 | 50 | 220 | 3 | 13.2 | 660 | 264 | 924 | 42.8736
February | 28 | 150 | 600 | 5 | 20 | 1800 | 400 | 2200 | 102.08
March | 31 | 250 | 1100 | 7 | 30.8 | 3300 | 616 | 3916 | 181.7024
April | 30 | 500 | 2143 | 7 | 30.002 | 6429 | 600.04 | 7029.04 | 326.1475
May | 31 | 1000 | 4400 | 10 | 44 | 13200 | 880 | 14080 | 653.312
June | 30 | 2500 | 10715 | 12 | 51.432 | 32145 | 1028.64 | 33173.64 | 1539.2569
July | 31 | 2500 | 11000 | 12 | 52.8 | 33000 | 1056 | 34056 | 1580.1984
August | 31 | 2000 | 8800 | 10 | 44 | 26400 | 880 | 27280 | 1265.792
September | 30 | 1000 | 4286 | 7 | 30.002 | 12858 | 600.04 | 13458.04 | 624.4531
October | 31 | 250 | 1100 | 7 | 30.8 | 3300 | 616 | 3916 | 181.7024
November | 30 | 50 | 214.3 | 3 | 12.858 | 642.9 | 257.16 | 900.06 | 41.7628
December | 31 | 50 | 220 | 3 | 13.2 | 660 | 264 | 924 | 42.8736
[8 empty] | Annual Total = | 6582.1546

## Solar Thermal Supply
| Annual Hot Water Heat Requirement (kWh) | 6582.1546
| Solar Collector Area (m2) | 11.0256 |  | Specific Heat Capacity of Water (Wh/kgK) | 1.16
| Solar Fraction | 0.6 |  | Cold Water Temp. (oC) | 10
| Average System Efficiency | 0.35 |  | Hot Water Temp. (oC) | 50
| Days in Month | Average Daily Solar Irradiation @ 30o Inclination (kWh/m2/day) | Average Monthly Solar Irradiation @ 30o Inclination (kWh/m2) | Solar Fraction | Average System Efficiency | Monthly heat generated by solar collector (kWh)
January | 31 | 0.864 | 26.784 | 0.6 | 0.35 | 172.2634
February | 28 | 1.615 | 45.22 | 0.6 | 0.35 | 290.836
March | 31 | 2.6 | 80.6 | 0.6 | 0.35 | 518.3852
April | 30 | 3.884 | 116.52 | 0.6 | 0.35 | 749.4075
May | 31 | 4.759 | 147.529 | 0.6 | 0.35 | 948.8443
June | 30 | 4.755 | 142.65 | 0.6 | 0.35 | 917.4647
July | 31 | 4.717 | 146.227 | 0.6 | 0.35 | 940.4704
August | 31 | 3.861 | 119.691 | 0.6 | 0.35 | 769.8021
September | 30 | 3.029 | 90.87 | 0.6 | 0.35 | 584.4375
October | 31 | 1.782 | 55.242 | 0.6 | 0.35 | 355.2933
November | 30 | 1.117 | 33.51 | 0.6 | 0.35 | 215.5222
December | 31 | 0.599 | 18.569 | 0.6 | 0.35 | 119.428
|  | Annual Total = | 1023.412 |  | Annual Total = | 6582.1546