## Instructions
This spreadsheet can be used to interrogate results for the standard wind turbine, PV panels and climate data investigated during the project. Alternatively, new climate data or more direct outputs can be utilised, potentially with different turbine and PV panel parameters in order to perform more realistic calculation of outputs and matching for a real site on which you have more accurate data.
All calculations are based upon hourly climate and output data, whereby 1kW is assumed to equal 1kWh. Modifications would be required for data with a higher or lower time resolution.
The purpose of the worksheets and the individual inputs and outputs are described below.
Wind_and_summary_calcs
Wind speed data, turbine characteristics, PV capacity and overall farm constraints are entered in this sheet. Power outputs for wind and PV are calculated and summary data is presented for analysis.
Location: enter name of location for reference
Wind Farm Input Data:
Reference height: Entered the height at which wind data was measured (usually 10m)
Hub height: Enter the hub height of the proposed turbine on site
Ground Surface Roughness: Enter GSR related to land surface of farm (usually 0.1)
Air density: Enter air density for turbine lookup table (usually 1.225kg/m2)
Radius: Enter radius of wind turbine (used for calculation of space between turbines)
Grid/Wind Farm Capacity: Enter the per turbine grid capacity in kW. If no further information is available, assume this is equal to the nominal turbine power rating
Wind farm loss factor: Enter the wind system loss factor (applied to all turbine outputs). Industry advice suggests 0.15 (15%) as an initial approximation
PV Park:
Nominal PV capacity: Enter desired nominal PV capacity in kW to investigate matching. This is used to calculate PV outputs
Solar panel efficiency: For reference – do NOT enter here as primary output is in PV sheet.
Number of panels required: Calculated from nominal PV capacity (based on the assumption that arrays are made up from 250W panels)
Physical land space required: Calculated from the number of panels
Proportion of space required: Calculated from number of panels and wind turbine size.
Minimum space between turbines: Calculated from the assumption that the minimum spacing between turbines is 4D x 6D (as per planning regulations)
Outputs from Calculations: These are cumulative energy outputs which assume that power outputs are constant across each time period.
Total Wind Turbine Output: Calculated and summed annual wind turbine output.
Total PV Output: Calculated and summed annual PV array output
Total site generation: Sum of wind and PV. Takes no account of energy spill
Annual PV contribution: Proportion of annual total power output supplied by PV. Takes no account of energy spilled.
PV nominal/wind nominal capacity: The ratio of PV:wind (nominal)
Statistics: Initial annual analysis outcomes
Time capacity is exceeded: Number of hours in the year when total output is greater than the grid capacity limit
Actual energy spilled: Sum of total generation which is greater than grid capacity limit in that particular hour for the whole year (MWh)
Annually wasted power: Actual energy spilled/sum of total site generation
Wind farm capacity factor: Sum of turbine output/nominal annual capacity
PV capacity factor: Sum of PV output/nominal annual capacity for the hours when sun 12.5 degrees or higher above the horizon
Overall capacity factor: Total generation – spill / annual grid connection capacity
Main Spreadsheet:
Is set up for hourly input for the entire year starting from 1st January.
Paste special (to maintain formatting) Raw Wind Data (wind speed in m/s) into Column D from Row 12.
Corrected Wind Speed: As explained in the Climate page of website
Turbine Characteristics: from cell T12. This is the wind speed ‘vs’ turbine output lookup table for different air densities. Data is direct from manufacturers data sheets. Characteristics from alternative turbines can be entered here.
PV data and calcs
This sheet is used for inputting solar and location data.
Solar and PV calculations are carried out, then transferred to Wind_and_summary_calcs to allow analysis alongside wind outputs.
Location Data: Insert name of location for reference
Latitude: Enter 0N from the equator in (Degrees) column
Longitude: Enter 0W from ref longitude (GMT dateline for the UK in (Degrees) column
Ref longitude: Enter 0W of ref longitude (00 in the UK) in the (Degrees) column
Daylight hours: This is calculated by the spreadsheet
Panel Data:
Orientation: Enter orientation of PV panels in (Degrees) column. E.g. South = 00, North = 1800
Tilt: Enter tilt from horizontal of PV panels in (Degrees) column
Panel efficiency: Enter nominal PV panel efficiency. E.g. 15% = 0.15
Performance factor: Enter PV system performance factor to represent system losses. E.g. 90% = 0.9
Area: This is calculated by the spreadsheet
Main spreadsheet:
Is set up for hourly input for the entire year starting from 1st January.
Paste special (to maintain formatting) direct solar irradiance (W/m2) into Column C from Row 12 and diffuse solar irradiance (W/m2) into Column D from Row 12.

## Wind_and_summary_calcs
Location: |  | Wind Farm Input Data |  |  |  | PV Park |  |  |  | Outputs from Calculations |  |  |  | Statistics
HEMSBY |  | Reference Height: | 10 | meters |  | Nominal PV capacity: | 2000 | kW |  | Total Wind Turbine output: | 4704.8044 | MWh |  | Time capacity is exceeded: | 317 | hours/year
|  | Hub Height: | 80 | meters |  | Solar panel efficiency: | 15% | % |  | Total PV Output: | 1628.9844 | MWh |  | Actual energy spilled | 103.9817 | MWh
|  | Ground Surface Roughness: | 0.1 |  |  | Number of panels required: | 8000 |  |  | Total Site Generation: | 6333.7888 | MWh |  | Annually wasted power | 1.642% | %
|  | Air density - ρ: | 1.225 | kg per sq meter |  | Physical land space required: | 13200 | square meters |  | Annual Contribution to Generation from PV | 25.72% | % |  | Wind farm capacity factor: | 26.85% | %
|  | Radius: | 42 | meters |  | Proportion of space between turbines required | 7.795% | % |  | PV nominal/ Turbine nominal capacity | 1 | ratio |  | PV capacity factor - α >=12.5 degrees: | 25.8% | %
|  | Grid/Wind Farm Capacity: | 2000 | kW |  | Min space between turbines | 169344 | square meters | [5 empty] | Overall capacity factor | 35.56% | %
|  | wind farm loss factor | 0.15
Date (DOY) | Time (hours) | Month (month) | Raw Wind Data (m/s) | Corrected Wind speed (m/s) | Calculated Turbine Output (kW) | Calculated PV Output (kW) | Total Site Generation (kW) | Hour Exceeds Capacity? | Output Constrained to (kW) | Excess generation (kW) | % over generation limit | PV constrained - % wind contribution (to 2MW limit) | PV constrained - % PV contribution (to 2MW) | PV constrained - % PV generation spilled | Wind constrained - % wind contribution (to 2MW limit) | Wind constrained - % PV contribution (to 2MW limit) | Wind constrained - % wind generation spilled
1 | 1 | January | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | Wind | Turbine Output Power kW - Lookup Table (Vestas V90)
1 | 2 | January | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | speed
1 | 3 | January | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | [m/s] | ρ = 1.225 | ρ = 0.95 | ρ = 0.975 | ρ = 1 | ρ = 1.025 | ρ = 1.05 | ρ = 1.075 | ρ = 1.1 | ρ = 1.125 | ρ = 1.15 | ρ = 1.175 | ρ = 1.2 | ρ = 1.25 | ρ = 1.275
1 | 4 | January | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 4 | 89 | 63 | 66 | 68 | 70 | 73 | 75 | 78 | 80 | 82 | 85 | 87 | 92 | 94
1 | 5 | January | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 4.5 | 142 | 105 | 108 | 112 | 115 | 119 | 122 | 125 | 129 | 132 | 136 | 139 | 146 | 149
1 | 6 | January | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 5 | 204 | 154 | 158 | 163 | 167 | 172 | 177 | 181 | 186 | 191 | 195 | 200 | 209 | 213
1 | 7 | January | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 5.5 | 279 | 211 | 217 | 224 | 230 | 236 | 242 | 248 | 254 | 260 | 266 | 272 | 285 | 291
1 | 8 | January | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 6 | 368 | 280 | 288 | 296 | 304 | 312 | 320 | 328 | 336 | 344 | 352 | 360 | 376 | 383
1 | 9 | January | 6.7 | 8.2487 | 761.6 | 23.814 | 785.414 | 0 | 785.414 | 0 | 0 | 96.968 | 3.032 | 0 | 96.968 | 3.032 | 0 | 6.5 | 470 | 356 | 366 | 377 | 387 | 398 | 408 | 418 | 429 | 439 | 449 | 459 | 480 | 490
1 | 10 | January | 8.2 | 10.0954 | 1359.15 | 155.4795 | 1514.6295 | 0 | 1514.6295 | 0 | 0 | 89.7348 | 10.2652 | 0 | 89.7348 | 10.2652 | 0 | 7 | 594 | 453 | 465 | 478 | 491 | 504 | 517 | 530 | 542 | 555 | 568 | 581 | 606 | 619
1 | 11 | January | 12.3 | 15.1431 | 1700 | 516.958 | 2216.958 | 1 | 2000 | 216.958 | 10.8479 | 76.6816 | 15 | 41.9682 | 74.1521 | 23.3184 | 12.7622 | 7.5 | 736 | 563 | 579 | 595 | 611 | 626 | 642 | 658 | 673 | 689 | 705 | 720 | 751 | 767
1 | 12 | January | 10.3 | 12.6808 | 1694.9 | 653.7723 | 2348.6723 | 1 | 2000 | 348.6723 | 17.4336 | 72.1642 | 15.255 | 53.3324 | 67.3114 | 27.8358 | 20.5719 | 8 | 896 | 688 | 707 | 726 | 745 | 764 | 783 | 802 | 821 | 840 | 858 | 877 | 915 | 933
1 | 13 | January | 9.8 | 12.0652 | 1683.85 | 183.658 | 1867.508 | 0 | 1867.508 | 0 | 0 | 90.1656 | 9.8344 | 0 | 90.1656 | 9.8344 | 0 | 8.5 | 1069 | 823 | 846 | 868 | 890 | 913 | 935 | 957 | 979 | 1002 | 1024 | 1046 | 1091 | 1113
1 | 14 | January | 10.3 | 12.6808 | 1694.9 | 414.1492 | 2109.0492 | 1 | 2000 | 109.0492 | 5.4525 | 80.3632 | 15.255 | 26.3309 | 79.2925 | 19.6368 | 6.434 | 9 | 1247 | 963 | 989 | 1015 | 1041 | 1067 | 1093 | 1118 | 1144 | 1170 | 1196 | 1222 | 1273 | 1299
1 | 15 | January | 11.8 | 14.5275 | 1700 | 93.0635 | 1793.0635 | 0 | 1793.0635 | 0 | 0 | 94.8098 | 5.1902 | 0 | 94.8098 | 5.1902 | 0 | 9.5 | 1428 | 1104 | 1134 | 1163 | 1193 | 1223 | 1252 | 1281 | 1311 | 1340 | 1370 | 1399 | 1457 | 1485
1 | 16 | January | 9.8 | 12.0652 | 1683.85 | 9.261 | 1693.111 | 0 | 1693.111 | 0 | 0 | 99.453 | 0.54698 | 0 | 99.453 | 0.54698 | 0 | 10 | 1599 | 1241 | 1274 | 1307 | 1340 | 1374 | 1406 | 1439 | 1472 | 1505 | 1536 | 1568 | 1629 | 1660
1 | 17 | January | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 10.5 | 1753 | 1375 | 1412 | 1448 | 1484 | 1521 | 1555 | 1590 | 1625 | 1660 | 1691 | 1722 | 1780 | 1806
1 | 18 | January | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 11 | 1881 | 1506 | 1545 | 1585 | 1624 | 1664 | 1698 | 1733 | 1767 | 1802 | 1828 | 1855 | 1900 | 1919
1 | 19 | January | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 11.5 | 1951 | 1633 | 1672 | 1711 | 1751 | 1790 | 1818 | 1847 | 1875 | 1903 | 1919 | 1935 | 1960 | 1969
1 | 20 | January | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 12 | 1981 | 1752 | 1786 | 1820 | 1854 | 1889 | 1906 | 1924 | 1942 | 1959 | 1967 | 1974 | 1985 | 1989
1 | 21 | January | 12.3 | 15.1431 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 12.5 | 1994 | 1852 | 1876 | 1900 | 1924 | 1949 | 1957 | 1966 | 1975 | 1984 | 1987 | 1990 | 1995 | 1997
1 | 22 | January | 13.4 | 16.4973 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 13 | 1998 | 1923 | 1937 | 1951 | 1964 | 1978 | 1982 | 1986 | 1990 | 1994 | 1996 | 1997 | 1999 | 1999
1 | 23 | January | 12.3 | 15.1431 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 13.5 | 2000 | 1962 | 1969 | 1977 | 1985 | 1992 | 1994 | 1996 | 1997 | 1999 | 1999 | 2000 | 2000 | 2000
1 | 24 | January | 13.4 | 16.4973 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 14 | 2000 | 1984 | 1988 | 1991 | 1994 | 1998 | 1998 | 1999 | 1999 | 2000 | 2000 | 2000 | 2000 | 2000
2 | 1 | January | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 14.5 | 2000 | 1994 | 1996 | 1997 | 1998 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
2 | 2 | January | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 15 | 2000 | 1998 | 1998 | 1999 | 1999 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
2 | 3 | January | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 15.5 | 2000 | 1999 | 1999 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
2 | 4 | January | 12.3 | 15.1431 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 16 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
2 | 5 | January | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 16.5 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
2 | 6 | January | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 17 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
2 | 7 | January | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 17.5 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
2 | 8 | January | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 18 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
2 | 9 | January | 11.8 | 14.5275 | 1700 | 13.23 | 1713.23 | 0 | 1713.23 | 0 | 0 | 99.2278 | 0.77223 | 0 | 99.2278 | 0.77223 | 0 | 18.5 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
2 | 10 | January | 9.8 | 12.0652 | 1683.85 | 309.2467 | 1993.0967 | 0 | 1993.0967 | 0 | 0 | 84.4841 | 15.5159 | 0 | 84.4841 | 15.5159 | 0 | 19 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
2 | 11 | January | 8.2 | 10.0954 | 1359.15 | 346.6247 | 1705.7747 | 0 | 1705.7747 | 0 | 0 | 79.6793 | 20.3207 | 0 | 79.6793 | 20.3207 | 0 | 19.5 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
2 | 12 | January | 8.2 | 10.0954 | 1359.15 | 271.0826 | 1630.2326 | 0 | 1630.2326 | 0 | 0 | 83.3715 | 16.6285 | 0 | 83.3715 | 16.6285 | 0 | 20 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
2 | 13 | January | 11.8 | 14.5275 | 1700 | 513.076 | 2213.076 | 1 | 2000 | 213.076 | 10.6538 | 76.8162 | 15 | 41.5291 | 74.3462 | 23.1838 | 12.5339 | 20.5 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
2 | 14 | January | 9.3 | 11.4496 | 1598.85 | 318.4386 | 1917.2886 | 0 | 1917.2886 | 0 | 0 | 83.3912 | 16.6088 | 0 | 83.3912 | 16.6088 | 0 | 21 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
2 | 15 | January | 9.3 | 11.4496 | 1598.85 | 226.0461 | 1824.8961 | 0 | 1824.8961 | 0 | 0 | 87.6132 | 12.3868 | 0 | 87.6132 | 12.3868 | 0 | 21.5 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
2 | 16 | January | 9.3 | 11.4496 | 1598.85 | 17.199 | 1616.049 | 0 | 1616.049 | 0 | 0 | 98.9357 | 1.0643 | 0 | 98.9357 | 1.0643 | 0 | 22 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
2 | 17 | January | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 22.5 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
2 | 18 | January | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 23 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
2 | 19 | January | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 23.5 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
2 | 20 | January | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 24 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
2 | 21 | January | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 24.5 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
2 | 22 | January | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 25 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
2 | 23 | January | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2 | 24 | January | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3 | 1 | January | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3 | 3 | January | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 4 | January | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 5 | January | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 6 | January | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 7 | January | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 8 | January | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 9 | January | 1 | 1.2311 | 0 | 23.814 | 23.814 | 0 | 23.814 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
3 | 10 | January | 1 | 1.2311 | 0 | 312.7422 | 312.7422 | 0 | 312.7422 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
3 | 11 | January | 1 | 1.2311 | 0 | 451.3921 | 451.3921 | 0 | 451.3921 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
3 | 12 | January | 1 | 1.2311 | 0 | 646.8567 | 646.8567 | 0 | 646.8567 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
3 | 13 | January | 1 | 1.2311 | 0 | 617.0082 | 617.0082 | 0 | 617.0082 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
3 | 14 | January | 1 | 1.2311 | 0 | 447.7055 | 447.7055 | 0 | 447.7055 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
3 | 15 | January | 1 | 1.2311 | 0 | 212.4968 | 212.4968 | 0 | 212.4968 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
3 | 16 | January | 1.5 | 1.8467 | 0 | 13.23 | 13.23 | 0 | 13.23 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
3 | 17 | January | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 18 | January | 0.5 | 0.61557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 19 | January | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3 | 20 | January | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 21 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3 | 22 | January | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3 | 23 | January | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3 | 24 | January | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4 | 1 | January | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4 | 2 | January | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4 | 3 | January | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4 | 4 | January | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4 | 5 | January | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4 | 6 | January | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4 | 7 | January | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4 | 8 | January | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4 | 9 | January | 5.1 | 6.2788 | 312.8 | 23.814 | 336.614 | 0 | 336.614 | 0 | 0 | 92.9254 | 7.0746 | 0 | 92.9254 | 7.0746 | 0
4 | 10 | January | 5.1 | 6.2788 | 312.8 | 138.4456 | 451.2456 | 0 | 451.2456 | 0 | 0 | 69.3192 | 30.6808 | 0 | 69.3192 | 30.6808 | 0
4 | 11 | January | 5.7 | 7.0175 | 504.9 | 224.5783 | 729.4783 | 0 | 729.4783 | 0 | 0 | 69.2138 | 30.7862 | 0 | 69.2138 | 30.7862 | 0
4 | 12 | January | 6.7 | 8.2487 | 761.6 | 584.5641 | 1346.1641 | 0 | 1346.1641 | 0 | 0 | 56.5756 | 43.4244 | 0 | 56.5756 | 43.4244 | 0
4 | 13 | January | 7.2 | 8.8642 | 908.65 | 513.2675 | 1421.9175 | 0 | 1421.9175 | 0 | 0 | 63.9031 | 36.0969 | 0 | 63.9031 | 36.0969 | 0
4 | 14 | January | 8.2 | 10.0954 | 1359.15 | 303.021 | 1662.171 | 0 | 1662.171 | 0 | 0 | 81.7696 | 18.2304 | 0 | 81.7696 | 18.2304 | 0
4 | 15 | January | 5.7 | 7.0175 | 504.9 | 58.212 | 563.112 | 0 | 563.112 | 0 | 0 | 89.6624 | 10.3376 | 0 | 89.6624 | 10.3376 | 0
4 | 16 | January | 6.2 | 7.6331 | 625.6 | 10.584 | 636.184 | 0 | 636.184 | 0 | 0 | 98.3363 | 1.6637 | 0 | 98.3363 | 1.6637 | 0
4 | 17 | January | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4 | 18 | January | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4 | 19 | January | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4 | 20 | January | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4 | 21 | January | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4 | 22 | January | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4 | 23 | January | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4 | 24 | January | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5 | 1 | January | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5 | 2 | January | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5 | 3 | January | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5 | 4 | January | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5 | 5 | January | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5 | 6 | January | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5 | 7 | January | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5 | 8 | January | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5 | 9 | January | 8.7 | 10.711 | 1490.05 | 14.553 | 1504.603 | 0 | 1504.603 | 0 | 0 | 99.0328 | 0.96723 | 0 | 99.0328 | 0.96723 | 0
5 | 10 | January | 8.7 | 10.711 | 1490.05 | 68.7583 | 1558.8083 | 0 | 1558.8083 | 0 | 0 | 95.589 | 4.411 | 0 | 95.589 | 4.411 | 0
5 | 11 | January | 11.8 | 14.5275 | 1700 | 126.4029 | 1826.4029 | 0 | 1826.4029 | 0 | 0 | 93.0791 | 6.9209 | 0 | 93.0791 | 6.9209 | 0
5 | 12 | January | 10.3 | 12.6808 | 1694.9 | 91.287 | 1786.187 | 0 | 1786.187 | 0 | 0 | 94.8893 | 5.1107 | 0 | 94.8893 | 5.1107 | 0
5 | 13 | January | 12.3 | 15.1431 | 1700 | 89.964 | 1789.964 | 0 | 1789.964 | 0 | 0 | 94.974 | 5.026 | 0 | 94.974 | 5.026 | 0
5 | 14 | January | 10.3 | 12.6808 | 1694.9 | 71.442 | 1766.342 | 0 | 1766.342 | 0 | 0 | 95.9554 | 4.0446 | 0 | 95.9554 | 4.0446 | 0
5 | 15 | January | 10.8 | 13.2964 | 1698.3 | 37.044 | 1735.344 | 0 | 1735.344 | 0 | 0 | 97.8653 | 2.1347 | 0 | 97.8653 | 2.1347 | 0
5 | 16 | January | 12.9 | 15.8818 | 1700 | 7.938 | 1707.938 | 0 | 1707.938 | 0 | 0 | 99.5352 | 0.46477 | 0 | 99.5352 | 0.46477 | 0
5 | 17 | January | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5 | 18 | January | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5 | 19 | January | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5 | 20 | January | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5 | 21 | January | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5 | 22 | January | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5 | 23 | January | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5 | 24 | January | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6 | 1 | January | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6 | 2 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6 | 3 | January | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 4 | January | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 5 | January | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 6 | January | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | January | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | January | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 9 | January | 0 | 0 | 0 | 14.553 | 14.553 | 0 | 14.553 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
6 | 10 | January | 3.1 | 3.8165 | 0 | 176.1539 | 176.1539 | 0 | 176.1539 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
6 | 11 | January | 3.6 | 4.4321 | 75.65 | 264.5344 | 340.1844 | 0 | 340.1844 | 0 | 0 | 22.2379 | 77.7621 | 0 | 22.2379 | 77.7621 | 0
6 | 12 | January | 4.6 | 5.6633 | 237.15 | 546.5471 | 783.6971 | 0 | 783.6971 | 0 | 0 | 30.2604 | 69.7396 | 0 | 30.2604 | 69.7396 | 0
6 | 13 | January | 7.7 | 9.4798 | 1059.95 | 630.9552 | 1690.9052 | 0 | 1690.9052 | 0 | 0 | 62.6854 | 37.3146 | 0 | 62.6854 | 37.3146 | 0
6 | 14 | January | 6.7 | 8.2487 | 761.6 | 238.5189 | 1000.1189 | 0 | 1000.1189 | 0 | 0 | 76.1509 | 23.8491 | 0 | 76.1509 | 23.8491 | 0
6 | 15 | January | 5.1 | 6.2788 | 312.8 | 97.3392 | 410.1392 | 0 | 410.1392 | 0 | 0 | 76.2668 | 23.7332 | 0 | 76.2668 | 23.7332 | 0
6 | 16 | January | 6.2 | 7.6331 | 625.6 | 18.522 | 644.122 | 0 | 644.122 | 0 | 0 | 97.1245 | 2.8755 | 0 | 97.1245 | 2.8755 | 0
6 | 17 | January | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6 | 18 | January | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6 | 19 | January | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6 | 20 | January | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6 | 21 | January | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6 | 22 | January | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6 | 23 | January | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6 | 24 | January | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1 | January | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2 | January | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7 | 4 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7 | 5 | January | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 6 | January | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | January | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | January | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 9 | January | 1.5 | 1.8467 | 0 | 18.522 | 18.522 | 0 | 18.522 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
7 | 10 | January | 1.5 | 1.8467 | 0 | 201.1115 | 201.1115 | 0 | 201.1115 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
7 | 11 | January | 1.5 | 1.8467 | 0 | 130.9969 | 130.9969 | 0 | 130.9969 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
7 | 12 | January | 2.6 | 3.201 | 0 | 176.6497 | 176.6497 | 0 | 176.6497 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
7 | 13 | January | 2.1 | 2.5854 | 0 | 173.6414 | 173.6414 | 0 | 173.6414 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
7 | 14 | January | 2.1 | 2.5854 | 0 | 128.9718 | 128.9718 | 0 | 128.9718 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
7 | 15 | January | 3.1 | 3.8165 | 0 | 63.504 | 63.504 | 0 | 63.504 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
7 | 16 | January | 2.6 | 3.201 | 0 | 13.23 | 13.23 | 0 | 13.23 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
7 | 17 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7 | 18 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7 | 19 | January | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 20 | January | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7 | 21 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7 | 22 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7 | 23 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7 | 24 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8 | 1 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8 | 2 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8 | 3 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8 | 4 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8 | 5 | January | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8 | 6 | January | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8 | 7 | January | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8 | 8 | January | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | January | 3.6 | 4.4321 | 75.65 | 9.261 | 84.911 | 0 | 84.911 | 0 | 0 | 89.0933 | 10.9067 | 0 | 89.0933 | 10.9067 | 0
8 | 10 | January | 3.6 | 4.4321 | 75.65 | 41.013 | 116.663 | 0 | 116.663 | 0 | 0 | 64.8449 | 35.1551 | 0 | 64.8449 | 35.1551 | 0
8 | 11 | January | 5.1 | 6.2788 | 312.8 | 74.088 | 386.888 | 0 | 386.888 | 0 | 0 | 80.8503 | 19.1497 | 0 | 80.8503 | 19.1497 | 0
8 | 12 | January | 5.1 | 6.2788 | 312.8 | 92.61 | 405.41 | 0 | 405.41 | 0 | 0 | 77.1565 | 22.8435 | 0 | 77.1565 | 22.8435 | 0
8 | 13 | January | 7.7 | 9.4798 | 1059.95 | 92.61 | 1152.56 | 0 | 1152.56 | 0 | 0 | 91.9648 | 8.0352 | 0 | 91.9648 | 8.0352 | 0
8 | 14 | January | 6.2 | 7.6331 | 625.6 | 130.9241 | 756.5241 | 0 | 756.5241 | 0 | 0 | 82.694 | 17.306 | 0 | 82.694 | 17.306 | 0
8 | 15 | January | 7.2 | 8.8642 | 908.65 | 64.827 | 973.477 | 0 | 973.477 | 0 | 0 | 93.3407 | 6.6593 | 0 | 93.3407 | 6.6593 | 0
8 | 16 | January | 6.2 | 7.6331 | 625.6 | 21.168 | 646.768 | 0 | 646.768 | 0 | 0 | 96.7271 | 3.2729 | 0 | 96.7271 | 3.2729 | 0
8 | 17 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8 | 18 | January | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8 | 19 | January | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8 | 20 | January | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8 | 21 | January | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8 | 22 | January | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | January | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8 | 24 | January | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
9 | 1 | January | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
9 | 2 | January | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
9 | 3 | January | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
9 | 4 | January | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
9 | 5 | January | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
9 | 6 | January | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
9 | 7 | January | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
9 | 8 | January | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
9 | 9 | January | 6.2 | 7.6331 | 625.6 | 26.46 | 652.06 | 0 | 652.06 | 0 | 0 | 95.9421 | 4.0579 | 0 | 95.9421 | 4.0579 | 0
9 | 10 | January | 6.7 | 8.2487 | 761.6 | 72.7569 | 834.3569 | 0 | 834.3569 | 0 | 0 | 91.2799 | 8.7201 | 0 | 91.2799 | 8.7201 | 0
9 | 11 | January | 7.2 | 8.8642 | 908.65 | 75.411 | 984.061 | 0 | 984.061 | 0 | 0 | 92.3368 | 7.6632 | 0 | 92.3368 | 7.6632 | 0
9 | 12 | January | 8.7 | 10.711 | 1490.05 | 93.933 | 1583.983 | 0 | 1583.983 | 0 | 0 | 94.0698 | 5.9302 | 0 | 94.0698 | 5.9302 | 0
9 | 13 | January | 10.3 | 12.6808 | 1694.9 | 93.933 | 1788.833 | 0 | 1788.833 | 0 | 0 | 94.7489 | 5.2511 | 0 | 94.7489 | 5.2511 | 0
9 | 14 | January | 9.3 | 11.4496 | 1598.85 | 75.411 | 1674.261 | 0 | 1674.261 | 0 | 0 | 95.4959 | 4.5041 | 0 | 95.4959 | 4.5041 | 0
9 | 15 | January | 11.3 | 13.9119 | 1700 | 41.013 | 1741.013 | 0 | 1741.013 | 0 | 0 | 97.6443 | 2.3557 | 0 | 97.6443 | 2.3557 | 0
9 | 16 | January | 11.8 | 14.5275 | 1700 | 14.553 | 1714.553 | 0 | 1714.553 | 0 | 0 | 99.1512 | 0.84879 | 0 | 99.1512 | 0.84879 | 0
9 | 17 | January | 12.9 | 15.8818 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
9 | 18 | January | 14.4 | 17.7285 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
9 | 19 | January | 12.9 | 15.8818 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
9 | 20 | January | 11.8 | 14.5275 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
9 | 21 | January | 12.3 | 15.1431 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
9 | 22 | January | 13.7 | 16.8667 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
9 | 23 | January | 15 | 18.4672 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
9 | 24 | January | 16.4 | 20.1908 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
10 | 1 | January | 14.5 | 17.8516 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
10 | 2 | January | 12.7 | 15.6355 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
10 | 3 | January | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
10 | 4 | January | 9.9 | 12.1883 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
10 | 5 | January | 9.1 | 11.2034 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
10 | 6 | January | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
10 | 7 | January | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
10 | 8 | January | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
10 | 9 | January | 7.5 | 9.2336 | 1059.95 | 26.46 | 1086.41 | 0 | 1086.41 | 0 | 0 | 97.5645 | 2.4355 | 0 | 97.5645 | 2.4355 | 0
10 | 10 | January | 8.2 | 10.0954 | 1359.15 | 191.3016 | 1550.4516 | 0 | 1550.4516 | 0 | 0 | 87.6616 | 12.3384 | 0 | 87.6616 | 12.3384 | 0
10 | 11 | January | 9.3 | 11.4496 | 1598.85 | 277.1712 | 1876.0212 | 0 | 1876.0212 | 0 | 0 | 85.2256 | 14.7744 | 0 | 85.2256 | 14.7744 | 0
10 | 12 | January | 8.7 | 10.711 | 1490.05 | 95.256 | 1585.306 | 0 | 1585.306 | 0 | 0 | 93.9913 | 6.0087 | 0 | 93.9913 | 6.0087 | 0
10 | 13 | January | 10.8 | 13.2964 | 1698.3 | 95.256 | 1793.556 | 0 | 1793.556 | 0 | 0 | 94.689 | 5.311 | 0 | 94.689 | 5.311 | 0
10 | 14 | January | 6.7 | 8.2487 | 761.6 | 76.734 | 838.334 | 0 | 838.334 | 0 | 0 | 90.8468 | 9.1532 | 0 | 90.8468 | 9.1532 | 0
10 | 15 | January | 5.1 | 6.2788 | 312.8 | 42.336 | 355.136 | 0 | 355.136 | 0 | 0 | 88.0789 | 11.9211 | 0 | 88.0789 | 11.9211 | 0
10 | 16 | January | 1.5 | 1.8467 | 0 | 9.261 | 9.261 | 0 | 9.261 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
10 | 17 | January | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | January | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | January | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
10 | 20 | January | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
10 | 21 | January | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
10 | 22 | January | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
10 | 23 | January | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
10 | 24 | January | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
11 | 1 | January | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
11 | 2 | January | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
11 | 3 | January | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
11 | 4 | January | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
11 | 5 | January | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
11 | 6 | January | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
11 | 7 | January | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
11 | 8 | January | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
11 | 9 | January | 5.7 | 7.0175 | 504.9 | 27.783 | 532.683 | 0 | 532.683 | 0 | 0 | 94.7843 | 5.2157 | 0 | 94.7843 | 5.2157 | 0
11 | 10 | January | 8.2 | 10.0954 | 1359.15 | 195.6757 | 1554.8257 | 0 | 1554.8257 | 0 | 0 | 87.4149 | 12.5851 | 0 | 87.4149 | 12.5851 | 0
11 | 11 | January | 7.7 | 9.4798 | 1059.95 | 467.7563 | 1527.7063 | 0 | 1527.7063 | 0 | 0 | 69.3818 | 30.6182 | 0 | 69.3818 | 30.6182 | 0
11 | 12 | January | 8.7 | 10.711 | 1490.05 | 314.6426 | 1804.6926 | 0 | 1804.6926 | 0 | 0 | 82.5653 | 17.4347 | 0 | 82.5653 | 17.4347 | 0
11 | 13 | January | 7.7 | 9.4798 | 1059.95 | 292.0989 | 1352.0489 | 0 | 1352.0489 | 0 | 0 | 78.3958 | 21.6042 | 0 | 78.3958 | 21.6042 | 0
11 | 14 | January | 8.7 | 10.711 | 1490.05 | 474.0263 | 1964.0763 | 0 | 1964.0763 | 0 | 0 | 75.8652 | 24.1348 | 0 | 75.8652 | 24.1348 | 0
11 | 15 | January | 8 | 9.8492 | 1213.8 | 207.6939 | 1421.4939 | 0 | 1421.4939 | 0 | 0 | 85.389 | 14.611 | 0 | 85.389 | 14.611 | 0
11 | 16 | January | 7.2 | 8.8642 | 908.65 | 21.168 | 929.818 | 0 | 929.818 | 0 | 0 | 97.7234 | 2.2766 | 0 | 97.7234 | 2.2766 | 0
11 | 17 | January | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
11 | 18 | January | 11.8 | 14.5275 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
11 | 19 | January | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
11 | 20 | January | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
11 | 21 | January | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
11 | 22 | January | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
11 | 23 | January | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
11 | 24 | January | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
12 | 1 | January | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
12 | 2 | January | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
12 | 3 | January | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
12 | 4 | January | 13.4 | 16.4973 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
12 | 5 | January | 12.3 | 15.1431 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
12 | 6 | January | 12.3 | 15.1431 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
12 | 7 | January | 11.8 | 14.5275 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
12 | 8 | January | 13.4 | 16.4973 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
12 | 9 | January | 12.3 | 15.1431 | 1700 | 29.106 | 1729.106 | 0 | 1729.106 | 0 | 0 | 98.3167 | 1.6833 | 0 | 98.3167 | 1.6833 | 0
12 | 10 | January | 12.3 | 15.1431 | 1700 | 267.3446 | 1967.3446 | 0 | 1967.3446 | 0 | 0 | 86.4109 | 13.5891 | 0 | 86.4109 | 13.5891 | 0
12 | 11 | January | 10.3 | 12.6808 | 1694.9 | 260.1928 | 1955.0928 | 0 | 1955.0928 | 0 | 0 | 86.6915 | 13.3085 | 0 | 86.6915 | 13.3085 | 0
12 | 12 | January | 11.8 | 14.5275 | 1700 | 481.0682 | 2181.0682 | 1 | 2000 | 181.0682 | 9.0534 | 77.9435 | 15 | 37.6388 | 75.9466 | 22.0565 | 10.6511
12 | 13 | January | 12.3 | 15.1431 | 1700 | 577.324 | 2277.324 | 1 | 2000 | 277.324 | 13.8662 | 74.649 | 15 | 48.0361 | 71.1338 | 25.351 | 16.3132
12 | 14 | January | 10.8 | 13.2964 | 1698.3 | 265.8114 | 1964.1114 | 0 | 1964.1114 | 0 | 0 | 86.4666 | 13.5334 | 0 | 86.4666 | 13.5334 | 0
12 | 15 | January | 8.2 | 10.0954 | 1359.15 | 270.7005 | 1629.8505 | 0 | 1629.8505 | 0 | 0 | 83.3911 | 16.6089 | 0 | 83.3911 | 16.6089 | 0
12 | 16 | January | 6.7 | 8.2487 | 761.6 | 30.429 | 792.029 | 0 | 792.029 | 0 | 0 | 96.1581 | 3.8419 | 0 | 96.1581 | 3.8419 | 0
12 | 17 | January | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
12 | 18 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
12 | 19 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
12 | 20 | January | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
12 | 21 | January | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
12 | 22 | January | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
12 | 23 | January | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
12 | 24 | January | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 1 | January | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 2 | January | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 3 | January | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 4 | January | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 5 | January | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 6 | January | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 7 | January | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 8 | January | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
13 | 9 | January | 3.6 | 4.4321 | 75.65 | 10.584 | 86.234 | 0 | 86.234 | 0 | 0 | 87.7264 | 12.2736 | 0 | 87.7264 | 12.2736 | 0
13 | 10 | January | 4.6 | 5.6633 | 237.15 | 46.305 | 283.455 | 0 | 283.455 | 0 | 0 | 83.6641 | 16.3359 | 0 | 83.6641 | 16.3359 | 0
13 | 11 | January | 5.1 | 6.2788 | 312.8 | 80.703 | 393.503 | 0 | 393.503 | 0 | 0 | 79.4911 | 20.5089 | 0 | 79.4911 | 20.5089 | 0
13 | 12 | January | 5.1 | 6.2788 | 312.8 | 100.548 | 413.348 | 0 | 413.348 | 0 | 0 | 75.6747 | 24.3253 | 0 | 75.6747 | 24.3253 | 0
13 | 13 | January | 5.1 | 6.2788 | 312.8 | 100.548 | 413.348 | 0 | 413.348 | 0 | 0 | 75.6747 | 24.3253 | 0 | 75.6747 | 24.3253 | 0
13 | 14 | January | 3.6 | 4.4321 | 75.65 | 80.703 | 156.353 | 0 | 156.353 | 0 | 0 | 48.3841 | 51.6159 | 0 | 48.3841 | 51.6159 | 0
13 | 15 | January | 4.1 | 5.0477 | 173.4 | 78.5724 | 251.9724 | 0 | 251.9724 | 0 | 0 | 68.8171 | 31.1829 | 0 | 68.8171 | 31.1829 | 0
13 | 16 | January | 3.6 | 4.4321 | 75.65 | 18.522 | 94.172 | 0 | 94.172 | 0 | 0 | 80.3317 | 19.6683 | 0 | 80.3317 | 19.6683 | 0
13 | 17 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
13 | 18 | January | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 19 | January | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 20 | January | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 21 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
13 | 22 | January | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 23 | January | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
13 | 24 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
14 | 1 | January | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 2 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
14 | 3 | January | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 4 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
14 | 5 | January | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
14 | 6 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
14 | 7 | January | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
14 | 8 | January | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
14 | 9 | January | 5.7 | 7.0175 | 504.9 | 22.491 | 527.391 | 0 | 527.391 | 0 | 0 | 95.7354 | 4.2646 | 0 | 95.7354 | 4.2646 | 0
14 | 10 | January | 5.7 | 7.0175 | 504.9 | 84.4012 | 589.3012 | 0 | 589.3012 | 0 | 0 | 85.6778 | 14.3222 | 0 | 85.6778 | 14.3222 | 0
14 | 11 | January | 6.2 | 7.6331 | 625.6 | 140.7378 | 766.3378 | 0 | 766.3378 | 0 | 0 | 81.635 | 18.365 | 0 | 81.635 | 18.365 | 0
14 | 12 | January | 6.7 | 8.2487 | 761.6 | 191.3801 | 952.9801 | 0 | 952.9801 | 0 | 0 | 79.9177 | 20.0823 | 0 | 79.9177 | 20.0823 | 0
14 | 13 | January | 6.7 | 8.2487 | 761.6 | 189.7038 | 951.3038 | 0 | 951.3038 | 0 | 0 | 80.0585 | 19.9415 | 0 | 80.0585 | 19.9415 | 0
14 | 14 | January | 5.1 | 6.2788 | 312.8 | 146.5732 | 459.3732 | 0 | 459.3732 | 0 | 0 | 68.0928 | 31.9072 | 0 | 68.0928 | 31.9072 | 0
14 | 15 | January | 5.7 | 7.0175 | 504.9 | 78.4177 | 583.3177 | 0 | 583.3177 | 0 | 0 | 86.5566 | 13.4434 | 0 | 86.5566 | 13.4434 | 0
14 | 16 | January | 4.6 | 5.6633 | 237.15 | 19.845 | 256.995 | 0 | 256.995 | 0 | 0 | 92.2781 | 7.7219 | 0 | 92.2781 | 7.7219 | 0
14 | 17 | January | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
14 | 18 | January | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
14 | 19 | January | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
14 | 20 | January | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
14 | 21 | January | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
14 | 22 | January | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
14 | 23 | January | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
14 | 24 | January | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
15 | 1 | January | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
15 | 2 | January | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
15 | 3 | January | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
15 | 4 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
15 | 5 | January | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 6 | January | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 7 | January | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 8 | January | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 9 | January | 2.6 | 3.201 | 0 | 11.907 | 11.907 | 0 | 11.907 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
15 | 10 | January | 3.6 | 4.4321 | 75.65 | 46.305 | 121.955 | 0 | 121.955 | 0 | 0 | 62.0311 | 37.9689 | 0 | 62.0311 | 37.9689 | 0
15 | 11 | January | 2.6 | 3.201 | 0 | 82.026 | 82.026 | 0 | 82.026 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
15 | 12 | January | 4.1 | 5.0477 | 173.4 | 101.871 | 275.271 | 0 | 275.271 | 0 | 0 | 62.9925 | 37.0075 | 0 | 62.9925 | 37.0075 | 0
15 | 13 | January | 6.2 | 7.6331 | 625.6 | 412.5681 | 1038.1681 | 0 | 1038.1681 | 0 | 0 | 60.26 | 39.74 | 0 | 60.26 | 39.74 | 0
15 | 14 | January | 5.7 | 7.0175 | 504.9 | 156.9845 | 661.8845 | 0 | 661.8845 | 0 | 0 | 76.2822 | 23.7178 | 0 | 76.2822 | 23.7178 | 0
15 | 15 | January | 4.1 | 5.0477 | 173.4 | 272.5472 | 445.9472 | 0 | 445.9472 | 0 | 0 | 38.8835 | 61.1165 | 0 | 38.8835 | 61.1165 | 0
15 | 16 | January | 4.1 | 5.0477 | 173.4 | 21.168 | 194.568 | 0 | 194.568 | 0 | 0 | 89.1205 | 10.8795 | 0 | 89.1205 | 10.8795 | 0
15 | 17 | January | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
15 | 18 | January | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
15 | 19 | January | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
15 | 20 | January | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
15 | 21 | January | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
15 | 22 | January | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
15 | 23 | January | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
15 | 24 | January | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
16 | 1 | January | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
16 | 2 | January | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
16 | 3 | January | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
16 | 4 | January | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
16 | 5 | January | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
16 | 6 | January | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
16 | 7 | January | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
16 | 8 | January | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
16 | 9 | January | 11.8 | 14.5275 | 1700 | 19.845 | 1719.845 | 0 | 1719.845 | 0 | 0 | 98.8461 | 1.1539 | 0 | 98.8461 | 1.1539 | 0
16 | 10 | January | 10.8 | 13.2964 | 1698.3 | 220.1265 | 1918.4265 | 0 | 1918.4265 | 0 | 0 | 88.5257 | 11.4743 | 0 | 88.5257 | 11.4743 | 0
16 | 11 | January | 10.3 | 12.6808 | 1694.9 | 423.8573 | 2118.7573 | 1 | 2000 | 118.7573 | 5.9379 | 79.995 | 15.255 | 28.0182 | 78.8071 | 20.005 | 7.0067
16 | 12 | January | 11.3 | 13.9119 | 1700 | 214.2639 | 1914.2639 | 0 | 1914.2639 | 0 | 0 | 88.807 | 11.193 | 0 | 88.807 | 11.193 | 0
16 | 13 | January | 11.8 | 14.5275 | 1700 | 198.6165 | 1898.6165 | 0 | 1898.6165 | 0 | 0 | 89.5389 | 10.4611 | 0 | 89.5389 | 10.4611 | 0
16 | 14 | January | 10.3 | 12.6808 | 1694.9 | 159.1539 | 1854.0539 | 0 | 1854.0539 | 0 | 0 | 91.4159 | 8.5841 | 0 | 91.4159 | 8.5841 | 0
16 | 15 | January | 9.3 | 11.4496 | 1598.85 | 85.2657 | 1684.1157 | 0 | 1684.1157 | 0 | 0 | 94.9371 | 5.0629 | 0 | 94.9371 | 5.0629 | 0
16 | 16 | January | 12.9 | 15.8818 | 1700 | 14.553 | 1714.553 | 0 | 1714.553 | 0 | 0 | 99.1512 | 0.84879 | 0 | 99.1512 | 0.84879 | 0
16 | 17 | January | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
16 | 18 | January | 13.4 | 16.4973 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
16 | 19 | January | 11.8 | 14.5275 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
16 | 20 | January | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
16 | 21 | January | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
16 | 22 | January | 12.9 | 15.8818 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
16 | 23 | January | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
16 | 24 | January | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
17 | 1 | January | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
17 | 2 | January | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
17 | 3 | January | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
17 | 4 | January | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
17 | 5 | January | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
17 | 6 | January | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
17 | 7 | January | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
17 | 8 | January | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
17 | 9 | January | 9.8 | 12.0652 | 1683.85 | 13.23 | 1697.08 | 0 | 1697.08 | 0 | 0 | 99.2204 | 0.77957 | 0 | 99.2204 | 0.77957 | 0
17 | 10 | January | 11.8 | 14.5275 | 1700 | 48.951 | 1748.951 | 0 | 1748.951 | 0 | 0 | 97.2011 | 2.7989 | 0 | 97.2011 | 2.7989 | 0
17 | 11 | January | 11.3 | 13.9119 | 1700 | 84.672 | 1784.672 | 0 | 1784.672 | 0 | 0 | 95.2556 | 4.7444 | 0 | 95.2556 | 4.7444 | 0
17 | 12 | January | 12.3 | 15.1431 | 1700 | 105.84 | 1805.84 | 0 | 1805.84 | 0 | 0 | 94.139 | 5.861 | 0 | 94.139 | 5.861 | 0
17 | 13 | January | 10.3 | 12.6808 | 1694.9 | 105.84 | 1800.74 | 0 | 1800.74 | 0 | 0 | 94.1224 | 5.8776 | 0 | 94.1224 | 5.8776 | 0
17 | 14 | January | 11.8 | 14.5275 | 1700 | 87.318 | 1787.318 | 0 | 1787.318 | 0 | 0 | 95.1146 | 4.8854 | 0 | 95.1146 | 4.8854 | 0
17 | 15 | January | 11.8 | 14.5275 | 1700 | 52.92 | 1752.92 | 0 | 1752.92 | 0 | 0 | 96.981 | 3.019 | 0 | 96.981 | 3.019 | 0
17 | 16 | January | 13.9 | 17.1129 | 1700 | 14.553 | 1714.553 | 0 | 1714.553 | 0 | 0 | 99.1512 | 0.84879 | 0 | 99.1512 | 0.84879 | 0
17 | 17 | January | 12.9 | 15.8818 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
17 | 18 | January | 15.9 | 19.5752 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
17 | 19 | January | 15.4 | 18.9596 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
17 | 20 | January | 15.9 | 19.5752 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
17 | 21 | January | 17.5 | 21.545 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
17 | 22 | January | 17 | 20.9295 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
17 | 23 | January | 14.4 | 17.7285 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
17 | 24 | January | 11.8 | 14.5275 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
18 | 1 | January | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
18 | 2 | January | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
18 | 3 | January | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
18 | 4 | January | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
18 | 5 | January | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
18 | 6 | January | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
18 | 7 | January | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
18 | 8 | January | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
18 | 9 | January | 6.2 | 7.6331 | 625.6 | 21.168 | 646.768 | 0 | 646.768 | 0 | 0 | 96.7271 | 3.2729 | 0 | 96.7271 | 3.2729 | 0
18 | 10 | January | 5.7 | 7.0175 | 504.9 | 99.4389 | 604.3389 | 0 | 604.3389 | 0 | 0 | 83.5458 | 16.4542 | 0 | 83.5458 | 16.4542 | 0
18 | 11 | January | 5.7 | 7.0175 | 504.9 | 283.8938 | 788.7938 | 0 | 788.7938 | 0 | 0 | 64.0091 | 35.9909 | 0 | 64.0091 | 35.9909 | 0
18 | 12 | January | 5.7 | 7.0175 | 504.9 | 613.7525 | 1118.6525 | 0 | 1118.6525 | 0 | 0 | 45.1347 | 54.8653 | 0 | 45.1347 | 54.8653 | 0
18 | 13 | January | 7.7 | 9.4798 | 1059.95 | 716.8976 | 1776.8476 | 0 | 1776.8476 | 0 | 0 | 59.6534 | 40.3466 | 0 | 59.6534 | 40.3466 | 0
18 | 14 | January | 7.7 | 9.4798 | 1059.95 | 556.5047 | 1616.4547 | 0 | 1616.4547 | 0 | 0 | 65.5725 | 34.4275 | 0 | 65.5725 | 34.4275 | 0
18 | 15 | January | 5.7 | 7.0175 | 504.9 | 319.1367 | 824.0367 | 0 | 824.0367 | 0 | 0 | 61.2715 | 38.7285 | 0 | 61.2715 | 38.7285 | 0
18 | 16 | January | 5.1 | 6.2788 | 312.8 | 89.6491 | 402.4491 | 0 | 402.4491 | 0 | 0 | 77.7241 | 22.2759 | 0 | 77.7241 | 22.2759 | 0
18 | 17 | January | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
18 | 18 | January | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
18 | 19 | January | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
18 | 20 | January | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
18 | 21 | January | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
18 | 22 | January | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 23 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
18 | 24 | January | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
19 | 1 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
19 | 2 | January | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
19 | 3 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
19 | 4 | January | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
19 | 5 | January | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
19 | 6 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
19 | 7 | January | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
19 | 8 | January | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
19 | 9 | January | 4.6 | 5.6633 | 237.15 | 86.3999 | 323.5499 | 0 | 323.5499 | 0 | 0 | 73.2963 | 26.7037 | 0 | 73.2963 | 26.7037 | 0
19 | 10 | January | 6.7 | 8.2487 | 761.6 | 226.9197 | 988.5197 | 0 | 988.5197 | 0 | 0 | 77.0445 | 22.9555 | 0 | 77.0445 | 22.9555 | 0
19 | 11 | January | 8.2 | 10.0954 | 1359.15 | 178.5809 | 1537.7309 | 0 | 1537.7309 | 0 | 0 | 88.3867 | 11.6133 | 0 | 88.3867 | 11.6133 | 0
19 | 12 | January | 11.8 | 14.5275 | 1700 | 108.486 | 1808.486 | 0 | 1808.486 | 0 | 0 | 94.0013 | 5.9987 | 0 | 94.0013 | 5.9987 | 0
19 | 13 | January | 11.8 | 14.5275 | 1700 | 109.809 | 1809.809 | 0 | 1809.809 | 0 | 0 | 93.9326 | 6.0674 | 0 | 93.9326 | 6.0674 | 0
19 | 14 | January | 12.9 | 15.8818 | 1700 | 91.287 | 1791.287 | 0 | 1791.287 | 0 | 0 | 94.9038 | 5.0962 | 0 | 94.9038 | 5.0962 | 0
19 | 15 | January | 16.4 | 20.1908 | 1700 | 55.566 | 1755.566 | 0 | 1755.566 | 0 | 0 | 96.8349 | 3.1651 | 0 | 96.8349 | 3.1651 | 0
19 | 16 | January | 16.4 | 20.1908 | 1700 | 15.876 | 1715.876 | 0 | 1715.876 | 0 | 0 | 99.0748 | 0.92524 | 0 | 99.0748 | 0.92524 | 0
19 | 17 | January | 18.5 | 22.7762 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
19 | 18 | January | 14.9 | 18.3441 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
19 | 19 | January | 11.8 | 14.5275 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
19 | 20 | January | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
19 | 21 | January | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
19 | 22 | January | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
19 | 23 | January | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
19 | 24 | January | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
20 | 1 | January | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
20 | 2 | January | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
20 | 3 | January | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
20 | 4 | January | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
20 | 5 | January | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
20 | 6 | January | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
20 | 7 | January | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
20 | 8 | January | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
20 | 9 | January | 12.3 | 15.1431 | 1700 | 74.6627 | 1774.6627 | 0 | 1774.6627 | 0 | 0 | 95.7929 | 4.2071 | 0 | 95.7929 | 4.2071 | 0
20 | 10 | January | 10.3 | 12.6808 | 1694.9 | 231.5116 | 1926.4116 | 0 | 1926.4116 | 0 | 0 | 87.9822 | 12.0178 | 0 | 87.9822 | 12.0178 | 0
20 | 11 | January | 8.2 | 10.0954 | 1359.15 | 449.1538 | 1808.3038 | 0 | 1808.3038 | 0 | 0 | 75.1616 | 24.8384 | 0 | 75.1616 | 24.8384 | 0
20 | 12 | January | 8.7 | 10.711 | 1490.05 | 226.5921 | 1716.6421 | 0 | 1716.6421 | 0 | 0 | 86.8003 | 13.1997 | 0 | 86.8003 | 13.1997 | 0
20 | 13 | January | 10.8 | 13.2964 | 1698.3 | 513.0409 | 2211.3409 | 1 | 2000 | 211.3409 | 10.567 | 76.7996 | 15.085 | 41.1938 | 74.348 | 23.2004 | 12.4443
20 | 14 | January | 10.8 | 13.2964 | 1698.3 | 580.2494 | 2278.5494 | 1 | 2000 | 278.5494 | 13.9275 | 74.5343 | 15.085 | 48.0051 | 70.9875 | 25.4657 | 16.4017
20 | 15 | January | 8.2 | 10.0954 | 1359.15 | 253.1685 | 1612.3185 | 0 | 1612.3185 | 0 | 0 | 84.2979 | 15.7021 | 0 | 84.2979 | 15.7021 | 0
20 | 16 | January | 7.7 | 9.4798 | 1059.95 | 50.8172 | 1110.7672 | 0 | 1110.7672 | 0 | 0 | 95.425 | 4.575 | 0 | 95.425 | 4.575 | 0
20 | 17 | January | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
20 | 18 | January | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
20 | 19 | January | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
20 | 20 | January | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
20 | 21 | January | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
20 | 22 | January | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
20 | 23 | January | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
20 | 24 | January | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
21 | 1 | January | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
21 | 2 | January | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
21 | 3 | January | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
21 | 4 | January | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
21 | 5 | January | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
21 | 6 | January | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
21 | 7 | January | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
21 | 8 | January | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
21 | 9 | January | 6.7 | 8.2487 | 761.6 | 23.814 | 785.414 | 0 | 785.414 | 0 | 0 | 96.968 | 3.032 | 0 | 96.968 | 3.032 | 0
21 | 10 | January | 8.2 | 10.0954 | 1359.15 | 109.4237 | 1468.5737 | 0 | 1468.5737 | 0 | 0 | 92.549 | 7.451 | 0 | 92.549 | 7.451 | 0
21 | 11 | January | 11.3 | 13.9119 | 1700 | 185.1054 | 1885.1054 | 0 | 1885.1054 | 0 | 0 | 90.1806 | 9.8194 | 0 | 90.1806 | 9.8194 | 0
21 | 12 | January | 12.3 | 15.1431 | 1700 | 112.455 | 1812.455 | 0 | 1812.455 | 0 | 0 | 93.7954 | 6.2046 | 0 | 93.7954 | 6.2046 | 0
21 | 13 | January | 14.9 | 18.3441 | 1700 | 113.778 | 1813.778 | 0 | 1813.778 | 0 | 0 | 93.727 | 6.273 | 0 | 93.727 | 6.273 | 0
21 | 14 | January | 13.4 | 16.4973 | 1700 | 95.256 | 1795.256 | 0 | 1795.256 | 0 | 0 | 94.694 | 5.306 | 0 | 94.694 | 5.306 | 0
21 | 15 | January | 17 | 20.9295 | 1700 | 59.535 | 1759.535 | 0 | 1759.535 | 0 | 0 | 96.6164 | 3.3836 | 0 | 96.6164 | 3.3836 | 0
21 | 16 | January | 16.4 | 20.1908 | 1700 | 18.522 | 1718.522 | 0 | 1718.522 | 0 | 0 | 98.9222 | 1.0778 | 0 | 98.9222 | 1.0778 | 0
21 | 17 | January | 8.7 | 10.711 | 1490.05 | 1.323 | 1491.373 | 0 | 1491.373 | 0 | 0 | 99.9113 | 0.08871 | 0 | 99.9113 | 0.08871 | 0
21 | 18 | January | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
21 | 19 | January | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
21 | 20 | January | 11.8 | 14.5275 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
21 | 21 | January | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
21 | 22 | January | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
21 | 23 | January | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
21 | 24 | January | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
22 | 1 | January | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
22 | 2 | January | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
22 | 3 | January | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
22 | 4 | January | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
22 | 5 | January | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
22 | 6 | January | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
22 | 7 | January | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
22 | 8 | January | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
22 | 9 | January | 8.2 | 10.0954 | 1359.15 | 25.137 | 1384.287 | 0 | 1384.287 | 0 | 0 | 98.1841 | 1.8159 | 0 | 98.1841 | 1.8159 | 0
22 | 10 | January | 7.2 | 8.8642 | 908.65 | 112.7814 | 1021.4314 | 0 | 1021.4314 | 0 | 0 | 88.9585 | 11.0415 | 0 | 88.9585 | 11.0415 | 0
22 | 11 | January | 6.7 | 8.2487 | 761.6 | 189.0477 | 950.6477 | 0 | 950.6477 | 0 | 0 | 80.1138 | 19.8862 | 0 | 80.1138 | 19.8862 | 0
22 | 12 | January | 5.1 | 6.2788 | 312.8 | 216.7561 | 529.5561 | 0 | 529.5561 | 0 | 0 | 59.0683 | 40.9317 | 0 | 59.0683 | 40.9317 | 0
22 | 13 | January | 5.7 | 7.0175 | 504.9 | 115.101 | 620.001 | 0 | 620.001 | 0 | 0 | 81.4354 | 18.5646 | 0 | 81.4354 | 18.5646 | 0
22 | 14 | January | 4.6 | 5.6633 | 237.15 | 96.579 | 333.729 | 0 | 333.729 | 0 | 0 | 71.0607 | 28.9393 | 0 | 71.0607 | 28.9393 | 0
22 | 15 | January | 4.6 | 5.6633 | 237.15 | 60.858 | 298.008 | 0 | 298.008 | 0 | 0 | 79.5784 | 20.4216 | 0 | 79.5784 | 20.4216 | 0
22 | 16 | January | 3.6 | 4.4321 | 75.65 | 18.522 | 94.172 | 0 | 94.172 | 0 | 0 | 80.3317 | 19.6683 | 0 | 80.3317 | 19.6683 | 0
22 | 17 | January | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 18 | January | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 19 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
22 | 20 | January | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
22 | 21 | January | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
22 | 22 | January | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
22 | 23 | January | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
22 | 24 | January | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
23 | 1 | January | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
23 | 2 | January | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
23 | 3 | January | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
23 | 4 | January | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
23 | 5 | January | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
23 | 6 | January | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
23 | 7 | January | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
23 | 8 | January | 11.8 | 14.5275 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
23 | 9 | January | 12.3 | 15.1431 | 1700 | 25.137 | 1725.137 | 0 | 1725.137 | 0 | 0 | 98.5429 | 1.4571 | 0 | 98.5429 | 1.4571 | 0
23 | 10 | January | 12.3 | 15.1431 | 1700 | 224.7401 | 1924.7401 | 0 | 1924.7401 | 0 | 0 | 88.3236 | 11.6764 | 0 | 88.3236 | 11.6764 | 0
23 | 11 | January | 11.3 | 13.9119 | 1700 | 427.768 | 2127.768 | 1 | 2000 | 127.768 | 6.3884 | 79.8959 | 15 | 29.8685 | 78.6116 | 20.1041 | 7.5158
23 | 12 | January | 12.9 | 15.8818 | 1700 | 701.7412 | 2401.7412 | 1 | 2000 | 401.7412 | 20.0871 | 70.782 | 15 | 57.2492 | 64.9129 | 29.218 | 23.6318
23 | 13 | January | 12.9 | 15.8818 | 1700 | 780.9753 | 2480.9753 | 1 | 2000 | 480.9753 | 24.0488 | 68.5214 | 15 | 61.5865 | 60.9512 | 31.4786 | 28.2927
23 | 14 | January | 12.9 | 15.8818 | 1700 | 635.3375 | 2335.3375 | 1 | 2000 | 335.3375 | 16.7669 | 72.7946 | 15 | 52.781 | 68.2331 | 27.2054 | 19.7257
23 | 15 | January | 14.4 | 17.7285 | 1700 | 183.7927 | 1883.7927 | 0 | 1883.7927 | 0 | 0 | 90.2435 | 9.7565 | 0 | 90.2435 | 9.7565 | 0
23 | 16 | January | 12.9 | 15.8818 | 1700 | 37.044 | 1737.044 | 0 | 1737.044 | 0 | 0 | 97.8674 | 2.1326 | 0 | 97.8674 | 2.1326 | 0
23 | 17 | January | 11.8 | 14.5275 | 1700 | 1.323 | 1701.323 | 0 | 1701.323 | 0 | 0 | 99.9222 | 0.077763 | 0 | 99.9222 | 0.077763 | 0
23 | 18 | January | 13.9 | 17.1129 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
23 | 19 | January | 11.8 | 14.5275 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
23 | 20 | January | 13.9 | 17.1129 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
23 | 21 | January | 12.9 | 15.8818 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
23 | 22 | January | 11.8 | 14.5275 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
23 | 23 | January | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
23 | 24 | January | 11.8 | 14.5275 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
24 | 1 | January | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
24 | 2 | January | 12.9 | 15.8818 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
24 | 3 | January | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
24 | 4 | January | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
24 | 5 | January | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
24 | 6 | January | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
24 | 7 | January | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
24 | 8 | January | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
24 | 9 | January | 6.2 | 7.6331 | 625.6 | 108.4807 | 734.0807 | 0 | 734.0807 | 0 | 0 | 85.2222 | 14.7778 | 0 | 85.2222 | 14.7778 | 0
24 | 10 | January | 7.2 | 8.8642 | 908.65 | 230.4336 | 1139.0836 | 0 | 1139.0836 | 0 | 0 | 79.7703 | 20.2297 | 0 | 79.7703 | 20.2297 | 0
24 | 11 | January | 9.8 | 12.0652 | 1683.85 | 183.1527 | 1867.0027 | 0 | 1867.0027 | 0 | 0 | 90.19 | 9.81 | 0 | 90.19 | 9.81 | 0
24 | 12 | January | 9.3 | 11.4496 | 1598.85 | 232.6083 | 1831.4583 | 0 | 1831.4583 | 0 | 0 | 87.2993 | 12.7007 | 0 | 87.2993 | 12.7007 | 0
24 | 13 | January | 9.3 | 11.4496 | 1598.85 | 234.1863 | 1833.0363 | 0 | 1833.0363 | 0 | 0 | 87.2241 | 12.7759 | 0 | 87.2241 | 12.7759 | 0
24 | 14 | January | 9.8 | 12.0652 | 1683.85 | 193.721 | 1877.571 | 0 | 1877.571 | 0 | 0 | 89.6824 | 10.3176 | 0 | 89.6824 | 10.3176 | 0
24 | 15 | January | 7.7 | 9.4798 | 1059.95 | 64.827 | 1124.777 | 0 | 1124.777 | 0 | 0 | 94.2365 | 5.7635 | 0 | 94.2365 | 5.7635 | 0
24 | 16 | January | 6.7 | 8.2487 | 761.6 | 21.168 | 782.768 | 0 | 782.768 | 0 | 0 | 97.2958 | 2.7042 | 0 | 97.2958 | 2.7042 | 0
24 | 17 | January | 4.6 | 5.6633 | 237.15 | 1.323 | 238.473 | 0 | 238.473 | 0 | 0 | 99.4452 | 0.55478 | 0 | 99.4452 | 0.55478 | 0
24 | 18 | January | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
24 | 19 | January | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
24 | 20 | January | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
24 | 21 | January | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
24 | 22 | January | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 23 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
24 | 24 | January | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 1 | January | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 2 | January | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 3 | January | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 4 | January | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 5 | January | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 6 | January | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 7 | January | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 8 | January | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 9 | January | 0 | 0 | 0 | 27.783 | 27.783 | 0 | 27.783 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
25 | 10 | January | 0 | 0 | 0 | 59.535 | 59.535 | 0 | 59.535 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
25 | 11 | January | 0 | 0 | 0 | 97.902 | 97.902 | 0 | 97.902 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
25 | 12 | January | 0 | 0 | 0 | 119.07 | 119.07 | 0 | 119.07 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
25 | 13 | January | 0 | 0 | 0 | 121.716 | 121.716 | 0 | 121.716 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
25 | 14 | January | 0 | 0 | 0 | 103.194 | 103.194 | 0 | 103.194 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
25 | 15 | January | 3.1 | 3.8165 | 0 | 67.473 | 67.473 | 0 | 67.473 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
25 | 16 | January | 4.6 | 5.6633 | 237.15 | 22.491 | 259.641 | 0 | 259.641 | 0 | 0 | 91.3377 | 8.6623 | 0 | 91.3377 | 8.6623 | 0
25 | 17 | January | 3.1 | 3.8165 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
25 | 18 | January | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
25 | 19 | January | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
25 | 20 | January | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
25 | 21 | January | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
25 | 22 | January | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
25 | 23 | January | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
25 | 24 | January | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
26 | 1 | January | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
26 | 2 | January | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
26 | 3 | January | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
26 | 4 | January | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
26 | 5 | January | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
26 | 6 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
26 | 7 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
26 | 8 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
26 | 9 | January | 6.7 | 8.2487 | 761.6 | 18.522 | 780.122 | 0 | 780.122 | 0 | 0 | 97.6258 | 2.3742 | 0 | 97.6258 | 2.3742 | 0
26 | 10 | January | 9.8 | 12.0652 | 1683.85 | 60.858 | 1744.708 | 0 | 1744.708 | 0 | 0 | 96.5119 | 3.4881 | 0 | 96.5119 | 3.4881 | 0
26 | 11 | January | 13.4 | 16.4973 | 1700 | 99.225 | 1799.225 | 0 | 1799.225 | 0 | 0 | 94.4851 | 5.5149 | 0 | 94.4851 | 5.5149 | 0
26 | 12 | January | 18 | 22.1606 | 1700 | 121.716 | 1821.716 | 0 | 1821.716 | 0 | 0 | 93.3186 | 6.6814 | 0 | 93.3186 | 6.6814 | 0
26 | 13 | January | 15.4 | 18.9596 | 1700 | 124.362 | 1824.362 | 0 | 1824.362 | 0 | 0 | 93.1833 | 6.8167 | 0 | 93.1833 | 6.8167 | 0
26 | 14 | January | 13.4 | 16.4973 | 1700 | 105.84 | 1805.84 | 0 | 1805.84 | 0 | 0 | 94.139 | 5.861 | 0 | 94.139 | 5.861 | 0
26 | 15 | January | 11.8 | 14.5275 | 1700 | 118.4636 | 1818.4636 | 0 | 1818.4636 | 0 | 0 | 93.4855 | 6.5145 | 0 | 93.4855 | 6.5145 | 0
26 | 16 | January | 15.4 | 18.9596 | 1700 | 39.69 | 1739.69 | 0 | 1739.69 | 0 | 0 | 97.7186 | 2.2814 | 0 | 97.7186 | 2.2814 | 0
26 | 17 | January | 9.8 | 12.0652 | 1683.85 | 2.646 | 1686.496 | 0 | 1686.496 | 0 | 0 | 99.8431 | 0.15689 | 0 | 99.8431 | 0.15689 | 0
26 | 18 | January | 11.8 | 14.5275 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
26 | 19 | January | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
26 | 20 | January | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
26 | 21 | January | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
26 | 22 | January | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
26 | 23 | January | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
26 | 24 | January | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
27 | 1 | January | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
27 | 2 | January | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
27 | 3 | January | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
27 | 4 | January | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
27 | 5 | January | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
27 | 6 | January | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
27 | 7 | January | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
27 | 8 | January | 3.1 | 3.8165 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
27 | 9 | January | 3.1 | 3.8165 | 0 | 18.522 | 18.522 | 0 | 18.522 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
27 | 10 | January | 4.1 | 5.0477 | 173.4 | 63.504 | 236.904 | 0 | 236.904 | 0 | 0 | 73.1942 | 26.8058 | 0 | 73.1942 | 26.8058 | 0
27 | 11 | January | 4.1 | 5.0477 | 173.4 | 101.871 | 275.271 | 0 | 275.271 | 0 | 0 | 62.9925 | 37.0075 | 0 | 62.9925 | 37.0075 | 0
27 | 12 | January | 3.1 | 3.8165 | 0 | 124.362 | 124.362 | 0 | 124.362 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
27 | 13 | January | 3.6 | 4.4321 | 75.65 | 127.008 | 202.658 | 0 | 202.658 | 0 | 0 | 37.3289 | 62.6711 | 0 | 37.3289 | 62.6711 | 0
27 | 14 | January | 4.6 | 5.6633 | 237.15 | 108.486 | 345.636 | 0 | 345.636 | 0 | 0 | 68.6126 | 31.3874 | 0 | 68.6126 | 31.3874 | 0
27 | 15 | January | 6.2 | 7.6331 | 625.6 | 71.442 | 697.042 | 0 | 697.042 | 0 | 0 | 89.7507 | 10.2493 | 0 | 89.7507 | 10.2493 | 0
27 | 16 | January | 7.7 | 9.4798 | 1059.95 | 26.46 | 1086.41 | 0 | 1086.41 | 0 | 0 | 97.5645 | 2.4355 | 0 | 97.5645 | 2.4355 | 0
27 | 17 | January | 11.8 | 14.5275 | 1700 | 1.323 | 1701.323 | 0 | 1701.323 | 0 | 0 | 99.9222 | 0.077763 | 0 | 99.9222 | 0.077763 | 0
27 | 18 | January | 12.3 | 15.1431 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
27 | 19 | January | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
27 | 20 | January | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
27 | 21 | January | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
27 | 22 | January | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
27 | 23 | January | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
27 | 24 | January | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
28 | 1 | January | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
28 | 2 | January | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
28 | 3 | January | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
28 | 4 | January | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
28 | 5 | January | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
28 | 6 | January | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
28 | 7 | January | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
28 | 8 | January | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
28 | 9 | January | 8.7 | 10.711 | 1490.05 | 31.752 | 1521.802 | 0 | 1521.802 | 0 | 0 | 97.9135 | 2.0865 | 0 | 97.9135 | 2.0865 | 0
28 | 10 | January | 7.2 | 8.8642 | 908.65 | 393.1925 | 1301.8425 | 0 | 1301.8425 | 0 | 0 | 69.7972 | 30.2028 | 0 | 69.7972 | 30.2028 | 0
28 | 11 | January | 9.3 | 11.4496 | 1598.85 | 722.6679 | 2321.5179 | 1 | 2000 | 321.5179 | 16.0759 | 68.8709 | 20.0575 | 44.4904 | 63.8666 | 31.1291 | 20.1093
28 | 12 | January | 11.3 | 13.9119 | 1700 | 811.3595 | 2511.3595 | 1 | 2000 | 511.3595 | 25.568 | 67.6924 | 15 | 63.025 | 59.432 | 32.3076 | 30.08
28 | 13 | January | 9.3 | 11.4496 | 1598.85 | 794.0003 | 2392.8503 | 1 | 2000 | 392.8503 | 19.6425 | 66.8178 | 20.0575 | 49.4774 | 60.3 | 33.1822 | 24.5708
28 | 14 | January | 8.2 | 10.0954 | 1359.15 | 210.1152 | 1569.2652 | 0 | 1569.2652 | 0 | 0 | 86.6106 | 13.3894 | 0 | 86.6106 | 13.3894 | 0
28 | 15 | January | 10.8 | 13.2964 | 1698.3 | 126.6537 | 1824.9537 | 0 | 1824.9537 | 0 | 0 | 93.0599 | 6.9401 | 0 | 93.0599 | 6.9401 | 0
28 | 16 | January | 7.2 | 8.8642 | 908.65 | 43.659 | 952.309 | 0 | 952.309 | 0 | 0 | 95.4155 | 4.5845 | 0 | 95.4155 | 4.5845 | 0
28 | 17 | January | 6.2 | 7.6331 | 625.6 | 2.646 | 628.246 | 0 | 628.246 | 0 | 0 | 99.5788 | 0.42117 | 0 | 99.5788 | 0.42117 | 0
28 | 18 | January | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
28 | 19 | January | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
28 | 20 | January | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
28 | 21 | January | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
28 | 22 | January | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
28 | 23 | January | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
28 | 24 | January | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
29 | 1 | January | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
29 | 2 | January | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
29 | 3 | January | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
29 | 4 | January | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
29 | 5 | January | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
29 | 6 | January | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
29 | 7 | January | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
29 | 8 | January | 6.2 | 7.6331 | 625.6 | 1.323 | 626.923 | 0 | 626.923 | 0 | 0 | 99.789 | 0.21103 | 0 | 99.789 | 0.21103 | 0
29 | 9 | January | 5.1 | 6.2788 | 312.8 | 33.075 | 345.875 | 0 | 345.875 | 0 | 0 | 90.4373 | 9.5627 | 0 | 90.4373 | 9.5627 | 0
29 | 10 | January | 4.1 | 5.0477 | 173.4 | 115.811 | 289.211 | 0 | 289.211 | 0 | 0 | 59.9562 | 40.0438 | 0 | 59.9562 | 40.0438 | 0
29 | 11 | January | 2.1 | 2.5854 | 0 | 213.2176 | 213.2176 | 0 | 213.2176 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
29 | 12 | January | 3.1 | 3.8165 | 0 | 240.2599 | 240.2599 | 0 | 240.2599 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
29 | 13 | January | 3.1 | 3.8165 | 0 | 129.654 | 129.654 | 0 | 129.654 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
29 | 14 | January | 2.6 | 3.201 | 0 | 208.1476 | 208.1476 | 0 | 208.1476 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
29 | 15 | January | 4.1 | 5.0477 | 173.4 | 129.3928 | 302.7928 | 0 | 302.7928 | 0 | 0 | 57.2669 | 42.7331 | 0 | 57.2669 | 42.7331 | 0
29 | 16 | January | 3.6 | 4.4321 | 75.65 | 46.305 | 121.955 | 0 | 121.955 | 0 | 0 | 62.0311 | 37.9689 | 0 | 62.0311 | 37.9689 | 0
29 | 17 | January | 3.6 | 4.4321 | 75.65 | 3.969 | 79.619 | 0 | 79.619 | 0 | 0 | 95.015 | 4.985 | 0 | 95.015 | 4.985 | 0
29 | 18 | January | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
29 | 19 | January | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
29 | 20 | January | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
29 | 21 | January | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
29 | 22 | January | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
29 | 23 | January | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
29 | 24 | January | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
30 | 1 | January | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
30 | 2 | January | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
30 | 3 | January | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
30 | 4 | January | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
30 | 5 | January | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
30 | 6 | January | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
30 | 7 | January | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
30 | 8 | January | 5.1 | 6.2788 | 312.8 | 2.646 | 315.446 | 0 | 315.446 | 0 | 0 | 99.1612 | 0.83881 | 0 | 99.1612 | 0.83881 | 0
30 | 9 | January | 5.1 | 6.2788 | 312.8 | 147.1289 | 459.9289 | 0 | 459.9289 | 0 | 0 | 68.0105 | 31.9895 | 0 | 68.0105 | 31.9895 | 0
30 | 10 | January | 6.7 | 8.2487 | 761.6 | 447.0603 | 1208.6603 | 0 | 1208.6603 | 0 | 0 | 63.0119 | 36.9881 | 0 | 63.0119 | 36.9881 | 0
30 | 11 | January | 5.1 | 6.2788 | 312.8 | 472.7554 | 785.5554 | 0 | 785.5554 | 0 | 0 | 39.819 | 60.181 | 0 | 39.819 | 60.181 | 0
30 | 12 | January | 5.1 | 6.2788 | 312.8 | 776.5099 | 1089.3099 | 0 | 1089.3099 | 0 | 0 | 28.7154 | 71.2846 | 0 | 28.7154 | 71.2846 | 0
30 | 13 | January | 6.2 | 7.6331 | 625.6 | 855.8381 | 1481.4381 | 0 | 1481.4381 | 0 | 0 | 42.2292 | 57.7708 | 0 | 42.2292 | 57.7708 | 0
30 | 14 | January | 6.7 | 8.2487 | 761.6 | 715.7963 | 1477.3963 | 0 | 1477.3963 | 0 | 0 | 51.5502 | 48.4498 | 0 | 51.5502 | 48.4498 | 0
30 | 15 | January | 5.7 | 7.0175 | 504.9 | 479.5278 | 984.4278 | 0 | 984.4278 | 0 | 0 | 51.2887 | 48.7113 | 0 | 51.2887 | 48.7113 | 0
30 | 16 | January | 4.1 | 5.0477 | 173.4 | 161.1193 | 334.5193 | 0 | 334.5193 | 0 | 0 | 51.8356 | 48.1644 | 0 | 51.8356 | 48.1644 | 0
30 | 17 | January | 3.6 | 4.4321 | 75.65 | 6.615 | 82.265 | 0 | 82.265 | 0 | 0 | 91.9589 | 8.0411 | 0 | 91.9589 | 8.0411 | 0
30 | 18 | January | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 19 | January | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 20 | January | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 21 | January | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 22 | January | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 23 | January | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 24 | January | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 1 | January | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
31 | 2 | January | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
31 | 3 | January | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
31 | 4 | January | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
31 | 5 | January | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
31 | 6 | January | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
31 | 7 | January | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
31 | 8 | January | 13.9 | 17.1129 | 1700 | 1.323 | 1701.323 | 0 | 1701.323 | 0 | 0 | 99.9222 | 0.077763 | 0 | 99.9222 | 0.077763 | 0
31 | 9 | January | 11.3 | 13.9119 | 1700 | 23.814 | 1723.814 | 0 | 1723.814 | 0 | 0 | 98.6185 | 1.3815 | 0 | 98.6185 | 1.3815 | 0
31 | 10 | January | 12.9 | 15.8818 | 1700 | 70.119 | 1770.119 | 0 | 1770.119 | 0 | 0 | 96.0387 | 3.9613 | 0 | 96.0387 | 3.9613 | 0
31 | 11 | January | 10.8 | 13.2964 | 1698.3 | 109.809 | 1808.109 | 0 | 1808.109 | 0 | 0 | 93.9269 | 6.0731 | 0 | 93.9269 | 6.0731 | 0
31 | 12 | January | 12.9 | 15.8818 | 1700 | 132.3 | 1832.3 | 0 | 1832.3 | 0 | 0 | 92.7796 | 7.2204 | 0 | 92.7796 | 7.2204 | 0
31 | 13 | January | 9.8 | 12.0652 | 1683.85 | 133.623 | 1817.473 | 0 | 1817.473 | 0 | 0 | 92.6479 | 7.3521 | 0 | 92.6479 | 7.3521 | 0
31 | 14 | January | 10.3 | 12.6808 | 1694.9 | 115.101 | 1810.001 | 0 | 1810.001 | 0 | 0 | 93.6408 | 6.3592 | 0 | 93.6408 | 6.3592 | 0
31 | 15 | January | 10.3 | 12.6808 | 1694.9 | 79.38 | 1774.28 | 0 | 1774.28 | 0 | 0 | 95.5261 | 4.4739 | 0 | 95.5261 | 4.4739 | 0
31 | 16 | January | 11.3 | 13.9119 | 1700 | 33.075 | 1733.075 | 0 | 1733.075 | 0 | 0 | 98.0915 | 1.9085 | 0 | 98.0915 | 1.9085 | 0
31 | 17 | January | 9.8 | 12.0652 | 1683.85 | 2.646 | 1686.496 | 0 | 1686.496 | 0 | 0 | 99.8431 | 0.15689 | 0 | 99.8431 | 0.15689 | 0
31 | 18 | January | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
31 | 19 | January | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
31 | 20 | January | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
31 | 21 | January | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
31 | 22 | January | 11.8 | 14.5275 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
31 | 23 | January | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
31 | 24 | January | 12.3 | 15.1431 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
32 | 1 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 2 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 3 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 4 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
32 | 5 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
32 | 6 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 7 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
32 | 8 | February | 3 | 3.6934 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
32 | 9 | February | 3 | 3.6934 | 0 | 25.137 | 25.137 | 0 | 25.137 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
32 | 10 | February | 3 | 3.6934 | 0 | 72.765 | 72.765 | 0 | 72.765 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
32 | 11 | February | 3 | 3.6934 | 0 | 112.455 | 112.455 | 0 | 112.455 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
32 | 12 | February | 3 | 3.6934 | 0 | 276.2066 | 276.2066 | 0 | 276.2066 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
32 | 13 | February | 3 | 3.6934 | 0 | 258.3111 | 258.3111 | 0 | 258.3111 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
32 | 14 | February | 3 | 3.6934 | 0 | 119.07 | 119.07 | 0 | 119.07 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
32 | 15 | February | 2 | 2.4623 | 0 | 83.349 | 83.349 | 0 | 83.349 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
32 | 16 | February | 2 | 2.4623 | 0 | 35.721 | 35.721 | 0 | 35.721 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
32 | 17 | February | 2 | 2.4623 | 0 | 3.969 | 3.969 | 0 | 3.969 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
32 | 18 | February | 2 | 2.4623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 19 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 20 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 21 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 22 | February | 2 | 2.4623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 23 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 24 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 1 | February | 2 | 2.4623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 2 | February | 2 | 2.4623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 3 | February | 2 | 2.4623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 4 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 5 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 6 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
33 | 7 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 8 | February | 3 | 3.6934 | 0 | 3.969 | 3.969 | 0 | 3.969 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
33 | 9 | February | 5 | 6.1557 | 312.8 | 27.783 | 340.583 | 0 | 340.583 | 0 | 0 | 91.8425 | 8.1575 | 0 | 91.8425 | 8.1575 | 0
33 | 10 | February | 4 | 4.9246 | 120.7 | 151.9832 | 272.6832 | 0 | 272.6832 | 0 | 0 | 44.2638 | 55.7362 | 0 | 44.2638 | 55.7362 | 0
33 | 11 | February | 4 | 4.9246 | 120.7 | 222.4699 | 343.1699 | 0 | 343.1699 | 0 | 0 | 35.1721 | 64.8279 | 0 | 35.1721 | 64.8279 | 0
33 | 12 | February | 6 | 7.3869 | 504.9 | 429.5015 | 934.4015 | 0 | 934.4015 | 0 | 0 | 54.0346 | 45.9654 | 0 | 54.0346 | 45.9654 | 0
33 | 13 | February | 6 | 7.3869 | 504.9 | 393.3754 | 898.2754 | 0 | 898.2754 | 0 | 0 | 56.2077 | 43.7923 | 0 | 56.2077 | 43.7923 | 0
33 | 14 | February | 5 | 6.1557 | 312.8 | 371.6789 | 684.4789 | 0 | 684.4789 | 0 | 0 | 45.699 | 54.301 | 0 | 45.699 | 54.301 | 0
33 | 15 | February | 5 | 6.1557 | 312.8 | 156.4628 | 469.2628 | 0 | 469.2628 | 0 | 0 | 66.6577 | 33.3423 | 0 | 66.6577 | 33.3423 | 0
33 | 16 | February | 6 | 7.3869 | 504.9 | 61.4165 | 566.3165 | 0 | 566.3165 | 0 | 0 | 89.1551 | 10.8449 | 0 | 89.1551 | 10.8449 | 0
33 | 17 | February | 6 | 7.3869 | 504.9 | 6.615 | 511.515 | 0 | 511.515 | 0 | 0 | 98.7068 | 1.2932 | 0 | 98.7068 | 1.2932 | 0
33 | 18 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
33 | 19 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
33 | 20 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
33 | 21 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
33 | 22 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
33 | 23 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
33 | 24 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
34 | 1 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
34 | 2 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
34 | 3 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
34 | 4 | February | 8 | 9.8492 | 1213.8 | 0 | 1213.8 | 0 | 1213.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
34 | 5 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
34 | 6 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
34 | 7 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
34 | 8 | February | 6 | 7.3869 | 504.9 | 3.969 | 508.869 | 0 | 508.869 | 0 | 0 | 99.22 | 0.77996 | 0 | 99.22 | 0.77996 | 0
34 | 9 | February | 5 | 6.1557 | 312.8 | 46.305 | 359.105 | 0 | 359.105 | 0 | 0 | 87.1054 | 12.8946 | 0 | 87.1054 | 12.8946 | 0
34 | 10 | February | 6 | 7.3869 | 504.9 | 146.5898 | 651.4898 | 0 | 651.4898 | 0 | 0 | 77.4993 | 22.5007 | 0 | 77.4993 | 22.5007 | 0
34 | 11 | February | 6 | 7.3869 | 504.9 | 235.3673 | 740.2673 | 0 | 740.2673 | 0 | 0 | 68.2051 | 31.7949 | 0 | 68.2051 | 31.7949 | 0
34 | 12 | February | 7 | 8.618 | 908.65 | 263.8061 | 1172.4561 | 0 | 1172.4561 | 0 | 0 | 77.4997 | 22.5003 | 0 | 77.4997 | 22.5003 | 0
34 | 13 | February | 6 | 7.3869 | 504.9 | 265.9968 | 770.8968 | 0 | 770.8968 | 0 | 0 | 65.4951 | 34.5049 | 0 | 65.4951 | 34.5049 | 0
34 | 14 | February | 6 | 7.3869 | 504.9 | 233.7323 | 738.6323 | 0 | 738.6323 | 0 | 0 | 68.3561 | 31.6439 | 0 | 68.3561 | 31.6439 | 0
34 | 15 | February | 6 | 7.3869 | 504.9 | 160.975 | 665.875 | 0 | 665.875 | 0 | 0 | 75.825 | 24.175 | 0 | 75.825 | 24.175 | 0
34 | 16 | February | 5 | 6.1557 | 312.8 | 64.6304 | 377.4304 | 0 | 377.4304 | 0 | 0 | 82.8762 | 17.1238 | 0 | 82.8762 | 17.1238 | 0
34 | 17 | February | 5 | 6.1557 | 312.8 | 7.938 | 320.738 | 0 | 320.738 | 0 | 0 | 97.5251 | 2.4749 | 0 | 97.5251 | 2.4749 | 0
34 | 18 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
34 | 19 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
34 | 20 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
34 | 21 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
34 | 22 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
34 | 23 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
34 | 24 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
35 | 1 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
35 | 2 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
35 | 3 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
35 | 4 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
35 | 5 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
35 | 6 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
35 | 7 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
35 | 8 | February | 4 | 4.9246 | 120.7 | 2.646 | 123.346 | 0 | 123.346 | 0 | 0 | 97.8548 | 2.1452 | 0 | 97.8548 | 2.1452 | 0
35 | 9 | February | 5 | 6.1557 | 312.8 | 48.951 | 361.751 | 0 | 361.751 | 0 | 0 | 86.4683 | 13.5317 | 0 | 86.4683 | 13.5317 | 0
35 | 10 | February | 5 | 6.1557 | 312.8 | 149.369 | 462.169 | 0 | 462.169 | 0 | 0 | 67.6809 | 32.3191 | 0 | 67.6809 | 32.3191 | 0
35 | 11 | February | 6 | 7.3869 | 504.9 | 378.8864 | 883.7864 | 0 | 883.7864 | 0 | 0 | 57.1292 | 42.8708 | 0 | 57.1292 | 42.8708 | 0
35 | 12 | February | 6 | 7.3869 | 504.9 | 834.3632 | 1339.2632 | 0 | 1339.2632 | 0 | 0 | 37.6998 | 62.3002 | 0 | 37.6998 | 62.3002 | 0
35 | 13 | February | 6 | 7.3869 | 504.9 | 930.8505 | 1435.7505 | 0 | 1435.7505 | 0 | 0 | 35.1663 | 64.8337 | 0 | 35.1663 | 64.8337 | 0
35 | 14 | February | 5 | 6.1557 | 312.8 | 763.6465 | 1076.4465 | 0 | 1076.4465 | 0 | 0 | 29.0586 | 70.9414 | 0 | 29.0586 | 70.9414 | 0
35 | 15 | February | 5 | 6.1557 | 312.8 | 532.448 | 845.248 | 0 | 845.248 | 0 | 0 | 37.0069 | 62.9931 | 0 | 37.0069 | 62.9931 | 0
35 | 16 | February | 5 | 6.1557 | 312.8 | 198.2677 | 511.0677 | 0 | 511.0677 | 0 | 0 | 61.2052 | 38.7948 | 0 | 61.2052 | 38.7948 | 0
35 | 17 | February | 4 | 4.9246 | 120.7 | 13.23 | 133.93 | 0 | 133.93 | 0 | 0 | 90.1217 | 9.8783 | 0 | 90.1217 | 9.8783 | 0
35 | 18 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
35 | 19 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
35 | 20 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
35 | 21 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
35 | 22 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
35 | 23 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
35 | 24 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
36 | 1 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
36 | 2 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
36 | 3 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
36 | 4 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
36 | 5 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
36 | 6 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
36 | 7 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
36 | 8 | February | 6 | 7.3869 | 504.9 | 3.969 | 508.869 | 0 | 508.869 | 0 | 0 | 99.22 | 0.77996 | 0 | 99.22 | 0.77996 | 0
36 | 9 | February | 5 | 6.1557 | 312.8 | 50.274 | 363.074 | 0 | 363.074 | 0 | 0 | 86.1532 | 13.8468 | 0 | 86.1532 | 13.8468 | 0
36 | 10 | February | 6 | 7.3869 | 504.9 | 152.1511 | 657.0511 | 0 | 657.0511 | 0 | 0 | 76.8433 | 23.1567 | 0 | 76.8433 | 23.1567 | 0
36 | 11 | February | 6 | 7.3869 | 504.9 | 233.5833 | 738.4833 | 0 | 738.4833 | 0 | 0 | 68.3699 | 31.6301 | 0 | 68.3699 | 31.6301 | 0
36 | 12 | February | 6 | 7.3869 | 504.9 | 460.6148 | 965.5148 | 0 | 965.5148 | 0 | 0 | 52.2933 | 47.7067 | 0 | 52.2933 | 47.7067 | 0
36 | 13 | February | 6 | 7.3869 | 504.9 | 291.0789 | 795.9789 | 0 | 795.9789 | 0 | 0 | 63.4313 | 36.5687 | 0 | 63.4313 | 36.5687 | 0
36 | 14 | February | 5 | 6.1557 | 312.8 | 239.8086 | 552.6086 | 0 | 552.6086 | 0 | 0 | 56.6043 | 43.3957 | 0 | 56.6043 | 43.3957 | 0
36 | 15 | February | 5 | 6.1557 | 312.8 | 166.6329 | 479.4329 | 0 | 479.4329 | 0 | 0 | 65.2437 | 34.7563 | 0 | 65.2437 | 34.7563 | 0
36 | 16 | February | 5 | 6.1557 | 312.8 | 70.5134 | 383.3134 | 0 | 383.3134 | 0 | 0 | 81.6042 | 18.3958 | 0 | 81.6042 | 18.3958 | 0
36 | 17 | February | 5 | 6.1557 | 312.8 | 10.584 | 323.384 | 0 | 323.384 | 0 | 0 | 96.7271 | 3.2729 | 0 | 96.7271 | 3.2729 | 0
36 | 18 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
36 | 19 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
36 | 20 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
36 | 21 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
36 | 22 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
36 | 23 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
36 | 24 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 1 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
37 | 2 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
37 | 3 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
37 | 4 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
37 | 5 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
37 | 6 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
37 | 7 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 8 | February | 5 | 6.1557 | 312.8 | 7.938 | 320.738 | 0 | 320.738 | 0 | 0 | 97.5251 | 2.4749 | 0 | 97.5251 | 2.4749 | 0
37 | 9 | February | 4 | 4.9246 | 120.7 | 238.7877 | 359.4877 | 0 | 359.4877 | 0 | 0 | 33.5756 | 66.4244 | 0 | 33.5756 | 66.4244 | 0
37 | 10 | February | 5 | 6.1557 | 312.8 | 614.5698 | 927.3698 | 0 | 927.3698 | 0 | 0 | 33.7298 | 66.2702 | 0 | 33.7298 | 66.2702 | 0
37 | 11 | February | 5 | 6.1557 | 312.8 | 701.3685 | 1014.1685 | 0 | 1014.1685 | 0 | 0 | 30.843 | 69.157 | 0 | 30.843 | 69.157 | 0
37 | 12 | February | 6 | 7.3869 | 504.9 | 465.568 | 970.468 | 0 | 970.468 | 0 | 0 | 52.0264 | 47.9736 | 0 | 52.0264 | 47.9736 | 0
37 | 13 | February | 6 | 7.3869 | 504.9 | 295.4361 | 800.3361 | 0 | 800.3361 | 0 | 0 | 63.086 | 36.914 | 0 | 63.086 | 36.914 | 0
37 | 14 | February | 6 | 7.3869 | 504.9 | 242.7162 | 747.6162 | 0 | 747.6162 | 0 | 0 | 67.5347 | 32.4653 | 0 | 67.5347 | 32.4653 | 0
37 | 15 | February | 6 | 7.3869 | 504.9 | 170.3229 | 675.2229 | 0 | 675.2229 | 0 | 0 | 74.7753 | 25.2247 | 0 | 74.7753 | 25.2247 | 0
37 | 16 | February | 6 | 7.3869 | 504.9 | 73.7503 | 578.6503 | 0 | 578.6503 | 0 | 0 | 87.2548 | 12.7452 | 0 | 87.2548 | 12.7452 | 0
37 | 17 | February | 4 | 4.9246 | 120.7 | 10.584 | 131.284 | 0 | 131.284 | 0 | 0 | 91.9381 | 8.0619 | 0 | 91.9381 | 8.0619 | 0
37 | 18 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
37 | 19 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
37 | 20 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
37 | 21 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
37 | 22 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
37 | 23 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
37 | 24 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
38 | 1 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
38 | 2 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
38 | 3 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
38 | 4 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 5 | February | 2 | 2.4623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 6 | February | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 7 | February | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 8 | February | 1 | 1.2311 | 0 | 5.292 | 5.292 | 0 | 5.292 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
38 | 9 | February | 1 | 1.2311 | 0 | 56.889 | 56.889 | 0 | 56.889 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
38 | 10 | February | 0 | 0 | 0 | 172.357 | 172.357 | 0 | 172.357 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
38 | 11 | February | 1 | 1.2311 | 0 | 244.2329 | 244.2329 | 0 | 244.2329 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
38 | 12 | February | 4 | 4.9246 | 120.7 | 280.5952 | 401.2952 | 0 | 401.2952 | 0 | 0 | 30.0776 | 69.9224 | 0 | 30.0776 | 69.9224 | 0
38 | 13 | February | 4 | 4.9246 | 120.7 | 281.4485 | 402.1485 | 0 | 402.1485 | 0 | 0 | 30.0138 | 69.9862 | 0 | 30.0138 | 69.9862 | 0
38 | 14 | February | 3 | 3.6934 | 0 | 134.946 | 134.946 | 0 | 134.946 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
38 | 15 | February | 3 | 3.6934 | 0 | 96.579 | 96.579 | 0 | 96.579 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
38 | 16 | February | 3 | 3.6934 | 0 | 47.628 | 47.628 | 0 | 47.628 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
38 | 17 | February | 3 | 3.6934 | 0 | 7.938 | 7.938 | 0 | 7.938 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
38 | 18 | February | 2 | 2.4623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 19 | February | 2 | 2.4623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 20 | February | 2 | 2.4623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 21 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 22 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
38 | 23 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
38 | 24 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | 1 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
39 | 2 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
39 | 3 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
39 | 4 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | 5 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
39 | 6 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
39 | 7 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
39 | 8 | February | 5 | 6.1557 | 312.8 | 9.261 | 322.061 | 0 | 322.061 | 0 | 0 | 97.1245 | 2.8755 | 0 | 97.1245 | 2.8755 | 0
39 | 9 | February | 5 | 6.1557 | 312.8 | 61.1426 | 373.9426 | 0 | 373.9426 | 0 | 0 | 83.6492 | 16.3508 | 0 | 83.6492 | 16.3508 | 0
39 | 10 | February | 5 | 6.1557 | 312.8 | 463.6474 | 776.4474 | 0 | 776.4474 | 0 | 0 | 40.2861 | 59.7139 | 0 | 40.2861 | 59.7139 | 0
39 | 11 | February | 4 | 4.9246 | 120.7 | 726.8633 | 847.5633 | 0 | 847.5633 | 0 | 0 | 14.2408 | 85.7592 | 0 | 14.2408 | 85.7592 | 0
39 | 12 | February | 4 | 4.9246 | 120.7 | 945.8044 | 1066.5044 | 0 | 1066.5044 | 0 | 0 | 11.3173 | 88.6827 | 0 | 11.3173 | 88.6827 | 0
39 | 13 | February | 4 | 4.9246 | 120.7 | 657.7845 | 778.4845 | 0 | 778.4845 | 0 | 0 | 15.5045 | 84.4955 | 0 | 15.5045 | 84.4955 | 0
39 | 14 | February | 4 | 4.9246 | 120.7 | 261.5613 | 382.2613 | 0 | 382.2613 | 0 | 0 | 31.5753 | 68.4247 | 0 | 31.5753 | 68.4247 | 0
39 | 15 | February | 5 | 6.1557 | 312.8 | 187.3144 | 500.1144 | 0 | 500.1144 | 0 | 0 | 62.5457 | 37.4543 | 0 | 62.5457 | 37.4543 | 0
39 | 16 | February | 4 | 4.9246 | 120.7 | 50.274 | 170.974 | 0 | 170.974 | 0 | 0 | 70.5955 | 29.4045 | 0 | 70.5955 | 29.4045 | 0
39 | 17 | February | 4 | 4.9246 | 120.7 | 7.938 | 128.638 | 0 | 128.638 | 0 | 0 | 93.8292 | 6.1708 | 0 | 93.8292 | 6.1708 | 0
39 | 18 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
39 | 19 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
39 | 20 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
39 | 21 | February | 8 | 9.8492 | 1213.8 | 0 | 1213.8 | 0 | 1213.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
39 | 22 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
39 | 23 | February | 8 | 9.8492 | 1213.8 | 0 | 1213.8 | 0 | 1213.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
39 | 24 | February | 8 | 9.8492 | 1213.8 | 0 | 1213.8 | 0 | 1213.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
40 | 1 | February | 8 | 9.8492 | 1213.8 | 0 | 1213.8 | 0 | 1213.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
40 | 2 | February | 8 | 9.8492 | 1213.8 | 0 | 1213.8 | 0 | 1213.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
40 | 3 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
40 | 4 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
40 | 5 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
40 | 6 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
40 | 7 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
40 | 8 | February | 6 | 7.3869 | 504.9 | 6.615 | 511.515 | 0 | 511.515 | 0 | 0 | 98.7068 | 1.2932 | 0 | 98.7068 | 1.2932 | 0
40 | 9 | February | 6 | 7.3869 | 504.9 | 62.4743 | 567.3743 | 0 | 567.3743 | 0 | 0 | 88.9889 | 11.0111 | 0 | 88.9889 | 11.0111 | 0
40 | 10 | February | 7 | 8.618 | 908.65 | 180.1935 | 1088.8435 | 0 | 1088.8435 | 0 | 0 | 83.4509 | 16.5491 | 0 | 83.4509 | 16.5491 | 0
40 | 11 | February | 7 | 8.618 | 908.65 | 248.8487 | 1157.4987 | 0 | 1157.4987 | 0 | 0 | 78.5012 | 21.4988 | 0 | 78.5012 | 21.4988 | 0
40 | 12 | February | 6 | 7.3869 | 504.9 | 156.114 | 661.014 | 0 | 661.014 | 0 | 0 | 76.3826 | 23.6174 | 0 | 76.3826 | 23.6174 | 0
40 | 13 | February | 6 | 7.3869 | 504.9 | 158.76 | 663.66 | 0 | 663.66 | 0 | 0 | 76.0781 | 23.9219 | 0 | 76.0781 | 23.9219 | 0
40 | 14 | February | 5 | 6.1557 | 312.8 | 138.915 | 451.715 | 0 | 451.715 | 0 | 0 | 69.2472 | 30.7528 | 0 | 69.2472 | 30.7528 | 0
40 | 15 | February | 6 | 7.3869 | 504.9 | 303.2077 | 808.1077 | 0 | 808.1077 | 0 | 0 | 62.4793 | 37.5207 | 0 | 62.4793 | 37.5207 | 0
40 | 16 | February | 6 | 7.3869 | 504.9 | 126.4267 | 631.3267 | 0 | 631.3267 | 0 | 0 | 79.9744 | 20.0256 | 0 | 79.9744 | 20.0256 | 0
40 | 17 | February | 6 | 7.3869 | 504.9 | 22.491 | 527.391 | 0 | 527.391 | 0 | 0 | 95.7354 | 4.2646 | 0 | 95.7354 | 4.2646 | 0
40 | 18 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
40 | 19 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
40 | 20 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
40 | 21 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
40 | 22 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
40 | 23 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
40 | 24 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
41 | 1 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
41 | 2 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
41 | 3 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
41 | 4 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
41 | 5 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
41 | 6 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
41 | 7 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
41 | 8 | February | 5 | 6.1557 | 312.8 | 7.938 | 320.738 | 0 | 320.738 | 0 | 0 | 97.5251 | 2.4749 | 0 | 97.5251 | 2.4749 | 0
41 | 9 | February | 7 | 8.618 | 908.65 | 70.0043 | 978.6543 | 0 | 978.6543 | 0 | 0 | 92.8469 | 7.1531 | 0 | 92.8469 | 7.1531 | 0
41 | 10 | February | 5 | 6.1557 | 312.8 | 186.2271 | 499.0271 | 0 | 499.0271 | 0 | 0 | 62.682 | 37.318 | 0 | 62.682 | 37.318 | 0
41 | 11 | February | 5 | 6.1557 | 312.8 | 255.4785 | 568.2785 | 0 | 568.2785 | 0 | 0 | 55.0434 | 44.9566 | 0 | 55.0434 | 44.9566 | 0
41 | 12 | February | 5 | 6.1557 | 312.8 | 492.0024 | 804.8024 | 0 | 804.8024 | 0 | 0 | 38.8667 | 61.1333 | 0 | 38.8667 | 61.1333 | 0
41 | 13 | February | 4 | 4.9246 | 120.7 | 315.1386 | 435.8386 | 0 | 435.8386 | 0 | 0 | 27.6937 | 72.3063 | 0 | 27.6937 | 72.3063 | 0
41 | 14 | February | 5 | 6.1557 | 312.8 | 257.9019 | 570.7019 | 0 | 570.7019 | 0 | 0 | 54.8097 | 45.1903 | 0 | 54.8097 | 45.1903 | 0
41 | 15 | February | 5 | 6.1557 | 312.8 | 189.1457 | 501.9457 | 0 | 501.9457 | 0 | 0 | 62.3175 | 37.6825 | 0 | 62.3175 | 37.6825 | 0
41 | 16 | February | 5 | 6.1557 | 312.8 | 88.8392 | 401.6392 | 0 | 401.6392 | 0 | 0 | 77.8808 | 22.1192 | 0 | 77.8808 | 22.1192 | 0
41 | 17 | February | 4 | 4.9246 | 120.7 | 21.168 | 141.868 | 0 | 141.868 | 0 | 0 | 85.0791 | 14.9209 | 0 | 85.0791 | 14.9209 | 0
41 | 18 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | 19 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
41 | 20 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
41 | 21 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
41 | 22 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
41 | 23 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
41 | 24 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
42 | 1 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
42 | 2 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
42 | 3 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
42 | 4 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
42 | 5 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
42 | 6 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
42 | 7 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
42 | 8 | February | 5 | 6.1557 | 312.8 | 15.876 | 328.676 | 0 | 328.676 | 0 | 0 | 95.1697 | 4.8303 | 0 | 95.1697 | 4.8303 | 0
42 | 9 | February | 6 | 7.3869 | 504.9 | 75.1374 | 580.0374 | 0 | 580.0374 | 0 | 0 | 87.0461 | 12.9539 | 0 | 87.0461 | 12.9539 | 0
42 | 10 | February | 7 | 8.618 | 908.65 | 95.256 | 1003.906 | 0 | 1003.906 | 0 | 0 | 90.5115 | 9.4885 | 0 | 90.5115 | 9.4885 | 0
42 | 11 | February | 7 | 8.618 | 908.65 | 137.592 | 1046.242 | 0 | 1046.242 | 0 | 0 | 86.8489 | 13.1511 | 0 | 86.8489 | 13.1511 | 0
42 | 12 | February | 7 | 8.618 | 908.65 | 320.7437 | 1229.3937 | 0 | 1229.3937 | 0 | 0 | 73.9104 | 26.0896 | 0 | 73.9104 | 26.0896 | 0
42 | 13 | February | 7 | 8.618 | 908.65 | 298.282 | 1206.932 | 0 | 1206.932 | 0 | 0 | 75.2859 | 24.7141 | 0 | 75.2859 | 24.7141 | 0
42 | 14 | February | 7 | 8.618 | 908.65 | 262.112 | 1170.762 | 0 | 1170.762 | 0 | 0 | 77.6118 | 22.3882 | 0 | 77.6118 | 22.3882 | 0
42 | 15 | February | 6 | 7.3869 | 504.9 | 107.163 | 612.063 | 0 | 612.063 | 0 | 0 | 82.4915 | 17.5085 | 0 | 82.4915 | 17.5085 | 0
42 | 16 | February | 6 | 7.3869 | 504.9 | 55.566 | 560.466 | 0 | 560.466 | 0 | 0 | 90.0858 | 9.9142 | 0 | 90.0858 | 9.9142 | 0
42 | 17 | February | 6 | 7.3869 | 504.9 | 10.584 | 515.484 | 0 | 515.484 | 0 | 0 | 97.9468 | 2.0532 | 0 | 97.9468 | 2.0532 | 0
42 | 18 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
42 | 19 | February | 2 | 2.4623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | 20 | February | 2 | 2.4623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | 21 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | 22 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
42 | 23 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | 24 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | 1 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | 2 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | 3 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | 4 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | 5 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
43 | 6 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
43 | 7 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
43 | 8 | February | 5 | 6.1557 | 312.8 | 9.261 | 322.061 | 0 | 322.061 | 0 | 0 | 97.1245 | 2.8755 | 0 | 97.1245 | 2.8755 | 0
43 | 9 | February | 5 | 6.1557 | 312.8 | 81.942 | 394.742 | 0 | 394.742 | 0 | 0 | 79.2416 | 20.7584 | 0 | 79.2416 | 20.7584 | 0
43 | 10 | February | 7 | 8.618 | 908.65 | 196.5445 | 1105.1945 | 0 | 1105.1945 | 0 | 0 | 82.2163 | 17.7837 | 0 | 82.2163 | 17.7837 | 0
43 | 11 | February | 8 | 9.8492 | 1213.8 | 259.3426 | 1473.1426 | 0 | 1473.1426 | 0 | 0 | 82.3953 | 17.6047 | 0 | 82.3953 | 17.6047 | 0
43 | 12 | February | 7 | 8.618 | 908.65 | 301.698 | 1210.348 | 0 | 1210.348 | 0 | 0 | 75.0735 | 24.9265 | 0 | 75.0735 | 24.9265 | 0
43 | 13 | February | 10 | 12.3114 | 1683.85 | 305.0795 | 1988.9295 | 0 | 1988.9295 | 0 | 0 | 84.6611 | 15.3389 | 0 | 84.6611 | 15.3389 | 0
43 | 14 | February | 9 | 11.0803 | 1598.85 | 266.1049 | 1864.9549 | 0 | 1864.9549 | 0 | 0 | 85.7313 | 14.2687 | 0 | 85.7313 | 14.2687 | 0
43 | 15 | February | 10 | 12.3114 | 1683.85 | 197.9496 | 1881.7996 | 0 | 1881.7996 | 0 | 0 | 89.4808 | 10.5192 | 0 | 89.4808 | 10.5192 | 0
43 | 16 | February | 8 | 9.8492 | 1213.8 | 96.7253 | 1310.5253 | 0 | 1310.5253 | 0 | 0 | 92.6193 | 7.3807 | 0 | 92.6193 | 7.3807 | 0
43 | 17 | February | 8 | 9.8492 | 1213.8 | 18.522 | 1232.322 | 0 | 1232.322 | 0 | 0 | 98.497 | 1.503 | 0 | 98.497 | 1.503 | 0
43 | 18 | February | 9 | 11.0803 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
43 | 19 | February | 8 | 9.8492 | 1213.8 | 0 | 1213.8 | 0 | 1213.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
43 | 20 | February | 9 | 11.0803 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
43 | 21 | February | 9 | 11.0803 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
43 | 22 | February | 9 | 11.0803 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
43 | 23 | February | 8 | 9.8492 | 1213.8 | 0 | 1213.8 | 0 | 1213.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
43 | 24 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
44 | 1 | February | 8 | 9.8492 | 1213.8 | 0 | 1213.8 | 0 | 1213.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
44 | 2 | February | 8 | 9.8492 | 1213.8 | 0 | 1213.8 | 0 | 1213.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
44 | 3 | February | 8 | 9.8492 | 1213.8 | 0 | 1213.8 | 0 | 1213.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
44 | 4 | February | 9 | 11.0803 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
44 | 5 | February | 9 | 11.0803 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
44 | 6 | February | 9 | 11.0803 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
44 | 7 | February | 9 | 11.0803 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
44 | 8 | February | 7 | 8.618 | 908.65 | 10.584 | 919.234 | 0 | 919.234 | 0 | 0 | 98.8486 | 1.1514 | 0 | 98.8486 | 1.1514 | 0
44 | 9 | February | 6 | 7.3869 | 504.9 | 46.305 | 551.205 | 0 | 551.205 | 0 | 0 | 91.5993 | 8.4007 | 0 | 91.5993 | 8.4007 | 0
44 | 10 | February | 6 | 7.3869 | 504.9 | 99.225 | 604.125 | 0 | 604.125 | 0 | 0 | 83.5754 | 16.4246 | 0 | 83.5754 | 16.4246 | 0
44 | 11 | February | 6 | 7.3869 | 504.9 | 142.884 | 647.784 | 0 | 647.784 | 0 | 0 | 77.9426 | 22.0574 | 0 | 77.9426 | 22.0574 | 0
44 | 12 | February | 6 | 7.3869 | 504.9 | 166.698 | 671.598 | 0 | 671.598 | 0 | 0 | 75.1789 | 24.8211 | 0 | 75.1789 | 24.8211 | 0
44 | 13 | February | 4 | 4.9246 | 120.7 | 169.344 | 290.044 | 0 | 290.044 | 0 | 0 | 41.6144 | 58.3856 | 0 | 41.6144 | 58.3856 | 0
44 | 14 | February | 4 | 4.9246 | 120.7 | 150.822 | 271.522 | 0 | 271.522 | 0 | 0 | 44.4531 | 55.5469 | 0 | 44.4531 | 55.5469 | 0
44 | 15 | February | 4 | 4.9246 | 120.7 | 112.455 | 233.155 | 0 | 233.155 | 0 | 0 | 51.7681 | 48.2319 | 0 | 51.7681 | 48.2319 | 0
44 | 16 | February | 4 | 4.9246 | 120.7 | 60.858 | 181.558 | 0 | 181.558 | 0 | 0 | 66.4801 | 33.5199 | 0 | 66.4801 | 33.5199 | 0
44 | 17 | February | 4 | 4.9246 | 120.7 | 19.845 | 140.545 | 0 | 140.545 | 0 | 0 | 85.88 | 14.12 | 0 | 85.88 | 14.12 | 0
44 | 18 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
44 | 19 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
44 | 20 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
44 | 21 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
44 | 22 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
44 | 23 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
44 | 24 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
45 | 1 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 2 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
45 | 3 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
45 | 4 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 5 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 6 | February | 2 | 2.4623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 7 | February | 2 | 2.4623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 8 | February | 3 | 3.6934 | 0 | 21.168 | 21.168 | 0 | 21.168 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
45 | 9 | February | 2 | 2.4623 | 0 | 288.9271 | 288.9271 | 0 | 288.9271 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
45 | 10 | February | 2 | 2.4623 | 0 | 718.5878 | 718.5878 | 0 | 718.5878 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
45 | 11 | February | 2 | 2.4623 | 0 | 937.989 | 937.989 | 0 | 937.989 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
45 | 12 | February | 1 | 1.2311 | 0 | 1055.9868 | 1055.9868 | 0 | 1055.9868 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
45 | 13 | February | 2 | 2.4623 | 0 | 1027.9204 | 1027.9204 | 0 | 1027.9204 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
45 | 14 | February | 1 | 1.2311 | 0 | 825.6863 | 825.6863 | 0 | 825.6863 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
45 | 15 | February | 4 | 4.9246 | 120.7 | 624.9851 | 745.6851 | 0 | 745.6851 | 0 | 0 | 16.1865 | 83.8135 | 0 | 16.1865 | 83.8135 | 0
45 | 16 | February | 3 | 3.6934 | 0 | 336.8013 | 336.8013 | 0 | 336.8013 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
45 | 17 | February | 2 | 2.4623 | 0 | 55.0786 | 55.0786 | 0 | 55.0786 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
45 | 18 | February | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 19 | February | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 20 | February | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 21 | February | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 22 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 23 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 24 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | 1 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | 2 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | 3 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
46 | 4 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
46 | 5 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
46 | 6 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
46 | 7 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
46 | 8 | February | 6 | 7.3869 | 504.9 | 17.199 | 522.099 | 0 | 522.099 | 0 | 0 | 96.7058 | 3.2942 | 0 | 96.7058 | 3.2942 | 0
46 | 9 | February | 6 | 7.3869 | 504.9 | 51.597 | 556.497 | 0 | 556.497 | 0 | 0 | 90.7283 | 9.2717 | 0 | 90.7283 | 9.2717 | 0
46 | 10 | February | 6 | 7.3869 | 504.9 | 105.84 | 610.74 | 0 | 610.74 | 0 | 0 | 82.6702 | 17.3298 | 0 | 82.6702 | 17.3298 | 0
46 | 11 | February | 6 | 7.3869 | 504.9 | 149.499 | 654.399 | 0 | 654.399 | 0 | 0 | 77.1548 | 22.8452 | 0 | 77.1548 | 22.8452 | 0
46 | 12 | February | 5 | 6.1557 | 312.8 | 173.313 | 486.113 | 0 | 486.113 | 0 | 0 | 64.3472 | 35.6528 | 0 | 64.3472 | 35.6528 | 0
46 | 13 | February | 6 | 7.3869 | 504.9 | 177.282 | 682.182 | 0 | 682.182 | 0 | 0 | 74.0125 | 25.9875 | 0 | 74.0125 | 25.9875 | 0
46 | 14 | February | 6 | 7.3869 | 504.9 | 157.437 | 662.337 | 0 | 662.337 | 0 | 0 | 76.2301 | 23.7699 | 0 | 76.2301 | 23.7699 | 0
46 | 15 | February | 6 | 7.3869 | 504.9 | 117.747 | 622.647 | 0 | 622.647 | 0 | 0 | 81.0893 | 18.9107 | 0 | 81.0893 | 18.9107 | 0
46 | 16 | February | 6 | 7.3869 | 504.9 | 64.827 | 569.727 | 0 | 569.727 | 0 | 0 | 88.6214 | 11.3786 | 0 | 88.6214 | 11.3786 | 0
46 | 17 | February | 7 | 8.618 | 908.65 | 14.553 | 923.203 | 0 | 923.203 | 0 | 0 | 98.4236 | 1.5764 | 0 | 98.4236 | 1.5764 | 0
46 | 18 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
46 | 19 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
46 | 20 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
46 | 21 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
46 | 22 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
46 | 23 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
46 | 24 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
47 | 1 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
47 | 2 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
47 | 3 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
47 | 4 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
47 | 5 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
47 | 6 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
47 | 7 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
47 | 8 | February | 7 | 8.618 | 908.65 | 9.261 | 917.911 | 0 | 917.911 | 0 | 0 | 98.9911 | 1.0089 | 0 | 98.9911 | 1.0089 | 0
47 | 9 | February | 6 | 7.3869 | 504.9 | 54.243 | 559.143 | 0 | 559.143 | 0 | 0 | 90.2989 | 9.7011 | 0 | 90.2989 | 9.7011 | 0
47 | 10 | February | 6 | 7.3869 | 504.9 | 108.486 | 613.386 | 0 | 613.386 | 0 | 0 | 82.3136 | 17.6864 | 0 | 82.3136 | 17.6864 | 0
47 | 11 | February | 6 | 7.3869 | 504.9 | 152.145 | 657.045 | 0 | 657.045 | 0 | 0 | 76.8441 | 23.1559 | 0 | 76.8441 | 23.1559 | 0
47 | 12 | February | 6 | 7.3869 | 504.9 | 177.282 | 682.182 | 0 | 682.182 | 0 | 0 | 74.0125 | 25.9875 | 0 | 74.0125 | 25.9875 | 0
47 | 13 | February | 5 | 6.1557 | 312.8 | 179.928 | 492.728 | 0 | 492.728 | 0 | 0 | 63.4833 | 36.5167 | 0 | 63.4833 | 36.5167 | 0
47 | 14 | February | 5 | 6.1557 | 312.8 | 161.406 | 474.206 | 0 | 474.206 | 0 | 0 | 65.9629 | 34.0371 | 0 | 65.9629 | 34.0371 | 0
47 | 15 | February | 6 | 7.3869 | 504.9 | 121.716 | 626.616 | 0 | 626.616 | 0 | 0 | 80.5757 | 19.4243 | 0 | 80.5757 | 19.4243 | 0
47 | 16 | February | 6 | 7.3869 | 504.9 | 67.473 | 572.373 | 0 | 572.373 | 0 | 0 | 88.2117 | 11.7883 | 0 | 88.2117 | 11.7883 | 0
47 | 17 | February | 7 | 8.618 | 908.65 | 15.876 | 924.526 | 0 | 924.526 | 0 | 0 | 98.2828 | 1.7172 | 0 | 98.2828 | 1.7172 | 0
47 | 18 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
47 | 19 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
47 | 20 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
47 | 21 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
47 | 22 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
47 | 23 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
47 | 24 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
48 | 1 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
48 | 2 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
48 | 3 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
48 | 4 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
48 | 5 | February | 6.5 | 8.0024 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
48 | 6 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
48 | 7 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
48 | 8 | February | 7 | 8.618 | 908.65 | 9.261 | 917.911 | 0 | 917.911 | 0 | 0 | 98.9911 | 1.0089 | 0 | 98.9911 | 1.0089 | 0
48 | 9 | February | 7 | 8.618 | 908.65 | 55.566 | 964.216 | 0 | 964.216 | 0 | 0 | 94.2372 | 5.7628 | 0 | 94.2372 | 5.7628 | 0
48 | 10 | February | 5 | 6.1557 | 312.8 | 111.132 | 423.932 | 0 | 423.932 | 0 | 0 | 73.7854 | 26.2146 | 0 | 73.7854 | 26.2146 | 0
48 | 11 | February | 6 | 7.3869 | 504.9 | 156.114 | 661.014 | 0 | 661.014 | 0 | 0 | 76.3826 | 23.6174 | 0 | 76.3826 | 23.6174 | 0
48 | 12 | February | 6 | 7.3869 | 504.9 | 179.928 | 684.828 | 0 | 684.828 | 0 | 0 | 73.7265 | 26.2735 | 0 | 73.7265 | 26.2735 | 0
48 | 13 | February | 5 | 6.1557 | 312.8 | 183.897 | 496.697 | 0 | 496.697 | 0 | 0 | 62.976 | 37.024 | 0 | 62.976 | 37.024 | 0
48 | 14 | February | 6 | 7.3869 | 504.9 | 164.052 | 668.952 | 0 | 668.952 | 0 | 0 | 75.4763 | 24.5237 | 0 | 75.4763 | 24.5237 | 0
48 | 15 | February | 4 | 4.9246 | 120.7 | 124.362 | 245.062 | 0 | 245.062 | 0 | 0 | 49.2528 | 50.7472 | 0 | 49.2528 | 50.7472 | 0
48 | 16 | February | 4 | 4.9246 | 120.7 | 70.119 | 190.819 | 0 | 190.819 | 0 | 0 | 63.2537 | 36.7463 | 0 | 63.2537 | 36.7463 | 0
48 | 17 | February | 5 | 6.1557 | 312.8 | 17.199 | 329.999 | 0 | 329.999 | 0 | 0 | 94.7882 | 5.2118 | 0 | 94.7882 | 5.2118 | 0
48 | 18 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
48 | 19 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
48 | 20 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
48 | 21 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
48 | 22 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
48 | 23 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
48 | 24 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
49 | 1 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
49 | 2 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
49 | 3 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
49 | 4 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
49 | 5 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
49 | 6 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
49 | 7 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
49 | 8 | February | 5 | 6.1557 | 312.8 | 10.584 | 323.384 | 0 | 323.384 | 0 | 0 | 96.7271 | 3.2729 | 0 | 96.7271 | 3.2729 | 0
49 | 9 | February | 6 | 7.3869 | 504.9 | 58.212 | 563.112 | 0 | 563.112 | 0 | 0 | 89.6624 | 10.3376 | 0 | 89.6624 | 10.3376 | 0
49 | 10 | February | 4 | 4.9246 | 120.7 | 113.778 | 234.478 | 0 | 234.478 | 0 | 0 | 51.476 | 48.524 | 0 | 51.476 | 48.524 | 0
49 | 11 | February | 4 | 4.9246 | 120.7 | 157.437 | 278.137 | 0 | 278.137 | 0 | 0 | 43.3959 | 56.6041 | 0 | 43.3959 | 56.6041 | 0
49 | 12 | February | 4 | 4.9246 | 120.7 | 182.574 | 303.274 | 0 | 303.274 | 0 | 0 | 39.799 | 60.201 | 0 | 39.799 | 60.201 | 0
49 | 13 | February | 4 | 4.9246 | 120.7 | 185.22 | 305.92 | 0 | 305.92 | 0 | 0 | 39.4548 | 60.5452 | 0 | 39.4548 | 60.5452 | 0
49 | 14 | February | 4 | 4.9246 | 120.7 | 165.375 | 286.075 | 0 | 286.075 | 0 | 0 | 42.1917 | 57.8083 | 0 | 42.1917 | 57.8083 | 0
49 | 15 | February | 4 | 4.9246 | 120.7 | 125.685 | 246.385 | 0 | 246.385 | 0 | 0 | 48.9884 | 51.0116 | 0 | 48.9884 | 51.0116 | 0
49 | 16 | February | 4 | 4.9246 | 120.7 | 72.765 | 193.465 | 0 | 193.465 | 0 | 0 | 62.3885 | 37.6115 | 0 | 62.3885 | 37.6115 | 0
49 | 17 | February | 4 | 4.9246 | 120.7 | 18.522 | 139.222 | 0 | 139.222 | 0 | 0 | 86.6961 | 13.3039 | 0 | 86.6961 | 13.3039 | 0
49 | 18 | February | 9 | 11.0803 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
49 | 19 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49 | 20 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49 | 21 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49 | 22 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
49 | 23 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
49 | 24 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
50 | 1 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
50 | 2 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
50 | 3 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
50 | 4 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
50 | 5 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
50 | 6 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
50 | 7 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
50 | 8 | February | 8 | 9.8492 | 1213.8 | 11.907 | 1225.707 | 0 | 1225.707 | 0 | 0 | 99.0286 | 0.97144 | 0 | 99.0286 | 0.97144 | 0
50 | 9 | February | 7 | 8.618 | 908.65 | 60.858 | 969.508 | 0 | 969.508 | 0 | 0 | 93.7228 | 6.2772 | 0 | 93.7228 | 6.2772 | 0
50 | 10 | February | 7 | 8.618 | 908.65 | 117.747 | 1026.397 | 0 | 1026.397 | 0 | 0 | 88.5281 | 11.4719 | 0 | 88.5281 | 11.4719 | 0
50 | 11 | February | 7 | 8.618 | 908.65 | 161.406 | 1070.056 | 0 | 1070.056 | 0 | 0 | 84.9161 | 15.0839 | 0 | 84.9161 | 15.0839 | 0
50 | 12 | February | 6 | 7.3869 | 504.9 | 186.543 | 691.443 | 0 | 691.443 | 0 | 0 | 73.0212 | 26.9788 | 0 | 73.0212 | 26.9788 | 0
50 | 13 | February | 7 | 8.618 | 908.65 | 189.189 | 1097.839 | 0 | 1097.839 | 0 | 0 | 82.7671 | 17.2329 | 0 | 82.7671 | 17.2329 | 0
50 | 14 | February | 8 | 9.8492 | 1213.8 | 169.344 | 1383.144 | 0 | 1383.144 | 0 | 0 | 87.7566 | 12.2434 | 0 | 87.7566 | 12.2434 | 0
50 | 15 | February | 6 | 7.3869 | 504.9 | 235.7495 | 740.6495 | 0 | 740.6495 | 0 | 0 | 68.1699 | 31.8301 | 0 | 68.1699 | 31.8301 | 0
50 | 16 | February | 4 | 4.9246 | 120.7 | 127.68 | 248.38 | 0 | 248.38 | 0 | 0 | 48.5949 | 51.4051 | 0 | 48.5949 | 51.4051 | 0
50 | 17 | February | 5 | 6.1557 | 312.8 | 18.522 | 331.322 | 0 | 331.322 | 0 | 0 | 94.4097 | 5.5903 | 0 | 94.4097 | 5.5903 | 0
50 | 18 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
50 | 19 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
50 | 20 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
50 | 21 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
50 | 22 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
50 | 23 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
50 | 24 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
51 | 1 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
51 | 2 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
51 | 3 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
51 | 4 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
51 | 5 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
51 | 6 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
51 | 7 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
51 | 8 | February | 6 | 7.3869 | 504.9 | 13.23 | 518.13 | 0 | 518.13 | 0 | 0 | 97.4466 | 2.5534 | 0 | 97.4466 | 2.5534 | 0
51 | 9 | February | 6 | 7.3869 | 504.9 | 63.504 | 568.404 | 0 | 568.404 | 0 | 0 | 88.8277 | 11.1723 | 0 | 88.8277 | 11.1723 | 0
51 | 10 | February | 5 | 6.1557 | 312.8 | 120.393 | 433.193 | 0 | 433.193 | 0 | 0 | 72.208 | 27.792 | 0 | 72.208 | 27.792 | 0
51 | 11 | February | 6 | 7.3869 | 504.9 | 164.052 | 668.952 | 0 | 668.952 | 0 | 0 | 75.4763 | 24.5237 | 0 | 75.4763 | 24.5237 | 0
51 | 12 | February | 6 | 7.3869 | 504.9 | 189.189 | 694.089 | 0 | 694.089 | 0 | 0 | 72.7428 | 27.2572 | 0 | 72.7428 | 27.2572 | 0
51 | 13 | February | 5 | 6.1557 | 312.8 | 367.8968 | 680.6968 | 0 | 680.6968 | 0 | 0 | 45.9529 | 54.0471 | 0 | 45.9529 | 54.0471 | 0
51 | 14 | February | 5 | 6.1557 | 312.8 | 321.4878 | 634.2878 | 0 | 634.2878 | 0 | 0 | 49.3152 | 50.6848 | 0 | 49.3152 | 50.6848 | 0
51 | 15 | February | 5 | 6.1557 | 312.8 | 242.3781 | 555.1781 | 0 | 555.1781 | 0 | 0 | 56.3423 | 43.6577 | 0 | 56.3423 | 43.6577 | 0
51 | 16 | February | 5 | 6.1557 | 312.8 | 194.0968 | 506.8968 | 0 | 506.8968 | 0 | 0 | 61.7088 | 38.2912 | 0 | 61.7088 | 38.2912 | 0
51 | 17 | February | 5 | 6.1557 | 312.8 | 33.075 | 345.875 | 0 | 345.875 | 0 | 0 | 90.4373 | 9.5627 | 0 | 90.4373 | 9.5627 | 0
51 | 18 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
51 | 19 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
51 | 20 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
51 | 21 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
51 | 22 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
51 | 23 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
51 | 24 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
52 | 1 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
52 | 2 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
52 | 3 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
52 | 4 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
52 | 5 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
52 | 6 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
52 | 7 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
52 | 8 | February | 8 | 9.8492 | 1213.8 | 72.3741 | 1286.1741 | 0 | 1286.1741 | 0 | 0 | 94.3729 | 5.6271 | 0 | 94.3729 | 5.6271 | 0
52 | 9 | February | 7 | 8.618 | 908.65 | 363.2911 | 1271.9411 | 0 | 1271.9411 | 0 | 0 | 71.4381 | 28.5619 | 0 | 71.4381 | 28.5619 | 0
52 | 10 | February | 8 | 9.8492 | 1213.8 | 776.1486 | 1989.9486 | 0 | 1989.9486 | 0 | 0 | 60.9966 | 39.0034 | 0 | 60.9966 | 39.0034 | 0
52 | 11 | February | 7 | 8.618 | 908.65 | 1014.8321 | 1923.4821 | 0 | 1923.4821 | 0 | 0 | 47.2398 | 52.7602 | 0 | 47.2398 | 52.7602 | 0
52 | 12 | February | 7 | 8.618 | 908.65 | 1131.9409 | 2040.5909 | 1 | 2000 | 40.5909 | 2.0295 | 44.5288 | 54.5675 | 3.586 | 43.403 | 55.4712 | 4.4672
52 | 13 | February | 8 | 9.8492 | 1213.8 | 1106.8326 | 2320.6326 | 1 | 2000 | 320.6326 | 16.0316 | 52.3047 | 39.31 | 28.9685 | 44.6584 | 47.6953 | 26.4156
52 | 14 | February | 7 | 8.618 | 908.65 | 965.2735 | 1873.9235 | 0 | 1873.9235 | 0 | 0 | 48.4892 | 51.5108 | 0 | 48.4892 | 51.5108 | 0
52 | 15 | February | 8 | 9.8492 | 1213.8 | 704.2206 | 1918.0206 | 0 | 1918.0206 | 0 | 0 | 63.284 | 36.716 | 0 | 63.284 | 36.716 | 0
52 | 16 | February | 8 | 9.8492 | 1213.8 | 396.8156 | 1610.6156 | 0 | 1610.6156 | 0 | 0 | 75.3625 | 24.6375 | 0 | 75.3625 | 24.6375 | 0
52 | 17 | February | 8 | 9.8492 | 1213.8 | 86.5892 | 1300.3892 | 0 | 1300.3892 | 0 | 0 | 93.3413 | 6.6587 | 0 | 93.3413 | 6.6587 | 0
52 | 18 | February | 7 | 8.618 | 908.65 | 1.323 | 909.973 | 0 | 909.973 | 0 | 0 | 99.8546 | 0.14539 | 0 | 99.8546 | 0.14539 | 0
52 | 19 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
52 | 20 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
52 | 21 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
52 | 22 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
52 | 23 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
52 | 24 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
53 | 1 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
53 | 2 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
53 | 3 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
53 | 4 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | 5 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | 6 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | 7 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | 8 | February | 3 | 3.6934 | 0 | 87.4584 | 87.4584 | 0 | 87.4584 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
53 | 9 | February | 3 | 3.6934 | 0 | 370.9772 | 370.9772 | 0 | 370.9772 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
53 | 10 | February | 4 | 4.9246 | 120.7 | 783.0578 | 903.7578 | 0 | 903.7578 | 0 | 0 | 13.3553 | 86.6447 | 0 | 13.3553 | 86.6447 | 0
53 | 11 | February | 4 | 4.9246 | 120.7 | 1026.4313 | 1147.1313 | 0 | 1147.1313 | 0 | 0 | 10.5219 | 89.4781 | 0 | 10.5219 | 89.4781 | 0
53 | 12 | February | 5 | 6.1557 | 312.8 | 1140.1703 | 1452.9703 | 0 | 1452.9703 | 0 | 0 | 21.5283 | 78.4717 | 0 | 21.5283 | 78.4717 | 0
53 | 13 | February | 4 | 4.9246 | 120.7 | 1117.4095 | 1238.1095 | 0 | 1238.1095 | 0 | 0 | 9.7487 | 90.2513 | 0 | 9.7487 | 90.2513 | 0
53 | 14 | February | 4 | 4.9246 | 120.7 | 973.7674 | 1094.4674 | 0 | 1094.4674 | 0 | 0 | 11.0282 | 88.9718 | 0 | 11.0282 | 88.9718 | 0
53 | 15 | February | 4 | 4.9246 | 120.7 | 712.7565 | 833.4565 | 0 | 833.4565 | 0 | 0 | 14.4819 | 85.5181 | 0 | 14.4819 | 85.5181 | 0
53 | 16 | February | 4 | 4.9246 | 120.7 | 404.0091 | 524.7091 | 0 | 524.7091 | 0 | 0 | 23.0032 | 76.9968 | 0 | 23.0032 | 76.9968 | 0
53 | 17 | February | 3 | 3.6934 | 0 | 92.4495 | 92.4495 | 0 | 92.4495 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
53 | 18 | February | 3 | 3.6934 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
53 | 19 | February | 2 | 2.4623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | 20 | February | 2 | 2.4623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | 21 | February | 2 | 2.4623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | 22 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | 23 | February | 2 | 2.4623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | 24 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | 1 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | 2 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | 3 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | 4 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | 5 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | 6 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
54 | 7 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
54 | 8 | February | 4 | 4.9246 | 120.7 | 91.171 | 211.871 | 0 | 211.871 | 0 | 0 | 56.9686 | 43.0314 | 0 | 56.9686 | 43.0314 | 0
54 | 9 | February | 4 | 4.9246 | 120.7 | 380.9235 | 501.6235 | 0 | 501.6235 | 0 | 0 | 24.0619 | 75.9381 | 0 | 24.0619 | 75.9381 | 0
54 | 10 | February | 3 | 3.6934 | 0 | 791.1269 | 791.1269 | 0 | 791.1269 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
54 | 11 | February | 4 | 4.9246 | 120.7 | 1033.0775 | 1153.7775 | 0 | 1153.7775 | 0 | 0 | 10.4613 | 89.5387 | 0 | 10.4613 | 89.5387 | 0
54 | 12 | February | 4 | 4.9246 | 120.7 | 1141.7446 | 1262.4446 | 0 | 1262.4446 | 0 | 0 | 9.5608 | 90.4392 | 0 | 9.5608 | 90.4392 | 0
54 | 13 | February | 4 | 4.9246 | 120.7 | 1117.6844 | 1238.3844 | 0 | 1238.3844 | 0 | 0 | 9.7466 | 90.2534 | 0 | 9.7466 | 90.2534 | 0
54 | 14 | February | 4 | 4.9246 | 120.7 | 974.2947 | 1094.9947 | 0 | 1094.9947 | 0 | 0 | 11.0229 | 88.9771 | 0 | 11.0229 | 88.9771 | 0
54 | 15 | February | 4 | 4.9246 | 120.7 | 725.4399 | 846.1399 | 0 | 846.1399 | 0 | 0 | 14.2648 | 85.7352 | 0 | 14.2648 | 85.7352 | 0
54 | 16 | February | 4 | 4.9246 | 120.7 | 407.3217 | 528.0217 | 0 | 528.0217 | 0 | 0 | 22.8589 | 77.1411 | 0 | 22.8589 | 77.1411 | 0
54 | 17 | February | 4 | 4.9246 | 120.7 | 98.6742 | 219.3742 | 0 | 219.3742 | 0 | 0 | 55.0202 | 44.9798 | 0 | 55.0202 | 44.9798 | 0
54 | 18 | February | 2 | 2.4623 | 0 | 2.646 | 2.646 | 0 | 2.646 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
54 | 19 | February | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | 20 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | 21 | February | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | 22 | February | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | 23 | February | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | 24 | February | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | 1 | February | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | 2 | February | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | 3 | February | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | 4 | February | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | 5 | February | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | 6 | February | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | 7 | February | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | 8 | February | 1 | 1.2311 | 0 | 26.46 | 26.46 | 0 | 26.46 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
55 | 9 | February | 0 | 0 | 0 | 270.8886 | 270.8886 | 0 | 270.8886 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
55 | 10 | February | 3 | 3.6934 | 0 | 247.8047 | 247.8047 | 0 | 247.8047 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
55 | 11 | February | 3 | 3.6934 | 0 | 494.1536 | 494.1536 | 0 | 494.1536 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
55 | 12 | February | 3 | 3.6934 | 0 | 372.7446 | 372.7446 | 0 | 372.7446 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
55 | 13 | February | 4 | 4.9246 | 120.7 | 379.1503 | 499.8503 | 0 | 499.8503 | 0 | 0 | 24.1472 | 75.8528 | 0 | 24.1472 | 75.8528 | 0
55 | 14 | February | 3 | 3.6934 | 0 | 182.574 | 182.574 | 0 | 182.574 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
55 | 15 | February | 4 | 4.9246 | 120.7 | 261.6538 | 382.3538 | 0 | 382.3538 | 0 | 0 | 31.5676 | 68.4324 | 0 | 31.5676 | 68.4324 | 0
55 | 16 | February | 4 | 4.9246 | 120.7 | 147.9805 | 268.6805 | 0 | 268.6805 | 0 | 0 | 44.9232 | 55.0768 | 0 | 44.9232 | 55.0768 | 0
55 | 17 | February | 4 | 4.9246 | 120.7 | 43.659 | 164.359 | 0 | 164.359 | 0 | 0 | 73.4368 | 26.5632 | 0 | 73.4368 | 26.5632 | 0
55 | 18 | February | 5 | 6.1557 | 312.8 | 1.323 | 314.123 | 0 | 314.123 | 0 | 0 | 99.5788 | 0.42117 | 0 | 99.5788 | 0.42117 | 0
55 | 19 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | 20 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | 21 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | 22 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
55 | 23 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
55 | 24 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
56 | 1 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
56 | 2 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
56 | 3 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | 4 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
56 | 5 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
56 | 6 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
56 | 7 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
56 | 8 | February | 5 | 6.1557 | 312.8 | 54.8267 | 367.6267 | 0 | 367.6267 | 0 | 0 | 85.0863 | 14.9137 | 0 | 85.0863 | 14.9137 | 0
56 | 9 | February | 7 | 8.618 | 908.65 | 196.6042 | 1105.2542 | 0 | 1105.2542 | 0 | 0 | 82.2119 | 17.7881 | 0 | 82.2119 | 17.7881 | 0
56 | 10 | February | 7 | 8.618 | 908.65 | 244.0588 | 1152.7088 | 0 | 1152.7088 | 0 | 0 | 78.8274 | 21.1726 | 0 | 78.8274 | 21.1726 | 0
56 | 11 | February | 6 | 7.3869 | 504.9 | 339.5949 | 844.4949 | 0 | 844.4949 | 0 | 0 | 59.7872 | 40.2128 | 0 | 59.7872 | 40.2128 | 0
56 | 12 | February | 6 | 7.3869 | 504.9 | 383.8642 | 888.7642 | 0 | 888.7642 | 0 | 0 | 56.8092 | 43.1908 | 0 | 56.8092 | 43.1908 | 0
56 | 13 | February | 6 | 7.3869 | 504.9 | 386.1507 | 891.0507 | 0 | 891.0507 | 0 | 0 | 56.6634 | 43.3366 | 0 | 56.6634 | 43.3366 | 0
56 | 14 | February | 6 | 7.3869 | 504.9 | 344.3174 | 849.2174 | 0 | 849.2174 | 0 | 0 | 59.4547 | 40.5453 | 0 | 59.4547 | 40.5453 | 0
56 | 15 | February | 6 | 7.3869 | 504.9 | 378.9174 | 883.8174 | 0 | 883.8174 | 0 | 0 | 57.1272 | 42.8728 | 0 | 57.1272 | 42.8728 | 0
56 | 16 | February | 6 | 7.3869 | 504.9 | 216.0029 | 720.9029 | 0 | 720.9029 | 0 | 0 | 70.0372 | 29.9628 | 0 | 70.0372 | 29.9628 | 0
56 | 17 | February | 5 | 6.1557 | 312.8 | 109.4209 | 422.2209 | 0 | 422.2209 | 0 | 0 | 74.0844 | 25.9156 | 0 | 74.0844 | 25.9156 | 0
56 | 18 | February | 4 | 4.9246 | 120.7 | 2.646 | 123.346 | 0 | 123.346 | 0 | 0 | 97.8548 | 2.1452 | 0 | 97.8548 | 2.1452 | 0
56 | 19 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
56 | 20 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | 21 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
56 | 22 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
56 | 23 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
56 | 24 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
57 | 1 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
57 | 2 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
57 | 3 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
57 | 4 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
57 | 5 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
57 | 6 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
57 | 7 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
57 | 8 | February | 6 | 7.3869 | 504.9 | 30.429 | 535.329 | 0 | 535.329 | 0 | 0 | 94.3158 | 5.6842 | 0 | 94.3158 | 5.6842 | 0
57 | 9 | February | 7 | 8.618 | 908.65 | 134.2638 | 1042.9138 | 0 | 1042.9138 | 0 | 0 | 87.1261 | 12.8739 | 0 | 87.1261 | 12.8739 | 0
57 | 10 | February | 8 | 9.8492 | 1213.8 | 249.4069 | 1463.2069 | 0 | 1463.2069 | 0 | 0 | 82.9548 | 17.0452 | 0 | 82.9548 | 17.0452 | 0
57 | 11 | February | 8 | 9.8492 | 1213.8 | 346.5485 | 1560.3485 | 0 | 1560.3485 | 0 | 0 | 77.7903 | 22.2097 | 0 | 77.7903 | 22.2097 | 0
57 | 12 | February | 9 | 11.0803 | 1598.85 | 209.0586 | 1807.9086 | 0 | 1807.9086 | 0 | 0 | 88.4364 | 11.5636 | 0 | 88.4364 | 11.5636 | 0
57 | 13 | February | 7 | 8.618 | 908.65 | 211.6665 | 1120.3165 | 0 | 1120.3165 | 0 | 0 | 81.1065 | 18.8935 | 0 | 81.1065 | 18.8935 | 0
57 | 14 | February | 7 | 8.618 | 908.65 | 189.189 | 1097.839 | 0 | 1097.839 | 0 | 0 | 82.7671 | 17.2329 | 0 | 82.7671 | 17.2329 | 0
57 | 15 | February | 6 | 7.3869 | 504.9 | 148.176 | 653.076 | 0 | 653.076 | 0 | 0 | 77.3111 | 22.6889 | 0 | 77.3111 | 22.6889 | 0
57 | 16 | February | 8 | 9.8492 | 1213.8 | 91.287 | 1305.087 | 0 | 1305.087 | 0 | 0 | 93.0053 | 6.9947 | 0 | 93.0053 | 6.9947 | 0
57 | 17 | February | 7 | 8.618 | 908.65 | 30.429 | 939.079 | 0 | 939.079 | 0 | 0 | 96.7597 | 3.2403 | 0 | 96.7597 | 3.2403 | 0
57 | 18 | February | 6 | 7.3869 | 504.9 | 1.323 | 506.223 | 0 | 506.223 | 0 | 0 | 99.7387 | 0.26135 | 0 | 99.7387 | 0.26135 | 0
57 | 19 | February | 8 | 9.8492 | 1213.8 | 0 | 1213.8 | 0 | 1213.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
57 | 20 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
57 | 21 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
57 | 22 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
57 | 23 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
57 | 24 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
58 | 1 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
58 | 2 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
58 | 3 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58 | 4 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58 | 5 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
58 | 6 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
58 | 7 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
58 | 8 | February | 5 | 6.1557 | 312.8 | 21.168 | 333.968 | 0 | 333.968 | 0 | 0 | 93.6617 | 6.3383 | 0 | 93.6617 | 6.3383 | 0
58 | 9 | February | 4 | 4.9246 | 120.7 | 79.38 | 200.08 | 0 | 200.08 | 0 | 0 | 60.3259 | 39.6741 | 0 | 60.3259 | 39.6741 | 0
58 | 10 | February | 3 | 3.6934 | 0 | 137.592 | 137.592 | 0 | 137.592 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
58 | 11 | February | 5 | 6.1557 | 312.8 | 182.574 | 495.374 | 0 | 495.374 | 0 | 0 | 63.1442 | 36.8558 | 0 | 63.1442 | 36.8558 | 0
58 | 12 | February | 5 | 6.1557 | 312.8 | 398.2995 | 711.0995 | 0 | 711.0995 | 0 | 0 | 43.9882 | 56.0118 | 0 | 43.9882 | 56.0118 | 0
58 | 13 | February | 4 | 4.9246 | 120.7 | 212.9691 | 333.6691 | 0 | 333.6691 | 0 | 0 | 36.1736 | 63.8264 | 0 | 36.1736 | 63.8264 | 0
58 | 14 | February | 4 | 4.9246 | 120.7 | 354.0425 | 474.7425 | 0 | 474.7425 | 0 | 0 | 25.4243 | 74.5757 | 0 | 25.4243 | 74.5757 | 0
58 | 15 | February | 4 | 4.9246 | 120.7 | 258.8012 | 379.5012 | 0 | 379.5012 | 0 | 0 | 31.8049 | 68.1951 | 0 | 31.8049 | 68.1951 | 0
58 | 16 | February | 5 | 6.1557 | 312.8 | 152.2166 | 465.0166 | 0 | 465.0166 | 0 | 0 | 67.2664 | 32.7336 | 0 | 67.2664 | 32.7336 | 0
58 | 17 | February | 7 | 8.618 | 908.65 | 31.752 | 940.402 | 0 | 940.402 | 0 | 0 | 96.6236 | 3.3764 | 0 | 96.6236 | 3.3764 | 0
58 | 18 | February | 5 | 6.1557 | 312.8 | 1.323 | 314.123 | 0 | 314.123 | 0 | 0 | 99.5788 | 0.42117 | 0 | 99.5788 | 0.42117 | 0
58 | 19 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
58 | 20 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
58 | 21 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
58 | 22 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
58 | 23 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
58 | 24 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
59 | 1 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
59 | 2 | February | 5 | 6.1557 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
59 | 3 | February | 3 | 3.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59 | 4 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
59 | 5 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
59 | 6 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
59 | 7 | February | 4 | 4.9246 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
59 | 8 | February | 4 | 4.9246 | 120.7 | 22.491 | 143.191 | 0 | 143.191 | 0 | 0 | 84.293 | 15.707 | 0 | 84.293 | 15.707 | 0
59 | 9 | February | 6 | 7.3869 | 504.9 | 148.8653 | 653.7653 | 0 | 653.7653 | 0 | 0 | 77.2296 | 22.7704 | 0 | 77.2296 | 22.7704 | 0
59 | 10 | February | 6 | 7.3869 | 504.9 | 258.0993 | 762.9993 | 0 | 762.9993 | 0 | 0 | 66.1731 | 33.8269 | 0 | 66.1731 | 33.8269 | 0
59 | 11 | February | 5 | 6.1557 | 312.8 | 330.8357 | 643.6357 | 0 | 643.6357 | 0 | 0 | 48.5989 | 51.4011 | 0 | 48.5989 | 51.4011 | 0
59 | 12 | February | 6 | 7.3869 | 504.9 | 213.144 | 718.044 | 0 | 718.044 | 0 | 0 | 70.316 | 29.684 | 0 | 70.316 | 29.684 | 0
59 | 13 | February | 8 | 9.8492 | 1213.8 | 212.9961 | 1426.7961 | 0 | 1426.7961 | 0 | 0 | 85.0717 | 14.9283 | 0 | 85.0717 | 14.9283 | 0
59 | 14 | February | 6 | 7.3869 | 504.9 | 191.835 | 696.735 | 0 | 696.735 | 0 | 0 | 72.4666 | 27.5334 | 0 | 72.4666 | 27.5334 | 0
59 | 15 | February | 6 | 7.3869 | 504.9 | 150.822 | 655.722 | 0 | 655.722 | 0 | 0 | 76.9991 | 23.0009 | 0 | 76.9991 | 23.0009 | 0
59 | 16 | February | 6 | 7.3869 | 504.9 | 159.6426 | 664.5426 | 0 | 664.5426 | 0 | 0 | 75.9771 | 24.0229 | 0 | 75.9771 | 24.0229 | 0
59 | 17 | February | 5 | 6.1557 | 312.8 | 54.243 | 367.043 | 0 | 367.043 | 0 | 0 | 85.2216 | 14.7784 | 0 | 85.2216 | 14.7784 | 0
59 | 18 | February | 5 | 6.1557 | 312.8 | 2.646 | 315.446 | 0 | 315.446 | 0 | 0 | 99.1612 | 0.83881 | 0 | 99.1612 | 0.83881 | 0
59 | 19 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
59 | 20 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
59 | 21 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
59 | 22 | February | 6 | 7.3869 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
59 | 23 | February | 8 | 9.8492 | 1213.8 | 0 | 1213.8 | 0 | 1213.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
59 | 24 | February | 7 | 8.618 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
60 | 1 | March | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
60 | 2 | March | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
60 | 3 | March | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
60 | 4 | March | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
60 | 5 | March | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
60 | 6 | March | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
60 | 7 | March | 9.8 | 12.0652 | 1683.85 | 2.646 | 1686.496 | 0 | 1686.496 | 0 | 0 | 99.8431 | 0.15689 | 0 | 99.8431 | 0.15689 | 0
60 | 8 | March | 9.8 | 12.0652 | 1683.85 | 87.5805 | 1771.4305 | 0 | 1771.4305 | 0 | 0 | 95.0559 | 4.9441 | 0 | 95.0559 | 4.9441 | 0
60 | 9 | March | 9.3 | 11.4496 | 1598.85 | 255.9762 | 1854.8262 | 0 | 1854.8262 | 0 | 0 | 86.1995 | 13.8005 | 0 | 86.1995 | 13.8005 | 0
60 | 10 | March | 10.8 | 13.2964 | 1698.3 | 760.267 | 2458.567 | 1 | 2000 | 458.567 | 22.9284 | 69.0768 | 15.085 | 60.3166 | 61.9866 | 30.9232 | 27.0015
60 | 11 | March | 11.3 | 13.9119 | 1700 | 709.0589 | 2409.0589 | 1 | 2000 | 409.0589 | 20.4529 | 70.567 | 15 | 57.6904 | 64.5471 | 29.433 | 24.0623
60 | 12 | March | 8.7 | 10.711 | 1490.05 | 796.2608 | 2286.3108 | 1 | 2000 | 286.3108 | 14.3155 | 65.1727 | 25.4975 | 35.9569 | 60.187 | 34.8273 | 19.2148
60 | 13 | March | 11.8 | 14.5275 | 1700 | 1063.3528 | 2763.3528 | 1 | 2000 | 763.3528 | 38.1676 | 61.5195 | 15 | 71.7874 | 46.8324 | 38.4805 | 44.9031
60 | 14 | March | 6.2 | 7.6331 | 625.6 | 955.8339 | 1581.4339 | 0 | 1581.4339 | 0 | 0 | 39.559 | 60.441 | 0 | 39.559 | 60.441 | 0
60 | 15 | March | 13.4 | 16.4973 | 1700 | 643.596 | 2343.596 | 1 | 2000 | 343.596 | 17.1798 | 72.5381 | 15 | 53.3869 | 67.8202 | 27.4619 | 20.2115
60 | 16 | March | 10.3 | 12.6808 | 1694.9 | 445.417 | 2140.317 | 1 | 2000 | 140.317 | 7.0158 | 79.1892 | 15.255 | 31.5024 | 77.7292 | 20.8108 | 8.2788
60 | 17 | March | 10.3 | 12.6808 | 1694.9 | 122.5505 | 1817.4505 | 0 | 1817.4505 | 0 | 0 | 93.257 | 6.743 | 0 | 93.257 | 6.743 | 0
60 | 18 | March | 9.3 | 11.4496 | 1598.85 | 6.615 | 1605.465 | 0 | 1605.465 | 0 | 0 | 99.588 | 0.41203 | 0 | 99.588 | 0.41203 | 0
60 | 19 | March | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
60 | 20 | March | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
60 | 21 | March | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
60 | 22 | March | 11.8 | 14.5275 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
60 | 23 | March | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
60 | 24 | March | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
61 | 1 | March | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
61 | 2 | March | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
61 | 3 | March | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
61 | 4 | March | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
61 | 5 | March | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
61 | 6 | March | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
61 | 7 | March | 5.1 | 6.2788 | 312.8 | 2.646 | 315.446 | 0 | 315.446 | 0 | 0 | 99.1612 | 0.83881 | 0 | 99.1612 | 0.83881 | 0
61 | 8 | March | 5.1 | 6.2788 | 312.8 | 46.305 | 359.105 | 0 | 359.105 | 0 | 0 | 87.1054 | 12.8946 | 0 | 87.1054 | 12.8946 | 0
61 | 9 | March | 6.2 | 7.6331 | 625.6 | 256.9184 | 882.5184 | 0 | 882.5184 | 0 | 0 | 70.888 | 29.112 | 0 | 70.888 | 29.112 | 0
61 | 10 | March | 6.7 | 8.2487 | 761.6 | 567.9015 | 1329.5015 | 0 | 1329.5015 | 0 | 0 | 57.2846 | 42.7154 | 0 | 57.2846 | 42.7154 | 0
61 | 11 | March | 6.2 | 7.6331 | 625.6 | 699.3636 | 1324.9636 | 0 | 1324.9636 | 0 | 0 | 47.2164 | 52.7836 | 0 | 47.2164 | 52.7836 | 0
61 | 12 | March | 6.2 | 7.6331 | 625.6 | 590.9173 | 1216.5173 | 0 | 1216.5173 | 0 | 0 | 51.4255 | 48.5745 | 0 | 51.4255 | 48.5745 | 0
61 | 13 | March | 7.2 | 8.8642 | 908.65 | 406.6239 | 1315.2739 | 0 | 1315.2739 | 0 | 0 | 69.0845 | 30.9155 | 0 | 69.0845 | 30.9155 | 0
61 | 14 | March | 6.2 | 7.6331 | 625.6 | 369.7555 | 995.3555 | 0 | 995.3555 | 0 | 0 | 62.8519 | 37.1481 | 0 | 62.8519 | 37.1481 | 0
61 | 15 | March | 6.7 | 8.2487 | 761.6 | 289.6344 | 1051.2344 | 0 | 1051.2344 | 0 | 0 | 72.4482 | 27.5518 | 0 | 72.4482 | 27.5518 | 0
61 | 16 | March | 5.1 | 6.2788 | 312.8 | 248.5766 | 561.3766 | 0 | 561.3766 | 0 | 0 | 55.7202 | 44.2798 | 0 | 55.7202 | 44.2798 | 0
61 | 17 | March | 4.1 | 5.0477 | 173.4 | 39.69 | 213.09 | 0 | 213.09 | 0 | 0 | 81.3741 | 18.6259 | 0 | 81.3741 | 18.6259 | 0
61 | 18 | March | 3.1 | 3.8165 | 0 | 5.292 | 5.292 | 0 | 5.292 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
61 | 19 | March | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | 20 | March | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | 21 | March | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
61 | 22 | March | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
61 | 23 | March | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
61 | 24 | March | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
62 | 1 | March | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
62 | 2 | March | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
62 | 3 | March | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
62 | 4 | March | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
62 | 5 | March | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
62 | 6 | March | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
62 | 7 | March | 7.2 | 8.8642 | 908.65 | 1.323 | 909.973 | 0 | 909.973 | 0 | 0 | 99.8546 | 0.14539 | 0 | 99.8546 | 0.14539 | 0
62 | 8 | March | 6.7 | 8.2487 | 761.6 | 30.429 | 792.029 | 0 | 792.029 | 0 | 0 | 96.1581 | 3.8419 | 0 | 96.1581 | 3.8419 | 0
62 | 9 | March | 6.7 | 8.2487 | 761.6 | 92.61 | 854.21 | 0 | 854.21 | 0 | 0 | 89.1584 | 10.8416 | 0 | 89.1584 | 10.8416 | 0
62 | 10 | March | 6.7 | 8.2487 | 761.6 | 153.468 | 915.068 | 0 | 915.068 | 0 | 0 | 83.2288 | 16.7712 | 0 | 83.2288 | 16.7712 | 0
62 | 11 | March | 6.7 | 8.2487 | 761.6 | 199.7648 | 961.3648 | 0 | 961.3648 | 0 | 0 | 79.2207 | 20.7793 | 0 | 79.2207 | 20.7793 | 0
62 | 12 | March | 6.2 | 7.6331 | 625.6 | 225.0632 | 850.6632 | 0 | 850.6632 | 0 | 0 | 73.5426 | 26.4574 | 0 | 73.5426 | 26.4574 | 0
62 | 13 | March | 5.7 | 7.0175 | 504.9 | 423.1004 | 928.0004 | 0 | 928.0004 | 0 | 0 | 54.4073 | 45.5927 | 0 | 54.4073 | 45.5927 | 0
62 | 14 | March | 7.7 | 9.4798 | 1059.95 | 848.8702 | 1908.8202 | 0 | 1908.8202 | 0 | 0 | 55.5291 | 44.4709 | 0 | 55.5291 | 44.4709 | 0
62 | 15 | March | 9.8 | 12.0652 | 1683.85 | 293.4599 | 1977.3099 | 0 | 1977.3099 | 0 | 0 | 85.1586 | 14.8414 | 0 | 85.1586 | 14.8414 | 0
62 | 16 | March | 6.7 | 8.2487 | 761.6 | 184.9217 | 946.5217 | 0 | 946.5217 | 0 | 0 | 80.463 | 19.537 | 0 | 80.463 | 19.537 | 0
62 | 17 | March | 4.1 | 5.0477 | 173.4 | 91.0686 | 264.4686 | 0 | 264.4686 | 0 | 0 | 65.5654 | 34.4346 | 0 | 65.5654 | 34.4346 | 0
62 | 18 | March | 5.1 | 6.2788 | 312.8 | 6.615 | 319.415 | 0 | 319.415 | 0 | 0 | 97.929 | 2.071 | 0 | 97.929 | 2.071 | 0
62 | 19 | March | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
62 | 20 | March | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
62 | 21 | March | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
62 | 22 | March | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62 | 23 | March | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62 | 24 | March | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63 | 1 | March | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
63 | 2 | March | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
63 | 3 | March | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
63 | 4 | March | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
63 | 5 | March | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63 | 6 | March | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
63 | 7 | March | 5.7 | 7.0175 | 504.9 | 5.292 | 510.192 | 0 | 510.192 | 0 | 0 | 98.9627 | 1.0373 | 0 | 98.9627 | 1.0373 | 0
63 | 8 | March | 4.1 | 5.0477 | 173.4 | 110.9457 | 284.3457 | 0 | 284.3457 | 0 | 0 | 60.9821 | 39.0179 | 0 | 60.9821 | 39.0179 | 0
63 | 9 | March | 6.2 | 7.6331 | 625.6 | 472.3917 | 1097.9917 | 0 | 1097.9917 | 0 | 0 | 56.9768 | 43.0232 | 0 | 56.9768 | 43.0232 | 0
63 | 10 | March | 9.3 | 11.4496 | 1598.85 | 582.9 | 2181.75 | 1 | 2000 | 181.75 | 9.0875 | 73.2829 | 20.0575 | 31.1803 | 70.855 | 26.7171 | 11.3675
63 | 11 | March | 9.3 | 11.4496 | 1598.85 | 973.4877 | 2572.3377 | 1 | 2000 | 572.3377 | 28.6169 | 62.1555 | 20.0575 | 58.7925 | 51.3256 | 37.8445 | 35.7968
63 | 12 | March | 5.1 | 6.2788 | 312.8 | 237.6049 | 550.4049 | 0 | 550.4049 | 0 | 0 | 56.8309 | 43.1691 | 0 | 56.8309 | 43.1691 | 0
63 | 13 | March | 3.6 | 4.4321 | 75.65 | 426.1042 | 501.7542 | 0 | 501.7542 | 0 | 0 | 15.0771 | 84.9229 | 0 | 15.0771 | 84.9229 | 0
63 | 14 | March | 8.7 | 10.711 | 1490.05 | 377.1732 | 1867.2232 | 0 | 1867.2232 | 0 | 0 | 79.8003 | 20.1997 | 0 | 79.8003 | 20.1997 | 0
63 | 15 | March | 5.7 | 7.0175 | 504.9 | 418.474 | 923.374 | 0 | 923.374 | 0 | 0 | 54.6799 | 45.3201 | 0 | 54.6799 | 45.3201 | 0
63 | 16 | March | 6.7 | 8.2487 | 761.6 | 252.4276 | 1014.0276 | 0 | 1014.0276 | 0 | 0 | 75.1064 | 24.8936 | 0 | 75.1064 | 24.8936 | 0
63 | 17 | March | 5.1 | 6.2788 | 312.8 | 70.119 | 382.919 | 0 | 382.919 | 0 | 0 | 81.6883 | 18.3117 | 0 | 81.6883 | 18.3117 | 0
63 | 18 | March | 6.2 | 7.6331 | 625.6 | 9.261 | 634.861 | 0 | 634.861 | 0 | 0 | 98.5413 | 1.4587 | 0 | 98.5413 | 1.4587 | 0
63 | 19 | March | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
63 | 20 | March | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
63 | 21 | March | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
63 | 22 | March | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
63 | 23 | March | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
63 | 24 | March | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
64 | 1 | March | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
64 | 2 | March | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
64 | 3 | March | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
64 | 4 | March | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
64 | 5 | March | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
64 | 6 | March | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
64 | 7 | March | 5.1 | 6.2788 | 312.8 | 3.969 | 316.769 | 0 | 316.769 | 0 | 0 | 98.747 | 1.253 | 0 | 98.747 | 1.253 | 0
64 | 8 | March | 4.6 | 5.6633 | 237.15 | 56.889 | 294.039 | 0 | 294.039 | 0 | 0 | 80.6526 | 19.3474 | 0 | 80.6526 | 19.3474 | 0
64 | 9 | March | 6.7 | 8.2487 | 761.6 | 279.3544 | 1040.9544 | 0 | 1040.9544 | 0 | 0 | 73.1636 | 26.8364 | 0 | 73.1636 | 26.8364 | 0
64 | 10 | March | 6.2 | 7.6331 | 625.6 | 295.2341 | 920.8341 | 0 | 920.8341 | 0 | 0 | 67.9384 | 32.0616 | 0 | 67.9384 | 32.0616 | 0
64 | 11 | March | 6.2 | 7.6331 | 625.6 | 557.5211 | 1183.1211 | 0 | 1183.1211 | 0 | 0 | 52.8771 | 47.1229 | 0 | 52.8771 | 47.1229 | 0
64 | 12 | March | 6.7 | 8.2487 | 761.6 | 625.7616 | 1387.3616 | 0 | 1387.3616 | 0 | 0 | 54.8956 | 45.1044 | 0 | 54.8956 | 45.1044 | 0
64 | 13 | March | 6.7 | 8.2487 | 761.6 | 420.9195 | 1182.5195 | 0 | 1182.5195 | 0 | 0 | 64.4049 | 35.5951 | 0 | 64.4049 | 35.5951 | 0
64 | 14 | March | 7.7 | 9.4798 | 1059.95 | 214.0941 | 1274.0441 | 0 | 1274.0441 | 0 | 0 | 83.1957 | 16.8043 | 0 | 83.1957 | 16.8043 | 0
64 | 15 | March | 7.7 | 9.4798 | 1059.95 | 170.667 | 1230.617 | 0 | 1230.617 | 0 | 0 | 86.1316 | 13.8684 | 0 | 86.1316 | 13.8684 | 0
64 | 16 | March | 7.2 | 8.8642 | 908.65 | 111.132 | 1019.782 | 0 | 1019.782 | 0 | 0 | 89.1024 | 10.8976 | 0 | 89.1024 | 10.8976 | 0
64 | 17 | March | 7.2 | 8.8642 | 908.65 | 46.305 | 954.955 | 0 | 954.955 | 0 | 0 | 95.1511 | 4.8489 | 0 | 95.1511 | 4.8489 | 0
64 | 18 | March | 6.2 | 7.6331 | 625.6 | 5.292 | 630.892 | 0 | 630.892 | 0 | 0 | 99.1612 | 0.83881 | 0 | 99.1612 | 0.83881 | 0
64 | 19 | March | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
64 | 20 | March | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
64 | 21 | March | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
64 | 22 | March | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
64 | 23 | March | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
64 | 24 | March | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
65 | 1 | March | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
65 | 2 | March | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
65 | 3 | March | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
65 | 4 | March | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
65 | 5 | March | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
65 | 6 | March | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
65 | 7 | March | 5.7 | 7.0175 | 504.9 | 3.969 | 508.869 | 0 | 508.869 | 0 | 0 | 99.22 | 0.77996 | 0 | 99.22 | 0.77996 | 0
65 | 8 | March | 6.2 | 7.6331 | 625.6 | 59.535 | 685.135 | 0 | 685.135 | 0 | 0 | 91.3105 | 8.6895 | 0 | 91.3105 | 8.6895 | 0
65 | 9 | March | 5.7 | 7.0175 | 504.9 | 134.1789 | 639.0789 | 0 | 639.0789 | 0 | 0 | 79.0043 | 20.9957 | 0 | 79.0043 | 20.9957 | 0
65 | 10 | March | 8.2 | 10.0954 | 1359.15 | 161.406 | 1520.556 | 0 | 1520.556 | 0 | 0 | 89.3851 | 10.6149 | 0 | 89.3851 | 10.6149 | 0
65 | 11 | March | 8.7 | 10.711 | 1490.05 | 209.0506 | 1699.1006 | 0 | 1699.1006 | 0 | 0 | 87.6964 | 12.3036 | 0 | 87.6964 | 12.3036 | 0
65 | 12 | March | 9.3 | 11.4496 | 1598.85 | 234.4374 | 1833.2874 | 0 | 1833.2874 | 0 | 0 | 87.2122 | 12.7878 | 0 | 87.2122 | 12.7878 | 0
65 | 13 | March | 8.2 | 10.0954 | 1359.15 | 235.5967 | 1594.7467 | 0 | 1594.7467 | 0 | 0 | 85.2267 | 14.7733 | 0 | 85.2267 | 14.7733 | 0
65 | 14 | March | 8.7 | 10.711 | 1490.05 | 214.1027 | 1704.1527 | 0 | 1704.1527 | 0 | 0 | 87.4364 | 12.5636 | 0 | 87.4364 | 12.5636 | 0
65 | 15 | March | 10.3 | 12.6808 | 1694.9 | 170.667 | 1865.567 | 0 | 1865.567 | 0 | 0 | 90.8517 | 9.1483 | 0 | 90.8517 | 9.1483 | 0
65 | 16 | March | 11.3 | 13.9119 | 1700 | 112.455 | 1812.455 | 0 | 1812.455 | 0 | 0 | 93.7954 | 6.2046 | 0 | 93.7954 | 6.2046 | 0
65 | 17 | March | 10.3 | 12.6808 | 1694.9 | 76.097 | 1770.997 | 0 | 1770.997 | 0 | 0 | 95.7032 | 4.2968 | 0 | 95.7032 | 4.2968 | 0
65 | 18 | March | 9.8 | 12.0652 | 1683.85 | 9.261 | 1693.111 | 0 | 1693.111 | 0 | 0 | 99.453 | 0.54698 | 0 | 99.453 | 0.54698 | 0
65 | 19 | March | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
65 | 20 | March | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
65 | 21 | March | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
65 | 22 | March | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
65 | 23 | March | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
65 | 24 | March | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
66 | 1 | March | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
66 | 2 | March | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
66 | 3 | March | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
66 | 4 | March | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
66 | 5 | March | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
66 | 6 | March | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
66 | 7 | March | 9.8 | 12.0652 | 1683.85 | 6.615 | 1690.465 | 0 | 1690.465 | 0 | 0 | 99.6087 | 0.39131 | 0 | 99.6087 | 0.39131 | 0
66 | 8 | March | 8.7 | 10.711 | 1490.05 | 141.1696 | 1631.2196 | 0 | 1631.2196 | 0 | 0 | 91.3458 | 8.6542 | 0 | 91.3458 | 8.6542 | 0
66 | 9 | March | 9.3 | 11.4496 | 1598.85 | 184.4721 | 1783.3221 | 0 | 1783.3221 | 0 | 0 | 89.6557 | 10.3443 | 0 | 89.6557 | 10.3443 | 0
66 | 10 | March | 9.8 | 12.0652 | 1683.85 | 710.5373 | 2394.3873 | 1 | 2000 | 394.3873 | 19.7194 | 70.3249 | 15.8075 | 55.5055 | 64.4731 | 29.6751 | 23.4218
66 | 11 | March | 10.3 | 12.6808 | 1694.9 | 791.5362 | 2486.4362 | 1 | 2000 | 486.4362 | 24.3218 | 68.1658 | 15.255 | 61.4547 | 60.4232 | 31.8342 | 28.7
66 | 12 | March | 10.8 | 13.2964 | 1698.3 | 833.524 | 2531.824 | 1 | 2000 | 531.824 | 26.5912 | 67.0781 | 15.085 | 63.8043 | 58.3238 | 32.9219 | 31.3151
66 | 13 | March | 9.8 | 12.0652 | 1683.85 | 1075.3072 | 2759.1572 | 1 | 2000 | 759.1572 | 37.9579 | 61.0277 | 15.8075 | 70.5991 | 46.2346 | 38.9723 | 45.0846
66 | 14 | March | 11.8 | 14.5275 | 1700 | 393.1672 | 2093.1672 | 1 | 2000 | 93.1672 | 4.6584 | 81.2166 | 15 | 23.6966 | 80.3416 | 18.7834 | 5.4804
66 | 15 | March | 9.8 | 12.0652 | 1683.85 | 557.4666 | 2241.3166 | 1 | 2000 | 241.3166 | 12.0658 | 75.1277 | 15.8075 | 43.2881 | 72.1267 | 24.8723 | 14.3312
66 | 16 | March | 7.7 | 9.4798 | 1059.95 | 277.291 | 1337.241 | 0 | 1337.241 | 0 | 0 | 79.2639 | 20.7361 | 0 | 79.2639 | 20.7361 | 0
66 | 17 | March | 7.7 | 9.4798 | 1059.95 | 79.4405 | 1139.3905 | 0 | 1139.3905 | 0 | 0 | 93.0278 | 6.9722 | 0 | 93.0278 | 6.9722 | 0
66 | 18 | March | 5.1 | 6.2788 | 312.8 | 15.876 | 328.676 | 0 | 328.676 | 0 | 0 | 95.1697 | 4.8303 | 0 | 95.1697 | 4.8303 | 0
66 | 19 | March | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
66 | 20 | March | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
66 | 21 | March | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
66 | 22 | March | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66 | 23 | March | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
66 | 24 | March | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 1 | March | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 2 | March | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 3 | March | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 4 | March | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 5 | March | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 6 | March | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 7 | March | 1 | 1.2311 | 0 | 7.938 | 7.938 | 0 | 7.938 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
67 | 8 | March | 1.5 | 1.8467 | 0 | 67.473 | 67.473 | 0 | 67.473 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
67 | 9 | March | 1 | 1.2311 | 0 | 186.1348 | 186.1348 | 0 | 186.1348 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
67 | 10 | March | 1 | 1.2311 | 0 | 305.9204 | 305.9204 | 0 | 305.9204 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
67 | 11 | March | 1.5 | 1.8467 | 0 | 378.0701 | 378.0701 | 0 | 378.0701 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
67 | 12 | March | 1 | 1.2311 | 0 | 422.4427 | 422.4427 | 0 | 422.4427 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
67 | 13 | March | 1.5 | 1.8467 | 0 | 420.0276 | 420.0276 | 0 | 420.0276 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
67 | 14 | March | 3.1 | 3.8165 | 0 | 844.1584 | 844.1584 | 0 | 844.1584 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
67 | 15 | March | 4.6 | 5.6633 | 237.15 | 317.0332 | 554.1832 | 0 | 554.1832 | 0 | 0 | 42.7927 | 57.2073 | 0 | 42.7927 | 57.2073 | 0
67 | 16 | March | 3.1 | 3.8165 | 0 | 203.8699 | 203.8699 | 0 | 203.8699 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
67 | 17 | March | 3.6 | 4.4321 | 75.65 | 83.421 | 159.071 | 0 | 159.071 | 0 | 0 | 47.5574 | 52.4426 | 0 | 47.5574 | 52.4426 | 0
67 | 18 | March | 3.1 | 3.8165 | 0 | 10.584 | 10.584 | 0 | 10.584 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
67 | 19 | March | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
67 | 20 | March | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 21 | March | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 22 | March | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 23 | March | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
67 | 24 | March | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | 1 | March | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
68 | 2 | March | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | 3 | March | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | 4 | March | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | 5 | March | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | 6 | March | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | 7 | March | 3.1 | 3.8165 | 0 | 7.938 | 7.938 | 0 | 7.938 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
68 | 8 | March | 4.1 | 5.0477 | 173.4 | 71.442 | 244.842 | 0 | 244.842 | 0 | 0 | 70.8212 | 29.1788 | 0 | 70.8212 | 29.1788 | 0
68 | 9 | March | 4.6 | 5.6633 | 237.15 | 190.2557 | 427.4057 | 0 | 427.4057 | 0 | 0 | 55.4859 | 44.5141 | 0 | 55.4859 | 44.5141 | 0
68 | 10 | March | 3.6 | 4.4321 | 75.65 | 309.0177 | 384.6677 | 0 | 384.6677 | 0 | 0 | 19.6663 | 80.3337 | 0 | 19.6663 | 80.3337 | 0
68 | 11 | March | 3.6 | 4.4321 | 75.65 | 382.3245 | 457.9745 | 0 | 457.9745 | 0 | 0 | 16.5184 | 83.4816 | 0 | 16.5184 | 83.4816 | 0
68 | 12 | March | 5.1 | 6.2788 | 312.8 | 248.2186 | 561.0186 | 0 | 561.0186 | 0 | 0 | 55.7557 | 44.2443 | 0 | 55.7557 | 44.2443 | 0
68 | 13 | March | 4.1 | 5.0477 | 173.4 | 446.8848 | 620.2848 | 0 | 620.2848 | 0 | 0 | 27.9549 | 72.0451 | 0 | 27.9549 | 72.0451 | 0
68 | 14 | March | 6.2 | 7.6331 | 625.6 | 224.315 | 849.915 | 0 | 849.915 | 0 | 0 | 73.6074 | 26.3926 | 0 | 73.6074 | 26.3926 | 0
68 | 15 | March | 4.1 | 5.0477 | 173.4 | 177.282 | 350.682 | 0 | 350.682 | 0 | 0 | 49.4465 | 50.5535 | 0 | 49.4465 | 50.5535 | 0
68 | 16 | March | 4.1 | 5.0477 | 173.4 | 119.07 | 292.47 | 0 | 292.47 | 0 | 0 | 59.2881 | 40.7119 | 0 | 59.2881 | 40.7119 | 0
68 | 17 | March | 2.6 | 3.201 | 0 | 52.92 | 52.92 | 0 | 52.92 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
68 | 18 | March | 2.6 | 3.201 | 0 | 11.907 | 11.907 | 0 | 11.907 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
68 | 19 | March | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | 20 | March | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | 21 | March | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | 22 | March | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | 23 | March | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
68 | 24 | March | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69 | 1 | March | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69 | 2 | March | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69 | 3 | March | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69 | 4 | March | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
69 | 5 | March | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
69 | 6 | March | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
69 | 7 | March | 8.7 | 10.711 | 1490.05 | 5.292 | 1495.342 | 0 | 1495.342 | 0 | 0 | 99.6461 | 0.3539 | 0 | 99.6461 | 0.3539 | 0
69 | 8 | March | 8.2 | 10.0954 | 1359.15 | 47.628 | 1406.778 | 0 | 1406.778 | 0 | 0 | 96.6144 | 3.3856 | 0 | 96.6144 | 3.3856 | 0
69 | 9 | March | 6.2 | 7.6331 | 625.6 | 205.0923 | 830.6923 | 0 | 830.6923 | 0 | 0 | 75.3107 | 24.6893 | 0 | 75.3107 | 24.6893 | 0
69 | 10 | March | 5.1 | 6.2788 | 312.8 | 315.7043 | 628.5043 | 0 | 628.5043 | 0 | 0 | 49.769 | 50.231 | 0 | 49.769 | 50.231 | 0
69 | 11 | March | 6.2 | 7.6331 | 625.6 | 914.2565 | 1539.8565 | 0 | 1539.8565 | 0 | 0 | 40.6272 | 59.3728 | 0 | 40.6272 | 59.3728 | 0
69 | 12 | March | 8.7 | 10.711 | 1490.05 | 1078.986 | 2569.036 | 1 | 2000 | 569.036 | 28.4518 | 58.0004 | 25.4975 | 52.738 | 46.0507 | 41.9996 | 38.1891
69 | 13 | March | 9.3 | 11.4496 | 1598.85 | 867.0878 | 2465.9378 | 1 | 2000 | 465.9378 | 23.2969 | 64.8374 | 20.0575 | 53.7359 | 56.6456 | 35.1626 | 29.1421
69 | 14 | March | 8.7 | 10.711 | 1490.05 | 410.6395 | 1900.6895 | 0 | 1900.6895 | 0 | 0 | 78.3952 | 21.6048 | 0 | 78.3952 | 21.6048 | 0
69 | 15 | March | 9.8 | 12.0652 | 1683.85 | 311.0315 | 1994.8815 | 0 | 1994.8815 | 0 | 0 | 84.4085 | 15.5915 | 0 | 84.4085 | 15.5915 | 0
69 | 16 | March | 8.2 | 10.0954 | 1359.15 | 211.5617 | 1570.7117 | 0 | 1570.7117 | 0 | 0 | 86.5308 | 13.4692 | 0 | 86.5308 | 13.4692 | 0
69 | 17 | March | 8.2 | 10.0954 | 1359.15 | 89.0896 | 1448.2396 | 0 | 1448.2396 | 0 | 0 | 93.8484 | 6.1516 | 0 | 93.8484 | 6.1516 | 0
69 | 18 | March | 9.8 | 12.0652 | 1683.85 | 13.23 | 1697.08 | 0 | 1697.08 | 0 | 0 | 99.2204 | 0.77957 | 0 | 99.2204 | 0.77957 | 0
69 | 19 | March | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
69 | 20 | March | 6.9 | 8.4949 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
69 | 21 | March | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
69 | 22 | March | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
69 | 23 | March | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
69 | 24 | March | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
70 | 1 | March | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
70 | 2 | March | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
70 | 3 | March | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
70 | 4 | March | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
70 | 5 | March | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
70 | 6 | March | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
70 | 7 | March | 5.1 | 6.2788 | 312.8 | 9.261 | 322.061 | 0 | 322.061 | 0 | 0 | 97.1245 | 2.8755 | 0 | 97.1245 | 2.8755 | 0
70 | 8 | March | 6.2 | 7.6331 | 625.6 | 82.0295 | 707.6295 | 0 | 707.6295 | 0 | 0 | 88.4078 | 11.5922 | 0 | 88.4078 | 11.5922 | 0
70 | 9 | March | 6.7 | 8.2487 | 761.6 | 116.424 | 878.024 | 0 | 878.024 | 0 | 0 | 86.7402 | 13.2598 | 0 | 86.7402 | 13.2598 | 0
70 | 10 | March | 6.7 | 8.2487 | 761.6 | 177.282 | 938.882 | 0 | 938.882 | 0 | 0 | 81.1178 | 18.8822 | 0 | 81.1178 | 18.8822 | 0
70 | 11 | March | 7.7 | 9.4798 | 1059.95 | 418.6258 | 1478.5758 | 0 | 1478.5758 | 0 | 0 | 71.6872 | 28.3128 | 0 | 71.6872 | 28.3128 | 0
70 | 12 | March | 8.2 | 10.0954 | 1359.15 | 255.024 | 1614.174 | 0 | 1614.174 | 0 | 0 | 84.201 | 15.799 | 0 | 84.201 | 15.799 | 0
70 | 13 | March | 8.2 | 10.0954 | 1359.15 | 252.9843 | 1612.1343 | 0 | 1612.1343 | 0 | 0 | 84.3075 | 15.6925 | 0 | 84.3075 | 15.6925 | 0
70 | 14 | March | 7.2 | 8.8642 | 908.65 | 229.8374 | 1138.4874 | 0 | 1138.4874 | 0 | 0 | 79.812 | 20.188 | 0 | 79.812 | 20.188 | 0
70 | 15 | March | 9.3 | 11.4496 | 1598.85 | 183.897 | 1782.747 | 0 | 1782.747 | 0 | 0 | 89.6846 | 10.3154 | 0 | 89.6846 | 10.3154 | 0
70 | 16 | March | 7.7 | 9.4798 | 1059.95 | 124.362 | 1184.312 | 0 | 1184.312 | 0 | 0 | 89.4992 | 10.5008 | 0 | 89.4992 | 10.5008 | 0
70 | 17 | March | 10.3 | 12.6808 | 1694.9 | 56.889 | 1751.789 | 0 | 1751.789 | 0 | 0 | 96.7525 | 3.2475 | 0 | 96.7525 | 3.2475 | 0
70 | 18 | March | 10.8 | 13.2964 | 1698.3 | 7.938 | 1706.238 | 0 | 1706.238 | 0 | 0 | 99.5348 | 0.46523 | 0 | 99.5348 | 0.46523 | 0
70 | 19 | March | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
70 | 20 | March | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
70 | 21 | March | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
70 | 22 | March | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
70 | 23 | March | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
70 | 24 | March | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
71 | 1 | March | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
71 | 2 | March | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71 | 3 | March | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
71 | 4 | March | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
71 | 5 | March | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
71 | 6 | March | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
71 | 7 | March | 3.1 | 3.8165 | 0 | 6.615 | 6.615 | 0 | 6.615 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
71 | 8 | March | 5.1 | 6.2788 | 312.8 | 51.597 | 364.397 | 0 | 364.397 | 0 | 0 | 85.8404 | 14.1596 | 0 | 85.8404 | 14.1596 | 0
71 | 9 | March | 4.6 | 5.6633 | 237.15 | 119.07 | 356.22 | 0 | 356.22 | 0 | 0 | 66.574 | 33.426 | 0 | 66.574 | 33.426 | 0
71 | 10 | March | 5.1 | 6.2788 | 312.8 | 179.928 | 492.728 | 0 | 492.728 | 0 | 0 | 63.4833 | 36.5167 | 0 | 63.4833 | 36.5167 | 0
71 | 11 | March | 7.7 | 9.4798 | 1059.95 | 424.4386 | 1484.3886 | 0 | 1484.3886 | 0 | 0 | 71.4065 | 28.5935 | 0 | 71.4065 | 28.5935 | 0
71 | 12 | March | 10.3 | 12.6808 | 1694.9 | 440.7676 | 2135.6676 | 1 | 2000 | 135.6676 | 6.7834 | 79.3616 | 15.255 | 30.7799 | 77.9616 | 20.6384 | 8.0045
71 | 13 | March | 6.7 | 8.2487 | 761.6 | 439.6075 | 1201.2075 | 0 | 1201.2075 | 0 | 0 | 63.4029 | 36.5971 | 0 | 63.4029 | 36.5971 | 0
71 | 14 | March | 5.7 | 7.0175 | 504.9 | 232.6735 | 737.5735 | 0 | 737.5735 | 0 | 0 | 68.4542 | 31.5458 | 0 | 68.4542 | 31.5458 | 0
71 | 15 | March | 7.7 | 9.4798 | 1059.95 | 187.866 | 1247.816 | 0 | 1247.816 | 0 | 0 | 84.9444 | 15.0556 | 0 | 84.9444 | 15.0556 | 0
71 | 16 | March | 6.2 | 7.6331 | 625.6 | 217.4469 | 843.0469 | 0 | 843.0469 | 0 | 0 | 74.207 | 25.793 | 0 | 74.207 | 25.793 | 0
71 | 17 | March | 7.2 | 8.8642 | 908.65 | 95.7315 | 1004.3815 | 0 | 1004.3815 | 0 | 0 | 90.4686 | 9.5314 | 0 | 90.4686 | 9.5314 | 0
71 | 18 | March | 5.7 | 7.0175 | 504.9 | 9.261 | 514.161 | 0 | 514.161 | 0 | 0 | 98.1988 | 1.8012 | 0 | 98.1988 | 1.8012 | 0
71 | 19 | March | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71 | 20 | March | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
71 | 21 | March | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
71 | 22 | March | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
71 | 23 | March | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
71 | 24 | March | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
72 | 1 | March | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | 2 | March | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | 3 | March | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | 4 | March | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | 5 | March | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | 6 | March | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | 7 | March | 1.5 | 1.8467 | 0 | 7.938 | 7.938 | 0 | 7.938 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
72 | 8 | March | 3.1 | 3.8165 | 0 | 55.566 | 55.566 | 0 | 55.566 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
72 | 9 | March | 3.6 | 4.4321 | 75.65 | 123.039 | 198.689 | 0 | 198.689 | 0 | 0 | 38.0746 | 61.9254 | 0 | 38.0746 | 61.9254 | 0
72 | 10 | March | 3.6 | 4.4321 | 75.65 | 183.897 | 259.547 | 0 | 259.547 | 0 | 0 | 29.1469 | 70.8531 | 0 | 29.1469 | 70.8531 | 0
72 | 11 | March | 5.1 | 6.2788 | 312.8 | 231.7079 | 544.5079 | 0 | 544.5079 | 0 | 0 | 57.4464 | 42.5536 | 0 | 57.4464 | 42.5536 | 0
72 | 12 | March | 6.7 | 8.2487 | 761.6 | 467.1798 | 1228.7798 | 0 | 1228.7798 | 0 | 0 | 61.9802 | 38.0198 | 0 | 61.9802 | 38.0198 | 0
72 | 13 | March | 6.2 | 7.6331 | 625.6 | 442.4432 | 1068.0432 | 0 | 1068.0432 | 0 | 0 | 58.5744 | 41.4256 | 0 | 58.5744 | 41.4256 | 0
72 | 14 | March | 7.2 | 8.8642 | 908.65 | 238.7125 | 1147.3625 | 0 | 1147.3625 | 0 | 0 | 79.1947 | 20.8053 | 0 | 79.1947 | 20.8053 | 0
72 | 15 | March | 6.2 | 7.6331 | 625.6 | 189.189 | 814.789 | 0 | 814.789 | 0 | 0 | 76.7806 | 23.2194 | 0 | 76.7806 | 23.2194 | 0
72 | 16 | March | 5.7 | 7.0175 | 504.9 | 129.654 | 634.554 | 0 | 634.554 | 0 | 0 | 79.5677 | 20.4323 | 0 | 79.5677 | 20.4323 | 0
72 | 17 | March | 3.6 | 4.4321 | 75.65 | 62.181 | 137.831 | 0 | 137.831 | 0 | 0 | 54.8861 | 45.1139 | 0 | 54.8861 | 45.1139 | 0
72 | 18 | March | 3.6 | 4.4321 | 75.65 | 10.584 | 86.234 | 0 | 86.234 | 0 | 0 | 87.7264 | 12.2736 | 0 | 87.7264 | 12.2736 | 0
72 | 19 | March | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | 20 | March | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | 21 | March | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | 22 | March | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | 23 | March | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | 24 | March | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | 1 | March | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | 2 | March | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | 3 | March | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | 4 | March | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | 5 | March | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | 6 | March | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | 7 | March | 1 | 1.2311 | 0 | 13.23 | 13.23 | 0 | 13.23 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
73 | 8 | March | 1.5 | 1.8467 | 0 | 109.2272 | 109.2272 | 0 | 109.2272 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
73 | 9 | March | 2.1 | 2.5854 | 0 | 223.9939 | 223.9939 | 0 | 223.9939 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
73 | 10 | March | 2.1 | 2.5854 | 0 | 349.2988 | 349.2988 | 0 | 349.2988 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
73 | 11 | March | 2.6 | 3.201 | 0 | 424.6344 | 424.6344 | 0 | 424.6344 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
73 | 12 | March | 2.6 | 3.201 | 0 | 450.5735 | 450.5735 | 0 | 450.5735 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
73 | 13 | March | 3.1 | 3.8165 | 0 | 463.9428 | 463.9428 | 0 | 463.9428 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
73 | 14 | March | 3.6 | 4.4321 | 75.65 | 407.0744 | 482.7244 | 0 | 482.7244 | 0 | 0 | 15.6715 | 84.3285 | 0 | 15.6715 | 84.3285 | 0
73 | 15 | March | 7.2 | 8.8642 | 908.65 | 329.6063 | 1238.2563 | 0 | 1238.2563 | 0 | 0 | 73.3814 | 26.6186 | 0 | 73.3814 | 26.6186 | 0
73 | 16 | March | 5.1 | 6.2788 | 312.8 | 132.3 | 445.1 | 0 | 445.1 | 0 | 0 | 70.2763 | 29.7237 | 0 | 70.2763 | 29.7237 | 0
73 | 17 | March | 5.7 | 7.0175 | 504.9 | 63.504 | 568.404 | 0 | 568.404 | 0 | 0 | 88.8277 | 11.1723 | 0 | 88.8277 | 11.1723 | 0
73 | 18 | March | 5.7 | 7.0175 | 504.9 | 10.584 | 515.484 | 0 | 515.484 | 0 | 0 | 97.9468 | 2.0532 | 0 | 97.9468 | 2.0532 | 0
73 | 19 | March | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
73 | 20 | March | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
73 | 21 | March | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
73 | 22 | March | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
73 | 23 | March | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
73 | 24 | March | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
74 | 1 | March | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
74 | 2 | March | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
74 | 3 | March | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
74 | 4 | March | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
74 | 5 | March | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
74 | 6 | March | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
74 | 7 | March | 6.7 | 8.2487 | 761.6 | 9.261 | 770.861 | 0 | 770.861 | 0 | 0 | 98.7986 | 1.2014 | 0 | 98.7986 | 1.2014 | 0
74 | 8 | March | 7.7 | 9.4798 | 1059.95 | 59.535 | 1119.485 | 0 | 1119.485 | 0 | 0 | 94.6819 | 5.3181 | 0 | 94.6819 | 5.3181 | 0
74 | 9 | March | 8.7 | 10.711 | 1490.05 | 127.008 | 1617.058 | 0 | 1617.058 | 0 | 0 | 92.1457 | 7.8543 | 0 | 92.1457 | 7.8543 | 0
74 | 10 | March | 9.3 | 11.4496 | 1598.85 | 187.866 | 1786.716 | 0 | 1786.716 | 0 | 0 | 89.4854 | 10.5146 | 0 | 89.4854 | 10.5146 | 0
74 | 11 | March | 9.8 | 12.0652 | 1683.85 | 237.0412 | 1920.8912 | 0 | 1920.8912 | 0 | 0 | 87.6598 | 12.3402 | 0 | 87.6598 | 12.3402 | 0
74 | 12 | March | 8.7 | 10.711 | 1490.05 | 262.6185 | 1752.6685 | 0 | 1752.6685 | 0 | 0 | 85.0161 | 14.9839 | 0 | 85.0161 | 14.9839 | 0
74 | 13 | March | 9.3 | 11.4496 | 1598.85 | 262.3485 | 1861.1985 | 0 | 1861.1985 | 0 | 0 | 85.9043 | 14.0957 | 0 | 85.9043 | 14.0957 | 0
74 | 14 | March | 10.3 | 12.6808 | 1694.9 | 239.1594 | 1934.0594 | 0 | 1934.0594 | 0 | 0 | 87.6343 | 12.3657 | 0 | 87.6343 | 12.3657 | 0
74 | 15 | March | 12.3 | 15.1431 | 1700 | 193.158 | 1893.158 | 0 | 1893.158 | 0 | 0 | 89.797 | 10.203 | 0 | 89.797 | 10.203 | 0
74 | 16 | March | 12.3 | 15.1431 | 1700 | 132.3 | 1832.3 | 0 | 1832.3 | 0 | 0 | 92.7796 | 7.2204 | 0 | 92.7796 | 7.2204 | 0
74 | 17 | March | 10.8 | 13.2964 | 1698.3 | 207.6988 | 1905.9988 | 0 | 1905.9988 | 0 | 0 | 89.1029 | 10.8971 | 0 | 89.1029 | 10.8971 | 0
74 | 18 | March | 12.3 | 15.1431 | 1700 | 31.752 | 1731.752 | 0 | 1731.752 | 0 | 0 | 98.1665 | 1.8335 | 0 | 98.1665 | 1.8335 | 0
74 | 19 | March | 11.8 | 14.5275 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
74 | 20 | March | 12.9 | 15.8818 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
74 | 21 | March | 12.3 | 15.1431 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
74 | 22 | March | 13.9 | 17.1129 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
74 | 23 | March | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
74 | 24 | March | 12.3 | 15.1431 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
75 | 1 | March | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
75 | 2 | March | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
75 | 3 | March | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
75 | 4 | March | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
75 | 5 | March | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
75 | 6 | March | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
75 | 7 | March | 7.2 | 8.8642 | 908.65 | 21.168 | 929.818 | 0 | 929.818 | 0 | 0 | 97.7234 | 2.2766 | 0 | 97.7234 | 2.2766 | 0
75 | 8 | March | 6.7 | 8.2487 | 761.6 | 108.5269 | 870.1269 | 0 | 870.1269 | 0 | 0 | 87.5275 | 12.4725 | 0 | 87.5275 | 12.4725 | 0
75 | 9 | March | 5.7 | 7.0175 | 504.9 | 231.4226 | 736.3226 | 0 | 736.3226 | 0 | 0 | 68.5705 | 31.4295 | 0 | 68.5705 | 31.4295 | 0
75 | 10 | March | 7.2 | 8.8642 | 908.65 | 344.0144 | 1252.6644 | 0 | 1252.6644 | 0 | 0 | 72.5374 | 27.4626 | 0 | 72.5374 | 27.4626 | 0
75 | 11 | March | 8.2 | 10.0954 | 1359.15 | 804.6825 | 2163.8325 | 1 | 2000 | 163.8325 | 8.1916 | 62.8122 | 32.0425 | 20.3599 | 59.7659 | 37.1878 | 12.054
75 | 12 | March | 10.8 | 13.2964 | 1698.3 | 271.1613 | 1969.4613 | 0 | 1969.4613 | 0 | 0 | 86.2317 | 13.7683 | 0 | 86.2317 | 13.7683 | 0
75 | 13 | March | 12.3 | 15.1431 | 1700 | 269.198 | 1969.198 | 0 | 1969.198 | 0 | 0 | 86.3296 | 13.6704 | 0 | 86.3296 | 13.6704 | 0
75 | 14 | March | 9.8 | 12.0652 | 1683.85 | 626.4539 | 2310.3039 | 1 | 2000 | 310.3039 | 15.5152 | 72.8844 | 15.8075 | 49.5334 | 68.6773 | 27.1156 | 18.4282
75 | 15 | March | 9.8 | 12.0652 | 1683.85 | 345.9136 | 2029.7636 | 1 | 2000 | 29.7636 | 1.4882 | 82.9579 | 15.8075 | 8.6043 | 82.7043 | 17.0421 | 1.7676
75 | 16 | March | 9.8 | 12.0652 | 1683.85 | 136.269 | 1820.119 | 0 | 1820.119 | 0 | 0 | 92.5132 | 7.4868 | 0 | 92.5132 | 7.4868 | 0
75 | 17 | March | 8.2 | 10.0954 | 1359.15 | 67.473 | 1426.623 | 0 | 1426.623 | 0 | 0 | 95.2704 | 4.7296 | 0 | 95.2704 | 4.7296 | 0
75 | 18 | March | 9.8 | 12.0652 | 1683.85 | 11.907 | 1695.757 | 0 | 1695.757 | 0 | 0 | 99.2978 | 0.70216 | 0 | 99.2978 | 0.70216 | 0
75 | 19 | March | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
75 | 20 | March | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
75 | 21 | March | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
75 | 22 | March | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
75 | 23 | March | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
75 | 24 | March | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76 | 1 | March | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
76 | 2 | March | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
76 | 3 | March | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
76 | 4 | March | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
76 | 5 | March | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
76 | 6 | March | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
76 | 7 | March | 3.6 | 4.4321 | 75.65 | 22.491 | 98.141 | 0 | 98.141 | 0 | 0 | 77.083 | 22.917 | 0 | 77.083 | 22.917 | 0
76 | 8 | March | 4.6 | 5.6633 | 237.15 | 275.6509 | 512.8009 | 0 | 512.8009 | 0 | 0 | 46.246 | 53.754 | 0 | 46.246 | 53.754 | 0
76 | 9 | March | 3.6 | 4.4321 | 75.65 | 506.2818 | 581.9318 | 0 | 581.9318 | 0 | 0 | 12.9998 | 87.0002 | 0 | 12.9998 | 87.0002 | 0
76 | 10 | March | 6.2 | 7.6331 | 625.6 | 907.6764 | 1533.2764 | 0 | 1533.2764 | 0 | 0 | 40.8015 | 59.1985 | 0 | 40.8015 | 59.1985 | 0
76 | 11 | March | 4.1 | 5.0477 | 173.4 | 1155.5472 | 1328.9472 | 0 | 1328.9472 | 0 | 0 | 13.0479 | 86.9521 | 0 | 13.0479 | 86.9521 | 0
76 | 12 | March | 4.1 | 5.0477 | 173.4 | 916.8282 | 1090.2282 | 0 | 1090.2282 | 0 | 0 | 15.9049 | 84.0951 | 0 | 15.9049 | 84.0951 | 0
76 | 13 | March | 4.1 | 5.0477 | 173.4 | 933.371 | 1106.771 | 0 | 1106.771 | 0 | 0 | 15.6672 | 84.3328 | 0 | 15.6672 | 84.3328 | 0
76 | 14 | March | 1 | 1.2311 | 0 | 604.7918 | 604.7918 | 0 | 604.7918 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
76 | 15 | March | 3.6 | 4.4321 | 75.65 | 467.6042 | 543.2542 | 0 | 543.2542 | 0 | 0 | 13.9253 | 86.0747 | 0 | 13.9253 | 86.0747 | 0
76 | 16 | March | 3.1 | 3.8165 | 0 | 320.2505 | 320.2505 | 0 | 320.2505 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
76 | 17 | March | 1.5 | 1.8467 | 0 | 112.0043 | 112.0043 | 0 | 112.0043 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
76 | 18 | March | 1 | 1.2311 | 0 | 19.845 | 19.845 | 0 | 19.845 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
76 | 19 | March | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76 | 20 | March | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76 | 21 | March | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76 | 22 | March | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76 | 23 | March | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76 | 24 | March | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 | 1 | March | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 | 2 | March | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 | 3 | March | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 | 4 | March | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 | 5 | March | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 | 6 | March | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 | 7 | March | 3.1 | 3.8165 | 0 | 39.7927 | 39.7927 | 0 | 39.7927 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
77 | 8 | March | 3.1 | 3.8165 | 0 | 285.2244 | 285.2244 | 0 | 285.2244 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
77 | 9 | March | 5.1 | 6.2788 | 312.8 | 657.8002 | 970.6002 | 0 | 970.6002 | 0 | 0 | 32.2275 | 67.7725 | 0 | 32.2275 | 67.7725 | 0
77 | 10 | March | 4.6 | 5.6633 | 237.15 | 969.0192 | 1206.1692 | 0 | 1206.1692 | 0 | 0 | 19.6614 | 80.3386 | 0 | 19.6614 | 80.3386 | 0
77 | 11 | March | 5.1 | 6.2788 | 312.8 | 855.8514 | 1168.6514 | 0 | 1168.6514 | 0 | 0 | 26.7659 | 73.2341 | 0 | 26.7659 | 73.2341 | 0
77 | 12 | March | 5.1 | 6.2788 | 312.8 | 1104.2233 | 1417.0233 | 0 | 1417.0233 | 0 | 0 | 22.0744 | 77.9256 | 0 | 22.0744 | 77.9256 | 0
77 | 13 | March | 6.2 | 7.6331 | 625.6 | 710.2506 | 1335.8506 | 0 | 1335.8506 | 0 | 0 | 46.8316 | 53.1684 | 0 | 46.8316 | 53.1684 | 0
77 | 14 | March | 6.2 | 7.6331 | 625.6 | 440.2461 | 1065.8461 | 0 | 1065.8461 | 0 | 0 | 58.6952 | 41.3048 | 0 | 58.6952 | 41.3048 | 0
77 | 15 | March | 6.2 | 7.6331 | 625.6 | 352.1295 | 977.7295 | 0 | 977.7295 | 0 | 0 | 63.985 | 36.015 | 0 | 63.985 | 36.015 | 0
77 | 16 | March | 6.7 | 8.2487 | 761.6 | 141.561 | 903.161 | 0 | 903.161 | 0 | 0 | 84.3261 | 15.6739 | 0 | 84.3261 | 15.6739 | 0
77 | 17 | March | 6.7 | 8.2487 | 761.6 | 71.442 | 833.042 | 0 | 833.042 | 0 | 0 | 91.424 | 8.576 | 0 | 91.424 | 8.576 | 0
77 | 18 | March | 6.7 | 8.2487 | 761.6 | 13.23 | 774.83 | 0 | 774.83 | 0 | 0 | 98.2925 | 1.7075 | 0 | 98.2925 | 1.7075 | 0
77 | 19 | March | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
77 | 20 | March | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
77 | 21 | March | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
77 | 22 | March | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
77 | 23 | March | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
77 | 24 | March | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
78 | 1 | March | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
78 | 2 | March | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
78 | 3 | March | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
78 | 4 | March | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
78 | 5 | March | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
78 | 6 | March | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
78 | 7 | March | 5.7 | 7.0175 | 504.9 | 13.23 | 518.13 | 0 | 518.13 | 0 | 0 | 97.4466 | 2.5534 | 0 | 97.4466 | 2.5534 | 0
78 | 8 | March | 5.7 | 7.0175 | 504.9 | 70.119 | 575.019 | 0 | 575.019 | 0 | 0 | 87.8058 | 12.1942 | 0 | 87.8058 | 12.1942 | 0
78 | 9 | March | 4.6 | 5.6633 | 237.15 | 138.915 | 376.065 | 0 | 376.065 | 0 | 0 | 63.0609 | 36.9391 | 0 | 63.0609 | 36.9391 | 0
78 | 10 | March | 6.2 | 7.6331 | 625.6 | 199.773 | 825.373 | 0 | 825.373 | 0 | 0 | 75.796 | 24.204 | 0 | 75.796 | 24.204 | 0
78 | 11 | March | 6.7 | 8.2487 | 761.6 | 449.9044 | 1211.5044 | 0 | 1211.5044 | 0 | 0 | 62.864 | 37.136 | 0 | 62.864 | 37.136 | 0
78 | 12 | March | 6.7 | 8.2487 | 761.6 | 274.8923 | 1036.4923 | 0 | 1036.4923 | 0 | 0 | 73.4786 | 26.5214 | 0 | 73.4786 | 26.5214 | 0
78 | 13 | March | 7.2 | 8.8642 | 908.65 | 274.598 | 1183.248 | 0 | 1183.248 | 0 | 0 | 76.7929 | 23.2071 | 0 | 76.7929 | 23.2071 | 0
78 | 14 | March | 7.2 | 8.8642 | 908.65 | 440.4183 | 1349.0683 | 0 | 1349.0683 | 0 | 0 | 67.3539 | 32.6461 | 0 | 67.3539 | 32.6461 | 0
78 | 15 | March | 7.7 | 9.4798 | 1059.95 | 203.1577 | 1263.1077 | 0 | 1263.1077 | 0 | 0 | 83.916 | 16.084 | 0 | 83.916 | 16.084 | 0
78 | 16 | March | 7.2 | 8.8642 | 908.65 | 141.561 | 1050.211 | 0 | 1050.211 | 0 | 0 | 86.5207 | 13.4793 | 0 | 86.5207 | 13.4793 | 0
78 | 17 | March | 7.7 | 9.4798 | 1059.95 | 72.765 | 1132.715 | 0 | 1132.715 | 0 | 0 | 93.5761 | 6.4239 | 0 | 93.5761 | 6.4239 | 0
78 | 18 | March | 7.2 | 8.8642 | 908.65 | 22.491 | 931.141 | 0 | 931.141 | 0 | 0 | 97.5846 | 2.4154 | 0 | 97.5846 | 2.4154 | 0
78 | 19 | March | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
78 | 20 | March | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
78 | 21 | March | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
78 | 22 | March | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
78 | 23 | March | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
78 | 24 | March | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
79 | 1 | March | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
79 | 2 | March | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
79 | 3 | March | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
79 | 4 | March | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
79 | 5 | March | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
79 | 6 | March | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
79 | 7 | March | 7.2 | 8.8642 | 908.65 | 49.1096 | 957.7596 | 0 | 957.7596 | 0 | 0 | 94.8725 | 5.1275 | 0 | 94.8725 | 5.1275 | 0
79 | 8 | March | 7.7 | 9.4798 | 1059.95 | 312.5657 | 1372.5157 | 0 | 1372.5157 | 0 | 0 | 77.2268 | 22.7732 | 0 | 77.2268 | 22.7732 | 0
79 | 9 | March | 6.2 | 7.6331 | 625.6 | 664.8234 | 1290.4234 | 0 | 1290.4234 | 0 | 0 | 48.4802 | 51.5198 | 0 | 48.4802 | 51.5198 | 0
79 | 10 | March | 6.7 | 8.2487 | 761.6 | 1005.5988 | 1767.1988 | 0 | 1767.1988 | 0 | 0 | 43.0965 | 56.9035 | 0 | 43.0965 | 56.9035 | 0
79 | 11 | March | 6.2 | 7.6331 | 625.6 | 854.9035 | 1480.5035 | 0 | 1480.5035 | 0 | 0 | 42.2559 | 57.7441 | 0 | 42.2559 | 57.7441 | 0
79 | 12 | March | 5.1 | 6.2788 | 312.8 | 949.5669 | 1262.3669 | 0 | 1262.3669 | 0 | 0 | 24.7789 | 75.2211 | 0 | 24.7789 | 75.2211 | 0
79 | 13 | March | 3.6 | 4.4321 | 75.65 | 499.9222 | 575.5722 | 0 | 575.5722 | 0 | 0 | 13.1434 | 86.8566 | 0 | 13.1434 | 86.8566 | 0
79 | 14 | March | 3.1 | 3.8165 | 0 | 426.8816 | 426.8816 | 0 | 426.8816 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
79 | 15 | March | 4.6 | 5.6633 | 237.15 | 348.3296 | 585.4796 | 0 | 585.4796 | 0 | 0 | 40.5053 | 59.4947 | 0 | 40.5053 | 59.4947 | 0
79 | 16 | March | 6.2 | 7.6331 | 625.6 | 144.207 | 769.807 | 0 | 769.807 | 0 | 0 | 81.2671 | 18.7329 | 0 | 81.2671 | 18.7329 | 0
79 | 17 | March | 4.6 | 5.6633 | 237.15 | 75.411 | 312.561 | 0 | 312.561 | 0 | 0 | 75.8732 | 24.1268 | 0 | 75.8732 | 24.1268 | 0
79 | 18 | March | 3.6 | 4.4321 | 75.65 | 14.553 | 90.203 | 0 | 90.203 | 0 | 0 | 83.8664 | 16.1336 | 0 | 83.8664 | 16.1336 | 0
79 | 19 | March | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
79 | 20 | March | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
79 | 21 | March | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
79 | 22 | March | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
79 | 23 | March | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
79 | 24 | March | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
80 | 1 | March | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
80 | 2 | March | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
80 | 3 | March | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
80 | 4 | March | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
80 | 5 | March | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
80 | 6 | March | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
80 | 7 | March | 4.6 | 5.6633 | 237.15 | 14.553 | 251.703 | 0 | 251.703 | 0 | 0 | 94.2182 | 5.7818 | 0 | 94.2182 | 5.7818 | 0
80 | 8 | March | 4.1 | 5.0477 | 173.4 | 75.411 | 248.811 | 0 | 248.811 | 0 | 0 | 69.6915 | 30.3085 | 0 | 69.6915 | 30.3085 | 0
80 | 9 | March | 4.1 | 5.0477 | 173.4 | 145.53 | 318.93 | 0 | 318.93 | 0 | 0 | 54.3693 | 45.6307 | 0 | 54.3693 | 45.6307 | 0
80 | 10 | March | 4.6 | 5.6633 | 237.15 | 381.2122 | 618.3622 | 0 | 618.3622 | 0 | 0 | 38.3513 | 61.6487 | 0 | 38.3513 | 61.6487 | 0
80 | 11 | March | 3.6 | 4.4321 | 75.65 | 437.1695 | 512.8195 | 0 | 512.8195 | 0 | 0 | 14.7518 | 85.2482 | 0 | 14.7518 | 85.2482 | 0
80 | 12 | March | 3.6 | 4.4321 | 75.65 | 280.2537 | 355.9037 | 0 | 355.9037 | 0 | 0 | 21.2557 | 78.7443 | 0 | 21.2557 | 78.7443 | 0
80 | 13 | March | 4.6 | 5.6633 | 237.15 | 504.2928 | 741.4428 | 0 | 741.4428 | 0 | 0 | 31.9849 | 68.0151 | 0 | 31.9849 | 68.0151 | 0
80 | 14 | March | 2.1 | 2.5854 | 0 | 431.0255 | 431.0255 | 0 | 431.0255 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
80 | 15 | March | 4.1 | 5.0477 | 173.4 | 209.4979 | 382.8979 | 0 | 382.8979 | 0 | 0 | 45.2862 | 54.7138 | 0 | 45.2862 | 54.7138 | 0
80 | 16 | March | 4.1 | 5.0477 | 173.4 | 248.3954 | 421.7954 | 0 | 421.7954 | 0 | 0 | 41.11 | 58.89 | 0 | 41.11 | 58.89 | 0
80 | 17 | March | 2.6 | 3.201 | 0 | 123.8297 | 123.8297 | 0 | 123.8297 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
80 | 18 | March | 1.8 | 2.2161 | 0 | 25.137 | 25.137 | 0 | 25.137 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
80 | 19 | March | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80 | 20 | March | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
80 | 21 | March | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
80 | 22 | March | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
80 | 23 | March | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
80 | 24 | March | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
81 | 1 | March | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
81 | 2 | March | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
81 | 3 | March | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
81 | 4 | March | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
81 | 5 | March | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
81 | 6 | March | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
81 | 7 | March | 4.1 | 5.0477 | 173.4 | 57.1003 | 230.5003 | 0 | 230.5003 | 0 | 0 | 75.2277 | 24.7723 | 0 | 75.2277 | 24.7723 | 0
81 | 8 | March | 4.6 | 5.6633 | 237.15 | 351.476 | 588.626 | 0 | 588.626 | 0 | 0 | 40.2887 | 59.7113 | 0 | 40.2887 | 59.7113 | 0
81 | 9 | March | 5.1 | 6.2788 | 312.8 | 716.9065 | 1029.7065 | 0 | 1029.7065 | 0 | 0 | 30.3776 | 69.6224 | 0 | 30.3776 | 69.6224 | 0
81 | 10 | March | 3.6 | 4.4321 | 75.65 | 991.21 | 1066.86 | 0 | 1066.86 | 0 | 0 | 7.0909 | 92.9091 | 0 | 7.0909 | 92.9091 | 0
81 | 11 | March | 3.1 | 3.8165 | 0 | 1225.7718 | 1225.7718 | 0 | 1225.7718 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
81 | 12 | March | 4.6 | 5.6633 | 237.15 | 929.2966 | 1166.4466 | 0 | 1166.4466 | 0 | 0 | 20.331 | 79.669 | 0 | 20.331 | 79.669 | 0
81 | 13 | March | 4.1 | 5.0477 | 173.4 | 1087.0527 | 1260.4527 | 0 | 1260.4527 | 0 | 0 | 13.757 | 86.243 | 0 | 13.757 | 86.243 | 0
81 | 14 | March | 3.1 | 3.8165 | 0 | 1070.4446 | 1070.4446 | 0 | 1070.4446 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
81 | 15 | March | 2.1 | 2.5854 | 0 | 522.4789 | 522.4789 | 0 | 522.4789 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
81 | 16 | March | 4.6 | 5.6633 | 237.15 | 252.6617 | 489.8117 | 0 | 489.8117 | 0 | 0 | 48.4166 | 51.5834 | 0 | 48.4166 | 51.5834 | 0
81 | 17 | March | 6.7 | 8.2487 | 761.6 | 126.4961 | 888.0961 | 0 | 888.0961 | 0 | 0 | 85.7565 | 14.2435 | 0 | 85.7565 | 14.2435 | 0
81 | 18 | March | 2.6 | 3.201 | 0 | 26.46 | 26.46 | 0 | 26.46 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
81 | 19 | March | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
81 | 20 | March | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
81 | 21 | March | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
81 | 22 | March | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
81 | 23 | March | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
81 | 24 | March | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
82 | 1 | March | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
82 | 2 | March | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
82 | 3 | March | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
82 | 4 | March | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
82 | 5 | March | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
82 | 6 | March | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
82 | 7 | March | 7.7 | 9.4798 | 1059.95 | 37.044 | 1096.994 | 0 | 1096.994 | 0 | 0 | 96.6231 | 3.3769 | 0 | 96.6231 | 3.3769 | 0
82 | 8 | March | 7.7 | 9.4798 | 1059.95 | 135.3698 | 1195.3198 | 0 | 1195.3198 | 0 | 0 | 88.675 | 11.325 | 0 | 88.675 | 11.325 | 0
82 | 9 | March | 10.8 | 13.2964 | 1698.3 | 269.1435 | 1967.4435 | 0 | 1967.4435 | 0 | 0 | 86.3201 | 13.6799 | 0 | 86.3201 | 13.6799 | 0
82 | 10 | March | 5.1 | 6.2788 | 312.8 | 371.8172 | 684.6172 | 0 | 684.6172 | 0 | 0 | 45.6898 | 54.3102 | 0 | 45.6898 | 54.3102 | 0
82 | 11 | March | 8.7 | 10.711 | 1490.05 | 479.191 | 1969.241 | 0 | 1969.241 | 0 | 0 | 75.6662 | 24.3338 | 0 | 75.6662 | 24.3338 | 0
82 | 12 | March | 6.7 | 8.2487 | 761.6 | 517.6311 | 1279.2311 | 0 | 1279.2311 | 0 | 0 | 59.5358 | 40.4642 | 0 | 59.5358 | 40.4642 | 0
82 | 13 | March | 6.2 | 7.6331 | 625.6 | 511.2037 | 1136.8037 | 0 | 1136.8037 | 0 | 0 | 55.0315 | 44.9685 | 0 | 55.0315 | 44.9685 | 0
82 | 14 | March | 6.2 | 7.6331 | 625.6 | 818.4278 | 1444.0278 | 0 | 1444.0278 | 0 | 0 | 43.3233 | 56.6767 | 0 | 43.3233 | 56.6767 | 0
82 | 15 | March | 7.7 | 9.4798 | 1059.95 | 520.9863 | 1580.9363 | 0 | 1580.9363 | 0 | 0 | 67.0457 | 32.9543 | 0 | 67.0457 | 32.9543 | 0
82 | 16 | March | 7.7 | 9.4798 | 1059.95 | 345.7711 | 1405.7211 | 0 | 1405.7211 | 0 | 0 | 75.4026 | 24.5974 | 0 | 75.4026 | 24.5974 | 0
82 | 17 | March | 8.2 | 10.0954 | 1359.15 | 171.5337 | 1530.6837 | 0 | 1530.6837 | 0 | 0 | 88.7937 | 11.2063 | 0 | 88.7937 | 11.2063 | 0
82 | 18 | March | 8.2 | 10.0954 | 1359.15 | 46.5183 | 1405.6683 | 0 | 1405.6683 | 0 | 0 | 96.6907 | 3.3093 | 0 | 96.6907 | 3.3093 | 0
82 | 19 | March | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
82 | 20 | March | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
82 | 21 | March | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
82 | 22 | March | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
82 | 23 | March | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
82 | 24 | March | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
83 | 1 | March | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
83 | 2 | March | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
83 | 3 | March | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
83 | 4 | March | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
83 | 5 | March | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
83 | 6 | March | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
83 | 7 | March | 6.7 | 8.2487 | 761.6 | 31.752 | 793.352 | 0 | 793.352 | 0 | 0 | 95.9977 | 4.0023 | 0 | 95.9977 | 4.0023 | 0
83 | 8 | March | 8.7 | 10.711 | 1490.05 | 83.349 | 1573.399 | 0 | 1573.399 | 0 | 0 | 94.7026 | 5.2974 | 0 | 94.7026 | 5.2974 | 0
83 | 9 | March | 9.3 | 11.4496 | 1598.85 | 153.468 | 1752.318 | 0 | 1752.318 | 0 | 0 | 91.242 | 8.758 | 0 | 91.242 | 8.758 | 0
83 | 10 | March | 9.8 | 12.0652 | 1683.85 | 216.8786 | 1900.7286 | 0 | 1900.7286 | 0 | 0 | 88.5897 | 11.4103 | 0 | 88.5897 | 11.4103 | 0
83 | 11 | March | 12.9 | 15.8818 | 1700 | 724.4636 | 2424.4636 | 1 | 2000 | 424.4636 | 21.2232 | 70.1186 | 15 | 58.5901 | 63.7768 | 29.8814 | 24.9684
83 | 12 | March | 13.4 | 16.4973 | 1700 | 766.4268 | 2466.4268 | 1 | 2000 | 466.4268 | 23.3213 | 68.9256 | 15 | 60.8573 | 61.6787 | 31.0744 | 27.4369
83 | 13 | March | 18 | 22.1606 | 1700 | 687.1374 | 2387.1374 | 1 | 2000 | 387.1374 | 19.3569 | 71.215 | 15 | 56.3406 | 65.6431 | 28.785 | 22.7728
83 | 14 | March | 12.3 | 15.1431 | 1700 | 466.7946 | 2166.7946 | 1 | 2000 | 166.7946 | 8.3397 | 78.4569 | 15 | 35.7319 | 76.6603 | 21.5431 | 9.8114
83 | 15 | March | 13.4 | 16.4973 | 1700 | 376.5978 | 2076.5978 | 1 | 2000 | 76.5978 | 3.8299 | 81.8647 | 15 | 20.3394 | 81.1701 | 18.1353 | 4.5058
83 | 16 | March | 13.9 | 17.1129 | 1700 | 263.2795 | 1963.2795 | 0 | 1963.2795 | 0 | 0 | 86.5898 | 13.4102 | 0 | 86.5898 | 13.4102 | 0
83 | 17 | March | 13.9 | 17.1129 | 1700 | 176.4496 | 1876.4496 | 0 | 1876.4496 | 0 | 0 | 90.5966 | 9.4034 | 0 | 90.5966 | 9.4034 | 0
83 | 18 | March | 15.4 | 18.9596 | 1700 | 19.845 | 1719.845 | 0 | 1719.845 | 0 | 0 | 98.8461 | 1.1539 | 0 | 98.8461 | 1.1539 | 0
83 | 19 | March | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
83 | 20 | March | 9 | 11.0803 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
83 | 21 | March | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
83 | 22 | March | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
83 | 23 | March | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
83 | 24 | March | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
84 | 1 | March | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
84 | 2 | March | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
84 | 3 | March | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
84 | 4 | March | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
84 | 5 | March | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
84 | 6 | March | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
84 | 7 | March | 3.1 | 3.8165 | 0 | 22.491 | 22.491 | 0 | 22.491 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
84 | 8 | March | 4.6 | 5.6633 | 237.15 | 85.995 | 323.145 | 0 | 323.145 | 0 | 0 | 73.3881 | 26.6119 | 0 | 73.3881 | 26.6119 | 0
84 | 9 | March | 3.6 | 4.4321 | 75.65 | 157.437 | 233.087 | 0 | 233.087 | 0 | 0 | 32.4557 | 67.5443 | 0 | 32.4557 | 67.5443 | 0
84 | 10 | March | 5.1 | 6.2788 | 312.8 | 222.139 | 534.939 | 0 | 534.939 | 0 | 0 | 58.474 | 41.526 | 0 | 58.474 | 41.526 | 0
84 | 11 | March | 5.7 | 7.0175 | 504.9 | 270.8319 | 775.7319 | 0 | 775.7319 | 0 | 0 | 65.0869 | 34.9131 | 0 | 65.0869 | 34.9131 | 0
84 | 12 | March | 6.7 | 8.2487 | 761.6 | 529.9669 | 1291.5669 | 0 | 1291.5669 | 0 | 0 | 58.9671 | 41.0329 | 0 | 58.9671 | 41.0329 | 0
84 | 13 | March | 7.2 | 8.8642 | 908.65 | 1073.4248 | 1982.0748 | 0 | 1982.0748 | 0 | 0 | 45.8434 | 54.1566 | 0 | 45.8434 | 54.1566 | 0
84 | 14 | March | 8.2 | 10.0954 | 1359.15 | 1005.0442 | 2364.1942 | 1 | 2000 | 364.1942 | 18.2097 | 57.4889 | 32.0425 | 36.2366 | 49.7478 | 42.5111 | 26.7957
84 | 15 | March | 10 | 12.3114 | 1683.85 | 752.4745 | 2436.3245 | 1 | 2000 | 436.3245 | 21.8162 | 69.1144 | 15.8075 | 57.9853 | 62.3763 | 30.8856 | 25.9123
84 | 16 | March | 11.1 | 13.6657 | 1700 | 473.7508 | 2173.7508 | 1 | 2000 | 173.7508 | 8.6875 | 78.2058 | 15 | 36.6756 | 76.3125 | 21.7942 | 10.2206
84 | 17 | March | 11.8 | 14.5275 | 1700 | 239.5123 | 1939.5123 | 0 | 1939.5123 | 0 | 0 | 87.6509 | 12.3491 | 0 | 87.6509 | 12.3491 | 0
84 | 18 | March | 14 | 17.236 | 1700 | 42.336 | 1742.336 | 0 | 1742.336 | 0 | 0 | 97.5702 | 2.4298 | 0 | 97.5702 | 2.4298 | 0
84 | 19 | March | 9.5 | 11.6959 | 1658.35 | 1.323 | 1659.673 | 0 | 1659.673 | 0 | 0 | 99.9203 | 0.079714 | 0 | 99.9203 | 0.079714 | 0
84 | 20 | March | 8.9 | 10.9572 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
84 | 21 | March | 8.3 | 10.2185 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
84 | 22 | March | 12.1 | 14.8968 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
84 | 23 | March | 10.6 | 13.0501 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
84 | 24 | March | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
85 | 1 | March | 7.4 | 9.1105 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
85 | 2 | March | 9.7 | 11.9421 | 1658.35 | 0 | 1658.35 | 0 | 1658.35 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
85 | 3 | March | 9.9 | 12.1883 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
85 | 4 | March | 9.7 | 11.9421 | 1658.35 | 0 | 1658.35 | 0 | 1658.35 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
85 | 5 | March | 8.8 | 10.8341 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
85 | 6 | March | 8 | 9.8492 | 1213.8 | 0 | 1213.8 | 0 | 1213.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
85 | 7 | March | 7.2 | 8.8642 | 908.65 | 23.814 | 932.464 | 0 | 932.464 | 0 | 0 | 97.4461 | 2.5539 | 0 | 97.4461 | 2.5539 | 0
85 | 8 | March | 8.9 | 10.9572 | 1490.05 | 89.964 | 1580.014 | 0 | 1580.014 | 0 | 0 | 94.3061 | 5.6939 | 0 | 94.3061 | 5.6939 | 0
85 | 9 | March | 8.1 | 9.9723 | 1213.8 | 161.406 | 1375.206 | 0 | 1375.206 | 0 | 0 | 88.2631 | 11.7369 | 0 | 88.2631 | 11.7369 | 0
85 | 10 | March | 9.9 | 12.1883 | 1683.85 | 226.123 | 1909.973 | 0 | 1909.973 | 0 | 0 | 88.1609 | 11.8391 | 0 | 88.1609 | 11.8391 | 0
85 | 11 | March | 10.7 | 13.1732 | 1698.3 | 271.6506 | 1969.9506 | 0 | 1969.9506 | 0 | 0 | 86.2103 | 13.7897 | 0 | 86.2103 | 13.7897 | 0
85 | 12 | March | 11.9 | 14.6506 | 1700 | 297.1422 | 1997.1422 | 0 | 1997.1422 | 0 | 0 | 85.1216 | 14.8784 | 0 | 85.1216 | 14.8784 | 0
85 | 13 | March | 12.6 | 15.5124 | 1700 | 388.1759 | 2088.1759 | 1 | 2000 | 88.1759 | 4.4088 | 81.4108 | 15 | 22.7155 | 80.5912 | 18.5892 | 5.1868
85 | 14 | March | 13.8 | 16.9898 | 1700 | 310.6278 | 2010.6278 | 1 | 2000 | 10.6278 | 0.53139 | 84.5507 | 15 | 3.4214 | 84.4686 | 15.4493 | 0.62516
85 | 15 | March | 15.1 | 18.5903 | 1700 | 223.3141 | 1923.3141 | 0 | 1923.3141 | 0 | 0 | 88.3891 | 11.6109 | 0 | 88.3891 | 11.6109 | 0
85 | 16 | March | 15.8 | 19.4521 | 1700 | 160.083 | 1860.083 | 0 | 1860.083 | 0 | 0 | 91.3938 | 8.6062 | 0 | 91.3938 | 8.6062 | 0
85 | 17 | March | 16.1 | 19.8214 | 1700 | 111.132 | 1811.132 | 0 | 1811.132 | 0 | 0 | 93.8639 | 6.1361 | 0 | 93.8639 | 6.1361 | 0
85 | 18 | March | 17.8 | 21.9144 | 1700 | 22.491 | 1722.491 | 0 | 1722.491 | 0 | 0 | 98.6943 | 1.3057 | 0 | 98.6943 | 1.3057 | 0
85 | 19 | March | 12.9 | 15.8818 | 1700 | 1.323 | 1701.323 | 0 | 1701.323 | 0 | 0 | 99.9222 | 0.077763 | 0 | 99.9222 | 0.077763 | 0
85 | 20 | March | 11.8 | 14.5275 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
85 | 21 | March | 10.7 | 13.1732 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
85 | 22 | March | 14 | 17.236 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
85 | 23 | March | 12.2 | 15.02 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
85 | 24 | March | 10.4 | 12.8039 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
86 | 1 | March | 8.5 | 10.4647 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
86 | 2 | March | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
86 | 3 | March | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
86 | 4 | March | 9.2 | 11.3265 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
86 | 5 | March | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
86 | 6 | March | 10.3 | 12.6808 | 1694.9 | 1.323 | 1696.223 | 0 | 1696.223 | 0 | 0 | 99.922 | 0.077997 | 0 | 99.922 | 0.077997 | 0
86 | 7 | March | 8.2 | 10.0954 | 1359.15 | 41.013 | 1400.163 | 0 | 1400.163 | 0 | 0 | 97.0708 | 2.9292 | 0 | 97.0708 | 2.9292 | 0
86 | 8 | March | 10.3 | 12.6808 | 1694.9 | 92.61 | 1787.51 | 0 | 1787.51 | 0 | 0 | 94.819 | 5.181 | 0 | 94.819 | 5.181 | 0
86 | 9 | March | 10.1 | 12.4346 | 1683.85 | 204.0178 | 1887.8678 | 0 | 1887.8678 | 0 | 0 | 89.1932 | 10.8068 | 0 | 89.1932 | 10.8068 | 0
86 | 10 | March | 10 | 12.3114 | 1683.85 | 325.1407 | 2008.9907 | 1 | 2000 | 8.9907 | 0.44953 | 83.8157 | 15.8075 | 2.7652 | 83.743 | 16.1843 | 0.53393
86 | 11 | March | 9.8 | 12.0652 | 1683.85 | 479.2601 | 2163.1101 | 1 | 2000 | 163.1101 | 8.1555 | 77.8439 | 15.8075 | 34.0337 | 76.037 | 22.1561 | 9.6867
86 | 12 | March | 9.3 | 11.4496 | 1598.85 | 589.5081 | 2188.3581 | 1 | 2000 | 188.3581 | 9.4179 | 73.0616 | 20.0575 | 31.9517 | 70.5246 | 26.9384 | 11.7808
86 | 13 | March | 8.7 | 10.711 | 1490.05 | 651.983 | 2142.033 | 1 | 2000 | 142.033 | 7.1016 | 69.5624 | 25.4975 | 21.7848 | 67.4009 | 30.4376 | 9.5321
86 | 14 | March | 8.2 | 10.0954 | 1359.15 | 686.0954 | 2045.2454 | 1 | 2000 | 45.2454 | 2.2623 | 66.4541 | 32.0425 | 6.5946 | 65.6952 | 33.5459 | 3.329
86 | 15 | March | 7.2 | 8.8642 | 908.65 | 778.3087 | 1686.9587 | 0 | 1686.9587 | 0 | 0 | 53.8632 | 46.1368 | 0 | 53.8632 | 46.1368 | 0
86 | 16 | March | 6.2 | 7.6331 | 625.6 | 548.646 | 1174.246 | 0 | 1174.246 | 0 | 0 | 53.2767 | 46.7233 | 0 | 53.2767 | 46.7233 | 0
86 | 17 | March | 5.1 | 6.2788 | 312.8 | 223.1579 | 535.9579 | 0 | 535.9579 | 0 | 0 | 58.3628 | 41.6372 | 0 | 58.3628 | 41.6372 | 0
86 | 18 | March | 4.1 | 5.0477 | 173.4 | 48.951 | 222.351 | 0 | 222.351 | 0 | 0 | 77.9848 | 22.0152 | 0 | 77.9848 | 22.0152 | 0
86 | 19 | March | 2.6 | 3.201 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
86 | 20 | March | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
86 | 21 | March | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
86 | 22 | March | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
86 | 23 | March | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
86 | 24 | March | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87 | 1 | March | 0.2 | 0.24623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87 | 2 | March | 1.1 | 1.3543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87 | 3 | March | 1.9 | 2.3392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87 | 4 | March | 1.8 | 2.2161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87 | 5 | March | 2 | 2.4623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87 | 6 | March | 2.5 | 3.0779 | 0 | 2.646 | 2.646 | 0 | 2.646 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
87 | 7 | March | 2.3 | 2.8316 | 0 | 90.018 | 90.018 | 0 | 90.018 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
87 | 8 | March | 3.4 | 4.1859 | 75.65 | 234.6532 | 310.3032 | 0 | 310.3032 | 0 | 0 | 24.3794 | 75.6206 | 0 | 24.3794 | 75.6206 | 0
87 | 9 | March | 4.4 | 5.417 | 173.4 | 366.5484 | 539.9484 | 0 | 539.9484 | 0 | 0 | 32.1142 | 67.8858 | 0 | 32.1142 | 67.8858 | 0
87 | 10 | March | 4.8 | 5.9095 | 237.15 | 450.1014 | 687.2514 | 0 | 687.2514 | 0 | 0 | 34.507 | 65.493 | 0 | 34.507 | 65.493 | 0
87 | 11 | March | 5.3 | 6.5251 | 399.5 | 309.9061 | 709.4061 | 0 | 709.4061 | 0 | 0 | 56.3147 | 43.6853 | 0 | 56.3147 | 43.6853 | 0
87 | 12 | March | 6 | 7.3869 | 504.9 | 302.1411 | 807.0411 | 0 | 807.0411 | 0 | 0 | 62.5619 | 37.4381 | 0 | 62.5619 | 37.4381 | 0
87 | 13 | March | 6.5 | 8.0024 | 761.6 | 375.7772 | 1137.3772 | 0 | 1137.3772 | 0 | 0 | 66.9611 | 33.0389 | 0 | 66.9611 | 33.0389 | 0
87 | 14 | March | 7.2 | 8.8642 | 908.65 | 272.4363 | 1181.0863 | 0 | 1181.0863 | 0 | 0 | 76.9334 | 23.0666 | 0 | 76.9334 | 23.0666 | 0
87 | 15 | March | 6.9 | 8.4949 | 761.6 | 415.6072 | 1177.2072 | 0 | 1177.2072 | 0 | 0 | 64.6955 | 35.3045 | 0 | 64.6955 | 35.3045 | 0
87 | 16 | March | 6.6 | 8.1256 | 761.6 | 297.1704 | 1058.7704 | 0 | 1058.7704 | 0 | 0 | 71.9325 | 28.0675 | 0 | 71.9325 | 28.0675 | 0
87 | 17 | March | 6.1 | 7.51 | 625.6 | 130.3167 | 755.9167 | 0 | 755.9167 | 0 | 0 | 82.7604 | 17.2396 | 0 | 82.7604 | 17.2396 | 0
87 | 18 | March | 5.6 | 6.8944 | 399.5 | 34.398 | 433.898 | 0 | 433.898 | 0 | 0 | 92.0723 | 7.9277 | 0 | 92.0723 | 7.9277 | 0
87 | 19 | March | 4.8 | 5.9095 | 237.15 | 2.646 | 239.796 | 0 | 239.796 | 0 | 0 | 98.8966 | 1.1034 | 0 | 98.8966 | 1.1034 | 0
87 | 20 | March | 4.4 | 5.417 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
87 | 21 | March | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
87 | 22 | March | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
87 | 23 | March | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
87 | 24 | March | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
88 | 1 | March | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88 | 2 | March | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88 | 3 | March | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88 | 4 | March | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88 | 5 | March | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88 | 6 | March | 3.1 | 3.8165 | 0 | 2.646 | 2.646 | 0 | 2.646 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
88 | 7 | March | 2.6 | 3.201 | 0 | 98.5818 | 98.5818 | 0 | 98.5818 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
88 | 8 | March | 3.1 | 3.8165 | 0 | 253.4878 | 253.4878 | 0 | 253.4878 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
88 | 9 | March | 4.1 | 5.0477 | 173.4 | 438.4168 | 611.8168 | 0 | 611.8168 | 0 | 0 | 28.3418 | 71.6582 | 0 | 28.3418 | 71.6582 | 0
88 | 10 | March | 3.6 | 4.4321 | 75.65 | 575.7652 | 651.4152 | 0 | 651.4152 | 0 | 0 | 11.6132 | 88.3868 | 0 | 11.6132 | 88.3868 | 0
88 | 11 | March | 3.6 | 4.4321 | 75.65 | 499.1584 | 574.8084 | 0 | 574.8084 | 0 | 0 | 13.1609 | 86.8391 | 0 | 13.1609 | 86.8391 | 0
88 | 12 | March | 3.6 | 4.4321 | 75.65 | 542.5112 | 618.1612 | 0 | 618.1612 | 0 | 0 | 12.2379 | 87.7621 | 0 | 12.2379 | 87.7621 | 0
88 | 13 | March | 3.6 | 4.4321 | 75.65 | 535.7464 | 611.3964 | 0 | 611.3964 | 0 | 0 | 12.3733 | 87.6267 | 0 | 12.3733 | 87.6267 | 0
88 | 14 | March | 3.6 | 4.4321 | 75.65 | 487.7188 | 563.3688 | 0 | 563.3688 | 0 | 0 | 13.4281 | 86.5719 | 0 | 13.4281 | 86.5719 | 0
88 | 15 | March | 3.6 | 4.4321 | 75.65 | 383.3576 | 459.0076 | 0 | 459.0076 | 0 | 0 | 16.4812 | 83.5188 | 0 | 16.4812 | 83.5188 | 0
88 | 16 | March | 3.6 | 4.4321 | 75.65 | 165.375 | 241.025 | 0 | 241.025 | 0 | 0 | 31.3868 | 68.6132 | 0 | 31.3868 | 68.6132 | 0
88 | 17 | March | 3.3 | 4.0628 | 75.65 | 123.039 | 198.689 | 0 | 198.689 | 0 | 0 | 38.0746 | 61.9254 | 0 | 38.0746 | 61.9254 | 0
88 | 18 | March | 3.1 | 3.8165 | 0 | 42.336 | 42.336 | 0 | 42.336 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
88 | 19 | March | 2.6 | 3.201 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
88 | 20 | March | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88 | 21 | March | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88 | 22 | March | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88 | 23 | March | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88 | 24 | March | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89 | 1 | March | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89 | 2 | March | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89 | 3 | March | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89 | 4 | March | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89 | 5 | March | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89 | 6 | March | 3.6 | 4.4321 | 75.65 | 1.323 | 76.973 | 0 | 76.973 | 0 | 0 | 98.2812 | 1.7188 | 0 | 98.2812 | 1.7188 | 0
89 | 7 | March | 3.1 | 3.8165 | 0 | 31.752 | 31.752 | 0 | 31.752 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
89 | 8 | March | 4.6 | 5.6633 | 237.15 | 100.548 | 337.698 | 0 | 337.698 | 0 | 0 | 70.2255 | 29.7745 | 0 | 70.2255 | 29.7745 | 0
89 | 9 | March | 5.7 | 7.0175 | 504.9 | 171.99 | 676.89 | 0 | 676.89 | 0 | 0 | 74.5911 | 25.4089 | 0 | 74.5911 | 25.4089 | 0
89 | 10 | March | 6.2 | 7.6331 | 625.6 | 236.7476 | 862.3476 | 0 | 862.3476 | 0 | 0 | 72.5462 | 27.4538 | 0 | 72.5462 | 27.4538 | 0
89 | 11 | March | 5.7 | 7.0175 | 504.9 | 285.7058 | 790.6058 | 0 | 790.6058 | 0 | 0 | 63.8624 | 36.1376 | 0 | 63.8624 | 36.1376 | 0
89 | 12 | March | 4.6 | 5.6633 | 237.15 | 309.0126 | 546.1626 | 0 | 546.1626 | 0 | 0 | 43.4211 | 56.5789 | 0 | 43.4211 | 56.5789 | 0
89 | 13 | March | 6.2 | 7.6331 | 625.6 | 308.38 | 933.98 | 0 | 933.98 | 0 | 0 | 66.9822 | 33.0178 | 0 | 66.9822 | 33.0178 | 0
89 | 14 | March | 5.1 | 6.2788 | 312.8 | 281.5144 | 594.3144 | 0 | 594.3144 | 0 | 0 | 52.6321 | 47.3679 | 0 | 52.6321 | 47.3679 | 0
89 | 15 | March | 5.7 | 7.0175 | 504.9 | 233.1182 | 738.0182 | 0 | 738.0182 | 0 | 0 | 68.4129 | 31.5871 | 0 | 68.4129 | 31.5871 | 0
89 | 16 | March | 5.1 | 6.2788 | 312.8 | 168.021 | 480.821 | 0 | 480.821 | 0 | 0 | 65.0554 | 34.9446 | 0 | 65.0554 | 34.9446 | 0
89 | 17 | March | 6.2 | 7.6331 | 625.6 | 95.256 | 720.856 | 0 | 720.856 | 0 | 0 | 86.7857 | 13.2143 | 0 | 86.7857 | 13.2143 | 0
89 | 18 | March | 6.7 | 8.2487 | 761.6 | 27.783 | 789.383 | 0 | 789.383 | 0 | 0 | 96.4804 | 3.5196 | 0 | 96.4804 | 3.5196 | 0
89 | 19 | March | 12.9 | 15.8818 | 1700 | 1.323 | 1701.323 | 0 | 1701.323 | 0 | 0 | 99.9222 | 0.077763 | 0 | 99.9222 | 0.077763 | 0
89 | 20 | March | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
89 | 21 | March | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
89 | 22 | March | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
89 | 23 | March | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
89 | 24 | March | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
90 | 1 | March | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
90 | 2 | March | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
90 | 3 | March | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
90 | 4 | March | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
90 | 5 | March | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
90 | 6 | March | 5.1 | 6.2788 | 312.8 | 3.969 | 316.769 | 0 | 316.769 | 0 | 0 | 98.747 | 1.253 | 0 | 98.747 | 1.253 | 0
90 | 7 | March | 5.7 | 7.0175 | 504.9 | 34.398 | 539.298 | 0 | 539.298 | 0 | 0 | 93.6217 | 6.3783 | 0 | 93.6217 | 6.3783 | 0
90 | 8 | March | 6.7 | 8.2487 | 761.6 | 177.104 | 938.704 | 0 | 938.704 | 0 | 0 | 81.1331 | 18.8669 | 0 | 81.1331 | 18.8669 | 0
90 | 9 | March | 6.2 | 7.6331 | 625.6 | 175.959 | 801.559 | 0 | 801.559 | 0 | 0 | 78.0479 | 21.9521 | 0 | 78.0479 | 21.9521 | 0
90 | 10 | March | 7.7 | 9.4798 | 1059.95 | 239.4122 | 1299.3622 | 0 | 1299.3622 | 0 | 0 | 81.5746 | 18.4254 | 0 | 81.5746 | 18.4254 | 0
90 | 11 | March | 8.2 | 10.0954 | 1359.15 | 288.3928 | 1647.5428 | 0 | 1647.5428 | 0 | 0 | 82.4956 | 17.5044 | 0 | 82.4956 | 17.5044 | 0
90 | 12 | March | 8.7 | 10.711 | 1490.05 | 555.0647 | 2045.1147 | 1 | 2000 | 45.1147 | 2.2557 | 72.859 | 25.4975 | 8.1278 | 72.2468 | 27.141 | 3.0277
90 | 13 | March | 8.7 | 10.711 | 1490.05 | 544.4315 | 2034.4815 | 1 | 2000 | 34.4815 | 1.7241 | 73.2398 | 25.4975 | 6.3335 | 72.7784 | 26.7602 | 2.3141
90 | 14 | March | 7.7 | 9.4798 | 1059.95 | 855.1403 | 1915.0903 | 0 | 1915.0903 | 0 | 0 | 55.3473 | 44.6527 | 0 | 55.3473 | 44.6527 | 0
90 | 15 | March | 8.7 | 10.711 | 1490.05 | 684.0015 | 2174.0515 | 1 | 2000 | 174.0515 | 8.7026 | 68.5379 | 25.4975 | 25.4461 | 65.7999 | 31.4621 | 11.6809
90 | 16 | March | 7.2 | 8.8642 | 908.65 | 536.0066 | 1444.6566 | 0 | 1444.6566 | 0 | 0 | 62.8973 | 37.1027 | 0 | 62.8973 | 37.1027 | 0
90 | 17 | March | 6.2 | 7.6331 | 625.6 | 288.2014 | 913.8014 | 0 | 913.8014 | 0 | 0 | 68.4613 | 31.5387 | 0 | 68.4613 | 31.5387 | 0
90 | 18 | March | 3.6 | 4.4321 | 75.65 | 68.7427 | 144.3927 | 0 | 144.3927 | 0 | 0 | 52.3918 | 47.6082 | 0 | 52.3918 | 47.6082 | 0
90 | 19 | March | 2.1 | 2.5854 | 0 | 3.969 | 3.969 | 0 | 3.969 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
90 | 20 | March | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90 | 21 | March | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90 | 22 | March | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90 | 23 | March | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90 | 24 | March | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | 1 | April | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | 2 | April | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | 3 | April | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | 4 | April | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | 5 | April | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | 6 | April | 1.5 | 1.8467 | 0 | 6.615 | 6.615 | 0 | 6.615 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
91 | 7 | April | 2.1 | 2.5854 | 0 | 136.1568 | 136.1568 | 0 | 136.1568 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
91 | 8 | April | 3.1 | 3.8165 | 0 | 475.4076 | 475.4076 | 0 | 475.4076 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
91 | 9 | April | 4.1 | 5.0477 | 173.4 | 825.5961 | 998.9961 | 0 | 998.9961 | 0 | 0 | 17.3574 | 82.6426 | 0 | 17.3574 | 82.6426 | 0
91 | 10 | April | 4.6 | 5.6633 | 237.15 | 1139.4646 | 1376.6146 | 0 | 1376.6146 | 0 | 0 | 17.227 | 82.773 | 0 | 17.227 | 82.773 | 0
91 | 11 | April | 5.1 | 6.2788 | 312.8 | 1346.0358 | 1658.8358 | 0 | 1658.8358 | 0 | 0 | 18.8566 | 81.1434 | 0 | 18.8566 | 81.1434 | 0
91 | 12 | April | 4.1 | 5.0477 | 173.4 | 1409.1331 | 1582.5331 | 0 | 1582.5331 | 0 | 0 | 10.9571 | 89.0429 | 0 | 10.9571 | 89.0429 | 0
91 | 13 | April | 4.6 | 5.6633 | 237.15 | 1367.9149 | 1605.0649 | 0 | 1605.0649 | 0 | 0 | 14.7751 | 85.2249 | 0 | 14.7751 | 85.2249 | 0
91 | 14 | April | 4.1 | 5.0477 | 173.4 | 1203.0592 | 1376.4592 | 0 | 1376.4592 | 0 | 0 | 12.5975 | 87.4025 | 0 | 12.5975 | 87.4025 | 0
91 | 15 | April | 4.6 | 5.6633 | 237.15 | 942.5856 | 1179.7356 | 0 | 1179.7356 | 0 | 0 | 20.102 | 79.898 | 0 | 20.102 | 79.898 | 0
91 | 16 | April | 4.1 | 5.0477 | 173.4 | 618.2874 | 791.6874 | 0 | 791.6874 | 0 | 0 | 21.9026 | 78.0974 | 0 | 21.9026 | 78.0974 | 0
91 | 17 | April | 3.6 | 4.4321 | 75.65 | 291.1785 | 366.8285 | 0 | 366.8285 | 0 | 0 | 20.6227 | 79.3773 | 0 | 20.6227 | 79.3773 | 0
91 | 18 | April | 1.5 | 1.8467 | 0 | 68.8345 | 68.8345 | 0 | 68.8345 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
91 | 19 | April | 0 | 0 | 0 | 3.969 | 3.969 | 0 | 3.969 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
91 | 20 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | 21 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | 22 | April | 0.5 | 0.61557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | 23 | April | 0.5 | 0.61557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | 24 | April | 0.5 | 0.61557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | 1 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | 2 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | 3 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | 4 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | 5 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | 6 | April | 0 | 0 | 0 | 2.646 | 2.646 | 0 | 2.646 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
92 | 7 | April | 0 | 0 | 0 | 37.044 | 37.044 | 0 | 37.044 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
92 | 8 | April | 0 | 0 | 0 | 105.84 | 105.84 | 0 | 105.84 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
92 | 9 | April | 0 | 0 | 0 | 177.282 | 177.282 | 0 | 177.282 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
92 | 10 | April | 0 | 0 | 0 | 242.0945 | 242.0945 | 0 | 242.0945 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
92 | 11 | April | 0 | 0 | 0 | 289.7954 | 289.7954 | 0 | 289.7954 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
92 | 12 | April | 2.1 | 2.5854 | 0 | 314.4297 | 314.4297 | 0 | 314.4297 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
92 | 13 | April | 2.1 | 2.5854 | 0 | 311.1332 | 311.1332 | 0 | 311.1332 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
92 | 14 | April | 3.6 | 4.4321 | 75.65 | 285.5601 | 361.2101 | 0 | 361.2101 | 0 | 0 | 20.9435 | 79.0565 | 0 | 20.9435 | 79.0565 | 0
92 | 15 | April | 4.1 | 5.0477 | 173.4 | 235.7911 | 409.1911 | 0 | 409.1911 | 0 | 0 | 42.3763 | 57.6237 | 0 | 42.3763 | 57.6237 | 0
92 | 16 | April | 3.4 | 4.1859 | 75.65 | 229.3525 | 305.0025 | 0 | 305.0025 | 0 | 0 | 24.8031 | 75.1969 | 0 | 24.8031 | 75.1969 | 0
92 | 17 | April | 2.6 | 3.201 | 0 | 157.7464 | 157.7464 | 0 | 157.7464 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
92 | 18 | April | 2.6 | 3.201 | 0 | 50.274 | 50.274 | 0 | 50.274 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
92 | 19 | April | 2.6 | 3.201 | 0 | 2.646 | 2.646 | 0 | 2.646 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
92 | 20 | April | 2.8 | 3.4472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | 21 | April | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | 22 | April | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | 23 | April | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | 24 | April | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
93 | 1 | April | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
93 | 2 | April | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
93 | 3 | April | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
93 | 4 | April | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
93 | 5 | April | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
93 | 6 | April | 6.2 | 7.6331 | 625.6 | 6.615 | 632.215 | 0 | 632.215 | 0 | 0 | 98.9537 | 1.0463 | 0 | 98.9537 | 1.0463 | 0
93 | 7 | April | 6.2 | 7.6331 | 625.6 | 86.584 | 712.184 | 0 | 712.184 | 0 | 0 | 87.8425 | 12.1575 | 0 | 87.8425 | 12.1575 | 0
93 | 8 | April | 8.7 | 10.711 | 1490.05 | 178.6448 | 1668.6948 | 0 | 1668.6948 | 0 | 0 | 89.2943 | 10.7057 | 0 | 89.2943 | 10.7057 | 0
93 | 9 | April | 9.3 | 11.4496 | 1598.85 | 316.0598 | 1914.9098 | 0 | 1914.9098 | 0 | 0 | 83.4948 | 16.5052 | 0 | 83.4948 | 16.5052 | 0
93 | 10 | April | 8.7 | 10.711 | 1490.05 | 246.0819 | 1736.1319 | 0 | 1736.1319 | 0 | 0 | 85.8259 | 14.1741 | 0 | 85.8259 | 14.1741 | 0
93 | 11 | April | 8.7 | 10.711 | 1490.05 | 525.7299 | 2015.7799 | 1 | 2000 | 15.7799 | 0.789 | 73.9193 | 25.4975 | 3.0015 | 73.7135 | 26.0807 | 1.059
93 | 12 | April | 10.3 | 12.6808 | 1694.9 | 1159.0152 | 2853.9152 | 1 | 2000 | 853.9152 | 42.6958 | 59.3886 | 15.255 | 73.6759 | 42.0492 | 40.6114 | 50.3815
93 | 13 | April | 11.8 | 14.5275 | 1700 | 559.2096 | 2259.2096 | 1 | 2000 | 259.2096 | 12.9605 | 75.2476 | 15 | 46.3529 | 72.0395 | 24.7524 | 15.2476
93 | 14 | April | 10.3 | 12.6808 | 1694.9 | 653.6371 | 2348.5371 | 1 | 2000 | 348.5371 | 17.4269 | 72.1683 | 15.255 | 53.3227 | 67.3181 | 27.8317 | 20.5639
93 | 15 | April | 12.3 | 15.1431 | 1700 | 560.8704 | 2260.8704 | 1 | 2000 | 260.8704 | 13.0435 | 75.1923 | 15 | 46.5117 | 71.9565 | 24.8077 | 15.3453
93 | 16 | April | 10.8 | 13.2964 | 1698.3 | 290.7054 | 1989.0054 | 0 | 1989.0054 | 0 | 0 | 85.3844 | 14.6156 | 0 | 85.3844 | 14.6156 | 0
93 | 17 | April | 11.8 | 14.5275 | 1700 | 164.4903 | 1864.4903 | 0 | 1864.4903 | 0 | 0 | 91.1777 | 8.8223 | 0 | 91.1777 | 8.8223 | 0
93 | 18 | April | 9.8 | 12.0652 | 1683.85 | 76.3095 | 1760.1595 | 0 | 1760.1595 | 0 | 0 | 95.6646 | 4.3354 | 0 | 95.6646 | 4.3354 | 0
93 | 19 | April | 8.2 | 10.0954 | 1359.15 | 5.292 | 1364.442 | 0 | 1364.442 | 0 | 0 | 99.6121 | 0.38785 | 0 | 99.6121 | 0.38785 | 0
93 | 20 | April | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
93 | 21 | April | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
93 | 22 | April | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
93 | 23 | April | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
93 | 24 | April | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
94 | 1 | April | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
94 | 2 | April | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
94 | 3 | April | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
94 | 4 | April | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
94 | 5 | April | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
94 | 6 | April | 6.7 | 8.2487 | 761.6 | 9.261 | 770.861 | 0 | 770.861 | 0 | 0 | 98.7986 | 1.2014 | 0 | 98.7986 | 1.2014 | 0
94 | 7 | April | 6.2 | 7.6331 | 625.6 | 104.542 | 730.142 | 0 | 730.142 | 0 | 0 | 85.682 | 14.318 | 0 | 85.682 | 14.318 | 0
94 | 8 | April | 7.7 | 9.4798 | 1059.95 | 183.6966 | 1243.6466 | 0 | 1243.6466 | 0 | 0 | 85.2292 | 14.7708 | 0 | 85.2292 | 14.7708 | 0
94 | 9 | April | 8.2 | 10.0954 | 1359.15 | 331.9384 | 1691.0884 | 0 | 1691.0884 | 0 | 0 | 80.3713 | 19.6287 | 0 | 80.3713 | 19.6287 | 0
94 | 10 | April | 7.7 | 9.4798 | 1059.95 | 616.1257 | 1676.0757 | 0 | 1676.0757 | 0 | 0 | 63.24 | 36.76 | 0 | 63.24 | 36.76 | 0
94 | 11 | April | 7.2 | 8.8642 | 908.65 | 702.1683 | 1610.8183 | 0 | 1610.8183 | 0 | 0 | 56.4092 | 43.5908 | 0 | 56.4092 | 43.5908 | 0
94 | 12 | April | 7.2 | 8.8642 | 908.65 | 1235.529 | 2144.179 | 1 | 2000 | 144.179 | 7.2089 | 42.3775 | 54.5675 | 11.6694 | 38.2236 | 57.6225 | 15.8674
94 | 13 | April | 5.7 | 7.0175 | 504.9 | 1344.7191 | 1849.6191 | 0 | 1849.6191 | 0 | 0 | 27.2975 | 72.7025 | 0 | 27.2975 | 72.7025 | 0
94 | 14 | April | 6.2 | 7.6331 | 625.6 | 1239.0252 | 1864.6252 | 0 | 1864.6252 | 0 | 0 | 33.551 | 66.449 | 0 | 33.551 | 66.449 | 0
94 | 15 | April | 4.6 | 5.6633 | 237.15 | 428.5614 | 665.7114 | 0 | 665.7114 | 0 | 0 | 35.6235 | 64.3765 | 0 | 35.6235 | 64.3765 | 0
94 | 16 | April | 3.1 | 3.8165 | 0 | 178.605 | 178.605 | 0 | 178.605 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
94 | 17 | April | 0.5 | 0.61557 | 0 | 104.517 | 104.517 | 0 | 104.517 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
94 | 18 | April | 5.1 | 6.2788 | 312.8 | 34.398 | 347.198 | 0 | 347.198 | 0 | 0 | 90.0927 | 9.9073 | 0 | 90.0927 | 9.9073 | 0
94 | 19 | April | 4.6 | 5.6633 | 237.15 | 2.646 | 239.796 | 0 | 239.796 | 0 | 0 | 98.8966 | 1.1034 | 0 | 98.8966 | 1.1034 | 0
94 | 20 | April | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
94 | 21 | April | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
94 | 22 | April | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
94 | 23 | April | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
94 | 24 | April | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
95 | 1 | April | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
95 | 2 | April | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
95 | 3 | April | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
95 | 4 | April | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
95 | 5 | April | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
95 | 6 | April | 11.3 | 13.9119 | 1700 | 3.969 | 1703.969 | 0 | 1703.969 | 0 | 0 | 99.7671 | 0.23293 | 0 | 99.7671 | 0.23293 | 0
95 | 7 | April | 10.8 | 13.2964 | 1698.3 | 43.659 | 1741.959 | 0 | 1741.959 | 0 | 0 | 97.4937 | 2.5063 | 0 | 97.4937 | 2.5063 | 0
95 | 8 | April | 11.8 | 14.5275 | 1700 | 113.778 | 1813.778 | 0 | 1813.778 | 0 | 0 | 93.727 | 6.273 | 0 | 93.727 | 6.273 | 0
95 | 9 | April | 12.9 | 15.8818 | 1700 | 334.7126 | 2034.7126 | 1 | 2000 | 34.7126 | 1.7356 | 83.5499 | 15 | 10.3709 | 83.2644 | 16.4501 | 2.0419
95 | 10 | April | 12.3 | 15.1431 | 1700 | 251.4168 | 1951.4168 | 0 | 1951.4168 | 0 | 0 | 87.1162 | 12.8838 | 0 | 87.1162 | 12.8838 | 0
95 | 11 | April | 13.4 | 16.4973 | 1700 | 531.6634 | 2231.6634 | 1 | 2000 | 231.6634 | 11.5832 | 76.1764 | 15 | 43.5733 | 73.4168 | 23.8236 | 13.6273
95 | 12 | April | 15.4 | 18.9596 | 1700 | 561.5541 | 2261.5541 | 1 | 2000 | 261.5541 | 13.0777 | 75.1695 | 15 | 46.5768 | 71.9223 | 24.8305 | 15.3855
95 | 13 | April | 14.4 | 17.7285 | 1700 | 319.0327 | 2019.0327 | 1 | 2000 | 19.0327 | 0.95164 | 84.1987 | 15 | 5.9658 | 84.0484 | 15.8013 | 1.1196
95 | 14 | April | 13.9 | 17.1129 | 1700 | 292.2323 | 1992.2323 | 0 | 1992.2323 | 0 | 0 | 85.3314 | 14.6686 | 0 | 85.3314 | 14.6686 | 0
95 | 15 | April | 13.4 | 16.4973 | 1700 | 242.4313 | 1942.4313 | 0 | 1942.4313 | 0 | 0 | 87.5192 | 12.4808 | 0 | 87.5192 | 12.4808 | 0
95 | 16 | April | 15.4 | 18.9596 | 1700 | 295.945 | 1995.945 | 0 | 1995.945 | 0 | 0 | 85.1727 | 14.8273 | 0 | 85.1727 | 14.8273 | 0
95 | 17 | April | 12.9 | 15.8818 | 1700 | 216.5357 | 1916.5357 | 0 | 1916.5357 | 0 | 0 | 88.7017 | 11.2983 | 0 | 88.7017 | 11.2983 | 0
95 | 18 | April | 11.8 | 14.5275 | 1700 | 56.889 | 1756.889 | 0 | 1756.889 | 0 | 0 | 96.7619 | 3.2381 | 0 | 96.7619 | 3.2381 | 0
95 | 19 | April | 9.8 | 12.0652 | 1683.85 | 2.646 | 1686.496 | 0 | 1686.496 | 0 | 0 | 99.8431 | 0.15689 | 0 | 99.8431 | 0.15689 | 0
95 | 20 | April | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
95 | 21 | April | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
95 | 22 | April | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
95 | 23 | April | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
95 | 24 | April | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
96 | 1 | April | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
96 | 2 | April | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
96 | 3 | April | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
96 | 4 | April | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
96 | 5 | April | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
96 | 6 | April | 4.6 | 5.6633 | 237.15 | 13.23 | 250.38 | 0 | 250.38 | 0 | 0 | 94.716 | 5.284 | 0 | 94.716 | 5.284 | 0
96 | 7 | April | 3.6 | 4.4321 | 75.65 | 165.8515 | 241.5015 | 0 | 241.5015 | 0 | 0 | 31.3249 | 68.6751 | 0 | 31.3249 | 68.6751 | 0
96 | 8 | April | 3.6 | 4.4321 | 75.65 | 486.9556 | 562.6056 | 0 | 562.6056 | 0 | 0 | 13.4464 | 86.5536 | 0 | 13.4464 | 86.5536 | 0
96 | 9 | April | 3.6 | 4.4321 | 75.65 | 834.6786 | 910.3286 | 0 | 910.3286 | 0 | 0 | 8.3102 | 91.6898 | 0 | 8.3102 | 91.6898 | 0
96 | 10 | April | 3.6 | 4.4321 | 75.65 | 1109.8836 | 1185.5336 | 0 | 1185.5336 | 0 | 0 | 6.3811 | 93.6189 | 0 | 6.3811 | 93.6189 | 0
96 | 11 | April | 3.1 | 3.8165 | 0 | 1362.9327 | 1362.9327 | 0 | 1362.9327 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
96 | 12 | April | 4.1 | 5.0477 | 173.4 | 1451.2506 | 1624.6506 | 0 | 1624.6506 | 0 | 0 | 10.6731 | 89.3269 | 0 | 10.6731 | 89.3269 | 0
96 | 13 | April | 3.6 | 4.4321 | 75.65 | 1397.7045 | 1473.3545 | 0 | 1473.3545 | 0 | 0 | 5.1345 | 94.8655 | 0 | 5.1345 | 94.8655 | 0
96 | 14 | April | 3.1 | 3.8165 | 0 | 1236.4591 | 1236.4591 | 0 | 1236.4591 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
96 | 15 | April | 4.1 | 5.0477 | 173.4 | 967.5153 | 1140.9153 | 0 | 1140.9153 | 0 | 0 | 15.1983 | 84.8017 | 0 | 15.1983 | 84.8017 | 0
96 | 16 | April | 4.6 | 5.6633 | 237.15 | 640.9712 | 878.1212 | 0 | 878.1212 | 0 | 0 | 27.0065 | 72.9935 | 0 | 27.0065 | 72.9935 | 0
96 | 17 | April | 5.1 | 6.2788 | 312.8 | 312.4592 | 625.2592 | 0 | 625.2592 | 0 | 0 | 50.0273 | 49.9727 | 0 | 50.0273 | 49.9727 | 0
96 | 18 | April | 4.6 | 5.6633 | 237.15 | 79.0042 | 316.1542 | 0 | 316.1542 | 0 | 0 | 75.0109 | 24.9891 | 0 | 75.0109 | 24.9891 | 0
96 | 19 | April | 3.6 | 4.4321 | 75.65 | 6.615 | 82.265 | 0 | 82.265 | 0 | 0 | 91.9589 | 8.0411 | 0 | 91.9589 | 8.0411 | 0
96 | 20 | April | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
96 | 21 | April | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
96 | 22 | April | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
96 | 23 | April | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
96 | 24 | April | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
97 | 1 | April | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
97 | 2 | April | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
97 | 3 | April | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
97 | 4 | April | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
97 | 5 | April | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
97 | 6 | April | 2.1 | 2.5854 | 0 | 9.261 | 9.261 | 0 | 9.261 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
97 | 7 | April | 2.1 | 2.5854 | 0 | 47.628 | 47.628 | 0 | 47.628 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
97 | 8 | April | 3.1 | 3.8165 | 0 | 120.393 | 120.393 | 0 | 120.393 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
97 | 9 | April | 4.1 | 5.0477 | 173.4 | 193.158 | 366.558 | 0 | 366.558 | 0 | 0 | 47.3049 | 52.6951 | 0 | 47.3049 | 52.6951 | 0
97 | 10 | April | 5.7 | 7.0175 | 504.9 | 259.4489 | 764.3489 | 0 | 764.3489 | 0 | 0 | 66.0562 | 33.9438 | 0 | 66.0562 | 33.9438 | 0
97 | 11 | April | 6.2 | 7.6331 | 625.6 | 543.3082 | 1168.9082 | 0 | 1168.9082 | 0 | 0 | 53.52 | 46.48 | 0 | 53.52 | 46.48 | 0
97 | 12 | April | 7.7 | 9.4798 | 1059.95 | 574.6588 | 1634.6088 | 0 | 1634.6088 | 0 | 0 | 64.8443 | 35.1557 | 0 | 64.8443 | 35.1557 | 0
97 | 13 | April | 7.7 | 9.4798 | 1059.95 | 793.4594 | 1853.4094 | 0 | 1853.4094 | 0 | 0 | 57.1892 | 42.8108 | 0 | 57.1892 | 42.8108 | 0
97 | 14 | April | 6.7 | 8.2487 | 761.6 | 729.1146 | 1490.7146 | 0 | 1490.7146 | 0 | 0 | 51.0896 | 48.9104 | 0 | 51.0896 | 48.9104 | 0
97 | 15 | April | 5.7 | 7.0175 | 504.9 | 807.4186 | 1312.3186 | 0 | 1312.3186 | 0 | 0 | 38.4739 | 61.5261 | 0 | 38.4739 | 61.5261 | 0
97 | 16 | April | 5.1 | 6.2788 | 312.8 | 634.7443 | 947.5443 | 0 | 947.5443 | 0 | 0 | 33.0116 | 66.9884 | 0 | 33.0116 | 66.9884 | 0
97 | 17 | April | 4.6 | 5.6633 | 237.15 | 262.3477 | 499.4977 | 0 | 499.4977 | 0 | 0 | 47.4777 | 52.5223 | 0 | 47.4777 | 52.5223 | 0
97 | 18 | April | 3.6 | 4.4321 | 75.65 | 76.395 | 152.045 | 0 | 152.045 | 0 | 0 | 49.755 | 50.245 | 0 | 49.755 | 50.245 | 0
97 | 19 | April | 2.6 | 3.201 | 0 | 6.615 | 6.615 | 0 | 6.615 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
97 | 20 | April | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97 | 21 | April | 0.5 | 0.61557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97 | 22 | April | 0.5 | 0.61557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97 | 23 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97 | 24 | April | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
98 | 1 | April | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98 | 2 | April | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
98 | 3 | April | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
98 | 4 | April | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98 | 5 | April | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
98 | 6 | April | 2.6 | 3.201 | 0 | 17.199 | 17.199 | 0 | 17.199 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
98 | 7 | April | 4.1 | 5.0477 | 173.4 | 114.0679 | 287.4679 | 0 | 287.4679 | 0 | 0 | 60.3198 | 39.6802 | 0 | 60.3198 | 39.6802 | 0
98 | 8 | April | 5.7 | 7.0175 | 504.9 | 204.9628 | 709.8628 | 0 | 709.8628 | 0 | 0 | 71.1264 | 28.8736 | 0 | 71.1264 | 28.8736 | 0
98 | 9 | April | 4.6 | 5.6633 | 237.15 | 339.3947 | 576.5447 | 0 | 576.5447 | 0 | 0 | 41.133 | 58.867 | 0 | 41.133 | 58.867 | 0
98 | 10 | April | 5.1 | 6.2788 | 312.8 | 466.4473 | 779.2473 | 0 | 779.2473 | 0 | 0 | 40.1413 | 59.8587 | 0 | 40.1413 | 59.8587 | 0
98 | 11 | April | 4.1 | 5.0477 | 173.4 | 542.5552 | 715.9552 | 0 | 715.9552 | 0 | 0 | 24.2194 | 75.7806 | 0 | 24.2194 | 75.7806 | 0
98 | 12 | April | 6.2 | 7.6331 | 625.6 | 554.5585 | 1180.1585 | 0 | 1180.1585 | 0 | 0 | 53.0098 | 46.9902 | 0 | 53.0098 | 46.9902 | 0
98 | 13 | April | 5.7 | 7.0175 | 504.9 | 551.2826 | 1056.1826 | 0 | 1056.1826 | 0 | 0 | 47.8042 | 52.1958 | 0 | 47.8042 | 52.1958 | 0
98 | 14 | April | 6.2 | 7.6331 | 625.6 | 503.6338 | 1129.2338 | 0 | 1129.2338 | 0 | 0 | 55.4004 | 44.5996 | 0 | 55.4004 | 44.5996 | 0
98 | 15 | April | 4.6 | 5.6633 | 237.15 | 426.2044 | 663.3544 | 0 | 663.3544 | 0 | 0 | 35.7501 | 64.2499 | 0 | 35.7501 | 64.2499 | 0
98 | 16 | April | 5.1 | 6.2788 | 312.8 | 310.8631 | 623.6631 | 0 | 623.6631 | 0 | 0 | 50.1553 | 49.8447 | 0 | 50.1553 | 49.8447 | 0
98 | 17 | April | 4.1 | 5.0477 | 173.4 | 178.2756 | 351.6756 | 0 | 351.6756 | 0 | 0 | 49.3068 | 50.6932 | 0 | 49.3068 | 50.6932 | 0
98 | 18 | April | 3.1 | 3.8165 | 0 | 64.827 | 64.827 | 0 | 64.827 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
98 | 19 | April | 3.6 | 4.4321 | 75.65 | 5.292 | 80.942 | 0 | 80.942 | 0 | 0 | 93.462 | 6.538 | 0 | 93.462 | 6.538 | 0
98 | 20 | April | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98 | 21 | April | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98 | 22 | April | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98 | 23 | April | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98 | 24 | April | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | 1 | April | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | 2 | April | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | 3 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | 4 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | 5 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | 6 | April | 1.5 | 1.8467 | 0 | 10.584 | 10.584 | 0 | 10.584 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
99 | 7 | April | 1.5 | 1.8467 | 0 | 83.349 | 83.349 | 0 | 83.349 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
99 | 8 | April | 1 | 1.2311 | 0 | 202.7573 | 202.7573 | 0 | 202.7573 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
99 | 9 | April | 1 | 1.2311 | 0 | 343.6098 | 343.6098 | 0 | 343.6098 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
99 | 10 | April | 1 | 1.2311 | 0 | 469.4427 | 469.4427 | 0 | 469.4427 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
99 | 11 | April | 1.5 | 1.8467 | 0 | 545.5356 | 545.5356 | 0 | 545.5356 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
99 | 12 | April | 3.1 | 3.8165 | 0 | 560.2251 | 560.2251 | 0 | 560.2251 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
99 | 13 | April | 2.6 | 3.201 | 0 | 554.0745 | 554.0745 | 0 | 554.0745 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
99 | 14 | April | 3.1 | 3.8165 | 0 | 679.3096 | 679.3096 | 0 | 679.3096 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
99 | 15 | April | 2.6 | 3.201 | 0 | 581.9865 | 581.9865 | 0 | 581.9865 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
99 | 16 | April | 2.6 | 3.201 | 0 | 597.2778 | 597.2778 | 0 | 597.2778 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
99 | 17 | April | 1.5 | 1.8467 | 0 | 319.2686 | 319.2686 | 0 | 319.2686 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
99 | 18 | April | 1 | 1.2311 | 0 | 85.5136 | 85.5136 | 0 | 85.5136 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
99 | 19 | April | 0 | 0 | 0 | 11.907 | 11.907 | 0 | 11.907 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
99 | 20 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | 21 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | 22 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | 23 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | 24 | April | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100 | 1 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100 | 2 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100 | 3 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100 | 4 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100 | 5 | April | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100 | 6 | April | 1.5 | 1.8467 | 0 | 15.876 | 15.876 | 0 | 15.876 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
100 | 7 | April | 0.5 | 0.61557 | 0 | 124.6039 | 124.6039 | 0 | 124.6039 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
100 | 8 | April | 2.1 | 2.5854 | 0 | 492.8208 | 492.8208 | 0 | 492.8208 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
100 | 9 | April | 1 | 1.2311 | 0 | 508.2219 | 508.2219 | 0 | 508.2219 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
100 | 10 | April | 2.6 | 3.201 | 0 | 843.4291 | 843.4291 | 0 | 843.4291 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
100 | 11 | April | 3.6 | 4.4321 | 75.65 | 771.4394 | 847.0894 | 0 | 847.0894 | 0 | 0 | 8.9306 | 91.0694 | 0 | 8.9306 | 91.0694 | 0
100 | 12 | April | 4.6 | 5.6633 | 237.15 | 577.2081 | 814.3581 | 0 | 814.3581 | 0 | 0 | 29.1211 | 70.8789 | 0 | 29.1211 | 70.8789 | 0
100 | 13 | April | 5.1 | 6.2788 | 312.8 | 574.7625 | 887.5625 | 0 | 887.5625 | 0 | 0 | 35.2426 | 64.7574 | 0 | 35.2426 | 64.7574 | 0
100 | 14 | April | 6.2 | 7.6331 | 625.6 | 722.9417 | 1348.5417 | 0 | 1348.5417 | 0 | 0 | 46.3909 | 53.6091 | 0 | 46.3909 | 53.6091 | 0
100 | 15 | April | 7.2 | 8.8642 | 908.65 | 432.0138 | 1340.6638 | 0 | 1340.6638 | 0 | 0 | 67.7761 | 32.2239 | 0 | 67.7761 | 32.2239 | 0
100 | 16 | April | 6.7 | 8.2487 | 761.6 | 309.3466 | 1070.9466 | 0 | 1070.9466 | 0 | 0 | 71.1147 | 28.8853 | 0 | 71.1147 | 28.8853 | 0
100 | 17 | April | 5.1 | 6.2788 | 312.8 | 272.2791 | 585.0791 | 0 | 585.0791 | 0 | 0 | 53.4629 | 46.5371 | 0 | 53.4629 | 46.5371 | 0
100 | 18 | April | 2.1 | 2.5854 | 0 | 103.3977 | 103.3977 | 0 | 103.3977 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
100 | 19 | April | 0 | 0 | 0 | 11.907 | 11.907 | 0 | 11.907 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
100 | 20 | April | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100 | 21 | April | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100 | 22 | April | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100 | 23 | April | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100 | 24 | April | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
101 | 1 | April | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
101 | 2 | April | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
101 | 3 | April | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
101 | 4 | April | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
101 | 5 | April | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
101 | 6 | April | 5.1 | 6.2788 | 312.8 | 13.23 | 326.03 | 0 | 326.03 | 0 | 0 | 95.9421 | 4.0579 | 0 | 95.9421 | 4.0579 | 0
101 | 7 | April | 7.2 | 8.8642 | 908.65 | 89.964 | 998.614 | 0 | 998.614 | 0 | 0 | 90.9911 | 9.0089 | 0 | 90.9911 | 9.0089 | 0
101 | 8 | April | 7.7 | 9.4798 | 1059.95 | 325.8196 | 1385.7696 | 0 | 1385.7696 | 0 | 0 | 76.4882 | 23.5118 | 0 | 76.4882 | 23.5118 | 0
101 | 9 | April | 9.8 | 12.0652 | 1683.85 | 358.4292 | 2042.2792 | 1 | 2000 | 42.2792 | 2.114 | 82.4496 | 15.8075 | 11.7957 | 82.0785 | 17.5504 | 2.5109
101 | 10 | April | 10.8 | 13.2964 | 1698.3 | 475.4181 | 2173.7181 | 1 | 2000 | 173.7181 | 8.6859 | 78.1288 | 15.085 | 36.5401 | 76.2291 | 21.8712 | 10.2289
101 | 11 | April | 11.3 | 13.9119 | 1700 | 549.8076 | 2249.8076 | 1 | 2000 | 249.8076 | 12.4904 | 75.562 | 15 | 45.4355 | 72.5096 | 24.438 | 14.6946
101 | 12 | April | 12.3 | 15.1431 | 1700 | 587.4925 | 2287.4925 | 1 | 2000 | 287.4925 | 14.3746 | 74.3172 | 15 | 48.9355 | 70.6254 | 25.6828 | 16.9113
101 | 13 | April | 12.9 | 15.8818 | 1700 | 753.0634 | 2453.0634 | 1 | 2000 | 453.0634 | 22.6532 | 69.3011 | 15 | 60.1627 | 62.3468 | 30.6989 | 26.6508
101 | 14 | April | 12.3 | 15.1431 | 1700 | 694.3968 | 2394.3968 | 1 | 2000 | 394.3968 | 19.7198 | 70.9991 | 15 | 56.797 | 65.2802 | 29.0009 | 23.1998
101 | 15 | April | 9.8 | 12.0652 | 1683.85 | 716.9179 | 2400.7679 | 1 | 2000 | 400.7679 | 20.0384 | 70.138 | 15.8075 | 55.9015 | 64.1541 | 29.862 | 23.8007
101 | 16 | April | 10.8 | 13.2964 | 1698.3 | 569.3424 | 2267.6424 | 1 | 2000 | 267.6424 | 13.3821 | 74.8928 | 15.085 | 47.009 | 71.5329 | 25.1072 | 15.7594
101 | 17 | April | 8.7 | 10.711 | 1490.05 | 319.5391 | 1809.5891 | 0 | 1809.5891 | 0 | 0 | 82.3419 | 17.6581 | 0 | 82.3419 | 17.6581 | 0
101 | 18 | April | 8.7 | 10.711 | 1490.05 | 98.0165 | 1588.0665 | 0 | 1588.0665 | 0 | 0 | 93.8279 | 6.1721 | 0 | 93.8279 | 6.1721 | 0
101 | 19 | April | 8.7 | 10.711 | 1490.05 | 10.584 | 1500.634 | 0 | 1500.634 | 0 | 0 | 99.2947 | 0.7053 | 0 | 99.2947 | 0.7053 | 0
101 | 20 | April | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
101 | 21 | April | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
101 | 22 | April | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
101 | 23 | April | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
101 | 24 | April | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
102 | 1 | April | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
102 | 2 | April | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
102 | 3 | April | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
102 | 4 | April | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
102 | 5 | April | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
102 | 6 | April | 4.6 | 5.6633 | 237.15 | 14.553 | 251.703 | 0 | 251.703 | 0 | 0 | 94.2182 | 5.7818 | 0 | 94.2182 | 5.7818 | 0
102 | 7 | April | 7.2 | 8.8642 | 908.65 | 98.067 | 1006.717 | 0 | 1006.717 | 0 | 0 | 90.2587 | 9.7413 | 0 | 90.2587 | 9.7413 | 0
102 | 8 | April | 8.2 | 10.0954 | 1359.15 | 329.1054 | 1688.2554 | 0 | 1688.2554 | 0 | 0 | 80.5062 | 19.4938 | 0 | 80.5062 | 19.4938 | 0
102 | 9 | April | 9.3 | 11.4496 | 1598.85 | 851.804 | 2450.654 | 1 | 2000 | 450.654 | 22.5327 | 65.2418 | 20.0575 | 52.9058 | 57.4098 | 34.7582 | 28.1861
102 | 10 | April | 8.7 | 10.711 | 1490.05 | 829.941 | 2319.991 | 1 | 2000 | 319.991 | 15.9996 | 64.2265 | 25.4975 | 38.5559 | 58.5029 | 35.7735 | 21.4752
102 | 11 | April | 8.7 | 10.711 | 1490.05 | 1160.2686 | 2650.3186 | 1 | 2000 | 650.3186 | 32.5159 | 56.2215 | 25.4975 | 56.049 | 41.9866 | 43.7785 | 43.6441
102 | 12 | April | 9.3 | 11.4496 | 1598.85 | 1350.0252 | 2948.8752 | 1 | 2000 | 948.8752 | 47.4438 | 54.219 | 20.0575 | 70.2857 | 32.4987 | 45.781 | 59.3474
102 | 13 | April | 8.2 | 10.0954 | 1359.15 | 1188.0058 | 2547.1558 | 1 | 2000 | 547.1558 | 27.3578 | 53.3595 | 32.0425 | 46.0567 | 40.5997 | 46.6405 | 40.2572
102 | 14 | April | 9.3 | 11.4496 | 1598.85 | 1084.0341 | 2682.8841 | 1 | 2000 | 682.8841 | 34.1442 | 59.5944 | 20.0575 | 62.9947 | 45.7983 | 40.4056 | 42.711
102 | 15 | April | 8.7 | 10.711 | 1490.05 | 919.3701 | 2409.4201 | 1 | 2000 | 409.4201 | 20.471 | 61.8427 | 25.4975 | 44.5327 | 54.0315 | 38.1573 | 27.4769
102 | 16 | April | 9.3 | 11.4496 | 1598.85 | 630.0911 | 2228.9411 | 1 | 2000 | 228.9411 | 11.4471 | 71.7314 | 20.0575 | 36.3346 | 68.4954 | 28.2686 | 14.3191
102 | 17 | April | 7.7 | 9.4798 | 1059.95 | 331.3557 | 1391.3057 | 0 | 1391.3057 | 0 | 0 | 76.1838 | 23.8162 | 0 | 76.1838 | 23.8162 | 0
102 | 18 | April | 6.2 | 7.6331 | 625.6 | 100.0791 | 725.6791 | 0 | 725.6791 | 0 | 0 | 86.2089 | 13.7911 | 0 | 86.2089 | 13.7911 | 0
102 | 19 | April | 3.6 | 4.4321 | 75.65 | 14.553 | 90.203 | 0 | 90.203 | 0 | 0 | 83.8664 | 16.1336 | 0 | 83.8664 | 16.1336 | 0
102 | 20 | April | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102 | 21 | April | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102 | 22 | April | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102 | 23 | April | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102 | 24 | April | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | 1 | April | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | 2 | April | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | 3 | April | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | 4 | April | 0.5 | 0.61557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | 5 | April | 0.2 | 0.24623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | 6 | April | 0 | 0 | 0 | 22.491 | 22.491 | 0 | 22.491 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
103 | 7 | April | 0 | 0 | 0 | 100.0879 | 100.0879 | 0 | 100.0879 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
103 | 8 | April | 2.6 | 3.201 | 0 | 220.9953 | 220.9953 | 0 | 220.9953 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
103 | 9 | April | 3.1 | 3.8165 | 0 | 362.7029 | 362.7029 | 0 | 362.7029 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
103 | 10 | April | 2.1 | 2.5854 | 0 | 486.757 | 486.757 | 0 | 486.757 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
103 | 11 | April | 3.6 | 4.4321 | 75.65 | 561.3384 | 636.9884 | 0 | 636.9884 | 0 | 0 | 11.8762 | 88.1238 | 0 | 11.8762 | 88.1238 | 0
103 | 12 | April | 2.1 | 2.5854 | 0 | 594.6217 | 594.6217 | 0 | 594.6217 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
103 | 13 | April | 5.1 | 6.2788 | 312.8 | 810.6333 | 1123.4333 | 0 | 1123.4333 | 0 | 0 | 27.8432 | 72.1568 | 0 | 27.8432 | 72.1568 | 0
103 | 14 | April | 4.6 | 5.6633 | 237.15 | 908.6401 | 1145.7901 | 0 | 1145.7901 | 0 | 0 | 20.6975 | 79.3025 | 0 | 20.6975 | 79.3025 | 0
103 | 15 | April | 5.1 | 6.2788 | 312.8 | 602.3123 | 915.1123 | 0 | 915.1123 | 0 | 0 | 34.1816 | 65.8184 | 0 | 34.1816 | 65.8184 | 0
103 | 16 | April | 2.6 | 3.201 | 0 | 422.627 | 422.627 | 0 | 422.627 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
103 | 17 | April | 3.1 | 3.8165 | 0 | 191.5005 | 191.5005 | 0 | 191.5005 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
103 | 18 | April | 3.1 | 3.8165 | 0 | 76.734 | 76.734 | 0 | 76.734 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
103 | 19 | April | 1.5 | 1.8467 | 0 | 5.292 | 5.292 | 0 | 5.292 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
103 | 20 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | 21 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | 22 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | 23 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | 24 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104 | 1 | April | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104 | 2 | April | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
104 | 3 | April | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104 | 4 | April | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
104 | 5 | April | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104 | 6 | April | 3.1 | 3.8165 | 0 | 15.876 | 15.876 | 0 | 15.876 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
104 | 7 | April | 3.6 | 4.4321 | 75.65 | 102.7696 | 178.4196 | 0 | 178.4196 | 0 | 0 | 42.4 | 57.6 | 0 | 42.4 | 57.6 | 0
104 | 8 | April | 5.7 | 7.0175 | 504.9 | 223.6917 | 728.5917 | 0 | 728.5917 | 0 | 0 | 69.2981 | 30.7019 | 0 | 69.2981 | 30.7019 | 0
104 | 9 | April | 6.7 | 8.2487 | 761.6 | 360.8206 | 1122.4206 | 0 | 1122.4206 | 0 | 0 | 67.8534 | 32.1466 | 0 | 67.8534 | 32.1466 | 0
104 | 10 | April | 5.7 | 7.0175 | 504.9 | 272.669 | 777.569 | 0 | 777.569 | 0 | 0 | 64.9331 | 35.0669 | 0 | 64.9331 | 35.0669 | 0
104 | 11 | April | 6.2 | 7.6331 | 625.6 | 322.4898 | 948.0898 | 0 | 948.0898 | 0 | 0 | 65.9853 | 34.0147 | 0 | 65.9853 | 34.0147 | 0
104 | 12 | April | 7.2 | 8.8642 | 908.65 | 343.0616 | 1251.7116 | 0 | 1251.7116 | 0 | 0 | 72.5926 | 27.4074 | 0 | 72.5926 | 27.4074 | 0
104 | 13 | April | 7.2 | 8.8642 | 908.65 | 340.906 | 1249.556 | 0 | 1249.556 | 0 | 0 | 72.7178 | 27.2822 | 0 | 72.7178 | 27.2822 | 0
104 | 14 | April | 7.7 | 9.4798 | 1059.95 | 312.2809 | 1372.2309 | 0 | 1372.2309 | 0 | 0 | 77.2428 | 22.7572 | 0 | 77.2428 | 22.7572 | 0
104 | 15 | April | 8.7 | 10.711 | 1490.05 | 262.7306 | 1752.7806 | 0 | 1752.7806 | 0 | 0 | 85.0106 | 14.9894 | 0 | 85.0106 | 14.9894 | 0
104 | 16 | April | 7.2 | 8.8642 | 908.65 | 433.1385 | 1341.7885 | 0 | 1341.7885 | 0 | 0 | 67.7193 | 32.2807 | 0 | 67.7193 | 32.2807 | 0
104 | 17 | April | 8.2 | 10.0954 | 1359.15 | 194.198 | 1553.348 | 0 | 1553.348 | 0 | 0 | 87.4981 | 12.5019 | 0 | 87.4981 | 12.5019 | 0
104 | 18 | April | 6.2 | 7.6331 | 625.6 | 106.4871 | 732.0871 | 0 | 732.0871 | 0 | 0 | 85.4543 | 14.5457 | 0 | 85.4543 | 14.5457 | 0
104 | 19 | April | 6.2 | 7.6331 | 625.6 | 9.261 | 634.861 | 0 | 634.861 | 0 | 0 | 98.5413 | 1.4587 | 0 | 98.5413 | 1.4587 | 0
104 | 20 | April | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
104 | 21 | April | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
104 | 22 | April | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
104 | 23 | April | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
104 | 24 | April | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
105 | 1 | April | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
105 | 2 | April | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
105 | 3 | April | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
105 | 4 | April | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
105 | 5 | April | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
105 | 6 | April | 6.2 | 7.6331 | 625.6 | 18.522 | 644.122 | 0 | 644.122 | 0 | 0 | 97.1245 | 2.8755 | 0 | 97.1245 | 2.8755 | 0
105 | 7 | April | 8.2 | 10.0954 | 1359.15 | 113.2439 | 1472.3939 | 0 | 1472.3939 | 0 | 0 | 92.3089 | 7.6911 | 0 | 92.3089 | 7.6911 | 0
105 | 8 | April | 7.7 | 9.4798 | 1059.95 | 229.5003 | 1289.4503 | 0 | 1289.4503 | 0 | 0 | 82.2017 | 17.7983 | 0 | 82.2017 | 17.7983 | 0
105 | 9 | April | 7.2 | 8.8642 | 908.65 | 378.5423 | 1287.1923 | 0 | 1287.1923 | 0 | 0 | 70.5916 | 29.4084 | 0 | 70.5916 | 29.4084 | 0
105 | 10 | April | 6.7 | 8.2487 | 761.6 | 495.3951 | 1256.9951 | 0 | 1256.9951 | 0 | 0 | 60.5889 | 39.4111 | 0 | 60.5889 | 39.4111 | 0
105 | 11 | April | 8.2 | 10.0954 | 1359.15 | 568.5253 | 1927.6753 | 0 | 1927.6753 | 0 | 0 | 70.5072 | 29.4928 | 0 | 70.5072 | 29.4928 | 0
105 | 12 | April | 5.7 | 7.0175 | 504.9 | 1202.4692 | 1707.3692 | 0 | 1707.3692 | 0 | 0 | 29.5718 | 70.4282 | 0 | 29.5718 | 70.4282 | 0
105 | 13 | April | 6.7 | 8.2487 | 761.6 | 839.3968 | 1600.9968 | 0 | 1600.9968 | 0 | 0 | 47.5704 | 52.4296 | 0 | 47.5704 | 52.4296 | 0
105 | 14 | April | 7.7 | 9.4798 | 1059.95 | 754.436 | 1814.386 | 0 | 1814.386 | 0 | 0 | 58.4192 | 41.5808 | 0 | 58.4192 | 41.5808 | 0
105 | 15 | April | 7.2 | 8.8642 | 908.65 | 588.3299 | 1496.9799 | 0 | 1496.9799 | 0 | 0 | 60.6989 | 39.3011 | 0 | 60.6989 | 39.3011 | 0
105 | 16 | April | 7.7 | 9.4798 | 1059.95 | 521.2614 | 1581.2114 | 0 | 1581.2114 | 0 | 0 | 67.034 | 32.966 | 0 | 67.034 | 32.966 | 0
105 | 17 | April | 8.2 | 10.0954 | 1359.15 | 318.9683 | 1678.1183 | 0 | 1678.1183 | 0 | 0 | 80.9925 | 19.0075 | 0 | 80.9925 | 19.0075 | 0
105 | 18 | April | 6.2 | 7.6331 | 625.6 | 97.59 | 723.19 | 0 | 723.19 | 0 | 0 | 86.5056 | 13.4944 | 0 | 86.5056 | 13.4944 | 0
105 | 19 | April | 5.1 | 6.2788 | 312.8 | 13.23 | 326.03 | 0 | 326.03 | 0 | 0 | 95.9421 | 4.0579 | 0 | 95.9421 | 4.0579 | 0
105 | 20 | April | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
105 | 21 | April | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
105 | 22 | April | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
105 | 23 | April | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
105 | 24 | April | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
106 | 1 | April | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
106 | 2 | April | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
106 | 3 | April | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
106 | 4 | April | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
106 | 5 | April | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
106 | 6 | April | 3.6 | 4.4321 | 75.65 | 19.845 | 95.495 | 0 | 95.495 | 0 | 0 | 79.2188 | 20.7812 | 0 | 79.2188 | 20.7812 | 0
106 | 7 | April | 4.6 | 5.6633 | 237.15 | 112.262 | 349.412 | 0 | 349.412 | 0 | 0 | 67.8712 | 32.1288 | 0 | 67.8712 | 32.1288 | 0
106 | 8 | April | 4.6 | 5.6633 | 237.15 | 233.911 | 471.061 | 0 | 471.061 | 0 | 0 | 50.3438 | 49.6562 | 0 | 50.3438 | 49.6562 | 0
106 | 9 | April | 5.7 | 7.0175 | 504.9 | 373.9585 | 878.8585 | 0 | 878.8585 | 0 | 0 | 57.4495 | 42.5505 | 0 | 57.4495 | 42.5505 | 0
106 | 10 | April | 5.7 | 7.0175 | 504.9 | 496.9841 | 1001.8841 | 0 | 1001.8841 | 0 | 0 | 50.3951 | 49.6049 | 0 | 50.3951 | 49.6049 | 0
106 | 11 | April | 5.1 | 6.2788 | 312.8 | 569.9367 | 882.7367 | 0 | 882.7367 | 0 | 0 | 35.4353 | 64.5647 | 0 | 35.4353 | 64.5647 | 0
106 | 12 | April | 4.6 | 5.6633 | 237.15 | 841.4783 | 1078.6283 | 0 | 1078.6283 | 0 | 0 | 21.9863 | 78.0137 | 0 | 21.9863 | 78.0137 | 0
106 | 13 | April | 5.1 | 6.2788 | 312.8 | 1165.0908 | 1477.8908 | 0 | 1477.8908 | 0 | 0 | 21.1653 | 78.8347 | 0 | 21.1653 | 78.8347 | 0
106 | 14 | April | 5.1 | 6.2788 | 312.8 | 544.5769 | 857.3769 | 0 | 857.3769 | 0 | 0 | 36.4834 | 63.5166 | 0 | 36.4834 | 63.5166 | 0
106 | 15 | April | 4.6 | 5.6633 | 237.15 | 613.7992 | 850.9492 | 0 | 850.9492 | 0 | 0 | 27.8689 | 72.1311 | 0 | 27.8689 | 72.1311 | 0
106 | 16 | April | 5.7 | 7.0175 | 504.9 | 622.3904 | 1127.2904 | 0 | 1127.2904 | 0 | 0 | 44.7888 | 55.2112 | 0 | 44.7888 | 55.2112 | 0
106 | 17 | April | 6.7 | 8.2487 | 761.6 | 292.8553 | 1054.4553 | 0 | 1054.4553 | 0 | 0 | 72.2269 | 27.7731 | 0 | 72.2269 | 27.7731 | 0
106 | 18 | April | 6.2 | 7.6331 | 625.6 | 84.672 | 710.272 | 0 | 710.272 | 0 | 0 | 88.0789 | 11.9211 | 0 | 88.0789 | 11.9211 | 0
106 | 19 | April | 5.7 | 7.0175 | 504.9 | 11.907 | 516.807 | 0 | 516.807 | 0 | 0 | 97.696 | 2.304 | 0 | 97.696 | 2.304 | 0
106 | 20 | April | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
106 | 21 | April | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
106 | 22 | April | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
106 | 23 | April | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
106 | 24 | April | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
107 | 1 | April | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
107 | 2 | April | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
107 | 3 | April | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
107 | 4 | April | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
107 | 5 | April | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
107 | 6 | April | 5.7 | 7.0175 | 504.9 | 13.23 | 518.13 | 0 | 518.13 | 0 | 0 | 97.4466 | 2.5534 | 0 | 97.4466 | 2.5534 | 0
107 | 7 | April | 6.2 | 7.6331 | 625.6 | 70.119 | 695.719 | 0 | 695.719 | 0 | 0 | 89.9214 | 10.0786 | 0 | 89.9214 | 10.0786 | 0
107 | 8 | April | 5.1 | 6.2788 | 312.8 | 262.2251 | 575.0251 | 0 | 575.0251 | 0 | 0 | 54.3976 | 45.6024 | 0 | 54.3976 | 45.6024 | 0
107 | 9 | April | 5.1 | 6.2788 | 312.8 | 375.6611 | 688.4611 | 0 | 688.4611 | 0 | 0 | 45.4347 | 54.5653 | 0 | 45.4347 | 54.5653 | 0
107 | 10 | April | 5.7 | 7.0175 | 504.9 | 1022.7474 | 1527.6474 | 0 | 1527.6474 | 0 | 0 | 33.0508 | 66.9492 | 0 | 33.0508 | 66.9492 | 0
107 | 11 | April | 5.7 | 7.0175 | 504.9 | 1186.6552 | 1691.5552 | 0 | 1691.5552 | 0 | 0 | 29.8483 | 70.1517 | 0 | 29.8483 | 70.1517 | 0
107 | 12 | April | 3.6 | 4.4321 | 75.65 | 1269.4843 | 1345.1343 | 0 | 1345.1343 | 0 | 0 | 5.624 | 94.376 | 0 | 5.624 | 94.376 | 0
107 | 13 | April | 3.1 | 3.8165 | 0 | 1362.6034 | 1362.6034 | 0 | 1362.6034 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
107 | 14 | April | 3.6 | 4.4321 | 75.65 | 1177.7851 | 1253.4351 | 0 | 1253.4351 | 0 | 0 | 6.0354 | 93.9646 | 0 | 6.0354 | 93.9646 | 0
107 | 15 | April | 4.1 | 5.0477 | 173.4 | 985.355 | 1158.755 | 0 | 1158.755 | 0 | 0 | 14.9643 | 85.0357 | 0 | 14.9643 | 85.0357 | 0
107 | 16 | April | 4.1 | 5.0477 | 173.4 | 666.1612 | 839.5612 | 0 | 839.5612 | 0 | 0 | 20.6536 | 79.3464 | 0 | 20.6536 | 79.3464 | 0
107 | 17 | April | 4.1 | 5.0477 | 173.4 | 350.9175 | 524.3175 | 0 | 524.3175 | 0 | 0 | 33.0716 | 66.9284 | 0 | 33.0716 | 66.9284 | 0
107 | 18 | April | 4.1 | 5.0477 | 173.4 | 106.992 | 280.392 | 0 | 280.392 | 0 | 0 | 61.842 | 38.158 | 0 | 61.842 | 38.158 | 0
107 | 19 | April | 3.6 | 4.4321 | 75.65 | 18.522 | 94.172 | 0 | 94.172 | 0 | 0 | 80.3317 | 19.6683 | 0 | 80.3317 | 19.6683 | 0
107 | 20 | April | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
107 | 21 | April | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
107 | 22 | April | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
107 | 23 | April | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
107 | 24 | April | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | 1 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | 2 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | 3 | April | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | 4 | April | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | 5 | April | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | 6 | April | 2.1 | 2.5854 | 0 | 13.23 | 13.23 | 0 | 13.23 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
108 | 7 | April | 2.1 | 2.5854 | 0 | 72.765 | 72.765 | 0 | 72.765 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
108 | 8 | April | 2.1 | 2.5854 | 0 | 148.176 | 148.176 | 0 | 148.176 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
108 | 9 | April | 3.6 | 4.4321 | 75.65 | 389.4778 | 465.1278 | 0 | 465.1278 | 0 | 0 | 16.2643 | 83.7357 | 0 | 16.2643 | 83.7357 | 0
108 | 10 | April | 3.6 | 4.4321 | 75.65 | 502.8183 | 578.4683 | 0 | 578.4683 | 0 | 0 | 13.0776 | 86.9224 | 0 | 13.0776 | 86.9224 | 0
108 | 11 | April | 5.1 | 6.2788 | 312.8 | 574.23 | 887.03 | 0 | 887.03 | 0 | 0 | 35.2637 | 64.7363 | 0 | 35.2637 | 64.7363 | 0
108 | 12 | April | 4.6 | 5.6633 | 237.15 | 608.7709 | 845.9209 | 0 | 845.9209 | 0 | 0 | 28.0345 | 71.9655 | 0 | 28.0345 | 71.9655 | 0
108 | 13 | April | 5.1 | 6.2788 | 312.8 | 598.7171 | 911.5171 | 0 | 911.5171 | 0 | 0 | 34.3164 | 65.6836 | 0 | 34.3164 | 65.6836 | 0
108 | 14 | April | 6.2 | 7.6331 | 625.6 | 546.1631 | 1171.7631 | 0 | 1171.7631 | 0 | 0 | 53.3896 | 46.6104 | 0 | 53.3896 | 46.6104 | 0
108 | 15 | April | 5.7 | 7.0175 | 504.9 | 456.4678 | 961.3678 | 0 | 961.3678 | 0 | 0 | 52.5189 | 47.4811 | 0 | 52.5189 | 47.4811 | 0
108 | 16 | April | 5.7 | 7.0175 | 504.9 | 331.1189 | 836.0189 | 0 | 836.0189 | 0 | 0 | 60.3934 | 39.6066 | 0 | 60.3934 | 39.6066 | 0
108 | 17 | April | 6.2 | 7.6331 | 625.6 | 261.1076 | 886.7076 | 0 | 886.7076 | 0 | 0 | 70.5531 | 29.4469 | 0 | 70.5531 | 29.4469 | 0
108 | 18 | April | 5.7 | 7.0175 | 504.9 | 109.2341 | 614.1341 | 0 | 614.1341 | 0 | 0 | 82.2133 | 17.7867 | 0 | 82.2133 | 17.7867 | 0
108 | 19 | April | 5.7 | 7.0175 | 504.9 | 23.814 | 528.714 | 0 | 528.714 | 0 | 0 | 95.4959 | 4.5041 | 0 | 95.4959 | 4.5041 | 0
108 | 20 | April | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
108 | 21 | April | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
108 | 22 | April | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
108 | 23 | April | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
108 | 24 | April | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
109 | 1 | April | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
109 | 2 | April | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
109 | 3 | April | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
109 | 4 | April | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
109 | 5 | April | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
109 | 6 | April | 8.2 | 10.0954 | 1359.15 | 23.814 | 1382.964 | 0 | 1382.964 | 0 | 0 | 98.278 | 1.722 | 0 | 98.278 | 1.722 | 0
109 | 7 | April | 7.7 | 9.4798 | 1059.95 | 122.7843 | 1182.7343 | 0 | 1182.7343 | 0 | 0 | 89.6186 | 10.3814 | 0 | 89.6186 | 10.3814 | 0
109 | 8 | April | 7.7 | 9.4798 | 1059.95 | 370.2731 | 1430.2231 | 0 | 1430.2231 | 0 | 0 | 74.1108 | 25.8892 | 0 | 74.1108 | 25.8892 | 0
109 | 9 | April | 7.2 | 8.8642 | 908.65 | 389.6593 | 1298.3093 | 0 | 1298.3093 | 0 | 0 | 69.9872 | 30.0128 | 0 | 69.9872 | 30.0128 | 0
109 | 10 | April | 7.7 | 9.4798 | 1059.95 | 488.9328 | 1548.8828 | 0 | 1548.8828 | 0 | 0 | 68.4332 | 31.5668 | 0 | 68.4332 | 31.5668 | 0
109 | 11 | April | 8.7 | 10.711 | 1490.05 | 559.0473 | 2049.0973 | 1 | 2000 | 49.0973 | 2.4549 | 72.7174 | 25.4975 | 8.7823 | 72.0476 | 27.2826 | 3.295
109 | 12 | April | 8.2 | 10.0954 | 1359.15 | 616.0474 | 1975.1974 | 0 | 1975.1974 | 0 | 0 | 68.8108 | 31.1892 | 0 | 68.8108 | 31.1892 | 0
109 | 13 | April | 9.3 | 11.4496 | 1598.85 | 1154.6223 | 2753.4723 | 1 | 2000 | 753.4723 | 37.6736 | 58.0667 | 20.0575 | 65.257 | 42.2689 | 41.9333 | 47.1259
109 | 14 | April | 10.3 | 12.6808 | 1694.9 | 774.787 | 2469.687 | 1 | 2000 | 469.687 | 23.4844 | 68.6281 | 15.255 | 60.6214 | 61.2606 | 31.3719 | 27.7118
109 | 15 | April | 10.3 | 12.6808 | 1694.9 | 945.2584 | 2640.1584 | 1 | 2000 | 640.1584 | 32.0079 | 64.1969 | 15.255 | 67.7231 | 52.7371 | 35.8031 | 37.7697
109 | 16 | April | 9.8 | 12.0652 | 1683.85 | 454.4534 | 2138.3034 | 1 | 2000 | 138.3034 | 6.9152 | 78.747 | 15.8075 | 30.4329 | 77.2773 | 21.253 | 8.2135
109 | 17 | April | 10.3 | 12.6808 | 1694.9 | 266.6633 | 1961.5633 | 0 | 1961.5633 | 0 | 0 | 86.4056 | 13.5944 | 0 | 86.4056 | 13.5944 | 0
109 | 18 | April | 8.2 | 10.0954 | 1359.15 | 115.6872 | 1474.8372 | 0 | 1474.8372 | 0 | 0 | 92.1559 | 7.8441 | 0 | 92.1559 | 7.8441 | 0
109 | 19 | April | 8.7 | 10.711 | 1490.05 | 17.199 | 1507.249 | 0 | 1507.249 | 0 | 0 | 98.8589 | 1.1411 | 0 | 98.8589 | 1.1411 | 0
109 | 20 | April | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
109 | 21 | April | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
109 | 22 | April | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
109 | 23 | April | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
109 | 24 | April | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
110 | 1 | April | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
110 | 2 | April | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
110 | 3 | April | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
110 | 4 | April | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
110 | 5 | April | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
110 | 6 | April | 7.2 | 8.8642 | 908.65 | 46.2966 | 954.9466 | 0 | 954.9466 | 0 | 0 | 95.1519 | 4.8481 | 0 | 95.1519 | 4.8481 | 0
110 | 7 | April | 6.7 | 8.2487 | 761.6 | 273.4547 | 1035.0547 | 0 | 1035.0547 | 0 | 0 | 73.5807 | 26.4193 | 0 | 73.5807 | 26.4193 | 0
110 | 8 | April | 6.2 | 7.6331 | 625.6 | 575.1237 | 1200.7237 | 0 | 1200.7237 | 0 | 0 | 52.1019 | 47.8981 | 0 | 52.1019 | 47.8981 | 0
110 | 9 | April | 5.7 | 7.0175 | 504.9 | 400.9182 | 905.8182 | 0 | 905.8182 | 0 | 0 | 55.7397 | 44.2603 | 0 | 55.7397 | 44.2603 | 0
110 | 10 | April | 5.1 | 6.2788 | 312.8 | 671.4322 | 984.2322 | 0 | 984.2322 | 0 | 0 | 31.7811 | 68.2189 | 0 | 31.7811 | 68.2189 | 0
110 | 11 | April | 5.1 | 6.2788 | 312.8 | 1327.7934 | 1640.5934 | 0 | 1640.5934 | 0 | 0 | 19.0663 | 80.9337 | 0 | 19.0663 | 80.9337 | 0
110 | 12 | April | 5.1 | 6.2788 | 312.8 | 1517.2152 | 1830.0152 | 0 | 1830.0152 | 0 | 0 | 17.0928 | 82.9072 | 0 | 17.0928 | 82.9072 | 0
110 | 13 | April | 4.6 | 5.6633 | 237.15 | 1437.2738 | 1674.4238 | 0 | 1674.4238 | 0 | 0 | 14.1631 | 85.8369 | 0 | 14.1631 | 85.8369 | 0
110 | 14 | April | 4.6 | 5.6633 | 237.15 | 1290.3922 | 1527.5422 | 0 | 1527.5422 | 0 | 0 | 15.5249 | 84.4751 | 0 | 15.5249 | 84.4751 | 0
110 | 15 | April | 3.6 | 4.4321 | 75.65 | 988.871 | 1064.521 | 0 | 1064.521 | 0 | 0 | 7.1065 | 92.8935 | 0 | 7.1065 | 92.8935 | 0
110 | 16 | April | 3.6 | 4.4321 | 75.65 | 694.0659 | 769.7159 | 0 | 769.7159 | 0 | 0 | 9.8283 | 90.1717 | 0 | 9.8283 | 90.1717 | 0
110 | 17 | April | 2.6 | 3.201 | 0 | 368.2372 | 368.2372 | 0 | 368.2372 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
110 | 18 | April | 2.1 | 2.5854 | 0 | 124.0115 | 124.0115 | 0 | 124.0115 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
110 | 19 | April | 1.5 | 1.8467 | 0 | 26.46 | 26.46 | 0 | 26.46 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
110 | 20 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110 | 21 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110 | 22 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110 | 23 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110 | 24 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111 | 1 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111 | 2 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111 | 3 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111 | 4 | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111 | 5 | April | 0 | 0 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
111 | 6 | April | 0 | 0 | 0 | 52.5531 | 52.5531 | 0 | 52.5531 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
111 | 7 | April | 3.1 | 3.8165 | 0 | 294.1628 | 294.1628 | 0 | 294.1628 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
111 | 8 | April | 5.1 | 6.2788 | 312.8 | 618.17 | 930.97 | 0 | 930.97 | 0 | 0 | 33.5994 | 66.4006 | 0 | 33.5994 | 66.4006 | 0
111 | 9 | April | 4.1 | 5.0477 | 173.4 | 943.077 | 1116.477 | 0 | 1116.477 | 0 | 0 | 15.531 | 84.469 | 0 | 15.531 | 84.469 | 0
111 | 10 | April | 4.6 | 5.6633 | 237.15 | 881.0459 | 1118.1959 | 0 | 1118.1959 | 0 | 0 | 21.2083 | 78.7917 | 0 | 21.2083 | 78.7917 | 0
111 | 11 | April | 4.6 | 5.6633 | 237.15 | 1368.345 | 1605.495 | 0 | 1605.495 | 0 | 0 | 14.7711 | 85.2289 | 0 | 14.7711 | 85.2289 | 0
111 | 12 | April | 3.6 | 4.4321 | 75.65 | 1487.6414 | 1563.2914 | 0 | 1563.2914 | 0 | 0 | 4.8391 | 95.1609 | 0 | 4.8391 | 95.1609 | 0
111 | 13 | April | 4.6 | 5.6633 | 237.15 | 611.6374 | 848.7874 | 0 | 848.7874 | 0 | 0 | 27.9399 | 72.0601 | 0 | 27.9399 | 72.0601 | 0
111 | 14 | April | 4.6 | 5.6633 | 237.15 | 558.5456 | 795.6956 | 0 | 795.6956 | 0 | 0 | 29.8041 | 70.1959 | 0 | 29.8041 | 70.1959 | 0
111 | 15 | April | 8.2 | 10.0954 | 1359.15 | 457.191 | 1816.341 | 0 | 1816.341 | 0 | 0 | 74.829 | 25.171 | 0 | 74.829 | 25.171 | 0
111 | 16 | April | 8.2 | 10.0954 | 1359.15 | 341.3921 | 1700.5421 | 0 | 1700.5421 | 0 | 0 | 79.9245 | 20.0755 | 0 | 79.9245 | 20.0755 | 0
111 | 17 | April | 6.2 | 7.6331 | 625.6 | 214.8229 | 840.4229 | 0 | 840.4229 | 0 | 0 | 74.4387 | 25.5613 | 0 | 74.4387 | 25.5613 | 0
111 | 18 | April | 6.2 | 7.6331 | 625.6 | 97.9727 | 723.5727 | 0 | 723.5727 | 0 | 0 | 86.4599 | 13.5401 | 0 | 86.4599 | 13.5401 | 0
111 | 19 | April | 5.7 | 7.0175 | 504.9 | 15.876 | 520.776 | 0 | 520.776 | 0 | 0 | 96.9515 | 3.0485 | 0 | 96.9515 | 3.0485 | 0
111 | 20 | April | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
111 | 21 | April | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
111 | 22 | April | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
111 | 23 | April | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
111 | 24 | April | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
112 | 1 | April | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
112 | 2 | April | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
112 | 3 | April | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
112 | 4 | April | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
112 | 5 | April | 4.1 | 5.0477 | 173.4 | 1.323 | 174.723 | 0 | 174.723 | 0 | 0 | 99.2428 | 0.7572 | 0 | 99.2428 | 0.7572 | 0
112 | 6 | April | 6.2 | 7.6331 | 625.6 | 39.69 | 665.29 | 0 | 665.29 | 0 | 0 | 94.0342 | 5.9658 | 0 | 94.0342 | 5.9658 | 0
112 | 7 | April | 6.2 | 7.6331 | 625.6 | 185.084 | 810.684 | 0 | 810.684 | 0 | 0 | 77.1694 | 22.8306 | 0 | 77.1694 | 22.8306 | 0
112 | 8 | April | 6.7 | 8.2487 | 761.6 | 379.6872 | 1141.2872 | 0 | 1141.2872 | 0 | 0 | 66.7317 | 33.2683 | 0 | 66.7317 | 33.2683 | 0
112 | 9 | April | 6.2 | 7.6331 | 625.6 | 398.368 | 1023.968 | 0 | 1023.968 | 0 | 0 | 61.0957 | 38.9043 | 0 | 61.0957 | 38.9043 | 0
112 | 10 | April | 7.2 | 8.8642 | 908.65 | 498.6701 | 1407.3201 | 0 | 1407.3201 | 0 | 0 | 64.566 | 35.434 | 0 | 64.566 | 35.434 | 0
112 | 11 | April | 6.7 | 8.2487 | 761.6 | 767.1938 | 1528.7938 | 0 | 1528.7938 | 0 | 0 | 49.8171 | 50.1829 | 0 | 49.8171 | 50.1829 | 0
112 | 12 | April | 6.7 | 8.2487 | 761.6 | 817.8595 | 1579.4595 | 0 | 1579.4595 | 0 | 0 | 48.219 | 51.781 | 0 | 48.219 | 51.781 | 0
112 | 13 | April | 6.2 | 7.6331 | 625.6 | 1260.3359 | 1885.9359 | 0 | 1885.9359 | 0 | 0 | 33.1719 | 66.8281 | 0 | 33.1719 | 66.8281 | 0
112 | 14 | April | 7.2 | 8.8642 | 908.65 | 1211.8033 | 2120.4533 | 1 | 2000 | 120.4533 | 6.0227 | 42.8517 | 54.5675 | 9.94 | 39.4098 | 57.1483 | 13.2563
112 | 15 | April | 5.1 | 6.2788 | 312.8 | 859.1347 | 1171.9347 | 0 | 1171.9347 | 0 | 0 | 26.6909 | 73.3091 | 0 | 26.6909 | 73.3091 | 0
112 | 16 | April | 5.1 | 6.2788 | 312.8 | 547.5743 | 860.3743 | 0 | 860.3743 | 0 | 0 | 36.3563 | 63.6437 | 0 | 36.3563 | 63.6437 | 0
112 | 17 | April | 4.6 | 5.6633 | 237.15 | 316.9379 | 554.0879 | 0 | 554.0879 | 0 | 0 | 42.8001 | 57.1999 | 0 | 42.8001 | 57.1999 | 0
112 | 18 | April | 3.6 | 4.4321 | 75.65 | 129.9111 | 205.5611 | 0 | 205.5611 | 0 | 0 | 36.8017 | 63.1983 | 0 | 36.8017 | 63.1983 | 0
112 | 19 | April | 2.6 | 3.201 | 0 | 26.46 | 26.46 | 0 | 26.46 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
112 | 20 | April | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112 | 21 | April | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112 | 22 | April | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112 | 23 | April | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112 | 24 | April | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
113 | 1 | April | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
113 | 2 | April | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
113 | 3 | April | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
113 | 4 | April | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
113 | 5 | April | 5.1 | 6.2788 | 312.8 | 1.323 | 314.123 | 0 | 314.123 | 0 | 0 | 99.5788 | 0.42117 | 0 | 99.5788 | 0.42117 | 0
113 | 6 | April | 6.2 | 7.6331 | 625.6 | 34.398 | 659.998 | 0 | 659.998 | 0 | 0 | 94.7882 | 5.2118 | 0 | 94.7882 | 5.2118 | 0
113 | 7 | April | 5.7 | 7.0175 | 504.9 | 137.5568 | 642.4568 | 0 | 642.4568 | 0 | 0 | 78.5889 | 21.4111 | 0 | 78.5889 | 21.4111 | 0
113 | 8 | April | 6.2 | 7.6331 | 625.6 | 261.5967 | 887.1967 | 0 | 887.1967 | 0 | 0 | 70.5142 | 29.4858 | 0 | 70.5142 | 29.4858 | 0
113 | 9 | April | 6.7 | 8.2487 | 761.6 | 236.2318 | 997.8318 | 0 | 997.8318 | 0 | 0 | 76.3255 | 23.6745 | 0 | 76.3255 | 23.6745 | 0
113 | 10 | April | 8.2 | 10.0954 | 1359.15 | 524.5501 | 1883.7001 | 0 | 1883.7001 | 0 | 0 | 72.1532 | 27.8468 | 0 | 72.1532 | 27.8468 | 0
113 | 11 | April | 8.2 | 10.0954 | 1359.15 | 592.7526 | 1951.9026 | 0 | 1951.9026 | 0 | 0 | 69.6321 | 30.3679 | 0 | 69.6321 | 30.3679 | 0
113 | 12 | April | 8.2 | 10.0954 | 1359.15 | 624.2689 | 1983.4189 | 0 | 1983.4189 | 0 | 0 | 68.5256 | 31.4744 | 0 | 68.5256 | 31.4744 | 0
113 | 13 | April | 7.2 | 8.8642 | 908.65 | 846.8449 | 1755.4949 | 0 | 1755.4949 | 0 | 0 | 51.7603 | 48.2397 | 0 | 51.7603 | 48.2397 | 0
113 | 14 | April | 7.7 | 9.4798 | 1059.95 | 557.3012 | 1617.2512 | 0 | 1617.2512 | 0 | 0 | 65.5402 | 34.4598 | 0 | 65.5402 | 34.4598 | 0
113 | 15 | April | 7.2 | 8.8642 | 908.65 | 472.5918 | 1381.2418 | 0 | 1381.2418 | 0 | 0 | 65.785 | 34.215 | 0 | 65.785 | 34.215 | 0
113 | 16 | April | 6.7 | 8.2487 | 761.6 | 347.6287 | 1109.2287 | 0 | 1109.2287 | 0 | 0 | 68.6603 | 31.3397 | 0 | 68.6603 | 31.3397 | 0
113 | 17 | April | 7.7 | 9.4798 | 1059.95 | 220.6366 | 1280.5866 | 0 | 1280.5866 | 0 | 0 | 82.7707 | 17.2293 | 0 | 82.7707 | 17.2293 | 0
113 | 18 | April | 6.7 | 8.2487 | 761.6 | 102.022 | 863.622 | 0 | 863.622 | 0 | 0 | 88.1867 | 11.8133 | 0 | 88.1867 | 11.8133 | 0
113 | 19 | April | 4.6 | 5.6633 | 237.15 | 22.491 | 259.641 | 0 | 259.641 | 0 | 0 | 91.3377 | 8.6623 | 0 | 91.3377 | 8.6623 | 0
113 | 20 | April | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
113 | 21 | April | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
113 | 22 | April | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
113 | 23 | April | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
113 | 24 | April | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
114 | 1 | April | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
114 | 2 | April | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
114 | 3 | April | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
114 | 4 | April | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
114 | 5 | April | 6.2 | 7.6331 | 625.6 | 1.323 | 626.923 | 0 | 626.923 | 0 | 0 | 99.789 | 0.21103 | 0 | 99.789 | 0.21103 | 0
114 | 6 | April | 5.1 | 6.2788 | 312.8 | 35.721 | 348.521 | 0 | 348.521 | 0 | 0 | 89.7507 | 10.2493 | 0 | 89.7507 | 10.2493 | 0
114 | 7 | April | 7.7 | 9.4798 | 1059.95 | 140.8055 | 1200.7555 | 0 | 1200.7555 | 0 | 0 | 88.2736 | 11.7264 | 0 | 88.2736 | 11.7264 | 0
114 | 8 | April | 7.2 | 8.8642 | 908.65 | 264.2896 | 1172.9396 | 0 | 1172.9396 | 0 | 0 | 77.4678 | 22.5322 | 0 | 77.4678 | 22.5322 | 0
114 | 9 | April | 10.8 | 13.2964 | 1698.3 | 403.1436 | 2101.4436 | 1 | 2000 | 101.4436 | 5.0722 | 80.8159 | 15.085 | 25.1631 | 79.8428 | 19.1841 | 5.9732
114 | 10 | April | 10.8 | 13.2964 | 1698.3 | 297.9668 | 1996.2668 | 0 | 1996.2668 | 0 | 0 | 85.0738 | 14.9262 | 0 | 85.0738 | 14.9262 | 0
114 | 11 | April | 10.3 | 12.6808 | 1694.9 | 345.4987 | 2040.3987 | 1 | 2000 | 40.3987 | 2.0199 | 83.0671 | 15.255 | 11.6929 | 82.7251 | 16.9329 | 2.3835
114 | 12 | April | 11.3 | 13.9119 | 1700 | 366.0711 | 2066.0711 | 1 | 2000 | 66.0711 | 3.3036 | 82.2818 | 15 | 18.0487 | 81.6964 | 17.7182 | 3.8865
114 | 13 | April | 10.8 | 13.2964 | 1698.3 | 362.4879 | 2060.7879 | 1 | 2000 | 60.7879 | 3.0394 | 82.4102 | 15.085 | 16.7696 | 81.8756 | 17.5898 | 3.5793
114 | 14 | April | 10.3 | 12.6808 | 1694.9 | 333.6731 | 2028.5731 | 1 | 2000 | 28.5731 | 1.4287 | 83.5513 | 15.255 | 8.5632 | 83.3163 | 16.4487 | 1.6858
114 | 15 | April | 9.8 | 12.0652 | 1683.85 | 283.5834 | 1967.4334 | 0 | 1967.4334 | 0 | 0 | 85.5861 | 14.4139 | 0 | 85.5861 | 14.4139 | 0
114 | 16 | April | 9.3 | 11.4496 | 1598.85 | 215.9259 | 1814.7759 | 0 | 1814.7759 | 0 | 0 | 88.1018 | 11.8982 | 0 | 88.1018 | 11.8982 | 0
114 | 17 | April | 9.3 | 11.4496 | 1598.85 | 222.6066 | 1821.4566 | 0 | 1821.4566 | 0 | 0 | 87.7786 | 12.2214 | 0 | 87.7786 | 12.2214 | 0
114 | 18 | April | 8 | 9.8492 | 1213.8 | 104.7507 | 1318.5507 | 0 | 1318.5507 | 0 | 0 | 92.0556 | 7.9444 | 0 | 92.0556 | 7.9444 | 0
114 | 19 | April | 6.7 | 8.2487 | 761.6 | 18.522 | 780.122 | 0 | 780.122 | 0 | 0 | 97.6258 | 2.3742 | 0 | 97.6258 | 2.3742 | 0
114 | 20 | April | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
114 | 21 | April | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
114 | 22 | April | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
114 | 23 | April | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
114 | 24 | April | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115 | 1 | April | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115 | 2 | April | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115 | 3 | April | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115 | 4 | April | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115 | 5 | April | 2.6 | 3.201 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
115 | 6 | April | 5.1 | 6.2788 | 312.8 | 23.814 | 336.614 | 0 | 336.614 | 0 | 0 | 92.9254 | 7.0746 | 0 | 92.9254 | 7.0746 | 0
115 | 7 | April | 4.6 | 5.6633 | 237.15 | 88.641 | 325.791 | 0 | 325.791 | 0 | 0 | 72.7921 | 27.2079 | 0 | 72.7921 | 27.2079 | 0
115 | 8 | April | 4.6 | 5.6633 | 237.15 | 164.052 | 401.202 | 0 | 401.202 | 0 | 0 | 59.1099 | 40.8901 | 0 | 59.1099 | 40.8901 | 0
115 | 9 | April | 5.7 | 7.0175 | 504.9 | 238.9017 | 743.8017 | 0 | 743.8017 | 0 | 0 | 67.881 | 32.119 | 0 | 67.881 | 32.119 | 0
115 | 10 | April | 5.7 | 7.0175 | 504.9 | 302.473 | 807.373 | 0 | 807.373 | 0 | 0 | 62.5362 | 37.4638 | 0 | 62.5362 | 37.4638 | 0
115 | 11 | April | 5.1 | 6.2788 | 312.8 | 345.526 | 658.326 | 0 | 658.326 | 0 | 0 | 47.5144 | 52.4856 | 0 | 47.5144 | 52.4856 | 0
115 | 12 | April | 6.2 | 7.6331 | 625.6 | 361.0537 | 986.6537 | 0 | 986.6537 | 0 | 0 | 63.4062 | 36.5938 | 0 | 63.4062 | 36.5938 | 0
115 | 13 | April | 6.7 | 8.2487 | 761.6 | 362.5087 | 1124.1087 | 0 | 1124.1087 | 0 | 0 | 67.7515 | 32.2485 | 0 | 67.7515 | 32.2485 | 0
115 | 14 | April | 7.2 | 8.8642 | 908.65 | 333.6703 | 1242.3203 | 0 | 1242.3203 | 0 | 0 | 73.1414 | 26.8586 | 0 | 73.1414 | 26.8586 | 0
115 | 15 | April | 6.2 | 7.6331 | 625.6 | 283.5973 | 909.1973 | 0 | 909.1973 | 0 | 0 | 68.8079 | 31.1921 | 0 | 68.8079 | 31.1921 | 0
115 | 16 | April | 6.2 | 7.6331 | 625.6 | 217.2521 | 842.8521 | 0 | 842.8521 | 0 | 0 | 74.2242 | 25.7758 | 0 | 74.2242 | 25.7758 | 0
115 | 17 | April | 4.9 | 6.0326 | 312.8 | 141.561 | 454.361 | 0 | 454.361 | 0 | 0 | 68.8439 | 31.1561 | 0 | 68.8439 | 31.1561 | 0
115 | 18 | April | 3.6 | 4.4321 | 75.65 | 67.473 | 143.123 | 0 | 143.123 | 0 | 0 | 52.8566 | 47.1434 | 0 | 52.8566 | 47.1434 | 0
115 | 19 | April | 4.4 | 5.417 | 173.4 | 11.907 | 185.307 | 0 | 185.307 | 0 | 0 | 93.5744 | 6.4256 | 0 | 93.5744 | 6.4256 | 0
115 | 20 | April | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
115 | 21 | April | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
115 | 22 | April | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
115 | 23 | April | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
115 | 24 | April | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
116 | 1 | April | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
116 | 2 | April | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
116 | 3 | April | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
116 | 4 | April | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
116 | 5 | April | 5.7 | 7.0175 | 504.9 | 1.323 | 506.223 | 0 | 506.223 | 0 | 0 | 99.7387 | 0.26135 | 0 | 99.7387 | 0.26135 | 0
116 | 6 | April | 5.7 | 7.0175 | 504.9 | 25.137 | 530.037 | 0 | 530.037 | 0 | 0 | 95.2575 | 4.7425 | 0 | 95.2575 | 4.7425 | 0
116 | 7 | April | 6.2 | 7.6331 | 625.6 | 89.964 | 715.564 | 0 | 715.564 | 0 | 0 | 87.4275 | 12.5725 | 0 | 87.4275 | 12.5725 | 0
116 | 8 | April | 5.7 | 7.0175 | 504.9 | 166.698 | 671.598 | 0 | 671.598 | 0 | 0 | 75.1789 | 24.8211 | 0 | 75.1789 | 24.8211 | 0
116 | 9 | April | 5.7 | 7.0175 | 504.9 | 240.236 | 745.136 | 0 | 745.136 | 0 | 0 | 67.7594 | 32.2406 | 0 | 67.7594 | 32.2406 | 0
116 | 10 | April | 6.7 | 8.2487 | 761.6 | 303.8214 | 1065.4214 | 0 | 1065.4214 | 0 | 0 | 71.4834 | 28.5166 | 0 | 71.4834 | 28.5166 | 0
116 | 11 | April | 5.7 | 7.0175 | 504.9 | 346.8752 | 851.7752 | 0 | 851.7752 | 0 | 0 | 59.2762 | 40.7238 | 0 | 59.2762 | 40.7238 | 0
116 | 12 | April | 5.7 | 7.0175 | 504.9 | 362.3844 | 867.2844 | 0 | 867.2844 | 0 | 0 | 58.2162 | 41.7838 | 0 | 58.2162 | 41.7838 | 0
116 | 13 | April | 6.2 | 7.6331 | 625.6 | 362.5286 | 988.1286 | 0 | 988.1286 | 0 | 0 | 63.3116 | 36.6884 | 0 | 63.3116 | 36.6884 | 0
116 | 14 | April | 6.7 | 8.2487 | 761.6 | 333.6869 | 1095.2869 | 0 | 1095.2869 | 0 | 0 | 69.5343 | 30.4657 | 0 | 69.5343 | 30.4657 | 0
116 | 15 | April | 5.7 | 7.0175 | 504.9 | 284.934 | 789.834 | 0 | 789.834 | 0 | 0 | 63.9248 | 36.0752 | 0 | 63.9248 | 36.0752 | 0
116 | 16 | April | 5.1 | 6.2788 | 312.8 | 217.2554 | 530.0554 | 0 | 530.0554 | 0 | 0 | 59.0127 | 40.9873 | 0 | 59.0127 | 40.9873 | 0
116 | 17 | April | 4.1 | 5.0477 | 173.4 | 142.884 | 316.284 | 0 | 316.284 | 0 | 0 | 54.8241 | 45.1759 | 0 | 54.8241 | 45.1759 | 0
116 | 18 | April | 4.1 | 5.0477 | 173.4 | 68.796 | 242.196 | 0 | 242.196 | 0 | 0 | 71.5949 | 28.4051 | 0 | 71.5949 | 28.4051 | 0
116 | 19 | April | 4.6 | 5.6633 | 237.15 | 11.907 | 249.057 | 0 | 249.057 | 0 | 0 | 95.2192 | 4.7808 | 0 | 95.2192 | 4.7808 | 0
116 | 20 | April | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
116 | 21 | April | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
116 | 22 | April | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
116 | 23 | April | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
116 | 24 | April | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
117 | 1 | April | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
117 | 2 | April | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
117 | 3 | April | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
117 | 4 | April | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
117 | 5 | April | 3.1 | 3.8165 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
117 | 6 | April | 1.5 | 1.8467 | 0 | 27.783 | 27.783 | 0 | 27.783 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
117 | 7 | April | 1.5 | 1.8467 | 0 | 92.61 | 92.61 | 0 | 92.61 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
117 | 8 | April | 2.1 | 2.5854 | 0 | 168.021 | 168.021 | 0 | 168.021 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
117 | 9 | April | 3.1 | 3.8165 | 0 | 241.57 | 241.57 | 0 | 241.57 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
117 | 10 | April | 3.6 | 4.4321 | 75.65 | 305.1689 | 380.8189 | 0 | 380.8189 | 0 | 0 | 19.8651 | 80.1349 | 0 | 19.8651 | 80.1349 | 0
117 | 11 | April | 3.1 | 3.8165 | 0 | 348.2232 | 348.2232 | 0 | 348.2232 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
117 | 12 | April | 2.1 | 2.5854 | 0 | 634.1797 | 634.1797 | 0 | 634.1797 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
117 | 13 | April | 3.6 | 4.4321 | 75.65 | 600.3998 | 676.0498 | 0 | 676.0498 | 0 | 0 | 11.19 | 88.81 | 0 | 11.19 | 88.81 | 0
117 | 14 | April | 3.6 | 4.4321 | 75.65 | 564.519 | 640.169 | 0 | 640.169 | 0 | 0 | 11.8172 | 88.1828 | 0 | 11.8172 | 88.1828 | 0
117 | 15 | April | 2.1 | 2.5854 | 0 | 769.1276 | 769.1276 | 0 | 769.1276 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
117 | 16 | April | 2.1 | 2.5854 | 0 | 358.5518 | 358.5518 | 0 | 358.5518 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
117 | 17 | April | 2.6 | 3.201 | 0 | 230.055 | 230.055 | 0 | 230.055 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
117 | 18 | April | 3.1 | 3.8165 | 0 | 132.5915 | 132.5915 | 0 | 132.5915 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
117 | 19 | April | 3.6 | 4.4321 | 75.65 | 31.752 | 107.402 | 0 | 107.402 | 0 | 0 | 70.4363 | 29.5637 | 0 | 70.4363 | 29.5637 | 0
117 | 20 | April | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
117 | 21 | April | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
117 | 22 | April | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
117 | 23 | April | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
117 | 24 | April | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
118 | 1 | April | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
118 | 2 | April | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
118 | 3 | April | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
118 | 4 | April | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
118 | 5 | April | 5.1 | 6.2788 | 312.8 | 1.323 | 314.123 | 0 | 314.123 | 0 | 0 | 99.5788 | 0.42117 | 0 | 99.5788 | 0.42117 | 0
118 | 6 | April | 5.1 | 6.2788 | 312.8 | 46.305 | 359.105 | 0 | 359.105 | 0 | 0 | 87.1054 | 12.8946 | 0 | 87.1054 | 12.8946 | 0
118 | 7 | April | 5.7 | 7.0175 | 504.9 | 93.933 | 598.833 | 0 | 598.833 | 0 | 0 | 84.314 | 15.686 | 0 | 84.314 | 15.686 | 0
118 | 8 | April | 6.7 | 8.2487 | 761.6 | 285.0121 | 1046.6121 | 0 | 1046.6121 | 0 | 0 | 72.7681 | 27.2319 | 0 | 72.7681 | 27.2319 | 0
118 | 9 | April | 7.7 | 9.4798 | 1059.95 | 404.3165 | 1464.2665 | 0 | 1464.2665 | 0 | 0 | 72.3878 | 27.6122 | 0 | 72.3878 | 27.6122 | 0
118 | 10 | April | 9.3 | 11.4496 | 1598.85 | 729.6551 | 2328.5051 | 1 | 2000 | 328.5051 | 16.4253 | 68.6642 | 20.0575 | 45.022 | 63.5172 | 31.3358 | 20.5463
118 | 11 | April | 10.8 | 13.2964 | 1698.3 | 1276.4337 | 2974.7337 | 1 | 2000 | 974.7337 | 48.7367 | 57.0908 | 15.085 | 76.3638 | 36.1783 | 42.9092 | 57.3947
118 | 12 | April | 10.3 | 12.6808 | 1694.9 | 905.8394 | 2600.7394 | 1 | 2000 | 600.7394 | 30.037 | 65.1699 | 15.255 | 66.3185 | 54.708 | 34.8301 | 35.4439
118 | 13 | April | 11.3 | 13.9119 | 1700 | 824.6398 | 2524.6398 | 1 | 2000 | 524.6398 | 26.232 | 67.3363 | 15 | 63.6205 | 58.768 | 32.6637 | 30.8612
118 | 14 | April | 10.3 | 12.6808 | 1694.9 | 952.082 | 2646.982 | 1 | 2000 | 646.982 | 32.3491 | 64.0314 | 15.255 | 67.9544 | 52.3959 | 35.9686 | 38.1723
118 | 15 | April | 8.7 | 10.711 | 1490.05 | 288.5039 | 1778.5539 | 0 | 1778.5539 | 0 | 0 | 83.7787 | 16.2213 | 0 | 83.7787 | 16.2213 | 0
118 | 16 | April | 6.2 | 7.6331 | 625.6 | 474.3739 | 1099.9739 | 0 | 1099.9739 | 0 | 0 | 56.8741 | 43.1259 | 0 | 56.8741 | 43.1259 | 0
118 | 17 | April | 6.2 | 7.6331 | 625.6 | 230.3953 | 855.9953 | 0 | 855.9953 | 0 | 0 | 73.0845 | 26.9155 | 0 | 73.0845 | 26.9155 | 0
118 | 18 | April | 8.7 | 10.711 | 1490.05 | 114.1287 | 1604.1787 | 0 | 1604.1787 | 0 | 0 | 92.8855 | 7.1145 | 0 | 92.8855 | 7.1145 | 0
118 | 19 | April | 8.2 | 10.0954 | 1359.15 | 14.553 | 1373.703 | 0 | 1373.703 | 0 | 0 | 98.9406 | 1.0594 | 0 | 98.9406 | 1.0594 | 0
118 | 20 | April | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
118 | 21 | April | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
118 | 22 | April | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
118 | 23 | April | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
118 | 24 | April | 10.5 | 12.927 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
119 | 1 | April | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
119 | 2 | April | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
119 | 3 | April | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
119 | 4 | April | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
119 | 5 | April | 9.8 | 12.0652 | 1683.85 | 3.969 | 1687.819 | 0 | 1687.819 | 0 | 0 | 99.7648 | 0.23516 | 0 | 99.7648 | 0.23516 | 0
119 | 6 | April | 10.3 | 12.6808 | 1694.9 | 48.951 | 1743.851 | 0 | 1743.851 | 0 | 0 | 97.1929 | 2.8071 | 0 | 97.1929 | 2.8071 | 0
119 | 7 | April | 9.8 | 12.0652 | 1683.85 | 157.3254 | 1841.1754 | 0 | 1841.1754 | 0 | 0 | 91.4552 | 8.5448 | 0 | 91.4552 | 8.5448 | 0
119 | 8 | April | 9.3 | 11.4496 | 1598.85 | 280.3799 | 1879.2299 | 0 | 1879.2299 | 0 | 0 | 85.0801 | 14.9199 | 0 | 85.0801 | 14.9199 | 0
119 | 9 | April | 10.8 | 13.2964 | 1698.3 | 248.076 | 1946.376 | 0 | 1946.376 | 0 | 0 | 87.2545 | 12.7455 | 0 | 87.2545 | 12.7455 | 0
119 | 10 | April | 10.8 | 13.2964 | 1698.3 | 539.0129 | 2237.3129 | 1 | 2000 | 237.3129 | 11.8656 | 75.908 | 15.085 | 44.0273 | 73.0494 | 24.092 | 13.9736
119 | 11 | April | 10.8 | 13.2964 | 1698.3 | 605.3225 | 2303.6225 | 1 | 2000 | 303.6225 | 15.1811 | 73.723 | 15.085 | 50.1588 | 69.7339 | 26.277 | 17.878
119 | 12 | April | 9.3 | 11.4496 | 1598.85 | 374.1193 | 1972.9693 | 0 | 1972.9693 | 0 | 0 | 81.0378 | 18.9622 | 0 | 81.0378 | 18.9622 | 0
119 | 13 | April | 10.8 | 13.2964 | 1698.3 | 364.7344 | 2063.0344 | 1 | 2000 | 63.0344 | 3.1517 | 82.3205 | 15.085 | 17.2823 | 81.7633 | 17.6795 | 3.7116
119 | 14 | April | 7.2 | 8.8642 | 908.65 | 340.3751 | 1249.0251 | 0 | 1249.0251 | 0 | 0 | 72.7487 | 27.2513 | 0 | 72.7487 | 27.2513 | 0
119 | 15 | April | 8.2 | 10.0954 | 1359.15 | 291.3774 | 1650.5274 | 0 | 1650.5274 | 0 | 0 | 82.3464 | 17.6536 | 0 | 82.3464 | 17.6536 | 0
119 | 16 | April | 7.5 | 9.2336 | 1059.95 | 295.6056 | 1355.5556 | 0 | 1355.5556 | 0 | 0 | 78.193 | 21.807 | 0 | 78.193 | 21.807 | 0
119 | 17 | April | 6.7 | 8.2487 | 761.6 | 235.2586 | 996.8586 | 0 | 996.8586 | 0 | 0 | 76.4 | 23.6 | 0 | 76.4 | 23.6 | 0
119 | 18 | April | 5.7 | 7.0175 | 504.9 | 115.5519 | 620.4519 | 0 | 620.4519 | 0 | 0 | 81.3762 | 18.6238 | 0 | 81.3762 | 18.6238 | 0
119 | 19 | April | 4.1 | 5.0477 | 173.4 | 23.814 | 197.214 | 0 | 197.214 | 0 | 0 | 87.9248 | 12.0752 | 0 | 87.9248 | 12.0752 | 0
119 | 20 | April | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
119 | 21 | April | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
119 | 22 | April | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
119 | 23 | April | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
119 | 24 | April | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120 | 1 | April | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120 | 2 | April | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120 | 3 | April | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120 | 4 | April | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120 | 5 | April | 2.1 | 2.5854 | 0 | 6.615 | 6.615 | 0 | 6.615 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
120 | 6 | April | 2.6 | 3.201 | 0 | 91.9097 | 91.9097 | 0 | 91.9097 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
120 | 7 | April | 2.6 | 3.201 | 0 | 291.9094 | 291.9094 | 0 | 291.9094 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
120 | 8 | April | 2.6 | 3.201 | 0 | 308.4459 | 308.4459 | 0 | 308.4459 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
120 | 9 | April | 3.1 | 3.8165 | 0 | 430.9462 | 430.9462 | 0 | 430.9462 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
120 | 10 | April | 3.1 | 3.8165 | 0 | 534.4663 | 534.4663 | 0 | 534.4663 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
120 | 11 | April | 3.3 | 4.0628 | 75.65 | 666.2885 | 741.9385 | 0 | 741.9385 | 0 | 0 | 10.1963 | 89.8037 | 0 | 10.1963 | 89.8037 | 0
120 | 12 | April | 3.4 | 4.1859 | 75.65 | 791.4726 | 867.1226 | 0 | 867.1226 | 0 | 0 | 8.7243 | 91.2757 | 0 | 8.7243 | 91.2757 | 0
120 | 13 | April | 3.6 | 4.4321 | 75.65 | 849.7132 | 925.3632 | 0 | 925.3632 | 0 | 0 | 8.1752 | 91.8248 | 0 | 8.1752 | 91.8248 | 0
120 | 14 | April | 2.6 | 3.201 | 0 | 568.5794 | 568.5794 | 0 | 568.5794 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
120 | 15 | April | 2.6 | 3.201 | 0 | 483.5952 | 483.5952 | 0 | 483.5952 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
120 | 16 | April | 2.6 | 3.201 | 0 | 480.0884 | 480.0884 | 0 | 480.0884 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
120 | 17 | April | 2.6 | 3.201 | 0 | 337.9737 | 337.9737 | 0 | 337.9737 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
120 | 18 | April | 2.6 | 3.201 | 0 | 138.3247 | 138.3247 | 0 | 138.3247 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
120 | 19 | April | 1.5 | 1.8467 | 0 | 26.46 | 26.46 | 0 | 26.46 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
120 | 20 | April | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120 | 21 | April | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120 | 22 | April | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120 | 23 | April | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
120 | 24 | April | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121 | 1 | May | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121 | 2 | May | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121 | 3 | May | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121 | 4 | May | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121 | 5 | May | 1.5 | 1.8467 | 0 | 6.615 | 6.615 | 0 | 6.615 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
121 | 6 | May | 1.5 | 1.8467 | 0 | 84.4762 | 84.4762 | 0 | 84.4762 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
121 | 7 | May | 1.2 | 1.4774 | 0 | 301.5655 | 301.5655 | 0 | 301.5655 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
121 | 8 | May | 1 | 1.2311 | 0 | 390.9791 | 390.9791 | 0 | 390.9791 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
121 | 9 | May | 2.6 | 3.201 | 0 | 242.683 | 242.683 | 0 | 242.683 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
121 | 10 | May | 2.6 | 3.201 | 0 | 1059.9149 | 1059.9149 | 0 | 1059.9149 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
121 | 11 | May | 3.1 | 3.8165 | 0 | 1014.2119 | 1014.2119 | 0 | 1014.2119 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
121 | 12 | May | 5.1 | 6.2788 | 312.8 | 1046.0583 | 1358.8583 | 0 | 1358.8583 | 0 | 0 | 23.0193 | 76.9807 | 0 | 23.0193 | 76.9807 | 0
121 | 13 | May | 5.1 | 6.2788 | 312.8 | 864.457 | 1177.257 | 0 | 1177.257 | 0 | 0 | 26.5702 | 73.4298 | 0 | 26.5702 | 73.4298 | 0
121 | 14 | May | 5.7 | 7.0175 | 504.9 | 770.1286 | 1275.0286 | 0 | 1275.0286 | 0 | 0 | 39.5991 | 60.4009 | 0 | 39.5991 | 60.4009 | 0
121 | 15 | May | 6.7 | 8.2487 | 761.6 | 760.5175 | 1522.1175 | 0 | 1522.1175 | 0 | 0 | 50.0356 | 49.9644 | 0 | 50.0356 | 49.9644 | 0
121 | 16 | May | 4.6 | 5.6633 | 237.15 | 650.5686 | 887.7186 | 0 | 887.7186 | 0 | 0 | 26.7145 | 73.2855 | 0 | 26.7145 | 73.2855 | 0
121 | 17 | May | 5.1 | 6.2788 | 312.8 | 351.5337 | 664.3337 | 0 | 664.3337 | 0 | 0 | 47.0848 | 52.9152 | 0 | 47.0848 | 52.9152 | 0
121 | 18 | May | 6.7 | 8.2487 | 761.6 | 159.4211 | 921.0211 | 0 | 921.0211 | 0 | 0 | 82.6908 | 17.3092 | 0 | 82.6908 | 17.3092 | 0
121 | 19 | May | 5.1 | 6.2788 | 312.8 | 42.336 | 355.136 | 0 | 355.136 | 0 | 0 | 88.0789 | 11.9211 | 0 | 88.0789 | 11.9211 | 0
121 | 20 | May | 3.6 | 4.4321 | 75.65 | 1.323 | 76.973 | 0 | 76.973 | 0 | 0 | 98.2812 | 1.7188 | 0 | 98.2812 | 1.7188 | 0
121 | 21 | May | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121 | 22 | May | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
121 | 23 | May | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
121 | 24 | May | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
122 | 1 | May | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
122 | 2 | May | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
122 | 3 | May | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
122 | 4 | May | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
122 | 5 | May | 4.1 | 5.0477 | 173.4 | 2.646 | 176.046 | 0 | 176.046 | 0 | 0 | 98.497 | 1.503 | 0 | 98.497 | 1.503 | 0
122 | 6 | May | 6.2 | 7.6331 | 625.6 | 30.429 | 656.029 | 0 | 656.029 | 0 | 0 | 95.3616 | 4.6384 | 0 | 95.3616 | 4.6384 | 0
122 | 7 | May | 6.2 | 7.6331 | 625.6 | 95.256 | 720.856 | 0 | 720.856 | 0 | 0 | 86.7857 | 13.2143 | 0 | 86.7857 | 13.2143 | 0
122 | 8 | May | 6.7 | 8.2487 | 761.6 | 170.667 | 932.267 | 0 | 932.267 | 0 | 0 | 81.6933 | 18.3067 | 0 | 81.6933 | 18.3067 | 0
122 | 9 | May | 7.2 | 8.8642 | 908.65 | 246.6654 | 1155.3154 | 0 | 1155.3154 | 0 | 0 | 78.6495 | 21.3505 | 0 | 78.6495 | 21.3505 | 0
122 | 10 | May | 7.7 | 9.4798 | 1059.95 | 309.2448 | 1369.1948 | 0 | 1369.1948 | 0 | 0 | 77.4141 | 22.5859 | 0 | 77.4141 | 22.5859 | 0
122 | 11 | May | 7.7 | 9.4798 | 1059.95 | 353.6238 | 1413.5738 | 0 | 1413.5738 | 0 | 0 | 74.9837 | 25.0163 | 0 | 74.9837 | 25.0163 | 0
122 | 12 | May | 7.7 | 9.4798 | 1059.95 | 369.0386 | 1428.9886 | 0 | 1428.9886 | 0 | 0 | 74.1748 | 25.8252 | 0 | 74.1748 | 25.8252 | 0
122 | 13 | May | 7.2 | 8.8642 | 908.65 | 364.7507 | 1273.4007 | 0 | 1273.4007 | 0 | 0 | 71.3562 | 28.6438 | 0 | 71.3562 | 28.6438 | 0
122 | 14 | May | 7.2 | 8.8642 | 908.65 | 570.3861 | 1479.0361 | 0 | 1479.0361 | 0 | 0 | 61.4353 | 38.5647 | 0 | 61.4353 | 38.5647 | 0
122 | 15 | May | 8.2 | 10.0954 | 1359.15 | 288.0745 | 1647.2245 | 0 | 1647.2245 | 0 | 0 | 82.5115 | 17.4885 | 0 | 82.5115 | 17.4885 | 0
122 | 16 | May | 7.7 | 9.4798 | 1059.95 | 357.3463 | 1417.2963 | 0 | 1417.2963 | 0 | 0 | 74.7868 | 25.2132 | 0 | 74.7868 | 25.2132 | 0
122 | 17 | May | 6.7 | 8.2487 | 761.6 | 145.53 | 907.13 | 0 | 907.13 | 0 | 0 | 83.9571 | 16.0429 | 0 | 83.9571 | 16.0429 | 0
122 | 18 | May | 6.2 | 7.6331 | 625.6 | 113.778 | 739.378 | 0 | 739.378 | 0 | 0 | 84.6117 | 15.3883 | 0 | 84.6117 | 15.3883 | 0
122 | 19 | May | 5.1 | 6.2788 | 312.8 | 15.876 | 328.676 | 0 | 328.676 | 0 | 0 | 95.1697 | 4.8303 | 0 | 95.1697 | 4.8303 | 0
122 | 20 | May | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
122 | 21 | May | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
122 | 22 | May | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
122 | 23 | May | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
122 | 24 | May | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
123 | 1 | May | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
123 | 2 | May | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
123 | 3 | May | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
123 | 4 | May | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
123 | 5 | May | 3.1 | 3.8165 | 0 | 6.615 | 6.615 | 0 | 6.615 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
123 | 6 | May | 3.6 | 4.4321 | 75.65 | 77.0024 | 152.6524 | 0 | 152.6524 | 0 | 0 | 49.557 | 50.443 | 0 | 49.557 | 50.443 | 0
123 | 7 | May | 4.6 | 5.6633 | 237.15 | 305.6094 | 542.7594 | 0 | 542.7594 | 0 | 0 | 43.6934 | 56.3066 | 0 | 43.6934 | 56.3066 | 0
123 | 8 | May | 4.1 | 5.0477 | 173.4 | 575.4709 | 748.8709 | 0 | 748.8709 | 0 | 0 | 23.1549 | 76.8451 | 0 | 23.1549 | 76.8451 | 0
123 | 9 | May | 4.1 | 5.0477 | 173.4 | 849.2742 | 1022.6742 | 0 | 1022.6742 | 0 | 0 | 16.9555 | 83.0445 | 0 | 16.9555 | 83.0445 | 0
123 | 10 | May | 3.6 | 4.4321 | 75.65 | 1075.3566 | 1151.0066 | 0 | 1151.0066 | 0 | 0 | 6.5725 | 93.4275 | 0 | 6.5725 | 93.4275 | 0
123 | 11 | May | 3.1 | 3.8165 | 0 | 1229.1222 | 1229.1222 | 0 | 1229.1222 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
123 | 12 | May | 4.1 | 5.0477 | 173.4 | 1260.1205 | 1433.5205 | 0 | 1433.5205 | 0 | 0 | 12.0961 | 87.9039 | 0 | 12.0961 | 87.9039 | 0
123 | 13 | May | 3.6 | 4.4321 | 75.65 | 1317.863 | 1393.513 | 0 | 1393.513 | 0 | 0 | 5.4287 | 94.5713 | 0 | 5.4287 | 94.5713 | 0
123 | 14 | May | 4.1 | 5.0477 | 173.4 | 1243.4505 | 1416.8505 | 0 | 1416.8505 | 0 | 0 | 12.2384 | 87.7616 | 0 | 12.2384 | 87.7616 | 0
123 | 15 | May | 3.1 | 3.8165 | 0 | 989.8115 | 989.8115 | 0 | 989.8115 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
123 | 16 | May | 3.1 | 3.8165 | 0 | 697.5728 | 697.5728 | 0 | 697.5728 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
123 | 17 | May | 1.5 | 1.8467 | 0 | 388.3375 | 388.3375 | 0 | 388.3375 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
123 | 18 | May | 2.1 | 2.5854 | 0 | 149.7593 | 149.7593 | 0 | 149.7593 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
123 | 19 | May | 2.6 | 3.201 | 0 | 47.628 | 47.628 | 0 | 47.628 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
123 | 20 | May | 1 | 1.2311 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
123 | 21 | May | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
123 | 22 | May | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
123 | 23 | May | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
123 | 24 | May | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
124 | 1 | May | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
124 | 2 | May | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
124 | 3 | May | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
124 | 4 | May | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
124 | 5 | May | 0 | 0 | 0 | 9.261 | 9.261 | 0 | 9.261 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
124 | 6 | May | 1 | 1.2311 | 0 | 97.0732 | 97.0732 | 0 | 97.0732 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
124 | 7 | May | 1 | 1.2311 | 0 | 337.5252 | 337.5252 | 0 | 337.5252 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
124 | 8 | May | 1 | 1.2311 | 0 | 658.4301 | 658.4301 | 0 | 658.4301 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
124 | 9 | May | 1 | 1.2311 | 0 | 959.1648 | 959.1648 | 0 | 959.1648 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
124 | 10 | May | 3.1 | 3.8165 | 0 | 1250.1539 | 1250.1539 | 0 | 1250.1539 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
124 | 11 | May | 4.6 | 5.6633 | 237.15 | 1209.8769 | 1447.0269 | 0 | 1447.0269 | 0 | 0 | 16.3888 | 83.6112 | 0 | 16.3888 | 83.6112 | 0
124 | 12 | May | 3.1 | 3.8165 | 0 | 1375.8994 | 1375.8994 | 0 | 1375.8994 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
124 | 13 | May | 3.1 | 3.8165 | 0 | 1394.4897 | 1394.4897 | 0 | 1394.4897 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
124 | 14 | May | 2.6 | 3.201 | 0 | 1249.7706 | 1249.7706 | 0 | 1249.7706 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
124 | 15 | May | 3.1 | 3.8165 | 0 | 960.3659 | 960.3659 | 0 | 960.3659 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
124 | 16 | May | 2.6 | 3.201 | 0 | 672.228 | 672.228 | 0 | 672.228 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
124 | 17 | May | 2.6 | 3.201 | 0 | 390.3434 | 390.3434 | 0 | 390.3434 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
124 | 18 | May | 3.1 | 3.8165 | 0 | 152.0078 | 152.0078 | 0 | 152.0078 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
124 | 19 | May | 2.6 | 3.201 | 0 | 48.951 | 48.951 | 0 | 48.951 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
124 | 20 | May | 1 | 1.2311 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
124 | 21 | May | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
124 | 22 | May | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
124 | 23 | May | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
124 | 24 | May | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
125 | 1 | May | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
125 | 2 | May | 3.9 | 4.8015 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
125 | 3 | May | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
125 | 4 | May | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
125 | 5 | May | 3.6 | 4.4321 | 75.65 | 9.261 | 84.911 | 0 | 84.911 | 0 | 0 | 89.0933 | 10.9067 | 0 | 89.0933 | 10.9067 | 0
125 | 6 | May | 4.1 | 5.0477 | 173.4 | 83.7176 | 257.1176 | 0 | 257.1176 | 0 | 0 | 67.44 | 32.56 | 0 | 67.44 | 32.56 | 0
125 | 7 | May | 4.1 | 5.0477 | 173.4 | 295.2698 | 468.6698 | 0 | 468.6698 | 0 | 0 | 36.9983 | 63.0017 | 0 | 36.9983 | 63.0017 | 0
125 | 8 | May | 5.1 | 6.2788 | 312.8 | 624.8144 | 937.6144 | 0 | 937.6144 | 0 | 0 | 33.3613 | 66.6387 | 0 | 33.3613 | 66.6387 | 0
125 | 9 | May | 5.1 | 6.2788 | 312.8 | 971.8981 | 1284.6981 | 0 | 1284.6981 | 0 | 0 | 24.3481 | 75.6519 | 0 | 24.3481 | 75.6519 | 0
125 | 10 | May | 5.7 | 7.0175 | 504.9 | 1196.2015 | 1701.1015 | 0 | 1701.1015 | 0 | 0 | 29.6808 | 70.3192 | 0 | 29.6808 | 70.3192 | 0
125 | 11 | May | 5.7 | 7.0175 | 504.9 | 1397.6666 | 1902.5666 | 0 | 1902.5666 | 0 | 0 | 26.5378 | 73.4622 | 0 | 26.5378 | 73.4622 | 0
125 | 12 | May | 6.2 | 7.6331 | 625.6 | 1497.9761 | 2123.5761 | 1 | 2000 | 123.5761 | 6.1788 | 29.4597 | 68.72 | 8.2495 | 25.1012 | 70.5403 | 19.7532
125 | 13 | May | 6.2 | 7.6331 | 625.6 | 1440.1374 | 2065.7374 | 1 | 2000 | 65.7374 | 3.2869 | 30.2846 | 68.72 | 4.5647 | 27.9931 | 69.7154 | 10.5079
125 | 14 | May | 6.2 | 7.6331 | 625.6 | 1271.2241 | 1896.8241 | 0 | 1896.8241 | 0 | 0 | 32.9814 | 67.0186 | 0 | 32.9814 | 67.0186 | 0
125 | 15 | May | 6.2 | 7.6331 | 625.6 | 1018.7343 | 1644.3343 | 0 | 1644.3343 | 0 | 0 | 38.0458 | 61.9542 | 0 | 38.0458 | 61.9542 | 0
125 | 16 | May | 6.2 | 7.6331 | 625.6 | 706.4988 | 1332.0988 | 0 | 1332.0988 | 0 | 0 | 46.9635 | 53.0365 | 0 | 46.9635 | 53.0365 | 0
125 | 17 | May | 6.2 | 7.6331 | 625.6 | 395.7725 | 1021.3725 | 0 | 1021.3725 | 0 | 0 | 61.2509 | 38.7491 | 0 | 61.2509 | 38.7491 | 0
125 | 18 | May | 5.7 | 7.0175 | 504.9 | 154.9077 | 659.8077 | 0 | 659.8077 | 0 | 0 | 76.5223 | 23.4777 | 0 | 76.5223 | 23.4777 | 0
125 | 19 | May | 4.6 | 5.6633 | 237.15 | 50.274 | 287.424 | 0 | 287.424 | 0 | 0 | 82.5088 | 17.4912 | 0 | 82.5088 | 17.4912 | 0
125 | 20 | May | 4.6 | 5.6633 | 237.15 | 2.646 | 239.796 | 0 | 239.796 | 0 | 0 | 98.8966 | 1.1034 | 0 | 98.8966 | 1.1034 | 0
125 | 21 | May | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
125 | 22 | May | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
125 | 23 | May | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
125 | 24 | May | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
126 | 1 | May | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
126 | 2 | May | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
126 | 3 | May | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
126 | 4 | May | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
126 | 5 | May | 4.6 | 5.6633 | 237.15 | 11.907 | 249.057 | 0 | 249.057 | 0 | 0 | 95.2192 | 4.7808 | 0 | 95.2192 | 4.7808 | 0
126 | 6 | May | 5.1 | 6.2788 | 312.8 | 104.6357 | 417.4357 | 0 | 417.4357 | 0 | 0 | 74.9337 | 25.0663 | 0 | 74.9337 | 25.0663 | 0
126 | 7 | May | 5.1 | 6.2788 | 312.8 | 330.7298 | 643.5298 | 0 | 643.5298 | 0 | 0 | 48.6069 | 51.3931 | 0 | 48.6069 | 51.3931 | 0
126 | 8 | May | 5.7 | 7.0175 | 504.9 | 655.6628 | 1160.5628 | 0 | 1160.5628 | 0 | 0 | 43.5048 | 56.4952 | 0 | 43.5048 | 56.4952 | 0
126 | 9 | May | 5.1 | 6.2788 | 312.8 | 948.6599 | 1261.4599 | 0 | 1261.4599 | 0 | 0 | 24.7967 | 75.2033 | 0 | 24.7967 | 75.2033 | 0
126 | 10 | May | 5.1 | 6.2788 | 312.8 | 1221.0895 | 1533.8895 | 0 | 1533.8895 | 0 | 0 | 20.3926 | 79.6074 | 0 | 20.3926 | 79.6074 | 0
126 | 11 | May | 5.1 | 6.2788 | 312.8 | 1413.2934 | 1726.0934 | 0 | 1726.0934 | 0 | 0 | 18.1218 | 81.8782 | 0 | 18.1218 | 81.8782 | 0
126 | 12 | May | 4.6 | 5.6633 | 237.15 | 1465.2653 | 1702.4153 | 0 | 1702.4153 | 0 | 0 | 13.9302 | 86.0698 | 0 | 13.9302 | 86.0698 | 0
126 | 13 | May | 5.7 | 7.0175 | 504.9 | 1335.8021 | 1840.7021 | 0 | 1840.7021 | 0 | 0 | 27.4298 | 72.5702 | 0 | 27.4298 | 72.5702 | 0
126 | 14 | May | 6.7 | 8.2487 | 761.6 | 1091.5005 | 1853.1005 | 0 | 1853.1005 | 0 | 0 | 41.0987 | 58.9013 | 0 | 41.0987 | 58.9013 | 0
126 | 15 | May | 6.2 | 7.6331 | 625.6 | 959.6545 | 1585.2545 | 0 | 1585.2545 | 0 | 0 | 39.4637 | 60.5363 | 0 | 39.4637 | 60.5363 | 0
126 | 16 | May | 7.2 | 8.8642 | 908.65 | 676.2271 | 1584.8771 | 0 | 1584.8771 | 0 | 0 | 57.3325 | 42.6675 | 0 | 57.3325 | 42.6675 | 0
126 | 17 | May | 7.2 | 8.8642 | 908.65 | 393.8076 | 1302.4576 | 0 | 1302.4576 | 0 | 0 | 69.7643 | 30.2357 | 0 | 69.7643 | 30.2357 | 0
126 | 18 | May | 6.2 | 7.6331 | 625.6 | 165.4917 | 791.0917 | 0 | 791.0917 | 0 | 0 | 79.0806 | 20.9194 | 0 | 79.0806 | 20.9194 | 0
126 | 19 | May | 6.2 | 7.6331 | 625.6 | 47.628 | 673.228 | 0 | 673.228 | 0 | 0 | 92.9254 | 7.0746 | 0 | 92.9254 | 7.0746 | 0
126 | 20 | May | 6.2 | 7.6331 | 625.6 | 2.646 | 628.246 | 0 | 628.246 | 0 | 0 | 99.5788 | 0.42117 | 0 | 99.5788 | 0.42117 | 0
126 | 21 | May | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
126 | 22 | May | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
126 | 23 | May | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
126 | 24 | May | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
127 | 1 | May | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
127 | 2 | May | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
127 | 3 | May | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
127 | 4 | May | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
127 | 5 | May | 7.2 | 8.8642 | 908.65 | 11.907 | 920.557 | 0 | 920.557 | 0 | 0 | 98.7065 | 1.2935 | 0 | 98.7065 | 1.2935 | 0
127 | 6 | May | 8.2 | 10.0954 | 1359.15 | 107.1472 | 1466.2972 | 0 | 1466.2972 | 0 | 0 | 92.6927 | 7.3073 | 0 | 92.6927 | 7.3073 | 0
127 | 7 | May | 8.7 | 10.711 | 1490.05 | 352.665 | 1842.715 | 0 | 1842.715 | 0 | 0 | 80.8617 | 19.1383 | 0 | 80.8617 | 19.1383 | 0
127 | 8 | May | 7.7 | 9.4798 | 1059.95 | 670.9758 | 1730.9258 | 0 | 1730.9258 | 0 | 0 | 61.236 | 38.764 | 0 | 61.236 | 38.764 | 0
127 | 9 | May | 8.7 | 10.711 | 1490.05 | 991.967 | 2482.017 | 1 | 2000 | 482.017 | 24.1009 | 60.0338 | 25.4975 | 48.592 | 50.4016 | 39.9662 | 32.3491
127 | 10 | May | 7.7 | 9.4798 | 1059.95 | 1257.784 | 2317.734 | 1 | 2000 | 317.734 | 15.8867 | 45.7322 | 47.0025 | 25.2614 | 37.1108 | 54.2678 | 29.9763
127 | 11 | May | 8.2 | 10.0954 | 1359.15 | 1434.4359 | 2793.5859 | 1 | 2000 | 793.5859 | 39.6793 | 48.6525 | 32.0425 | 55.3239 | 28.2782 | 51.3475 | 58.3884
127 | 12 | May | 8.2 | 10.0954 | 1359.15 | 1485.8498 | 2844.9998 | 1 | 2000 | 844.9998 | 42.25 | 47.7733 | 32.0425 | 56.8698 | 25.7075 | 52.2267 | 62.1712
127 | 13 | May | 9.3 | 11.4496 | 1598.85 | 1428.5348 | 3027.3848 | 1 | 2000 | 1027.3848 | 51.3692 | 52.8129 | 20.0575 | 71.9188 | 28.5733 | 47.1871 | 64.2577
127 | 14 | May | 8.7 | 10.711 | 1490.05 | 1264.3935 | 2754.4435 | 1 | 2000 | 754.4435 | 37.7222 | 54.0962 | 25.4975 | 59.6684 | 36.7803 | 45.9038 | 50.6321
127 | 15 | May | 8.7 | 10.711 | 1490.05 | 1009.7599 | 2499.8099 | 1 | 2000 | 499.8099 | 24.9905 | 59.6065 | 25.4975 | 49.4979 | 49.512 | 40.3935 | 33.5432
127 | 16 | May | 8.7 | 10.711 | 1490.05 | 708.9755 | 2199.0255 | 1 | 2000 | 199.0255 | 9.9513 | 67.7596 | 25.4975 | 28.0723 | 64.5512 | 32.2404 | 13.357
127 | 17 | May | 8.2 | 10.0954 | 1359.15 | 390.4569 | 1749.6069 | 0 | 1749.6069 | 0 | 0 | 77.6832 | 22.3168 | 0 | 77.6832 | 22.3168 | 0
127 | 18 | May | 8 | 9.8492 | 1213.8 | 166.3102 | 1380.1102 | 0 | 1380.1102 | 0 | 0 | 87.9495 | 12.0505 | 0 | 87.9495 | 12.0505 | 0
127 | 19 | May | 7.7 | 9.4798 | 1059.95 | 42.336 | 1102.286 | 0 | 1102.286 | 0 | 0 | 96.1593 | 3.8407 | 0 | 96.1593 | 3.8407 | 0
127 | 20 | May | 8.7 | 10.711 | 1490.05 | 1.323 | 1491.373 | 0 | 1491.373 | 0 | 0 | 99.9113 | 0.08871 | 0 | 99.9113 | 0.08871 | 0
127 | 21 | May | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
127 | 22 | May | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
127 | 23 | May | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
127 | 24 | May | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
128 | 1 | May | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
128 | 2 | May | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
128 | 3 | May | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
128 | 4 | May | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
128 | 5 | May | 8.2 | 10.0954 | 1359.15 | 11.907 | 1371.057 | 0 | 1371.057 | 0 | 0 | 99.1315 | 0.86845 | 0 | 99.1315 | 0.86845 | 0
128 | 6 | May | 8.2 | 10.0954 | 1359.15 | 80.0979 | 1439.2479 | 0 | 1439.2479 | 0 | 0 | 94.4347 | 5.5653 | 0 | 94.4347 | 5.5653 | 0
128 | 7 | May | 9.3 | 11.4496 | 1598.85 | 280.8075 | 1879.6575 | 0 | 1879.6575 | 0 | 0 | 85.0607 | 14.9393 | 0 | 85.0607 | 14.9393 | 0
128 | 8 | May | 8.7 | 10.711 | 1490.05 | 635.8624 | 2125.9124 | 1 | 2000 | 125.9124 | 6.2956 | 70.0899 | 25.4975 | 19.8018 | 68.2069 | 29.9101 | 8.4502
128 | 9 | May | 8.7 | 10.711 | 1490.05 | 942.8214 | 2432.8714 | 1 | 2000 | 432.8714 | 21.6436 | 61.2466 | 25.4975 | 45.9123 | 52.8589 | 38.7534 | 29.0508
128 | 10 | May | 8.7 | 10.711 | 1490.05 | 547.6126 | 2037.6626 | 1 | 2000 | 37.6626 | 1.8831 | 73.1255 | 25.4975 | 6.8776 | 72.6194 | 26.8745 | 2.5276
128 | 11 | May | 9.3 | 11.4496 | 1598.85 | 599.9278 | 2198.7778 | 1 | 2000 | 198.7778 | 9.9389 | 72.7154 | 20.0575 | 33.1336 | 70.0036 | 27.2846 | 12.4325
128 | 12 | May | 9.8 | 12.0652 | 1683.85 | 631.238 | 2315.088 | 1 | 2000 | 315.088 | 15.7544 | 72.7337 | 15.8075 | 49.9159 | 68.4381 | 27.2663 | 18.7124
128 | 13 | May | 9.3 | 11.4496 | 1598.85 | 619.0739 | 2217.9239 | 1 | 2000 | 217.9239 | 10.8962 | 72.0877 | 20.0575 | 35.2016 | 69.0463 | 27.9123 | 13.63
128 | 14 | May | 9.8 | 12.0652 | 1683.85 | 348.3738 | 2032.2238 | 1 | 2000 | 32.2238 | 1.6112 | 82.8575 | 15.8075 | 9.2498 | 82.5813 | 17.1425 | 1.9137
128 | 15 | May | 9.3 | 11.4496 | 1598.85 | 493.7693 | 2092.6193 | 1 | 2000 | 92.6193 | 4.631 | 76.4042 | 20.0575 | 18.7576 | 75.3115 | 23.5958 | 5.7929
128 | 16 | May | 8.7 | 10.711 | 1490.05 | 371.5485 | 1861.5985 | 0 | 1861.5985 | 0 | 0 | 80.0414 | 19.9586 | 0 | 80.0414 | 19.9586 | 0
128 | 17 | May | 8.7 | 10.711 | 1490.05 | 246.2682 | 1736.3182 | 0 | 1736.3182 | 0 | 0 | 85.8166 | 14.1834 | 0 | 85.8166 | 14.1834 | 0
128 | 18 | May | 8.7 | 10.711 | 1490.05 | 127.2346 | 1617.2846 | 0 | 1617.2846 | 0 | 0 | 92.1328 | 7.8672 | 0 | 92.1328 | 7.8672 | 0
128 | 19 | May | 8.7 | 10.711 | 1490.05 | 34.398 | 1524.448 | 0 | 1524.448 | 0 | 0 | 97.7436 | 2.2564 | 0 | 97.7436 | 2.2564 | 0
128 | 20 | May | 8.7 | 10.711 | 1490.05 | 2.646 | 1492.696 | 0 | 1492.696 | 0 | 0 | 99.8227 | 0.17726 | 0 | 99.8227 | 0.17726 | 0
128 | 21 | May | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
128 | 22 | May | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
128 | 23 | May | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
128 | 24 | May | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
129 | 1 | May | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
129 | 2 | May | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
129 | 3 | May | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
129 | 4 | May | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
129 | 5 | May | 8.2 | 10.0954 | 1359.15 | 14.553 | 1373.703 | 0 | 1373.703 | 0 | 0 | 98.9406 | 1.0594 | 0 | 98.9406 | 1.0594 | 0
129 | 6 | May | 7.7 | 9.4798 | 1059.95 | 110.6786 | 1170.6286 | 0 | 1170.6286 | 0 | 0 | 90.5454 | 9.4546 | 0 | 90.5454 | 9.4546 | 0
129 | 7 | May | 7.7 | 9.4798 | 1059.95 | 274.7068 | 1334.6568 | 0 | 1334.6568 | 0 | 0 | 79.4174 | 20.5826 | 0 | 79.4174 | 20.5826 | 0
129 | 8 | May | 7.7 | 9.4798 | 1059.95 | 411.2598 | 1471.2098 | 0 | 1471.2098 | 0 | 0 | 72.0462 | 27.9538 | 0 | 72.0462 | 27.9538 | 0
129 | 9 | May | 6.2 | 7.6331 | 625.6 | 851.7106 | 1477.3106 | 0 | 1477.3106 | 0 | 0 | 42.3472 | 57.6528 | 0 | 42.3472 | 57.6528 | 0
129 | 10 | May | 8.2 | 10.0954 | 1359.15 | 1167.8663 | 2527.0163 | 1 | 2000 | 527.0163 | 26.3508 | 53.7848 | 32.0425 | 45.1264 | 41.6067 | 46.2152 | 38.7754
129 | 11 | May | 8.7 | 10.711 | 1490.05 | 1393.8553 | 2883.9053 | 1 | 2000 | 883.9053 | 44.1953 | 51.6678 | 25.4975 | 63.4144 | 30.3072 | 48.3322 | 59.3205
129 | 12 | May | 8.2 | 10.0954 | 1359.15 | 1381.4495 | 2740.5995 | 1 | 2000 | 740.5995 | 37.03 | 49.5932 | 32.0425 | 53.6103 | 30.9275 | 50.4068 | 54.4899
129 | 13 | May | 7.7 | 9.4798 | 1059.95 | 1411.4319 | 2471.3819 | 1 | 2000 | 471.3819 | 23.5691 | 42.889 | 47.0025 | 33.3974 | 29.4284 | 57.111 | 44.4721
129 | 14 | May | 8.2 | 10.0954 | 1359.15 | 1258.8766 | 2618.0266 | 1 | 2000 | 618.0266 | 30.9013 | 51.9151 | 32.0425 | 49.0935 | 37.0562 | 48.0849 | 45.4716
129 | 15 | May | 6.7 | 8.2487 | 761.6 | 1013.8369 | 1775.4369 | 0 | 1775.4369 | 0 | 0 | 42.8965 | 57.1035 | 0 | 42.8965 | 57.1035 | 0
129 | 16 | May | 6.7 | 8.2487 | 761.6 | 708.123 | 1469.723 | 0 | 1469.723 | 0 | 0 | 51.8193 | 48.1807 | 0 | 51.8193 | 48.1807 | 0
129 | 17 | May | 6.2 | 7.6331 | 625.6 | 405.279 | 1030.879 | 0 | 1030.879 | 0 | 0 | 60.6861 | 39.3139 | 0 | 60.6861 | 39.3139 | 0
129 | 18 | May | 6.7 | 8.2487 | 761.6 | 176.1181 | 937.7181 | 0 | 937.7181 | 0 | 0 | 81.2184 | 18.7816 | 0 | 81.2184 | 18.7816 | 0
129 | 19 | May | 5.1 | 6.2788 | 312.8 | 46.305 | 359.105 | 0 | 359.105 | 0 | 0 | 87.1054 | 12.8946 | 0 | 87.1054 | 12.8946 | 0
129 | 20 | May | 4.1 | 5.0477 | 173.4 | 2.646 | 176.046 | 0 | 176.046 | 0 | 0 | 98.497 | 1.503 | 0 | 98.497 | 1.503 | 0
129 | 21 | May | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
129 | 22 | May | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
129 | 23 | May | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
129 | 24 | May | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
130 | 1 | May | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
130 | 2 | May | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
130 | 3 | May | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
130 | 4 | May | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
130 | 5 | May | 3.1 | 3.8165 | 0 | 15.876 | 15.876 | 0 | 15.876 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
130 | 6 | May | 3.1 | 3.8165 | 0 | 116.9998 | 116.9998 | 0 | 116.9998 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
130 | 7 | May | 5.7 | 7.0175 | 504.9 | 344.1834 | 849.0834 | 0 | 849.0834 | 0 | 0 | 59.4641 | 40.5359 | 0 | 59.4641 | 40.5359 | 0
130 | 8 | May | 6.2 | 7.6331 | 625.6 | 675.0662 | 1300.6662 | 0 | 1300.6662 | 0 | 0 | 48.0984 | 51.9016 | 0 | 48.0984 | 51.9016 | 0
130 | 9 | May | 7.2 | 8.8642 | 908.65 | 864.6731 | 1773.3231 | 0 | 1773.3231 | 0 | 0 | 51.24 | 48.76 | 0 | 51.24 | 48.76 | 0
130 | 10 | May | 6.7 | 8.2487 | 761.6 | 1222.3302 | 1983.9302 | 0 | 1983.9302 | 0 | 0 | 38.3884 | 61.6116 | 0 | 38.3884 | 61.6116 | 0
130 | 11 | May | 5.1 | 6.2788 | 312.8 | 1070.9093 | 1383.7093 | 0 | 1383.7093 | 0 | 0 | 22.6059 | 77.3941 | 0 | 22.6059 | 77.3941 | 0
130 | 12 | May | 5.7 | 7.0175 | 504.9 | 1354.0808 | 1858.9808 | 0 | 1858.9808 | 0 | 0 | 27.16 | 72.84 | 0 | 27.16 | 72.84 | 0
130 | 13 | May | 6.2 | 7.6331 | 625.6 | 1386.0287 | 2011.6287 | 1 | 2000 | 11.6287 | 0.58144 | 31.0992 | 68.72 | 0.839 | 30.6986 | 68.9008 | 1.8588
130 | 14 | May | 4.6 | 5.6633 | 237.15 | 1237.2336 | 1474.3836 | 0 | 1474.3836 | 0 | 0 | 16.0847 | 83.9153 | 0 | 16.0847 | 83.9153 | 0
130 | 15 | May | 5.4 | 6.6482 | 399.5 | 1007.848 | 1407.348 | 0 | 1407.348 | 0 | 0 | 28.3867 | 71.6133 | 0 | 28.3867 | 71.6133 | 0
130 | 16 | May | 6.2 | 7.6331 | 625.6 | 710.9772 | 1336.5772 | 0 | 1336.5772 | 0 | 0 | 46.8061 | 53.1939 | 0 | 46.8061 | 53.1939 | 0
130 | 17 | May | 5.9 | 7.2638 | 504.9 | 408.8925 | 913.7925 | 0 | 913.7925 | 0 | 0 | 55.2532 | 44.7468 | 0 | 55.2532 | 44.7468 | 0
130 | 18 | May | 5.7 | 7.0175 | 504.9 | 167.6825 | 672.5825 | 0 | 672.5825 | 0 | 0 | 75.0689 | 24.9311 | 0 | 75.0689 | 24.9311 | 0
130 | 19 | May | 5.1 | 6.2788 | 312.8 | 59.535 | 372.335 | 0 | 372.335 | 0 | 0 | 84.0104 | 15.9896 | 0 | 84.0104 | 15.9896 | 0
130 | 20 | May | 2.6 | 3.201 | 0 | 5.292 | 5.292 | 0 | 5.292 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
130 | 21 | May | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
130 | 22 | May | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
130 | 23 | May | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
130 | 24 | May | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
131 | 1 | May | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
131 | 2 | May | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
131 | 3 | May | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
131 | 4 | May | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
131 | 5 | May | 6.2 | 7.6331 | 625.6 | 9.261 | 634.861 | 0 | 634.861 | 0 | 0 | 98.5413 | 1.4587 | 0 | 98.5413 | 1.4587 | 0
131 | 6 | May | 6.2 | 7.6331 | 625.6 | 117.1041 | 742.7041 | 0 | 742.7041 | 0 | 0 | 84.2327 | 15.7673 | 0 | 84.2327 | 15.7673 | 0
131 | 7 | May | 6.7 | 8.2487 | 761.6 | 178.3432 | 939.9432 | 0 | 939.9432 | 0 | 0 | 81.0262 | 18.9738 | 0 | 81.0262 | 18.9738 | 0
131 | 8 | May | 6.2 | 7.6331 | 625.6 | 583.0075 | 1208.6075 | 0 | 1208.6075 | 0 | 0 | 51.762 | 48.238 | 0 | 51.762 | 48.238 | 0
131 | 9 | May | 6.7 | 8.2487 | 761.6 | 872.5257 | 1634.1257 | 0 | 1634.1257 | 0 | 0 | 46.606 | 53.394 | 0 | 46.606 | 53.394 | 0
131 | 10 | May | 7.2 | 8.8642 | 908.65 | 1170.2991 | 2078.9491 | 1 | 2000 | 78.9491 | 3.9475 | 43.7072 | 54.5675 | 6.7461 | 41.485 | 56.2928 | 8.6886
131 | 11 | May | 7.7 | 9.4798 | 1059.95 | 1397.9507 | 2457.9007 | 1 | 2000 | 457.9007 | 22.895 | 43.1242 | 47.0025 | 32.7551 | 30.1025 | 56.8758 | 43.2002
131 | 12 | May | 7.2 | 8.8642 | 908.65 | 1458.9738 | 2367.6238 | 1 | 2000 | 367.6238 | 18.3812 | 38.3781 | 54.5675 | 25.1974 | 27.0513 | 61.6219 | 40.4582
131 | 13 | May | 7.2 | 8.8642 | 908.65 | 1418.1261 | 2326.7761 | 1 | 2000 | 326.7761 | 16.3388 | 39.0519 | 54.5675 | 23.0428 | 29.0937 | 60.9481 | 35.9628
131 | 14 | May | 7.2 | 8.8642 | 908.65 | 1262.9432 | 2171.5932 | 1 | 2000 | 171.5932 | 8.5797 | 41.8426 | 54.5675 | 13.5868 | 36.8528 | 58.1574 | 18.8844
131 | 15 | May | 7.2 | 8.8642 | 908.65 | 1019.0056 | 1927.6556 | 0 | 1927.6556 | 0 | 0 | 47.1376 | 52.8624 | 0 | 47.1376 | 52.8624 | 0
131 | 16 | May | 6.2 | 7.6331 | 625.6 | 714.8241 | 1340.4241 | 0 | 1340.4241 | 0 | 0 | 46.6718 | 53.3282 | 0 | 46.6718 | 53.3282 | 0
131 | 17 | May | 6.7 | 8.2487 | 761.6 | 412.7695 | 1174.3695 | 0 | 1174.3695 | 0 | 0 | 64.8518 | 35.1482 | 0 | 64.8518 | 35.1482 | 0
131 | 18 | May | 3.6 | 4.4321 | 75.65 | 170.3109 | 245.9609 | 0 | 245.9609 | 0 | 0 | 30.7569 | 69.2431 | 0 | 30.7569 | 69.2431 | 0
131 | 19 | May | 6.2 | 7.6331 | 625.6 | 64.827 | 690.427 | 0 | 690.427 | 0 | 0 | 90.6106 | 9.3894 | 0 | 90.6106 | 9.3894 | 0
131 | 20 | May | 5.7 | 7.0175 | 504.9 | 5.292 | 510.192 | 0 | 510.192 | 0 | 0 | 98.9627 | 1.0373 | 0 | 98.9627 | 1.0373 | 0
131 | 21 | May | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
131 | 22 | May | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
131 | 23 | May | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
131 | 24 | May | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
132 | 1 | May | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
132 | 2 | May | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
132 | 3 | May | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
132 | 4 | May | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
132 | 5 | May | 5.1 | 6.2788 | 312.8 | 18.522 | 331.322 | 0 | 331.322 | 0 | 0 | 94.4097 | 5.5903 | 0 | 94.4097 | 5.5903 | 0
132 | 6 | May | 6.7 | 8.2487 | 761.6 | 125.0145 | 886.6145 | 0 | 886.6145 | 0 | 0 | 85.8998 | 14.1002 | 0 | 85.8998 | 14.1002 | 0
132 | 7 | May | 4.6 | 5.6633 | 237.15 | 369.5296 | 606.6796 | 0 | 606.6796 | 0 | 0 | 39.0898 | 60.9102 | 0 | 39.0898 | 60.9102 | 0
132 | 8 | May | 6.2 | 7.6331 | 625.6 | 690.8462 | 1316.4462 | 0 | 1316.4462 | 0 | 0 | 47.5219 | 52.4781 | 0 | 47.5219 | 52.4781 | 0
132 | 9 | May | 5.7 | 7.0175 | 504.9 | 998.7744 | 1503.6744 | 0 | 1503.6744 | 0 | 0 | 33.5777 | 66.4223 | 0 | 33.5777 | 66.4223 | 0
132 | 10 | May | 5.1 | 6.2788 | 312.8 | 1261.0511 | 1573.8511 | 0 | 1573.8511 | 0 | 0 | 19.8748 | 80.1252 | 0 | 19.8748 | 80.1252 | 0
132 | 11 | May | 6.2 | 7.6331 | 625.6 | 1409.8653 | 2035.4653 | 1 | 2000 | 35.4653 | 1.7733 | 30.735 | 68.72 | 2.5155 | 29.5067 | 69.265 | 5.669
132 | 12 | May | 8.2 | 10.0954 | 1359.15 | 1457.3781 | 2816.5281 | 1 | 2000 | 816.5281 | 40.8264 | 48.2562 | 32.0425 | 56.0272 | 27.1311 | 51.7438 | 60.0764
132 | 13 | May | 7.7 | 9.4798 | 1059.95 | 1404.6116 | 2464.5616 | 1 | 2000 | 464.5616 | 23.2281 | 43.0076 | 47.0025 | 33.074 | 29.7694 | 56.9924 | 43.8286
132 | 14 | May | 8.2 | 10.0954 | 1359.15 | 1249.8191 | 2608.9691 | 1 | 2000 | 608.9691 | 30.4485 | 52.0953 | 32.0425 | 48.7246 | 37.509 | 47.9047 | 44.8051
132 | 15 | May | 7.7 | 9.4798 | 1059.95 | 900.7252 | 1960.6752 | 0 | 1960.6752 | 0 | 0 | 54.0605 | 45.9395 | 0 | 54.0605 | 45.9395 | 0
132 | 16 | May | 8.2 | 10.0954 | 1359.15 | 584.3978 | 1943.5478 | 0 | 1943.5478 | 0 | 0 | 69.9314 | 30.0686 | 0 | 69.9314 | 30.0686 | 0
132 | 17 | May | 7.7 | 9.4798 | 1059.95 | 363.6999 | 1423.6499 | 0 | 1423.6499 | 0 | 0 | 74.453 | 25.547 | 0 | 74.453 | 25.547 | 0
132 | 18 | May | 8.7 | 10.711 | 1490.05 | 161.7252 | 1651.7752 | 0 | 1651.7752 | 0 | 0 | 90.209 | 9.791 | 0 | 90.209 | 9.791 | 0
132 | 19 | May | 8.7 | 10.711 | 1490.05 | 41.013 | 1531.063 | 0 | 1531.063 | 0 | 0 | 97.3213 | 2.6787 | 0 | 97.3213 | 2.6787 | 0
132 | 20 | May | 7.7 | 9.4798 | 1059.95 | 3.969 | 1063.919 | 0 | 1063.919 | 0 | 0 | 99.6269 | 0.37305 | 0 | 99.6269 | 0.37305 | 0
132 | 21 | May | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
132 | 22 | May | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
132 | 23 | May | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
132 | 24 | May | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
133 | 1 | May | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
133 | 2 | May | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
133 | 3 | May | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
133 | 4 | May | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
133 | 5 | May | 9.3 | 11.4496 | 1598.85 | 6.615 | 1605.465 | 0 | 1605.465 | 0 | 0 | 99.588 | 0.41203 | 0 | 99.588 | 0.41203 | 0
133 | 6 | May | 8.7 | 10.711 | 1490.05 | 44.982 | 1535.032 | 0 | 1535.032 | 0 | 0 | 97.0696 | 2.9304 | 0 | 97.0696 | 2.9304 | 0
133 | 7 | May | 6.2 | 7.6331 | 625.6 | 113.778 | 739.378 | 0 | 739.378 | 0 | 0 | 84.6117 | 15.3883 | 0 | 84.6117 | 15.3883 | 0
133 | 8 | May | 6.7 | 8.2487 | 761.6 | 190.512 | 952.112 | 0 | 952.112 | 0 | 0 | 79.9906 | 20.0094 | 0 | 79.9906 | 20.0094 | 0
133 | 9 | May | 6.2 | 7.6331 | 625.6 | 266.411 | 892.011 | 0 | 892.011 | 0 | 0 | 70.1337 | 29.8663 | 0 | 70.1337 | 29.8663 | 0
133 | 10 | May | 5.7 | 7.0175 | 504.9 | 328.1266 | 833.0266 | 0 | 833.0266 | 0 | 0 | 60.6103 | 39.3897 | 0 | 60.6103 | 39.3897 | 0
133 | 11 | May | 5.7 | 7.0175 | 504.9 | 364.9606 | 869.8606 | 0 | 869.8606 | 0 | 0 | 58.0438 | 41.9562 | 0 | 58.0438 | 41.9562 | 0
133 | 12 | May | 5.7 | 7.0175 | 504.9 | 383.6373 | 888.5373 | 0 | 888.5373 | 0 | 0 | 56.8237 | 43.1763 | 0 | 56.8237 | 43.1763 | 0
133 | 13 | May | 4.6 | 5.6633 | 237.15 | 379.349 | 616.499 | 0 | 616.499 | 0 | 0 | 38.4672 | 61.5328 | 0 | 38.4672 | 61.5328 | 0
133 | 14 | May | 5.7 | 7.0175 | 504.9 | 350.7546 | 855.6546 | 0 | 855.6546 | 0 | 0 | 59.0075 | 40.9925 | 0 | 59.0075 | 40.9925 | 0
133 | 15 | May | 5.7 | 7.0175 | 504.9 | 304.7984 | 809.6984 | 0 | 809.6984 | 0 | 0 | 62.3566 | 37.6434 | 0 | 62.3566 | 37.6434 | 0
133 | 16 | May | 4.6 | 5.6633 | 237.15 | 238.3234 | 475.4734 | 0 | 475.4734 | 0 | 0 | 49.8766 | 50.1234 | 0 | 49.8766 | 50.1234 | 0
133 | 17 | May | 4.6 | 5.6633 | 237.15 | 257.8888 | 495.0388 | 0 | 495.0388 | 0 | 0 | 47.9053 | 52.0947 | 0 | 47.9053 | 52.0947 | 0
133 | 18 | May | 4.6 | 5.6633 | 237.15 | 138.2244 | 375.3744 | 0 | 375.3744 | 0 | 0 | 63.1769 | 36.8231 | 0 | 63.1769 | 36.8231 | 0
133 | 19 | May | 3.1 | 3.8165 | 0 | 42.336 | 42.336 | 0 | 42.336 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
133 | 20 | May | 2.6 | 3.201 | 0 | 2.646 | 2.646 | 0 | 2.646 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
133 | 21 | May | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
133 | 22 | May | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
133 | 23 | May | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
133 | 24 | May | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134 | 1 | May | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134 | 2 | May | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134 | 3 | May | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134 | 4 | May | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134 | 5 | May | 2.6 | 3.201 | 0 | 6.615 | 6.615 | 0 | 6.615 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
134 | 6 | May | 3.6 | 4.4321 | 75.65 | 46.305 | 121.955 | 0 | 121.955 | 0 | 0 | 62.0311 | 37.9689 | 0 | 62.0311 | 37.9689 | 0
134 | 7 | May | 4.6 | 5.6633 | 237.15 | 115.101 | 352.251 | 0 | 352.251 | 0 | 0 | 67.3242 | 32.6758 | 0 | 67.3242 | 32.6758 | 0
134 | 8 | May | 5.7 | 7.0175 | 504.9 | 191.835 | 696.735 | 0 | 696.735 | 0 | 0 | 72.4666 | 27.5334 | 0 | 72.4666 | 27.5334 | 0
134 | 9 | May | 5.1 | 6.2788 | 312.8 | 267.7429 | 580.5429 | 0 | 580.5429 | 0 | 0 | 53.8806 | 46.1194 | 0 | 53.8806 | 46.1194 | 0
134 | 10 | May | 5.1 | 6.2788 | 312.8 | 328.0326 | 640.8326 | 0 | 640.8326 | 0 | 0 | 48.8115 | 51.1885 | 0 | 48.8115 | 51.1885 | 0
134 | 11 | May | 5.7 | 7.0175 | 504.9 | 364.9636 | 869.8636 | 0 | 869.8636 | 0 | 0 | 58.0436 | 41.9564 | 0 | 58.0436 | 41.9564 | 0
134 | 12 | May | 7.2 | 8.8642 | 908.65 | 659.5477 | 1568.1977 | 0 | 1568.1977 | 0 | 0 | 57.9423 | 42.0577 | 0 | 57.9423 | 42.0577 | 0
134 | 13 | May | 6.2 | 7.6331 | 625.6 | 628.4027 | 1254.0027 | 0 | 1254.0027 | 0 | 0 | 49.8882 | 50.1118 | 0 | 49.8882 | 50.1118 | 0
134 | 14 | May | 6.7 | 8.2487 | 761.6 | 579.2729 | 1340.8729 | 0 | 1340.8729 | 0 | 0 | 56.7988 | 43.2012 | 0 | 56.7988 | 43.2012 | 0
134 | 15 | May | 7.7 | 9.4798 | 1059.95 | 502.3922 | 1562.3422 | 0 | 1562.3422 | 0 | 0 | 67.8437 | 32.1563 | 0 | 67.8437 | 32.1563 | 0
134 | 16 | May | 7.7 | 9.4798 | 1059.95 | 384.8785 | 1444.8285 | 0 | 1444.8285 | 0 | 0 | 73.3616 | 26.6384 | 0 | 73.3616 | 26.6384 | 0
134 | 17 | May | 7.7 | 9.4798 | 1059.95 | 260.2039 | 1320.1539 | 0 | 1320.1539 | 0 | 0 | 80.2899 | 19.7101 | 0 | 80.2899 | 19.7101 | 0
134 | 18 | May | 7.2 | 8.8642 | 908.65 | 139.5606 | 1048.2106 | 0 | 1048.2106 | 0 | 0 | 86.6858 | 13.3142 | 0 | 86.6858 | 13.3142 | 0
134 | 19 | May | 6.2 | 7.6331 | 625.6 | 44.982 | 670.582 | 0 | 670.582 | 0 | 0 | 93.2921 | 6.7079 | 0 | 93.2921 | 6.7079 | 0
134 | 20 | May | 6.7 | 8.2487 | 761.6 | 2.646 | 764.246 | 0 | 764.246 | 0 | 0 | 99.6538 | 0.34622 | 0 | 99.6538 | 0.34622 | 0
134 | 21 | May | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
134 | 22 | May | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
134 | 23 | May | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
134 | 24 | May | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
135 | 1 | May | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
135 | 2 | May | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
135 | 3 | May | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
135 | 4 | May | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
135 | 5 | May | 5.1 | 6.2788 | 312.8 | 21.168 | 333.968 | 0 | 333.968 | 0 | 0 | 93.6617 | 6.3383 | 0 | 93.6617 | 6.3383 | 0
135 | 6 | May | 5.1 | 6.2788 | 312.8 | 135.0088 | 447.8088 | 0 | 447.8088 | 0 | 0 | 69.8512 | 30.1488 | 0 | 69.8512 | 30.1488 | 0
135 | 7 | May | 7.7 | 9.4798 | 1059.95 | 384.5681 | 1444.5181 | 0 | 1444.5181 | 0 | 0 | 73.3774 | 26.6226 | 0 | 73.3774 | 26.6226 | 0
135 | 8 | May | 8.2 | 10.0954 | 1359.15 | 713.4563 | 2072.6063 | 1 | 2000 | 72.6063 | 3.6303 | 65.5769 | 32.0425 | 10.1767 | 64.3272 | 34.4231 | 5.342
135 | 9 | May | 8.2 | 10.0954 | 1359.15 | 990.8282 | 2349.9782 | 1 | 2000 | 349.9782 | 17.4989 | 57.8367 | 32.0425 | 35.3218 | 50.4586 | 42.1633 | 25.7498
135 | 10 | May | 8.2 | 10.0954 | 1359.15 | 929.4906 | 2288.6406 | 1 | 2000 | 288.6406 | 14.432 | 59.3868 | 32.0425 | 31.0536 | 53.5255 | 40.6132 | 21.2369
135 | 11 | May | 8.7 | 10.711 | 1490.05 | 889.834 | 2379.884 | 1 | 2000 | 379.884 | 18.9942 | 62.6102 | 25.4975 | 42.6916 | 55.5083 | 37.3898 | 25.4947
135 | 12 | May | 7.7 | 9.4798 | 1059.95 | 666.503 | 1726.453 | 0 | 1726.453 | 0 | 0 | 61.3947 | 38.6053 | 0 | 61.3947 | 38.6053 | 0
135 | 13 | May | 9.3 | 11.4496 | 1598.85 | 903.8492 | 2502.6992 | 1 | 2000 | 502.6992 | 25.135 | 63.885 | 20.0575 | 55.6176 | 54.8075 | 36.115 | 31.4413
135 | 14 | May | 8.2 | 10.0954 | 1359.15 | 786.3171 | 2145.4671 | 1 | 2000 | 145.4671 | 7.2734 | 63.3498 | 32.0425 | 18.4998 | 60.6841 | 36.6502 | 10.7028
135 | 15 | May | 7.7 | 9.4798 | 1059.95 | 809.9234 | 1869.8734 | 0 | 1869.8734 | 0 | 0 | 56.6857 | 43.3143 | 0 | 56.6857 | 43.3143 | 0
135 | 16 | May | 5.1 | 6.2788 | 312.8 | 700.4783 | 1013.2783 | 0 | 1013.2783 | 0 | 0 | 30.8701 | 69.1299 | 0 | 30.8701 | 69.1299 | 0
135 | 17 | May | 7.7 | 9.4798 | 1059.95 | 434.5449 | 1494.4949 | 0 | 1494.4949 | 0 | 0 | 70.9236 | 29.0764 | 0 | 70.9236 | 29.0764 | 0
135 | 18 | May | 7.2 | 8.8642 | 908.65 | 166.1289 | 1074.7789 | 0 | 1074.7789 | 0 | 0 | 84.543 | 15.457 | 0 | 84.543 | 15.457 | 0
135 | 19 | May | 4.1 | 5.0477 | 173.4 | 76.734 | 250.134 | 0 | 250.134 | 0 | 0 | 69.3228 | 30.6772 | 0 | 69.3228 | 30.6772 | 0
135 | 20 | May | 3.6 | 4.4321 | 75.65 | 7.938 | 83.588 | 0 | 83.588 | 0 | 0 | 90.5034 | 9.4966 | 0 | 90.5034 | 9.4966 | 0
135 | 21 | May | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
135 | 22 | May | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
135 | 23 | May | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
135 | 24 | May | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
136 | 1 | May | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
136 | 2 | May | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
136 | 3 | May | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
136 | 4 | May | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
136 | 5 | May | 3.6 | 4.4321 | 75.65 | 18.522 | 94.172 | 0 | 94.172 | 0 | 0 | 80.3317 | 19.6683 | 0 | 80.3317 | 19.6683 | 0
136 | 6 | May | 5.1 | 6.2788 | 312.8 | 126.4382 | 439.2382 | 0 | 439.2382 | 0 | 0 | 71.2142 | 28.7858 | 0 | 71.2142 | 28.7858 | 0
136 | 7 | May | 6.2 | 7.6331 | 625.6 | 190.95 | 816.55 | 0 | 816.55 | 0 | 0 | 76.615 | 23.385 | 0 | 76.615 | 23.385 | 0
136 | 8 | May | 6.7 | 8.2487 | 761.6 | 314.3063 | 1075.9063 | 0 | 1075.9063 | 0 | 0 | 70.7868 | 29.2132 | 0 | 70.7868 | 29.2132 | 0
136 | 9 | May | 7.2 | 8.8642 | 908.65 | 457.5925 | 1366.2425 | 0 | 1366.2425 | 0 | 0 | 66.5072 | 33.4928 | 0 | 66.5072 | 33.4928 | 0
136 | 10 | May | 8.2 | 10.0954 | 1359.15 | 563.7432 | 1922.8932 | 0 | 1922.8932 | 0 | 0 | 70.6826 | 29.3174 | 0 | 70.6826 | 29.3174 | 0
136 | 11 | May | 8.7 | 10.711 | 1490.05 | 616.1494 | 2106.1994 | 1 | 2000 | 106.1994 | 5.31 | 70.7459 | 25.4975 | 17.236 | 69.1925 | 29.2541 | 7.1272
136 | 12 | May | 7.7 | 9.4798 | 1059.95 | 644.5198 | 1704.4698 | 0 | 1704.4698 | 0 | 0 | 62.1865 | 37.8135 | 0 | 62.1865 | 37.8135 | 0
136 | 13 | May | 7.2 | 8.8642 | 908.65 | 893.7185 | 1802.3685 | 0 | 1802.3685 | 0 | 0 | 50.4142 | 49.5858 | 0 | 50.4142 | 49.5858 | 0
136 | 14 | May | 8.7 | 10.711 | 1490.05 | 595.3258 | 2085.3758 | 1 | 2000 | 85.3758 | 4.2688 | 71.4523 | 25.4975 | 14.341 | 70.2337 | 28.5477 | 5.7297
136 | 15 | May | 8.7 | 10.711 | 1490.05 | 506.3693 | 1996.4193 | 0 | 1996.4193 | 0 | 0 | 74.6361 | 25.3639 | 0 | 74.6361 | 25.3639 | 0
136 | 16 | May | 9.3 | 11.4496 | 1598.85 | 390.7553 | 1989.6053 | 0 | 1989.6053 | 0 | 0 | 80.3602 | 19.6398 | 0 | 80.3602 | 19.6398 | 0
136 | 17 | May | 8.7 | 10.711 | 1490.05 | 264.7444 | 1754.7944 | 0 | 1754.7944 | 0 | 0 | 84.9131 | 15.0869 | 0 | 84.9131 | 15.0869 | 0
136 | 18 | May | 8.2 | 10.0954 | 1359.15 | 145.0135 | 1504.1635 | 0 | 1504.1635 | 0 | 0 | 90.3592 | 9.6408 | 0 | 90.3592 | 9.6408 | 0
136 | 19 | May | 7.2 | 8.8642 | 908.65 | 47.628 | 956.278 | 0 | 956.278 | 0 | 0 | 95.0194 | 4.9806 | 0 | 95.0194 | 4.9806 | 0
136 | 20 | May | 7.2 | 8.8642 | 908.65 | 2.646 | 911.296 | 0 | 911.296 | 0 | 0 | 99.7096 | 0.29036 | 0 | 99.7096 | 0.29036 | 0
136 | 21 | May | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
136 | 22 | May | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
136 | 23 | May | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
136 | 24 | May | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
137 | 1 | May | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
137 | 2 | May | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
137 | 3 | May | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
137 | 4 | May | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
137 | 5 | May | 7.7 | 9.4798 | 1059.95 | 22.491 | 1082.441 | 0 | 1082.441 | 0 | 0 | 97.9222 | 2.0778 | 0 | 97.9222 | 2.0778 | 0
137 | 6 | May | 7.7 | 9.4798 | 1059.95 | 79.38 | 1139.33 | 0 | 1139.33 | 0 | 0 | 93.0327 | 6.9673 | 0 | 93.0327 | 6.9673 | 0
137 | 7 | May | 8.7 | 10.711 | 1490.05 | 190.2566 | 1680.3066 | 0 | 1680.3066 | 0 | 0 | 88.6773 | 11.3227 | 0 | 88.6773 | 11.3227 | 0
137 | 8 | May | 8.7 | 10.711 | 1490.05 | 533.8332 | 2023.8832 | 1 | 2000 | 23.8832 | 1.1942 | 73.6233 | 25.4975 | 4.4739 | 73.3083 | 26.3767 | 1.6028
137 | 9 | May | 9.3 | 11.4496 | 1598.85 | 773.2009 | 2372.0509 | 1 | 2000 | 372.0509 | 18.6025 | 67.4037 | 20.0575 | 48.1183 | 61.34 | 32.5963 | 23.2699
137 | 10 | May | 9.3 | 11.4496 | 1598.85 | 747.1468 | 2345.9968 | 1 | 2000 | 345.9968 | 17.2998 | 68.1523 | 20.0575 | 46.3091 | 62.6427 | 31.8477 | 21.6404
137 | 11 | May | 11.3 | 13.9119 | 1700 | 631.4505 | 2331.4505 | 1 | 2000 | 331.4505 | 16.5725 | 72.916 | 15 | 52.4903 | 68.4275 | 27.084 | 19.4971
137 | 12 | May | 10.3 | 12.6808 | 1694.9 | 642.964 | 2337.864 | 1 | 2000 | 337.864 | 16.8932 | 72.4978 | 15.255 | 52.5479 | 67.8518 | 27.5022 | 19.9342
137 | 13 | May | 9.3 | 11.4496 | 1598.85 | 386.6189 | 1985.4689 | 0 | 1985.4689 | 0 | 0 | 80.5276 | 19.4724 | 0 | 80.5276 | 19.4724 | 0
137 | 14 | May | 9.3 | 11.4496 | 1598.85 | 601.1694 | 2200.0194 | 1 | 2000 | 200.0194 | 10.001 | 72.6744 | 20.0575 | 33.2717 | 69.9415 | 27.3256 | 12.5102
137 | 15 | May | 9.3 | 11.4496 | 1598.85 | 507.7925 | 2106.6425 | 1 | 2000 | 106.6425 | 5.3321 | 75.8956 | 20.0575 | 21.0012 | 74.6104 | 24.1044 | 6.67
137 | 16 | May | 8.7 | 10.711 | 1490.05 | 509.7555 | 1999.8055 | 0 | 1999.8055 | 0 | 0 | 74.5097 | 25.4903 | 0 | 74.5097 | 25.4903 | 0
137 | 17 | May | 8.2 | 10.0954 | 1359.15 | 419.9754 | 1779.1254 | 0 | 1779.1254 | 0 | 0 | 76.3943 | 23.6057 | 0 | 76.3943 | 23.6057 | 0
137 | 18 | May | 9.3 | 11.4496 | 1598.85 | 169.1774 | 1768.0274 | 0 | 1768.0274 | 0 | 0 | 90.4313 | 9.5687 | 0 | 90.4313 | 9.5687 | 0
137 | 19 | May | 8.2 | 10.0954 | 1359.15 | 48.951 | 1408.101 | 0 | 1408.101 | 0 | 0 | 96.5236 | 3.4764 | 0 | 96.5236 | 3.4764 | 0
137 | 20 | May | 8.2 | 10.0954 | 1359.15 | 5.292 | 1364.442 | 0 | 1364.442 | 0 | 0 | 99.6121 | 0.38785 | 0 | 99.6121 | 0.38785 | 0
137 | 21 | May | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
137 | 22 | May | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
137 | 23 | May | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
137 | 24 | May | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
138 | 1 | May | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
138 | 2 | May | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
138 | 3 | May | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
138 | 4 | May | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
138 | 5 | May | 4.1 | 5.0477 | 173.4 | 13.23 | 186.63 | 0 | 186.63 | 0 | 0 | 92.9111 | 7.0889 | 0 | 92.9111 | 7.0889 | 0
138 | 6 | May | 4.1 | 5.0477 | 173.4 | 82.026 | 255.426 | 0 | 255.426 | 0 | 0 | 67.8866 | 32.1134 | 0 | 67.8866 | 32.1134 | 0
138 | 7 | May | 4.6 | 5.6633 | 237.15 | 192.9121 | 430.0621 | 0 | 430.0621 | 0 | 0 | 55.1432 | 44.8568 | 0 | 55.1432 | 44.8568 | 0
138 | 8 | May | 3.6 | 4.4321 | 75.65 | 446.5829 | 522.2329 | 0 | 522.2329 | 0 | 0 | 14.4859 | 85.5141 | 0 | 14.4859 | 85.5141 | 0
138 | 9 | May | 2.6 | 3.201 | 0 | 457.1978 | 457.1978 | 0 | 457.1978 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
138 | 10 | May | 1 | 1.2311 | 0 | 770.3515 | 770.3515 | 0 | 770.3515 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
138 | 11 | May | 3.1 | 3.8165 | 0 | 632.8109 | 632.8109 | 0 | 632.8109 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
138 | 12 | May | 4.1 | 5.0477 | 173.4 | 911.5481 | 1084.9481 | 0 | 1084.9481 | 0 | 0 | 15.9823 | 84.0177 | 0 | 15.9823 | 84.0177 | 0
138 | 13 | May | 5.1 | 6.2788 | 312.8 | 1245.9561 | 1558.7561 | 0 | 1558.7561 | 0 | 0 | 20.0673 | 79.9327 | 0 | 20.0673 | 79.9327 | 0
138 | 14 | May | 5.1 | 6.2788 | 312.8 | 1239.1686 | 1551.9686 | 0 | 1551.9686 | 0 | 0 | 20.155 | 79.845 | 0 | 20.155 | 79.845 | 0
138 | 15 | May | 5.7 | 7.0175 | 504.9 | 1022.9146 | 1527.8146 | 0 | 1527.8146 | 0 | 0 | 33.0472 | 66.9528 | 0 | 33.0472 | 66.9528 | 0
138 | 16 | May | 5.7 | 7.0175 | 504.9 | 726.5088 | 1231.4088 | 0 | 1231.4088 | 0 | 0 | 41.0018 | 58.9982 | 0 | 41.0018 | 58.9982 | 0
138 | 17 | May | 5.1 | 6.2788 | 312.8 | 430.2864 | 743.0864 | 0 | 743.0864 | 0 | 0 | 42.0947 | 57.9053 | 0 | 42.0947 | 57.9053 | 0
138 | 18 | May | 5.1 | 6.2788 | 312.8 | 187.9943 | 500.7943 | 0 | 500.7943 | 0 | 0 | 62.4608 | 37.5392 | 0 | 62.4608 | 37.5392 | 0
138 | 19 | May | 3.6 | 4.4321 | 75.65 | 79.38 | 155.03 | 0 | 155.03 | 0 | 0 | 48.797 | 51.203 | 0 | 48.797 | 51.203 | 0
138 | 20 | May | 2.6 | 3.201 | 0 | 10.584 | 10.584 | 0 | 10.584 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
138 | 21 | May | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
138 | 22 | May | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
138 | 23 | May | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
138 | 24 | May | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139 | 1 | May | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139 | 2 | May | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139 | 3 | May | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139 | 4 | May | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139 | 5 | May | 0 | 0 | 0 | 9.261 | 9.261 | 0 | 9.261 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
139 | 6 | May | 2.1 | 2.5854 | 0 | 51.597 | 51.597 | 0 | 51.597 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
139 | 7 | May | 0 | 0 | 0 | 120.393 | 120.393 | 0 | 120.393 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
139 | 8 | May | 3.1 | 3.8165 | 0 | 197.127 | 197.127 | 0 | 197.127 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
139 | 9 | May | 1 | 1.2311 | 0 | 271.7464 | 271.7464 | 0 | 271.7464 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
139 | 10 | May | 1 | 1.2311 | 0 | 552.5849 | 552.5849 | 0 | 552.5849 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
139 | 11 | May | 2.1 | 2.5854 | 0 | 627.2651 | 627.2651 | 0 | 627.2651 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
139 | 12 | May | 3.6 | 4.4321 | 75.65 | 658.252 | 733.902 | 0 | 733.902 | 0 | 0 | 10.3079 | 89.6921 | 0 | 10.3079 | 89.6921 | 0
139 | 13 | May | 2.6 | 3.201 | 0 | 889.9158 | 889.9158 | 0 | 889.9158 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
139 | 14 | May | 3.1 | 3.8165 | 0 | 596.7844 | 596.7844 | 0 | 596.7844 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
139 | 15 | May | 4.6 | 5.6633 | 237.15 | 671.8665 | 909.0165 | 0 | 909.0165 | 0 | 0 | 26.0886 | 73.9114 | 0 | 26.0886 | 73.9114 | 0
139 | 16 | May | 5.1 | 6.2788 | 312.8 | 599.015 | 911.815 | 0 | 911.815 | 0 | 0 | 34.3052 | 65.6948 | 0 | 34.3052 | 65.6948 | 0
139 | 17 | May | 5.1 | 6.2788 | 312.8 | 420.2902 | 733.0902 | 0 | 733.0902 | 0 | 0 | 42.6687 | 57.3313 | 0 | 42.6687 | 57.3313 | 0
139 | 18 | May | 3.6 | 4.4321 | 75.65 | 192.7396 | 268.3896 | 0 | 268.3896 | 0 | 0 | 28.1866 | 71.8134 | 0 | 28.1866 | 71.8134 | 0
139 | 19 | May | 1.5 | 1.8467 | 0 | 76.734 | 76.734 | 0 | 76.734 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
139 | 20 | May | 1.5 | 1.8467 | 0 | 9.261 | 9.261 | 0 | 9.261 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
139 | 21 | May | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139 | 22 | May | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139 | 23 | May | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139 | 24 | May | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
140 | 1 | May | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
140 | 2 | May | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
140 | 3 | May | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
140 | 4 | May | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
140 | 5 | May | 5.1 | 6.2788 | 312.8 | 14.553 | 327.353 | 0 | 327.353 | 0 | 0 | 95.5543 | 4.4457 | 0 | 95.5543 | 4.4457 | 0
140 | 6 | May | 4.1 | 5.0477 | 173.4 | 52.92 | 226.32 | 0 | 226.32 | 0 | 0 | 76.6172 | 23.3828 | 0 | 76.6172 | 23.3828 | 0
140 | 7 | May | 6.2 | 7.6331 | 625.6 | 121.716 | 747.316 | 0 | 747.316 | 0 | 0 | 83.7129 | 16.2871 | 0 | 83.7129 | 16.2871 | 0
140 | 8 | May | 5.1 | 6.2788 | 312.8 | 198.45 | 511.25 | 0 | 511.25 | 0 | 0 | 61.1834 | 38.8166 | 0 | 61.1834 | 38.8166 | 0
140 | 9 | May | 6.7 | 8.2487 | 761.6 | 273.0744 | 1034.6744 | 0 | 1034.6744 | 0 | 0 | 73.6077 | 26.3923 | 0 | 73.6077 | 26.3923 | 0
140 | 10 | May | 7.2 | 8.8642 | 908.65 | 334.7957 | 1243.4457 | 0 | 1243.4457 | 0 | 0 | 73.0752 | 26.9248 | 0 | 73.0752 | 26.9248 | 0
140 | 11 | May | 7.2 | 8.8642 | 908.65 | 371.5914 | 1280.2414 | 0 | 1280.2414 | 0 | 0 | 70.9749 | 29.0251 | 0 | 70.9749 | 29.0251 | 0
140 | 12 | May | 5.1 | 6.2788 | 312.8 | 388.9448 | 701.7448 | 0 | 701.7448 | 0 | 0 | 44.5746 | 55.4254 | 0 | 44.5746 | 55.4254 | 0
140 | 13 | May | 5.1 | 6.2788 | 312.8 | 384.6608 | 697.4608 | 0 | 697.4608 | 0 | 0 | 44.8484 | 55.1516 | 0 | 44.8484 | 55.1516 | 0
140 | 14 | May | 4.6 | 5.6633 | 237.15 | 357.3925 | 594.5425 | 0 | 594.5425 | 0 | 0 | 39.8878 | 60.1122 | 0 | 39.8878 | 60.1122 | 0
140 | 15 | May | 4.1 | 5.0477 | 173.4 | 311.5042 | 484.9042 | 0 | 484.9042 | 0 | 0 | 35.7596 | 64.2404 | 0 | 35.7596 | 64.2404 | 0
140 | 16 | May | 3.6 | 4.4321 | 75.65 | 245.9576 | 321.6076 | 0 | 321.6076 | 0 | 0 | 23.5225 | 76.4775 | 0 | 23.5225 | 76.4775 | 0
140 | 17 | May | 2.1 | 2.5854 | 0 | 171.99 | 171.99 | 0 | 171.99 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
140 | 18 | May | 2.8 | 3.4472 | 0 | 127.008 | 127.008 | 0 | 127.008 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
140 | 19 | May | 3.6 | 4.4321 | 75.65 | 54.243 | 129.893 | 0 | 129.893 | 0 | 0 | 58.2402 | 41.7598 | 0 | 58.2402 | 41.7598 | 0
140 | 20 | May | 3.1 | 3.8165 | 0 | 6.615 | 6.615 | 0 | 6.615 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
140 | 21 | May | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
140 | 22 | May | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
140 | 23 | May | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
140 | 24 | May | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
141 | 1 | May | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
141 | 2 | May | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
141 | 3 | May | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
141 | 4 | May | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
141 | 5 | May | 3.1 | 3.8165 | 0 | 19.845 | 19.845 | 0 | 19.845 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
141 | 6 | May | 3.1 | 3.8165 | 0 | 85.995 | 85.995 | 0 | 85.995 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
141 | 7 | May | 4.1 | 5.0477 | 173.4 | 123.039 | 296.439 | 0 | 296.439 | 0 | 0 | 58.4943 | 41.5057 | 0 | 58.4943 | 41.5057 | 0
141 | 8 | May | 1 | 1.2311 | 0 | 343.8743 | 343.8743 | 0 | 343.8743 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
141 | 9 | May | 1 | 1.2311 | 0 | 462.0381 | 462.0381 | 0 | 462.0381 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
141 | 10 | May | 2.6 | 3.201 | 0 | 563.5183 | 563.5183 | 0 | 563.5183 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
141 | 11 | May | 6.2 | 7.6331 | 625.6 | 618.4438 | 1244.0438 | 0 | 1244.0438 | 0 | 0 | 50.2876 | 49.7124 | 0 | 50.2876 | 49.7124 | 0
141 | 12 | May | 6.7 | 8.2487 | 761.6 | 649.6662 | 1411.2662 | 0 | 1411.2662 | 0 | 0 | 53.9657 | 46.0343 | 0 | 53.9657 | 46.0343 | 0
141 | 13 | May | 7.7 | 9.4798 | 1059.95 | 390.6189 | 1450.5689 | 0 | 1450.5689 | 0 | 0 | 73.0713 | 26.9287 | 0 | 73.0713 | 26.9287 | 0
141 | 14 | May | 6.2 | 7.6331 | 625.6 | 360.088 | 985.688 | 0 | 985.688 | 0 | 0 | 63.4684 | 36.5316 | 0 | 63.4684 | 36.5316 | 0
141 | 15 | May | 6.7 | 8.2487 | 761.6 | 515.2046 | 1276.8046 | 0 | 1276.8046 | 0 | 0 | 59.6489 | 40.3511 | 0 | 59.6489 | 40.3511 | 0
141 | 16 | May | 5.7 | 7.0175 | 504.9 | 607.2612 | 1112.1612 | 0 | 1112.1612 | 0 | 0 | 45.3981 | 54.6019 | 0 | 45.3981 | 54.6019 | 0
141 | 17 | May | 4.1 | 5.0477 | 173.4 | 269.6418 | 443.0418 | 0 | 443.0418 | 0 | 0 | 39.1385 | 60.8615 | 0 | 39.1385 | 60.8615 | 0
141 | 18 | May | 5.1 | 6.2788 | 312.8 | 209.1624 | 521.9624 | 0 | 521.9624 | 0 | 0 | 59.9277 | 40.0723 | 0 | 59.9277 | 40.0723 | 0
141 | 19 | May | 2.1 | 2.5854 | 0 | 55.566 | 55.566 | 0 | 55.566 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
141 | 20 | May | 1 | 1.2311 | 0 | 6.615 | 6.615 | 0 | 6.615 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
141 | 21 | May | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
141 | 22 | May | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
141 | 23 | May | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
141 | 24 | May | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
142 | 1 | May | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
142 | 2 | May | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
142 | 3 | May | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
142 | 4 | May | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
142 | 5 | May | 0 | 0 | 0 | 27.783 | 27.783 | 0 | 27.783 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
142 | 6 | May | 1 | 1.2311 | 0 | 154.3315 | 154.3315 | 0 | 154.3315 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
142 | 7 | May | 1 | 1.2311 | 0 | 404.3837 | 404.3837 | 0 | 404.3837 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
142 | 8 | May | 1 | 1.2311 | 0 | 727.2258 | 727.2258 | 0 | 727.2258 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
142 | 9 | May | 3.6 | 4.4321 | 75.65 | 1037.8562 | 1113.5062 | 0 | 1113.5062 | 0 | 0 | 6.7939 | 93.2061 | 0 | 6.7939 | 93.2061 | 0
142 | 10 | May | 4.6 | 5.6633 | 237.15 | 1280.6449 | 1517.7949 | 0 | 1517.7949 | 0 | 0 | 15.6246 | 84.3754 | 0 | 15.6246 | 84.3754 | 0
142 | 11 | May | 5.7 | 7.0175 | 504.9 | 1453.2627 | 1958.1627 | 0 | 1958.1627 | 0 | 0 | 25.7844 | 74.2156 | 0 | 25.7844 | 74.2156 | 0
142 | 12 | May | 6.2 | 7.6331 | 625.6 | 1507.7127 | 2133.3127 | 1 | 2000 | 133.3127 | 6.6656 | 29.3253 | 68.72 | 8.842 | 24.6144 | 70.6747 | 21.3096
142 | 13 | May | 6.2 | 7.6331 | 625.6 | 1446.5968 | 2072.1968 | 1 | 2000 | 72.1968 | 3.6098 | 30.1902 | 68.72 | 4.9908 | 27.6702 | 69.8098 | 11.5404
142 | 14 | May | 6.2 | 7.6331 | 625.6 | 1288.0293 | 1913.6293 | 0 | 1913.6293 | 0 | 0 | 32.6918 | 67.3082 | 0 | 32.6918 | 67.3082 | 0
142 | 15 | May | 6.2 | 7.6331 | 625.6 | 1044.2241 | 1669.8241 | 0 | 1669.8241 | 0 | 0 | 37.465 | 62.535 | 0 | 37.465 | 62.535 | 0
142 | 16 | May | 6.2 | 7.6331 | 625.6 | 746.3687 | 1371.9687 | 0 | 1371.9687 | 0 | 0 | 45.5987 | 54.4013 | 0 | 45.5987 | 54.4013 | 0
142 | 17 | May | 6.2 | 7.6331 | 625.6 | 445.2037 | 1070.8037 | 0 | 1070.8037 | 0 | 0 | 58.4234 | 41.5766 | 0 | 58.4234 | 41.5766 | 0
142 | 18 | May | 4.6 | 5.6633 | 237.15 | 197.8348 | 434.9848 | 0 | 434.9848 | 0 | 0 | 54.5191 | 45.4809 | 0 | 54.5191 | 45.4809 | 0
142 | 19 | May | 5.1 | 6.2788 | 312.8 | 87.318 | 400.118 | 0 | 400.118 | 0 | 0 | 78.1769 | 21.8231 | 0 | 78.1769 | 21.8231 | 0
142 | 20 | May | 3.6 | 4.4321 | 75.65 | 13.23 | 88.88 | 0 | 88.88 | 0 | 0 | 85.1148 | 14.8852 | 0 | 85.1148 | 14.8852 | 0
142 | 21 | May | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
142 | 22 | May | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
142 | 23 | May | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
142 | 24 | May | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
143 | 1 | May | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
143 | 2 | May | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
143 | 3 | May | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
143 | 4 | May | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
143 | 5 | May | 4.6 | 5.6633 | 237.15 | 21.168 | 258.318 | 0 | 258.318 | 0 | 0 | 91.8054 | 8.1946 | 0 | 91.8054 | 8.1946 | 0
143 | 6 | May | 4.6 | 5.6633 | 237.15 | 132.9078 | 370.0578 | 0 | 370.0578 | 0 | 0 | 64.0846 | 35.9154 | 0 | 64.0846 | 35.9154 | 0
143 | 7 | May | 4.6 | 5.6633 | 237.15 | 381.8485 | 618.9985 | 0 | 618.9985 | 0 | 0 | 38.3119 | 61.6881 | 0 | 38.3119 | 61.6881 | 0
143 | 8 | May | 5.7 | 7.0175 | 504.9 | 707.4441 | 1212.3441 | 0 | 1212.3441 | 0 | 0 | 41.6466 | 58.3534 | 0 | 41.6466 | 58.3534 | 0
143 | 9 | May | 5.7 | 7.0175 | 504.9 | 1019.3887 | 1524.2887 | 0 | 1524.2887 | 0 | 0 | 33.1236 | 66.8764 | 0 | 33.1236 | 66.8764 | 0
143 | 10 | May | 6.2 | 7.6331 | 625.6 | 1256.3926 | 1881.9926 | 0 | 1881.9926 | 0 | 0 | 33.2414 | 66.7586 | 0 | 33.2414 | 66.7586 | 0
143 | 11 | May | 6.2 | 7.6331 | 625.6 | 1417.4802 | 2043.0802 | 1 | 2000 | 43.0802 | 2.154 | 30.6204 | 68.72 | 3.0392 | 29.126 | 69.3796 | 6.8862
143 | 12 | May | 6.7 | 8.2487 | 761.6 | 1466.7681 | 2228.3681 | 1 | 2000 | 228.3681 | 11.4184 | 34.1775 | 61.92 | 15.5695 | 26.6616 | 65.8225 | 29.9853
143 | 13 | May | 7.2 | 8.8642 | 908.65 | 1413.8523 | 2322.5023 | 1 | 2000 | 322.5023 | 16.1251 | 39.1237 | 54.5675 | 22.8102 | 29.3074 | 60.8763 | 35.4925
143 | 14 | May | 7.2 | 8.8642 | 908.65 | 1264.4749 | 2173.1249 | 1 | 2000 | 173.1249 | 8.6562 | 41.8131 | 54.5675 | 13.6914 | 36.7763 | 58.1869 | 19.053
143 | 15 | May | 6.2 | 7.6331 | 625.6 | 1043.1863 | 1668.7863 | 0 | 1668.7863 | 0 | 0 | 37.4883 | 62.5117 | 0 | 37.4883 | 62.5117 | 0
143 | 16 | May | 6.7 | 8.2487 | 761.6 | 747.181 | 1508.781 | 0 | 1508.781 | 0 | 0 | 50.4778 | 49.5222 | 0 | 50.4778 | 49.5222 | 0
143 | 17 | May | 6.7 | 8.2487 | 761.6 | 444.0935 | 1205.6935 | 0 | 1205.6935 | 0 | 0 | 63.167 | 36.833 | 0 | 63.167 | 36.833 | 0
143 | 18 | May | 7.2 | 8.8642 | 908.65 | 199.3022 | 1107.9522 | 0 | 1107.9522 | 0 | 0 | 82.0117 | 17.9883 | 0 | 82.0117 | 17.9883 | 0
143 | 19 | May | 6.7 | 8.2487 | 761.6 | 83.349 | 844.949 | 0 | 844.949 | 0 | 0 | 90.1356 | 9.8644 | 0 | 90.1356 | 9.8644 | 0
143 | 20 | May | 6.7 | 8.2487 | 761.6 | 13.23 | 774.83 | 0 | 774.83 | 0 | 0 | 98.2925 | 1.7075 | 0 | 98.2925 | 1.7075 | 0
143 | 21 | May | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
143 | 22 | May | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
143 | 23 | May | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
143 | 24 | May | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
144 | 1 | May | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
144 | 2 | May | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
144 | 3 | May | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
144 | 4 | May | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
144 | 5 | May | 6.2 | 7.6331 | 625.6 | 25.137 | 650.737 | 0 | 650.737 | 0 | 0 | 96.1371 | 3.8629 | 0 | 96.1371 | 3.8629 | 0
144 | 6 | May | 5.1 | 6.2788 | 312.8 | 91.287 | 404.087 | 0 | 404.087 | 0 | 0 | 77.4091 | 22.5909 | 0 | 77.4091 | 22.5909 | 0
144 | 7 | May | 5.6 | 6.8944 | 399.5 | 203.899 | 603.399 | 0 | 603.399 | 0 | 0 | 66.2083 | 33.7917 | 0 | 66.2083 | 33.7917 | 0
144 | 8 | May | 6.2 | 7.6331 | 625.6 | 331.5347 | 957.1347 | 0 | 957.1347 | 0 | 0 | 65.3617 | 34.6383 | 0 | 65.3617 | 34.6383 | 0
144 | 9 | May | 6.7 | 8.2487 | 761.6 | 460.7422 | 1222.3422 | 0 | 1222.3422 | 0 | 0 | 62.3066 | 37.6934 | 0 | 62.3066 | 37.6934 | 0
144 | 10 | May | 6.7 | 8.2487 | 761.6 | 560.7323 | 1322.3323 | 0 | 1322.3323 | 0 | 0 | 57.5952 | 42.4048 | 0 | 57.5952 | 42.4048 | 0
144 | 11 | May | 6.7 | 8.2487 | 761.6 | 379.1983 | 1140.7983 | 0 | 1140.7983 | 0 | 0 | 66.7603 | 33.2397 | 0 | 66.7603 | 33.2397 | 0
144 | 12 | May | 6.7 | 8.2487 | 761.6 | 680.7877 | 1442.3877 | 0 | 1442.3877 | 0 | 0 | 52.8013 | 47.1987 | 0 | 52.8013 | 47.1987 | 0
144 | 13 | May | 6.2 | 7.6331 | 625.6 | 652.643 | 1278.243 | 0 | 1278.243 | 0 | 0 | 48.9422 | 51.0578 | 0 | 48.9422 | 51.0578 | 0
144 | 14 | May | 6.9 | 8.4949 | 761.6 | 592.9321 | 1354.5321 | 0 | 1354.5321 | 0 | 0 | 56.2261 | 43.7739 | 0 | 56.2261 | 43.7739 | 0
144 | 15 | May | 7.7 | 9.4798 | 1059.95 | 517.9305 | 1577.8805 | 0 | 1577.8805 | 0 | 0 | 67.1756 | 32.8244 | 0 | 67.1756 | 32.8244 | 0
144 | 16 | May | 7.2 | 8.8642 | 908.65 | 404.1115 | 1312.7615 | 0 | 1312.7615 | 0 | 0 | 69.2167 | 30.7833 | 0 | 69.2167 | 30.7833 | 0
144 | 17 | May | 7.2 | 8.8642 | 908.65 | 279.6193 | 1188.2693 | 0 | 1188.2693 | 0 | 0 | 76.4684 | 23.5316 | 0 | 76.4684 | 23.5316 | 0
144 | 18 | May | 6.2 | 7.6331 | 625.6 | 160.003 | 785.603 | 0 | 785.603 | 0 | 0 | 79.6331 | 20.3669 | 0 | 79.6331 | 20.3669 | 0
144 | 19 | May | 5.7 | 7.0175 | 504.9 | 60.858 | 565.758 | 0 | 565.758 | 0 | 0 | 89.2431 | 10.7569 | 0 | 89.2431 | 10.7569 | 0
144 | 20 | May | 6.2 | 7.6331 | 625.6 | 7.938 | 633.538 | 0 | 633.538 | 0 | 0 | 98.747 | 1.253 | 0 | 98.747 | 1.253 | 0
144 | 21 | May | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
144 | 22 | May | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
144 | 23 | May | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
144 | 24 | May | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
145 | 1 | May | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
145 | 2 | May | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
145 | 3 | May | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
145 | 4 | May | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
145 | 5 | May | 5.7 | 7.0175 | 504.9 | 10.584 | 515.484 | 0 | 515.484 | 0 | 0 | 97.9468 | 2.0532 | 0 | 97.9468 | 2.0532 | 0
145 | 6 | May | 6.7 | 8.2487 | 761.6 | 58.212 | 819.812 | 0 | 819.812 | 0 | 0 | 92.8993 | 7.1007 | 0 | 92.8993 | 7.1007 | 0
145 | 7 | May | 6.7 | 8.2487 | 761.6 | 127.008 | 888.608 | 0 | 888.608 | 0 | 0 | 85.7071 | 14.2929 | 0 | 85.7071 | 14.2929 | 0
145 | 8 | May | 6.2 | 7.6331 | 625.6 | 203.742 | 829.342 | 0 | 829.342 | 0 | 0 | 75.4333 | 24.5667 | 0 | 75.4333 | 24.5667 | 0
145 | 9 | May | 5.7 | 7.0175 | 504.9 | 278.2863 | 783.1863 | 0 | 783.1863 | 0 | 0 | 64.4674 | 35.5326 | 0 | 64.4674 | 35.5326 | 0
145 | 10 | May | 6.7 | 8.2487 | 761.6 | 338.7798 | 1100.3798 | 0 | 1100.3798 | 0 | 0 | 69.2125 | 30.7875 | 0 | 69.2125 | 30.7875 | 0
145 | 11 | May | 7.7 | 9.4798 | 1059.95 | 644.3002 | 1704.2502 | 0 | 1704.2502 | 0 | 0 | 62.1945 | 37.8055 | 0 | 62.1945 | 37.8055 | 0
145 | 12 | May | 7.7 | 9.4798 | 1059.95 | 653.6955 | 1713.6455 | 0 | 1713.6455 | 0 | 0 | 61.8535 | 38.1465 | 0 | 61.8535 | 38.1465 | 0
145 | 13 | May | 7.7 | 9.4798 | 1059.95 | 644.6225 | 1704.5725 | 0 | 1704.5725 | 0 | 0 | 62.1827 | 37.8173 | 0 | 62.1827 | 37.8173 | 0
145 | 14 | May | 7.2 | 8.8642 | 908.65 | 596.9952 | 1505.6452 | 0 | 1505.6452 | 0 | 0 | 60.3495 | 39.6505 | 0 | 60.3495 | 39.6505 | 0
145 | 15 | May | 8 | 9.8492 | 1213.8 | 519.3509 | 1733.1509 | 0 | 1733.1509 | 0 | 0 | 70.0343 | 29.9657 | 0 | 70.0343 | 29.9657 | 0
145 | 16 | May | 8.7 | 10.711 | 1490.05 | 406.404 | 1896.454 | 0 | 1896.454 | 0 | 0 | 78.5703 | 21.4297 | 0 | 78.5703 | 21.4297 | 0
145 | 17 | May | 8.2 | 10.0954 | 1359.15 | 282.3051 | 1641.4551 | 0 | 1641.4551 | 0 | 0 | 82.8015 | 17.1985 | 0 | 82.8015 | 17.1985 | 0
145 | 18 | May | 8 | 9.8492 | 1213.8 | 161.3464 | 1375.1464 | 0 | 1375.1464 | 0 | 0 | 88.267 | 11.733 | 0 | 88.267 | 11.733 | 0
145 | 19 | May | 7.7 | 9.4798 | 1059.95 | 62.181 | 1122.131 | 0 | 1122.131 | 0 | 0 | 94.4587 | 5.5413 | 0 | 94.4587 | 5.5413 | 0
145 | 20 | May | 8.7 | 10.711 | 1490.05 | 9.261 | 1499.311 | 0 | 1499.311 | 0 | 0 | 99.3823 | 0.61768 | 0 | 99.3823 | 0.61768 | 0
145 | 21 | May | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
145 | 22 | May | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
145 | 23 | May | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
145 | 24 | May | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
146 | 1 | May | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
146 | 2 | May | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
146 | 3 | May | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
146 | 4 | May | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
146 | 5 | May | 7.7 | 9.4798 | 1059.95 | 11.907 | 1071.857 | 0 | 1071.857 | 0 | 0 | 98.8891 | 1.1109 | 0 | 98.8891 | 1.1109 | 0
146 | 6 | May | 8.7 | 10.711 | 1490.05 | 58.212 | 1548.262 | 0 | 1548.262 | 0 | 0 | 96.2402 | 3.7598 | 0 | 96.2402 | 3.7598 | 0
146 | 7 | May | 8.7 | 10.711 | 1490.05 | 276.8937 | 1766.9437 | 0 | 1766.9437 | 0 | 0 | 84.3292 | 15.6708 | 0 | 84.3292 | 15.6708 | 0
146 | 8 | May | 7.7 | 9.4798 | 1059.95 | 330.2817 | 1390.2317 | 0 | 1390.2317 | 0 | 0 | 76.2427 | 23.7573 | 0 | 76.2427 | 23.7573 | 0
146 | 9 | May | 8.2 | 10.0954 | 1359.15 | 470.0114 | 1829.1614 | 0 | 1829.1614 | 0 | 0 | 74.3045 | 25.6955 | 0 | 74.3045 | 25.6955 | 0
146 | 10 | May | 8.2 | 10.0954 | 1359.15 | 571.6412 | 1930.7912 | 0 | 1930.7912 | 0 | 0 | 70.3934 | 29.6066 | 0 | 70.3934 | 29.6066 | 0
146 | 11 | May | 7.7 | 9.4798 | 1059.95 | 886.2461 | 1946.1961 | 0 | 1946.1961 | 0 | 0 | 54.4627 | 45.5373 | 0 | 54.4627 | 45.5373 | 0
146 | 12 | May | 8.2 | 10.0954 | 1359.15 | 668.7265 | 2027.8765 | 1 | 2000 | 27.8765 | 1.3938 | 67.0233 | 32.0425 | 4.1686 | 66.5637 | 32.9767 | 2.051
146 | 13 | May | 7.7 | 9.4798 | 1059.95 | 394.6213 | 1454.5713 | 0 | 1454.5713 | 0 | 0 | 72.8703 | 27.1297 | 0 | 72.8703 | 27.1297 | 0
146 | 14 | May | 9.3 | 11.4496 | 1598.85 | 364.0761 | 1962.9261 | 0 | 1962.9261 | 0 | 0 | 81.4524 | 18.5476 | 0 | 81.4524 | 18.5476 | 0
146 | 15 | May | 8.7 | 10.711 | 1490.05 | 318.0169 | 1808.0669 | 0 | 1808.0669 | 0 | 0 | 82.4112 | 17.5888 | 0 | 82.4112 | 17.5888 | 0
146 | 16 | May | 6.2 | 7.6331 | 625.6 | 252.5104 | 878.1104 | 0 | 878.1104 | 0 | 0 | 71.2439 | 28.7561 | 0 | 71.2439 | 28.7561 | 0
146 | 17 | May | 7.2 | 8.8642 | 908.65 | 178.605 | 1087.255 | 0 | 1087.255 | 0 | 0 | 83.5729 | 16.4271 | 0 | 83.5729 | 16.4271 | 0
146 | 18 | May | 7.7 | 9.4798 | 1059.95 | 103.194 | 1163.144 | 0 | 1163.144 | 0 | 0 | 91.128 | 8.872 | 0 | 91.128 | 8.872 | 0
146 | 19 | May | 7.2 | 8.8642 | 908.65 | 39.69 | 948.34 | 0 | 948.34 | 0 | 0 | 95.8148 | 4.1852 | 0 | 95.8148 | 4.1852 | 0
146 | 20 | May | 7.7 | 9.4798 | 1059.95 | 5.292 | 1065.242 | 0 | 1065.242 | 0 | 0 | 99.5032 | 0.49679 | 0 | 99.5032 | 0.49679 | 0
146 | 21 | May | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
146 | 22 | May | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
146 | 23 | May | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
146 | 24 | May | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
147 | 1 | May | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
147 | 2 | May | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
147 | 3 | May | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
147 | 4 | May | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
147 | 5 | May | 4.6 | 5.6633 | 237.15 | 11.907 | 249.057 | 0 | 249.057 | 0 | 0 | 95.2192 | 4.7808 | 0 | 95.2192 | 4.7808 | 0
147 | 6 | May | 5.1 | 6.2788 | 312.8 | 59.535 | 372.335 | 0 | 372.335 | 0 | 0 | 84.0104 | 15.9896 | 0 | 84.0104 | 15.9896 | 0
147 | 7 | May | 5.7 | 7.0175 | 504.9 | 129.654 | 634.554 | 0 | 634.554 | 0 | 0 | 79.5677 | 20.4323 | 0 | 79.5677 | 20.4323 | 0
147 | 8 | May | 5.7 | 7.0175 | 504.9 | 205.065 | 709.965 | 0 | 709.965 | 0 | 0 | 71.1162 | 28.8838 | 0 | 71.1162 | 28.8838 | 0
147 | 9 | May | 5.1 | 6.2788 | 312.8 | 279.6124 | 592.4124 | 0 | 592.4124 | 0 | 0 | 52.8011 | 47.1989 | 0 | 52.8011 | 47.1989 | 0
147 | 10 | May | 5.7 | 7.0175 | 504.9 | 340.1042 | 845.0042 | 0 | 845.0042 | 0 | 0 | 59.7512 | 40.2488 | 0 | 59.7512 | 40.2488 | 0
147 | 11 | May | 4.6 | 5.6633 | 237.15 | 376.8885 | 614.0385 | 0 | 614.0385 | 0 | 0 | 38.6214 | 61.3786 | 0 | 38.6214 | 61.3786 | 0
147 | 12 | May | 8.2 | 10.0954 | 1359.15 | 395.568 | 1754.718 | 0 | 1754.718 | 0 | 0 | 77.4569 | 22.5431 | 0 | 77.4569 | 22.5431 | 0
147 | 13 | May | 8.2 | 10.0954 | 1359.15 | 391.2915 | 1750.4415 | 0 | 1750.4415 | 0 | 0 | 77.6461 | 22.3539 | 0 | 77.6461 | 22.3539 | 0
147 | 14 | May | 7.7 | 9.4798 | 1059.95 | 365.4028 | 1425.3528 | 0 | 1425.3528 | 0 | 0 | 74.364 | 25.636 | 0 | 74.364 | 25.636 | 0
147 | 15 | May | 5.1 | 6.2788 | 312.8 | 319.3537 | 632.1537 | 0 | 632.1537 | 0 | 0 | 49.4816 | 50.5184 | 0 | 49.4816 | 50.5184 | 0
147 | 16 | May | 4.6 | 5.6633 | 237.15 | 254.6963 | 491.8463 | 0 | 491.8463 | 0 | 0 | 48.2163 | 51.7837 | 0 | 48.2163 | 51.7837 | 0
147 | 17 | May | 4.1 | 5.0477 | 173.4 | 181.251 | 354.651 | 0 | 354.651 | 0 | 0 | 48.8931 | 51.1069 | 0 | 48.8931 | 51.1069 | 0
147 | 18 | May | 1 | 1.2311 | 0 | 104.517 | 104.517 | 0 | 104.517 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
147 | 19 | May | 2.6 | 3.201 | 0 | 41.013 | 41.013 | 0 | 41.013 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
147 | 20 | May | 3.6 | 4.4321 | 75.65 | 9.261 | 84.911 | 0 | 84.911 | 0 | 0 | 89.0933 | 10.9067 | 0 | 89.0933 | 10.9067 | 0
147 | 21 | May | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
147 | 22 | May | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
147 | 23 | May | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
147 | 24 | May | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
148 | 1 | May | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
148 | 2 | May | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
148 | 3 | May | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
148 | 4 | May | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
148 | 5 | May | 3.6 | 4.4321 | 75.65 | 11.907 | 87.557 | 0 | 87.557 | 0 | 0 | 86.4009 | 13.5991 | 0 | 86.4009 | 13.5991 | 0
148 | 6 | May | 4.6 | 5.6633 | 237.15 | 96.579 | 333.729 | 0 | 333.729 | 0 | 0 | 71.0607 | 28.9393 | 0 | 71.0607 | 28.9393 | 0
148 | 7 | May | 5.7 | 7.0175 | 504.9 | 209.4805 | 714.3805 | 0 | 714.3805 | 0 | 0 | 70.6766 | 29.3234 | 0 | 70.6766 | 29.3234 | 0
148 | 8 | May | 5.7 | 7.0175 | 504.9 | 336.813 | 841.713 | 0 | 841.713 | 0 | 0 | 59.9848 | 40.0152 | 0 | 59.9848 | 40.0152 | 0
148 | 9 | May | 4.6 | 5.6633 | 237.15 | 278.8654 | 516.0154 | 0 | 516.0154 | 0 | 0 | 45.9579 | 54.0421 | 0 | 45.9579 | 54.0421 | 0
148 | 10 | May | 4.6 | 5.6633 | 237.15 | 341.427 | 578.577 | 0 | 578.577 | 0 | 0 | 40.9885 | 59.0115 | 0 | 40.9885 | 59.0115 | 0
148 | 11 | May | 3.1 | 3.8165 | 0 | 379.5346 | 379.5346 | 0 | 379.5346 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
148 | 12 | May | 3.1 | 3.8165 | 0 | 680.1129 | 680.1129 | 0 | 680.1129 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
148 | 13 | May | 3.1 | 3.8165 | 0 | 651.5145 | 651.5145 | 0 | 651.5145 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
148 | 14 | May | 2.1 | 2.5854 | 0 | 371.2157 | 371.2157 | 0 | 371.2157 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
148 | 15 | May | 2.6 | 3.201 | 0 | 322.0136 | 322.0136 | 0 | 322.0136 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
148 | 16 | May | 3.1 | 3.8165 | 0 | 256.0305 | 256.0305 | 0 | 256.0305 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
148 | 17 | May | 3.6 | 4.4321 | 75.65 | 182.574 | 258.224 | 0 | 258.224 | 0 | 0 | 29.2963 | 70.7037 | 0 | 29.2963 | 70.7037 | 0
148 | 18 | May | 3.6 | 4.4321 | 75.65 | 165.8723 | 241.5223 | 0 | 241.5223 | 0 | 0 | 31.3222 | 68.6778 | 0 | 31.3222 | 68.6778 | 0
148 | 19 | May | 4.1 | 5.0477 | 173.4 | 66.15 | 239.55 | 0 | 239.55 | 0 | 0 | 72.3857 | 27.6143 | 0 | 72.3857 | 27.6143 | 0
148 | 20 | May | 4.6 | 5.6633 | 237.15 | 15.876 | 253.026 | 0 | 253.026 | 0 | 0 | 93.7255 | 6.2745 | 0 | 93.7255 | 6.2745 | 0
148 | 21 | May | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
148 | 22 | May | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
148 | 23 | May | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
148 | 24 | May | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
149 | 1 | May | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
149 | 2 | May | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
149 | 3 | May | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149 | 4 | May | 4.1 | 5.0477 | 173.4 | 1.323 | 174.723 | 0 | 174.723 | 0 | 0 | 99.2428 | 0.7572 | 0 | 99.2428 | 0.7572 | 0
149 | 5 | May | 3.1 | 3.8165 | 0 | 37.044 | 37.044 | 0 | 37.044 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
149 | 6 | May | 4.1 | 5.0477 | 173.4 | 168.0033 | 341.4033 | 0 | 341.4033 | 0 | 0 | 50.7904 | 49.2096 | 0 | 50.7904 | 49.2096 | 0
149 | 7 | May | 4.6 | 5.6633 | 237.15 | 417.9826 | 655.1326 | 0 | 655.1326 | 0 | 0 | 36.1988 | 63.8012 | 0 | 36.1988 | 63.8012 | 0
149 | 8 | May | 5.1 | 6.2788 | 312.8 | 734.6403 | 1047.4403 | 0 | 1047.4403 | 0 | 0 | 29.8633 | 70.1367 | 0 | 29.8633 | 70.1367 | 0
149 | 9 | May | 4.6 | 5.6633 | 237.15 | 995.0727 | 1232.2227 | 0 | 1232.2227 | 0 | 0 | 19.2457 | 80.7543 | 0 | 19.2457 | 80.7543 | 0
149 | 10 | May | 5.7 | 7.0175 | 504.9 | 960.3244 | 1465.2244 | 0 | 1465.2244 | 0 | 0 | 34.4589 | 65.5411 | 0 | 34.4589 | 65.5411 | 0
149 | 11 | May | 5.1 | 6.2788 | 312.8 | 1341.9019 | 1654.7019 | 0 | 1654.7019 | 0 | 0 | 18.9037 | 81.0963 | 0 | 18.9037 | 81.0963 | 0
149 | 12 | May | 4.6 | 5.6633 | 237.15 | 1419.8187 | 1656.9687 | 0 | 1656.9687 | 0 | 0 | 14.3123 | 85.6877 | 0 | 14.3123 | 85.6877 | 0
149 | 13 | May | 6.2 | 7.6331 | 625.6 | 1099.015 | 1724.615 | 0 | 1724.615 | 0 | 0 | 36.2748 | 63.7252 | 0 | 36.2748 | 63.7252 | 0
149 | 14 | May | 5.7 | 7.0175 | 504.9 | 1119.17 | 1624.07 | 0 | 1624.07 | 0 | 0 | 31.0886 | 68.9114 | 0 | 31.0886 | 68.9114 | 0
149 | 15 | May | 6.2 | 7.6331 | 625.6 | 941.0886 | 1566.6886 | 0 | 1566.6886 | 0 | 0 | 39.9314 | 60.0686 | 0 | 39.9314 | 60.0686 | 0
149 | 16 | May | 6.7 | 8.2487 | 761.6 | 536.6641 | 1298.2641 | 0 | 1298.2641 | 0 | 0 | 58.6629 | 41.3371 | 0 | 58.6629 | 41.3371 | 0
149 | 17 | May | 6.7 | 8.2487 | 761.6 | 287.6162 | 1049.2162 | 0 | 1049.2162 | 0 | 0 | 72.5875 | 27.4125 | 0 | 72.5875 | 27.4125 | 0
149 | 18 | May | 4.6 | 5.6633 | 237.15 | 168.3775 | 405.5275 | 0 | 405.5275 | 0 | 0 | 58.4794 | 41.5206 | 0 | 58.4794 | 41.5206 | 0
149 | 19 | May | 4.6 | 5.6633 | 237.15 | 67.473 | 304.623 | 0 | 304.623 | 0 | 0 | 77.8503 | 22.1497 | 0 | 77.8503 | 22.1497 | 0
149 | 20 | May | 4.6 | 5.6633 | 237.15 | 6.615 | 243.765 | 0 | 243.765 | 0 | 0 | 97.2863 | 2.7137 | 0 | 97.2863 | 2.7137 | 0
149 | 21 | May | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
149 | 22 | May | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
149 | 23 | May | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
149 | 24 | May | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
150 | 1 | May | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 2 | May | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 3 | May | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 4 | May | 5.1 | 6.2788 | 312.8 | 1.323 | 314.123 | 0 | 314.123 | 0 | 0 | 99.5788 | 0.42117 | 0 | 99.5788 | 0.42117 | 0
150 | 5 | May | 5.1 | 6.2788 | 312.8 | 31.752 | 344.552 | 0 | 344.552 | 0 | 0 | 90.7846 | 9.2154 | 0 | 90.7846 | 9.2154 | 0
150 | 6 | May | 6.2 | 7.6331 | 625.6 | 143.9563 | 769.5563 | 0 | 769.5563 | 0 | 0 | 81.2936 | 18.7064 | 0 | 81.2936 | 18.7064 | 0
150 | 7 | May | 6.2 | 7.6331 | 625.6 | 277.698 | 903.298 | 0 | 903.298 | 0 | 0 | 69.2573 | 30.7427 | 0 | 69.2573 | 30.7427 | 0
150 | 8 | May | 7.7 | 9.4798 | 1059.95 | 463.666 | 1523.616 | 0 | 1523.616 | 0 | 0 | 69.5681 | 30.4319 | 0 | 69.5681 | 30.4319 | 0
150 | 9 | May | 7.7 | 9.4798 | 1059.95 | 648.8187 | 1708.7687 | 0 | 1708.7687 | 0 | 0 | 62.03 | 37.97 | 0 | 62.03 | 37.97 | 0
150 | 10 | May | 10.3 | 12.6808 | 1694.9 | 794.2212 | 2489.1212 | 1 | 2000 | 489.1212 | 24.4561 | 68.0923 | 15.255 | 61.585 | 60.2889 | 31.9077 | 28.8584
150 | 11 | May | 9.3 | 11.4496 | 1598.85 | 851.8007 | 2450.6507 | 1 | 2000 | 450.6507 | 22.5325 | 65.2419 | 20.0575 | 52.9057 | 57.41 | 34.7581 | 28.1859
150 | 12 | May | 10.8 | 13.2964 | 1698.3 | 677.2444 | 2375.5444 | 1 | 2000 | 375.5444 | 18.7772 | 71.491 | 15.085 | 55.4518 | 66.1378 | 28.509 | 22.113
150 | 13 | May | 8.7 | 10.711 | 1490.05 | 907.614 | 2397.664 | 1 | 2000 | 397.664 | 19.8832 | 62.1459 | 25.4975 | 43.8142 | 54.6193 | 37.8541 | 26.688
150 | 14 | May | 11.3 | 13.9119 | 1700 | 614.8496 | 2314.8496 | 1 | 2000 | 314.8496 | 15.7425 | 73.4389 | 15 | 51.2076 | 69.2575 | 26.5611 | 18.5206
150 | 15 | May | 11.3 | 13.9119 | 1700 | 527.5984 | 2227.5984 | 1 | 2000 | 227.5984 | 11.3799 | 76.3154 | 15 | 43.1386 | 73.6201 | 23.6846 | 13.3881
150 | 16 | May | 10.3 | 12.6808 | 1694.9 | 536.0985 | 2230.9985 | 1 | 2000 | 230.9985 | 11.5499 | 75.9705 | 15.255 | 43.0888 | 73.1951 | 24.0295 | 13.629
150 | 17 | May | 10.3 | 12.6808 | 1694.9 | 289.0183 | 1983.9183 | 0 | 1983.9183 | 0 | 0 | 85.4319 | 14.5681 | 0 | 85.4319 | 14.5681 | 0
150 | 18 | May | 8.2 | 10.0954 | 1359.15 | 200.0035 | 1559.1535 | 0 | 1559.1535 | 0 | 0 | 87.1723 | 12.8277 | 0 | 87.1723 | 12.8277 | 0
150 | 19 | May | 7.2 | 8.8642 | 908.65 | 92.61 | 1001.26 | 0 | 1001.26 | 0 | 0 | 90.7507 | 9.2493 | 0 | 90.7507 | 9.2493 | 0
150 | 20 | May | 7.7 | 9.4798 | 1059.95 | 14.553 | 1074.503 | 0 | 1074.503 | 0 | 0 | 98.6456 | 1.3544 | 0 | 98.6456 | 1.3544 | 0
150 | 21 | May | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
150 | 22 | May | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
150 | 23 | May | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
150 | 24 | May | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
151 | 1 | May | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
151 | 2 | May | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
151 | 3 | May | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
151 | 4 | May | 5.1 | 6.2788 | 312.8 | 1.323 | 314.123 | 0 | 314.123 | 0 | 0 | 99.5788 | 0.42117 | 0 | 99.5788 | 0.42117 | 0
151 | 5 | May | 6.7 | 8.2487 | 761.6 | 38.367 | 799.967 | 0 | 799.967 | 0 | 0 | 95.2039 | 4.7961 | 0 | 95.2039 | 4.7961 | 0
151 | 6 | May | 5.7 | 7.0175 | 504.9 | 164.6953 | 669.5953 | 0 | 669.5953 | 0 | 0 | 75.4038 | 24.5962 | 0 | 75.4038 | 24.5962 | 0
151 | 7 | May | 9.3 | 11.4496 | 1598.85 | 402.8667 | 2001.7167 | 1 | 2000 | 1.7167 | 0.085837 | 79.8739 | 20.0575 | 0.42613 | 79.8567 | 20.1261 | 0.10737
151 | 8 | May | 7.7 | 9.4798 | 1059.95 | 700.5045 | 1760.4545 | 0 | 1760.4545 | 0 | 0 | 60.2089 | 39.7911 | 0 | 60.2089 | 39.7911 | 0
151 | 9 | May | 8.2 | 10.0954 | 1359.15 | 930.285 | 2289.435 | 1 | 2000 | 289.435 | 14.4718 | 59.3662 | 32.0425 | 31.1125 | 53.4857 | 40.6338 | 21.2953
151 | 10 | May | 10.3 | 12.6808 | 1694.9 | 1206.4256 | 2901.3256 | 1 | 2000 | 901.3256 | 45.0663 | 58.4181 | 15.255 | 74.7104 | 39.6787 | 41.5819 | 53.1787
151 | 11 | May | 7.7 | 9.4798 | 1059.95 | 1234.0091 | 2293.9591 | 1 | 2000 | 293.9591 | 14.698 | 46.2061 | 47.0025 | 23.8215 | 38.2995 | 53.7939 | 27.7333
151 | 12 | May | 10.3 | 12.6808 | 1694.9 | 1398.3491 | 3093.2491 | 1 | 2000 | 1093.2491 | 54.6625 | 54.7935 | 15.255 | 78.1814 | 30.0825 | 45.2065 | 64.5023
151 | 13 | May | 9.3 | 11.4496 | 1598.85 | 1379.3969 | 2978.2469 | 1 | 2000 | 978.2469 | 48.9123 | 53.6843 | 20.0575 | 70.9185 | 31.0302 | 46.3157 | 61.1844
151 | 14 | May | 10.3 | 12.6808 | 1694.9 | 1017.7309 | 2712.6309 | 1 | 2000 | 712.6309 | 35.6315 | 62.4818 | 15.255 | 70.0215 | 49.1135 | 37.5182 | 42.0456
151 | 15 | May | 10.8 | 13.2964 | 1698.3 | 941.6721 | 2639.9721 | 1 | 2000 | 639.9721 | 31.9986 | 64.3302 | 15.085 | 67.9612 | 52.9164 | 35.6698 | 37.6831
151 | 16 | May | 8.2 | 10.0954 | 1359.15 | 542.6008 | 1901.7508 | 0 | 1901.7508 | 0 | 0 | 71.4684 | 28.5316 | 0 | 71.4684 | 28.5316 | 0
151 | 17 | May | 8.2 | 10.0954 | 1359.15 | 292.269 | 1651.419 | 0 | 1651.419 | 0 | 0 | 82.3019 | 17.6981 | 0 | 82.3019 | 17.6981 | 0
151 | 18 | May | 7.2 | 8.8642 | 908.65 | 201.8624 | 1110.5124 | 0 | 1110.5124 | 0 | 0 | 81.8226 | 18.1774 | 0 | 81.8226 | 18.1774 | 0
151 | 19 | May | 8.2 | 10.0954 | 1359.15 | 88.641 | 1447.791 | 0 | 1447.791 | 0 | 0 | 93.8775 | 6.1225 | 0 | 93.8775 | 6.1225 | 0
151 | 20 | May | 6.4 | 7.8793 | 625.6 | 18.522 | 644.122 | 0 | 644.122 | 0 | 0 | 97.1245 | 2.8755 | 0 | 97.1245 | 2.8755 | 0
151 | 21 | May | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
151 | 22 | May | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
151 | 23 | May | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
151 | 24 | May | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
152 | 1 | June | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
152 | 2 | June | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
152 | 3 | June | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
152 | 4 | June | 6.7 | 8.2487 | 761.6 | 1.323 | 762.923 | 0 | 762.923 | 0 | 0 | 99.8266 | 0.17341 | 0 | 99.8266 | 0.17341 | 0
152 | 5 | June | 8.2 | 10.0954 | 1359.15 | 44.982 | 1404.132 | 0 | 1404.132 | 0 | 0 | 96.7965 | 3.2035 | 0 | 96.7965 | 3.2035 | 0
152 | 6 | June | 8.7 | 10.711 | 1490.05 | 187.332 | 1677.382 | 0 | 1677.382 | 0 | 0 | 88.8319 | 11.1681 | 0 | 88.8319 | 11.1681 | 0
152 | 7 | June | 9.8 | 12.0652 | 1683.85 | 451.2638 | 2135.1138 | 1 | 2000 | 135.1138 | 6.7557 | 78.8646 | 15.8075 | 29.9412 | 77.4368 | 21.1354 | 8.0241
152 | 8 | June | 8.7 | 10.711 | 1490.05 | 773.8454 | 2263.8954 | 1 | 2000 | 263.8954 | 13.1948 | 65.818 | 25.4975 | 34.1018 | 61.3077 | 34.182 | 17.7105
152 | 9 | June | 8.2 | 10.0954 | 1359.15 | 1084.8625 | 2444.0125 | 1 | 2000 | 444.0125 | 22.2006 | 55.6114 | 32.0425 | 40.928 | 45.7569 | 44.3886 | 32.6684
152 | 10 | June | 8.7 | 10.711 | 1490.05 | 1322.3447 | 2812.3947 | 1 | 2000 | 812.3947 | 40.6197 | 52.9815 | 25.4975 | 61.4359 | 33.8828 | 47.0185 | 54.5213
152 | 11 | June | 8.7 | 10.711 | 1490.05 | 1480.2277 | 2970.2777 | 1 | 2000 | 970.2777 | 48.5139 | 50.1653 | 25.4975 | 65.5492 | 25.9886 | 49.8347 | 65.1171
152 | 12 | June | 9.8 | 12.0652 | 1683.85 | 1531.2926 | 3215.1426 | 1 | 2000 | 1215.1426 | 60.7571 | 52.3725 | 15.8075 | 79.354 | 23.4354 | 47.6275 | 72.1645
152 | 13 | June | 9.3 | 11.4496 | 1598.85 | 1474.2806 | 3073.1306 | 1 | 2000 | 1073.1306 | 53.6565 | 52.0268 | 20.0575 | 72.7901 | 26.286 | 47.9732 | 67.1189
152 | 14 | June | 9.8 | 12.0652 | 1683.85 | 1319.2492 | 3003.0992 | 1 | 2000 | 1003.0992 | 50.155 | 56.0704 | 15.8075 | 76.0356 | 34.0375 | 43.9296 | 59.5718
152 | 15 | June | 10.3 | 12.6808 | 1694.9 | 1081.922 | 2776.822 | 1 | 2000 | 776.822 | 38.8411 | 61.0374 | 15.255 | 71.8002 | 45.9039 | 38.9626 | 45.8329
152 | 16 | June | 10.3 | 12.6808 | 1694.9 | 786.3583 | 2481.2583 | 1 | 2000 | 481.2583 | 24.0629 | 68.3081 | 15.255 | 61.2009 | 60.6821 | 31.6919 | 28.3945
152 | 17 | June | 9.3 | 11.4496 | 1598.85 | 477.6075 | 2076.4575 | 1 | 2000 | 76.4575 | 3.8229 | 76.9989 | 20.0575 | 16.0084 | 76.1196 | 23.0011 | 4.782
152 | 18 | June | 10.3 | 12.6808 | 1694.9 | 218.7707 | 1913.6707 | 0 | 1913.6707 | 0 | 0 | 88.568 | 11.432 | 0 | 88.568 | 11.432 | 0
152 | 19 | June | 10.3 | 12.6808 | 1694.9 | 103.194 | 1798.094 | 0 | 1798.094 | 0 | 0 | 94.2609 | 5.7391 | 0 | 94.2609 | 5.7391 | 0
152 | 20 | June | 10.8 | 13.2964 | 1698.3 | 23.814 | 1722.114 | 0 | 1722.114 | 0 | 0 | 98.6172 | 1.3828 | 0 | 98.6172 | 1.3828 | 0
152 | 21 | June | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
152 | 22 | June | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
152 | 23 | June | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
152 | 24 | June | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
153 | 1 | June | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
153 | 2 | June | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
153 | 3 | June | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
153 | 4 | June | 9.8 | 12.0652 | 1683.85 | 2.646 | 1686.496 | 0 | 1686.496 | 0 | 0 | 99.8431 | 0.15689 | 0 | 99.8431 | 0.15689 | 0
153 | 5 | June | 8.7 | 10.711 | 1490.05 | 44.982 | 1535.032 | 0 | 1535.032 | 0 | 0 | 97.0696 | 2.9304 | 0 | 97.0696 | 2.9304 | 0
153 | 6 | June | 9.3 | 11.4496 | 1598.85 | 188.1811 | 1787.0311 | 0 | 1787.0311 | 0 | 0 | 89.4696 | 10.5304 | 0 | 89.4696 | 10.5304 | 0
153 | 7 | June | 8.7 | 10.711 | 1490.05 | 450.7544 | 1940.8044 | 0 | 1940.8044 | 0 | 0 | 76.7749 | 23.2251 | 0 | 76.7749 | 23.2251 | 0
153 | 8 | June | 9.3 | 11.4496 | 1598.85 | 769.7631 | 2368.6131 | 1 | 2000 | 368.6131 | 18.4307 | 67.5015 | 20.0575 | 47.8866 | 61.5118 | 32.4985 | 23.0549
153 | 9 | June | 8.7 | 10.711 | 1490.05 | 1078.9647 | 2569.0147 | 1 | 2000 | 569.0147 | 28.4507 | 58.0008 | 25.4975 | 52.7371 | 46.0518 | 41.9992 | 38.1876
153 | 10 | June | 9.3 | 11.4496 | 1598.85 | 1316.0172 | 2914.8672 | 1 | 2000 | 914.8672 | 45.7434 | 54.8516 | 20.0575 | 69.5179 | 34.1991 | 45.1484 | 57.2203
153 | 11 | June | 9.8 | 12.0652 | 1683.85 | 1478.343 | 3162.193 | 1 | 2000 | 1162.193 | 58.1096 | 53.2494 | 15.8075 | 78.6146 | 26.0829 | 46.7506 | 69.02
153 | 12 | June | 9.8 | 12.0652 | 1683.85 | 1527.924 | 3211.774 | 1 | 2000 | 1211.774 | 60.5887 | 52.4274 | 15.8075 | 79.3085 | 23.6038 | 47.5726 | 71.9645
153 | 13 | June | 7.7 | 9.4798 | 1059.95 | 1474.3883 | 2534.3383 | 1 | 2000 | 534.3383 | 26.7169 | 41.8235 | 47.0025 | 36.2414 | 26.2806 | 58.1765 | 50.4116
153 | 14 | June | 7.7 | 9.4798 | 1059.95 | 1322.6644 | 2382.6144 | 1 | 2000 | 382.6144 | 19.1307 | 44.4868 | 47.0025 | 28.9276 | 33.8668 | 55.5132 | 36.0974
153 | 15 | June | 7.2 | 8.8642 | 908.65 | 1064.7443 | 1973.3943 | 0 | 1973.3943 | 0 | 0 | 46.045 | 53.955 | 0 | 46.045 | 53.955 | 0
153 | 16 | June | 8.7 | 10.711 | 1490.05 | 756.0829 | 2246.1329 | 1 | 2000 | 246.1329 | 12.3066 | 66.3385 | 25.4975 | 32.5537 | 62.1959 | 33.6615 | 16.5184
153 | 17 | June | 9.3 | 11.4496 | 1598.85 | 475.3502 | 2074.2002 | 1 | 2000 | 74.2002 | 3.71 | 77.0827 | 20.0575 | 15.6096 | 76.2325 | 22.9173 | 4.6408
153 | 18 | June | 8.7 | 10.711 | 1490.05 | 221.0213 | 1711.0713 | 0 | 1711.0713 | 0 | 0 | 87.0829 | 12.9171 | 0 | 87.0829 | 12.9171 | 0
153 | 19 | June | 7.2 | 8.8642 | 908.65 | 104.517 | 1013.167 | 0 | 1013.167 | 0 | 0 | 89.6841 | 10.3159 | 0 | 89.6841 | 10.3159 | 0
153 | 20 | June | 7.2 | 8.8642 | 908.65 | 23.814 | 932.464 | 0 | 932.464 | 0 | 0 | 97.4461 | 2.5539 | 0 | 97.4461 | 2.5539 | 0
153 | 21 | June | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
153 | 22 | June | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
153 | 23 | June | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
153 | 24 | June | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
154 | 1 | June | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
154 | 2 | June | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
154 | 3 | June | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
154 | 4 | June | 6.2 | 7.6331 | 625.6 | 2.646 | 628.246 | 0 | 628.246 | 0 | 0 | 99.5788 | 0.42117 | 0 | 99.5788 | 0.42117 | 0
154 | 5 | June | 5.7 | 7.0175 | 504.9 | 39.69 | 544.59 | 0 | 544.59 | 0 | 0 | 92.7119 | 7.2881 | 0 | 92.7119 | 7.2881 | 0
154 | 6 | June | 6.7 | 8.2487 | 761.6 | 111.4155 | 873.0155 | 0 | 873.0155 | 0 | 0 | 87.2379 | 12.7621 | 0 | 87.2379 | 12.7621 | 0
154 | 7 | June | 5.7 | 7.0175 | 504.9 | 141.561 | 646.461 | 0 | 646.461 | 0 | 0 | 78.1022 | 21.8978 | 0 | 78.1022 | 21.8978 | 0
154 | 8 | June | 5.1 | 6.2788 | 312.8 | 216.603 | 529.403 | 0 | 529.403 | 0 | 0 | 59.0854 | 40.9146 | 0 | 59.0854 | 40.9146 | 0
154 | 9 | June | 5.7 | 7.0175 | 504.9 | 290.094 | 794.994 | 0 | 794.994 | 0 | 0 | 63.5099 | 36.4901 | 0 | 63.5099 | 36.4901 | 0
154 | 10 | June | 5.1 | 6.2788 | 312.8 | 349.4606 | 662.2606 | 0 | 662.2606 | 0 | 0 | 47.2322 | 52.7678 | 0 | 47.2322 | 52.7678 | 0
154 | 11 | June | 5.1 | 6.2788 | 312.8 | 384.8241 | 697.6241 | 0 | 697.6241 | 0 | 0 | 44.8379 | 55.1621 | 0 | 44.8379 | 55.1621 | 0
154 | 12 | June | 5.7 | 7.0175 | 504.9 | 403.5098 | 908.4098 | 0 | 908.4098 | 0 | 0 | 55.5806 | 44.4194 | 0 | 55.5806 | 44.4194 | 0
154 | 13 | June | 4.6 | 5.6633 | 237.15 | 400.5659 | 637.7159 | 0 | 637.7159 | 0 | 0 | 37.1874 | 62.8126 | 0 | 37.1874 | 62.8126 | 0
154 | 14 | June | 5.7 | 7.0175 | 504.9 | 374.6896 | 879.5896 | 0 | 879.5896 | 0 | 0 | 57.4018 | 42.5982 | 0 | 57.4018 | 42.5982 | 0
154 | 15 | June | 5.7 | 7.0175 | 504.9 | 329.8637 | 834.7637 | 0 | 834.7637 | 0 | 0 | 60.4842 | 39.5158 | 0 | 60.4842 | 39.5158 | 0
154 | 16 | June | 6.7 | 8.2487 | 761.6 | 267.5447 | 1029.1447 | 0 | 1029.1447 | 0 | 0 | 74.0032 | 25.9968 | 0 | 74.0032 | 25.9968 | 0
154 | 17 | June | 5.7 | 7.0175 | 504.9 | 194.481 | 699.381 | 0 | 699.381 | 0 | 0 | 72.1924 | 27.8076 | 0 | 72.1924 | 27.8076 | 0
154 | 18 | June | 5.7 | 7.0175 | 504.9 | 119.07 | 623.97 | 0 | 623.97 | 0 | 0 | 80.9174 | 19.0826 | 0 | 80.9174 | 19.0826 | 0
154 | 19 | June | 5.1 | 6.2788 | 312.8 | 80.703 | 393.503 | 0 | 393.503 | 0 | 0 | 79.4911 | 20.5089 | 0 | 79.4911 | 20.5089 | 0
154 | 20 | June | 4.6 | 5.6633 | 237.15 | 14.553 | 251.703 | 0 | 251.703 | 0 | 0 | 94.2182 | 5.7818 | 0 | 94.2182 | 5.7818 | 0
154 | 21 | June | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
154 | 22 | June | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
154 | 23 | June | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
154 | 24 | June | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155 | 1 | June | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155 | 2 | June | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155 | 3 | June | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155 | 4 | June | 3.6 | 4.4321 | 75.65 | 1.323 | 76.973 | 0 | 76.973 | 0 | 0 | 98.2812 | 1.7188 | 0 | 98.2812 | 1.7188 | 0
155 | 5 | June | 2.6 | 3.201 | 0 | 27.783 | 27.783 | 0 | 27.783 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
155 | 6 | June | 3.1 | 3.8165 | 0 | 111.4158 | 111.4158 | 0 | 111.4158 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
155 | 7 | June | 3.1 | 3.8165 | 0 | 226.6328 | 226.6328 | 0 | 226.6328 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
155 | 8 | June | 3.6 | 4.4321 | 75.65 | 358.9653 | 434.6153 | 0 | 434.6153 | 0 | 0 | 17.4062 | 82.5938 | 0 | 17.4062 | 82.5938 | 0
155 | 9 | June | 3.1 | 3.8165 | 0 | 490.3404 | 490.3404 | 0 | 490.3404 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
155 | 10 | June | 3.1 | 3.8165 | 0 | 802.0464 | 802.0464 | 0 | 802.0464 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
155 | 11 | June | 2.6 | 3.201 | 0 | 867.8711 | 867.8711 | 0 | 867.8711 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
155 | 12 | June | 3.6 | 4.4321 | 75.65 | 904.2335 | 979.8835 | 0 | 979.8835 | 0 | 0 | 7.7203 | 92.2797 | 0 | 7.7203 | 92.2797 | 0
155 | 13 | June | 3.6 | 4.4321 | 75.65 | 1246.1639 | 1321.8139 | 0 | 1321.8139 | 0 | 0 | 5.7232 | 94.2768 | 0 | 5.7232 | 94.2768 | 0
155 | 14 | June | 4.1 | 5.0477 | 173.4 | 1246.9869 | 1420.3869 | 0 | 1420.3869 | 0 | 0 | 12.2079 | 87.7921 | 0 | 12.2079 | 87.7921 | 0
155 | 15 | June | 3.6 | 4.4321 | 75.65 | 1082.0456 | 1157.6956 | 0 | 1157.6956 | 0 | 0 | 6.5345 | 93.4655 | 0 | 6.5345 | 93.4655 | 0
155 | 16 | June | 3.6 | 4.4321 | 75.65 | 782.5339 | 858.1839 | 0 | 858.1839 | 0 | 0 | 8.8151 | 91.1849 | 0 | 8.8151 | 91.1849 | 0
155 | 17 | June | 4.1 | 5.0477 | 173.4 | 483.2878 | 656.6878 | 0 | 656.6878 | 0 | 0 | 26.4052 | 73.5948 | 0 | 26.4052 | 73.5948 | 0
155 | 18 | June | 4.1 | 5.0477 | 173.4 | 224.8478 | 398.2478 | 0 | 398.2478 | 0 | 0 | 43.5407 | 56.4593 | 0 | 43.5407 | 56.4593 | 0
155 | 19 | June | 4.1 | 5.0477 | 173.4 | 107.163 | 280.563 | 0 | 280.563 | 0 | 0 | 61.8043 | 38.1957 | 0 | 61.8043 | 38.1957 | 0
155 | 20 | June | 3.6 | 4.4321 | 75.65 | 18.522 | 94.172 | 0 | 94.172 | 0 | 0 | 80.3317 | 19.6683 | 0 | 80.3317 | 19.6683 | 0
155 | 21 | June | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
155 | 22 | June | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
155 | 23 | June | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
155 | 24 | June | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
156 | 1 | June | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
156 | 2 | June | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
156 | 3 | June | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
156 | 4 | June | 3.6 | 4.4321 | 75.65 | 2.646 | 78.296 | 0 | 78.296 | 0 | 0 | 96.6205 | 3.3795 | 0 | 96.6205 | 3.3795 | 0
156 | 5 | June | 4.1 | 5.0477 | 173.4 | 27.783 | 201.183 | 0 | 201.183 | 0 | 0 | 86.1902 | 13.8098 | 0 | 86.1902 | 13.8098 | 0
156 | 6 | June | 5.7 | 7.0175 | 504.9 | 111.416 | 616.316 | 0 | 616.316 | 0 | 0 | 81.9223 | 18.0777 | 0 | 81.9223 | 18.0777 | 0
156 | 7 | June | 5.7 | 7.0175 | 504.9 | 228.237 | 733.137 | 0 | 733.137 | 0 | 0 | 68.8684 | 31.1316 | 0 | 68.8684 | 31.1316 | 0
156 | 8 | June | 6.2 | 7.6331 | 625.6 | 355.0778 | 980.6778 | 0 | 980.6778 | 0 | 0 | 63.7926 | 36.2074 | 0 | 63.7926 | 36.2074 | 0
156 | 9 | June | 6.7 | 8.2487 | 761.6 | 658.9575 | 1420.5575 | 0 | 1420.5575 | 0 | 0 | 53.6128 | 46.3872 | 0 | 53.6128 | 46.3872 | 0
156 | 10 | June | 5.7 | 7.0175 | 504.9 | 1177.0997 | 1681.9997 | 0 | 1681.9997 | 0 | 0 | 30.0178 | 69.9822 | 0 | 30.0178 | 69.9822 | 0
156 | 11 | June | 5.7 | 7.0175 | 504.9 | 1445.4252 | 1950.3252 | 0 | 1950.3252 | 0 | 0 | 25.888 | 74.112 | 0 | 25.888 | 74.112 | 0
156 | 12 | June | 6.7 | 8.2487 | 761.6 | 1298.3991 | 2059.9991 | 1 | 2000 | 59.9991 | 3 | 36.9709 | 61.92 | 4.621 | 35.08 | 63.0291 | 7.878
156 | 13 | June | 6.7 | 8.2487 | 761.6 | 686.3778 | 1447.9778 | 0 | 1447.9778 | 0 | 0 | 52.5975 | 47.4025 | 0 | 52.5975 | 47.4025 | 0
156 | 14 | June | 7.7 | 9.4798 | 1059.95 | 850.9872 | 1910.9372 | 0 | 1910.9372 | 0 | 0 | 55.4675 | 44.5325 | 0 | 55.4675 | 44.5325 | 0
156 | 15 | June | 7.7 | 9.4798 | 1059.95 | 538.6103 | 1598.5603 | 0 | 1598.5603 | 0 | 0 | 66.3065 | 33.6935 | 0 | 66.3065 | 33.6935 | 0
156 | 16 | June | 6.7 | 8.2487 | 761.6 | 430.2811 | 1191.8811 | 0 | 1191.8811 | 0 | 0 | 63.899 | 36.101 | 0 | 63.899 | 36.101 | 0
156 | 17 | June | 7.2 | 8.8642 | 908.65 | 307.4276 | 1216.0776 | 0 | 1216.0776 | 0 | 0 | 74.7197 | 25.2803 | 0 | 74.7197 | 25.2803 | 0
156 | 18 | June | 7.2 | 8.8642 | 908.65 | 120.393 | 1029.043 | 0 | 1029.043 | 0 | 0 | 88.3005 | 11.6995 | 0 | 88.3005 | 11.6995 | 0
156 | 19 | June | 7.2 | 8.8642 | 908.65 | 83.349 | 991.999 | 0 | 991.999 | 0 | 0 | 91.5979 | 8.4021 | 0 | 91.5979 | 8.4021 | 0
156 | 20 | June | 6.7 | 8.2487 | 761.6 | 14.553 | 776.153 | 0 | 776.153 | 0 | 0 | 98.125 | 1.875 | 0 | 98.125 | 1.875 | 0
156 | 21 | June | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
156 | 22 | June | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
156 | 23 | June | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
156 | 24 | June | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
157 | 1 | June | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
157 | 2 | June | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
157 | 3 | June | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157 | 4 | June | 2.1 | 2.5854 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
157 | 5 | June | 2.6 | 3.201 | 0 | 27.783 | 27.783 | 0 | 27.783 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
157 | 6 | June | 5.7 | 7.0175 | 504.9 | 111.416 | 616.316 | 0 | 616.316 | 0 | 0 | 81.9223 | 18.0777 | 0 | 81.9223 | 18.0777 | 0
157 | 7 | June | 5.1 | 6.2788 | 312.8 | 227.6009 | 540.4009 | 0 | 540.4009 | 0 | 0 | 57.883 | 42.117 | 0 | 57.883 | 42.117 | 0
157 | 8 | June | 3.6 | 4.4321 | 75.65 | 578.6429 | 654.2929 | 0 | 654.2929 | 0 | 0 | 11.5621 | 88.4379 | 0 | 11.5621 | 88.4379 | 0
157 | 9 | June | 4.1 | 5.0477 | 173.4 | 1028.5958 | 1201.9958 | 0 | 1201.9958 | 0 | 0 | 14.426 | 85.574 | 0 | 14.426 | 85.574 | 0
157 | 10 | June | 6.2 | 7.6331 | 625.6 | 971.6375 | 1597.2375 | 0 | 1597.2375 | 0 | 0 | 39.1676 | 60.8324 | 0 | 39.1676 | 60.8324 | 0
157 | 11 | June | 6.2 | 7.6331 | 625.6 | 663.5958 | 1289.1958 | 0 | 1289.1958 | 0 | 0 | 48.5264 | 51.4736 | 0 | 48.5264 | 51.4736 | 0
157 | 12 | June | 7.2 | 8.8642 | 908.65 | 677.033 | 1585.683 | 0 | 1585.683 | 0 | 0 | 57.3034 | 42.6966 | 0 | 57.3034 | 42.6966 | 0
157 | 13 | June | 8.2 | 10.0954 | 1359.15 | 1278.9503 | 2638.1003 | 1 | 2000 | 638.1003 | 31.905 | 51.52 | 32.0425 | 49.8925 | 36.0525 | 48.48 | 46.9485
157 | 14 | June | 6.7 | 8.2487 | 761.6 | 863.6561 | 1625.2561 | 0 | 1625.2561 | 0 | 0 | 46.8603 | 53.1397 | 0 | 46.8603 | 53.1397 | 0
157 | 15 | June | 6.7 | 8.2487 | 761.6 | 537.5406 | 1299.1406 | 0 | 1299.1406 | 0 | 0 | 58.6234 | 41.3766 | 0 | 58.6234 | 41.3766 | 0
157 | 16 | June | 7.7 | 9.4798 | 1059.95 | 554.4023 | 1614.3523 | 0 | 1614.3523 | 0 | 0 | 65.6579 | 34.3421 | 0 | 65.6579 | 34.3421 | 0
157 | 17 | June | 8.7 | 10.711 | 1490.05 | 307.0388 | 1797.0888 | 0 | 1797.0888 | 0 | 0 | 82.9147 | 17.0853 | 0 | 82.9147 | 17.0853 | 0
157 | 18 | June | 7.2 | 8.8642 | 908.65 | 187.0676 | 1095.7176 | 0 | 1095.7176 | 0 | 0 | 82.9274 | 17.0726 | 0 | 82.9274 | 17.0726 | 0
157 | 19 | June | 5.1 | 6.2788 | 312.8 | 84.672 | 397.472 | 0 | 397.472 | 0 | 0 | 78.6974 | 21.3026 | 0 | 78.6974 | 21.3026 | 0
157 | 20 | June | 3.1 | 3.8165 | 0 | 9.261 | 9.261 | 0 | 9.261 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
157 | 21 | June | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157 | 22 | June | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
157 | 23 | June | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
157 | 24 | June | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
158 | 1 | June | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
158 | 2 | June | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
158 | 3 | June | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
158 | 4 | June | 4.6 | 5.6633 | 237.15 | 1.323 | 238.473 | 0 | 238.473 | 0 | 0 | 99.4452 | 0.55478 | 0 | 99.4452 | 0.55478 | 0
158 | 5 | June | 5.7 | 7.0175 | 504.9 | 18.522 | 523.422 | 0 | 523.422 | 0 | 0 | 96.4614 | 3.5386 | 0 | 96.4614 | 3.5386 | 0
158 | 6 | June | 0 | 0 | 0 | 70.119 | 70.119 | 0 | 70.119 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
158 | 7 | June | 4.1 | 5.0477 | 173.4 | 141.561 | 314.961 | 0 | 314.961 | 0 | 0 | 55.0544 | 44.9456 | 0 | 55.0544 | 44.9456 | 0
158 | 8 | June | 2.6 | 3.201 | 0 | 354.7347 | 354.7347 | 0 | 354.7347 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
158 | 9 | June | 3.4 | 4.1859 | 75.65 | 725.9657 | 801.6157 | 0 | 801.6157 | 0 | 0 | 9.4372 | 90.5628 | 0 | 9.4372 | 90.5628 | 0
158 | 10 | June | 4.1 | 5.0477 | 173.4 | 1111.4347 | 1284.8347 | 0 | 1284.8347 | 0 | 0 | 13.4959 | 86.5041 | 0 | 13.4959 | 86.5041 | 0
158 | 11 | June | 4.1 | 5.0477 | 173.4 | 1099.9857 | 1273.3857 | 0 | 1273.3857 | 0 | 0 | 13.6172 | 86.3828 | 0 | 13.6172 | 86.3828 | 0
158 | 12 | June | 4.1 | 5.0477 | 173.4 | 684.6939 | 858.0939 | 0 | 858.0939 | 0 | 0 | 20.2076 | 79.7924 | 0 | 20.2076 | 79.7924 | 0
158 | 13 | June | 3.6 | 4.4321 | 75.65 | 666.3457 | 741.9957 | 0 | 741.9957 | 0 | 0 | 10.1955 | 89.8045 | 0 | 10.1955 | 89.8045 | 0
158 | 14 | June | 3.1 | 3.8165 | 0 | 844.3046 | 844.3046 | 0 | 844.3046 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
158 | 15 | June | 4.6 | 5.6633 | 237.15 | 1038.9854 | 1276.1354 | 0 | 1276.1354 | 0 | 0 | 18.5835 | 81.4165 | 0 | 18.5835 | 81.4165 | 0
158 | 16 | June | 4.1 | 5.0477 | 173.4 | 791.4338 | 964.8338 | 0 | 964.8338 | 0 | 0 | 17.972 | 82.028 | 0 | 17.972 | 82.028 | 0
158 | 17 | June | 6.2 | 7.6331 | 625.6 | 481.7126 | 1107.3126 | 0 | 1107.3126 | 0 | 0 | 56.4971 | 43.5029 | 0 | 56.4971 | 43.5029 | 0
158 | 18 | June | 5.7 | 7.0175 | 504.9 | 222.6802 | 727.5802 | 0 | 727.5802 | 0 | 0 | 69.3944 | 30.6056 | 0 | 69.3944 | 30.6056 | 0
158 | 19 | June | 5.7 | 7.0175 | 504.9 | 101.871 | 606.771 | 0 | 606.771 | 0 | 0 | 83.211 | 16.789 | 0 | 83.211 | 16.789 | 0
158 | 20 | June | 3.6 | 4.4321 | 75.65 | 27.783 | 103.433 | 0 | 103.433 | 0 | 0 | 73.1391 | 26.8609 | 0 | 73.1391 | 26.8609 | 0
158 | 21 | June | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
158 | 22 | June | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
158 | 23 | June | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
158 | 24 | June | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
159 | 1 | June | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
159 | 2 | June | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
159 | 3 | June | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
159 | 4 | June | 3.1 | 3.8165 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
159 | 5 | June | 6.2 | 7.6331 | 625.6 | 29.106 | 654.706 | 0 | 654.706 | 0 | 0 | 95.5543 | 4.4457 | 0 | 95.5543 | 4.4457 | 0
159 | 6 | June | 5.7 | 7.0175 | 504.9 | 112.7389 | 617.6389 | 0 | 617.6389 | 0 | 0 | 81.7468 | 18.2532 | 0 | 81.7468 | 18.2532 | 0
159 | 7 | June | 4.6 | 5.6633 | 237.15 | 229.543 | 466.693 | 0 | 466.693 | 0 | 0 | 50.815 | 49.185 | 0 | 50.815 | 49.185 | 0
159 | 8 | June | 5.7 | 7.0175 | 504.9 | 488.3643 | 993.2643 | 0 | 993.2643 | 0 | 0 | 50.8324 | 49.1676 | 0 | 50.8324 | 49.1676 | 0
159 | 9 | June | 7.2 | 8.8642 | 908.65 | 483.5409 | 1392.1909 | 0 | 1392.1909 | 0 | 0 | 65.2676 | 34.7324 | 0 | 65.2676 | 34.7324 | 0
159 | 10 | June | 6.7 | 8.2487 | 761.6 | 1153.6609 | 1915.2609 | 0 | 1915.2609 | 0 | 0 | 39.7648 | 60.2352 | 0 | 39.7648 | 60.2352 | 0
159 | 11 | June | 7.2 | 8.8642 | 908.65 | 1385.132 | 2293.782 | 1 | 2000 | 293.782 | 14.6891 | 39.6136 | 54.5675 | 21.2097 | 30.7434 | 60.3864 | 32.3317
159 | 12 | June | 5.7 | 7.0175 | 504.9 | 1437.7636 | 1942.6636 | 0 | 1942.6636 | 0 | 0 | 25.9901 | 74.0099 | 0 | 25.9901 | 74.0099 | 0
159 | 13 | June | 5.1 | 6.2788 | 312.8 | 1120.4166 | 1433.2166 | 0 | 1433.2166 | 0 | 0 | 21.825 | 78.175 | 0 | 21.825 | 78.175 | 0
159 | 14 | June | 7.2 | 8.8642 | 908.65 | 1023.0402 | 1931.6902 | 0 | 1931.6902 | 0 | 0 | 47.0391 | 52.9609 | 0 | 47.0391 | 52.9609 | 0
159 | 15 | June | 6.2 | 7.6331 | 625.6 | 711.9792 | 1337.5792 | 0 | 1337.5792 | 0 | 0 | 46.7711 | 53.2289 | 0 | 46.7711 | 53.2289 | 0
159 | 16 | June | 4.6 | 5.6633 | 237.15 | 431.0093 | 668.1593 | 0 | 668.1593 | 0 | 0 | 35.493 | 64.507 | 0 | 35.493 | 64.507 | 0
159 | 17 | June | 4.1 | 5.0477 | 173.4 | 309.7141 | 483.1141 | 0 | 483.1141 | 0 | 0 | 35.8921 | 64.1079 | 0 | 35.8921 | 64.1079 | 0
159 | 18 | June | 3.1 | 3.8165 | 0 | 229.6129 | 229.6129 | 0 | 229.6129 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
159 | 19 | June | 2.6 | 3.201 | 0 | 125.685 | 125.685 | 0 | 125.685 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
159 | 20 | June | 2.1 | 2.5854 | 0 | 29.106 | 29.106 | 0 | 29.106 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
159 | 21 | June | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
159 | 22 | June | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
159 | 23 | June | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
159 | 24 | June | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
160 | 1 | June | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
160 | 2 | June | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
160 | 3 | June | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
160 | 4 | June | 3.1 | 3.8165 | 0 | 2.646 | 2.646 | 0 | 2.646 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
160 | 5 | June | 3.1 | 3.8165 | 0 | 50.274 | 50.274 | 0 | 50.274 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
160 | 6 | June | 3.1 | 3.8165 | 0 | 192.8084 | 192.8084 | 0 | 192.8084 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
160 | 7 | June | 3.1 | 3.8165 | 0 | 451.7057 | 451.7057 | 0 | 451.7057 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
160 | 8 | June | 3.1 | 3.8165 | 0 | 766.9679 | 766.9679 | 0 | 766.9679 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
160 | 9 | June | 5.1 | 6.2788 | 312.8 | 1079.5292 | 1392.3292 | 0 | 1392.3292 | 0 | 0 | 22.466 | 77.534 | 0 | 22.466 | 77.534 | 0
160 | 10 | June | 4.6 | 5.6633 | 237.15 | 1315.6054 | 1552.7554 | 0 | 1552.7554 | 0 | 0 | 15.2728 | 84.7272 | 0 | 15.2728 | 84.7272 | 0
160 | 11 | June | 3.6 | 4.4321 | 75.65 | 1453.6079 | 1529.2579 | 0 | 1529.2579 | 0 | 0 | 4.9468 | 95.0532 | 0 | 4.9468 | 95.0532 | 0
160 | 12 | June | 3.6 | 4.4321 | 75.65 | 1428.0208 | 1503.6708 | 0 | 1503.6708 | 0 | 0 | 5.031 | 94.969 | 0 | 5.031 | 94.969 | 0
160 | 13 | June | 2.6 | 3.201 | 0 | 1263.8732 | 1263.8732 | 0 | 1263.8732 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
160 | 14 | June | 6.2 | 7.6331 | 625.6 | 1122.1661 | 1747.7661 | 0 | 1747.7661 | 0 | 0 | 35.7943 | 64.2057 | 0 | 35.7943 | 64.2057 | 0
160 | 15 | June | 6.2 | 7.6331 | 625.6 | 857.774 | 1483.374 | 0 | 1483.374 | 0 | 0 | 42.1741 | 57.8259 | 0 | 42.1741 | 57.8259 | 0
160 | 16 | June | 6.2 | 7.6331 | 625.6 | 656.8668 | 1282.4668 | 0 | 1282.4668 | 0 | 0 | 48.781 | 51.219 | 0 | 48.781 | 51.219 | 0
160 | 17 | June | 6.7 | 8.2487 | 761.6 | 386.7884 | 1148.3884 | 0 | 1148.3884 | 0 | 0 | 66.319 | 33.681 | 0 | 66.319 | 33.681 | 0
160 | 18 | June | 4.6 | 5.6633 | 237.15 | 188.9093 | 426.0593 | 0 | 426.0593 | 0 | 0 | 55.6613 | 44.3387 | 0 | 55.6613 | 44.3387 | 0
160 | 19 | June | 3.1 | 3.8165 | 0 | 105.84 | 105.84 | 0 | 105.84 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
160 | 20 | June | 4.1 | 5.0477 | 173.4 | 29.106 | 202.506 | 0 | 202.506 | 0 | 0 | 85.6271 | 14.3729 | 0 | 85.6271 | 14.3729 | 0
160 | 21 | June | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
160 | 22 | June | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
160 | 23 | June | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160 | 24 | June | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
161 | 1 | June | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
161 | 2 | June | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
161 | 3 | June | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
161 | 4 | June | 4.1 | 5.0477 | 173.4 | 2.646 | 176.046 | 0 | 176.046 | 0 | 0 | 98.497 | 1.503 | 0 | 98.497 | 1.503 | 0
161 | 5 | June | 4.6 | 5.6633 | 237.15 | 50.274 | 287.424 | 0 | 287.424 | 0 | 0 | 82.5088 | 17.4912 | 0 | 82.5088 | 17.4912 | 0
161 | 6 | June | 5.1 | 6.2788 | 312.8 | 188.4887 | 501.2887 | 0 | 501.2887 | 0 | 0 | 62.3992 | 37.6008 | 0 | 62.3992 | 37.6008 | 0
161 | 7 | June | 4.1 | 5.0477 | 173.4 | 449.7268 | 623.1268 | 0 | 623.1268 | 0 | 0 | 27.8274 | 72.1726 | 0 | 27.8274 | 72.1726 | 0
161 | 8 | June | 6.2 | 7.6331 | 625.6 | 358.262 | 983.862 | 0 | 983.862 | 0 | 0 | 63.5862 | 36.4138 | 0 | 63.5862 | 36.4138 | 0
161 | 9 | June | 6.2 | 7.6331 | 625.6 | 951.8539 | 1577.4539 | 0 | 1577.4539 | 0 | 0 | 39.6588 | 60.3412 | 0 | 39.6588 | 60.3412 | 0
161 | 10 | June | 5.1 | 6.2788 | 312.8 | 1234.8606 | 1547.6606 | 0 | 1547.6606 | 0 | 0 | 20.2111 | 79.7889 | 0 | 20.2111 | 79.7889 | 0
161 | 11 | June | 6.2 | 7.6331 | 625.6 | 1103.8331 | 1729.4331 | 0 | 1729.4331 | 0 | 0 | 36.1737 | 63.8263 | 0 | 36.1737 | 63.8263 | 0
161 | 12 | June | 6.7 | 8.2487 | 761.6 | 948.6449 | 1710.2449 | 0 | 1710.2449 | 0 | 0 | 44.5316 | 55.4684 | 0 | 44.5316 | 55.4684 | 0
161 | 13 | June | 7.2 | 8.8642 | 908.65 | 679.0033 | 1587.6533 | 0 | 1587.6533 | 0 | 0 | 57.2323 | 42.7677 | 0 | 57.2323 | 42.7677 | 0
161 | 14 | June | 7.2 | 8.8642 | 908.65 | 625.9895 | 1534.6395 | 0 | 1534.6395 | 0 | 0 | 59.2093 | 40.7907 | 0 | 59.2093 | 40.7907 | 0
161 | 15 | June | 7.7 | 9.4798 | 1059.95 | 542.3326 | 1602.2826 | 0 | 1602.2826 | 0 | 0 | 66.1525 | 33.8475 | 0 | 66.1525 | 33.8475 | 0
161 | 16 | June | 6.7 | 8.2487 | 761.6 | 434.7566 | 1196.3566 | 0 | 1196.3566 | 0 | 0 | 63.6599 | 36.3401 | 0 | 63.6599 | 36.3401 | 0
161 | 17 | June | 6.7 | 8.2487 | 761.6 | 313.0178 | 1074.6178 | 0 | 1074.6178 | 0 | 0 | 70.8717 | 29.1283 | 0 | 70.8717 | 29.1283 | 0
161 | 18 | June | 7.2 | 8.8642 | 908.65 | 191.3719 | 1100.0219 | 0 | 1100.0219 | 0 | 0 | 82.6029 | 17.3971 | 0 | 82.6029 | 17.3971 | 0
161 | 19 | June | 7.7 | 9.4798 | 1059.95 | 88.641 | 1148.591 | 0 | 1148.591 | 0 | 0 | 92.2826 | 7.7174 | 0 | 92.2826 | 7.7174 | 0
161 | 20 | June | 6.7 | 8.2487 | 761.6 | 17.199 | 778.799 | 0 | 778.799 | 0 | 0 | 97.7916 | 2.2084 | 0 | 97.7916 | 2.2084 | 0
161 | 21 | June | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
161 | 22 | June | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
161 | 23 | June | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
161 | 24 | June | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
162 | 1 | June | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
162 | 2 | June | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
162 | 3 | June | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
162 | 4 | June | 6.7 | 8.2487 | 761.6 | 1.323 | 762.923 | 0 | 762.923 | 0 | 0 | 99.8266 | 0.17341 | 0 | 99.8266 | 0.17341 | 0
162 | 5 | June | 2.1 | 2.5854 | 0 | 30.429 | 30.429 | 0 | 30.429 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
162 | 6 | June | 3.1 | 3.8165 | 0 | 114.0609 | 114.0609 | 0 | 114.0609 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
162 | 7 | June | 4.1 | 5.0477 | 173.4 | 228.8813 | 402.2813 | 0 | 402.2813 | 0 | 0 | 43.1042 | 56.8958 | 0 | 43.1042 | 56.8958 | 0
162 | 8 | June | 4.6 | 5.6633 | 237.15 | 356.086 | 593.236 | 0 | 593.236 | 0 | 0 | 39.9757 | 60.0243 | 0 | 39.9757 | 60.0243 | 0
162 | 9 | June | 4.6 | 5.6633 | 237.15 | 289.1359 | 526.2859 | 0 | 526.2859 | 0 | 0 | 45.0611 | 54.9389 | 0 | 45.0611 | 54.9389 | 0
162 | 10 | June | 3.1 | 3.8165 | 0 | 346.0377 | 346.0377 | 0 | 346.0377 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
162 | 11 | June | 2.1 | 2.5854 | 0 | 387.5135 | 387.5135 | 0 | 387.5135 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
162 | 12 | June | 2.6 | 3.201 | 0 | 406.6815 | 406.6815 | 0 | 406.6815 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
162 | 13 | June | 3.1 | 3.8165 | 0 | 403.3508 | 403.3508 | 0 | 403.3508 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
162 | 14 | June | 2.6 | 3.201 | 0 | 377.7353 | 377.7353 | 0 | 377.7353 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
162 | 15 | June | 1.3 | 1.6005 | 0 | 332.2679 | 332.2679 | 0 | 332.2679 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
162 | 16 | June | 0 | 0 | 0 | 269.427 | 269.427 | 0 | 269.427 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
162 | 17 | June | 0 | 0 | 0 | 311.3805 | 311.3805 | 0 | 311.3805 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
162 | 18 | June | 0 | 0 | 0 | 191.2101 | 191.2101 | 0 | 191.2101 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
162 | 19 | June | 0 | 0 | 0 | 55.566 | 55.566 | 0 | 55.566 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
162 | 20 | June | 2.1 | 2.5854 | 0 | 17.199 | 17.199 | 0 | 17.199 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
162 | 21 | June | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
162 | 22 | June | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
162 | 23 | June | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
162 | 24 | June | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
163 | 1 | June | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
163 | 2 | June | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
163 | 3 | June | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
163 | 4 | June | 2.6 | 3.201 | 0 | 2.646 | 2.646 | 0 | 2.646 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
163 | 5 | June | 2.1 | 2.5854 | 0 | 38.367 | 38.367 | 0 | 38.367 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
163 | 6 | June | 3.1 | 3.8165 | 0 | 143.108 | 143.108 | 0 | 143.108 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
163 | 7 | June | 4.1 | 5.0477 | 173.4 | 228.8684 | 402.2684 | 0 | 402.2684 | 0 | 0 | 43.1056 | 56.8944 | 0 | 43.1056 | 56.8944 | 0
163 | 8 | June | 4.6 | 5.6633 | 237.15 | 353.7898 | 590.9398 | 0 | 590.9398 | 0 | 0 | 40.131 | 59.869 | 0 | 40.131 | 59.869 | 0
163 | 9 | June | 5.1 | 6.2788 | 312.8 | 481.232 | 794.032 | 0 | 794.032 | 0 | 0 | 39.3939 | 60.6061 | 0 | 39.3939 | 60.6061 | 0
163 | 10 | June | 5.7 | 7.0175 | 504.9 | 577.8403 | 1082.7403 | 0 | 1082.7403 | 0 | 0 | 46.6317 | 53.3683 | 0 | 46.6317 | 53.3683 | 0
163 | 11 | June | 4.6 | 5.6633 | 237.15 | 649.8888 | 887.0388 | 0 | 887.0388 | 0 | 0 | 26.735 | 73.265 | 0 | 26.735 | 73.265 | 0
163 | 12 | June | 2.6 | 3.201 | 0 | 679.6948 | 679.6948 | 0 | 679.6948 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
163 | 13 | June | 4.1 | 5.0477 | 173.4 | 409.3157 | 582.7157 | 0 | 582.7157 | 0 | 0 | 29.7572 | 70.2428 | 0 | 29.7572 | 70.2428 | 0
163 | 14 | June | 3.1 | 3.8165 | 0 | 634.8584 | 634.8584 | 0 | 634.8584 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
163 | 15 | June | 4.1 | 5.0477 | 173.4 | 540.164 | 713.564 | 0 | 713.564 | 0 | 0 | 24.3006 | 75.6994 | 0 | 24.3006 | 75.6994 | 0
163 | 16 | June | 5.7 | 7.0175 | 504.9 | 434.5176 | 939.4176 | 0 | 939.4176 | 0 | 0 | 53.7461 | 46.2539 | 0 | 53.7461 | 46.2539 | 0
163 | 17 | June | 4.1 | 5.0477 | 173.4 | 313.9036 | 487.3036 | 0 | 487.3036 | 0 | 0 | 35.5836 | 64.4164 | 0 | 35.5836 | 64.4164 | 0
163 | 18 | June | 3.1 | 3.8165 | 0 | 254.2573 | 254.2573 | 0 | 254.2573 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
163 | 19 | June | 3.1 | 3.8165 | 0 | 107.163 | 107.163 | 0 | 107.163 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
163 | 20 | June | 4.1 | 5.0477 | 173.4 | 30.429 | 203.829 | 0 | 203.829 | 0 | 0 | 85.0713 | 14.9287 | 0 | 85.0713 | 14.9287 | 0
163 | 21 | June | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
163 | 22 | June | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
163 | 23 | June | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
163 | 24 | June | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
164 | 1 | June | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
164 | 2 | June | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
164 | 3 | June | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
164 | 4 | June | 3.1 | 3.8165 | 0 | 2.646 | 2.646 | 0 | 2.646 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
164 | 5 | June | 3.6 | 4.4321 | 75.65 | 30.429 | 106.079 | 0 | 106.079 | 0 | 0 | 71.3148 | 28.6852 | 0 | 71.3148 | 28.6852 | 0
164 | 6 | June | 3.1 | 3.8165 | 0 | 161.5488 | 161.5488 | 0 | 161.5488 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
164 | 7 | June | 4.6 | 5.6633 | 237.15 | 361.4677 | 598.6177 | 0 | 598.6177 | 0 | 0 | 39.6163 | 60.3837 | 0 | 39.6163 | 60.3837 | 0
164 | 8 | June | 5.1 | 6.2788 | 312.8 | 358.1688 | 670.9688 | 0 | 670.9688 | 0 | 0 | 46.6192 | 53.3808 | 0 | 46.6192 | 53.3808 | 0
164 | 9 | June | 4.1 | 5.0477 | 173.4 | 481.1875 | 654.5875 | 0 | 654.5875 | 0 | 0 | 26.49 | 73.51 | 0 | 26.49 | 73.51 | 0
164 | 10 | June | 3.6 | 4.4321 | 75.65 | 347.4579 | 423.1079 | 0 | 423.1079 | 0 | 0 | 17.8796 | 82.1204 | 0 | 17.8796 | 82.1204 | 0
164 | 11 | June | 4.1 | 5.0477 | 173.4 | 387.5077 | 560.9077 | 0 | 560.9077 | 0 | 0 | 30.9142 | 69.0858 | 0 | 30.9142 | 69.0858 | 0
164 | 12 | June | 5.7 | 7.0175 | 504.9 | 695.8128 | 1200.7128 | 0 | 1200.7128 | 0 | 0 | 42.05 | 57.95 | 0 | 42.05 | 57.95 | 0
164 | 13 | June | 4.1 | 5.0477 | 173.4 | 409.3255 | 582.7255 | 0 | 582.7255 | 0 | 0 | 29.7567 | 70.2433 | 0 | 29.7567 | 70.2433 | 0
164 | 14 | June | 5.1 | 6.2788 | 312.8 | 633.559 | 946.359 | 0 | 946.359 | 0 | 0 | 33.053 | 66.947 | 0 | 33.053 | 66.947 | 0
164 | 15 | June | 5.1 | 6.2788 | 312.8 | 714.7303 | 1027.5303 | 0 | 1027.5303 | 0 | 0 | 30.4419 | 69.5581 | 0 | 30.4419 | 69.5581 | 0
164 | 16 | June | 4.1 | 5.0477 | 173.4 | 434.1548 | 607.5548 | 0 | 607.5548 | 0 | 0 | 28.5406 | 71.4594 | 0 | 28.5406 | 71.4594 | 0
164 | 17 | June | 2.6 | 3.201 | 0 | 313.9557 | 313.9557 | 0 | 313.9557 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
164 | 18 | June | 0 | 0 | 0 | 251.6011 | 251.6011 | 0 | 251.6011 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
164 | 19 | June | 3.1 | 3.8165 | 0 | 109.809 | 109.809 | 0 | 109.809 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
164 | 20 | June | 1.5 | 1.8467 | 0 | 31.752 | 31.752 | 0 | 31.752 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
164 | 21 | June | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
164 | 22 | June | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
164 | 23 | June | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
164 | 24 | June | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
165 | 1 | June | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
165 | 2 | June | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
165 | 3 | June | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
165 | 4 | June | 3.1 | 3.8165 | 0 | 2.646 | 2.646 | 0 | 2.646 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
165 | 5 | June | 2.1 | 2.5854 | 0 | 18.522 | 18.522 | 0 | 18.522 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
165 | 6 | June | 3.6 | 4.4321 | 75.65 | 114.3405 | 189.9905 | 0 | 189.9905 | 0 | 0 | 39.8178 | 60.1822 | 0 | 39.8178 | 60.1822 | 0
165 | 7 | June | 5.1 | 6.2788 | 312.8 | 230.7894 | 543.5894 | 0 | 543.5894 | 0 | 0 | 57.5434 | 42.4566 | 0 | 57.5434 | 42.4566 | 0
165 | 8 | June | 3.6 | 4.4321 | 75.65 | 360.4048 | 436.0548 | 0 | 436.0548 | 0 | 0 | 17.3487 | 82.6513 | 0 | 17.3487 | 82.6513 | 0
165 | 9 | June | 4.6 | 5.6633 | 237.15 | 488.8701 | 726.0201 | 0 | 726.0201 | 0 | 0 | 32.6644 | 67.3356 | 0 | 32.6644 | 67.3356 | 0
165 | 10 | June | 4.6 | 5.6633 | 237.15 | 587.3604 | 824.5104 | 0 | 824.5104 | 0 | 0 | 28.7625 | 71.2375 | 0 | 28.7625 | 71.2375 | 0
165 | 11 | June | 5.7 | 7.0175 | 504.9 | 905.858 | 1410.758 | 0 | 1410.758 | 0 | 0 | 35.7893 | 64.2107 | 0 | 35.7893 | 64.2107 | 0
165 | 12 | June | 6.7 | 8.2487 | 761.6 | 688.1611 | 1449.7611 | 0 | 1449.7611 | 0 | 0 | 52.5328 | 47.4672 | 0 | 52.5328 | 47.4672 | 0
165 | 13 | June | 7.2 | 8.8642 | 908.65 | 665.127 | 1573.777 | 0 | 1573.777 | 0 | 0 | 57.7369 | 42.2631 | 0 | 57.7369 | 42.2631 | 0
165 | 14 | June | 5.1 | 6.2788 | 312.8 | 628.8883 | 941.6883 | 0 | 941.6883 | 0 | 0 | 33.2169 | 66.7831 | 0 | 33.2169 | 66.7831 | 0
165 | 15 | June | 7.2 | 8.8642 | 908.65 | 548.2112 | 1456.8612 | 0 | 1456.8612 | 0 | 0 | 62.3704 | 37.6296 | 0 | 62.3704 | 37.6296 | 0
165 | 16 | June | 6.2 | 7.6331 | 625.6 | 439.5186 | 1065.1186 | 0 | 1065.1186 | 0 | 0 | 58.7352 | 41.2648 | 0 | 58.7352 | 41.2648 | 0
165 | 17 | June | 7.2 | 8.8642 | 908.65 | 318.8538 | 1227.5038 | 0 | 1227.5038 | 0 | 0 | 74.0242 | 25.9758 | 0 | 74.0242 | 25.9758 | 0
165 | 18 | June | 6.2 | 7.6331 | 625.6 | 197.3116 | 822.9116 | 0 | 822.9116 | 0 | 0 | 76.0228 | 23.9772 | 0 | 76.0228 | 23.9772 | 0
165 | 19 | June | 6.7 | 8.2487 | 761.6 | 92.61 | 854.21 | 0 | 854.21 | 0 | 0 | 89.1584 | 10.8416 | 0 | 89.1584 | 10.8416 | 0
165 | 20 | June | 5.7 | 7.0175 | 504.9 | 11.907 | 516.807 | 0 | 516.807 | 0 | 0 | 97.696 | 2.304 | 0 | 97.696 | 2.304 | 0
165 | 21 | June | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
165 | 22 | June | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
165 | 23 | June | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
165 | 24 | June | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
166 | 1 | June | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
166 | 2 | June | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
166 | 3 | June | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
166 | 4 | June | 2.6 | 3.201 | 0 | 2.646 | 2.646 | 0 | 2.646 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
166 | 5 | June | 2.1 | 2.5854 | 0 | 30.429 | 30.429 | 0 | 30.429 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
166 | 6 | June | 2.6 | 3.201 | 0 | 115.662 | 115.662 | 0 | 115.662 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
166 | 7 | June | 2.6 | 3.201 | 0 | 230.5553 | 230.5553 | 0 | 230.5553 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
166 | 8 | June | 3.1 | 3.8165 | 0 | 362.6371 | 362.6371 | 0 | 362.6371 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
166 | 9 | June | 3.1 | 3.8165 | 0 | 666.1617 | 666.1617 | 0 | 666.1617 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
166 | 10 | June | 3.6 | 4.4321 | 75.65 | 589.342 | 664.992 | 0 | 664.992 | 0 | 0 | 11.3761 | 88.6239 | 0 | 11.3761 | 88.6239 | 0
166 | 11 | June | 3.1 | 3.8165 | 0 | 645.4384 | 645.4384 | 0 | 645.4384 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
166 | 12 | June | 3.6 | 4.4321 | 75.65 | 949.7443 | 1025.3943 | 0 | 1025.3943 | 0 | 0 | 7.3776 | 92.6224 | 0 | 7.3776 | 92.6224 | 0
166 | 13 | June | 3.1 | 3.8165 | 0 | 1141.9933 | 1141.9933 | 0 | 1141.9933 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
166 | 14 | June | 3.6 | 4.4321 | 75.65 | 858.4282 | 934.0782 | 0 | 934.0782 | 0 | 0 | 8.0989 | 91.9011 | 0 | 8.0989 | 91.9011 | 0
166 | 15 | June | 3.1 | 3.8165 | 0 | 550.7238 | 550.7238 | 0 | 550.7238 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
166 | 16 | June | 3.1 | 3.8165 | 0 | 442.713 | 442.713 | 0 | 442.713 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
166 | 17 | June | 3.6 | 4.4321 | 75.65 | 320.767 | 396.417 | 0 | 396.417 | 0 | 0 | 19.0834 | 80.9166 | 0 | 19.0834 | 80.9166 | 0
166 | 18 | June | 3.6 | 4.4321 | 75.65 | 227.5966 | 303.2466 | 0 | 303.2466 | 0 | 0 | 24.9467 | 75.0533 | 0 | 24.9467 | 75.0533 | 0
166 | 19 | June | 2.6 | 3.201 | 0 | 92.61 | 92.61 | 0 | 92.61 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
166 | 20 | June | 1.5 | 1.8467 | 0 | 18.522 | 18.522 | 0 | 18.522 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
166 | 21 | June | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
166 | 22 | June | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
166 | 23 | June | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
166 | 24 | June | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
167 | 1 | June | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
167 | 2 | June | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
167 | 3 | June | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
167 | 4 | June | 1 | 1.2311 | 0 | 2.646 | 2.646 | 0 | 2.646 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
167 | 5 | June | 0 | 0 | 0 | 30.429 | 30.429 | 0 | 30.429 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
167 | 6 | June | 0.5 | 0.61557 | 0 | 144.0696 | 144.0696 | 0 | 144.0696 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
167 | 7 | June | 2.6 | 3.201 | 0 | 229.2244 | 229.2244 | 0 | 229.2244 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
167 | 8 | June | 2.6 | 3.201 | 0 | 361.2728 | 361.2728 | 0 | 361.2728 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
167 | 9 | June | 3.1 | 3.8165 | 0 | 491.1885 | 491.1885 | 0 | 491.1885 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
167 | 10 | June | 3.6 | 4.4321 | 75.65 | 588.6911 | 664.3411 | 0 | 664.3411 | 0 | 0 | 11.3872 | 88.6128 | 0 | 11.3872 | 88.6128 | 0
167 | 11 | June | 5.1 | 6.2788 | 312.8 | 642.5468 | 955.3468 | 0 | 955.3468 | 0 | 0 | 32.742 | 67.258 | 0 | 32.742 | 67.258 | 0
167 | 12 | June | 5.1 | 6.2788 | 312.8 | 944.4609 | 1257.2609 | 0 | 1257.2609 | 0 | 0 | 24.8795 | 75.1205 | 0 | 24.8795 | 75.1205 | 0
167 | 13 | June | 5.1 | 6.2788 | 312.8 | 1244.9213 | 1557.7213 | 0 | 1557.7213 | 0 | 0 | 20.0806 | 79.9194 | 0 | 20.0806 | 79.9194 | 0
167 | 14 | June | 5.7 | 7.0175 | 504.9 | 1290.3114 | 1795.2114 | 0 | 1795.2114 | 0 | 0 | 28.1248 | 71.8752 | 0 | 28.1248 | 71.8752 | 0
167 | 15 | June | 5.1 | 6.2788 | 312.8 | 1083.4226 | 1396.2226 | 0 | 1396.2226 | 0 | 0 | 22.4033 | 77.5967 | 0 | 22.4033 | 77.5967 | 0
167 | 16 | June | 5.7 | 7.0175 | 504.9 | 734.6025 | 1239.5025 | 0 | 1239.5025 | 0 | 0 | 40.7341 | 59.2659 | 0 | 40.7341 | 59.2659 | 0
167 | 17 | June | 4.6 | 5.6633 | 237.15 | 394.6681 | 631.8181 | 0 | 631.8181 | 0 | 0 | 37.5345 | 62.4655 | 0 | 37.5345 | 62.4655 | 0
167 | 18 | June | 4.6 | 5.6633 | 237.15 | 246.6708 | 483.8208 | 0 | 483.8208 | 0 | 0 | 49.0161 | 50.9839 | 0 | 49.0161 | 50.9839 | 0
167 | 19 | June | 5.1 | 6.2788 | 312.8 | 116.424 | 429.224 | 0 | 429.224 | 0 | 0 | 72.8757 | 27.1243 | 0 | 72.8757 | 27.1243 | 0
167 | 20 | June | 5.1 | 6.2788 | 312.8 | 23.814 | 336.614 | 0 | 336.614 | 0 | 0 | 92.9254 | 7.0746 | 0 | 92.9254 | 7.0746 | 0
167 | 21 | June | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
167 | 22 | June | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
167 | 23 | June | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
167 | 24 | June | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
168 | 1 | June | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
168 | 2 | June | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
168 | 3 | June | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
168 | 4 | June | 4.1 | 5.0477 | 173.4 | 2.646 | 176.046 | 0 | 176.046 | 0 | 0 | 98.497 | 1.503 | 0 | 98.497 | 1.503 | 0
168 | 5 | June | 3.6 | 4.4321 | 75.65 | 30.429 | 106.079 | 0 | 106.079 | 0 | 0 | 71.3148 | 28.6852 | 0 | 71.3148 | 28.6852 | 0
168 | 6 | June | 3.6 | 4.4321 | 75.65 | 115.6586 | 191.3086 | 0 | 191.3086 | 0 | 0 | 39.5434 | 60.4566 | 0 | 39.5434 | 60.4566 | 0
168 | 7 | June | 3.6 | 4.4321 | 75.65 | 230.5391 | 306.1891 | 0 | 306.1891 | 0 | 0 | 24.707 | 75.293 | 0 | 24.707 | 75.293 | 0
168 | 8 | June | 4.6 | 5.6633 | 237.15 | 361.2295 | 598.3795 | 0 | 598.3795 | 0 | 0 | 39.632 | 60.368 | 0 | 39.632 | 60.368 | 0
168 | 9 | June | 5.1 | 6.2788 | 312.8 | 949.9346 | 1262.7346 | 0 | 1262.7346 | 0 | 0 | 24.7716 | 75.2284 | 0 | 24.7716 | 75.2284 | 0
168 | 10 | June | 4.1 | 5.0477 | 173.4 | 1008.3707 | 1181.7707 | 0 | 1181.7707 | 0 | 0 | 14.6729 | 85.3271 | 0 | 14.6729 | 85.3271 | 0
168 | 11 | June | 3.6 | 4.4321 | 75.65 | 1254.3182 | 1329.9682 | 0 | 1329.9682 | 0 | 0 | 5.6881 | 94.3119 | 0 | 5.6881 | 94.3119 | 0
168 | 12 | June | 3.6 | 4.4321 | 75.65 | 1413.6164 | 1489.2664 | 0 | 1489.2664 | 0 | 0 | 5.0797 | 94.9203 | 0 | 5.0797 | 94.9203 | 0
168 | 13 | June | 3.6 | 4.4321 | 75.65 | 1394.1157 | 1469.7657 | 0 | 1469.7657 | 0 | 0 | 5.1471 | 94.8529 | 0 | 5.1471 | 94.8529 | 0
168 | 14 | June | 3.1 | 3.8165 | 0 | 1259.6561 | 1259.6561 | 0 | 1259.6561 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
168 | 15 | June | 3.6 | 4.4321 | 75.65 | 1047.9467 | 1123.5967 | 0 | 1123.5967 | 0 | 0 | 6.7328 | 93.2672 | 0 | 6.7328 | 93.2672 | 0
168 | 16 | June | 3.1 | 3.8165 | 0 | 778.7096 | 778.7096 | 0 | 778.7096 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
168 | 17 | June | 3.1 | 3.8165 | 0 | 500.1982 | 500.1982 | 0 | 500.1982 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
168 | 18 | June | 2.6 | 3.201 | 0 | 244.3717 | 244.3717 | 0 | 244.3717 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
168 | 19 | June | 2.6 | 3.201 | 0 | 107.163 | 107.163 | 0 | 107.163 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
168 | 20 | June | 2.6 | 3.201 | 0 | 34.398 | 34.398 | 0 | 34.398 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
168 | 21 | June | 2.6 | 3.201 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
168 | 22 | June | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
168 | 23 | June | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
168 | 24 | June | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
169 | 1 | June | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
169 | 2 | June | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
169 | 3 | June | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
169 | 4 | June | 2.1 | 2.5854 | 0 | 3.969 | 3.969 | 0 | 3.969 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
169 | 5 | June | 3.1 | 3.8165 | 0 | 46.305 | 46.305 | 0 | 46.305 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
169 | 6 | June | 2.6 | 3.201 | 0 | 115.3788 | 115.3788 | 0 | 115.3788 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
169 | 7 | June | 3.1 | 3.8165 | 0 | 405.1676 | 405.1676 | 0 | 405.1676 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
169 | 8 | June | 5.7 | 7.0175 | 504.9 | 750.2014 | 1255.1014 | 0 | 1255.1014 | 0 | 0 | 40.2278 | 59.7722 | 0 | 40.2278 | 59.7722 | 0
169 | 9 | June | 5.7 | 7.0175 | 504.9 | 490.6364 | 995.5364 | 0 | 995.5364 | 0 | 0 | 50.7164 | 49.2836 | 0 | 50.7164 | 49.2836 | 0
169 | 10 | June | 5.1 | 6.2788 | 312.8 | 576.3923 | 889.1923 | 0 | 889.1923 | 0 | 0 | 35.178 | 64.822 | 0 | 35.178 | 64.822 | 0
169 | 11 | June | 5.7 | 7.0175 | 504.9 | 654.1647 | 1159.0647 | 0 | 1159.0647 | 0 | 0 | 43.561 | 56.439 | 0 | 43.561 | 56.439 | 0
169 | 12 | June | 6.7 | 8.2487 | 761.6 | 1144.9484 | 1906.5484 | 0 | 1906.5484 | 0 | 0 | 39.9465 | 60.0535 | 0 | 39.9465 | 60.0535 | 0
169 | 13 | June | 6.7 | 8.2487 | 761.6 | 690.7239 | 1452.3239 | 0 | 1452.3239 | 0 | 0 | 52.4401 | 47.5599 | 0 | 52.4401 | 47.5599 | 0
169 | 14 | June | 5.7 | 7.0175 | 504.9 | 629.0674 | 1133.9674 | 0 | 1133.9674 | 0 | 0 | 44.5251 | 55.4749 | 0 | 44.5251 | 55.4749 | 0
169 | 15 | June | 4.1 | 5.0477 | 173.4 | 336.0692 | 509.4692 | 0 | 509.4692 | 0 | 0 | 34.0354 | 65.9646 | 0 | 34.0354 | 65.9646 | 0
169 | 16 | June | 5.7 | 7.0175 | 504.9 | 568.1419 | 1073.0419 | 0 | 1073.0419 | 0 | 0 | 47.0532 | 52.9468 | 0 | 47.0532 | 52.9468 | 0
169 | 17 | June | 5.1 | 6.2788 | 312.8 | 318.0318 | 630.8318 | 0 | 630.8318 | 0 | 0 | 49.5853 | 50.4147 | 0 | 49.5853 | 50.4147 | 0
169 | 18 | June | 7.2 | 8.8642 | 908.65 | 200.0474 | 1108.6974 | 0 | 1108.6974 | 0 | 0 | 81.9565 | 18.0435 | 0 | 81.9565 | 18.0435 | 0
169 | 19 | June | 6.7 | 8.2487 | 761.6 | 95.256 | 856.856 | 0 | 856.856 | 0 | 0 | 88.8831 | 11.1169 | 0 | 88.8831 | 11.1169 | 0
169 | 20 | June | 5.1 | 6.2788 | 312.8 | 19.845 | 332.645 | 0 | 332.645 | 0 | 0 | 94.0342 | 5.9658 | 0 | 94.0342 | 5.9658 | 0
169 | 21 | June | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
169 | 22 | June | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
169 | 23 | June | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
169 | 24 | June | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
170 | 1 | June | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
170 | 2 | June | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
170 | 3 | June | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
170 | 4 | June | 3.1 | 3.8165 | 0 | 2.646 | 2.646 | 0 | 2.646 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
170 | 5 | June | 4.1 | 5.0477 | 173.4 | 30.429 | 203.829 | 0 | 203.829 | 0 | 0 | 85.0713 | 14.9287 | 0 | 85.0713 | 14.9287 | 0
170 | 6 | June | 4.1 | 5.0477 | 173.4 | 71.442 | 244.842 | 0 | 244.842 | 0 | 0 | 70.8212 | 29.1788 | 0 | 70.8212 | 29.1788 | 0
170 | 7 | June | 5.1 | 6.2788 | 312.8 | 142.884 | 455.684 | 0 | 455.684 | 0 | 0 | 68.6441 | 31.3559 | 0 | 68.6441 | 31.3559 | 0
170 | 8 | June | 6.2 | 7.6331 | 625.6 | 217.9161 | 843.5161 | 0 | 843.5161 | 0 | 0 | 74.1657 | 25.8343 | 0 | 74.1657 | 25.8343 | 0
170 | 9 | June | 7.2 | 8.8642 | 908.65 | 289.2076 | 1197.8576 | 0 | 1197.8576 | 0 | 0 | 75.8563 | 24.1437 | 0 | 75.8563 | 24.1437 | 0
170 | 10 | June | 7.2 | 8.8642 | 908.65 | 347.3311 | 1255.9811 | 0 | 1255.9811 | 0 | 0 | 72.3458 | 27.6542 | 0 | 72.3458 | 27.6542 | 0
170 | 11 | June | 7.2 | 8.8642 | 908.65 | 387.489 | 1296.139 | 0 | 1296.139 | 0 | 0 | 70.1044 | 29.8956 | 0 | 70.1044 | 29.8956 | 0
170 | 12 | June | 7.2 | 8.8642 | 908.65 | 408.0066 | 1316.6566 | 0 | 1316.6566 | 0 | 0 | 69.0119 | 30.9881 | 0 | 69.0119 | 30.9881 | 0
170 | 13 | June | 5.8 | 7.1406 | 504.9 | 489.0255 | 993.9255 | 0 | 993.9255 | 0 | 0 | 50.7986 | 49.2014 | 0 | 50.7986 | 49.2014 | 0
170 | 14 | June | 4.5 | 5.5401 | 237.15 | 536.2191 | 773.3691 | 0 | 773.3691 | 0 | 0 | 30.6645 | 69.3355 | 0 | 30.6645 | 69.3355 | 0
170 | 15 | June | 3.1 | 3.8165 | 0 | 546.4193 | 546.4193 | 0 | 546.4193 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
170 | 16 | June | 4.6 | 5.6633 | 237.15 | 439.971 | 677.121 | 0 | 677.121 | 0 | 0 | 35.0233 | 64.9767 | 0 | 35.0233 | 64.9767 | 0
170 | 17 | June | 6.7 | 8.2487 | 761.6 | 320.0887 | 1081.6887 | 0 | 1081.6887 | 0 | 0 | 70.4084 | 29.5916 | 0 | 70.4084 | 29.5916 | 0
170 | 18 | June | 6.2 | 7.6331 | 625.6 | 128.331 | 753.931 | 0 | 753.931 | 0 | 0 | 82.9784 | 17.0216 | 0 | 82.9784 | 17.0216 | 0
170 | 19 | June | 2.6 | 3.201 | 0 | 59.535 | 59.535 | 0 | 59.535 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
170 | 20 | June | 3.6 | 4.4321 | 75.65 | 11.907 | 87.557 | 0 | 87.557 | 0 | 0 | 86.4009 | 13.5991 | 0 | 86.4009 | 13.5991 | 0
170 | 21 | June | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
170 | 22 | June | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
170 | 23 | June | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
170 | 24 | June | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
171 | 1 | June | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
171 | 2 | June | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
171 | 3 | June | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
171 | 4 | June | 4.1 | 5.0477 | 173.4 | 2.646 | 176.046 | 0 | 176.046 | 0 | 0 | 98.497 | 1.503 | 0 | 98.497 | 1.503 | 0
171 | 5 | June | 4.1 | 5.0477 | 173.4 | 48.951 | 222.351 | 0 | 222.351 | 0 | 0 | 77.9848 | 22.0152 | 0 | 77.9848 | 22.0152 | 0
171 | 6 | June | 3.6 | 4.4321 | 75.65 | 189.4786 | 265.1286 | 0 | 265.1286 | 0 | 0 | 28.5333 | 71.4667 | 0 | 28.5333 | 71.4667 | 0
171 | 7 | June | 3.6 | 4.4321 | 75.65 | 427.5378 | 503.1878 | 0 | 503.1878 | 0 | 0 | 15.0341 | 84.9659 | 0 | 15.0341 | 84.9659 | 0
171 | 8 | June | 3.6 | 4.4321 | 75.65 | 748.8716 | 824.5216 | 0 | 824.5216 | 0 | 0 | 9.175 | 90.825 | 0 | 9.175 | 90.825 | 0
171 | 9 | June | 5.1 | 6.2788 | 312.8 | 933.7343 | 1246.5343 | 0 | 1246.5343 | 0 | 0 | 25.0936 | 74.9064 | 0 | 25.0936 | 74.9064 | 0
171 | 10 | June | 5.1 | 6.2788 | 312.8 | 990.575 | 1303.375 | 0 | 1303.375 | 0 | 0 | 23.9992 | 76.0008 | 0 | 23.9992 | 76.0008 | 0
171 | 11 | June | 4.1 | 5.0477 | 173.4 | 1114.8683 | 1288.2683 | 0 | 1288.2683 | 0 | 0 | 13.4599 | 86.5401 | 0 | 13.4599 | 86.5401 | 0
171 | 12 | June | 4.6 | 5.6633 | 237.15 | 698.4862 | 935.6362 | 0 | 935.6362 | 0 | 0 | 25.3464 | 74.6536 | 0 | 25.3464 | 74.6536 | 0
171 | 13 | June | 7.2 | 8.8642 | 908.65 | 409.5206 | 1318.1706 | 0 | 1318.1706 | 0 | 0 | 68.9327 | 31.0673 | 0 | 68.9327 | 31.0673 | 0
171 | 14 | June | 7.2 | 8.8642 | 908.65 | 381.364 | 1290.014 | 0 | 1290.014 | 0 | 0 | 70.4372 | 29.5628 | 0 | 70.4372 | 29.5628 | 0
171 | 15 | June | 6.2 | 7.6331 | 625.6 | 339.2037 | 964.8037 | 0 | 964.8037 | 0 | 0 | 64.8422 | 35.1578 | 0 | 64.8422 | 35.1578 | 0
171 | 16 | June | 7.2 | 8.8642 | 908.65 | 276.5562 | 1185.2062 | 0 | 1185.2062 | 0 | 0 | 76.666 | 23.334 | 0 | 76.666 | 23.334 | 0
171 | 17 | June | 6.7 | 8.2487 | 761.6 | 204.3022 | 965.9022 | 0 | 965.9022 | 0 | 0 | 78.8486 | 21.1514 | 0 | 78.8486 | 21.1514 | 0
171 | 18 | June | 8.7 | 10.711 | 1490.05 | 128.331 | 1618.381 | 0 | 1618.381 | 0 | 0 | 92.0704 | 7.9296 | 0 | 92.0704 | 7.9296 | 0
171 | 19 | June | 10.3 | 12.6808 | 1694.9 | 59.535 | 1754.435 | 0 | 1754.435 | 0 | 0 | 96.6066 | 3.3934 | 0 | 96.6066 | 3.3934 | 0
171 | 20 | June | 8.2 | 10.0954 | 1359.15 | 19.845 | 1378.995 | 0 | 1378.995 | 0 | 0 | 98.5609 | 1.4391 | 0 | 98.5609 | 1.4391 | 0
171 | 21 | June | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
171 | 22 | June | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
171 | 23 | June | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
171 | 24 | June | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
172 | 1 | June | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
172 | 2 | June | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
172 | 3 | June | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
172 | 4 | June | 5.7 | 7.0175 | 504.9 | 3.969 | 508.869 | 0 | 508.869 | 0 | 0 | 99.22 | 0.77996 | 0 | 99.22 | 0.77996 | 0
172 | 5 | June | 4.6 | 5.6633 | 237.15 | 38.367 | 275.517 | 0 | 275.517 | 0 | 0 | 86.0745 | 13.9255 | 0 | 86.0745 | 13.9255 | 0
172 | 6 | June | 5.7 | 7.0175 | 504.9 | 142.6555 | 647.5555 | 0 | 647.5555 | 0 | 0 | 77.9702 | 22.0298 | 0 | 77.9702 | 22.0298 | 0
172 | 7 | June | 6.2 | 7.6331 | 625.6 | 438.5505 | 1064.1505 | 0 | 1064.1505 | 0 | 0 | 58.7887 | 41.2113 | 0 | 58.7887 | 41.2113 | 0
172 | 8 | June | 6.7 | 8.2487 | 761.6 | 659.0296 | 1420.6296 | 0 | 1420.6296 | 0 | 0 | 53.61 | 46.39 | 0 | 53.61 | 46.39 | 0
172 | 9 | June | 6.7 | 8.2487 | 761.6 | 1030.2642 | 1791.8642 | 0 | 1791.8642 | 0 | 0 | 42.5032 | 57.4968 | 0 | 42.5032 | 57.4968 | 0
172 | 10 | June | 7.2 | 8.8642 | 908.65 | 815.7175 | 1724.3675 | 0 | 1724.3675 | 0 | 0 | 52.6947 | 47.3053 | 0 | 52.6947 | 47.3053 | 0
172 | 11 | June | 8.2 | 10.0954 | 1359.15 | 1333.179 | 2692.329 | 1 | 2000 | 692.329 | 34.6165 | 50.4823 | 32.0425 | 51.9307 | 33.341 | 49.5177 | 50.9384
172 | 12 | June | 7.7 | 9.4798 | 1059.95 | 1172.2101 | 2232.1601 | 1 | 2000 | 232.1601 | 11.608 | 47.4854 | 47.0025 | 19.8053 | 41.3895 | 52.5146 | 21.9029
172 | 13 | June | 7.2 | 8.8642 | 908.65 | 1135.0654 | 2043.7154 | 1 | 2000 | 43.7154 | 2.1858 | 44.4607 | 54.5675 | 3.8514 | 43.2467 | 55.5393 | 4.811
172 | 14 | June | 10.3 | 12.6808 | 1694.9 | 1160.0045 | 2854.9045 | 1 | 2000 | 854.9045 | 42.7452 | 59.368 | 15.255 | 73.6984 | 41.9998 | 40.632 | 50.4398
172 | 15 | June | 8.2 | 10.0954 | 1359.15 | 554.3691 | 1913.5191 | 0 | 1913.5191 | 0 | 0 | 71.0288 | 28.9712 | 0 | 71.0288 | 28.9712 | 0
172 | 16 | June | 6.2 | 7.6331 | 625.6 | 442.8691 | 1068.4691 | 0 | 1068.4691 | 0 | 0 | 58.5511 | 41.4489 | 0 | 58.5511 | 41.4489 | 0
172 | 17 | June | 6.7 | 8.2487 | 761.6 | 507.7146 | 1269.3146 | 0 | 1269.3146 | 0 | 0 | 60.0009 | 39.9991 | 0 | 60.0009 | 39.9991 | 0
172 | 18 | June | 7.2 | 8.8642 | 908.65 | 240.7428 | 1149.3928 | 0 | 1149.3928 | 0 | 0 | 79.0548 | 20.9452 | 0 | 79.0548 | 20.9452 | 0
172 | 19 | June | 5.1 | 6.2788 | 312.8 | 120.393 | 433.193 | 0 | 433.193 | 0 | 0 | 72.208 | 27.792 | 0 | 72.208 | 27.792 | 0
172 | 20 | June | 4.6 | 5.6633 | 237.15 | 33.075 | 270.225 | 0 | 270.225 | 0 | 0 | 87.7602 | 12.2398 | 0 | 87.7602 | 12.2398 | 0
172 | 21 | June | 4.6 | 5.6633 | 237.15 | 1.323 | 238.473 | 0 | 238.473 | 0 | 0 | 99.4452 | 0.55478 | 0 | 99.4452 | 0.55478 | 0
172 | 22 | June | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
172 | 23 | June | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
172 | 24 | June | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
173 | 1 | June | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
173 | 2 | June | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
173 | 3 | June | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
173 | 4 | June | 3.1 | 3.8165 | 0 | 2.646 | 2.646 | 0 | 2.646 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
173 | 5 | June | 2.6 | 3.201 | 0 | 30.429 | 30.429 | 0 | 30.429 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
173 | 6 | June | 3.6 | 4.4321 | 75.65 | 112.7283 | 188.3783 | 0 | 188.3783 | 0 | 0 | 40.1586 | 59.8414 | 0 | 40.1586 | 59.8414 | 0
173 | 7 | June | 3.1 | 3.8165 | 0 | 227.8439 | 227.8439 | 0 | 227.8439 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
173 | 8 | June | 3.6 | 4.4321 | 75.65 | 483.7339 | 559.3839 | 0 | 559.3839 | 0 | 0 | 13.5238 | 86.4762 | 0 | 13.5238 | 86.4762 | 0
173 | 9 | June | 2.1 | 2.5854 | 0 | 664.5686 | 664.5686 | 0 | 664.5686 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
173 | 10 | June | 2.1 | 2.5854 | 0 | 583.5216 | 583.5216 | 0 | 583.5216 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
173 | 11 | June | 3.1 | 3.8165 | 0 | 905.2623 | 905.2623 | 0 | 905.2623 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
173 | 12 | June | 0 | 0 | 0 | 690.2925 | 690.2925 | 0 | 690.2925 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
173 | 13 | June | 5.7 | 7.0175 | 504.9 | 668.157 | 1173.057 | 0 | 1173.057 | 0 | 0 | 43.0414 | 56.9586 | 0 | 43.0414 | 56.9586 | 0
173 | 14 | June | 0 | 0 | 0 | 623.4598 | 623.4598 | 0 | 623.4598 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
173 | 15 | June | 2.6 | 3.201 | 0 | 728.0937 | 728.0937 | 0 | 728.0937 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
173 | 16 | June | 0.5 | 0.61557 | 0 | 668.5879 | 668.5879 | 0 | 668.5879 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
173 | 17 | June | 5.7 | 7.0175 | 504.9 | 446.1073 | 951.0073 | 0 | 951.0073 | 0 | 0 | 53.0911 | 46.9089 | 0 | 53.0911 | 46.9089 | 0
173 | 18 | June | 5.1 | 6.2788 | 312.8 | 241.7145 | 554.5145 | 0 | 554.5145 | 0 | 0 | 56.4097 | 43.5903 | 0 | 56.4097 | 43.5903 | 0
173 | 19 | June | 4.6 | 5.6633 | 237.15 | 111.132 | 348.282 | 0 | 348.282 | 0 | 0 | 68.0914 | 31.9086 | 0 | 68.0914 | 31.9086 | 0
173 | 20 | June | 3.1 | 3.8165 | 0 | 35.721 | 35.721 | 0 | 35.721 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
173 | 21 | June | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
173 | 22 | June | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
173 | 23 | June | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
173 | 24 | June | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
174 | 1 | June | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
174 | 2 | June | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
174 | 3 | June | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
174 | 4 | June | 6.2 | 7.6331 | 625.6 | 1.323 | 626.923 | 0 | 626.923 | 0 | 0 | 99.789 | 0.21103 | 0 | 99.789 | 0.21103 | 0
174 | 5 | June | 6.7 | 8.2487 | 761.6 | 29.106 | 790.706 | 0 | 790.706 | 0 | 0 | 96.319 | 3.681 | 0 | 96.319 | 3.681 | 0
174 | 6 | June | 5.7 | 7.0175 | 504.9 | 141.4583 | 646.3583 | 0 | 646.3583 | 0 | 0 | 78.1146 | 21.8854 | 0 | 78.1146 | 21.8854 | 0
174 | 7 | June | 7.7 | 9.4798 | 1059.95 | 301.1871 | 1361.1371 | 0 | 1361.1371 | 0 | 0 | 77.8724 | 22.1276 | 0 | 77.8724 | 22.1276 | 0
174 | 8 | June | 9.8 | 12.0652 | 1683.85 | 360.3053 | 2044.1553 | 1 | 2000 | 44.1553 | 2.2078 | 82.3739 | 15.8075 | 12.255 | 81.9847 | 17.6261 | 2.6223
174 | 9 | June | 10.3 | 12.6808 | 1694.9 | 486.8372 | 2181.7372 | 1 | 2000 | 181.7372 | 9.0869 | 77.6858 | 15.255 | 37.3302 | 75.6581 | 22.3142 | 10.7226
174 | 10 | June | 9.3 | 11.4496 | 1598.85 | 588.3274 | 2187.1774 | 1 | 2000 | 187.1774 | 9.3589 | 73.1011 | 20.0575 | 31.8152 | 70.5836 | 26.8989 | 11.707
174 | 11 | June | 9.8 | 12.0652 | 1683.85 | 642.4209 | 2326.2709 | 1 | 2000 | 326.2709 | 16.3135 | 72.3841 | 15.8075 | 50.7877 | 67.879 | 27.6159 | 19.3765
174 | 12 | June | 9.3 | 11.4496 | 1598.85 | 413.0336 | 2011.8836 | 1 | 2000 | 11.8836 | 0.59418 | 79.4703 | 20.0575 | 2.8771 | 79.3483 | 20.5297 | 0.74326
174 | 13 | June | 9.8 | 12.0652 | 1683.85 | 405.893 | 2089.743 | 1 | 2000 | 89.743 | 4.4872 | 80.5769 | 15.8075 | 22.11 | 79.7053 | 19.4231 | 5.3296
174 | 14 | June | 8.7 | 10.711 | 1490.05 | 381.3736 | 1871.4236 | 0 | 1871.4236 | 0 | 0 | 79.6212 | 20.3788 | 0 | 79.6212 | 20.3788 | 0
174 | 15 | June | 8.2 | 10.0954 | 1359.15 | 554.5367 | 1913.6867 | 0 | 1913.6867 | 0 | 0 | 71.0226 | 28.9774 | 0 | 71.0226 | 28.9774 | 0
174 | 16 | June | 8.7 | 10.711 | 1490.05 | 574.1978 | 2064.2478 | 1 | 2000 | 64.2478 | 3.2124 | 72.1837 | 25.4975 | 11.1891 | 71.2901 | 27.8163 | 4.3118
174 | 17 | June | 8.2 | 10.0954 | 1359.15 | 405.3635 | 1764.5135 | 0 | 1764.5135 | 0 | 0 | 77.0269 | 22.9731 | 0 | 77.0269 | 22.9731 | 0
174 | 18 | June | 7.7 | 9.4798 | 1059.95 | 251.6993 | 1311.6493 | 0 | 1311.6493 | 0 | 0 | 80.8105 | 19.1895 | 0 | 80.8105 | 19.1895 | 0
174 | 19 | June | 6.2 | 7.6331 | 625.6 | 121.716 | 747.316 | 0 | 747.316 | 0 | 0 | 83.7129 | 16.2871 | 0 | 83.7129 | 16.2871 | 0
174 | 20 | June | 4.1 | 5.0477 | 173.4 | 37.044 | 210.444 | 0 | 210.444 | 0 | 0 | 82.3972 | 17.6028 | 0 | 82.3972 | 17.6028 | 0
174 | 21 | June | 3.6 | 4.4321 | 75.65 | 1.323 | 76.973 | 0 | 76.973 | 0 | 0 | 98.2812 | 1.7188 | 0 | 98.2812 | 1.7188 | 0
174 | 22 | June | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
174 | 23 | June | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
174 | 24 | June | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
175 | 1 | June | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
175 | 2 | June | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
175 | 3 | June | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | 4 | June | 3.1 | 3.8165 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
175 | 5 | June | 4.1 | 5.0477 | 173.4 | 29.106 | 202.506 | 0 | 202.506 | 0 | 0 | 85.6271 | 14.3729 | 0 | 85.6271 | 14.3729 | 0
175 | 6 | June | 3.1 | 3.8165 | 0 | 141.3782 | 141.3782 | 0 | 141.3782 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
175 | 7 | June | 4.1 | 5.0477 | 173.4 | 438.289 | 611.689 | 0 | 611.689 | 0 | 0 | 28.3477 | 71.6523 | 0 | 28.3477 | 71.6523 | 0
175 | 8 | June | 5.7 | 7.0175 | 504.9 | 364.163 | 869.063 | 0 | 869.063 | 0 | 0 | 58.0971 | 41.9029 | 0 | 58.0971 | 41.9029 | 0
175 | 9 | June | 5.1 | 6.2788 | 312.8 | 489.2977 | 802.0977 | 0 | 802.0977 | 0 | 0 | 38.9977 | 61.0023 | 0 | 38.9977 | 61.0023 | 0
175 | 10 | June | 5.7 | 7.0175 | 504.9 | 1106.1358 | 1611.0358 | 0 | 1611.0358 | 0 | 0 | 31.3401 | 68.6599 | 0 | 31.3401 | 68.6599 | 0
175 | 11 | June | 5.7 | 7.0175 | 504.9 | 922.0379 | 1426.9379 | 0 | 1426.9379 | 0 | 0 | 35.3835 | 64.6165 | 0 | 35.3835 | 64.6165 | 0
175 | 12 | June | 5.7 | 7.0175 | 504.9 | 908.0368 | 1412.9368 | 0 | 1412.9368 | 0 | 0 | 35.7341 | 64.2659 | 0 | 35.7341 | 64.2659 | 0
175 | 13 | June | 4.1 | 5.0477 | 173.4 | 894.7678 | 1068.1678 | 0 | 1068.1678 | 0 | 0 | 16.2334 | 83.7666 | 0 | 16.2334 | 83.7666 | 0
175 | 14 | June | 5.1 | 6.2788 | 312.8 | 1048.7889 | 1361.5889 | 0 | 1361.5889 | 0 | 0 | 22.9732 | 77.0268 | 0 | 22.9732 | 77.0268 | 0
175 | 15 | June | 3.1 | 3.8165 | 0 | 883.6188 | 883.6188 | 0 | 883.6188 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
175 | 16 | June | 3.6 | 4.4321 | 75.65 | 577.0756 | 652.7256 | 0 | 652.7256 | 0 | 0 | 11.5899 | 88.4101 | 0 | 11.5899 | 88.4101 | 0
175 | 17 | June | 3.1 | 3.8165 | 0 | 323.4642 | 323.4642 | 0 | 323.4642 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
175 | 18 | June | 4.6 | 5.6633 | 237.15 | 203.0144 | 440.1644 | 0 | 440.1644 | 0 | 0 | 53.8776 | 46.1224 | 0 | 53.8776 | 46.1224 | 0
175 | 19 | June | 4.1 | 5.0477 | 173.4 | 96.579 | 269.979 | 0 | 269.979 | 0 | 0 | 64.2272 | 35.7728 | 0 | 64.2272 | 35.7728 | 0
175 | 20 | June | 4.1 | 5.0477 | 173.4 | 19.845 | 193.245 | 0 | 193.245 | 0 | 0 | 89.7307 | 10.2693 | 0 | 89.7307 | 10.2693 | 0
175 | 21 | June | 4.1 | 5.0477 | 173.4 | 1.323 | 174.723 | 0 | 174.723 | 0 | 0 | 99.2428 | 0.7572 | 0 | 99.2428 | 0.7572 | 0
175 | 22 | June | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
175 | 23 | June | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
175 | 24 | June | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | 1 | June | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | 2 | June | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | 3 | June | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | 4 | June | 2.1 | 2.5854 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
176 | 5 | June | 2.6 | 3.201 | 0 | 18.522 | 18.522 | 0 | 18.522 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
176 | 6 | June | 3.6 | 4.4321 | 75.65 | 70.119 | 145.769 | 0 | 145.769 | 0 | 0 | 51.8972 | 48.1028 | 0 | 51.8972 | 48.1028 | 0
176 | 7 | June | 4.1 | 5.0477 | 173.4 | 140.238 | 313.638 | 0 | 313.638 | 0 | 0 | 55.2867 | 44.7133 | 0 | 55.2867 | 44.7133 | 0
176 | 8 | June | 4.6 | 5.6633 | 237.15 | 216.5867 | 453.7367 | 0 | 453.7367 | 0 | 0 | 52.266 | 47.734 | 0 | 52.266 | 47.734 | 0
176 | 9 | June | 4.6 | 5.6633 | 237.15 | 289.9495 | 527.0995 | 0 | 527.0995 | 0 | 0 | 44.9915 | 55.0085 | 0 | 44.9915 | 55.0085 | 0
176 | 10 | June | 5.7 | 7.0175 | 504.9 | 349.3092 | 854.2092 | 0 | 854.2092 | 0 | 0 | 59.1073 | 40.8927 | 0 | 59.1073 | 40.8927 | 0
176 | 11 | June | 4.6 | 5.6633 | 237.15 | 386.1188 | 623.2688 | 0 | 623.2688 | 0 | 0 | 38.0494 | 61.9506 | 0 | 38.0494 | 61.9506 | 0
176 | 12 | June | 5.1 | 6.2788 | 312.8 | 409.3317 | 722.1317 | 0 | 722.1317 | 0 | 0 | 43.3162 | 56.6838 | 0 | 43.3162 | 56.6838 | 0
176 | 13 | June | 4.6 | 5.6633 | 237.15 | 406.0552 | 643.2052 | 0 | 643.2052 | 0 | 0 | 36.87 | 63.13 | 0 | 36.87 | 63.13 | 0
176 | 14 | June | 6.7 | 8.2487 | 761.6 | 381.8064 | 1143.4064 | 0 | 1143.4064 | 0 | 0 | 66.608 | 33.392 | 0 | 66.608 | 33.392 | 0
176 | 15 | June | 6.2 | 7.6331 | 625.6 | 336.3299 | 961.9299 | 0 | 961.9299 | 0 | 0 | 65.0359 | 34.9641 | 0 | 65.0359 | 34.9641 | 0
176 | 16 | June | 5.7 | 7.0175 | 504.9 | 275.6781 | 780.5781 | 0 | 780.5781 | 0 | 0 | 64.6828 | 35.3172 | 0 | 64.6828 | 35.3172 | 0
176 | 17 | June | 6.2 | 7.6331 | 625.6 | 205.065 | 830.665 | 0 | 830.665 | 0 | 0 | 75.3132 | 24.6868 | 0 | 75.3132 | 24.6868 | 0
176 | 18 | June | 5.1 | 6.2788 | 312.8 | 129.654 | 442.454 | 0 | 442.454 | 0 | 0 | 70.6966 | 29.3034 | 0 | 70.6966 | 29.3034 | 0
176 | 19 | June | 5.1 | 6.2788 | 312.8 | 60.858 | 373.658 | 0 | 373.658 | 0 | 0 | 83.7129 | 16.2871 | 0 | 83.7129 | 16.2871 | 0
176 | 20 | June | 5.7 | 7.0175 | 504.9 | 13.23 | 518.13 | 0 | 518.13 | 0 | 0 | 97.4466 | 2.5534 | 0 | 97.4466 | 2.5534 | 0
176 | 21 | June | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
176 | 22 | June | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
176 | 23 | June | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
176 | 24 | June | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
177 | 1 | June | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
177 | 2 | June | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
177 | 3 | June | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
177 | 4 | June | 4.6 | 5.6633 | 237.15 | 1.323 | 238.473 | 0 | 238.473 | 0 | 0 | 99.4452 | 0.55478 | 0 | 99.4452 | 0.55478 | 0
177 | 5 | June | 4.6 | 5.6633 | 237.15 | 29.106 | 266.256 | 0 | 266.256 | 0 | 0 | 89.0684 | 10.9316 | 0 | 89.0684 | 10.9316 | 0
177 | 6 | June | 5.1 | 6.2788 | 312.8 | 68.796 | 381.596 | 0 | 381.596 | 0 | 0 | 81.9715 | 18.0285 | 0 | 81.9715 | 18.0285 | 0
177 | 7 | June | 5.7 | 7.0175 | 504.9 | 225.5389 | 730.4389 | 0 | 730.4389 | 0 | 0 | 69.1228 | 30.8772 | 0 | 69.1228 | 30.8772 | 0
177 | 8 | June | 5.7 | 7.0175 | 504.9 | 350.6851 | 855.5851 | 0 | 855.5851 | 0 | 0 | 59.0122 | 40.9878 | 0 | 59.0122 | 40.9878 | 0
177 | 9 | June | 6.2 | 7.6331 | 625.6 | 286.4192 | 912.0192 | 0 | 912.0192 | 0 | 0 | 68.595 | 31.405 | 0 | 68.595 | 31.405 | 0
177 | 10 | June | 6.7 | 8.2487 | 761.6 | 344.6559 | 1106.2559 | 0 | 1106.2559 | 0 | 0 | 68.8448 | 31.1552 | 0 | 68.8448 | 31.1552 | 0
177 | 11 | June | 7.2 | 8.8642 | 908.65 | 665.7951 | 1574.4451 | 0 | 1574.4451 | 0 | 0 | 57.7124 | 42.2876 | 0 | 57.7124 | 42.2876 | 0
177 | 12 | June | 8.2 | 10.0954 | 1359.15 | 414.8832 | 1774.0332 | 0 | 1774.0332 | 0 | 0 | 76.6136 | 23.3864 | 0 | 76.6136 | 23.3864 | 0
177 | 13 | June | 8.2 | 10.0954 | 1359.15 | 406.0592 | 1765.2092 | 0 | 1765.2092 | 0 | 0 | 76.9965 | 23.0035 | 0 | 76.9965 | 23.0035 | 0
177 | 14 | June | 8.2 | 10.0954 | 1359.15 | 380.4899 | 1739.6399 | 0 | 1739.6399 | 0 | 0 | 78.1282 | 21.8718 | 0 | 78.1282 | 21.8718 | 0
177 | 15 | June | 7.7 | 9.4798 | 1059.95 | 547.7155 | 1607.6655 | 0 | 1607.6655 | 0 | 0 | 65.931 | 34.069 | 0 | 65.931 | 34.069 | 0
177 | 16 | June | 7.2 | 8.8642 | 908.65 | 276.6452 | 1185.2952 | 0 | 1185.2952 | 0 | 0 | 76.6602 | 23.3398 | 0 | 76.6602 | 23.3398 | 0
177 | 17 | June | 8.2 | 10.0954 | 1359.15 | 203.742 | 1562.892 | 0 | 1562.892 | 0 | 0 | 86.9638 | 13.0362 | 0 | 86.9638 | 13.0362 | 0
177 | 18 | June | 8.7 | 10.711 | 1490.05 | 129.654 | 1619.704 | 0 | 1619.704 | 0 | 0 | 91.9952 | 8.0048 | 0 | 91.9952 | 8.0048 | 0
177 | 19 | June | 8.7 | 10.711 | 1490.05 | 60.858 | 1550.908 | 0 | 1550.908 | 0 | 0 | 96.076 | 3.924 | 0 | 96.076 | 3.924 | 0
177 | 20 | June | 9.8 | 12.0652 | 1683.85 | 13.23 | 1697.08 | 0 | 1697.08 | 0 | 0 | 99.2204 | 0.77957 | 0 | 99.2204 | 0.77957 | 0
177 | 21 | June | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
177 | 22 | June | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
177 | 23 | June | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
177 | 24 | June | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
178 | 1 | June | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
178 | 2 | June | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
178 | 3 | June | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
178 | 4 | June | 11.8 | 14.5275 | 1700 | 1.323 | 1701.323 | 0 | 1701.323 | 0 | 0 | 99.9222 | 0.077763 | 0 | 99.9222 | 0.077763 | 0
178 | 5 | June | 10.3 | 12.6808 | 1694.9 | 17.199 | 1712.099 | 0 | 1712.099 | 0 | 0 | 98.9954 | 1.0046 | 0 | 98.9954 | 1.0046 | 0
178 | 6 | June | 11.8 | 14.5275 | 1700 | 68.796 | 1768.796 | 0 | 1768.796 | 0 | 0 | 96.1106 | 3.8894 | 0 | 96.1106 | 3.8894 | 0
178 | 7 | June | 11.3 | 13.9119 | 1700 | 138.915 | 1838.915 | 0 | 1838.915 | 0 | 0 | 92.4458 | 7.5542 | 0 | 92.4458 | 7.5542 | 0
178 | 8 | June | 10.8 | 13.2964 | 1698.3 | 215.2613 | 1913.5613 | 0 | 1913.5613 | 0 | 0 | 88.7507 | 11.2493 | 0 | 88.7507 | 11.2493 | 0
178 | 9 | June | 11.3 | 13.9119 | 1700 | 286.5265 | 1986.5265 | 0 | 1986.5265 | 0 | 0 | 85.5765 | 14.4235 | 0 | 85.5765 | 14.4235 | 0
178 | 10 | June | 10.3 | 12.6808 | 1694.9 | 344.6516 | 2039.5516 | 1 | 2000 | 39.5516 | 1.9776 | 83.1016 | 15.255 | 11.4758 | 82.7674 | 16.8984 | 2.3336
178 | 11 | June | 10.8 | 13.2964 | 1698.3 | 386.1405 | 2084.4405 | 1 | 2000 | 84.4405 | 4.222 | 81.4751 | 15.085 | 21.8678 | 80.693 | 18.5249 | 4.9721
178 | 12 | June | 10.3 | 12.6808 | 1694.9 | 408.0095 | 2102.9095 | 1 | 2000 | 102.9095 | 5.1455 | 80.5979 | 15.255 | 25.2223 | 79.5995 | 19.4021 | 6.0717
178 | 13 | June | 9.3 | 11.4496 | 1598.85 | 406.0631 | 2004.9131 | 1 | 2000 | 4.9131 | 0.24566 | 79.7466 | 20.0575 | 1.2099 | 79.6968 | 20.2534 | 0.30729
178 | 14 | June | 9.3 | 11.4496 | 1598.85 | 380.4961 | 1979.3461 | 0 | 1979.3461 | 0 | 0 | 80.7767 | 19.2233 | 0 | 80.7767 | 19.2233 | 0
178 | 15 | June | 9.3 | 11.4496 | 1598.85 | 336.3406 | 1935.1906 | 0 | 1935.1906 | 0 | 0 | 82.6198 | 17.3802 | 0 | 82.6198 | 17.3802 | 0
178 | 16 | June | 7.2 | 8.8642 | 908.65 | 275.6868 | 1184.3368 | 0 | 1184.3368 | 0 | 0 | 76.7223 | 23.2777 | 0 | 76.7223 | 23.2777 | 0
178 | 17 | June | 6.7 | 8.2487 | 761.6 | 203.742 | 965.342 | 0 | 965.342 | 0 | 0 | 78.8943 | 21.1057 | 0 | 78.8943 | 21.1057 | 0
178 | 18 | June | 5.7 | 7.0175 | 504.9 | 129.654 | 634.554 | 0 | 634.554 | 0 | 0 | 79.5677 | 20.4323 | 0 | 79.5677 | 20.4323 | 0
178 | 19 | June | 5.7 | 7.0175 | 504.9 | 60.858 | 565.758 | 0 | 565.758 | 0 | 0 | 89.2431 | 10.7569 | 0 | 89.2431 | 10.7569 | 0
178 | 20 | June | 6.2 | 7.6331 | 625.6 | 13.23 | 638.83 | 0 | 638.83 | 0 | 0 | 97.929 | 2.071 | 0 | 97.929 | 2.071 | 0
178 | 21 | June | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
178 | 22 | June | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
178 | 23 | June | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
178 | 24 | June | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
179 | 1 | June | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
179 | 2 | June | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
179 | 3 | June | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
179 | 4 | June | 0 | 0 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
179 | 5 | June | 2.6 | 3.201 | 0 | 44.982 | 44.982 | 0 | 44.982 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
179 | 6 | June | 3.6 | 4.4321 | 75.65 | 180.1605 | 255.8105 | 0 | 255.8105 | 0 | 0 | 29.5727 | 70.4273 | 0 | 29.5727 | 70.4273 | 0
179 | 7 | June | 4.6 | 5.6633 | 237.15 | 417.3732 | 654.5232 | 0 | 654.5232 | 0 | 0 | 36.2325 | 63.7675 | 0 | 36.2325 | 63.7675 | 0
179 | 8 | June | 3.6 | 4.4321 | 75.65 | 737.0501 | 812.7001 | 0 | 812.7001 | 0 | 0 | 9.3085 | 90.6915 | 0 | 9.3085 | 90.6915 | 0
179 | 9 | June | 4.1 | 5.0477 | 173.4 | 644.4116 | 817.8116 | 0 | 817.8116 | 0 | 0 | 21.2029 | 78.7971 | 0 | 21.2029 | 78.7971 | 0
179 | 10 | June | 3.6 | 4.4321 | 75.65 | 780.9219 | 856.5719 | 0 | 856.5719 | 0 | 0 | 8.8317 | 91.1683 | 0 | 8.8317 | 91.1683 | 0
179 | 11 | June | 2.6 | 3.201 | 0 | 1374.0344 | 1374.0344 | 0 | 1374.0344 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
179 | 12 | June | 4.6 | 5.6633 | 237.15 | 1492.6494 | 1729.7994 | 0 | 1729.7994 | 0 | 0 | 13.7097 | 86.2903 | 0 | 13.7097 | 86.2903 | 0
179 | 13 | June | 3.1 | 3.8165 | 0 | 1472.7433 | 1472.7433 | 0 | 1472.7433 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
179 | 14 | June | 2.6 | 3.201 | 0 | 1159.4524 | 1159.4524 | 0 | 1159.4524 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
179 | 15 | June | 4.6 | 5.6633 | 237.15 | 869.8898 | 1107.0398 | 0 | 1107.0398 | 0 | 0 | 21.422 | 78.578 | 0 | 21.422 | 78.578 | 0
179 | 16 | June | 5.7 | 7.0175 | 504.9 | 572.3535 | 1077.2535 | 0 | 1077.2535 | 0 | 0 | 46.8692 | 53.1308 | 0 | 46.8692 | 53.1308 | 0
179 | 17 | June | 1.5 | 1.8467 | 0 | 320.7953 | 320.7953 | 0 | 320.7953 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
179 | 18 | June | 0 | 0 | 0 | 201.2971 | 201.2971 | 0 | 201.2971 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
179 | 19 | June | 0 | 0 | 0 | 115.101 | 115.101 | 0 | 115.101 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
179 | 20 | June | 3.6 | 4.4321 | 75.65 | 26.46 | 102.11 | 0 | 102.11 | 0 | 0 | 74.0868 | 25.9132 | 0 | 74.0868 | 25.9132 | 0
179 | 21 | June | 4.1 | 5.0477 | 173.4 | 1.323 | 174.723 | 0 | 174.723 | 0 | 0 | 99.2428 | 0.7572 | 0 | 99.2428 | 0.7572 | 0
179 | 22 | June | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
179 | 23 | June | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
179 | 24 | June | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
180 | 1 | June | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
180 | 2 | June | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
180 | 3 | June | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
180 | 4 | June | 0 | 0 | 0 | 2.646 | 2.646 | 0 | 2.646 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
180 | 5 | June | 0 | 0 | 0 | 46.305 | 46.305 | 0 | 46.305 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
180 | 6 | June | 1 | 1.2311 | 0 | 170.7638 | 170.7638 | 0 | 170.7638 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
180 | 7 | June | 1.5 | 1.8467 | 0 | 389.9047 | 389.9047 | 0 | 389.9047 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
180 | 8 | June | 2.6 | 3.201 | 0 | 351.1713 | 351.1713 | 0 | 351.1713 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
180 | 9 | June | 2.6 | 3.201 | 0 | 285.0794 | 285.0794 | 0 | 285.0794 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
180 | 10 | June | 4.1 | 5.0477 | 173.4 | 343.3199 | 516.7199 | 0 | 516.7199 | 0 | 0 | 33.5578 | 66.4422 | 0 | 33.5578 | 66.4422 | 0
180 | 11 | June | 3.1 | 3.8165 | 0 | 386.1342 | 386.1342 | 0 | 386.1342 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
180 | 12 | June | 4.1 | 5.0477 | 173.4 | 406.6873 | 580.0873 | 0 | 580.0873 | 0 | 0 | 29.8921 | 70.1079 | 0 | 29.8921 | 70.1079 | 0
180 | 13 | June | 5.7 | 7.0175 | 504.9 | 404.7477 | 909.6477 | 0 | 909.6477 | 0 | 0 | 55.505 | 44.495 | 0 | 55.505 | 44.495 | 0
180 | 14 | June | 6.2 | 7.6331 | 625.6 | 380.5081 | 1006.1081 | 0 | 1006.1081 | 0 | 0 | 62.1802 | 37.8198 | 0 | 62.1802 | 37.8198 | 0
180 | 15 | June | 6.7 | 8.2487 | 761.6 | 336.3504 | 1097.9504 | 0 | 1097.9504 | 0 | 0 | 69.3656 | 30.6344 | 0 | 69.3656 | 30.6344 | 0
180 | 16 | June | 6.2 | 7.6331 | 625.6 | 275.6946 | 901.2946 | 0 | 901.2946 | 0 | 0 | 69.4113 | 30.5887 | 0 | 69.4113 | 30.5887 | 0
180 | 17 | June | 5.7 | 7.0175 | 504.9 | 203.742 | 708.642 | 0 | 708.642 | 0 | 0 | 71.249 | 28.751 | 0 | 71.249 | 28.751 | 0
180 | 18 | June | 5.1 | 6.2788 | 312.8 | 129.654 | 442.454 | 0 | 442.454 | 0 | 0 | 70.6966 | 29.3034 | 0 | 70.6966 | 29.3034 | 0
180 | 19 | June | 6.2 | 7.6331 | 625.6 | 60.858 | 686.458 | 0 | 686.458 | 0 | 0 | 91.1345 | 8.8655 | 0 | 91.1345 | 8.8655 | 0
180 | 20 | June | 5.1 | 6.2788 | 312.8 | 13.23 | 326.03 | 0 | 326.03 | 0 | 0 | 95.9421 | 4.0579 | 0 | 95.9421 | 4.0579 | 0
180 | 21 | June | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
180 | 22 | June | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
180 | 23 | June | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
180 | 24 | June | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
181 | 1 | June | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
181 | 2 | June | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
181 | 3 | June | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
181 | 4 | June | 7.2 | 8.8642 | 908.65 | 1.323 | 909.973 | 0 | 909.973 | 0 | 0 | 99.8546 | 0.14539 | 0 | 99.8546 | 0.14539 | 0
181 | 5 | June | 6.2 | 7.6331 | 625.6 | 17.199 | 642.799 | 0 | 642.799 | 0 | 0 | 97.3244 | 2.6756 | 0 | 97.3244 | 2.6756 | 0
181 | 6 | June | 6.7 | 8.2487 | 761.6 | 67.473 | 829.073 | 0 | 829.073 | 0 | 0 | 91.8616 | 8.1384 | 0 | 91.8616 | 8.1384 | 0
181 | 7 | June | 6.2 | 7.6331 | 625.6 | 137.592 | 763.192 | 0 | 763.192 | 0 | 0 | 81.9715 | 18.0285 | 0 | 81.9715 | 18.0285 | 0
181 | 8 | June | 5.7 | 7.0175 | 504.9 | 212.6116 | 717.5116 | 0 | 717.5116 | 0 | 0 | 70.3682 | 29.6318 | 0 | 70.3682 | 29.6318 | 0
181 | 9 | June | 5.7 | 7.0175 | 504.9 | 285.1894 | 790.0894 | 0 | 790.0894 | 0 | 0 | 63.9042 | 36.0958 | 0 | 63.9042 | 36.0958 | 0
181 | 10 | June | 6.2 | 7.6331 | 625.6 | 343.3156 | 968.9156 | 0 | 968.9156 | 0 | 0 | 64.567 | 35.433 | 0 | 64.567 | 35.433 | 0
181 | 11 | June | 6.2 | 7.6331 | 625.6 | 386.1311 | 1011.7311 | 0 | 1011.7311 | 0 | 0 | 61.8346 | 38.1654 | 0 | 61.8346 | 38.1654 | 0
181 | 12 | June | 6.7 | 8.2487 | 761.6 | 406.6877 | 1168.2877 | 0 | 1168.2877 | 0 | 0 | 65.1894 | 34.8106 | 0 | 65.1894 | 34.8106 | 0
181 | 13 | June | 7.2 | 8.8642 | 908.65 | 404.7514 | 1313.4014 | 0 | 1313.4014 | 0 | 0 | 69.183 | 30.817 | 0 | 69.183 | 30.817 | 0
181 | 14 | June | 6.2 | 7.6331 | 625.6 | 380.5138 | 1006.1138 | 0 | 1006.1138 | 0 | 0 | 62.1798 | 37.8202 | 0 | 62.1798 | 37.8202 | 0
181 | 15 | June | 6.2 | 7.6331 | 625.6 | 336.8122 | 962.4122 | 0 | 962.4122 | 0 | 0 | 65.0033 | 34.9967 | 0 | 65.0033 | 34.9967 | 0
181 | 16 | June | 8.2 | 10.0954 | 1359.15 | 276.6386 | 1635.7886 | 0 | 1635.7886 | 0 | 0 | 83.0884 | 16.9116 | 0 | 83.0884 | 16.9116 | 0
181 | 17 | June | 7.7 | 9.4798 | 1059.95 | 205.6348 | 1265.5848 | 0 | 1265.5848 | 0 | 0 | 83.7518 | 16.2482 | 0 | 83.7518 | 16.2482 | 0
181 | 18 | June | 6.7 | 8.2487 | 761.6 | 129.654 | 891.254 | 0 | 891.254 | 0 | 0 | 85.4526 | 14.5474 | 0 | 85.4526 | 14.5474 | 0
181 | 19 | June | 6.7 | 8.2487 | 761.6 | 60.858 | 822.458 | 0 | 822.458 | 0 | 0 | 92.6005 | 7.3995 | 0 | 92.6005 | 7.3995 | 0
181 | 20 | June | 5.7 | 7.0175 | 504.9 | 19.845 | 524.745 | 0 | 524.745 | 0 | 0 | 96.2182 | 3.7818 | 0 | 96.2182 | 3.7818 | 0
181 | 21 | June | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
181 | 22 | June | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
181 | 23 | June | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
181 | 24 | June | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
182 | 1 | July | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
182 | 2 | July | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
182 | 3 | July | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
182 | 4 | July | 1 | 1.2311 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
182 | 5 | July | 1.5 | 1.8467 | 0 | 33.075 | 33.075 | 0 | 33.075 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
182 | 6 | July | 1.5 | 1.8467 | 0 | 104.517 | 104.517 | 0 | 104.517 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
182 | 7 | July | 2.1 | 2.5854 | 0 | 217.927 | 217.927 | 0 | 217.927 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
182 | 8 | July | 2.1 | 2.5854 | 0 | 209.9643 | 209.9643 | 0 | 209.9643 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
182 | 9 | July | 3.1 | 3.8165 | 0 | 469.9025 | 469.9025 | 0 | 469.9025 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
182 | 10 | July | 4.1 | 5.0477 | 173.4 | 780.0738 | 953.4738 | 0 | 953.4738 | 0 | 0 | 18.1861 | 81.8139 | 0 | 18.1861 | 81.8139 | 0
182 | 11 | July | 3.6 | 4.4321 | 75.65 | 650.9942 | 726.6442 | 0 | 726.6442 | 0 | 0 | 10.4109 | 89.5891 | 0 | 10.4109 | 89.5891 | 0
182 | 12 | July | 3.1 | 3.8165 | 0 | 939.0166 | 939.0166 | 0 | 939.0166 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
182 | 13 | July | 3.6 | 4.4321 | 75.65 | 1111.5259 | 1187.1759 | 0 | 1187.1759 | 0 | 0 | 6.3723 | 93.6277 | 0 | 6.3723 | 93.6277 | 0
182 | 14 | July | 2.6 | 3.201 | 0 | 853.7212 | 853.7212 | 0 | 853.7212 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
182 | 15 | July | 0 | 0 | 0 | 546.0636 | 546.0636 | 0 | 546.0636 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
182 | 16 | July | 0 | 0 | 0 | 438.9206 | 438.9206 | 0 | 438.9206 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
182 | 17 | July | 2.6 | 3.201 | 0 | 319.3274 | 319.3274 | 0 | 319.3274 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
182 | 18 | July | 5.1 | 6.2788 | 312.8 | 198.4606 | 511.2606 | 0 | 511.2606 | 0 | 0 | 61.1821 | 38.8179 | 0 | 61.1821 | 38.8179 | 0
182 | 19 | July | 3.1 | 3.8165 | 0 | 93.933 | 93.933 | 0 | 93.933 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
182 | 20 | July | 1 | 1.2311 | 0 | 19.845 | 19.845 | 0 | 19.845 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
182 | 21 | July | 0.5 | 0.61557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
182 | 22 | July | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
182 | 23 | July | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
182 | 24 | July | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
183 | 1 | July | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
183 | 2 | July | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
183 | 3 | July | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
183 | 4 | July | 0 | 0 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
183 | 5 | July | 0 | 0 | 0 | 41.013 | 41.013 | 0 | 41.013 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
183 | 6 | July | 0 | 0 | 0 | 164.0955 | 164.0955 | 0 | 164.0955 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
183 | 7 | July | 0 | 0 | 0 | 381.141 | 381.141 | 0 | 381.141 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
183 | 8 | July | 2.1 | 2.5854 | 0 | 692.4707 | 692.4707 | 0 | 692.4707 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
183 | 9 | July | 2.6 | 3.201 | 0 | 983.435 | 983.435 | 0 | 983.435 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
183 | 10 | July | 2.6 | 3.201 | 0 | 1205.7722 | 1205.7722 | 0 | 1205.7722 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
183 | 11 | July | 4.1 | 5.0477 | 173.4 | 1363.4867 | 1536.8867 | 0 | 1536.8867 | 0 | 0 | 11.2825 | 88.7175 | 0 | 11.2825 | 88.7175 | 0
183 | 12 | July | 4.6 | 5.6633 | 237.15 | 1476.3508 | 1713.5008 | 0 | 1713.5008 | 0 | 0 | 13.8401 | 86.1599 | 0 | 13.8401 | 86.1599 | 0
183 | 13 | July | 4.6 | 5.6633 | 237.15 | 1377.1514 | 1614.3014 | 0 | 1614.3014 | 0 | 0 | 14.6906 | 85.3094 | 0 | 14.6906 | 85.3094 | 0
183 | 14 | July | 4.6 | 5.6633 | 237.15 | 1255.1759 | 1492.3259 | 0 | 1492.3259 | 0 | 0 | 15.8913 | 84.1087 | 0 | 15.8913 | 84.1087 | 0
183 | 15 | July | 4.1 | 5.0477 | 173.4 | 718.6964 | 892.0964 | 0 | 892.0964 | 0 | 0 | 19.4374 | 80.5626 | 0 | 19.4374 | 80.5626 | 0
183 | 16 | July | 3.9 | 4.8015 | 120.7 | 623.3053 | 744.0053 | 0 | 744.0053 | 0 | 0 | 16.223 | 83.777 | 0 | 16.223 | 83.777 | 0
183 | 17 | July | 3.6 | 4.4321 | 75.65 | 447.4555 | 523.1055 | 0 | 523.1055 | 0 | 0 | 14.4617 | 85.5383 | 0 | 14.4617 | 85.5383 | 0
183 | 18 | July | 3.1 | 3.8165 | 0 | 197.1496 | 197.1496 | 0 | 197.1496 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
183 | 19 | July | 2.1 | 2.5854 | 0 | 113.778 | 113.778 | 0 | 113.778 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
183 | 20 | July | 2.1 | 2.5854 | 0 | 34.398 | 34.398 | 0 | 34.398 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
183 | 21 | July | 2.1 | 2.5854 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
183 | 22 | July | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
183 | 23 | July | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
183 | 24 | July | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
184 | 1 | July | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
184 | 2 | July | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
184 | 3 | July | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
184 | 4 | July | 3.1 | 3.8165 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
184 | 5 | July | 1 | 1.2311 | 0 | 43.659 | 43.659 | 0 | 43.659 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
184 | 6 | July | 1 | 1.2311 | 0 | 167.6457 | 167.6457 | 0 | 167.6457 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
184 | 7 | July | 2.6 | 3.201 | 0 | 416.624 | 416.624 | 0 | 416.624 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
184 | 8 | July | 2.1 | 2.5854 | 0 | 724.9174 | 724.9174 | 0 | 724.9174 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
184 | 9 | July | 2.6 | 3.201 | 0 | 468.4518 | 468.4518 | 0 | 468.4518 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
184 | 10 | July | 3.1 | 3.8165 | 0 | 340.7489 | 340.7489 | 0 | 340.7489 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
184 | 11 | July | 3.6 | 4.4321 | 75.65 | 383.4759 | 459.1259 | 0 | 459.1259 | 0 | 0 | 16.477 | 83.523 | 0 | 16.477 | 83.523 | 0
184 | 12 | July | 3.6 | 4.4321 | 75.65 | 691.6491 | 767.2991 | 0 | 767.2991 | 0 | 0 | 9.8593 | 90.1407 | 0 | 9.8593 | 90.1407 | 0
184 | 13 | July | 4.1 | 5.0477 | 173.4 | 1353.0259 | 1526.4259 | 0 | 1526.4259 | 0 | 0 | 11.3599 | 88.6401 | 0 | 11.3599 | 88.6401 | 0
184 | 14 | July | 4.1 | 5.0477 | 173.4 | 1323.8091 | 1497.2091 | 0 | 1497.2091 | 0 | 0 | 11.5815 | 88.4185 | 0 | 11.5815 | 88.4185 | 0
184 | 15 | July | 5.1 | 6.2788 | 312.8 | 1093.3994 | 1406.1994 | 0 | 1406.1994 | 0 | 0 | 22.2444 | 77.7556 | 0 | 22.2444 | 77.7556 | 0
184 | 16 | July | 5.7 | 7.0175 | 504.9 | 811.1175 | 1316.0175 | 0 | 1316.0175 | 0 | 0 | 38.3657 | 61.6343 | 0 | 38.3657 | 61.6343 | 0
184 | 17 | July | 5.7 | 7.0175 | 504.9 | 507.5121 | 1012.4121 | 0 | 1012.4121 | 0 | 0 | 49.871 | 50.129 | 0 | 49.871 | 50.129 | 0
184 | 18 | July | 5.1 | 6.2788 | 312.8 | 244.8215 | 557.6215 | 0 | 557.6215 | 0 | 0 | 56.0954 | 43.9046 | 0 | 56.0954 | 43.9046 | 0
184 | 19 | July | 5.1 | 6.2788 | 312.8 | 111.132 | 423.932 | 0 | 423.932 | 0 | 0 | 73.7854 | 26.2146 | 0 | 73.7854 | 26.2146 | 0
184 | 20 | July | 4.1 | 5.0477 | 173.4 | 34.398 | 207.798 | 0 | 207.798 | 0 | 0 | 83.4464 | 16.5536 | 0 | 83.4464 | 16.5536 | 0
184 | 21 | July | 3.6 | 4.4321 | 75.65 | 1.323 | 76.973 | 0 | 76.973 | 0 | 0 | 98.2812 | 1.7188 | 0 | 98.2812 | 1.7188 | 0
184 | 22 | July | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
184 | 23 | July | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
184 | 24 | July | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
185 | 1 | July | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
185 | 2 | July | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
185 | 3 | July | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
185 | 4 | July | 4.1 | 5.0477 | 173.4 | 1.323 | 174.723 | 0 | 174.723 | 0 | 0 | 99.2428 | 0.7572 | 0 | 99.2428 | 0.7572 | 0
185 | 5 | July | 3.6 | 4.4321 | 75.65 | 42.336 | 117.986 | 0 | 117.986 | 0 | 0 | 64.1178 | 35.8822 | 0 | 64.1178 | 35.8822 | 0
185 | 6 | July | 4.6 | 5.6633 | 237.15 | 166.1582 | 403.3082 | 0 | 403.3082 | 0 | 0 | 58.8012 | 41.1988 | 0 | 58.8012 | 41.1988 | 0
185 | 7 | July | 4.6 | 5.6633 | 237.15 | 414.6525 | 651.8025 | 0 | 651.8025 | 0 | 0 | 36.3837 | 63.6163 | 0 | 36.3837 | 63.6163 | 0
185 | 8 | July | 5.1 | 6.2788 | 312.8 | 728.8897 | 1041.6897 | 0 | 1041.6897 | 0 | 0 | 30.0281 | 69.9719 | 0 | 30.0281 | 69.9719 | 0
185 | 9 | July | 6.2 | 7.6331 | 625.6 | 1036.6415 | 1662.2415 | 0 | 1662.2415 | 0 | 0 | 37.6359 | 62.3641 | 0 | 37.6359 | 62.3641 | 0
185 | 10 | July | 6.2 | 7.6331 | 625.6 | 1276.3915 | 1901.9915 | 0 | 1901.9915 | 0 | 0 | 32.8918 | 67.1082 | 0 | 32.8918 | 67.1082 | 0
185 | 11 | July | 6.2 | 7.6331 | 625.6 | 1447.1174 | 2072.7174 | 1 | 2000 | 72.7174 | 3.6359 | 30.1826 | 68.72 | 5.025 | 27.6441 | 69.8174 | 11.6236
185 | 12 | July | 6.2 | 7.6331 | 625.6 | 1507.0776 | 2132.6776 | 1 | 2000 | 132.6776 | 6.6339 | 29.334 | 68.72 | 8.8036 | 24.6461 | 70.666 | 21.208
185 | 13 | July | 5.7 | 7.0175 | 504.9 | 1462.1487 | 1967.0487 | 0 | 1967.0487 | 0 | 0 | 25.6679 | 74.3321 | 0 | 25.6679 | 74.3321 | 0
185 | 14 | July | 6.2 | 7.6331 | 625.6 | 1244.7209 | 1870.3209 | 0 | 1870.3209 | 0 | 0 | 33.4488 | 66.5512 | 0 | 33.4488 | 66.5512 | 0
185 | 15 | July | 5.1 | 6.2788 | 312.8 | 965.2874 | 1278.0874 | 0 | 1278.0874 | 0 | 0 | 24.4741 | 75.5259 | 0 | 24.4741 | 75.5259 | 0
185 | 16 | July | 4.6 | 5.6633 | 237.15 | 735.5496 | 972.6996 | 0 | 972.6996 | 0 | 0 | 24.3806 | 75.6194 | 0 | 24.3806 | 75.6194 | 0
185 | 17 | July | 5.1 | 6.2788 | 312.8 | 395.9472 | 708.7472 | 0 | 708.7472 | 0 | 0 | 44.1342 | 55.8658 | 0 | 44.1342 | 55.8658 | 0
185 | 18 | July | 4.6 | 5.6633 | 237.15 | 230.784 | 467.934 | 0 | 467.934 | 0 | 0 | 50.6802 | 49.3198 | 0 | 50.6802 | 49.3198 | 0
185 | 19 | July | 4.6 | 5.6633 | 237.15 | 125.685 | 362.835 | 0 | 362.835 | 0 | 0 | 65.3603 | 34.6397 | 0 | 65.3603 | 34.6397 | 0
185 | 20 | July | 4.6 | 5.6633 | 237.15 | 18.522 | 255.672 | 0 | 255.672 | 0 | 0 | 92.7556 | 7.2444 | 0 | 92.7556 | 7.2444 | 0
185 | 21 | July | 5.1 | 6.2788 | 312.8 | 1.323 | 314.123 | 0 | 314.123 | 0 | 0 | 99.5788 | 0.42117 | 0 | 99.5788 | 0.42117 | 0
185 | 22 | July | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
185 | 23 | July | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
185 | 24 | July | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
186 | 1 | July | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
186 | 2 | July | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
186 | 3 | July | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
186 | 4 | July | 3.1 | 3.8165 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
186 | 5 | July | 2.1 | 2.5854 | 0 | 39.69 | 39.69 | 0 | 39.69 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
186 | 6 | July | 1 | 1.2311 | 0 | 164.1726 | 164.1726 | 0 | 164.1726 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
186 | 7 | July | 0 | 0 | 0 | 411.1113 | 411.1113 | 0 | 411.1113 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
186 | 8 | July | 2.1 | 2.5854 | 0 | 687.8104 | 687.8104 | 0 | 687.8104 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
186 | 9 | July | 3.1 | 3.8165 | 0 | 774.9386 | 774.9386 | 0 | 774.9386 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
186 | 10 | July | 3.6 | 4.4321 | 75.65 | 567.2735 | 642.9235 | 0 | 642.9235 | 0 | 0 | 11.7666 | 88.2334 | 0 | 11.7666 | 88.2334 | 0
186 | 11 | July | 3.6 | 4.4321 | 75.65 | 624.1222 | 699.7722 | 0 | 699.7722 | 0 | 0 | 10.8107 | 89.1893 | 0 | 10.8107 | 89.1893 | 0
186 | 12 | July | 3.6 | 4.4321 | 75.65 | 925.8137 | 1001.4637 | 0 | 1001.4637 | 0 | 0 | 7.5539 | 92.4461 | 0 | 7.5539 | 92.4461 | 0
186 | 13 | July | 3.1 | 3.8165 | 0 | 666.0145 | 666.0145 | 0 | 666.0145 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
186 | 14 | July | 1 | 1.2311 | 0 | 608.9491 | 608.9491 | 0 | 608.9491 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
186 | 15 | July | 2.6 | 3.201 | 0 | 851.4409 | 851.4409 | 0 | 851.4409 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
186 | 16 | July | 4.6 | 5.6633 | 237.15 | 564.4218 | 801.5718 | 0 | 801.5718 | 0 | 0 | 29.5856 | 70.4144 | 0 | 29.5856 | 70.4144 | 0
186 | 17 | July | 4.6 | 5.6633 | 237.15 | 311.6488 | 548.7988 | 0 | 548.7988 | 0 | 0 | 43.2126 | 56.7874 | 0 | 43.2126 | 56.7874 | 0
186 | 18 | July | 4.1 | 5.0477 | 173.4 | 196.9306 | 370.3306 | 0 | 370.3306 | 0 | 0 | 46.823 | 53.177 | 0 | 46.823 | 53.177 | 0
186 | 19 | July | 1.5 | 1.8467 | 0 | 92.61 | 92.61 | 0 | 92.61 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
186 | 20 | July | 0 | 0 | 0 | 18.522 | 18.522 | 0 | 18.522 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
186 | 21 | July | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
186 | 22 | July | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
186 | 23 | July | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
186 | 24 | July | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
187 | 1 | July | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
187 | 2 | July | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
187 | 3 | July | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
187 | 4 | July | 5.1 | 6.2788 | 312.8 | 1.323 | 314.123 | 0 | 314.123 | 0 | 0 | 99.5788 | 0.42117 | 0 | 99.5788 | 0.42117 | 0
187 | 5 | July | 5.1 | 6.2788 | 312.8 | 38.367 | 351.167 | 0 | 351.167 | 0 | 0 | 89.0744 | 10.9256 | 0 | 89.0744 | 10.9256 | 0
187 | 6 | July | 5.1 | 6.2788 | 312.8 | 99.225 | 412.025 | 0 | 412.025 | 0 | 0 | 75.9177 | 24.0823 | 0 | 75.9177 | 24.0823 | 0
187 | 7 | July | 6.2 | 7.6331 | 625.6 | 395.2027 | 1020.8027 | 0 | 1020.8027 | 0 | 0 | 61.2851 | 38.7149 | 0 | 61.2851 | 38.7149 | 0
187 | 8 | July | 6.7 | 8.2487 | 761.6 | 719.3548 | 1480.9548 | 0 | 1480.9548 | 0 | 0 | 51.4263 | 48.5737 | 0 | 51.4263 | 48.5737 | 0
187 | 9 | July | 7.2 | 8.8642 | 908.65 | 902.9387 | 1811.5887 | 0 | 1811.5887 | 0 | 0 | 50.1576 | 49.8424 | 0 | 50.1576 | 49.8424 | 0
187 | 10 | July | 6.2 | 7.6331 | 625.6 | 1104.7456 | 1730.3456 | 0 | 1730.3456 | 0 | 0 | 36.1546 | 63.8454 | 0 | 36.1546 | 63.8454 | 0
187 | 11 | July | 6.7 | 8.2487 | 761.6 | 1335.9349 | 2097.5349 | 1 | 2000 | 97.5349 | 4.8767 | 36.3093 | 61.92 | 7.3009 | 33.2033 | 63.6907 | 12.8066
187 | 12 | July | 6.7 | 8.2487 | 761.6 | 1156.7984 | 1918.3984 | 0 | 1918.3984 | 0 | 0 | 39.6998 | 60.3002 | 0 | 39.6998 | 60.3002 | 0
187 | 13 | July | 6.2 | 7.6331 | 625.6 | 1355.7149 | 1981.3149 | 0 | 1981.3149 | 0 | 0 | 31.575 | 68.425 | 0 | 31.575 | 68.425 | 0
187 | 14 | July | 6.7 | 8.2487 | 761.6 | 1037.2456 | 1798.8456 | 0 | 1798.8456 | 0 | 0 | 42.3383 | 57.6617 | 0 | 42.3383 | 57.6617 | 0
187 | 15 | July | 6.7 | 8.2487 | 761.6 | 726.3919 | 1487.9919 | 0 | 1487.9919 | 0 | 0 | 51.1831 | 48.8169 | 0 | 51.1831 | 48.8169 | 0
187 | 16 | July | 5.1 | 6.2788 | 312.8 | 571.899 | 884.699 | 0 | 884.699 | 0 | 0 | 35.3567 | 64.6433 | 0 | 35.3567 | 64.6433 | 0
187 | 17 | July | 4.1 | 5.0477 | 173.4 | 318.1322 | 491.5322 | 0 | 491.5322 | 0 | 0 | 35.2774 | 64.7226 | 0 | 35.2774 | 64.7226 | 0
187 | 18 | July | 3.1 | 3.8165 | 0 | 197.1517 | 197.1517 | 0 | 197.1517 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
187 | 19 | July | 1.5 | 1.8467 | 0 | 92.61 | 92.61 | 0 | 92.61 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
187 | 20 | July | 1 | 1.2311 | 0 | 27.783 | 27.783 | 0 | 27.783 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
187 | 21 | July | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
187 | 22 | July | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
187 | 23 | July | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
187 | 24 | July | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
188 | 1 | July | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
188 | 2 | July | 2.3 | 2.8316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
188 | 3 | July | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
188 | 4 | July | 2.6 | 3.201 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
188 | 5 | July | 1 | 1.2311 | 0 | 38.367 | 38.367 | 0 | 38.367 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
188 | 6 | July | 2.6 | 3.201 | 0 | 163.3142 | 163.3142 | 0 | 163.3142 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
188 | 7 | July | 2.6 | 3.201 | 0 | 408.9357 | 408.9357 | 0 | 408.9357 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
188 | 8 | July | 2.6 | 3.201 | 0 | 718.3792 | 718.3792 | 0 | 718.3792 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
188 | 9 | July | 2.1 | 2.5854 | 0 | 1013.8168 | 1013.8168 | 0 | 1013.8168 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
188 | 10 | July | 3.6 | 4.4321 | 75.65 | 1207.0351 | 1282.6851 | 0 | 1282.6851 | 0 | 0 | 5.8978 | 94.1022 | 0 | 5.8978 | 94.1022 | 0
188 | 11 | July | 4.1 | 5.0477 | 173.4 | 1408.651 | 1582.051 | 0 | 1582.051 | 0 | 0 | 10.9605 | 89.0395 | 0 | 10.9605 | 89.0395 | 0
188 | 12 | July | 5.1 | 6.2788 | 312.8 | 1508.4299 | 1821.2299 | 0 | 1821.2299 | 0 | 0 | 17.1752 | 82.8248 | 0 | 17.1752 | 82.8248 | 0
188 | 13 | July | 5.7 | 7.0175 | 504.9 | 1445.2519 | 1950.1519 | 0 | 1950.1519 | 0 | 0 | 25.8903 | 74.1097 | 0 | 25.8903 | 74.1097 | 0
188 | 14 | July | 4.6 | 5.6633 | 237.15 | 1253.2615 | 1490.4115 | 0 | 1490.4115 | 0 | 0 | 15.9117 | 84.0883 | 0 | 15.9117 | 84.0883 | 0
188 | 15 | July | 3.6 | 4.4321 | 75.65 | 1088.5905 | 1164.2405 | 0 | 1164.2405 | 0 | 0 | 6.4978 | 93.5022 | 0 | 6.4978 | 93.5022 | 0
188 | 16 | July | 2.6 | 3.201 | 0 | 805.4486 | 805.4486 | 0 | 805.4486 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
188 | 17 | July | 3.6 | 4.4321 | 75.65 | 511.6237 | 587.2737 | 0 | 587.2737 | 0 | 0 | 12.8816 | 87.1184 | 0 | 12.8816 | 87.1184 | 0
188 | 18 | July | 3.6 | 4.4321 | 75.65 | 250.9785 | 326.6285 | 0 | 326.6285 | 0 | 0 | 23.1609 | 76.8391 | 0 | 23.1609 | 76.8391 | 0
188 | 19 | July | 3.1 | 3.8165 | 0 | 119.07 | 119.07 | 0 | 119.07 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
188 | 20 | July | 3.1 | 3.8165 | 0 | 31.752 | 31.752 | 0 | 31.752 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
188 | 21 | July | 2.6 | 3.201 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
188 | 22 | July | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
188 | 23 | July | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
188 | 24 | July | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
189 | 1 | July | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
189 | 2 | July | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
189 | 3 | July | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
189 | 4 | July | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
189 | 5 | July | 2.1 | 2.5854 | 0 | 13.23 | 13.23 | 0 | 13.23 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
189 | 6 | July | 2.6 | 3.201 | 0 | 60.858 | 60.858 | 0 | 60.858 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
189 | 7 | July | 3.1 | 3.8165 | 0 | 214.011 | 214.011 | 0 | 214.011 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
189 | 8 | July | 5.1 | 6.2788 | 312.8 | 207.309 | 520.109 | 0 | 520.109 | 0 | 0 | 60.1412 | 39.8588 | 0 | 60.1412 | 39.8588 | 0
189 | 9 | July | 5.7 | 7.0175 | 504.9 | 279.3644 | 784.2644 | 0 | 784.2644 | 0 | 0 | 64.3788 | 35.6212 | 0 | 64.3788 | 35.6212 | 0
189 | 10 | July | 4.1 | 5.0477 | 173.4 | 341.1701 | 514.5701 | 0 | 514.5701 | 0 | 0 | 33.698 | 66.302 | 0 | 33.698 | 66.302 | 0
189 | 11 | July | 5.1 | 6.2788 | 312.8 | 380.8147 | 693.6147 | 0 | 693.6147 | 0 | 0 | 45.0971 | 54.9029 | 0 | 45.0971 | 54.9029 | 0
189 | 12 | July | 4.1 | 5.0477 | 173.4 | 690.5974 | 863.9974 | 0 | 863.9974 | 0 | 0 | 20.0695 | 79.9305 | 0 | 20.0695 | 79.9305 | 0
189 | 13 | July | 5.1 | 6.2788 | 312.8 | 924.8727 | 1237.6727 | 0 | 1237.6727 | 0 | 0 | 25.2732 | 74.7268 | 0 | 25.2732 | 74.7268 | 0
189 | 14 | July | 5.1 | 6.2788 | 312.8 | 1145.2477 | 1458.0477 | 0 | 1458.0477 | 0 | 0 | 21.4533 | 78.5467 | 0 | 21.4533 | 78.5467 | 0
189 | 15 | July | 3.6 | 4.4321 | 75.65 | 715.3541 | 791.0041 | 0 | 791.0041 | 0 | 0 | 9.5638 | 90.4362 | 0 | 9.5638 | 90.4362 | 0
189 | 16 | July | 2.6 | 3.201 | 0 | 437.4156 | 437.4156 | 0 | 437.4156 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
189 | 17 | July | 1 | 1.2311 | 0 | 316.7404 | 316.7404 | 0 | 316.7404 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
189 | 18 | July | 3.1 | 3.8165 | 0 | 195.6003 | 195.6003 | 0 | 195.6003 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
189 | 19 | July | 2.3 | 2.8316 | 0 | 91.287 | 91.287 | 0 | 91.287 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
189 | 20 | July | 1.5 | 1.8467 | 0 | 17.199 | 17.199 | 0 | 17.199 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
189 | 21 | July | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
189 | 22 | July | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
189 | 23 | July | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
189 | 24 | July | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
190 | 1 | July | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
190 | 2 | July | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
190 | 3 | July | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
190 | 4 | July | 3.1 | 3.8165 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
190 | 5 | July | 2.1 | 2.5854 | 0 | 33.075 | 33.075 | 0 | 33.075 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
190 | 6 | July | 3.1 | 3.8165 | 0 | 137.6091 | 137.6091 | 0 | 137.6091 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
190 | 7 | July | 5.1 | 6.2788 | 312.8 | 270.7738 | 583.5738 | 0 | 583.5738 | 0 | 0 | 53.6008 | 46.3992 | 0 | 53.6008 | 46.3992 | 0
190 | 8 | July | 7.2 | 8.8642 | 908.65 | 611.3739 | 1520.0239 | 0 | 1520.0239 | 0 | 0 | 59.7787 | 40.2213 | 0 | 59.7787 | 40.2213 | 0
190 | 9 | July | 7.7 | 9.4798 | 1059.95 | 460.2495 | 1520.1995 | 0 | 1520.1995 | 0 | 0 | 69.7244 | 30.2756 | 0 | 69.7244 | 30.2756 | 0
190 | 10 | July | 5.7 | 7.0175 | 504.9 | 338.0734 | 842.9734 | 0 | 842.9734 | 0 | 0 | 59.8951 | 40.1049 | 0 | 59.8951 | 40.1049 | 0
190 | 11 | July | 6.2 | 7.6331 | 625.6 | 655.8584 | 1281.4584 | 0 | 1281.4584 | 0 | 0 | 48.8194 | 51.1806 | 0 | 48.8194 | 51.1806 | 0
190 | 12 | July | 3.6 | 4.4321 | 75.65 | 673.1352 | 748.7852 | 0 | 748.7852 | 0 | 0 | 10.103 | 89.897 | 0 | 10.103 | 89.897 | 0
190 | 13 | July | 7.2 | 8.8642 | 908.65 | 1265.6822 | 2174.3322 | 1 | 2000 | 174.3322 | 8.7166 | 41.7898 | 54.5675 | 13.7738 | 36.7159 | 58.2102 | 19.1858
190 | 14 | July | 5.1 | 6.2788 | 312.8 | 1152.2305 | 1465.0305 | 0 | 1465.0305 | 0 | 0 | 21.3511 | 78.6489 | 0 | 21.3511 | 78.6489 | 0
190 | 15 | July | 6.2 | 7.6331 | 625.6 | 1077.203 | 1702.803 | 0 | 1702.803 | 0 | 0 | 36.7394 | 63.2606 | 0 | 36.7394 | 63.2606 | 0
190 | 16 | July | 6.7 | 8.2487 | 761.6 | 802.7806 | 1564.3806 | 0 | 1564.3806 | 0 | 0 | 48.6838 | 51.3162 | 0 | 48.6838 | 51.3162 | 0
190 | 17 | July | 5.7 | 7.0175 | 504.9 | 505.9119 | 1010.8119 | 0 | 1010.8119 | 0 | 0 | 49.9499 | 50.0501 | 0 | 49.9499 | 50.0501 | 0
190 | 18 | July | 4.6 | 5.6633 | 237.15 | 242.8073 | 479.9573 | 0 | 479.9573 | 0 | 0 | 49.4106 | 50.5894 | 0 | 49.4106 | 50.5894 | 0
190 | 19 | July | 3.6 | 4.4321 | 75.65 | 109.809 | 185.459 | 0 | 185.459 | 0 | 0 | 40.7907 | 59.2093 | 0 | 40.7907 | 59.2093 | 0
190 | 20 | July | 2.6 | 3.201 | 0 | 30.429 | 30.429 | 0 | 30.429 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
190 | 21 | July | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
190 | 22 | July | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
190 | 23 | July | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
190 | 24 | July | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
191 | 1 | July | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
191 | 2 | July | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
191 | 3 | July | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
191 | 4 | July | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
191 | 5 | July | 1 | 1.2311 | 0 | 19.845 | 19.845 | 0 | 19.845 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
191 | 6 | July | 2.6 | 3.201 | 0 | 134.6703 | 134.6703 | 0 | 134.6703 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
191 | 7 | July | 1 | 1.2311 | 0 | 269.3175 | 269.3175 | 0 | 269.3175 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
191 | 8 | July | 2.1 | 2.5854 | 0 | 203.742 | 203.742 | 0 | 203.742 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
191 | 9 | July | 1 | 1.2311 | 0 | 458.8623 | 458.8623 | 0 | 458.8623 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
191 | 10 | July | 2.6 | 3.201 | 0 | 560.5806 | 560.5806 | 0 | 560.5806 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
191 | 11 | July | 3.1 | 3.8165 | 0 | 638.6081 | 638.6081 | 0 | 638.6081 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
191 | 12 | July | 3.6 | 4.4321 | 75.65 | 670.2229 | 745.8729 | 0 | 745.8729 | 0 | 0 | 10.1425 | 89.8575 | 0 | 10.1425 | 89.8575 | 0
191 | 13 | July | 3.1 | 3.8165 | 0 | 665.9198 | 665.9198 | 0 | 665.9198 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
191 | 14 | July | 3.1 | 3.8165 | 0 | 621.9456 | 621.9456 | 0 | 621.9456 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
191 | 15 | July | 3.1 | 3.8165 | 0 | 541.6025 | 541.6025 | 0 | 541.6025 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
191 | 16 | July | 3.6 | 4.4321 | 75.65 | 435.152 | 510.802 | 0 | 510.802 | 0 | 0 | 14.81 | 85.19 | 0 | 14.81 | 85.19 | 0
191 | 17 | July | 3.6 | 4.4321 | 75.65 | 391.6805 | 467.3305 | 0 | 467.3305 | 0 | 0 | 16.1877 | 83.8123 | 0 | 16.1877 | 83.8123 | 0
191 | 18 | July | 3.9 | 4.8015 | 120.7 | 210.3689 | 331.0689 | 0 | 331.0689 | 0 | 0 | 36.4577 | 63.5423 | 0 | 36.4577 | 63.5423 | 0
191 | 19 | July | 4.1 | 5.0477 | 173.4 | 88.641 | 262.041 | 0 | 262.041 | 0 | 0 | 66.1729 | 33.8271 | 0 | 66.1729 | 33.8271 | 0
191 | 20 | July | 2.6 | 3.201 | 0 | 17.199 | 17.199 | 0 | 17.199 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
191 | 21 | July | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
191 | 22 | July | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
191 | 23 | July | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
191 | 24 | July | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
192 | 1 | July | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
192 | 2 | July | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
192 | 3 | July | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
192 | 4 | July | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
192 | 5 | July | 2.6 | 3.201 | 0 | 18.522 | 18.522 | 0 | 18.522 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
192 | 6 | July | 3.6 | 4.4321 | 75.65 | 92.61 | 168.26 | 0 | 168.26 | 0 | 0 | 44.9602 | 55.0398 | 0 | 44.9602 | 55.0398 | 0
192 | 7 | July | 3.6 | 4.4321 | 75.65 | 203.9259 | 279.5759 | 0 | 279.5759 | 0 | 0 | 27.0588 | 72.9412 | 0 | 27.0588 | 72.9412 | 0
192 | 8 | July | 3.6 | 4.4321 | 75.65 | 330.0657 | 405.7157 | 0 | 405.7157 | 0 | 0 | 18.6461 | 81.3539 | 0 | 18.6461 | 81.3539 | 0
192 | 9 | July | 3.6 | 4.4321 | 75.65 | 458.6715 | 534.3215 | 0 | 534.3215 | 0 | 0 | 14.1581 | 85.8419 | 0 | 14.1581 | 85.8419 | 0
192 | 10 | July | 5.1 | 6.2788 | 312.8 | 559.2142 | 872.0142 | 0 | 872.0142 | 0 | 0 | 35.871 | 64.129 | 0 | 35.871 | 64.129 | 0
192 | 11 | July | 5.7 | 7.0175 | 504.9 | 635.7163 | 1140.6163 | 0 | 1140.6163 | 0 | 0 | 44.2655 | 55.7345 | 0 | 44.2655 | 55.7345 | 0
192 | 12 | July | 6.2 | 7.6331 | 625.6 | 671.8075 | 1297.4075 | 0 | 1297.4075 | 0 | 0 | 48.2192 | 51.7808 | 0 | 48.2192 | 51.7808 | 0
192 | 13 | July | 6.2 | 7.6331 | 625.6 | 664.6082 | 1290.2082 | 0 | 1290.2082 | 0 | 0 | 48.4883 | 51.5117 | 0 | 48.4883 | 51.5117 | 0
192 | 14 | July | 4.6 | 5.6633 | 237.15 | 380.4003 | 617.5503 | 0 | 617.5503 | 0 | 0 | 38.4017 | 61.5983 | 0 | 38.4017 | 61.5983 | 0
192 | 15 | July | 5.7 | 7.0175 | 504.9 | 539.2468 | 1044.1468 | 0 | 1044.1468 | 0 | 0 | 48.3553 | 51.6447 | 0 | 48.3553 | 51.6447 | 0
192 | 16 | July | 5.1 | 6.2788 | 312.8 | 435.1517 | 747.9517 | 0 | 747.9517 | 0 | 0 | 41.8209 | 58.1791 | 0 | 41.8209 | 58.1791 | 0
192 | 17 | July | 6.2 | 7.6331 | 625.6 | 314.0799 | 939.6799 | 0 | 939.6799 | 0 | 0 | 66.5759 | 33.4241 | 0 | 66.5759 | 33.4241 | 0
192 | 18 | July | 4.6 | 5.6633 | 237.15 | 123.039 | 360.189 | 0 | 360.189 | 0 | 0 | 65.8404 | 34.1596 | 0 | 65.8404 | 34.1596 | 0
192 | 19 | July | 4.6 | 5.6633 | 237.15 | 88.641 | 325.791 | 0 | 325.791 | 0 | 0 | 72.7921 | 27.2079 | 0 | 72.7921 | 27.2079 | 0
192 | 20 | July | 4.1 | 5.0477 | 173.4 | 17.199 | 190.599 | 0 | 190.599 | 0 | 0 | 90.9763 | 9.0237 | 0 | 90.9763 | 9.0237 | 0
192 | 21 | July | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
192 | 22 | July | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
192 | 23 | July | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
192 | 24 | July | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
193 | 1 | July | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
193 | 2 | July | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
193 | 3 | July | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
193 | 4 | July | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
193 | 5 | July | 6.2 | 7.6331 | 625.6 | 17.199 | 642.799 | 0 | 642.799 | 0 | 0 | 97.3244 | 2.6756 | 0 | 97.3244 | 2.6756 | 0
193 | 6 | July | 5.7 | 7.0175 | 504.9 | 91.287 | 596.187 | 0 | 596.187 | 0 | 0 | 84.6882 | 15.3118 | 0 | 84.6882 | 15.3118 | 0
193 | 7 | July | 6.2 | 7.6331 | 625.6 | 202.574 | 828.174 | 0 | 828.174 | 0 | 0 | 75.5397 | 24.4603 | 0 | 75.5397 | 24.4603 | 0
193 | 8 | July | 5.7 | 7.0175 | 504.9 | 201.096 | 705.996 | 0 | 705.996 | 0 | 0 | 71.516 | 28.484 | 0 | 71.516 | 28.484 | 0
193 | 9 | July | 5.1 | 6.2788 | 312.8 | 454.8922 | 767.6922 | 0 | 767.6922 | 0 | 0 | 40.7455 | 59.2545 | 0 | 40.7455 | 59.2545 | 0
193 | 10 | July | 6.7 | 8.2487 | 761.6 | 556.4381 | 1318.0381 | 0 | 1318.0381 | 0 | 0 | 57.7829 | 42.2171 | 0 | 57.7829 | 42.2171 | 0
193 | 11 | July | 6.2 | 7.6331 | 625.6 | 632.8248 | 1258.4248 | 0 | 1258.4248 | 0 | 0 | 49.7129 | 50.2871 | 0 | 49.7129 | 50.2871 | 0
193 | 12 | July | 7.2 | 8.8642 | 908.65 | 665.9826 | 1574.6326 | 0 | 1574.6326 | 0 | 0 | 57.7055 | 42.2945 | 0 | 57.7055 | 42.2945 | 0
193 | 13 | July | 6.2 | 7.6331 | 625.6 | 660.2167 | 1285.8167 | 0 | 1285.8167 | 0 | 0 | 48.6539 | 51.3461 | 0 | 48.6539 | 51.3461 | 0
193 | 14 | July | 6.7 | 8.2487 | 761.6 | 617.9281 | 1379.5281 | 0 | 1379.5281 | 0 | 0 | 55.2073 | 44.7927 | 0 | 55.2073 | 44.7927 | 0
193 | 15 | July | 6.7 | 8.2487 | 761.6 | 529.6599 | 1291.2599 | 0 | 1291.2599 | 0 | 0 | 58.9812 | 41.0188 | 0 | 58.9812 | 41.0188 | 0
193 | 16 | July | 5.7 | 7.0175 | 504.9 | 432.9232 | 937.8232 | 0 | 937.8232 | 0 | 0 | 53.8374 | 46.1626 | 0 | 53.8374 | 46.1626 | 0
193 | 17 | July | 6.2 | 7.6331 | 625.6 | 312.7464 | 938.3464 | 0 | 938.3464 | 0 | 0 | 66.6705 | 33.3295 | 0 | 66.6705 | 33.3295 | 0
193 | 18 | July | 3.6 | 4.4321 | 75.65 | 123.039 | 198.689 | 0 | 198.689 | 0 | 0 | 38.0746 | 61.9254 | 0 | 38.0746 | 61.9254 | 0
193 | 19 | July | 3.6 | 4.4321 | 75.65 | 54.243 | 129.893 | 0 | 129.893 | 0 | 0 | 58.2402 | 41.7598 | 0 | 58.2402 | 41.7598 | 0
193 | 20 | July | 3.1 | 3.8165 | 0 | 15.876 | 15.876 | 0 | 15.876 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
193 | 21 | July | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
193 | 22 | July | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
193 | 23 | July | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
193 | 24 | July | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
194 | 1 | July | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
194 | 2 | July | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
194 | 3 | July | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
194 | 4 | July | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
194 | 5 | July | 1.5 | 1.8467 | 0 | 22.491 | 22.491 | 0 | 22.491 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
194 | 6 | July | 2.1 | 2.5854 | 0 | 139.0952 | 139.0952 | 0 | 139.0952 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
194 | 7 | July | 2.6 | 3.201 | 0 | 384.8164 | 384.8164 | 0 | 384.8164 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
194 | 8 | July | 2.6 | 3.201 | 0 | 705.4712 | 705.4712 | 0 | 705.4712 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
194 | 9 | July | 2.6 | 3.201 | 0 | 1010.2655 | 1010.2655 | 0 | 1010.2655 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
194 | 10 | July | 3.1 | 3.8165 | 0 | 1253.525 | 1253.525 | 0 | 1253.525 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
194 | 11 | July | 5.7 | 7.0175 | 504.9 | 1427.1851 | 1932.0851 | 0 | 1932.0851 | 0 | 0 | 26.1324 | 73.8676 | 0 | 26.1324 | 73.8676 | 0
194 | 12 | July | 5.7 | 7.0175 | 504.9 | 1491.3558 | 1996.2558 | 0 | 1996.2558 | 0 | 0 | 25.2924 | 74.7076 | 0 | 25.2924 | 74.7076 | 0
194 | 13 | July | 6.2 | 7.6331 | 625.6 | 1450.2332 | 2075.8332 | 1 | 2000 | 75.8332 | 3.7917 | 30.1373 | 68.72 | 5.229 | 27.4883 | 69.8627 | 12.1217
194 | 14 | July | 6.2 | 7.6331 | 625.6 | 1313.1344 | 1938.7344 | 0 | 1938.7344 | 0 | 0 | 32.2685 | 67.7315 | 0 | 32.2685 | 67.7315 | 0
194 | 15 | July | 6.2 | 7.6331 | 625.6 | 1085.1047 | 1710.7047 | 0 | 1710.7047 | 0 | 0 | 36.5697 | 63.4303 | 0 | 36.5697 | 63.4303 | 0
194 | 16 | July | 5.7 | 7.0175 | 504.9 | 804.6242 | 1309.5242 | 0 | 1309.5242 | 0 | 0 | 38.556 | 61.444 | 0 | 38.556 | 61.444 | 0
194 | 17 | July | 5.1 | 6.2788 | 312.8 | 490.6704 | 803.4704 | 0 | 803.4704 | 0 | 0 | 38.9311 | 61.0689 | 0 | 38.9311 | 61.0689 | 0
194 | 18 | July | 5.7 | 7.0175 | 504.9 | 222.514 | 727.414 | 0 | 727.414 | 0 | 0 | 69.4103 | 30.5897 | 0 | 69.4103 | 30.5897 | 0
194 | 19 | July | 3.6 | 4.4321 | 75.65 | 85.995 | 161.645 | 0 | 161.645 | 0 | 0 | 46.8001 | 53.1999 | 0 | 46.8001 | 53.1999 | 0
194 | 20 | July | 5.1 | 6.2788 | 312.8 | 15.876 | 328.676 | 0 | 328.676 | 0 | 0 | 95.1697 | 4.8303 | 0 | 95.1697 | 4.8303 | 0
194 | 21 | July | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
194 | 22 | July | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
194 | 23 | July | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
194 | 24 | July | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
195 | 1 | July | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
195 | 2 | July | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
195 | 3 | July | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
195 | 4 | July | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
195 | 5 | July | 5.1 | 6.2788 | 312.8 | 10.584 | 323.384 | 0 | 323.384 | 0 | 0 | 96.7271 | 3.2729 | 0 | 96.7271 | 3.2729 | 0
195 | 6 | July | 4.1 | 5.0477 | 173.4 | 55.566 | 228.966 | 0 | 228.966 | 0 | 0 | 75.7318 | 24.2682 | 0 | 75.7318 | 24.2682 | 0
195 | 7 | July | 1.5 | 1.8467 | 0 | 198.8248 | 198.8248 | 0 | 198.8248 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
195 | 8 | July | 1 | 1.2311 | 0 | 602.7739 | 602.7739 | 0 | 602.7739 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
195 | 9 | July | 6.2 | 7.6331 | 625.6 | 764.9173 | 1390.5173 | 0 | 1390.5173 | 0 | 0 | 44.9905 | 55.0095 | 0 | 44.9905 | 55.0095 | 0
195 | 10 | July | 8.2 | 10.0954 | 1359.15 | 1223.784 | 2582.934 | 1 | 2000 | 582.934 | 29.1467 | 52.6204 | 32.0425 | 47.6337 | 38.8108 | 47.3796 | 42.8896
195 | 11 | July | 7.7 | 9.4798 | 1059.95 | 1450.5 | 2510.45 | 1 | 2000 | 510.45 | 25.5225 | 42.2215 | 47.0025 | 35.1913 | 27.475 | 57.7785 | 48.1579
195 | 12 | July | 4.1 | 5.0477 | 173.4 | 1402.9482 | 1576.3482 | 0 | 1576.3482 | 0 | 0 | 11.0001 | 88.9999 | 0 | 11.0001 | 88.9999 | 0
195 | 13 | July | 5.1 | 6.2788 | 312.8 | 1375.8374 | 1688.6374 | 0 | 1688.6374 | 0 | 0 | 18.5238 | 81.4762 | 0 | 18.5238 | 81.4762 | 0
195 | 14 | July | 4.6 | 5.6633 | 237.15 | 1010.3437 | 1247.4937 | 0 | 1247.4937 | 0 | 0 | 19.0101 | 80.9899 | 0 | 19.0101 | 80.9899 | 0
195 | 15 | July | 4.1 | 5.0477 | 173.4 | 536.1107 | 709.5107 | 0 | 709.5107 | 0 | 0 | 24.4394 | 75.5606 | 0 | 24.4394 | 75.5606 | 0
195 | 16 | July | 6.2 | 7.6331 | 625.6 | 652.0315 | 1277.6315 | 0 | 1277.6315 | 0 | 0 | 48.9656 | 51.0344 | 0 | 48.9656 | 51.0344 | 0
195 | 17 | July | 7.2 | 8.8642 | 908.65 | 385.1786 | 1293.8286 | 0 | 1293.8286 | 0 | 0 | 70.2295 | 29.7705 | 0 | 70.2295 | 29.7705 | 0
195 | 18 | July | 5.7 | 7.0175 | 504.9 | 120.393 | 625.293 | 0 | 625.293 | 0 | 0 | 80.7461 | 19.2539 | 0 | 80.7461 | 19.2539 | 0
195 | 19 | July | 6.2 | 7.6331 | 625.6 | 84.672 | 710.272 | 0 | 710.272 | 0 | 0 | 88.0789 | 11.9211 | 0 | 88.0789 | 11.9211 | 0
195 | 20 | July | 5.7 | 7.0175 | 504.9 | 9.261 | 514.161 | 0 | 514.161 | 0 | 0 | 98.1988 | 1.8012 | 0 | 98.1988 | 1.8012 | 0
195 | 21 | July | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
195 | 22 | July | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
195 | 23 | July | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
195 | 24 | July | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
196 | 1 | July | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
196 | 2 | July | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
196 | 3 | July | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
196 | 4 | July | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
196 | 5 | July | 4.1 | 5.0477 | 173.4 | 21.168 | 194.568 | 0 | 194.568 | 0 | 0 | 89.1205 | 10.8795 | 0 | 89.1205 | 10.8795 | 0
196 | 6 | July | 5.1 | 6.2788 | 312.8 | 142.8533 | 455.6533 | 0 | 455.6533 | 0 | 0 | 68.6487 | 31.3513 | 0 | 68.6487 | 31.3513 | 0
196 | 7 | July | 4.1 | 5.0477 | 173.4 | 381.2882 | 554.6882 | 0 | 554.6882 | 0 | 0 | 31.2608 | 68.7392 | 0 | 31.2608 | 68.7392 | 0
196 | 8 | July | 3.6 | 4.4321 | 75.65 | 605.2205 | 680.8705 | 0 | 680.8705 | 0 | 0 | 11.1108 | 88.8892 | 0 | 11.1108 | 88.8892 | 0
196 | 9 | July | 3.6 | 4.4321 | 75.65 | 623.7677 | 699.4177 | 0 | 699.4177 | 0 | 0 | 10.8161 | 89.1839 | 0 | 10.8161 | 89.1839 | 0
196 | 10 | July | 3.6 | 4.4321 | 75.65 | 944.0214 | 1019.6714 | 0 | 1019.6714 | 0 | 0 | 7.4191 | 92.5809 | 0 | 7.4191 | 92.5809 | 0
196 | 11 | July | 3.1 | 3.8165 | 0 | 882.8428 | 882.8428 | 0 | 882.8428 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
196 | 12 | July | 5.1 | 6.2788 | 312.8 | 673.3688 | 986.1688 | 0 | 986.1688 | 0 | 0 | 31.7187 | 68.2813 | 0 | 31.7187 | 68.2813 | 0
196 | 13 | July | 4.1 | 5.0477 | 173.4 | 655.0459 | 828.4459 | 0 | 828.4459 | 0 | 0 | 20.9308 | 79.0692 | 0 | 20.9308 | 79.0692 | 0
196 | 14 | July | 3.6 | 4.4321 | 75.65 | 613.3453 | 688.9953 | 0 | 688.9953 | 0 | 0 | 10.9798 | 89.0202 | 0 | 10.9798 | 89.0202 | 0
196 | 15 | July | 4.1 | 5.0477 | 173.4 | 542.1576 | 715.5576 | 0 | 715.5576 | 0 | 0 | 24.2329 | 75.7671 | 0 | 24.2329 | 75.7671 | 0
196 | 16 | July | 3.6 | 4.4321 | 75.65 | 268.2505 | 343.9005 | 0 | 343.9005 | 0 | 0 | 21.9976 | 78.0024 | 0 | 21.9976 | 78.0024 | 0
196 | 17 | July | 3.6 | 4.4321 | 75.65 | 197.127 | 272.777 | 0 | 272.777 | 0 | 0 | 27.7333 | 72.2667 | 0 | 27.7333 | 72.2667 | 0
196 | 18 | July | 3.6 | 4.4321 | 75.65 | 187.5596 | 263.2096 | 0 | 263.2096 | 0 | 0 | 28.7413 | 71.2587 | 0 | 28.7413 | 71.2587 | 0
196 | 19 | July | 3.1 | 3.8165 | 0 | 52.92 | 52.92 | 0 | 52.92 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
196 | 20 | July | 2.6 | 3.201 | 0 | 9.261 | 9.261 | 0 | 9.261 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
196 | 21 | July | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
196 | 22 | July | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
196 | 23 | July | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
196 | 24 | July | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
197 | 1 | July | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
197 | 2 | July | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
197 | 3 | July | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
197 | 4 | July | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
197 | 5 | July | 3.1 | 3.8165 | 0 | 9.261 | 9.261 | 0 | 9.261 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
197 | 6 | July | 3.1 | 3.8165 | 0 | 54.243 | 54.243 | 0 | 54.243 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
197 | 7 | July | 3.1 | 3.8165 | 0 | 121.716 | 121.716 | 0 | 121.716 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
197 | 8 | July | 5.1 | 6.2788 | 312.8 | 325.303 | 638.103 | 0 | 638.103 | 0 | 0 | 49.0203 | 50.9797 | 0 | 49.0203 | 50.9797 | 0
197 | 9 | July | 6.2 | 7.6331 | 625.6 | 270.5579 | 896.1579 | 0 | 896.1579 | 0 | 0 | 69.8091 | 30.1909 | 0 | 69.8091 | 30.1909 | 0
197 | 10 | July | 6.7 | 8.2487 | 761.6 | 331.3399 | 1092.9399 | 0 | 1092.9399 | 0 | 0 | 69.6836 | 30.3164 | 0 | 69.6836 | 30.3164 | 0
197 | 11 | July | 6.2 | 7.6331 | 625.6 | 375.4968 | 1001.0968 | 0 | 1001.0968 | 0 | 0 | 62.4915 | 37.5085 | 0 | 62.4915 | 37.5085 | 0
197 | 12 | July | 4.1 | 5.0477 | 173.4 | 396.1001 | 569.5001 | 0 | 569.5001 | 0 | 0 | 30.4478 | 69.5522 | 0 | 30.4478 | 69.5522 | 0
197 | 13 | July | 5.7 | 7.0175 | 504.9 | 395.5226 | 900.4226 | 0 | 900.4226 | 0 | 0 | 56.0737 | 43.9263 | 0 | 56.0737 | 43.9263 | 0
197 | 14 | July | 5.7 | 7.0175 | 504.9 | 625.9668 | 1130.8668 | 0 | 1130.8668 | 0 | 0 | 44.6472 | 55.3528 | 0 | 44.6472 | 55.3528 | 0
197 | 15 | July | 6.2 | 7.6331 | 625.6 | 533.9421 | 1159.5421 | 0 | 1159.5421 | 0 | 0 | 53.9523 | 46.0477 | 0 | 53.9523 | 46.0477 | 0
197 | 16 | July | 6.2 | 7.6331 | 625.6 | 555.7721 | 1181.3721 | 0 | 1181.3721 | 0 | 0 | 52.9554 | 47.0446 | 0 | 52.9554 | 47.0446 | 0
197 | 17 | July | 6.7 | 8.2487 | 761.6 | 492.8103 | 1254.4103 | 0 | 1254.4103 | 0 | 0 | 60.7138 | 39.2862 | 0 | 60.7138 | 39.2862 | 0
197 | 18 | July | 3.1 | 3.8165 | 0 | 237.2378 | 237.2378 | 0 | 237.2378 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
197 | 19 | July | 3.6 | 4.4321 | 75.65 | 104.517 | 180.167 | 0 | 180.167 | 0 | 0 | 41.9888 | 58.0112 | 0 | 41.9888 | 58.0112 | 0
197 | 20 | July | 3.6 | 4.4321 | 75.65 | 18.522 | 94.172 | 0 | 94.172 | 0 | 0 | 80.3317 | 19.6683 | 0 | 80.3317 | 19.6683 | 0
197 | 21 | July | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
197 | 22 | July | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
197 | 23 | July | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
197 | 24 | July | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
198 | 1 | July | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
198 | 2 | July | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
198 | 3 | July | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
198 | 4 | July | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
198 | 5 | July | 1 | 1.2311 | 0 | 26.46 | 26.46 | 0 | 26.46 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
198 | 6 | July | 2.6 | 3.201 | 0 | 141.4392 | 141.4392 | 0 | 141.4392 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
198 | 7 | July | 3.1 | 3.8165 | 0 | 363.2354 | 363.2354 | 0 | 363.2354 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
198 | 8 | July | 4.1 | 5.0477 | 173.4 | 675.8724 | 849.2724 | 0 | 849.2724 | 0 | 0 | 20.4175 | 79.5825 | 0 | 20.4175 | 79.5825 | 0
198 | 9 | July | 5.1 | 6.2788 | 312.8 | 756.9857 | 1069.7857 | 0 | 1069.7857 | 0 | 0 | 29.2395 | 70.7605 | 0 | 29.2395 | 70.7605 | 0
198 | 10 | July | 5.7 | 7.0175 | 504.9 | 759.3519 | 1264.2519 | 0 | 1264.2519 | 0 | 0 | 39.9367 | 60.0633 | 0 | 39.9367 | 60.0633 | 0
198 | 11 | July | 6.7 | 8.2487 | 761.6 | 868.3763 | 1629.9763 | 0 | 1629.9763 | 0 | 0 | 46.7246 | 53.2754 | 0 | 46.7246 | 53.2754 | 0
198 | 12 | July | 6.7 | 8.2487 | 761.6 | 1125.3405 | 1886.9405 | 0 | 1886.9405 | 0 | 0 | 40.3616 | 59.6384 | 0 | 40.3616 | 59.6384 | 0
198 | 13 | July | 7.7 | 9.4798 | 1059.95 | 1083.617 | 2143.567 | 1 | 2000 | 143.567 | 7.1783 | 49.448 | 47.0025 | 13.2489 | 45.8192 | 50.552 | 13.5447
198 | 14 | July | 6.2 | 7.6331 | 625.6 | 845.5254 | 1471.1254 | 0 | 1471.1254 | 0 | 0 | 42.5253 | 57.4747 | 0 | 42.5253 | 57.4747 | 0
198 | 15 | July | 6.7 | 8.2487 | 761.6 | 708.3531 | 1469.9531 | 0 | 1469.9531 | 0 | 0 | 51.8112 | 48.1888 | 0 | 51.8112 | 48.1888 | 0
198 | 16 | July | 7.2 | 8.8642 | 908.65 | 785.1033 | 1693.7533 | 0 | 1693.7533 | 0 | 0 | 53.6471 | 46.3529 | 0 | 53.6471 | 46.3529 | 0
198 | 17 | July | 6.2 | 7.6331 | 625.6 | 435.8423 | 1061.4423 | 0 | 1061.4423 | 0 | 0 | 58.9387 | 41.0613 | 0 | 58.9387 | 41.0613 | 0
198 | 18 | July | 6.7 | 8.2487 | 761.6 | 233.3409 | 994.9409 | 0 | 994.9409 | 0 | 0 | 76.5473 | 23.4527 | 0 | 76.5473 | 23.4527 | 0
198 | 19 | July | 5.7 | 7.0175 | 504.9 | 104.517 | 609.417 | 0 | 609.417 | 0 | 0 | 82.8497 | 17.1503 | 0 | 82.8497 | 17.1503 | 0
198 | 20 | July | 4.1 | 5.0477 | 173.4 | 21.168 | 194.568 | 0 | 194.568 | 0 | 0 | 89.1205 | 10.8795 | 0 | 89.1205 | 10.8795 | 0
198 | 21 | July | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
198 | 22 | July | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
198 | 23 | July | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
198 | 24 | July | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
199 | 1 | July | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
199 | 2 | July | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
199 | 3 | July | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
199 | 4 | July | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
199 | 5 | July | 3.6 | 4.4321 | 75.65 | 9.261 | 84.911 | 0 | 84.911 | 0 | 0 | 89.0933 | 10.9067 | 0 | 89.0933 | 10.9067 | 0
199 | 6 | July | 4.1 | 5.0477 | 173.4 | 51.597 | 224.997 | 0 | 224.997 | 0 | 0 | 77.0677 | 22.9323 | 0 | 77.0677 | 22.9323 | 0
199 | 7 | July | 5.1 | 6.2788 | 312.8 | 119.07 | 431.87 | 0 | 431.87 | 0 | 0 | 72.4292 | 27.5708 | 0 | 72.4292 | 27.5708 | 0
199 | 8 | July | 6.2 | 7.6331 | 625.6 | 320.3086 | 945.9086 | 0 | 945.9086 | 0 | 0 | 66.1375 | 33.8625 | 0 | 66.1375 | 33.8625 | 0
199 | 9 | July | 5.7 | 7.0175 | 504.9 | 447.7648 | 952.6648 | 0 | 952.6648 | 0 | 0 | 52.9987 | 47.0013 | 0 | 52.9987 | 47.0013 | 0
199 | 10 | July | 6.7 | 8.2487 | 761.6 | 757.9025 | 1519.5025 | 0 | 1519.5025 | 0 | 0 | 50.1217 | 49.8783 | 0 | 50.1217 | 49.8783 | 0
199 | 11 | July | 5.1 | 6.2788 | 312.8 | 632.8708 | 945.6708 | 0 | 945.6708 | 0 | 0 | 33.0771 | 66.9229 | 0 | 33.0771 | 66.9229 | 0
199 | 12 | July | 7.2 | 8.8642 | 908.65 | 652.4555 | 1561.1055 | 0 | 1561.1055 | 0 | 0 | 58.2055 | 41.7945 | 0 | 58.2055 | 41.7945 | 0
199 | 13 | July | 1 | 1.2311 | 0 | 908.3749 | 908.3749 | 0 | 908.3749 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
199 | 14 | July | 5.1 | 6.2788 | 312.8 | 618.4685 | 931.2685 | 0 | 931.2685 | 0 | 0 | 33.5886 | 66.4114 | 0 | 33.5886 | 66.4114 | 0
199 | 15 | July | 3.6 | 4.4321 | 75.65 | 539.4514 | 615.1014 | 0 | 615.1014 | 0 | 0 | 12.2988 | 87.7012 | 0 | 12.2988 | 87.7012 | 0
199 | 16 | July | 1.5 | 1.8467 | 0 | 429.4792 | 429.4792 | 0 | 429.4792 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
199 | 17 | July | 1 | 1.2311 | 0 | 194.481 | 194.481 | 0 | 194.481 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
199 | 18 | July | 3.1 | 3.8165 | 0 | 183.0795 | 183.0795 | 0 | 183.0795 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
199 | 19 | July | 3.6 | 4.4321 | 75.65 | 80.703 | 156.353 | 0 | 156.353 | 0 | 0 | 48.3841 | 51.6159 | 0 | 48.3841 | 51.6159 | 0
199 | 20 | July | 2.6 | 3.201 | 0 | 14.553 | 14.553 | 0 | 14.553 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
199 | 21 | July | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
199 | 22 | July | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
199 | 23 | July | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
199 | 24 | July | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
200 | 1 | July | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
200 | 2 | July | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
200 | 3 | July | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
200 | 4 | July | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
200 | 5 | July | 4.1 | 5.0477 | 173.4 | 25.137 | 198.537 | 0 | 198.537 | 0 | 0 | 87.3389 | 12.6611 | 0 | 87.3389 | 12.6611 | 0
200 | 6 | July | 4.1 | 5.0477 | 173.4 | 136.5676 | 309.9676 | 0 | 309.9676 | 0 | 0 | 55.9413 | 44.0587 | 0 | 55.9413 | 44.0587 | 0
200 | 7 | July | 5.1 | 6.2788 | 312.8 | 369.4676 | 682.2676 | 0 | 682.2676 | 0 | 0 | 45.8471 | 54.1529 | 0 | 45.8471 | 54.1529 | 0
200 | 8 | July | 6.2 | 7.6331 | 625.6 | 435.394 | 1060.994 | 0 | 1060.994 | 0 | 0 | 58.9636 | 41.0364 | 0 | 58.9636 | 41.0364 | 0
200 | 9 | July | 6.7 | 8.2487 | 761.6 | 450.7293 | 1212.3293 | 0 | 1212.3293 | 0 | 0 | 62.8212 | 37.1788 | 0 | 62.8212 | 37.1788 | 0
200 | 10 | July | 4.1 | 5.0477 | 173.4 | 327.1931 | 500.5931 | 0 | 500.5931 | 0 | 0 | 34.6389 | 65.3611 | 0 | 34.6389 | 65.3611 | 0
200 | 11 | July | 5.7 | 7.0175 | 504.9 | 370.2079 | 875.1079 | 0 | 875.1079 | 0 | 0 | 57.6957 | 42.3043 | 0 | 57.6957 | 42.3043 | 0
200 | 12 | July | 5.1 | 6.2788 | 312.8 | 394.7717 | 707.5717 | 0 | 707.5717 | 0 | 0 | 44.2075 | 55.7925 | 0 | 44.2075 | 55.7925 | 0
200 | 13 | July | 3.6 | 4.4321 | 75.65 | 394.1967 | 469.8467 | 0 | 469.8467 | 0 | 0 | 16.101 | 83.899 | 0 | 16.101 | 83.899 | 0
200 | 14 | July | 4.1 | 5.0477 | 173.4 | 369.9716 | 543.3716 | 0 | 543.3716 | 0 | 0 | 31.9119 | 68.0881 | 0 | 31.9119 | 68.0881 | 0
200 | 15 | July | 3.6 | 4.4321 | 75.65 | 323.2887 | 398.9387 | 0 | 398.9387 | 0 | 0 | 18.9628 | 81.0372 | 0 | 18.9628 | 81.0372 | 0
200 | 16 | July | 1.5 | 1.8467 | 0 | 264.2206 | 264.2206 | 0 | 264.2206 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
200 | 17 | July | 3.6 | 4.4321 | 75.65 | 302.5668 | 378.2168 | 0 | 378.2168 | 0 | 0 | 20.0018 | 79.9982 | 0 | 20.0018 | 79.9982 | 0
200 | 18 | July | 3.6 | 4.4321 | 75.65 | 214.3723 | 290.0223 | 0 | 290.0223 | 0 | 0 | 26.0842 | 73.9158 | 0 | 26.0842 | 73.9158 | 0
200 | 19 | July | 3.1 | 3.8165 | 0 | 79.38 | 79.38 | 0 | 79.38 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
200 | 20 | July | 2.6 | 3.201 | 0 | 13.23 | 13.23 | 0 | 13.23 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
200 | 21 | July | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200 | 22 | July | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200 | 23 | July | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200 | 24 | July | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201 | 1 | July | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201 | 2 | July | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
201 | 3 | July | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201 | 4 | July | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201 | 5 | July | 3.1 | 3.8165 | 0 | 17.199 | 17.199 | 0 | 17.199 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
201 | 6 | July | 3.6 | 4.4321 | 75.65 | 79.38 | 155.03 | 0 | 155.03 | 0 | 0 | 48.797 | 51.203 | 0 | 48.797 | 51.203 | 0
201 | 7 | July | 5.1 | 6.2788 | 312.8 | 251.1475 | 563.9475 | 0 | 563.9475 | 0 | 0 | 55.4662 | 44.5338 | 0 | 55.4662 | 44.5338 | 0
201 | 8 | July | 5.7 | 7.0175 | 504.9 | 431.426 | 936.326 | 0 | 936.326 | 0 | 0 | 53.9235 | 46.0765 | 0 | 53.9235 | 46.0765 | 0
201 | 9 | July | 6.2 | 7.6331 | 625.6 | 448.1479 | 1073.7479 | 0 | 1073.7479 | 0 | 0 | 58.2632 | 41.7368 | 0 | 58.2632 | 41.7368 | 0
201 | 10 | July | 6.7 | 8.2487 | 761.6 | 557.4841 | 1319.0841 | 0 | 1319.0841 | 0 | 0 | 57.737 | 42.263 | 0 | 57.737 | 42.263 | 0
201 | 11 | July | 7.2 | 8.8642 | 908.65 | 875.5853 | 1784.2353 | 0 | 1784.2353 | 0 | 0 | 50.9266 | 49.0734 | 0 | 50.9266 | 49.0734 | 0
201 | 12 | July | 4.6 | 5.6633 | 237.15 | 1350.3526 | 1587.5026 | 0 | 1587.5026 | 0 | 0 | 14.9386 | 85.0614 | 0 | 14.9386 | 85.0614 | 0
201 | 13 | July | 4.1 | 5.0477 | 173.4 | 1245.3563 | 1418.7563 | 0 | 1418.7563 | 0 | 0 | 12.222 | 87.778 | 0 | 12.222 | 87.778 | 0
201 | 14 | July | 8.2 | 10.0954 | 1359.15 | 850.2709 | 2209.4209 | 1 | 2000 | 209.4209 | 10.471 | 61.5161 | 32.0425 | 24.6299 | 57.4865 | 38.4839 | 15.4082
201 | 15 | July | 5.1 | 6.2788 | 312.8 | 535.2206 | 848.0206 | 0 | 848.0206 | 0 | 0 | 36.8859 | 63.1141 | 0 | 36.8859 | 63.1141 | 0
201 | 16 | July | 3.6 | 4.4321 | 75.65 | 426.7221 | 502.3721 | 0 | 502.3721 | 0 | 0 | 15.0586 | 84.9414 | 0 | 15.0586 | 84.9414 | 0
201 | 17 | July | 3.1 | 3.8165 | 0 | 434.0918 | 434.0918 | 0 | 434.0918 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
201 | 18 | July | 3.6 | 4.4321 | 75.65 | 233.0423 | 308.6923 | 0 | 308.6923 | 0 | 0 | 24.5066 | 75.4934 | 0 | 24.5066 | 75.4934 | 0
201 | 19 | July | 4.1 | 5.0477 | 173.4 | 100.548 | 273.948 | 0 | 273.948 | 0 | 0 | 63.2967 | 36.7033 | 0 | 63.2967 | 36.7033 | 0
201 | 20 | July | 4.1 | 5.0477 | 173.4 | 17.199 | 190.599 | 0 | 190.599 | 0 | 0 | 90.9763 | 9.0237 | 0 | 90.9763 | 9.0237 | 0
201 | 21 | July | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
201 | 22 | July | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
201 | 23 | July | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
201 | 24 | July | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
202 | 1 | July | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
202 | 2 | July | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
202 | 3 | July | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
202 | 4 | July | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
202 | 5 | July | 4.6 | 5.6633 | 237.15 | 23.814 | 260.964 | 0 | 260.964 | 0 | 0 | 90.8746 | 9.1254 | 0 | 90.8746 | 9.1254 | 0
202 | 6 | July | 4.6 | 5.6633 | 237.15 | 132.1876 | 369.3376 | 0 | 369.3376 | 0 | 0 | 64.2095 | 35.7905 | 0 | 64.2095 | 35.7905 | 0
202 | 7 | July | 5.1 | 6.2788 | 312.8 | 367.6187 | 680.4187 | 0 | 680.4187 | 0 | 0 | 45.9717 | 54.0283 | 0 | 45.9717 | 54.0283 | 0
202 | 8 | July | 4.6 | 5.6633 | 237.15 | 681.259 | 918.409 | 0 | 918.409 | 0 | 0 | 25.8218 | 74.1782 | 0 | 25.8218 | 74.1782 | 0
202 | 9 | July | 5.7 | 7.0175 | 504.9 | 986.8453 | 1491.7453 | 0 | 1491.7453 | 0 | 0 | 33.8463 | 66.1537 | 0 | 33.8463 | 66.1537 | 0
202 | 10 | July | 5.7 | 7.0175 | 504.9 | 1190.4087 | 1695.3087 | 0 | 1695.3087 | 0 | 0 | 29.7822 | 70.2178 | 0 | 29.7822 | 70.2178 | 0
202 | 11 | July | 5.7 | 7.0175 | 504.9 | 636.7041 | 1141.6041 | 0 | 1141.6041 | 0 | 0 | 44.2272 | 55.7728 | 0 | 44.2272 | 55.7728 | 0
202 | 12 | July | 6.2 | 7.6331 | 625.6 | 1130.8356 | 1756.4356 | 0 | 1756.4356 | 0 | 0 | 35.6176 | 64.3824 | 0 | 35.6176 | 64.3824 | 0
202 | 13 | July | 5.7 | 7.0175 | 504.9 | 1108.2417 | 1613.1417 | 0 | 1613.1417 | 0 | 0 | 31.2992 | 68.7008 | 0 | 31.2992 | 68.7008 | 0
202 | 14 | July | 6.7 | 8.2487 | 761.6 | 622.0498 | 1383.6498 | 0 | 1383.6498 | 0 | 0 | 55.0428 | 44.9572 | 0 | 55.0428 | 44.9572 | 0
202 | 15 | July | 6.2 | 7.6331 | 625.6 | 848.3273 | 1473.9273 | 0 | 1473.9273 | 0 | 0 | 42.4444 | 57.5556 | 0 | 42.4444 | 57.5556 | 0
202 | 16 | July | 5.7 | 7.0175 | 504.9 | 426.7387 | 931.6387 | 0 | 931.6387 | 0 | 0 | 54.1948 | 45.8052 | 0 | 54.1948 | 45.8052 | 0
202 | 17 | July | 6.2 | 7.6331 | 625.6 | 303.4692 | 929.0692 | 0 | 929.0692 | 0 | 0 | 67.3362 | 32.6638 | 0 | 67.3362 | 32.6638 | 0
202 | 18 | July | 3.1 | 3.8165 | 0 | 246.2728 | 246.2728 | 0 | 246.2728 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
202 | 19 | July | 2.8 | 3.4472 | 0 | 97.902 | 97.902 | 0 | 97.902 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
202 | 20 | July | 2.6 | 3.201 | 0 | 13.23 | 13.23 | 0 | 13.23 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
202 | 21 | July | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
202 | 22 | July | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
202 | 23 | July | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
202 | 24 | July | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
203 | 1 | July | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
203 | 2 | July | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
203 | 3 | July | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
203 | 4 | July | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
203 | 5 | July | 5.1 | 6.2788 | 312.8 | 7.938 | 320.738 | 0 | 320.738 | 0 | 0 | 97.5251 | 2.4749 | 0 | 97.5251 | 2.4749 | 0
203 | 6 | July | 5.1 | 6.2788 | 312.8 | 47.628 | 360.428 | 0 | 360.428 | 0 | 0 | 86.7857 | 13.2143 | 0 | 86.7857 | 13.2143 | 0
203 | 7 | July | 5.7 | 7.0175 | 504.9 | 113.778 | 618.678 | 0 | 618.678 | 0 | 0 | 81.6095 | 18.3905 | 0 | 81.6095 | 18.3905 | 0
203 | 8 | July | 5.1 | 6.2788 | 312.8 | 189.189 | 501.989 | 0 | 501.989 | 0 | 0 | 62.3121 | 37.6879 | 0 | 62.3121 | 37.6879 | 0
203 | 9 | July | 6.7 | 8.2487 | 761.6 | 262.7277 | 1024.3277 | 0 | 1024.3277 | 0 | 0 | 74.3512 | 25.6488 | 0 | 74.3512 | 25.6488 | 0
203 | 10 | July | 6.7 | 8.2487 | 761.6 | 539.9684 | 1301.5684 | 0 | 1301.5684 | 0 | 0 | 58.514 | 41.486 | 0 | 58.514 | 41.486 | 0
203 | 11 | July | 7.2 | 8.8642 | 908.65 | 374.5436 | 1283.1936 | 0 | 1283.1936 | 0 | 0 | 70.8116 | 29.1884 | 0 | 70.8116 | 29.1884 | 0
203 | 12 | July | 8.7 | 10.711 | 1490.05 | 392.3725 | 1882.4225 | 0 | 1882.4225 | 0 | 0 | 79.156 | 20.844 | 0 | 79.156 | 20.844 | 0
203 | 13 | July | 8.2 | 10.0954 | 1359.15 | 388.6824 | 1747.8324 | 0 | 1747.8324 | 0 | 0 | 77.762 | 22.238 | 0 | 77.762 | 22.238 | 0
203 | 14 | July | 9.3 | 11.4496 | 1598.85 | 617.7948 | 2216.6448 | 1 | 2000 | 216.6448 | 10.8322 | 72.1293 | 20.0575 | 35.0674 | 69.1103 | 27.8707 | 13.55
203 | 15 | July | 10.3 | 12.6808 | 1694.9 | 525.8322 | 2220.7322 | 1 | 2000 | 220.7322 | 11.0366 | 76.3217 | 15.255 | 41.9777 | 73.7084 | 23.6783 | 13.0233
203 | 16 | July | 13.4 | 16.4973 | 1700 | 419.7741 | 2119.7741 | 1 | 2000 | 119.7741 | 5.9887 | 80.1972 | 15 | 28.533 | 79.0113 | 19.8028 | 7.0455
203 | 17 | July | 9.3 | 11.4496 | 1598.85 | 298.1175 | 1896.9675 | 0 | 1896.9675 | 0 | 0 | 84.2845 | 15.7155 | 0 | 84.2845 | 15.7155 | 0
203 | 18 | July | 10.8 | 13.2964 | 1698.3 | 177.5273 | 1875.8273 | 0 | 1875.8273 | 0 | 0 | 90.5361 | 9.4639 | 0 | 90.5361 | 9.4639 | 0
203 | 19 | July | 7.2 | 8.8642 | 908.65 | 75.411 | 984.061 | 0 | 984.061 | 0 | 0 | 92.3368 | 7.6632 | 0 | 92.3368 | 7.6632 | 0
203 | 20 | July | 7.7 | 9.4798 | 1059.95 | 11.907 | 1071.857 | 0 | 1071.857 | 0 | 0 | 98.8891 | 1.1109 | 0 | 98.8891 | 1.1109 | 0
203 | 21 | July | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
203 | 22 | July | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
203 | 23 | July | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
203 | 24 | July | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
204 | 1 | July | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
204 | 2 | July | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
204 | 3 | July | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
204 | 4 | July | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
204 | 5 | July | 3.1 | 3.8165 | 0 | 21.168 | 21.168 | 0 | 21.168 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
204 | 6 | July | 3.6 | 4.4321 | 75.65 | 121.8703 | 197.5203 | 0 | 197.5203 | 0 | 0 | 38.2999 | 61.7001 | 0 | 38.2999 | 61.7001 | 0
204 | 7 | July | 3.1 | 3.8165 | 0 | 360.0358 | 360.0358 | 0 | 360.0358 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
204 | 8 | July | 2.6 | 3.201 | 0 | 682.4299 | 682.4299 | 0 | 682.4299 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
204 | 9 | July | 3.1 | 3.8165 | 0 | 945.2299 | 945.2299 | 0 | 945.2299 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
204 | 10 | July | 2.1 | 2.5854 | 0 | 1206.3441 | 1206.3441 | 0 | 1206.3441 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
204 | 11 | July | 3.1 | 3.8165 | 0 | 1403.5533 | 1403.5533 | 0 | 1403.5533 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
204 | 12 | July | 5.1 | 6.2788 | 312.8 | 1488.6604 | 1801.4604 | 0 | 1801.4604 | 0 | 0 | 17.3637 | 82.6363 | 0 | 17.3637 | 82.6363 | 0
204 | 13 | July | 5.7 | 7.0175 | 504.9 | 1426.5403 | 1931.4403 | 0 | 1931.4403 | 0 | 0 | 26.1411 | 73.8589 | 0 | 26.1411 | 73.8589 | 0
204 | 14 | July | 7.2 | 8.8642 | 908.65 | 1287.2357 | 2195.8857 | 1 | 2000 | 195.8857 | 9.7943 | 41.3797 | 54.5675 | 15.2175 | 35.6382 | 58.6203 | 21.5579
204 | 15 | July | 6.7 | 8.2487 | 761.6 | 1072.7963 | 1834.3963 | 0 | 1834.3963 | 0 | 0 | 41.5177 | 58.4823 | 0 | 41.5177 | 58.4823 | 0
204 | 16 | July | 6.7 | 8.2487 | 761.6 | 788.6753 | 1550.2753 | 0 | 1550.2753 | 0 | 0 | 49.1268 | 50.8732 | 0 | 49.1268 | 50.8732 | 0
204 | 17 | July | 6.2 | 7.6331 | 625.6 | 484.2064 | 1109.8064 | 0 | 1109.8064 | 0 | 0 | 56.3702 | 43.6298 | 0 | 56.3702 | 43.6298 | 0
204 | 18 | July | 5.1 | 6.2788 | 312.8 | 223.0692 | 535.8692 | 0 | 535.8692 | 0 | 0 | 58.3725 | 41.6275 | 0 | 58.3725 | 41.6275 | 0
204 | 19 | July | 3.6 | 4.4321 | 75.65 | 96.579 | 172.229 | 0 | 172.229 | 0 | 0 | 43.9241 | 56.0759 | 0 | 43.9241 | 56.0759 | 0
204 | 20 | July | 3.1 | 3.8165 | 0 | 21.168 | 21.168 | 0 | 21.168 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
204 | 21 | July | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
204 | 22 | July | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
204 | 23 | July | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
204 | 24 | July | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
205 | 1 | July | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
205 | 2 | July | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
205 | 3 | July | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
205 | 4 | July | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
205 | 5 | July | 2.1 | 2.5854 | 0 | 19.845 | 19.845 | 0 | 19.845 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
205 | 6 | July | 3.1 | 3.8165 | 0 | 122.26 | 122.26 | 0 | 122.26 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
205 | 7 | July | 3.6 | 4.4321 | 75.65 | 356.559 | 432.209 | 0 | 432.209 | 0 | 0 | 17.5031 | 82.4969 | 0 | 17.5031 | 82.4969 | 0
205 | 8 | July | 2.6 | 3.201 | 0 | 674.8112 | 674.8112 | 0 | 674.8112 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
205 | 9 | July | 1 | 1.2311 | 0 | 983.5399 | 983.5399 | 0 | 983.5399 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
205 | 10 | July | 1 | 1.2311 | 0 | 1216.0113 | 1216.0113 | 0 | 1216.0113 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
205 | 11 | July | 3.1 | 3.8165 | 0 | 1325.768 | 1325.768 | 0 | 1325.768 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
205 | 12 | July | 4.1 | 5.0477 | 173.4 | 1384.6798 | 1558.0798 | 0 | 1558.0798 | 0 | 0 | 11.1291 | 88.8709 | 0 | 11.1291 | 88.8709 | 0
205 | 13 | July | 5.1 | 6.2788 | 312.8 | 925.2311 | 1238.0311 | 0 | 1238.0311 | 0 | 0 | 25.2659 | 74.7341 | 0 | 25.2659 | 74.7341 | 0
205 | 14 | July | 5.1 | 6.2788 | 312.8 | 1121.5653 | 1434.3653 | 0 | 1434.3653 | 0 | 0 | 21.8076 | 78.1924 | 0 | 21.8076 | 78.1924 | 0
205 | 15 | July | 4.6 | 5.6633 | 237.15 | 835.7354 | 1072.8854 | 0 | 1072.8854 | 0 | 0 | 22.1039 | 77.8961 | 0 | 22.1039 | 77.8961 | 0
205 | 16 | July | 4.1 | 5.0477 | 173.4 | 772.0556 | 945.4556 | 0 | 945.4556 | 0 | 0 | 18.3404 | 81.6596 | 0 | 18.3404 | 81.6596 | 0
205 | 17 | July | 4.1 | 5.0477 | 173.4 | 478.0378 | 651.4378 | 0 | 651.4378 | 0 | 0 | 26.618 | 73.382 | 0 | 26.618 | 73.382 | 0
205 | 18 | July | 3.1 | 3.8165 | 0 | 229.2951 | 229.2951 | 0 | 229.2951 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
205 | 19 | July | 3.1 | 3.8165 | 0 | 95.256 | 95.256 | 0 | 95.256 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
205 | 20 | July | 3.1 | 3.8165 | 0 | 14.553 | 14.553 | 0 | 14.553 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
205 | 21 | July | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
205 | 22 | July | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
205 | 23 | July | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
205 | 24 | July | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
206 | 1 | July | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
206 | 2 | July | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
206 | 3 | July | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
206 | 4 | July | 0.5 | 0.61557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
206 | 5 | July | 2.1 | 2.5854 | 0 | 15.876 | 15.876 | 0 | 15.876 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
206 | 6 | July | 3.6 | 4.4321 | 75.65 | 103.0806 | 178.7306 | 0 | 178.7306 | 0 | 0 | 42.3263 | 57.6737 | 0 | 42.3263 | 57.6737 | 0
206 | 7 | July | 4.1 | 5.0477 | 173.4 | 331.381 | 504.781 | 0 | 504.781 | 0 | 0 | 34.3515 | 65.6485 | 0 | 34.3515 | 65.6485 | 0
206 | 8 | July | 4.6 | 5.6633 | 237.15 | 419.0661 | 656.2161 | 0 | 656.2161 | 0 | 0 | 36.139 | 63.861 | 0 | 36.139 | 63.861 | 0
206 | 9 | July | 5.7 | 7.0175 | 504.9 | 829.3701 | 1334.2701 | 0 | 1334.2701 | 0 | 0 | 37.8409 | 62.1591 | 0 | 37.8409 | 62.1591 | 0
206 | 10 | July | 5.1 | 6.2788 | 312.8 | 913.3844 | 1226.1844 | 0 | 1226.1844 | 0 | 0 | 25.51 | 74.49 | 0 | 25.51 | 74.49 | 0
206 | 11 | July | 5.1 | 6.2788 | 312.8 | 630.2934 | 943.0934 | 0 | 943.0934 | 0 | 0 | 33.1674 | 66.8326 | 0 | 33.1674 | 66.8326 | 0
206 | 12 | July | 4.6 | 5.6633 | 237.15 | 910.5945 | 1147.7445 | 0 | 1147.7445 | 0 | 0 | 20.6623 | 79.3377 | 0 | 20.6623 | 79.3377 | 0
206 | 13 | July | 4.6 | 5.6633 | 237.15 | 650.9465 | 888.0965 | 0 | 888.0965 | 0 | 0 | 26.7032 | 73.2968 | 0 | 26.7032 | 73.2968 | 0
206 | 14 | July | 5.1 | 6.2788 | 312.8 | 601.7535 | 914.5535 | 0 | 914.5535 | 0 | 0 | 34.2025 | 65.7975 | 0 | 34.2025 | 65.7975 | 0
206 | 15 | July | 5.7 | 7.0175 | 504.9 | 519.2037 | 1024.1037 | 0 | 1024.1037 | 0 | 0 | 49.3016 | 50.6984 | 0 | 49.3016 | 50.6984 | 0
206 | 16 | July | 5.7 | 7.0175 | 504.9 | 256.7476 | 761.6476 | 0 | 761.6476 | 0 | 0 | 66.2905 | 33.7095 | 0 | 66.2905 | 33.7095 | 0
206 | 17 | July | 6.2 | 7.6331 | 625.6 | 292.4195 | 918.0195 | 0 | 918.0195 | 0 | 0 | 68.1467 | 31.8533 | 0 | 68.1467 | 31.8533 | 0
206 | 18 | July | 6.2 | 7.6331 | 625.6 | 239.0775 | 864.6775 | 0 | 864.6775 | 0 | 0 | 72.3507 | 27.6493 | 0 | 72.3507 | 27.6493 | 0
206 | 19 | July | 6.2 | 7.6331 | 625.6 | 89.964 | 715.564 | 0 | 715.564 | 0 | 0 | 87.4275 | 12.5725 | 0 | 87.4275 | 12.5725 | 0
206 | 20 | July | 6.2 | 7.6331 | 625.6 | 18.522 | 644.122 | 0 | 644.122 | 0 | 0 | 97.1245 | 2.8755 | 0 | 97.1245 | 2.8755 | 0
206 | 21 | July | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
206 | 22 | July | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
206 | 23 | July | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
206 | 24 | July | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
207 | 1 | July | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
207 | 2 | July | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
207 | 3 | July | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
207 | 4 | July | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
207 | 5 | July | 8.2 | 10.0954 | 1359.15 | 13.23 | 1372.38 | 0 | 1372.38 | 0 | 0 | 99.036 | 0.96402 | 0 | 99.036 | 0.96402 | 0
207 | 6 | July | 7.2 | 8.8642 | 908.65 | 68.796 | 977.446 | 0 | 977.446 | 0 | 0 | 92.9617 | 7.0383 | 0 | 92.9617 | 7.0383 | 0
207 | 7 | July | 8.2 | 10.0954 | 1359.15 | 175.8955 | 1535.0455 | 0 | 1535.0455 | 0 | 0 | 88.5414 | 11.4586 | 0 | 88.5414 | 11.4586 | 0
207 | 8 | July | 5.7 | 7.0175 | 504.9 | 300.6931 | 805.5931 | 0 | 805.5931 | 0 | 0 | 62.6743 | 37.3257 | 0 | 62.6743 | 37.3257 | 0
207 | 9 | July | 4.1 | 5.0477 | 173.4 | 424.519 | 597.919 | 0 | 597.919 | 0 | 0 | 29.0006 | 70.9994 | 0 | 29.0006 | 70.9994 | 0
207 | 10 | July | 6.2 | 7.6331 | 625.6 | 533.2552 | 1158.8552 | 0 | 1158.8552 | 0 | 0 | 53.9843 | 46.0157 | 0 | 53.9843 | 46.0157 | 0
207 | 11 | July | 8.2 | 10.0954 | 1359.15 | 368.9938 | 1728.1438 | 0 | 1728.1438 | 0 | 0 | 78.648 | 21.352 | 0 | 78.648 | 21.352 | 0
207 | 12 | July | 7.7 | 9.4798 | 1059.95 | 385.2253 | 1445.1753 | 0 | 1445.1753 | 0 | 0 | 73.344 | 26.656 | 0 | 73.344 | 26.656 | 0
207 | 13 | July | 6.7 | 8.2487 | 761.6 | 384.6976 | 1146.2976 | 0 | 1146.2976 | 0 | 0 | 66.44 | 33.56 | 0 | 66.44 | 33.56 | 0
207 | 14 | July | 6.7 | 8.2487 | 761.6 | 360.6032 | 1122.2032 | 0 | 1122.2032 | 0 | 0 | 67.8665 | 32.1335 | 0 | 67.8665 | 32.1335 | 0
207 | 15 | July | 7.7 | 9.4798 | 1059.95 | 517.9631 | 1577.9131 | 0 | 1577.9131 | 0 | 0 | 67.1742 | 32.8258 | 0 | 67.1742 | 32.8258 | 0
207 | 16 | July | 7.7 | 9.4798 | 1059.95 | 411.969 | 1471.919 | 0 | 1471.919 | 0 | 0 | 72.0114 | 27.9886 | 0 | 72.0114 | 27.9886 | 0
207 | 17 | July | 5.7 | 7.0175 | 504.9 | 183.897 | 688.797 | 0 | 688.797 | 0 | 0 | 73.3017 | 26.6983 | 0 | 73.3017 | 26.6983 | 0
207 | 18 | July | 6.2 | 7.6331 | 625.6 | 108.486 | 734.086 | 0 | 734.086 | 0 | 0 | 85.2216 | 14.7784 | 0 | 85.2216 | 14.7784 | 0
207 | 19 | July | 3.6 | 4.4321 | 75.65 | 68.796 | 144.446 | 0 | 144.446 | 0 | 0 | 52.3725 | 47.6275 | 0 | 52.3725 | 47.6275 | 0
207 | 20 | July | 3.6 | 4.4321 | 75.65 | 17.199 | 92.849 | 0 | 92.849 | 0 | 0 | 81.4764 | 18.5236 | 0 | 81.4764 | 18.5236 | 0
207 | 21 | July | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
207 | 22 | July | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
207 | 23 | July | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
207 | 24 | July | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
208 | 1 | July | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
208 | 2 | July | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
208 | 3 | July | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
208 | 4 | July | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
208 | 5 | July | 5.7 | 7.0175 | 504.9 | 6.615 | 511.515 | 0 | 511.515 | 0 | 0 | 98.7068 | 1.2932 | 0 | 98.7068 | 1.2932 | 0
208 | 6 | July | 5.7 | 7.0175 | 504.9 | 42.336 | 547.236 | 0 | 547.236 | 0 | 0 | 92.2637 | 7.7363 | 0 | 92.2637 | 7.7363 | 0
208 | 7 | July | 5.7 | 7.0175 | 504.9 | 108.486 | 613.386 | 0 | 613.386 | 0 | 0 | 82.3136 | 17.6864 | 0 | 82.3136 | 17.6864 | 0
208 | 8 | July | 6.7 | 8.2487 | 761.6 | 183.897 | 945.497 | 0 | 945.497 | 0 | 0 | 80.5502 | 19.4498 | 0 | 80.5502 | 19.4498 | 0
208 | 9 | July | 7.7 | 9.4798 | 1059.95 | 430.277 | 1490.227 | 0 | 1490.227 | 0 | 0 | 71.1267 | 28.8733 | 0 | 71.1267 | 28.8733 | 0
208 | 10 | July | 7.2 | 8.8642 | 908.65 | 534.6094 | 1443.2594 | 0 | 1443.2594 | 0 | 0 | 62.9582 | 37.0418 | 0 | 62.9582 | 37.0418 | 0
208 | 11 | July | 7.7 | 9.4798 | 1059.95 | 867.9114 | 1927.8614 | 0 | 1927.8614 | 0 | 0 | 54.9806 | 45.0194 | 0 | 54.9806 | 45.0194 | 0
208 | 12 | July | 8.7 | 10.711 | 1490.05 | 898.8371 | 2388.8871 | 1 | 2000 | 388.8871 | 19.4444 | 62.3742 | 25.4975 | 43.2656 | 55.0581 | 37.6258 | 26.0989
208 | 13 | July | 7.7 | 9.4798 | 1059.95 | 1104.9671 | 2164.9171 | 1 | 2000 | 164.9171 | 8.2459 | 48.9603 | 47.0025 | 14.9251 | 44.7516 | 51.0397 | 15.5589
208 | 14 | July | 7.7 | 9.4798 | 1059.95 | 1208.3814 | 2268.3314 | 1 | 2000 | 268.3314 | 13.4166 | 46.7282 | 47.0025 | 22.2059 | 39.5809 | 53.2718 | 25.3155
208 | 15 | July | 6.2 | 7.6331 | 625.6 | 834.592 | 1460.192 | 0 | 1460.192 | 0 | 0 | 42.8437 | 57.1563 | 0 | 42.8437 | 57.1563 | 0
208 | 16 | July | 8.2 | 10.0954 | 1359.15 | 414.0914 | 1773.2414 | 0 | 1773.2414 | 0 | 0 | 76.6478 | 23.3522 | 0 | 76.6478 | 23.3522 | 0
208 | 17 | July | 5.1 | 6.2788 | 312.8 | 364.9485 | 677.7485 | 0 | 677.7485 | 0 | 0 | 46.1528 | 53.8472 | 0 | 46.1528 | 53.8472 | 0
208 | 18 | July | 4.1 | 5.0477 | 173.4 | 219.6122 | 393.0122 | 0 | 393.0122 | 0 | 0 | 44.1208 | 55.8792 | 0 | 44.1208 | 55.8792 | 0
208 | 19 | July | 3.1 | 3.8165 | 0 | 67.473 | 67.473 | 0 | 67.473 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
208 | 20 | July | 5.1 | 6.2788 | 312.8 | 9.261 | 322.061 | 0 | 322.061 | 0 | 0 | 97.1245 | 2.8755 | 0 | 97.1245 | 2.8755 | 0
208 | 21 | July | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
208 | 22 | July | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
208 | 23 | July | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
208 | 24 | July | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
209 | 1 | July | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
209 | 2 | July | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
209 | 3 | July | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
209 | 4 | July | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
209 | 5 | July | 4.1 | 5.0477 | 173.4 | 5.292 | 178.692 | 0 | 178.692 | 0 | 0 | 97.0385 | 2.9615 | 0 | 97.0385 | 2.9615 | 0
209 | 6 | July | 4.6 | 5.6633 | 237.15 | 41.013 | 278.163 | 0 | 278.163 | 0 | 0 | 85.2558 | 14.7442 | 0 | 85.2558 | 14.7442 | 0
209 | 7 | July | 5.7 | 7.0175 | 504.9 | 105.84 | 610.74 | 0 | 610.74 | 0 | 0 | 82.6702 | 17.3298 | 0 | 82.6702 | 17.3298 | 0
209 | 8 | July | 5.7 | 7.0175 | 504.9 | 181.251 | 686.151 | 0 | 686.151 | 0 | 0 | 73.5844 | 26.4156 | 0 | 73.5844 | 26.4156 | 0
209 | 9 | July | 5.7 | 7.0175 | 504.9 | 425.2097 | 930.1097 | 0 | 930.1097 | 0 | 0 | 54.2839 | 45.7161 | 0 | 54.2839 | 45.7161 | 0
209 | 10 | July | 5.7 | 7.0175 | 504.9 | 316.7332 | 821.6332 | 0 | 821.6332 | 0 | 0 | 61.4508 | 38.5492 | 0 | 61.4508 | 38.5492 | 0
209 | 11 | July | 5.7 | 7.0175 | 504.9 | 359.3539 | 864.2539 | 0 | 864.2539 | 0 | 0 | 58.4203 | 41.5797 | 0 | 58.4203 | 41.5797 | 0
209 | 12 | July | 5.1 | 6.2788 | 312.8 | 383.8929 | 696.6929 | 0 | 696.6929 | 0 | 0 | 44.8978 | 55.1022 | 0 | 44.8978 | 55.1022 | 0
209 | 13 | July | 7.2 | 8.8642 | 908.65 | 383.3634 | 1292.0134 | 0 | 1292.0134 | 0 | 0 | 70.3282 | 29.6718 | 0 | 70.3282 | 29.6718 | 0
209 | 14 | July | 6.2 | 7.6331 | 625.6 | 359.2657 | 984.8657 | 0 | 984.8657 | 0 | 0 | 63.5213 | 36.4787 | 0 | 63.5213 | 36.4787 | 0
209 | 15 | July | 6.2 | 7.6331 | 625.6 | 313.9867 | 939.5867 | 0 | 939.5867 | 0 | 0 | 66.5825 | 33.4175 | 0 | 66.5825 | 33.4175 | 0
209 | 16 | July | 5.7 | 7.0175 | 504.9 | 252.7088 | 757.6088 | 0 | 757.6088 | 0 | 0 | 66.6439 | 33.3561 | 0 | 66.6439 | 33.3561 | 0
209 | 17 | July | 5.1 | 6.2788 | 312.8 | 286.3588 | 599.1588 | 0 | 599.1588 | 0 | 0 | 52.2065 | 47.7935 | 0 | 52.2065 | 47.7935 | 0
209 | 18 | July | 4.1 | 5.0477 | 173.4 | 105.84 | 279.24 | 0 | 279.24 | 0 | 0 | 62.0971 | 37.9029 | 0 | 62.0971 | 37.9029 | 0
209 | 19 | July | 4.6 | 5.6633 | 237.15 | 83.349 | 320.499 | 0 | 320.499 | 0 | 0 | 73.994 | 26.006 | 0 | 73.994 | 26.006 | 0
209 | 20 | July | 3.6 | 4.4321 | 75.65 | 15.876 | 91.526 | 0 | 91.526 | 0 | 0 | 82.6541 | 17.3459 | 0 | 82.6541 | 17.3459 | 0
209 | 21 | July | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
209 | 22 | July | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
209 | 23 | July | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
209 | 24 | July | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
210 | 1 | July | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
210 | 2 | July | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
210 | 3 | July | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
210 | 4 | July | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
210 | 5 | July | 4.6 | 5.6633 | 237.15 | 5.292 | 242.442 | 0 | 242.442 | 0 | 0 | 97.8172 | 2.1828 | 0 | 97.8172 | 2.1828 | 0
210 | 6 | July | 3.6 | 4.4321 | 75.65 | 39.69 | 115.34 | 0 | 115.34 | 0 | 0 | 65.5887 | 34.4113 | 0 | 65.5887 | 34.4113 | 0
210 | 7 | July | 5.1 | 6.2788 | 312.8 | 105.84 | 418.64 | 0 | 418.64 | 0 | 0 | 74.7181 | 25.2819 | 0 | 74.7181 | 25.2819 | 0
210 | 8 | July | 3.1 | 3.8165 | 0 | 298.4823 | 298.4823 | 0 | 298.4823 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
210 | 9 | July | 4.1 | 5.0477 | 173.4 | 426.1846 | 599.5846 | 0 | 599.5846 | 0 | 0 | 28.92 | 71.08 | 0 | 28.92 | 71.08 | 0
210 | 10 | July | 5.7 | 7.0175 | 504.9 | 732.3242 | 1237.2242 | 0 | 1237.2242 | 0 | 0 | 40.8091 | 59.1909 | 0 | 40.8091 | 59.1909 | 0
210 | 11 | July | 6.2 | 7.6331 | 625.6 | 618.0602 | 1243.6602 | 0 | 1243.6602 | 0 | 0 | 50.3031 | 49.6969 | 0 | 50.3031 | 49.6969 | 0
210 | 12 | July | 8.2 | 10.0954 | 1359.15 | 1275.7012 | 2634.8512 | 1 | 2000 | 634.8512 | 31.7426 | 51.5836 | 32.0425 | 49.7649 | 36.2149 | 48.4164 | 46.7094
210 | 13 | July | 7.5 | 9.2336 | 1059.95 | 1085.5537 | 2145.5037 | 1 | 2000 | 145.5037 | 7.2752 | 49.4033 | 47.0025 | 13.4036 | 45.7223 | 50.5967 | 13.7274
210 | 14 | July | 6.7 | 8.2487 | 761.6 | 610.8029 | 1372.4029 | 0 | 1372.4029 | 0 | 0 | 55.4939 | 44.5061 | 0 | 55.4939 | 44.5061 | 0
210 | 15 | July | 5.7 | 7.0175 | 504.9 | 688.2764 | 1193.1764 | 0 | 1193.1764 | 0 | 0 | 42.3156 | 57.6844 | 0 | 42.3156 | 57.6844 | 0
210 | 16 | July | 6.7 | 8.2487 | 761.6 | 408.6092 | 1170.2092 | 0 | 1170.2092 | 0 | 0 | 65.0824 | 34.9176 | 0 | 65.0824 | 34.9176 | 0
210 | 17 | July | 4.6 | 5.6633 | 237.15 | 285.2975 | 522.4475 | 0 | 522.4475 | 0 | 0 | 45.3921 | 54.6079 | 0 | 45.3921 | 54.6079 | 0
210 | 18 | July | 7.2 | 8.8642 | 908.65 | 165.2053 | 1073.8553 | 0 | 1073.8553 | 0 | 0 | 84.6157 | 15.3843 | 0 | 84.6157 | 15.3843 | 0
210 | 19 | July | 5.7 | 7.0175 | 504.9 | 39.69 | 544.59 | 0 | 544.59 | 0 | 0 | 92.7119 | 7.2881 | 0 | 92.7119 | 7.2881 | 0
210 | 20 | July | 6.2 | 7.6331 | 625.6 | 5.292 | 630.892 | 0 | 630.892 | 0 | 0 | 99.1612 | 0.83881 | 0 | 99.1612 | 0.83881 | 0
210 | 21 | July | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
210 | 22 | July | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
210 | 23 | July | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
210 | 24 | July | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
211 | 1 | July | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
211 | 2 | July | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
211 | 3 | July | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
211 | 4 | July | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
211 | 5 | July | 5.1 | 6.2788 | 312.8 | 5.292 | 318.092 | 0 | 318.092 | 0 | 0 | 98.3363 | 1.6637 | 0 | 98.3363 | 1.6637 | 0
211 | 6 | July | 3.6 | 4.4321 | 75.65 | 38.367 | 114.017 | 0 | 114.017 | 0 | 0 | 66.3498 | 33.6502 | 0 | 66.3498 | 33.6502 | 0
211 | 7 | July | 5.7 | 7.0175 | 504.9 | 104.517 | 609.417 | 0 | 609.417 | 0 | 0 | 82.8497 | 17.1503 | 0 | 82.8497 | 17.1503 | 0
211 | 8 | July | 6.2 | 7.6331 | 625.6 | 295.7842 | 921.3842 | 0 | 921.3842 | 0 | 0 | 67.8978 | 32.1022 | 0 | 67.8978 | 32.1022 | 0
211 | 9 | July | 6.7 | 8.2487 | 761.6 | 252.1124 | 1013.7124 | 0 | 1013.7124 | 0 | 0 | 75.1298 | 24.8702 | 0 | 75.1298 | 24.8702 | 0
211 | 10 | July | 7.2 | 8.8642 | 908.65 | 529.0976 | 1437.7476 | 0 | 1437.7476 | 0 | 0 | 63.1996 | 36.8004 | 0 | 63.1996 | 36.8004 | 0
211 | 11 | July | 7.2 | 8.8642 | 908.65 | 608.404 | 1517.054 | 0 | 1517.054 | 0 | 0 | 59.8957 | 40.1043 | 0 | 59.8957 | 40.1043 | 0
211 | 12 | July | 6.7 | 8.2487 | 761.6 | 643.0883 | 1404.6883 | 0 | 1404.6883 | 0 | 0 | 54.2184 | 45.7816 | 0 | 54.2184 | 45.7816 | 0
211 | 13 | July | 5.1 | 6.2788 | 312.8 | 638.8808 | 951.6808 | 0 | 951.6808 | 0 | 0 | 32.8682 | 67.1318 | 0 | 32.8682 | 67.1318 | 0
211 | 14 | July | 3.6 | 4.4321 | 75.65 | 594.8871 | 670.5371 | 0 | 670.5371 | 0 | 0 | 11.282 | 88.718 | 0 | 11.282 | 88.718 | 0
211 | 15 | July | 4.1 | 5.0477 | 173.4 | 513.3839 | 686.7839 | 0 | 686.7839 | 0 | 0 | 25.2481 | 74.7519 | 0 | 25.2481 | 74.7519 | 0
211 | 16 | July | 5.7 | 7.0175 | 504.9 | 404.958 | 909.858 | 0 | 909.858 | 0 | 0 | 55.4922 | 44.5078 | 0 | 55.4922 | 44.5078 | 0
211 | 17 | July | 6.2 | 7.6331 | 625.6 | 440.949 | 1066.549 | 0 | 1066.549 | 0 | 0 | 58.6565 | 41.3435 | 0 | 58.6565 | 41.3435 | 0
211 | 18 | July | 6.7 | 8.2487 | 761.6 | 161.0036 | 922.6036 | 0 | 922.6036 | 0 | 0 | 82.549 | 17.451 | 0 | 82.549 | 17.451 | 0
211 | 19 | July | 6.7 | 8.2487 | 761.6 | 62.181 | 823.781 | 0 | 823.781 | 0 | 0 | 92.4518 | 7.5482 | 0 | 92.4518 | 7.5482 | 0
211 | 20 | July | 5.1 | 6.2788 | 312.8 | 14.553 | 327.353 | 0 | 327.353 | 0 | 0 | 95.5543 | 4.4457 | 0 | 95.5543 | 4.4457 | 0
211 | 21 | July | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
211 | 22 | July | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
211 | 23 | July | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
211 | 24 | July | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
212 | 1 | July | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
212 | 2 | July | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
212 | 3 | July | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
212 | 4 | July | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
212 | 5 | July | 2.3 | 2.8316 | 0 | 6.615 | 6.615 | 0 | 6.615 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
212 | 6 | July | 3.1 | 3.8165 | 0 | 60.858 | 60.858 | 0 | 60.858 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
212 | 7 | July | 4.1 | 5.0477 | 173.4 | 165.3987 | 338.7987 | 0 | 338.7987 | 0 | 0 | 51.1808 | 48.8192 | 0 | 51.1808 | 48.8192 | 0
212 | 8 | July | 5.1 | 6.2788 | 312.8 | 404.5506 | 717.3506 | 0 | 717.3506 | 0 | 0 | 43.6049 | 56.3951 | 0 | 43.6049 | 56.3951 | 0
212 | 9 | July | 4.1 | 5.0477 | 173.4 | 424.1533 | 597.5533 | 0 | 597.5533 | 0 | 0 | 29.0183 | 70.9817 | 0 | 29.0183 | 70.9817 | 0
212 | 10 | July | 4.1 | 5.0477 | 173.4 | 730.7915 | 904.1915 | 0 | 904.1915 | 0 | 0 | 19.1774 | 80.8226 | 0 | 19.1774 | 80.8226 | 0
212 | 11 | July | 4.1 | 5.0477 | 173.4 | 612.4435 | 785.8435 | 0 | 785.8435 | 0 | 0 | 22.0655 | 77.9345 | 0 | 22.0655 | 77.9345 | 0
212 | 12 | July | 6.2 | 7.6331 | 625.6 | 902.4134 | 1528.0134 | 0 | 1528.0134 | 0 | 0 | 40.942 | 59.058 | 0 | 40.942 | 59.058 | 0
212 | 13 | July | 3.6 | 4.4321 | 75.65 | 875.4904 | 951.1404 | 0 | 951.1404 | 0 | 0 | 7.9536 | 92.0464 | 0 | 7.9536 | 92.0464 | 0
212 | 14 | July | 4.1 | 5.0477 | 173.4 | 598.3658 | 771.7658 | 0 | 771.7658 | 0 | 0 | 22.468 | 77.532 | 0 | 22.468 | 77.532 | 0
212 | 15 | July | 3.6 | 4.4321 | 75.65 | 510.6425 | 586.2925 | 0 | 586.2925 | 0 | 0 | 12.9031 | 87.0969 | 0 | 12.9031 | 87.0969 | 0
212 | 16 | July | 2.1 | 2.5854 | 0 | 527.4496 | 527.4496 | 0 | 527.4496 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
212 | 17 | July | 3.6 | 4.4321 | 75.65 | 435.1041 | 510.7541 | 0 | 510.7541 | 0 | 0 | 14.8114 | 85.1886 | 0 | 14.8114 | 85.1886 | 0
212 | 18 | July | 3.1 | 3.8165 | 0 | 182.8746 | 182.8746 | 0 | 182.8746 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
212 | 19 | July | 2.6 | 3.201 | 0 | 76.734 | 76.734 | 0 | 76.734 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
212 | 20 | July | 2.1 | 2.5854 | 0 | 7.938 | 7.938 | 0 | 7.938 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
212 | 21 | July | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
212 | 22 | July | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
212 | 23 | July | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
212 | 24 | July | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213 | 1 | August | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213 | 2 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213 | 3 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213 | 4 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213 | 5 | August | 1 | 1.2311 | 0 | 10.584 | 10.584 | 0 | 10.584 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
213 | 6 | August | 1 | 1.2311 | 0 | 92.6959 | 92.6959 | 0 | 92.6959 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
213 | 7 | August | 2.6 | 3.201 | 0 | 289.7735 | 289.7735 | 0 | 289.7735 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
213 | 8 | August | 0 | 0 | 0 | 294.9262 | 294.9262 | 0 | 294.9262 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
213 | 9 | August | 1 | 1.2311 | 0 | 247.9884 | 247.9884 | 0 | 247.9884 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
213 | 10 | August | 1 | 1.2311 | 0 | 308.7016 | 308.7016 | 0 | 308.7016 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
213 | 11 | August | 2.6 | 3.201 | 0 | 357.9584 | 357.9584 | 0 | 357.9584 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
213 | 12 | August | 3.6 | 4.4321 | 75.65 | 380.1281 | 455.7781 | 0 | 455.7781 | 0 | 0 | 16.598 | 83.402 | 0 | 16.598 | 83.402 | 0
213 | 13 | August | 3.6 | 4.4321 | 75.65 | 639.6744 | 715.3244 | 0 | 715.3244 | 0 | 0 | 10.5756 | 89.4244 | 0 | 10.5756 | 89.4244 | 0
213 | 14 | August | 6.7 | 8.2487 | 761.6 | 1105.8823 | 1867.4823 | 0 | 1867.4823 | 0 | 0 | 40.7822 | 59.2178 | 0 | 40.7822 | 59.2178 | 0
213 | 15 | August | 4.1 | 5.0477 | 173.4 | 820.0609 | 993.4609 | 0 | 993.4609 | 0 | 0 | 17.4541 | 82.5459 | 0 | 17.4541 | 82.5459 | 0
213 | 16 | August | 3.6 | 4.4321 | 75.65 | 616.279 | 691.929 | 0 | 691.929 | 0 | 0 | 10.9332 | 89.0668 | 0 | 10.9332 | 89.0668 | 0
213 | 17 | August | 0 | 0 | 0 | 420.6365 | 420.6365 | 0 | 420.6365 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
213 | 18 | August | 3.6 | 4.4321 | 75.65 | 198.4338 | 274.0838 | 0 | 274.0838 | 0 | 0 | 27.6011 | 72.3989 | 0 | 27.6011 | 72.3989 | 0
213 | 19 | August | 3.6 | 4.4321 | 75.65 | 87.318 | 162.968 | 0 | 162.968 | 0 | 0 | 46.4202 | 53.5798 | 0 | 46.4202 | 53.5798 | 0
213 | 20 | August | 3.6 | 4.4321 | 75.65 | 11.907 | 87.557 | 0 | 87.557 | 0 | 0 | 86.4009 | 13.5991 | 0 | 86.4009 | 13.5991 | 0
213 | 21 | August | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
213 | 22 | August | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
213 | 23 | August | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213 | 24 | August | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
214 | 1 | August | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
214 | 2 | August | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
214 | 3 | August | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
214 | 4 | August | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
214 | 5 | August | 3.1 | 3.8165 | 0 | 11.907 | 11.907 | 0 | 11.907 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
214 | 6 | August | 4.1 | 5.0477 | 173.4 | 97.0546 | 270.4546 | 0 | 270.4546 | 0 | 0 | 64.1143 | 35.8857 | 0 | 64.1143 | 35.8857 | 0
214 | 7 | August | 4.6 | 5.6633 | 237.15 | 319.4435 | 556.5935 | 0 | 556.5935 | 0 | 0 | 42.6074 | 57.3926 | 0 | 42.6074 | 57.3926 | 0
214 | 8 | August | 4.1 | 5.0477 | 173.4 | 622.4602 | 795.8602 | 0 | 795.8602 | 0 | 0 | 21.7877 | 78.2123 | 0 | 21.7877 | 78.2123 | 0
214 | 9 | August | 7.2 | 8.8642 | 908.65 | 832.6563 | 1741.3063 | 0 | 1741.3063 | 0 | 0 | 52.1821 | 47.8179 | 0 | 52.1821 | 47.8179 | 0
214 | 10 | August | 6.7 | 8.2487 | 761.6 | 725.1294 | 1486.7294 | 0 | 1486.7294 | 0 | 0 | 51.2265 | 48.7735 | 0 | 51.2265 | 48.7735 | 0
214 | 11 | August | 4.6 | 5.6633 | 237.15 | 836.6802 | 1073.8302 | 0 | 1073.8302 | 0 | 0 | 22.0845 | 77.9155 | 0 | 22.0845 | 77.9155 | 0
214 | 12 | August | 5.7 | 7.0175 | 504.9 | 882.7123 | 1387.6123 | 0 | 1387.6123 | 0 | 0 | 36.3862 | 63.6138 | 0 | 36.3862 | 63.6138 | 0
214 | 13 | August | 7.7 | 9.4798 | 1059.95 | 866.3339 | 1926.2839 | 0 | 1926.2839 | 0 | 0 | 55.0256 | 44.9744 | 0 | 55.0256 | 44.9744 | 0
214 | 14 | August | 6.2 | 7.6331 | 625.6 | 800.3968 | 1425.9968 | 0 | 1425.9968 | 0 | 0 | 43.8711 | 56.1289 | 0 | 43.8711 | 56.1289 | 0
214 | 15 | August | 8.2 | 10.0954 | 1359.15 | 669.9215 | 2029.0715 | 1 | 2000 | 29.0715 | 1.4536 | 66.9838 | 32.0425 | 4.3395 | 66.5039 | 33.0162 | 2.1389
214 | 16 | August | 7.2 | 8.8642 | 908.65 | 397.0871 | 1305.7371 | 0 | 1305.7371 | 0 | 0 | 69.589 | 30.411 | 0 | 69.589 | 30.411 | 0
214 | 17 | August | 7.2 | 8.8642 | 908.65 | 343.7634 | 1252.4134 | 0 | 1252.4134 | 0 | 0 | 72.5519 | 27.4481 | 0 | 72.5519 | 27.4481 | 0
214 | 18 | August | 6.2 | 7.6331 | 625.6 | 181.7793 | 807.3793 | 0 | 807.3793 | 0 | 0 | 77.4853 | 22.5147 | 0 | 77.4853 | 22.5147 | 0
214 | 19 | August | 5.7 | 7.0175 | 504.9 | 79.38 | 584.28 | 0 | 584.28 | 0 | 0 | 86.414 | 13.586 | 0 | 86.414 | 13.586 | 0
214 | 20 | August | 4.1 | 5.0477 | 173.4 | 6.615 | 180.015 | 0 | 180.015 | 0 | 0 | 96.3253 | 3.6747 | 0 | 96.3253 | 3.6747 | 0
214 | 21 | August | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
214 | 22 | August | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
214 | 23 | August | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
214 | 24 | August | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
215 | 1 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
215 | 2 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
215 | 3 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
215 | 4 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
215 | 5 | August | 2.6 | 3.201 | 0 | 6.615 | 6.615 | 0 | 6.615 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
215 | 6 | August | 2.1 | 2.5854 | 0 | 54.243 | 54.243 | 0 | 54.243 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
215 | 7 | August | 2.1 | 2.5854 | 0 | 156.9405 | 156.9405 | 0 | 156.9405 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
215 | 8 | August | 3.1 | 3.8165 | 0 | 517.7871 | 517.7871 | 0 | 517.7871 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
215 | 9 | August | 2.1 | 2.5854 | 0 | 903.2187 | 903.2187 | 0 | 903.2187 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
215 | 10 | August | 4.1 | 5.0477 | 173.4 | 890.152 | 1063.552 | 0 | 1063.552 | 0 | 0 | 16.3039 | 83.6961 | 0 | 16.3039 | 83.6961 | 0
215 | 11 | August | 5.7 | 7.0175 | 504.9 | 836.1404 | 1341.0404 | 0 | 1341.0404 | 0 | 0 | 37.6499 | 62.3501 | 0 | 37.6499 | 62.3501 | 0
215 | 12 | August | 5.7 | 7.0175 | 504.9 | 834.183 | 1339.083 | 0 | 1339.083 | 0 | 0 | 37.7049 | 62.2951 | 0 | 37.7049 | 62.2951 | 0
215 | 13 | August | 5.1 | 6.2788 | 312.8 | 824.9555 | 1137.7555 | 0 | 1137.7555 | 0 | 0 | 27.4927 | 72.5073 | 0 | 27.4927 | 72.5073 | 0
215 | 14 | August | 6.2 | 7.6331 | 625.6 | 1230.7409 | 1856.3409 | 0 | 1856.3409 | 0 | 0 | 33.7007 | 66.2993 | 0 | 33.7007 | 66.2993 | 0
215 | 15 | August | 5.1 | 6.2788 | 312.8 | 1033.8216 | 1346.6216 | 0 | 1346.6216 | 0 | 0 | 23.2285 | 76.7715 | 0 | 23.2285 | 76.7715 | 0
215 | 16 | August | 6.2 | 7.6331 | 625.6 | 722.6564 | 1348.2564 | 0 | 1348.2564 | 0 | 0 | 46.4007 | 53.5993 | 0 | 46.4007 | 53.5993 | 0
215 | 17 | August | 5.7 | 7.0175 | 504.9 | 433.6808 | 938.5808 | 0 | 938.5808 | 0 | 0 | 53.794 | 46.206 | 0 | 53.794 | 46.206 | 0
215 | 18 | August | 4.6 | 5.6633 | 237.15 | 192.9326 | 430.0826 | 0 | 430.0826 | 0 | 0 | 55.1406 | 44.8594 | 0 | 55.1406 | 44.8594 | 0
215 | 19 | August | 5.7 | 7.0175 | 504.9 | 75.411 | 580.311 | 0 | 580.311 | 0 | 0 | 87.0051 | 12.9949 | 0 | 87.0051 | 12.9949 | 0
215 | 20 | August | 5.1 | 6.2788 | 312.8 | 10.584 | 323.384 | 0 | 323.384 | 0 | 0 | 96.7271 | 3.2729 | 0 | 96.7271 | 3.2729 | 0
215 | 21 | August | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
215 | 22 | August | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
215 | 23 | August | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
215 | 24 | August | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
216 | 1 | August | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
216 | 2 | August | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
216 | 3 | August | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
216 | 4 | August | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
216 | 5 | August | 4.6 | 5.6633 | 237.15 | 5.292 | 242.442 | 0 | 242.442 | 0 | 0 | 97.8172 | 2.1828 | 0 | 97.8172 | 2.1828 | 0
216 | 6 | August | 6.2 | 7.6331 | 625.6 | 52.92 | 678.52 | 0 | 678.52 | 0 | 0 | 92.2007 | 7.7993 | 0 | 92.2007 | 7.7993 | 0
216 | 7 | August | 6.7 | 8.2487 | 761.6 | 154.2658 | 915.8658 | 0 | 915.8658 | 0 | 0 | 83.1563 | 16.8437 | 0 | 83.1563 | 16.8437 | 0
216 | 8 | August | 7.2 | 8.8642 | 908.65 | 286.7322 | 1195.3822 | 0 | 1195.3822 | 0 | 0 | 76.0133 | 23.9867 | 0 | 76.0133 | 23.9867 | 0
216 | 9 | August | 6.2 | 7.6331 | 625.6 | 401.6302 | 1027.2302 | 0 | 1027.2302 | 0 | 0 | 60.9016 | 39.0984 | 0 | 60.9016 | 39.0984 | 0
216 | 10 | August | 4.1 | 5.0477 | 173.4 | 500.4506 | 673.8506 | 0 | 673.8506 | 0 | 0 | 25.7327 | 74.2673 | 0 | 25.7327 | 74.2673 | 0
216 | 11 | August | 3.1 | 3.8165 | 0 | 576.6898 | 576.6898 | 0 | 576.6898 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
216 | 12 | August | 9.3 | 11.4496 | 1598.85 | 378.9844 | 1977.8344 | 0 | 1977.8344 | 0 | 0 | 80.8384 | 19.1616 | 0 | 80.8384 | 19.1616 | 0
216 | 13 | August | 1 | 1.2311 | 0 | 375.2858 | 375.2858 | 0 | 375.2858 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
216 | 14 | August | 0 | 0 | 0 | 586.1882 | 586.1882 | 0 | 586.1882 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
216 | 15 | August | 3.1 | 3.8165 | 0 | 304.2482 | 304.2482 | 0 | 304.2482 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
216 | 16 | August | 5.1 | 6.2788 | 312.8 | 240.7611 | 553.5611 | 0 | 553.5611 | 0 | 0 | 56.5069 | 43.4931 | 0 | 56.5069 | 43.4931 | 0
216 | 17 | August | 1.5 | 1.8467 | 0 | 169.344 | 169.344 | 0 | 169.344 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
216 | 18 | August | 2 | 2.4623 | 0 | 124.362 | 124.362 | 0 | 124.362 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
216 | 19 | August | 2.6 | 3.201 | 0 | 51.597 | 51.597 | 0 | 51.597 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
216 | 20 | August | 3.1 | 3.8165 | 0 | 5.292 | 5.292 | 0 | 5.292 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
216 | 21 | August | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
216 | 22 | August | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
216 | 23 | August | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
216 | 24 | August | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217 | 1 | August | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217 | 2 | August | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217 | 3 | August | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217 | 4 | August | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217 | 5 | August | 2.6 | 3.201 | 0 | 5.292 | 5.292 | 0 | 5.292 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
217 | 6 | August | 2.1 | 2.5854 | 0 | 64.827 | 64.827 | 0 | 64.827 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
217 | 7 | August | 1.5 | 1.8467 | 0 | 150.3528 | 150.3528 | 0 | 150.3528 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
217 | 8 | August | 1.5 | 1.8467 | 0 | 509.3815 | 509.3815 | 0 | 509.3815 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
217 | 9 | August | 2.6 | 3.201 | 0 | 815.923 | 815.923 | 0 | 815.923 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
217 | 10 | August | 1.5 | 1.8467 | 0 | 517.6565 | 517.6565 | 0 | 517.6565 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
217 | 11 | August | 3.1 | 3.8165 | 0 | 576.8583 | 576.8583 | 0 | 576.8583 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
217 | 12 | August | 4.1 | 5.0477 | 173.4 | 614.1461 | 787.5461 | 0 | 787.5461 | 0 | 0 | 22.0178 | 77.9822 | 0 | 22.0178 | 77.9822 | 0
217 | 13 | August | 4.1 | 5.0477 | 173.4 | 1240.083 | 1413.483 | 0 | 1413.483 | 0 | 0 | 12.2676 | 87.7324 | 0 | 12.2676 | 87.7324 | 0
217 | 14 | August | 4.1 | 5.0477 | 173.4 | 607.9836 | 781.3836 | 0 | 781.3836 | 0 | 0 | 22.1914 | 77.8086 | 0 | 22.1914 | 77.8086 | 0
217 | 15 | August | 3.6 | 4.4321 | 75.65 | 664.7074 | 740.3574 | 0 | 740.3574 | 0 | 0 | 10.218 | 89.782 | 0 | 10.218 | 89.782 | 0
217 | 16 | August | 3.6 | 4.4321 | 75.65 | 733.9796 | 809.6296 | 0 | 809.6296 | 0 | 0 | 9.3438 | 90.6562 | 0 | 9.3438 | 90.6562 | 0
217 | 17 | August | 3.3 | 4.0628 | 75.65 | 442.3059 | 517.9559 | 0 | 517.9559 | 0 | 0 | 14.6055 | 85.3945 | 0 | 14.6055 | 85.3945 | 0
217 | 18 | August | 3.1 | 3.8165 | 0 | 197.542 | 197.542 | 0 | 197.542 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
217 | 19 | August | 2.1 | 2.5854 | 0 | 72.765 | 72.765 | 0 | 72.765 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
217 | 20 | August | 1.5 | 1.8467 | 0 | 9.261 | 9.261 | 0 | 9.261 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
217 | 21 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217 | 22 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217 | 23 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217 | 24 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
218 | 1 | August | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
218 | 2 | August | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
218 | 3 | August | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
218 | 4 | August | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
218 | 5 | August | 3.6 | 4.4321 | 75.65 | 5.292 | 80.942 | 0 | 80.942 | 0 | 0 | 93.462 | 6.538 | 0 | 93.462 | 6.538 | 0
218 | 6 | August | 4.1 | 5.0477 | 173.4 | 48.951 | 222.351 | 0 | 222.351 | 0 | 0 | 77.9848 | 22.0152 | 0 | 77.9848 | 22.0152 | 0
218 | 7 | August | 3.1 | 3.8165 | 0 | 148.7846 | 148.7846 | 0 | 148.7846 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
218 | 8 | August | 4.1 | 5.0477 | 173.4 | 273.8327 | 447.2327 | 0 | 447.2327 | 0 | 0 | 38.7718 | 61.2282 | 0 | 38.7718 | 61.2282 | 0
218 | 9 | August | 3.6 | 4.4321 | 75.65 | 565.1259 | 640.7759 | 0 | 640.7759 | 0 | 0 | 11.806 | 88.194 | 0 | 11.806 | 88.194 | 0
218 | 10 | August | 4.1 | 5.0477 | 173.4 | 514.7356 | 688.1356 | 0 | 688.1356 | 0 | 0 | 25.1985 | 74.8015 | 0 | 25.1985 | 74.8015 | 0
218 | 11 | August | 4.6 | 5.6633 | 237.15 | 575.4915 | 812.6415 | 0 | 812.6415 | 0 | 0 | 29.1826 | 70.8174 | 0 | 29.1826 | 70.8174 | 0
218 | 12 | August | 4.6 | 5.6633 | 237.15 | 611.4498 | 848.5998 | 0 | 848.5998 | 0 | 0 | 27.946 | 72.054 | 0 | 27.946 | 72.054 | 0
218 | 13 | August | 5.1 | 6.2788 | 312.8 | 864.8219 | 1177.6219 | 0 | 1177.6219 | 0 | 0 | 26.562 | 73.438 | 0 | 26.562 | 73.438 | 0
218 | 14 | August | 6.7 | 8.2487 | 761.6 | 758.5769 | 1520.1769 | 0 | 1520.1769 | 0 | 0 | 50.0994 | 49.9006 | 0 | 50.0994 | 49.9006 | 0
218 | 15 | August | 6.2 | 7.6331 | 625.6 | 641.2354 | 1266.8354 | 0 | 1266.8354 | 0 | 0 | 49.3829 | 50.6171 | 0 | 49.3829 | 50.6171 | 0
218 | 16 | August | 6.2 | 7.6331 | 625.6 | 500.6274 | 1126.2274 | 0 | 1126.2274 | 0 | 0 | 55.5483 | 44.4517 | 0 | 55.5483 | 44.4517 | 0
218 | 17 | August | 6.2 | 7.6331 | 625.6 | 409.8226 | 1035.4226 | 0 | 1035.4226 | 0 | 0 | 60.4198 | 39.5802 | 0 | 60.4198 | 39.5802 | 0
218 | 18 | August | 6.2 | 7.6331 | 625.6 | 143.3756 | 768.9756 | 0 | 768.9756 | 0 | 0 | 81.355 | 18.645 | 0 | 81.355 | 18.645 | 0
218 | 19 | August | 5.1 | 6.2788 | 312.8 | 68.796 | 381.596 | 0 | 381.596 | 0 | 0 | 81.9715 | 18.0285 | 0 | 81.9715 | 18.0285 | 0
218 | 20 | August | 6.2 | 7.6331 | 625.6 | 6.615 | 632.215 | 0 | 632.215 | 0 | 0 | 98.9537 | 1.0463 | 0 | 98.9537 | 1.0463 | 0
218 | 21 | August | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
218 | 22 | August | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
218 | 23 | August | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
218 | 24 | August | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
219 | 1 | August | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
219 | 2 | August | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
219 | 3 | August | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
219 | 4 | August | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
219 | 5 | August | 6.2 | 7.6331 | 625.6 | 5.292 | 630.892 | 0 | 630.892 | 0 | 0 | 99.1612 | 0.83881 | 0 | 99.1612 | 0.83881 | 0
219 | 6 | August | 6.2 | 7.6331 | 625.6 | 47.628 | 673.228 | 0 | 673.228 | 0 | 0 | 92.9254 | 7.0746 | 0 | 92.9254 | 7.0746 | 0
219 | 7 | August | 6.2 | 7.6331 | 625.6 | 147.4511 | 773.0511 | 0 | 773.0511 | 0 | 0 | 80.9261 | 19.0739 | 0 | 80.9261 | 19.0739 | 0
219 | 8 | August | 5.7 | 7.0175 | 504.9 | 272.4777 | 777.3777 | 0 | 777.3777 | 0 | 0 | 64.9491 | 35.0509 | 0 | 64.9491 | 35.0509 | 0
219 | 9 | August | 5.1 | 6.2788 | 312.8 | 406.0812 | 718.8812 | 0 | 718.8812 | 0 | 0 | 43.5121 | 56.4879 | 0 | 43.5121 | 56.4879 | 0
219 | 10 | August | 5.1 | 6.2788 | 312.8 | 511.4728 | 824.2728 | 0 | 824.2728 | 0 | 0 | 37.9486 | 62.0514 | 0 | 37.9486 | 62.0514 | 0
219 | 11 | August | 6.2 | 7.6331 | 625.6 | 810.1577 | 1435.7577 | 0 | 1435.7577 | 0 | 0 | 43.5728 | 56.4272 | 0 | 43.5728 | 56.4272 | 0
219 | 12 | August | 6.4 | 7.8793 | 625.6 | 1079.4371 | 1705.0371 | 0 | 1705.0371 | 0 | 0 | 36.6913 | 63.3087 | 0 | 36.6913 | 63.3087 | 0
219 | 13 | August | 6.7 | 8.2487 | 761.6 | 1210.7453 | 1972.3453 | 0 | 1972.3453 | 0 | 0 | 38.6139 | 61.3861 | 0 | 38.6139 | 61.3861 | 0
219 | 14 | August | 6.2 | 7.6331 | 625.6 | 1234.9674 | 1860.5674 | 0 | 1860.5674 | 0 | 0 | 33.6242 | 66.3758 | 0 | 33.6242 | 66.3758 | 0
219 | 15 | August | 6.7 | 8.2487 | 761.6 | 904.5091 | 1666.1091 | 0 | 1666.1091 | 0 | 0 | 45.7113 | 54.2887 | 0 | 45.7113 | 54.2887 | 0
219 | 16 | August | 6.7 | 8.2487 | 761.6 | 732.1857 | 1493.7857 | 0 | 1493.7857 | 0 | 0 | 50.9846 | 49.0154 | 0 | 50.9846 | 49.0154 | 0
219 | 17 | August | 5.1 | 6.2788 | 312.8 | 406.6373 | 719.4373 | 0 | 719.4373 | 0 | 0 | 43.4784 | 56.5216 | 0 | 43.4784 | 56.5216 | 0
219 | 18 | August | 5.7 | 7.0175 | 504.9 | 181.4173 | 686.3173 | 0 | 686.3173 | 0 | 0 | 73.5666 | 26.4334 | 0 | 73.5666 | 26.4334 | 0
219 | 19 | August | 5.1 | 6.2788 | 312.8 | 68.796 | 381.596 | 0 | 381.596 | 0 | 0 | 81.9715 | 18.0285 | 0 | 81.9715 | 18.0285 | 0
219 | 20 | August | 6.2 | 7.6331 | 625.6 | 6.615 | 632.215 | 0 | 632.215 | 0 | 0 | 98.9537 | 1.0463 | 0 | 98.9537 | 1.0463 | 0
219 | 21 | August | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
219 | 22 | August | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
219 | 23 | August | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
219 | 24 | August | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
220 | 1 | August | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
220 | 2 | August | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
220 | 3 | August | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
220 | 4 | August | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
220 | 5 | August | 5.1 | 6.2788 | 312.8 | 3.969 | 316.769 | 0 | 316.769 | 0 | 0 | 98.747 | 1.253 | 0 | 98.747 | 1.253 | 0
220 | 6 | August | 4.1 | 5.0477 | 173.4 | 44.982 | 218.382 | 0 | 218.382 | 0 | 0 | 79.4021 | 20.5979 | 0 | 79.4021 | 20.5979 | 0
220 | 7 | August | 5.1 | 6.2788 | 312.8 | 144.2557 | 457.0557 | 0 | 457.0557 | 0 | 0 | 68.4381 | 31.5619 | 0 | 68.4381 | 31.5619 | 0
220 | 8 | August | 5.1 | 6.2788 | 312.8 | 269.7998 | 582.5998 | 0 | 582.5998 | 0 | 0 | 53.6904 | 46.3096 | 0 | 53.6904 | 46.3096 | 0
220 | 9 | August | 6.2 | 7.6331 | 625.6 | 403.3726 | 1028.9726 | 0 | 1028.9726 | 0 | 0 | 60.7985 | 39.2015 | 0 | 60.7985 | 39.2015 | 0
220 | 10 | August | 5.1 | 6.2788 | 312.8 | 510.0904 | 822.8904 | 0 | 822.8904 | 0 | 0 | 38.0124 | 61.9876 | 0 | 38.0124 | 61.9876 | 0
220 | 11 | August | 5.1 | 6.2788 | 312.8 | 814.2858 | 1127.0858 | 0 | 1127.0858 | 0 | 0 | 27.753 | 72.247 | 0 | 27.753 | 72.247 | 0
220 | 12 | August | 6.2 | 7.6331 | 625.6 | 869.3536 | 1494.9536 | 0 | 1494.9536 | 0 | 0 | 41.8475 | 58.1525 | 0 | 41.8475 | 58.1525 | 0
220 | 13 | August | 5.1 | 6.2788 | 312.8 | 857.7022 | 1170.5022 | 0 | 1170.5022 | 0 | 0 | 26.7236 | 73.2764 | 0 | 26.7236 | 73.2764 | 0
220 | 14 | August | 6.2 | 7.6331 | 625.6 | 770.9926 | 1396.5926 | 0 | 1396.5926 | 0 | 0 | 44.7947 | 55.2053 | 0 | 44.7947 | 55.2053 | 0
220 | 15 | August | 5.7 | 7.0175 | 504.9 | 945.251 | 1450.151 | 0 | 1450.151 | 0 | 0 | 34.8171 | 65.1829 | 0 | 34.8171 | 65.1829 | 0
220 | 16 | August | 5.7 | 7.0175 | 504.9 | 741.3082 | 1246.2082 | 0 | 1246.2082 | 0 | 0 | 40.5149 | 59.4851 | 0 | 40.5149 | 59.4851 | 0
220 | 17 | August | 6.2 | 7.6331 | 625.6 | 430.9068 | 1056.5068 | 0 | 1056.5068 | 0 | 0 | 59.214 | 40.786 | 0 | 59.214 | 40.786 | 0
220 | 18 | August | 6.2 | 7.6331 | 625.6 | 169.8004 | 795.4004 | 0 | 795.4004 | 0 | 0 | 78.6522 | 21.3478 | 0 | 78.6522 | 21.3478 | 0
220 | 19 | August | 5.1 | 6.2788 | 312.8 | 64.827 | 377.627 | 0 | 377.627 | 0 | 0 | 82.8331 | 17.1669 | 0 | 82.8331 | 17.1669 | 0
220 | 20 | August | 5.1 | 6.2788 | 312.8 | 5.292 | 318.092 | 0 | 318.092 | 0 | 0 | 98.3363 | 1.6637 | 0 | 98.3363 | 1.6637 | 0
220 | 21 | August | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
220 | 22 | August | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
220 | 23 | August | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
220 | 24 | August | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
221 | 1 | August | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
221 | 2 | August | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
221 | 3 | August | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
221 | 4 | August | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
221 | 5 | August | 5.1 | 6.2788 | 312.8 | 6.615 | 319.415 | 0 | 319.415 | 0 | 0 | 97.929 | 2.071 | 0 | 97.929 | 2.071 | 0
221 | 6 | August | 5.7 | 7.0175 | 504.9 | 72.3433 | 577.2433 | 0 | 577.2433 | 0 | 0 | 87.4675 | 12.5325 | 0 | 87.4675 | 12.5325 | 0
221 | 7 | August | 6.2 | 7.6331 | 625.6 | 230.4955 | 856.0955 | 0 | 856.0955 | 0 | 0 | 73.076 | 26.924 | 0 | 73.076 | 26.924 | 0
221 | 8 | August | 6.2 | 7.6331 | 625.6 | 361.1449 | 986.7449 | 0 | 986.7449 | 0 | 0 | 63.4004 | 36.5996 | 0 | 63.4004 | 36.5996 | 0
221 | 9 | August | 6.2 | 7.6331 | 625.6 | 550.7565 | 1176.3565 | 0 | 1176.3565 | 0 | 0 | 53.1812 | 46.8188 | 0 | 53.1812 | 46.8188 | 0
221 | 10 | August | 6.7 | 8.2487 | 761.6 | 1004.3704 | 1765.9704 | 0 | 1765.9704 | 0 | 0 | 43.1264 | 56.8736 | 0 | 43.1264 | 56.8736 | 0
221 | 11 | August | 7.2 | 8.8642 | 908.65 | 1167.5588 | 2076.2088 | 1 | 2000 | 76.2088 | 3.8104 | 43.7649 | 54.5675 | 6.5272 | 41.6221 | 56.2351 | 8.387
221 | 12 | August | 8.2 | 10.0954 | 1359.15 | 1336.3097 | 2695.4597 | 1 | 2000 | 695.4597 | 34.773 | 50.4237 | 32.0425 | 52.0433 | 33.1845 | 49.5763 | 51.1687
221 | 13 | August | 7.7 | 9.4798 | 1059.95 | 1378.4985 | 2438.4485 | 1 | 2000 | 438.4485 | 21.9224 | 43.4682 | 47.0025 | 31.8062 | 31.0751 | 56.5318 | 41.365
221 | 14 | August | 8.7 | 10.711 | 1490.05 | 1237.7656 | 2727.8156 | 1 | 2000 | 727.8156 | 36.3908 | 54.6243 | 25.4975 | 58.8008 | 38.1117 | 45.3757 | 48.845
221 | 15 | August | 8.7 | 10.711 | 1490.05 | 972.6559 | 2462.7059 | 1 | 2000 | 462.7059 | 23.1353 | 60.5046 | 25.4975 | 47.5714 | 51.3672 | 39.4954 | 31.053
221 | 16 | August | 8.2 | 10.0954 | 1359.15 | 587.522 | 1946.672 | 0 | 1946.672 | 0 | 0 | 69.8192 | 30.1808 | 0 | 69.8192 | 30.1808 | 0
221 | 17 | August | 8.2 | 10.0954 | 1359.15 | 368.7192 | 1727.8692 | 0 | 1727.8692 | 0 | 0 | 78.6605 | 21.3395 | 0 | 78.6605 | 21.3395 | 0
221 | 18 | August | 7.7 | 9.4798 | 1059.95 | 176.125 | 1236.075 | 0 | 1236.075 | 0 | 0 | 85.7513 | 14.2487 | 0 | 85.7513 | 14.2487 | 0
221 | 19 | August | 7.7 | 9.4798 | 1059.95 | 60.858 | 1120.808 | 0 | 1120.808 | 0 | 0 | 94.5702 | 5.4298 | 0 | 94.5702 | 5.4298 | 0
221 | 20 | August | 9.8 | 12.0652 | 1683.85 | 5.292 | 1689.142 | 0 | 1689.142 | 0 | 0 | 99.6867 | 0.3133 | 0 | 99.6867 | 0.3133 | 0
221 | 21 | August | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
221 | 22 | August | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
221 | 23 | August | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
221 | 24 | August | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
222 | 1 | August | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
222 | 2 | August | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
222 | 3 | August | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
222 | 4 | August | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
222 | 5 | August | 10.3 | 12.6808 | 1694.9 | 2.646 | 1697.546 | 0 | 1697.546 | 0 | 0 | 99.8441 | 0.15587 | 0 | 99.8441 | 0.15587 | 0
222 | 6 | August | 9.3 | 11.4496 | 1598.85 | 26.46 | 1625.31 | 0 | 1625.31 | 0 | 0 | 98.372 | 1.628 | 0 | 98.372 | 1.628 | 0
222 | 7 | August | 9.3 | 11.4496 | 1598.85 | 87.318 | 1686.168 | 0 | 1686.168 | 0 | 0 | 94.8215 | 5.1785 | 0 | 94.8215 | 5.1785 | 0
222 | 8 | August | 9.3 | 11.4496 | 1598.85 | 161.406 | 1760.256 | 0 | 1760.256 | 0 | 0 | 90.8305 | 9.1695 | 0 | 90.8305 | 9.1695 | 0
222 | 9 | August | 9.3 | 11.4496 | 1598.85 | 235.1815 | 1834.0315 | 0 | 1834.0315 | 0 | 0 | 87.1768 | 12.8232 | 0 | 87.1768 | 12.8232 | 0
222 | 10 | August | 8.7 | 10.711 | 1490.05 | 296.6839 | 1786.7339 | 0 | 1786.7339 | 0 | 0 | 83.3952 | 16.6048 | 0 | 83.3952 | 16.6048 | 0
222 | 11 | August | 8.2 | 10.0954 | 1359.15 | 578.1668 | 1937.3168 | 0 | 1937.3168 | 0 | 0 | 70.1563 | 29.8437 | 0 | 70.1563 | 29.8437 | 0
222 | 12 | August | 8.2 | 10.0954 | 1359.15 | 619.5593 | 1978.7093 | 0 | 1978.7093 | 0 | 0 | 68.6887 | 31.3113 | 0 | 68.6887 | 31.3113 | 0
222 | 13 | August | 8.2 | 10.0954 | 1359.15 | 615.188 | 1974.338 | 0 | 1974.338 | 0 | 0 | 68.8408 | 31.1592 | 0 | 68.8408 | 31.1592 | 0
222 | 14 | August | 7.2 | 8.8642 | 908.65 | 564.9401 | 1473.5901 | 0 | 1473.5901 | 0 | 0 | 61.6623 | 38.3377 | 0 | 61.6623 | 38.3377 | 0
222 | 15 | August | 7.4 | 9.1105 | 1059.95 | 484.5189 | 1544.4689 | 0 | 1544.4689 | 0 | 0 | 68.6288 | 31.3712 | 0 | 68.6288 | 31.3712 | 0
222 | 16 | August | 7.7 | 9.4798 | 1059.95 | 370.47 | 1430.42 | 0 | 1430.42 | 0 | 0 | 74.1006 | 25.8994 | 0 | 74.1006 | 25.8994 | 0
222 | 17 | August | 7.2 | 8.8642 | 908.65 | 251.8407 | 1160.4907 | 0 | 1160.4907 | 0 | 0 | 78.2988 | 21.7012 | 0 | 78.2988 | 21.7012 | 0
222 | 18 | August | 6.7 | 8.2487 | 761.6 | 84.672 | 846.272 | 0 | 846.272 | 0 | 0 | 89.9947 | 10.0053 | 0 | 89.9947 | 10.0053 | 0
222 | 19 | August | 6.2 | 7.6331 | 625.6 | 25.137 | 650.737 | 0 | 650.737 | 0 | 0 | 96.1371 | 3.8629 | 0 | 96.1371 | 3.8629 | 0
222 | 20 | August | 7.2 | 8.8642 | 908.65 | 1.323 | 909.973 | 0 | 909.973 | 0 | 0 | 99.8546 | 0.14539 | 0 | 99.8546 | 0.14539 | 0
222 | 21 | August | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
222 | 22 | August | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
222 | 23 | August | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
222 | 24 | August | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
223 | 1 | August | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
223 | 2 | August | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
223 | 3 | August | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
223 | 4 | August | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
223 | 5 | August | 7.7 | 9.4798 | 1059.95 | 1.323 | 1061.273 | 0 | 1061.273 | 0 | 0 | 99.8753 | 0.12466 | 0 | 99.8753 | 0.12466 | 0
223 | 6 | August | 8.2 | 10.0954 | 1359.15 | 25.137 | 1384.287 | 0 | 1384.287 | 0 | 0 | 98.1841 | 1.8159 | 0 | 98.1841 | 1.8159 | 0
223 | 7 | August | 5.7 | 7.0175 | 504.9 | 84.672 | 589.572 | 0 | 589.572 | 0 | 0 | 85.6384 | 14.3616 | 0 | 85.6384 | 14.3616 | 0
223 | 8 | August | 7.2 | 8.8642 | 908.65 | 158.76 | 1067.41 | 0 | 1067.41 | 0 | 0 | 85.1266 | 14.8734 | 0 | 85.1266 | 14.8734 | 0
223 | 9 | August | 6.2 | 7.6331 | 625.6 | 232.5334 | 858.1334 | 0 | 858.1334 | 0 | 0 | 72.9024 | 27.0976 | 0 | 72.9024 | 27.0976 | 0
223 | 10 | August | 5.1 | 6.2788 | 312.8 | 294.0332 | 606.8332 | 0 | 606.8332 | 0 | 0 | 51.5463 | 48.4537 | 0 | 51.5463 | 48.4537 | 0
223 | 11 | August | 5.1 | 6.2788 | 312.8 | 338.7946 | 651.5946 | 0 | 651.5946 | 0 | 0 | 48.0053 | 51.9947 | 0 | 48.0053 | 51.9947 | 0
223 | 12 | August | 4.6 | 5.6633 | 237.15 | 362.3518 | 599.5018 | 0 | 599.5018 | 0 | 0 | 39.5578 | 60.4422 | 0 | 39.5578 | 60.4422 | 0
223 | 13 | August | 6.2 | 7.6331 | 625.6 | 625.5774 | 1251.1774 | 0 | 1251.1774 | 0 | 0 | 50.0009 | 49.9991 | 0 | 50.0009 | 49.9991 | 0
223 | 14 | August | 7.2 | 8.8642 | 908.65 | 340.9332 | 1249.5832 | 0 | 1249.5832 | 0 | 0 | 72.7162 | 27.2838 | 0 | 72.7162 | 27.2838 | 0
223 | 15 | August | 5.7 | 7.0175 | 504.9 | 291.5173 | 796.4173 | 0 | 796.4173 | 0 | 0 | 63.3964 | 36.6036 | 0 | 63.3964 | 36.6036 | 0
223 | 16 | August | 4.6 | 5.6633 | 237.15 | 228.4108 | 465.5608 | 0 | 465.5608 | 0 | 0 | 50.9386 | 49.0614 | 0 | 50.9386 | 49.0614 | 0
223 | 17 | August | 3.6 | 4.4321 | 75.65 | 156.114 | 231.764 | 0 | 231.764 | 0 | 0 | 32.641 | 67.359 | 0 | 32.641 | 67.359 | 0
223 | 18 | August | 3.6 | 4.4321 | 75.65 | 131.4126 | 207.0626 | 0 | 207.0626 | 0 | 0 | 36.5348 | 63.4652 | 0 | 36.5348 | 63.4652 | 0
223 | 19 | August | 3.1 | 3.8165 | 0 | 37.044 | 37.044 | 0 | 37.044 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
223 | 20 | August | 3.6 | 4.4321 | 75.65 | 2.646 | 78.296 | 0 | 78.296 | 0 | 0 | 96.6205 | 3.3795 | 0 | 96.6205 | 3.3795 | 0
223 | 21 | August | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
223 | 22 | August | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
223 | 23 | August | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
223 | 24 | August | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
224 | 1 | August | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
224 | 2 | August | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
224 | 3 | August | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
224 | 4 | August | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
224 | 5 | August | 7.7 | 9.4798 | 1059.95 | 1.323 | 1061.273 | 0 | 1061.273 | 0 | 0 | 99.8753 | 0.12466 | 0 | 99.8753 | 0.12466 | 0
224 | 6 | August | 7.7 | 9.4798 | 1059.95 | 23.814 | 1083.764 | 0 | 1083.764 | 0 | 0 | 97.8027 | 2.1973 | 0 | 97.8027 | 2.1973 | 0
224 | 7 | August | 7.2 | 8.8642 | 908.65 | 84.672 | 993.322 | 0 | 993.322 | 0 | 0 | 91.4759 | 8.5241 | 0 | 91.4759 | 8.5241 | 0
224 | 8 | August | 7.2 | 8.8642 | 908.65 | 158.76 | 1067.41 | 0 | 1067.41 | 0 | 0 | 85.1266 | 14.8734 | 0 | 85.1266 | 14.8734 | 0
224 | 9 | August | 7.7 | 9.4798 | 1059.95 | 231.2083 | 1291.1583 | 0 | 1291.1583 | 0 | 0 | 82.093 | 17.907 | 0 | 82.093 | 17.907 | 0
224 | 10 | August | 8.2 | 10.0954 | 1359.15 | 294.0284 | 1653.1784 | 0 | 1653.1784 | 0 | 0 | 82.2144 | 17.7856 | 0 | 82.2144 | 17.7856 | 0
224 | 11 | August | 8.7 | 10.711 | 1490.05 | 340.1104 | 1830.1604 | 0 | 1830.1604 | 0 | 0 | 81.4164 | 18.5836 | 0 | 81.4164 | 18.5836 | 0
224 | 12 | August | 9.3 | 11.4496 | 1598.85 | 362.3396 | 1961.1896 | 0 | 1961.1896 | 0 | 0 | 81.5245 | 18.4755 | 0 | 81.5245 | 18.4755 | 0
224 | 13 | August | 8.2 | 10.0954 | 1359.15 | 361.8246 | 1720.9746 | 0 | 1720.9746 | 0 | 0 | 78.9756 | 21.0244 | 0 | 78.9756 | 21.0244 | 0
224 | 14 | August | 6.7 | 8.2487 | 761.6 | 337.7306 | 1099.3306 | 0 | 1099.3306 | 0 | 0 | 69.2785 | 30.7215 | 0 | 69.2785 | 30.7215 | 0
224 | 15 | August | 7.7 | 9.4798 | 1059.95 | 291.5046 | 1351.4546 | 0 | 1351.4546 | 0 | 0 | 78.4303 | 21.5697 | 0 | 78.4303 | 21.5697 | 0
224 | 16 | August | 6.7 | 8.2487 | 761.6 | 369.9258 | 1131.5258 | 0 | 1131.5258 | 0 | 0 | 67.3073 | 32.6927 | 0 | 67.3073 | 32.6927 | 0
224 | 17 | August | 5.7 | 7.0175 | 504.9 | 246.3722 | 751.2722 | 0 | 751.2722 | 0 | 0 | 67.206 | 32.794 | 0 | 67.206 | 32.794 | 0
224 | 18 | August | 5.7 | 7.0175 | 504.9 | 128.8947 | 633.7947 | 0 | 633.7947 | 0 | 0 | 79.663 | 20.337 | 0 | 79.663 | 20.337 | 0
224 | 19 | August | 4.1 | 5.0477 | 173.4 | 35.721 | 209.121 | 0 | 209.121 | 0 | 0 | 82.9185 | 17.0815 | 0 | 82.9185 | 17.0815 | 0
224 | 20 | August | 2.6 | 3.201 | 0 | 2.646 | 2.646 | 0 | 2.646 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
224 | 21 | August | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
224 | 22 | August | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
224 | 23 | August | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
224 | 24 | August | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
225 | 1 | August | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
225 | 2 | August | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
225 | 3 | August | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
225 | 4 | August | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
225 | 5 | August | 5.1 | 6.2788 | 312.8 | 3.969 | 316.769 | 0 | 316.769 | 0 | 0 | 98.747 | 1.253 | 0 | 98.747 | 1.253 | 0
225 | 6 | August | 5.7 | 7.0175 | 504.9 | 63.29 | 568.19 | 0 | 568.19 | 0 | 0 | 88.8611 | 11.1389 | 0 | 88.8611 | 11.1389 | 0
225 | 7 | August | 6.2 | 7.6331 | 625.6 | 240.9744 | 866.5744 | 0 | 866.5744 | 0 | 0 | 72.1923 | 27.8077 | 0 | 72.1923 | 27.8077 | 0
225 | 8 | August | 6.7 | 8.2487 | 761.6 | 428.5163 | 1190.1163 | 0 | 1190.1163 | 0 | 0 | 63.9937 | 36.0063 | 0 | 63.9937 | 36.0063 | 0
225 | 9 | August | 7.2 | 8.8642 | 908.65 | 779.8054 | 1688.4554 | 0 | 1688.4554 | 0 | 0 | 53.8155 | 46.1845 | 0 | 53.8155 | 46.1845 | 0
225 | 10 | August | 7.7 | 9.4798 | 1059.95 | 1103.4262 | 2163.3762 | 1 | 2000 | 163.3762 | 8.1688 | 48.9952 | 47.0025 | 14.8063 | 44.8287 | 51.0048 | 15.4136
225 | 11 | August | 7.7 | 9.4798 | 1059.95 | 1291.2036 | 2351.1536 | 1 | 2000 | 351.1536 | 17.5577 | 45.0821 | 47.0025 | 27.1958 | 35.4398 | 54.9179 | 33.1293
225 | 12 | August | 8.2 | 10.0954 | 1359.15 | 1358.5166 | 2717.6666 | 1 | 2000 | 717.6666 | 35.8833 | 50.0117 | 32.0425 | 52.8272 | 32.0742 | 49.9883 | 52.8026
225 | 13 | August | 8.2 | 10.0954 | 1359.15 | 1372.4866 | 2731.6366 | 1 | 2000 | 731.6366 | 36.5818 | 49.7559 | 32.0425 | 53.3074 | 31.3757 | 50.2441 | 53.8305
225 | 14 | August | 9.3 | 11.4496 | 1598.85 | 1239.2201 | 2838.0701 | 1 | 2000 | 838.0701 | 41.9035 | 56.3358 | 20.0575 | 67.6288 | 38.039 | 43.6642 | 52.4171
225 | 15 | August | 7.7 | 9.4798 | 1059.95 | 1020.3539 | 2080.3039 | 1 | 2000 | 80.3039 | 4.0152 | 50.9517 | 47.0025 | 7.8702 | 48.9823 | 49.0483 | 7.5762
225 | 16 | August | 6.7 | 8.2487 | 761.6 | 719.6791 | 1481.2791 | 0 | 1481.2791 | 0 | 0 | 51.415 | 48.585 | 0 | 51.415 | 48.585 | 0
225 | 17 | August | 5.1 | 6.2788 | 312.8 | 412.7102 | 725.5102 | 0 | 725.5102 | 0 | 0 | 43.1145 | 56.8855 | 0 | 43.1145 | 56.8855 | 0
225 | 18 | August | 4.6 | 5.6633 | 237.15 | 165.7873 | 402.9373 | 0 | 402.9373 | 0 | 0 | 58.8553 | 41.1447 | 0 | 58.8553 | 41.1447 | 0
225 | 19 | August | 3.1 | 3.8165 | 0 | 48.951 | 48.951 | 0 | 48.951 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
225 | 20 | August | 2.6 | 3.201 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
225 | 21 | August | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
225 | 22 | August | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
225 | 23 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
225 | 24 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
226 | 1 | August | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
226 | 2 | August | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
226 | 3 | August | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
226 | 4 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
226 | 5 | August | 1.5 | 1.8467 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
226 | 6 | August | 2.6 | 3.201 | 0 | 52.92 | 52.92 | 0 | 52.92 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
226 | 7 | August | 3.1 | 3.8165 | 0 | 263.7014 | 263.7014 | 0 | 263.7014 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
226 | 8 | August | 4.6 | 5.6633 | 237.15 | 580.7999 | 817.9499 | 0 | 817.9499 | 0 | 0 | 28.9932 | 71.0068 | 0 | 28.9932 | 71.0068 | 0
226 | 9 | August | 4.1 | 5.0477 | 173.4 | 906.8768 | 1080.2768 | 0 | 1080.2768 | 0 | 0 | 16.0514 | 83.9486 | 0 | 16.0514 | 83.9486 | 0
226 | 10 | August | 4.6 | 5.6633 | 237.15 | 1127.2219 | 1364.3719 | 0 | 1364.3719 | 0 | 0 | 17.3816 | 82.6184 | 0 | 17.3816 | 82.6184 | 0
226 | 11 | August | 3.1 | 3.8165 | 0 | 822.5709 | 822.5709 | 0 | 822.5709 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
226 | 12 | August | 3.1 | 3.8165 | 0 | 1060.8454 | 1060.8454 | 0 | 1060.8454 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
226 | 13 | August | 5.1 | 6.2788 | 312.8 | 1015.9574 | 1328.7574 | 0 | 1328.7574 | 0 | 0 | 23.5408 | 76.4592 | 0 | 23.5408 | 76.4592 | 0
226 | 14 | August | 5.7 | 7.0175 | 504.9 | 1194.5348 | 1699.4348 | 0 | 1699.4348 | 0 | 0 | 29.7099 | 70.2901 | 0 | 29.7099 | 70.2901 | 0
226 | 15 | August | 6.7 | 8.2487 | 761.6 | 1013.92 | 1775.52 | 0 | 1775.52 | 0 | 0 | 42.8945 | 57.1055 | 0 | 42.8945 | 57.1055 | 0
226 | 16 | August | 5.7 | 7.0175 | 504.9 | 715.3447 | 1220.2447 | 0 | 1220.2447 | 0 | 0 | 41.3769 | 58.6231 | 0 | 41.3769 | 58.6231 | 0
226 | 17 | August | 4.1 | 5.0477 | 173.4 | 408.0487 | 581.4487 | 0 | 581.4487 | 0 | 0 | 29.8221 | 70.1779 | 0 | 29.8221 | 70.1779 | 0
226 | 18 | August | 3.6 | 4.4321 | 75.65 | 162.5191 | 238.1691 | 0 | 238.1691 | 0 | 0 | 31.7631 | 68.2369 | 0 | 31.7631 | 68.2369 | 0
226 | 19 | August | 3.6 | 4.4321 | 75.65 | 51.597 | 127.247 | 0 | 127.247 | 0 | 0 | 59.4513 | 40.5487 | 0 | 59.4513 | 40.5487 | 0
226 | 20 | August | 3.1 | 3.8165 | 0 | 2.646 | 2.646 | 0 | 2.646 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
226 | 21 | August | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
226 | 22 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
226 | 23 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
226 | 24 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
227 | 1 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
227 | 2 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
227 | 3 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
227 | 4 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
227 | 5 | August | 1 | 1.2311 | 0 | 2.646 | 2.646 | 0 | 2.646 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
227 | 6 | August | 1 | 1.2311 | 0 | 42.336 | 42.336 | 0 | 42.336 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
227 | 7 | August | 1 | 1.2311 | 0 | 128.0621 | 128.0621 | 0 | 128.0621 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
227 | 8 | August | 1 | 1.2311 | 0 | 355.0699 | 355.0699 | 0 | 355.0699 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
227 | 9 | August | 1 | 1.2311 | 0 | 383.6877 | 383.6877 | 0 | 383.6877 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
227 | 10 | August | 2.1 | 2.5854 | 0 | 695.2563 | 695.2563 | 0 | 695.2563 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
227 | 11 | August | 3.1 | 3.8165 | 0 | 1225.842 | 1225.842 | 0 | 1225.842 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
227 | 12 | August | 4.1 | 5.0477 | 173.4 | 1077.352 | 1250.752 | 0 | 1250.752 | 0 | 0 | 13.8637 | 86.1363 | 0 | 13.8637 | 86.1363 | 0
227 | 13 | August | 5.7 | 7.0175 | 504.9 | 1182.1184 | 1687.0184 | 0 | 1687.0184 | 0 | 0 | 29.9285 | 70.0715 | 0 | 29.9285 | 70.0715 | 0
227 | 14 | August | 6.2 | 7.6331 | 625.6 | 1166.5999 | 1792.1999 | 0 | 1792.1999 | 0 | 0 | 34.9068 | 65.0932 | 0 | 34.9068 | 65.0932 | 0
227 | 15 | August | 6.7 | 8.2487 | 761.6 | 993.9178 | 1755.5178 | 0 | 1755.5178 | 0 | 0 | 43.3832 | 56.6168 | 0 | 43.3832 | 56.6168 | 0
227 | 16 | August | 6.4 | 7.8793 | 625.6 | 704.9378 | 1330.5378 | 0 | 1330.5378 | 0 | 0 | 47.0186 | 52.9814 | 0 | 47.0186 | 52.9814 | 0
227 | 17 | August | 6.2 | 7.6331 | 625.6 | 401.7041 | 1027.3041 | 0 | 1027.3041 | 0 | 0 | 60.8973 | 39.1027 | 0 | 60.8973 | 39.1027 | 0
227 | 18 | August | 6.7 | 8.2487 | 761.6 | 161.0395 | 922.6395 | 0 | 922.6395 | 0 | 0 | 82.5458 | 17.4542 | 0 | 82.5458 | 17.4542 | 0
227 | 19 | August | 4.1 | 5.0477 | 173.4 | 50.274 | 223.674 | 0 | 223.674 | 0 | 0 | 77.5235 | 22.4765 | 0 | 77.5235 | 22.4765 | 0
227 | 20 | August | 3.6 | 4.4321 | 75.65 | 1.323 | 76.973 | 0 | 76.973 | 0 | 0 | 98.2812 | 1.7188 | 0 | 98.2812 | 1.7188 | 0
227 | 21 | August | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
227 | 22 | August | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
227 | 23 | August | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
227 | 24 | August | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
228 | 1 | August | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
228 | 2 | August | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
228 | 3 | August | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
228 | 4 | August | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
228 | 5 | August | 3.6 | 4.4321 | 75.65 | 2.646 | 78.296 | 0 | 78.296 | 0 | 0 | 96.6205 | 3.3795 | 0 | 96.6205 | 3.3795 | 0
228 | 6 | August | 4.1 | 5.0477 | 173.4 | 47.628 | 221.028 | 0 | 221.028 | 0 | 0 | 78.4516 | 21.5484 | 0 | 78.4516 | 21.5484 | 0
228 | 7 | August | 4.1 | 5.0477 | 173.4 | 255.6712 | 429.0712 | 0 | 429.0712 | 0 | 0 | 40.4129 | 59.5871 | 0 | 40.4129 | 59.5871 | 0
228 | 8 | August | 5.1 | 6.2788 | 312.8 | 535.5822 | 848.3822 | 0 | 848.3822 | 0 | 0 | 36.8702 | 63.1298 | 0 | 36.8702 | 63.1298 | 0
228 | 9 | August | 5.7 | 7.0175 | 504.9 | 676.7671 | 1181.6671 | 0 | 1181.6671 | 0 | 0 | 42.7278 | 57.2722 | 0 | 42.7278 | 57.2722 | 0
228 | 10 | August | 5.7 | 7.0175 | 504.9 | 488.1988 | 993.0988 | 0 | 993.0988 | 0 | 0 | 50.8409 | 49.1591 | 0 | 50.8409 | 49.1591 | 0
228 | 11 | August | 7.2 | 8.8642 | 908.65 | 1212.9646 | 2121.6146 | 1 | 2000 | 121.6146 | 6.0807 | 42.8282 | 54.5675 | 10.0262 | 39.3518 | 57.1718 | 13.3841
228 | 12 | August | 7.7 | 9.4798 | 1059.95 | 644.0553 | 1704.0053 | 0 | 1704.0053 | 0 | 0 | 62.2034 | 37.7966 | 0 | 62.2034 | 37.7966 | 0
228 | 13 | August | 7.2 | 8.8642 | 908.65 | 599.765 | 1508.415 | 0 | 1508.415 | 0 | 0 | 60.2387 | 39.7613 | 0 | 60.2387 | 39.7613 | 0
228 | 14 | August | 8.2 | 10.0954 | 1359.15 | 331.4412 | 1690.5912 | 0 | 1690.5912 | 0 | 0 | 80.395 | 19.605 | 0 | 80.395 | 19.605 | 0
228 | 15 | August | 7.7 | 9.4798 | 1059.95 | 468.2974 | 1528.2474 | 0 | 1528.2474 | 0 | 0 | 69.3572 | 30.6428 | 0 | 69.3572 | 30.6428 | 0
228 | 16 | August | 8.2 | 10.0954 | 1359.15 | 351.6105 | 1710.7605 | 0 | 1710.7605 | 0 | 0 | 79.4471 | 20.5529 | 0 | 79.4471 | 20.5529 | 0
228 | 17 | August | 6.2 | 7.6331 | 625.6 | 233.0953 | 858.6953 | 0 | 858.6953 | 0 | 0 | 72.8547 | 27.1453 | 0 | 72.8547 | 27.1453 | 0
228 | 18 | August | 6.7 | 8.2487 | 761.6 | 116.424 | 878.024 | 0 | 878.024 | 0 | 0 | 86.7402 | 13.2598 | 0 | 86.7402 | 13.2598 | 0
228 | 19 | August | 6.2 | 7.6331 | 625.6 | 26.46 | 652.06 | 0 | 652.06 | 0 | 0 | 95.9421 | 4.0579 | 0 | 95.9421 | 4.0579 | 0
228 | 20 | August | 2.6 | 3.201 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
228 | 21 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
228 | 22 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
228 | 23 | August | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
228 | 24 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
229 | 1 | August | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
229 | 2 | August | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
229 | 3 | August | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
229 | 4 | August | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
229 | 5 | August | 6.2 | 7.6331 | 625.6 | 1.323 | 626.923 | 0 | 626.923 | 0 | 0 | 99.789 | 0.21103 | 0 | 99.789 | 0.21103 | 0
229 | 6 | August | 5.1 | 6.2788 | 312.8 | 48.951 | 361.751 | 0 | 361.751 | 0 | 0 | 86.4683 | 13.5317 | 0 | 86.4683 | 13.5317 | 0
229 | 7 | August | 7.2 | 8.8642 | 908.65 | 122.7635 | 1031.4135 | 0 | 1031.4135 | 0 | 0 | 88.0975 | 11.9025 | 0 | 88.0975 | 11.9025 | 0
229 | 8 | August | 7.2 | 8.8642 | 908.65 | 243.2906 | 1151.9406 | 0 | 1151.9406 | 0 | 0 | 78.8799 | 21.1201 | 0 | 78.8799 | 21.1201 | 0
229 | 9 | August | 5.1 | 6.2788 | 312.8 | 370.1591 | 682.9591 | 0 | 682.9591 | 0 | 0 | 45.8007 | 54.1993 | 0 | 45.8007 | 54.1993 | 0
229 | 10 | August | 7.7 | 9.4798 | 1059.95 | 488.2427 | 1548.1927 | 0 | 1548.1927 | 0 | 0 | 68.4637 | 31.5363 | 0 | 68.4637 | 31.5363 | 0
229 | 11 | August | 5.7 | 7.0175 | 504.9 | 784.1864 | 1289.0864 | 0 | 1289.0864 | 0 | 0 | 39.1673 | 60.8327 | 0 | 39.1673 | 60.8327 | 0
229 | 12 | August | 6.2 | 7.6331 | 625.6 | 611.1715 | 1236.7715 | 0 | 1236.7715 | 0 | 0 | 50.5833 | 49.4167 | 0 | 50.5833 | 49.4167 | 0
229 | 13 | August | 6.2 | 7.6331 | 625.6 | 848.8541 | 1474.4541 | 0 | 1474.4541 | 0 | 0 | 42.4293 | 57.5707 | 0 | 42.4293 | 57.5707 | 0
229 | 14 | August | 7.2 | 8.8642 | 908.65 | 550.8969 | 1459.5469 | 0 | 1459.5469 | 0 | 0 | 62.2556 | 37.7444 | 0 | 62.2556 | 37.7444 | 0
229 | 15 | August | 5.7 | 7.0175 | 504.9 | 755.4679 | 1260.3679 | 0 | 1260.3679 | 0 | 0 | 40.0597 | 59.9403 | 0 | 40.0597 | 59.9403 | 0
229 | 16 | August | 6.2 | 7.6331 | 625.6 | 467.7741 | 1093.3741 | 0 | 1093.3741 | 0 | 0 | 57.2174 | 42.7826 | 0 | 57.2174 | 42.7826 | 0
229 | 17 | August | 6.7 | 8.2487 | 761.6 | 262.9773 | 1024.5773 | 0 | 1024.5773 | 0 | 0 | 74.3331 | 25.6669 | 0 | 74.3331 | 25.6669 | 0
229 | 18 | August | 7.2 | 8.8642 | 908.65 | 113.778 | 1022.428 | 0 | 1022.428 | 0 | 0 | 88.8718 | 11.1282 | 0 | 88.8718 | 11.1282 | 0
229 | 19 | August | 6.7 | 8.2487 | 761.6 | 25.137 | 786.737 | 0 | 786.737 | 0 | 0 | 96.8049 | 3.1951 | 0 | 96.8049 | 3.1951 | 0
229 | 20 | August | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
229 | 21 | August | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
229 | 22 | August | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
229 | 23 | August | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
229 | 24 | August | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
230 | 1 | August | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
230 | 2 | August | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
230 | 3 | August | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
230 | 4 | August | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
230 | 5 | August | 6.7 | 8.2487 | 761.6 | 1.323 | 762.923 | 0 | 762.923 | 0 | 0 | 99.8266 | 0.17341 | 0 | 99.8266 | 0.17341 | 0
230 | 6 | August | 5.7 | 7.0175 | 504.9 | 35.721 | 540.621 | 0 | 540.621 | 0 | 0 | 93.3926 | 6.6074 | 0 | 93.3926 | 6.6074 | 0
230 | 7 | August | 5.7 | 7.0175 | 504.9 | 244.976 | 749.876 | 0 | 749.876 | 0 | 0 | 67.3311 | 32.6689 | 0 | 67.3311 | 32.6689 | 0
230 | 8 | August | 6.2 | 7.6331 | 625.6 | 148.176 | 773.776 | 0 | 773.776 | 0 | 0 | 80.8503 | 19.1497 | 0 | 80.8503 | 19.1497 | 0
230 | 9 | August | 7.2 | 8.8642 | 908.65 | 397.4265 | 1306.0765 | 0 | 1306.0765 | 0 | 0 | 69.571 | 30.429 | 0 | 69.571 | 30.429 | 0
230 | 10 | August | 5.7 | 7.0175 | 504.9 | 979.947 | 1484.847 | 0 | 1484.847 | 0 | 0 | 34.0035 | 65.9965 | 0 | 34.0035 | 65.9965 | 0
230 | 11 | August | 6.7 | 8.2487 | 761.6 | 1174.0247 | 1935.6247 | 0 | 1935.6247 | 0 | 0 | 39.3465 | 60.6535 | 0 | 39.3465 | 60.6535 | 0
230 | 12 | August | 6.7 | 8.2487 | 761.6 | 1210.996 | 1972.596 | 0 | 1972.596 | 0 | 0 | 38.609 | 61.391 | 0 | 38.609 | 61.391 | 0
230 | 13 | August | 6.7 | 8.2487 | 761.6 | 1271.7697 | 2033.3697 | 1 | 2000 | 33.3697 | 1.6685 | 37.4551 | 61.92 | 2.6239 | 36.4115 | 62.5449 | 4.3815
230 | 14 | August | 5.9 | 7.2638 | 504.9 | 1191.5638 | 1696.4638 | 0 | 1696.4638 | 0 | 0 | 29.7619 | 70.2381 | 0 | 29.7619 | 70.2381 | 0
230 | 15 | August | 5.1 | 6.2788 | 312.8 | 980.1862 | 1292.9862 | 0 | 1292.9862 | 0 | 0 | 24.1921 | 75.8079 | 0 | 24.1921 | 75.8079 | 0
230 | 16 | August | 5.4 | 6.6482 | 399.5 | 638.4296 | 1037.9296 | 0 | 1037.9296 | 0 | 0 | 38.4901 | 61.5099 | 0 | 38.4901 | 61.5099 | 0
230 | 17 | August | 5.7 | 7.0175 | 504.9 | 329.022 | 833.922 | 0 | 833.922 | 0 | 0 | 60.5452 | 39.4548 | 0 | 60.5452 | 39.4548 | 0
230 | 18 | August | 5.1 | 6.2788 | 312.8 | 111.132 | 423.932 | 0 | 423.932 | 0 | 0 | 73.7854 | 26.2146 | 0 | 73.7854 | 26.2146 | 0
230 | 19 | August | 3.6 | 4.4321 | 75.65 | 22.491 | 98.141 | 0 | 98.141 | 0 | 0 | 77.083 | 22.917 | 0 | 77.083 | 22.917 | 0
230 | 20 | August | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
230 | 21 | August | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
230 | 22 | August | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230 | 23 | August | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230 | 24 | August | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
231 | 1 | August | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
231 | 2 | August | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
231 | 3 | August | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
231 | 4 | August | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
231 | 5 | August | 3.6 | 4.4321 | 75.65 | 1.323 | 76.973 | 0 | 76.973 | 0 | 0 | 98.2812 | 1.7188 | 0 | 98.2812 | 1.7188 | 0
231 | 6 | August | 3.1 | 3.8165 | 0 | 26.46 | 26.46 | 0 | 26.46 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
231 | 7 | August | 4.6 | 5.6633 | 237.15 | 226.5748 | 463.7248 | 0 | 463.7248 | 0 | 0 | 51.1402 | 48.8598 | 0 | 51.1402 | 48.8598 | 0
231 | 8 | August | 7.2 | 8.8642 | 908.65 | 244.2043 | 1152.8543 | 0 | 1152.8543 | 0 | 0 | 78.8174 | 21.1826 | 0 | 78.8174 | 21.1826 | 0
231 | 9 | August | 6.7 | 8.2487 | 761.6 | 523.0946 | 1284.6946 | 0 | 1284.6946 | 0 | 0 | 59.2826 | 40.7174 | 0 | 59.2826 | 40.7174 | 0
231 | 10 | August | 4.1 | 5.0477 | 173.4 | 484.2833 | 657.6833 | 0 | 657.6833 | 0 | 0 | 26.3653 | 73.6347 | 0 | 26.3653 | 73.6347 | 0
231 | 11 | August | 4.1 | 5.0477 | 173.4 | 554.9292 | 728.3292 | 0 | 728.3292 | 0 | 0 | 23.8079 | 76.1921 | 0 | 23.8079 | 76.1921 | 0
231 | 12 | August | 5.1 | 6.2788 | 312.8 | 823.6804 | 1136.4804 | 0 | 1136.4804 | 0 | 0 | 27.5236 | 72.4764 | 0 | 27.5236 | 72.4764 | 0
231 | 13 | August | 6.2 | 7.6331 | 625.6 | 1010.2368 | 1635.8368 | 0 | 1635.8368 | 0 | 0 | 38.2434 | 61.7566 | 0 | 38.2434 | 61.7566 | 0
231 | 14 | August | 6.2 | 7.6331 | 625.6 | 551.0156 | 1176.6156 | 0 | 1176.6156 | 0 | 0 | 53.1694 | 46.8306 | 0 | 53.1694 | 46.8306 | 0
231 | 15 | August | 6.2 | 7.6331 | 625.6 | 460.2699 | 1085.8699 | 0 | 1085.8699 | 0 | 0 | 57.6128 | 42.3872 | 0 | 57.6128 | 42.3872 | 0
231 | 16 | August | 7.2 | 8.8642 | 908.65 | 460.3522 | 1369.0022 | 0 | 1369.0022 | 0 | 0 | 66.3732 | 33.6268 | 0 | 66.3732 | 33.6268 | 0
231 | 17 | August | 6.2 | 7.6331 | 625.6 | 351.5477 | 977.1477 | 0 | 977.1477 | 0 | 0 | 64.0231 | 35.9769 | 0 | 64.0231 | 35.9769 | 0
231 | 18 | August | 5.1 | 6.2788 | 312.8 | 154.6148 | 467.4148 | 0 | 467.4148 | 0 | 0 | 66.9213 | 33.0787 | 0 | 66.9213 | 33.0787 | 0
231 | 19 | August | 4.1 | 5.0477 | 173.4 | 37.044 | 210.444 | 0 | 210.444 | 0 | 0 | 82.3972 | 17.6028 | 0 | 82.3972 | 17.6028 | 0
231 | 20 | August | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
231 | 21 | August | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
231 | 22 | August | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
231 | 23 | August | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
231 | 24 | August | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
232 | 1 | August | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
232 | 2 | August | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
232 | 3 | August | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
232 | 4 | August | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
232 | 5 | August | 3.1 | 3.8165 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
232 | 6 | August | 3.6 | 4.4321 | 75.65 | 31.752 | 107.402 | 0 | 107.402 | 0 | 0 | 70.4363 | 29.5637 | 0 | 70.4363 | 29.5637 | 0
232 | 7 | August | 3.6 | 4.4321 | 75.65 | 115.101 | 190.751 | 0 | 190.751 | 0 | 0 | 39.659 | 60.341 | 0 | 39.659 | 60.341 | 0
232 | 8 | August | 4.1 | 5.0477 | 173.4 | 235.3168 | 408.7168 | 0 | 408.7168 | 0 | 0 | 42.4255 | 57.5745 | 0 | 42.4255 | 57.5745 | 0
232 | 9 | August | 4.1 | 5.0477 | 173.4 | 363.4232 | 536.8232 | 0 | 536.8232 | 0 | 0 | 32.3011 | 67.6989 | 0 | 32.3011 | 67.6989 | 0
232 | 10 | August | 4.1 | 5.0477 | 173.4 | 481.3824 | 654.7824 | 0 | 654.7824 | 0 | 0 | 26.4821 | 73.5179 | 0 | 26.4821 | 73.5179 | 0
232 | 11 | August | 5.1 | 6.2788 | 312.8 | 564.5341 | 877.3341 | 0 | 877.3341 | 0 | 0 | 35.6535 | 64.3465 | 0 | 35.6535 | 64.3465 | 0
232 | 12 | August | 5.1 | 6.2788 | 312.8 | 590.0975 | 902.8975 | 0 | 902.8975 | 0 | 0 | 34.644 | 65.356 | 0 | 34.644 | 65.356 | 0
232 | 13 | August | 5.1 | 6.2788 | 312.8 | 814.8145 | 1127.6145 | 0 | 1127.6145 | 0 | 0 | 27.74 | 72.26 | 0 | 27.74 | 72.26 | 0
232 | 14 | August | 1 | 1.2311 | 0 | 543.6842 | 543.6842 | 0 | 543.6842 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
232 | 15 | August | 3.1 | 3.8165 | 0 | 454.9467 | 454.9467 | 0 | 454.9467 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
232 | 16 | August | 3.1 | 3.8165 | 0 | 340.6951 | 340.6951 | 0 | 340.6951 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
232 | 17 | August | 1.5 | 1.8467 | 0 | 220.3224 | 220.3224 | 0 | 220.3224 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
232 | 18 | August | 1 | 1.2311 | 0 | 104.517 | 104.517 | 0 | 104.517 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
232 | 19 | August | 1 | 1.2311 | 0 | 19.845 | 19.845 | 0 | 19.845 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
232 | 20 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
232 | 21 | August | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
232 | 22 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
232 | 23 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
232 | 24 | August | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
233 | 1 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
233 | 2 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
233 | 3 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
233 | 4 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
233 | 5 | August | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
233 | 6 | August | 1.5 | 1.8467 | 0 | 14.553 | 14.553 | 0 | 14.553 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
233 | 7 | August | 1.5 | 1.8467 | 0 | 112.455 | 112.455 | 0 | 112.455 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
233 | 8 | August | 2.1 | 2.5854 | 0 | 232.6587 | 232.6587 | 0 | 232.6587 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
233 | 9 | August | 2.6 | 3.201 | 0 | 725.7802 | 725.7802 | 0 | 725.7802 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
233 | 10 | August | 3.1 | 3.8165 | 0 | 1080.3938 | 1080.3938 | 0 | 1080.3938 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
233 | 11 | August | 4.1 | 5.0477 | 173.4 | 1261.1701 | 1434.5701 | 0 | 1434.5701 | 0 | 0 | 12.0872 | 87.9128 | 0 | 12.0872 | 87.9128 | 0
233 | 12 | August | 3.6 | 4.4321 | 75.65 | 1024.3097 | 1099.9597 | 0 | 1099.9597 | 0 | 0 | 6.8775 | 93.1225 | 0 | 6.8775 | 93.1225 | 0
233 | 13 | August | 4.1 | 5.0477 | 173.4 | 1165.055 | 1338.455 | 0 | 1338.455 | 0 | 0 | 12.9552 | 87.0448 | 0 | 12.9552 | 87.0448 | 0
233 | 14 | August | 4.1 | 5.0477 | 173.4 | 1142.7913 | 1316.1913 | 0 | 1316.1913 | 0 | 0 | 13.1744 | 86.8256 | 0 | 13.1744 | 86.8256 | 0
233 | 15 | August | 3.6 | 4.4321 | 75.65 | 847.9943 | 923.6443 | 0 | 923.6443 | 0 | 0 | 8.1904 | 91.8096 | 0 | 8.1904 | 91.8096 | 0
233 | 16 | August | 2.6 | 3.201 | 0 | 601.1401 | 601.1401 | 0 | 601.1401 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
233 | 17 | August | 2.6 | 3.201 | 0 | 339.1148 | 339.1148 | 0 | 339.1148 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
233 | 18 | August | 2.1 | 2.5854 | 0 | 129.8546 | 129.8546 | 0 | 129.8546 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
233 | 19 | August | 2.6 | 3.201 | 0 | 26.46 | 26.46 | 0 | 26.46 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
233 | 20 | August | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
233 | 21 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
233 | 22 | August | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
233 | 23 | August | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
233 | 24 | August | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
234 | 1 | August | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
234 | 2 | August | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
234 | 3 | August | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
234 | 4 | August | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
234 | 5 | August | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
234 | 6 | August | 6.2 | 7.6331 | 625.6 | 22.491 | 648.091 | 0 | 648.091 | 0 | 0 | 96.5297 | 3.4703 | 0 | 96.5297 | 3.4703 | 0
234 | 7 | August | 6.7 | 8.2487 | 761.6 | 109.809 | 871.409 | 0 | 871.409 | 0 | 0 | 87.3987 | 12.6013 | 0 | 87.3987 | 12.6013 | 0
234 | 8 | August | 6.7 | 8.2487 | 761.6 | 231.5185 | 993.1185 | 0 | 993.1185 | 0 | 0 | 76.6877 | 23.3123 | 0 | 76.6877 | 23.3123 | 0
234 | 9 | August | 6.7 | 8.2487 | 761.6 | 355.5707 | 1117.1707 | 0 | 1117.1707 | 0 | 0 | 68.1722 | 31.8278 | 0 | 68.1722 | 31.8278 | 0
234 | 10 | August | 6.7 | 8.2487 | 761.6 | 662.3564 | 1423.9564 | 0 | 1423.9564 | 0 | 0 | 53.4848 | 46.5152 | 0 | 53.4848 | 46.5152 | 0
234 | 11 | August | 7.7 | 9.4798 | 1059.95 | 1167.3221 | 2227.2721 | 1 | 2000 | 227.2721 | 11.3636 | 47.5896 | 47.0025 | 19.4695 | 41.6339 | 52.4104 | 21.4418
234 | 12 | August | 8.2 | 10.0954 | 1359.15 | 1388.4664 | 2747.6164 | 1 | 2000 | 747.6164 | 37.3808 | 49.4665 | 32.0425 | 53.8448 | 30.5767 | 50.5335 | 55.0062
234 | 13 | August | 7.7 | 9.4798 | 1059.95 | 1263.8747 | 2323.8247 | 1 | 2000 | 323.8247 | 16.1912 | 45.6123 | 47.0025 | 25.6216 | 36.8063 | 54.3877 | 30.5509
234 | 14 | August | 6.7 | 8.2487 | 761.6 | 719.4478 | 1481.0478 | 0 | 1481.0478 | 0 | 0 | 51.4231 | 48.5769 | 0 | 51.4231 | 48.5769 | 0
234 | 15 | August | 7.7 | 9.4798 | 1059.95 | 446.1183 | 1506.0683 | 0 | 1506.0683 | 0 | 0 | 70.3786 | 29.6214 | 0 | 70.3786 | 29.6214 | 0
234 | 16 | August | 7.2 | 8.8642 | 908.65 | 205.065 | 1113.715 | 0 | 1113.715 | 0 | 0 | 81.5873 | 18.4127 | 0 | 81.5873 | 18.4127 | 0
234 | 17 | August | 7.7 | 9.4798 | 1059.95 | 211.3986 | 1271.3486 | 0 | 1271.3486 | 0 | 0 | 83.3721 | 16.6279 | 0 | 83.3721 | 16.6279 | 0
234 | 18 | August | 6.2 | 7.6331 | 625.6 | 123.2401 | 748.8401 | 0 | 748.8401 | 0 | 0 | 83.5425 | 16.4575 | 0 | 83.5425 | 16.4575 | 0
234 | 19 | August | 6.7 | 8.2487 | 761.6 | 29.106 | 790.706 | 0 | 790.706 | 0 | 0 | 96.319 | 3.681 | 0 | 96.319 | 3.681 | 0
234 | 20 | August | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
234 | 21 | August | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
234 | 22 | August | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
234 | 23 | August | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
234 | 24 | August | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
235 | 1 | August | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
235 | 2 | August | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
235 | 3 | August | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
235 | 4 | August | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
235 | 5 | August | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
235 | 6 | August | 1.5 | 1.8467 | 0 | 26.46 | 26.46 | 0 | 26.46 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
235 | 7 | August | 1 | 1.2311 | 0 | 107.163 | 107.163 | 0 | 107.163 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
235 | 8 | August | 1.5 | 1.8467 | 0 | 236.6786 | 236.6786 | 0 | 236.6786 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
235 | 9 | August | 2.1 | 2.5854 | 0 | 348.789 | 348.789 | 0 | 348.789 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
235 | 10 | August | 3.1 | 3.8165 | 0 | 827.3235 | 827.3235 | 0 | 827.3235 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
235 | 11 | August | 2.1 | 2.5854 | 0 | 1276.593 | 1276.593 | 0 | 1276.593 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
235 | 12 | August | 2.8 | 3.4472 | 0 | 1345.6936 | 1345.6936 | 0 | 1345.6936 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
235 | 13 | August | 3.4 | 4.1859 | 75.65 | 1228.3213 | 1303.9713 | 0 | 1303.9713 | 0 | 0 | 5.8015 | 94.1985 | 0 | 5.8015 | 94.1985 | 0
235 | 14 | August | 4.1 | 5.0477 | 173.4 | 1035.6187 | 1209.0187 | 0 | 1209.0187 | 0 | 0 | 14.3422 | 85.6578 | 0 | 14.3422 | 85.6578 | 0
235 | 15 | August | 5.7 | 7.0175 | 504.9 | 442.7363 | 947.6363 | 0 | 947.6363 | 0 | 0 | 53.2799 | 46.7201 | 0 | 53.2799 | 46.7201 | 0
235 | 16 | August | 5.1 | 6.2788 | 312.8 | 328.8828 | 641.6828 | 0 | 641.6828 | 0 | 0 | 48.7468 | 51.2532 | 0 | 48.7468 | 51.2532 | 0
235 | 17 | August | 4.6 | 5.6633 | 237.15 | 301.6896 | 538.8396 | 0 | 538.8396 | 0 | 0 | 44.0112 | 55.9888 | 0 | 44.0112 | 55.9888 | 0
235 | 18 | August | 2.6 | 3.201 | 0 | 93.933 | 93.933 | 0 | 93.933 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
235 | 19 | August | 3.1 | 3.8165 | 0 | 15.876 | 15.876 | 0 | 15.876 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
235 | 20 | August | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
235 | 21 | August | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
235 | 22 | August | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
235 | 23 | August | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
235 | 24 | August | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
236 | 1 | August | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
236 | 2 | August | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
236 | 3 | August | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
236 | 4 | August | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
236 | 5 | August | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
236 | 6 | August | 2.6 | 3.201 | 0 | 33.075 | 33.075 | 0 | 33.075 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
236 | 7 | August | 3.6 | 4.4321 | 75.65 | 224.8284 | 300.4784 | 0 | 300.4784 | 0 | 0 | 25.1765 | 74.8235 | 0 | 25.1765 | 74.8235 | 0
236 | 8 | August | 6.2 | 7.6331 | 625.6 | 504.5305 | 1130.1305 | 0 | 1130.1305 | 0 | 0 | 55.3564 | 44.6436 | 0 | 55.3564 | 44.6436 | 0
236 | 9 | August | 6.2 | 7.6331 | 625.6 | 511.258 | 1136.858 | 0 | 1136.858 | 0 | 0 | 55.0289 | 44.9711 | 0 | 55.0289 | 44.9711 | 0
236 | 10 | August | 6.2 | 7.6331 | 625.6 | 830.7583 | 1456.3583 | 0 | 1456.3583 | 0 | 0 | 42.9565 | 57.0435 | 0 | 42.9565 | 57.0435 | 0
236 | 11 | August | 6.2 | 7.6331 | 625.6 | 557.1654 | 1182.7654 | 0 | 1182.7654 | 0 | 0 | 52.893 | 47.107 | 0 | 52.893 | 47.107 | 0
236 | 12 | August | 5.1 | 6.2788 | 312.8 | 589.2069 | 902.0069 | 0 | 902.0069 | 0 | 0 | 34.6782 | 65.3218 | 0 | 34.6782 | 65.3218 | 0
236 | 13 | August | 5.1 | 6.2788 | 312.8 | 582.8318 | 895.6318 | 0 | 895.6318 | 0 | 0 | 34.9251 | 65.0749 | 0 | 34.9251 | 65.0749 | 0
236 | 14 | August | 5.7 | 7.0175 | 504.9 | 533.6268 | 1038.5268 | 0 | 1038.5268 | 0 | 0 | 48.6169 | 51.3831 | 0 | 48.6169 | 51.3831 | 0
236 | 15 | August | 4.6 | 5.6633 | 237.15 | 601.3884 | 838.5384 | 0 | 838.5384 | 0 | 0 | 28.2814 | 71.7186 | 0 | 28.2814 | 71.7186 | 0
236 | 16 | August | 4.1 | 5.0477 | 173.4 | 613.0657 | 786.4657 | 0 | 786.4657 | 0 | 0 | 22.048 | 77.952 | 0 | 22.048 | 77.952 | 0
236 | 17 | August | 7.2 | 8.8642 | 908.65 | 260.1761 | 1168.8261 | 0 | 1168.8261 | 0 | 0 | 77.7404 | 22.2596 | 0 | 77.7404 | 22.2596 | 0
236 | 18 | August | 1 | 1.2311 | 0 | 114.9982 | 114.9982 | 0 | 114.9982 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
236 | 19 | August | 1 | 1.2311 | 0 | 14.553 | 14.553 | 0 | 14.553 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
236 | 20 | August | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
236 | 21 | August | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
236 | 22 | August | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
236 | 23 | August | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
236 | 24 | August | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
237 | 1 | August | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
237 | 2 | August | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
237 | 3 | August | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
237 | 4 | August | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
237 | 5 | August | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
237 | 6 | August | 2.6 | 3.201 | 0 | 30.429 | 30.429 | 0 | 30.429 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
237 | 7 | August | 2.6 | 3.201 | 0 | 216.8976 | 216.8976 | 0 | 216.8976 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
237 | 8 | August | 3.6 | 4.4321 | 75.65 | 520.0409 | 595.6909 | 0 | 595.6909 | 0 | 0 | 12.6995 | 87.3005 | 0 | 12.6995 | 87.3005 | 0
237 | 9 | August | 3.6 | 4.4321 | 75.65 | 647.7805 | 723.4305 | 0 | 723.4305 | 0 | 0 | 10.4571 | 89.5429 | 0 | 10.4571 | 89.5429 | 0
237 | 10 | August | 3.1 | 3.8165 | 0 | 464.9428 | 464.9428 | 0 | 464.9428 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
237 | 11 | August | 4.1 | 5.0477 | 173.4 | 539.6999 | 713.0999 | 0 | 713.0999 | 0 | 0 | 24.3164 | 75.6836 | 0 | 24.3164 | 75.6836 | 0
237 | 12 | August | 3.6 | 4.4321 | 75.65 | 574.8127 | 650.4627 | 0 | 650.4627 | 0 | 0 | 11.6302 | 88.3698 | 0 | 11.6302 | 88.3698 | 0
237 | 13 | August | 3.1 | 3.8165 | 0 | 566.4926 | 566.4926 | 0 | 566.4926 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
237 | 14 | August | 1.5 | 1.8467 | 0 | 519.8189 | 519.8189 | 0 | 519.8189 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
237 | 15 | August | 5.7 | 7.0175 | 504.9 | 436.7235 | 941.6235 | 0 | 941.6235 | 0 | 0 | 53.6202 | 46.3798 | 0 | 53.6202 | 46.3798 | 0
237 | 16 | August | 5.7 | 7.0175 | 504.9 | 429.8238 | 934.7238 | 0 | 934.7238 | 0 | 0 | 54.016 | 45.984 | 0 | 54.016 | 45.984 | 0
237 | 17 | August | 5.1 | 6.2788 | 312.8 | 254.0896 | 566.8896 | 0 | 566.8896 | 0 | 0 | 55.1783 | 44.8217 | 0 | 55.1783 | 44.8217 | 0
237 | 18 | August | 4.6 | 5.6633 | 237.15 | 87.318 | 324.468 | 0 | 324.468 | 0 | 0 | 73.0889 | 26.9111 | 0 | 73.0889 | 26.9111 | 0
237 | 19 | August | 1 | 1.2311 | 0 | 19.845 | 19.845 | 0 | 19.845 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
237 | 20 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
237 | 21 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
237 | 22 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
237 | 23 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
237 | 24 | August | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
238 | 1 | August | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
238 | 2 | August | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
238 | 3 | August | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
238 | 4 | August | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
238 | 5 | August | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
238 | 6 | August | 1.5 | 1.8467 | 0 | 17.199 | 17.199 | 0 | 17.199 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
238 | 7 | August | 3.1 | 3.8165 | 0 | 100.548 | 100.548 | 0 | 100.548 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
238 | 8 | August | 4.1 | 5.0477 | 173.4 | 221.2937 | 394.6937 | 0 | 394.6937 | 0 | 0 | 43.9328 | 56.0672 | 0 | 43.9328 | 56.0672 | 0
238 | 9 | August | 3.1 | 3.8165 | 0 | 344.812 | 344.812 | 0 | 344.812 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
238 | 10 | August | 4.6 | 5.6633 | 237.15 | 270.1281 | 507.2781 | 0 | 507.2781 | 0 | 0 | 46.7495 | 53.2505 | 0 | 46.7495 | 53.2505 | 0
238 | 11 | August | 4.6 | 5.6633 | 237.15 | 313.3281 | 550.4781 | 0 | 550.4781 | 0 | 0 | 43.0807 | 56.9193 | 0 | 43.0807 | 56.9193 | 0
238 | 12 | August | 4.1 | 5.0477 | 173.4 | 568.9094 | 742.3094 | 0 | 742.3094 | 0 | 0 | 23.3595 | 76.6405 | 0 | 23.3595 | 76.6405 | 0
238 | 13 | August | 4.6 | 5.6633 | 237.15 | 563.6466 | 800.7966 | 0 | 800.7966 | 0 | 0 | 29.6143 | 70.3857 | 0 | 29.6143 | 70.3857 | 0
238 | 14 | August | 4.1 | 5.0477 | 173.4 | 869.9204 | 1043.3204 | 0 | 1043.3204 | 0 | 0 | 16.62 | 83.38 | 0 | 16.62 | 83.38 | 0
238 | 15 | August | 3.6 | 4.4321 | 75.65 | 879.0915 | 954.7415 | 0 | 954.7415 | 0 | 0 | 7.9236 | 92.0764 | 0 | 7.9236 | 92.0764 | 0
238 | 16 | August | 3.1 | 3.8165 | 0 | 630.6165 | 630.6165 | 0 | 630.6165 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
238 | 17 | August | 3.1 | 3.8165 | 0 | 326.298 | 326.298 | 0 | 326.298 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
238 | 18 | August | 3.1 | 3.8165 | 0 | 84.672 | 84.672 | 0 | 84.672 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
238 | 19 | August | 3.1 | 3.8165 | 0 | 21.168 | 21.168 | 0 | 21.168 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
238 | 20 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
238 | 21 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
238 | 22 | August | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
238 | 23 | August | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
238 | 24 | August | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
239 | 1 | August | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
239 | 2 | August | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
239 | 3 | August | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
239 | 4 | August | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
239 | 5 | August | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
239 | 6 | August | 2.6 | 3.201 | 0 | 10.584 | 10.584 | 0 | 10.584 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
239 | 7 | August | 4.1 | 5.0477 | 173.4 | 97.902 | 271.302 | 0 | 271.302 | 0 | 0 | 63.914 | 36.086 | 0 | 63.914 | 36.086 | 0
239 | 8 | August | 5.7 | 7.0175 | 504.9 | 217.7683 | 722.6683 | 0 | 722.6683 | 0 | 0 | 69.8661 | 30.1339 | 0 | 69.8661 | 30.1339 | 0
239 | 9 | August | 7.7 | 9.4798 | 1059.95 | 340.9735 | 1400.9235 | 0 | 1400.9235 | 0 | 0 | 75.6608 | 24.3392 | 0 | 75.6608 | 24.3392 | 0
239 | 10 | August | 7.7 | 9.4798 | 1059.95 | 460.8167 | 1520.7667 | 0 | 1520.7667 | 0 | 0 | 69.6984 | 30.3016 | 0 | 69.6984 | 30.3016 | 0
239 | 11 | August | 6.7 | 8.2487 | 761.6 | 940.4824 | 1702.0824 | 0 | 1702.0824 | 0 | 0 | 44.7452 | 55.2548 | 0 | 44.7452 | 55.2548 | 0
239 | 12 | August | 1 | 1.2311 | 0 | 1176.7244 | 1176.7244 | 0 | 1176.7244 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
239 | 13 | August | 6.2 | 7.6331 | 625.6 | 1241.0561 | 1866.6561 | 0 | 1866.6561 | 0 | 0 | 33.5145 | 66.4855 | 0 | 33.5145 | 66.4855 | 0
239 | 14 | August | 6.2 | 7.6331 | 625.6 | 1177.1066 | 1802.7066 | 0 | 1802.7066 | 0 | 0 | 34.7034 | 65.2966 | 0 | 34.7034 | 65.2966 | 0
239 | 15 | August | 7.2 | 8.8642 | 908.65 | 933.828 | 1842.478 | 0 | 1842.478 | 0 | 0 | 49.3167 | 50.6833 | 0 | 49.3167 | 50.6833 | 0
239 | 16 | August | 6.2 | 7.6331 | 625.6 | 635.561 | 1261.161 | 0 | 1261.161 | 0 | 0 | 49.6051 | 50.3949 | 0 | 49.6051 | 50.3949 | 0
239 | 17 | August | 5.1 | 6.2788 | 312.8 | 331.5004 | 644.3004 | 0 | 644.3004 | 0 | 0 | 48.5488 | 51.4512 | 0 | 48.5488 | 51.4512 | 0
239 | 18 | August | 3.1 | 3.8165 | 0 | 116.9208 | 116.9208 | 0 | 116.9208 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
239 | 19 | August | 2.6 | 3.201 | 0 | 19.845 | 19.845 | 0 | 19.845 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
239 | 20 | August | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
239 | 21 | August | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
239 | 22 | August | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
239 | 23 | August | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
239 | 24 | August | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
240 | 1 | August | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
240 | 2 | August | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
240 | 3 | August | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
240 | 4 | August | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
240 | 5 | August | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
240 | 6 | August | 6.7 | 8.2487 | 761.6 | 27.783 | 789.383 | 0 | 789.383 | 0 | 0 | 96.4804 | 3.5196 | 0 | 96.4804 | 3.5196 | 0
240 | 7 | August | 6.7 | 8.2487 | 761.6 | 209.0647 | 970.6647 | 0 | 970.6647 | 0 | 0 | 78.4617 | 21.5383 | 0 | 78.4617 | 21.5383 | 0
240 | 8 | August | 7.2 | 8.8642 | 908.65 | 522.2626 | 1430.9126 | 0 | 1430.9126 | 0 | 0 | 63.5014 | 36.4986 | 0 | 63.5014 | 36.4986 | 0
240 | 9 | August | 8.2 | 10.0954 | 1359.15 | 845.4101 | 2204.5601 | 1 | 2000 | 204.5601 | 10.228 | 61.6518 | 32.0425 | 24.1966 | 57.7295 | 38.3482 | 15.0506
240 | 10 | August | 8.2 | 10.0954 | 1359.15 | 1129.7576 | 2488.9076 | 1 | 2000 | 488.9076 | 24.4454 | 54.6083 | 32.0425 | 43.2754 | 43.5121 | 45.3917 | 35.9716
240 | 11 | August | 8.7 | 10.711 | 1490.05 | 1255.2194 | 2745.2694 | 1 | 2000 | 745.2694 | 37.2635 | 54.277 | 25.4975 | 59.3736 | 37.239 | 45.723 | 50.0164
240 | 12 | August | 10.3 | 12.6808 | 1694.9 | 1316.0986 | 3010.9986 | 1 | 2000 | 1010.9986 | 50.5499 | 56.2903 | 15.255 | 76.8178 | 34.1951 | 43.7097 | 59.6495
240 | 13 | August | 9.3 | 11.4496 | 1598.85 | 1153.5759 | 2752.4259 | 1 | 2000 | 752.4259 | 37.6213 | 58.0888 | 20.0575 | 65.2255 | 42.3212 | 41.9112 | 47.0604
240 | 14 | August | 11.3 | 13.9119 | 1700 | 890.3418 | 2590.3418 | 1 | 2000 | 590.3418 | 29.5171 | 65.6284 | 15 | 66.3051 | 55.4829 | 34.3716 | 34.726
240 | 15 | August | 7.2 | 8.8642 | 908.65 | 587.9519 | 1496.6019 | 0 | 1496.6019 | 0 | 0 | 60.7142 | 39.2858 | 0 | 60.7142 | 39.2858 | 0
240 | 16 | August | 7.2 | 8.8642 | 908.65 | 503.7259 | 1412.3759 | 0 | 1412.3759 | 0 | 0 | 64.3349 | 35.6651 | 0 | 64.3349 | 35.6651 | 0
240 | 17 | August | 9.3 | 11.4496 | 1598.85 | 326.3105 | 1925.1605 | 0 | 1925.1605 | 0 | 0 | 83.0502 | 16.9498 | 0 | 83.0502 | 16.9498 | 0
240 | 18 | August | 7.7 | 9.4798 | 1059.95 | 113.3383 | 1173.2883 | 0 | 1173.2883 | 0 | 0 | 90.3401 | 9.6599 | 0 | 90.3401 | 9.6599 | 0
240 | 19 | August | 6.2 | 7.6331 | 625.6 | 18.522 | 644.122 | 0 | 644.122 | 0 | 0 | 97.1245 | 2.8755 | 0 | 97.1245 | 2.8755 | 0
240 | 20 | August | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
240 | 21 | August | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
240 | 22 | August | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
240 | 23 | August | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
240 | 24 | August | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
241 | 1 | August | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
241 | 2 | August | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
241 | 3 | August | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
241 | 4 | August | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
241 | 5 | August | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
241 | 6 | August | 5.1 | 6.2788 | 312.8 | 26.46 | 339.26 | 0 | 339.26 | 0 | 0 | 92.2007 | 7.7993 | 0 | 92.2007 | 7.7993 | 0
241 | 7 | August | 6.2 | 7.6331 | 625.6 | 193.3242 | 818.9242 | 0 | 818.9242 | 0 | 0 | 76.3929 | 23.6071 | 0 | 76.3929 | 23.6071 | 0
241 | 8 | August | 6.7 | 8.2487 | 761.6 | 450.7614 | 1212.3614 | 0 | 1212.3614 | 0 | 0 | 62.8196 | 37.1804 | 0 | 62.8196 | 37.1804 | 0
241 | 9 | August | 7.2 | 8.8642 | 908.65 | 492.9608 | 1401.6108 | 0 | 1401.6108 | 0 | 0 | 64.829 | 35.171 | 0 | 64.829 | 35.171 | 0
241 | 10 | August | 7.2 | 8.8642 | 908.65 | 663.0546 | 1571.7046 | 0 | 1571.7046 | 0 | 0 | 57.813 | 42.187 | 0 | 57.813 | 42.187 | 0
241 | 11 | August | 6.2 | 7.6331 | 625.6 | 944.2342 | 1569.8342 | 0 | 1569.8342 | 0 | 0 | 39.8513 | 60.1487 | 0 | 39.8513 | 60.1487 | 0
241 | 12 | August | 5.1 | 6.2788 | 312.8 | 798.9151 | 1111.7151 | 0 | 1111.7151 | 0 | 0 | 28.1367 | 71.8633 | 0 | 28.1367 | 71.8633 | 0
241 | 13 | August | 5.1 | 6.2788 | 312.8 | 1201.1551 | 1513.9551 | 0 | 1513.9551 | 0 | 0 | 20.6611 | 79.3389 | 0 | 20.6611 | 79.3389 | 0
241 | 14 | August | 5.1 | 6.2788 | 312.8 | 1012.4216 | 1325.2216 | 0 | 1325.2216 | 0 | 0 | 23.6036 | 76.3964 | 0 | 23.6036 | 76.3964 | 0
241 | 15 | August | 4.1 | 5.0477 | 173.4 | 590.132 | 763.532 | 0 | 763.532 | 0 | 0 | 22.7102 | 77.2898 | 0 | 22.7102 | 77.2898 | 0
241 | 16 | August | 3.6 | 4.4321 | 75.65 | 309.5831 | 385.2331 | 0 | 385.2331 | 0 | 0 | 19.6375 | 80.3625 | 0 | 19.6375 | 80.3625 | 0
241 | 17 | August | 4.1 | 5.0477 | 173.4 | 237.3532 | 410.7532 | 0 | 410.7532 | 0 | 0 | 42.2151 | 57.7849 | 0 | 42.2151 | 57.7849 | 0
241 | 18 | August | 1.5 | 1.8467 | 0 | 75.411 | 75.411 | 0 | 75.411 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
241 | 19 | August | 1 | 1.2311 | 0 | 14.553 | 14.553 | 0 | 14.553 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
241 | 20 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241 | 21 | August | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241 | 22 | August | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241 | 23 | August | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241 | 24 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242 | 1 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242 | 2 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242 | 3 | August | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242 | 4 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242 | 5 | August | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242 | 6 | August | 1 | 1.2311 | 0 | 14.553 | 14.553 | 0 | 14.553 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
242 | 7 | August | 1 | 1.2311 | 0 | 128.9077 | 128.9077 | 0 | 128.9077 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
242 | 8 | August | 1 | 1.2311 | 0 | 210.6012 | 210.6012 | 0 | 210.6012 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
242 | 9 | August | 1 | 1.2311 | 0 | 489.3425 | 489.3425 | 0 | 489.3425 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
242 | 10 | August | 2.6 | 3.201 | 0 | 453.9892 | 453.9892 | 0 | 453.9892 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
242 | 11 | August | 3.1 | 3.8165 | 0 | 525.7801 | 525.7801 | 0 | 525.7801 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
242 | 12 | August | 3.6 | 4.4321 | 75.65 | 332.8527 | 408.5027 | 0 | 408.5027 | 0 | 0 | 18.5189 | 81.4811 | 0 | 18.5189 | 81.4811 | 0
242 | 13 | August | 3.1 | 3.8165 | 0 | 325.0592 | 325.0592 | 0 | 325.0592 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
242 | 14 | August | 3.1 | 3.8165 | 0 | 297.6715 | 297.6715 | 0 | 297.6715 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
242 | 15 | August | 1 | 1.2311 | 0 | 250.6514 | 250.6514 | 0 | 250.6514 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
242 | 16 | August | 1.5 | 1.8467 | 0 | 303.6095 | 303.6095 | 0 | 303.6095 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
242 | 17 | August | 3.1 | 3.8165 | 0 | 180.9838 | 180.9838 | 0 | 180.9838 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
242 | 18 | August | 2.6 | 3.201 | 0 | 71.442 | 71.442 | 0 | 71.442 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
242 | 19 | August | 0 | 0 | 0 | 9.261 | 9.261 | 0 | 9.261 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
242 | 20 | August | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242 | 21 | August | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242 | 22 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242 | 23 | August | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242 | 24 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
243 | 1 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
243 | 2 | August | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
243 | 3 | August | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
243 | 4 | August | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
243 | 5 | August | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
243 | 6 | August | 0 | 0 | 0 | 7.938 | 7.938 | 0 | 7.938 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
243 | 7 | August | 1 | 1.2311 | 0 | 55.566 | 55.566 | 0 | 55.566 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
243 | 8 | August | 1 | 1.2311 | 0 | 125.685 | 125.685 | 0 | 125.685 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
243 | 9 | August | 3.1 | 3.8165 | 0 | 197.127 | 197.127 | 0 | 197.127 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
243 | 10 | August | 3.1 | 3.8165 | 0 | 259.4635 | 259.4635 | 0 | 259.4635 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
243 | 11 | August | 6.2 | 7.6331 | 625.6 | 521.4852 | 1147.0852 | 0 | 1147.0852 | 0 | 0 | 54.5382 | 45.4618 | 0 | 54.5382 | 45.4618 | 0
243 | 12 | August | 4.6 | 5.6633 | 237.15 | 555.0089 | 792.1589 | 0 | 792.1589 | 0 | 0 | 29.9372 | 70.0628 | 0 | 29.9372 | 70.0628 | 0
243 | 13 | August | 4.6 | 5.6633 | 237.15 | 327.8707 | 565.0207 | 0 | 565.0207 | 0 | 0 | 41.9719 | 58.0281 | 0 | 41.9719 | 58.0281 | 0
243 | 14 | August | 3.6 | 4.4321 | 75.65 | 295.0061 | 370.6561 | 0 | 370.6561 | 0 | 0 | 20.4098 | 79.5902 | 0 | 20.4098 | 79.5902 | 0
243 | 15 | August | 5.7 | 7.0175 | 504.9 | 247.9919 | 752.8919 | 0 | 752.8919 | 0 | 0 | 67.0614 | 32.9386 | 0 | 67.0614 | 32.9386 | 0
243 | 16 | August | 5.7 | 7.0175 | 504.9 | 298.6649 | 803.5649 | 0 | 803.5649 | 0 | 0 | 62.8325 | 37.1675 | 0 | 62.8325 | 37.1675 | 0
243 | 17 | August | 6.7 | 8.2487 | 761.6 | 176.5833 | 938.1833 | 0 | 938.1833 | 0 | 0 | 81.1782 | 18.8218 | 0 | 81.1782 | 18.8218 | 0
243 | 18 | August | 6.7 | 8.2487 | 761.6 | 42.336 | 803.936 | 0 | 803.936 | 0 | 0 | 94.7339 | 5.2661 | 0 | 94.7339 | 5.2661 | 0
243 | 19 | August | 7.2 | 8.8642 | 908.65 | 5.292 | 913.942 | 0 | 913.942 | 0 | 0 | 99.421 | 0.57903 | 0 | 99.421 | 0.57903 | 0
243 | 20 | August | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
243 | 21 | August | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
243 | 22 | August | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
243 | 23 | August | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
243 | 24 | August | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
244 | 1 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
244 | 2 | September | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
244 | 3 | September | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
244 | 4 | September | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
244 | 5 | September | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
244 | 6 | September | 4.6 | 5.6633 | 237.15 | 22.491 | 259.641 | 0 | 259.641 | 0 | 0 | 91.3377 | 8.6623 | 0 | 91.3377 | 8.6623 | 0
244 | 7 | September | 5.7 | 7.0175 | 504.9 | 87.318 | 592.218 | 0 | 592.218 | 0 | 0 | 85.2558 | 14.7442 | 0 | 85.2558 | 14.7442 | 0
244 | 8 | September | 6.2 | 7.6331 | 625.6 | 205.7304 | 831.3304 | 0 | 831.3304 | 0 | 0 | 75.2529 | 24.7471 | 0 | 75.2529 | 24.7471 | 0
244 | 9 | September | 6.2 | 7.6331 | 625.6 | 328.8257 | 954.4257 | 0 | 954.4257 | 0 | 0 | 65.5473 | 34.4527 | 0 | 65.5473 | 34.4527 | 0
244 | 10 | September | 7.2 | 8.8642 | 908.65 | 445.6508 | 1354.3008 | 0 | 1354.3008 | 0 | 0 | 67.0937 | 32.9063 | 0 | 67.0937 | 32.9063 | 0
244 | 11 | September | 7.7 | 9.4798 | 1059.95 | 518.8547 | 1578.8047 | 0 | 1578.8047 | 0 | 0 | 67.1362 | 32.8638 | 0 | 67.1362 | 32.8638 | 0
244 | 12 | September | 8.7 | 10.711 | 1490.05 | 553.6979 | 2043.7479 | 1 | 2000 | 43.7479 | 2.1874 | 72.9077 | 25.4975 | 7.901 | 72.3151 | 27.0923 | 2.936
244 | 13 | September | 7.7 | 9.4798 | 1059.95 | 545.2571 | 1605.2071 | 0 | 1605.2071 | 0 | 0 | 66.032 | 33.968 | 0 | 66.032 | 33.968 | 0
244 | 14 | September | 6.9 | 8.4949 | 761.6 | 496.8423 | 1258.4423 | 0 | 1258.4423 | 0 | 0 | 60.5193 | 39.4807 | 0 | 60.5193 | 39.4807 | 0
244 | 15 | September | 6.2 | 7.6331 | 625.6 | 412.2418 | 1037.8418 | 0 | 1037.8418 | 0 | 0 | 60.2789 | 39.7211 | 0 | 60.2789 | 39.7211 | 0
244 | 16 | September | 5.8 | 7.1406 | 504.9 | 294.9766 | 799.8766 | 0 | 799.8766 | 0 | 0 | 63.1222 | 36.8778 | 0 | 63.1222 | 36.8778 | 0
244 | 17 | September | 5.5 | 6.7713 | 399.5 | 175.6096 | 575.1096 | 0 | 575.1096 | 0 | 0 | 69.465 | 30.535 | 0 | 69.465 | 30.535 | 0
244 | 18 | September | 5.1 | 6.2788 | 312.8 | 66.15 | 378.95 | 0 | 378.95 | 0 | 0 | 82.5439 | 17.4561 | 0 | 82.5439 | 17.4561 | 0
244 | 19 | September | 4.4 | 5.417 | 173.4 | 6.615 | 180.015 | 0 | 180.015 | 0 | 0 | 96.3253 | 3.6747 | 0 | 96.3253 | 3.6747 | 0
244 | 20 | September | 3.8 | 4.6783 | 120.7 | 0 | 120.7 | 0 | 120.7 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
244 | 21 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
244 | 22 | September | 2.9 | 3.5703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
244 | 23 | September | 2.8 | 3.4472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
244 | 24 | September | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
245 | 1 | September | 2.4 | 2.9547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
245 | 2 | September | 2.3 | 2.8316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
245 | 3 | September | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
245 | 4 | September | 1.6 | 1.9698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
245 | 5 | September | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
245 | 6 | September | 0.5 | 0.61557 | 0 | 7.938 | 7.938 | 0 | 7.938 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
245 | 7 | September | 1 | 1.2311 | 0 | 52.92 | 52.92 | 0 | 52.92 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
245 | 8 | September | 1.6 | 1.9698 | 0 | 123.039 | 123.039 | 0 | 123.039 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
245 | 9 | September | 2.1 | 2.5854 | 0 | 194.481 | 194.481 | 0 | 194.481 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
245 | 10 | September | 2.8 | 3.4472 | 0 | 256.7675 | 256.7675 | 0 | 256.7675 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
245 | 11 | September | 3.4 | 4.1859 | 75.65 | 299.8419 | 375.4919 | 0 | 375.4919 | 0 | 0 | 20.1469 | 79.8531 | 0 | 20.1469 | 79.8531 | 0
245 | 12 | September | 4.1 | 5.0477 | 173.4 | 321.4015 | 494.8015 | 0 | 494.8015 | 0 | 0 | 35.0444 | 64.9556 | 0 | 35.0444 | 64.9556 | 0
245 | 13 | September | 3.4 | 4.1859 | 75.65 | 318.3843 | 394.0343 | 0 | 394.0343 | 0 | 0 | 19.1988 | 80.8012 | 0 | 19.1988 | 80.8012 | 0
245 | 14 | September | 2.8 | 3.4472 | 0 | 290.9971 | 290.9971 | 0 | 290.9971 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
245 | 15 | September | 2.1 | 2.5854 | 0 | 243.995 | 243.995 | 0 | 243.995 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
245 | 16 | September | 1.4 | 1.7236 | 0 | 218.1322 | 218.1322 | 0 | 218.1322 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
245 | 17 | September | 0.7 | 0.8618 | 0 | 152.0403 | 152.0403 | 0 | 152.0403 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
245 | 18 | September | 0 | 0 | 0 | 63.504 | 63.504 | 0 | 63.504 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
245 | 19 | September | 0.7 | 0.8618 | 0 | 5.292 | 5.292 | 0 | 5.292 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
245 | 20 | September | 1.4 | 1.7236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
245 | 21 | September | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
245 | 22 | September | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
245 | 23 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
245 | 24 | September | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
246 | 1 | September | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
246 | 2 | September | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
246 | 3 | September | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
246 | 4 | September | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
246 | 5 | September | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
246 | 6 | September | 2.6 | 3.201 | 0 | 19.845 | 19.845 | 0 | 19.845 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
246 | 7 | September | 3.6 | 4.4321 | 75.65 | 174.7314 | 250.3814 | 0 | 250.3814 | 0 | 0 | 30.2139 | 69.7861 | 0 | 30.2139 | 69.7861 | 0
246 | 8 | September | 5.7 | 7.0175 | 504.9 | 490.426 | 995.326 | 0 | 995.326 | 0 | 0 | 50.7271 | 49.2729 | 0 | 50.7271 | 49.2729 | 0
246 | 9 | September | 5.7 | 7.0175 | 504.9 | 834.1906 | 1339.0906 | 0 | 1339.0906 | 0 | 0 | 37.7047 | 62.2953 | 0 | 37.7047 | 62.2953 | 0
246 | 10 | September | 4.1 | 5.0477 | 173.4 | 950.9167 | 1124.3167 | 0 | 1124.3167 | 0 | 0 | 15.4227 | 84.5773 | 0 | 15.4227 | 84.5773 | 0
246 | 11 | September | 4.6 | 5.6633 | 237.15 | 1129.9529 | 1367.1029 | 0 | 1367.1029 | 0 | 0 | 17.3469 | 82.6531 | 0 | 17.3469 | 82.6531 | 0
246 | 12 | September | 4.1 | 5.0477 | 173.4 | 783.0994 | 956.4994 | 0 | 956.4994 | 0 | 0 | 18.1286 | 81.8714 | 0 | 18.1286 | 81.8714 | 0
246 | 13 | September | 4.1 | 5.0477 | 173.4 | 545.8763 | 719.2763 | 0 | 719.2763 | 0 | 0 | 24.1076 | 75.8924 | 0 | 24.1076 | 75.8924 | 0
246 | 14 | September | 4.1 | 5.0477 | 173.4 | 683.0903 | 856.4903 | 0 | 856.4903 | 0 | 0 | 20.2454 | 79.7546 | 0 | 20.2454 | 79.7546 | 0
246 | 15 | September | 3.6 | 4.4321 | 75.65 | 771.4271 | 847.0771 | 0 | 847.0771 | 0 | 0 | 8.9307 | 91.0693 | 0 | 8.9307 | 91.0693 | 0
246 | 16 | September | 2.1 | 2.5854 | 0 | 296.9085 | 296.9085 | 0 | 296.9085 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
246 | 17 | September | 2.1 | 2.5854 | 0 | 268.7903 | 268.7903 | 0 | 268.7903 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
246 | 18 | September | 1 | 1.2311 | 0 | 86.0562 | 86.0562 | 0 | 86.0562 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
246 | 19 | September | 0 | 0 | 0 | 10.584 | 10.584 | 0 | 10.584 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
246 | 20 | September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
246 | 21 | September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
246 | 22 | September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
246 | 23 | September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
246 | 24 | September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247 | 1 | September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247 | 2 | September | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247 | 3 | September | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247 | 4 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247 | 5 | September | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247 | 6 | September | 3.1 | 3.8165 | 0 | 18.522 | 18.522 | 0 | 18.522 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
247 | 7 | September | 3.1 | 3.8165 | 0 | 184.3834 | 184.3834 | 0 | 184.3834 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
247 | 8 | September | 4.6 | 5.6633 | 237.15 | 480.567 | 717.717 | 0 | 717.717 | 0 | 0 | 33.0423 | 66.9577 | 0 | 33.0423 | 66.9577 | 0
247 | 9 | September | 4.6 | 5.6633 | 237.15 | 475.8747 | 713.0247 | 0 | 713.0247 | 0 | 0 | 33.2597 | 66.7403 | 0 | 33.2597 | 66.7403 | 0
247 | 10 | September | 6.7 | 8.2487 | 761.6 | 441.4526 | 1203.0526 | 0 | 1203.0526 | 0 | 0 | 63.3056 | 36.6944 | 0 | 63.3056 | 36.6944 | 0
247 | 11 | September | 7.2 | 8.8642 | 908.65 | 732.3096 | 1640.9596 | 0 | 1640.9596 | 0 | 0 | 55.3731 | 44.6269 | 0 | 55.3731 | 44.6269 | 0
247 | 12 | September | 8.2 | 10.0954 | 1359.15 | 1208.0143 | 2567.1643 | 1 | 2000 | 567.1643 | 28.3582 | 52.9436 | 32.0425 | 46.9501 | 39.5993 | 47.0564 | 41.7293
247 | 13 | September | 8.7 | 10.711 | 1490.05 | 1279.8634 | 2769.9134 | 1 | 2000 | 769.9134 | 38.4957 | 53.7941 | 25.4975 | 60.1559 | 36.0068 | 46.2059 | 51.6703
247 | 14 | September | 8.7 | 10.711 | 1490.05 | 699.8337 | 2189.8837 | 1 | 2000 | 189.8837 | 9.4942 | 68.0424 | 25.4975 | 27.1327 | 65.0083 | 31.9576 | 12.7434
247 | 15 | September | 7.7 | 9.4798 | 1059.95 | 834.6125 | 1894.5625 | 0 | 1894.5625 | 0 | 0 | 55.947 | 44.053 | 0 | 55.947 | 44.053 | 0
247 | 16 | September | 6.2 | 7.6331 | 625.6 | 582.5879 | 1208.1879 | 0 | 1208.1879 | 0 | 0 | 51.78 | 48.22 | 0 | 51.78 | 48.22 | 0
247 | 17 | September | 5.7 | 7.0175 | 504.9 | 282.698 | 787.598 | 0 | 787.598 | 0 | 0 | 64.1063 | 35.8937 | 0 | 64.1063 | 35.8937 | 0
247 | 18 | September | 4.1 | 5.0477 | 173.4 | 83.4249 | 256.8249 | 0 | 256.8249 | 0 | 0 | 67.5168 | 32.4832 | 0 | 67.5168 | 32.4832 | 0
247 | 19 | September | 0.5 | 0.61557 | 0 | 9.261 | 9.261 | 0 | 9.261 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
247 | 20 | September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247 | 21 | September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247 | 22 | September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247 | 23 | September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247 | 24 | September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248 | 1 | September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248 | 2 | September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248 | 3 | September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248 | 4 | September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248 | 5 | September | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248 | 6 | September | 2.6 | 3.201 | 0 | 10.584 | 10.584 | 0 | 10.584 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
248 | 7 | September | 2.1 | 2.5854 | 0 | 78.057 | 78.057 | 0 | 78.057 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
248 | 8 | September | 1.5 | 1.8467 | 0 | 195.5182 | 195.5182 | 0 | 195.5182 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
248 | 9 | September | 2.6 | 3.201 | 0 | 653.9941 | 653.9941 | 0 | 653.9941 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
248 | 10 | September | 6.2 | 7.6331 | 625.6 | 435.8681 | 1061.4681 | 0 | 1061.4681 | 0 | 0 | 58.9372 | 41.0628 | 0 | 58.9372 | 41.0628 | 0
248 | 11 | September | 4.1 | 5.0477 | 173.4 | 907.0352 | 1080.4352 | 0 | 1080.4352 | 0 | 0 | 16.0491 | 83.9509 | 0 | 16.0491 | 83.9509 | 0
248 | 12 | September | 4.1 | 5.0477 | 173.4 | 993.8772 | 1167.2772 | 0 | 1167.2772 | 0 | 0 | 14.8551 | 85.1449 | 0 | 14.8551 | 85.1449 | 0
248 | 13 | September | 5.7 | 7.0175 | 504.9 | 1184.0188 | 1688.9188 | 0 | 1688.9188 | 0 | 0 | 29.8949 | 70.1051 | 0 | 29.8949 | 70.1051 | 0
248 | 14 | September | 4.6 | 5.6633 | 237.15 | 1078.3472 | 1315.4972 | 0 | 1315.4972 | 0 | 0 | 18.0274 | 81.9726 | 0 | 18.0274 | 81.9726 | 0
248 | 15 | September | 3.6 | 4.4321 | 75.65 | 396.4169 | 472.0669 | 0 | 472.0669 | 0 | 0 | 16.0253 | 83.9747 | 0 | 16.0253 | 83.9747 | 0
248 | 16 | September | 4.6 | 5.6633 | 237.15 | 278.3428 | 515.4928 | 0 | 515.4928 | 0 | 0 | 46.0045 | 53.9955 | 0 | 46.0045 | 53.9955 | 0
248 | 17 | September | 3.1 | 3.8165 | 0 | 159.0635 | 159.0635 | 0 | 159.0635 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
248 | 18 | September | 1.5 | 1.8467 | 0 | 52.92 | 52.92 | 0 | 52.92 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
248 | 19 | September | 0 | 0 | 0 | 6.615 | 6.615 | 0 | 6.615 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
248 | 20 | September | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248 | 21 | September | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
248 | 22 | September | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
248 | 23 | September | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248 | 24 | September | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
249 | 1 | September | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
249 | 2 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
249 | 3 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
249 | 4 | September | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
249 | 5 | September | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
249 | 6 | September | 3.1 | 3.8165 | 0 | 9.261 | 9.261 | 0 | 9.261 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
249 | 7 | September | 3.1 | 3.8165 | 0 | 75.411 | 75.411 | 0 | 75.411 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
249 | 8 | September | 4.1 | 5.0477 | 173.4 | 188.4374 | 361.8374 | 0 | 361.8374 | 0 | 0 | 47.9221 | 52.0779 | 0 | 47.9221 | 52.0779 | 0
249 | 9 | September | 3.6 | 4.4321 | 75.65 | 187.866 | 263.516 | 0 | 263.516 | 0 | 0 | 28.7079 | 71.2921 | 0 | 28.7079 | 71.2921 | 0
249 | 10 | September | 3.6 | 4.4321 | 75.65 | 250.2091 | 325.8591 | 0 | 325.8591 | 0 | 0 | 23.2156 | 76.7844 | 0 | 23.2156 | 76.7844 | 0
249 | 11 | September | 3.1 | 3.8165 | 0 | 295.2946 | 295.2946 | 0 | 295.2946 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
249 | 12 | September | 2.3 | 2.8316 | 0 | 419.4921 | 419.4921 | 0 | 419.4921 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
249 | 13 | September | 1.5 | 1.8467 | 0 | 531.3627 | 531.3627 | 0 | 531.3627 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
249 | 14 | September | 0 | 0 | 0 | 478.14 | 478.14 | 0 | 478.14 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
249 | 15 | September | 1.5 | 1.8467 | 0 | 531.6261 | 531.6261 | 0 | 531.6261 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
249 | 16 | September | 2.6 | 3.201 | 0 | 273.4345 | 273.4345 | 0 | 273.4345 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
249 | 17 | September | 5.1 | 6.2788 | 312.8 | 197.6098 | 510.4098 | 0 | 510.4098 | 0 | 0 | 61.2841 | 38.7159 | 0 | 61.2841 | 38.7159 | 0
249 | 18 | September | 4.6 | 5.6633 | 237.15 | 50.274 | 287.424 | 0 | 287.424 | 0 | 0 | 82.5088 | 17.4912 | 0 | 82.5088 | 17.4912 | 0
249 | 19 | September | 3.6 | 4.4321 | 75.65 | 5.292 | 80.942 | 0 | 80.942 | 0 | 0 | 93.462 | 6.538 | 0 | 93.462 | 6.538 | 0
249 | 20 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
249 | 21 | September | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
249 | 22 | September | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
249 | 23 | September | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
249 | 24 | September | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
250 | 1 | September | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
250 | 2 | September | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
250 | 3 | September | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
250 | 4 | September | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
250 | 5 | September | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
250 | 6 | September | 12.9 | 15.8818 | 1700 | 5.292 | 1705.292 | 0 | 1705.292 | 0 | 0 | 99.6897 | 0.31033 | 0 | 99.6897 | 0.31033 | 0
250 | 7 | September | 8.7 | 10.711 | 1490.05 | 44.982 | 1535.032 | 0 | 1535.032 | 0 | 0 | 97.0696 | 2.9304 | 0 | 97.0696 | 2.9304 | 0
250 | 8 | September | 9.3 | 11.4496 | 1598.85 | 191.9151 | 1790.7651 | 0 | 1790.7651 | 0 | 0 | 89.2831 | 10.7169 | 0 | 89.2831 | 10.7169 | 0
250 | 9 | September | 7.7 | 9.4798 | 1059.95 | 308.8426 | 1368.7926 | 0 | 1368.7926 | 0 | 0 | 77.4369 | 22.5631 | 0 | 77.4369 | 22.5631 | 0
250 | 10 | September | 4.1 | 5.0477 | 173.4 | 244.8295 | 418.2295 | 0 | 418.2295 | 0 | 0 | 41.4605 | 58.5395 | 0 | 41.4605 | 58.5395 | 0
250 | 11 | September | 5.1 | 6.2788 | 312.8 | 289.195 | 601.995 | 0 | 601.995 | 0 | 0 | 51.9606 | 48.0394 | 0 | 51.9606 | 48.0394 | 0
250 | 12 | September | 8.7 | 10.711 | 1490.05 | 741.7501 | 2231.8001 | 1 | 2000 | 231.8001 | 11.59 | 66.7645 | 25.4975 | 31.2504 | 62.9125 | 33.2355 | 15.5565
250 | 13 | September | 9.8 | 12.0652 | 1683.85 | 524.1954 | 2208.0454 | 1 | 2000 | 208.0454 | 10.4023 | 76.2598 | 15.8075 | 39.6885 | 73.7902 | 23.7402 | 12.3553
250 | 14 | September | 8.2 | 10.0954 | 1359.15 | 472.5627 | 1831.7127 | 0 | 1831.7127 | 0 | 0 | 74.201 | 25.799 | 0 | 74.201 | 25.799 | 0
250 | 15 | September | 9.3 | 11.4496 | 1598.85 | 379.3738 | 1978.2238 | 0 | 1978.2238 | 0 | 0 | 80.8225 | 19.1775 | 0 | 80.8225 | 19.1775 | 0
250 | 16 | September | 9.3 | 11.4496 | 1598.85 | 267.945 | 1866.795 | 0 | 1866.795 | 0 | 0 | 85.6468 | 14.3532 | 0 | 85.6468 | 14.3532 | 0
250 | 17 | September | 7.7 | 9.4798 | 1059.95 | 149.6693 | 1209.6193 | 0 | 1209.6193 | 0 | 0 | 87.6267 | 12.3733 | 0 | 87.6267 | 12.3733 | 0
250 | 18 | September | 8.7 | 10.711 | 1490.05 | 46.305 | 1536.355 | 0 | 1536.355 | 0 | 0 | 96.986 | 3.014 | 0 | 96.986 | 3.014 | 0
250 | 19 | September | 7.7 | 9.4798 | 1059.95 | 2.646 | 1062.596 | 0 | 1062.596 | 0 | 0 | 99.751 | 0.24901 | 0 | 99.751 | 0.24901 | 0
250 | 20 | September | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
250 | 21 | September | 6.4 | 7.8793 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
250 | 22 | September | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
250 | 23 | September | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
250 | 24 | September | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
251 | 1 | September | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
251 | 2 | September | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
251 | 3 | September | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
251 | 4 | September | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
251 | 5 | September | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
251 | 6 | September | 3.6 | 4.4321 | 75.65 | 5.292 | 80.942 | 0 | 80.942 | 0 | 0 | 93.462 | 6.538 | 0 | 93.462 | 6.538 | 0
251 | 7 | September | 3.6 | 4.4321 | 75.65 | 43.659 | 119.309 | 0 | 119.309 | 0 | 0 | 63.4068 | 36.5932 | 0 | 63.4068 | 36.5932 | 0
251 | 8 | September | 3.1 | 3.8165 | 0 | 112.455 | 112.455 | 0 | 112.455 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
251 | 9 | September | 3.1 | 3.8165 | 0 | 182.574 | 182.574 | 0 | 182.574 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
251 | 10 | September | 3.1 | 3.8165 | 0 | 243.4997 | 243.4997 | 0 | 243.4997 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
251 | 11 | September | 4.1 | 5.0477 | 173.4 | 286.5353 | 459.9353 | 0 | 459.9353 | 0 | 0 | 37.701 | 62.299 | 0 | 37.701 | 62.299 | 0
251 | 12 | September | 4.6 | 5.6633 | 237.15 | 411.4165 | 648.5665 | 0 | 648.5665 | 0 | 0 | 36.5653 | 63.4347 | 0 | 36.5653 | 63.4347 | 0
251 | 13 | September | 5.1 | 6.2788 | 312.8 | 518.4819 | 831.2819 | 0 | 831.2819 | 0 | 0 | 37.6286 | 62.3714 | 0 | 37.6286 | 62.3714 | 0
251 | 14 | September | 4.6 | 5.6633 | 237.15 | 466.9887 | 704.1387 | 0 | 704.1387 | 0 | 0 | 33.6794 | 66.3206 | 0 | 33.6794 | 66.3206 | 0
251 | 15 | September | 5.7 | 7.0175 | 504.9 | 372.8137 | 877.7137 | 0 | 877.7137 | 0 | 0 | 57.5245 | 42.4755 | 0 | 57.5245 | 42.4755 | 0
251 | 16 | September | 4.1 | 5.0477 | 173.4 | 263.0879 | 436.4879 | 0 | 436.4879 | 0 | 0 | 39.7262 | 60.2738 | 0 | 39.7262 | 60.2738 | 0
251 | 17 | September | 3.6 | 4.4321 | 75.65 | 145.2626 | 220.9126 | 0 | 220.9126 | 0 | 0 | 34.2443 | 65.7557 | 0 | 34.2443 | 65.7557 | 0
251 | 18 | September | 6.7 | 8.2487 | 761.6 | 43.659 | 805.259 | 0 | 805.259 | 0 | 0 | 94.5783 | 5.4217 | 0 | 94.5783 | 5.4217 | 0
251 | 19 | September | 6.7 | 8.2487 | 761.6 | 2.646 | 764.246 | 0 | 764.246 | 0 | 0 | 99.6538 | 0.34622 | 0 | 99.6538 | 0.34622 | 0
251 | 20 | September | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
251 | 21 | September | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
251 | 22 | September | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
251 | 23 | September | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
251 | 24 | September | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
252 | 1 | September | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
252 | 2 | September | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
252 | 3 | September | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
252 | 4 | September | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
252 | 5 | September | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
252 | 6 | September | 8.2 | 10.0954 | 1359.15 | 5.292 | 1364.442 | 0 | 1364.442 | 0 | 0 | 99.6121 | 0.38785 | 0 | 99.6121 | 0.38785 | 0
252 | 7 | September | 9.3 | 11.4496 | 1598.85 | 67.473 | 1666.323 | 0 | 1666.323 | 0 | 0 | 95.9508 | 4.0492 | 0 | 95.9508 | 4.0492 | 0
252 | 8 | September | 8.2 | 10.0954 | 1359.15 | 182.1745 | 1541.3245 | 0 | 1541.3245 | 0 | 0 | 88.1807 | 11.8193 | 0 | 88.1807 | 11.8193 | 0
252 | 9 | September | 8.2 | 10.0954 | 1359.15 | 624.1364 | 1983.2864 | 0 | 1983.2864 | 0 | 0 | 68.5302 | 31.4698 | 0 | 68.5302 | 31.4698 | 0
252 | 10 | September | 9.8 | 12.0652 | 1683.85 | 928.7143 | 2612.5643 | 1 | 2000 | 612.5643 | 30.6282 | 64.452 | 15.8075 | 65.9583 | 53.5643 | 35.548 | 36.3788
252 | 11 | September | 7.2 | 8.8642 | 908.65 | 1177.2145 | 2085.8645 | 1 | 2000 | 85.8645 | 4.2932 | 43.5623 | 54.5675 | 7.2939 | 41.1393 | 56.4377 | 9.4497
252 | 12 | September | 9.8 | 12.0652 | 1683.85 | 1125.4939 | 2809.3439 | 1 | 2000 | 809.3439 | 40.4672 | 59.9375 | 15.8075 | 71.9101 | 43.7253 | 40.0625 | 48.0651
252 | 13 | September | 8.2 | 10.0954 | 1359.15 | 729.9854 | 2089.1354 | 1 | 2000 | 89.1354 | 4.4568 | 65.058 | 32.0425 | 12.2106 | 63.5007 | 34.942 | 6.5582
252 | 14 | September | 6.2 | 7.6331 | 625.6 | 808.8027 | 1434.4027 | 0 | 1434.4027 | 0 | 0 | 43.614 | 56.386 | 0 | 43.614 | 56.386 | 0
252 | 15 | September | 5.7 | 7.0175 | 504.9 | 795.0866 | 1299.9866 | 0 | 1299.9866 | 0 | 0 | 38.8389 | 61.1611 | 0 | 38.8389 | 61.1611 | 0
252 | 16 | September | 4.6 | 5.6633 | 237.15 | 481.9156 | 719.0656 | 0 | 719.0656 | 0 | 0 | 32.9803 | 67.0197 | 0 | 32.9803 | 67.0197 | 0
252 | 17 | September | 5.1 | 6.2788 | 312.8 | 240.7653 | 553.5653 | 0 | 553.5653 | 0 | 0 | 56.5064 | 43.4936 | 0 | 56.5064 | 43.4936 | 0
252 | 18 | September | 3.1 | 3.8165 | 0 | 52.92 | 52.92 | 0 | 52.92 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
252 | 19 | September | 2.6 | 3.201 | 0 | 3.969 | 3.969 | 0 | 3.969 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
252 | 20 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
252 | 21 | September | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
252 | 22 | September | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
252 | 23 | September | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
252 | 24 | September | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
253 | 1 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
253 | 2 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
253 | 3 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
253 | 4 | September | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
253 | 5 | September | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
253 | 6 | September | 2.6 | 3.201 | 0 | 11.907 | 11.907 | 0 | 11.907 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
253 | 7 | September | 2.6 | 3.201 | 0 | 149.4464 | 149.4464 | 0 | 149.4464 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
253 | 8 | September | 2.1 | 2.5854 | 0 | 457.7268 | 457.7268 | 0 | 457.7268 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
253 | 9 | September | 3.1 | 3.8165 | 0 | 815.1971 | 815.1971 | 0 | 815.1971 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
253 | 10 | September | 3.6 | 4.4321 | 75.65 | 1100.2268 | 1175.8768 | 0 | 1175.8768 | 0 | 0 | 6.4335 | 93.5665 | 0 | 6.4335 | 93.5665 | 0
253 | 11 | September | 3.1 | 3.8165 | 0 | 1257.9843 | 1257.9843 | 0 | 1257.9843 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
253 | 12 | September | 1.5 | 1.8467 | 0 | 1120.7453 | 1120.7453 | 0 | 1120.7453 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
253 | 13 | September | 5.7 | 7.0175 | 504.9 | 1186.8675 | 1691.7675 | 0 | 1691.7675 | 0 | 0 | 29.8445 | 70.1555 | 0 | 29.8445 | 70.1555 | 0
253 | 14 | September | 7.2 | 8.8642 | 908.65 | 636.5138 | 1545.1638 | 0 | 1545.1638 | 0 | 0 | 58.8061 | 41.1939 | 0 | 58.8061 | 41.1939 | 0
253 | 15 | September | 6.7 | 8.2487 | 761.6 | 373.5375 | 1135.1375 | 0 | 1135.1375 | 0 | 0 | 67.0932 | 32.9068 | 0 | 67.0932 | 32.9068 | 0
253 | 16 | September | 6.2 | 7.6331 | 625.6 | 156.114 | 781.714 | 0 | 781.714 | 0 | 0 | 80.0293 | 19.9707 | 0 | 80.0293 | 19.9707 | 0
253 | 17 | September | 4.6 | 5.6633 | 237.15 | 85.995 | 323.145 | 0 | 323.145 | 0 | 0 | 73.3881 | 26.6119 | 0 | 73.3881 | 26.6119 | 0
253 | 18 | September | 4.1 | 5.0477 | 173.4 | 23.814 | 197.214 | 0 | 197.214 | 0 | 0 | 87.9248 | 12.0752 | 0 | 87.9248 | 12.0752 | 0
253 | 19 | September | 4.6 | 5.6633 | 237.15 | 1.323 | 238.473 | 0 | 238.473 | 0 | 0 | 99.4452 | 0.55478 | 0 | 99.4452 | 0.55478 | 0
253 | 20 | September | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
253 | 21 | September | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
253 | 22 | September | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
253 | 23 | September | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
253 | 24 | September | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
254 | 1 | September | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
254 | 2 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
254 | 3 | September | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
254 | 4 | September | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
254 | 5 | September | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
254 | 6 | September | 3.1 | 3.8165 | 0 | 6.615 | 6.615 | 0 | 6.615 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
254 | 7 | September | 4.1 | 5.0477 | 173.4 | 63.504 | 236.904 | 0 | 236.904 | 0 | 0 | 73.1942 | 26.8058 | 0 | 73.1942 | 26.8058 | 0
254 | 8 | September | 2.6 | 3.201 | 0 | 105.84 | 105.84 | 0 | 105.84 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
254 | 9 | September | 5.1 | 6.2788 | 312.8 | 440.9298 | 753.7298 | 0 | 753.7298 | 0 | 0 | 41.5003 | 58.4997 | 0 | 41.5003 | 58.4997 | 0
254 | 10 | September | 6.7 | 8.2487 | 761.6 | 236.8632 | 998.4632 | 0 | 998.4632 | 0 | 0 | 76.2772 | 23.7228 | 0 | 76.2772 | 23.7228 | 0
254 | 11 | September | 6.7 | 8.2487 | 761.6 | 279.8769 | 1041.4769 | 0 | 1041.4769 | 0 | 0 | 73.1269 | 26.8731 | 0 | 73.1269 | 26.8731 | 0
254 | 12 | September | 6.2 | 7.6331 | 625.6 | 298.5591 | 924.1591 | 0 | 924.1591 | 0 | 0 | 67.694 | 32.306 | 0 | 67.694 | 32.306 | 0
254 | 13 | September | 8.2 | 10.0954 | 1359.15 | 295.5757 | 1654.7257 | 0 | 1654.7257 | 0 | 0 | 82.1375 | 17.8625 | 0 | 82.1375 | 17.8625 | 0
254 | 14 | September | 6.7 | 8.2487 | 761.6 | 267.0339 | 1028.6339 | 0 | 1028.6339 | 0 | 0 | 74.0399 | 25.9601 | 0 | 74.0399 | 25.9601 | 0
254 | 15 | September | 6.2 | 7.6331 | 625.6 | 369.2116 | 994.8116 | 0 | 994.8116 | 0 | 0 | 62.8863 | 37.1137 | 0 | 62.8863 | 37.1137 | 0
254 | 16 | September | 5.1 | 6.2788 | 312.8 | 250.7076 | 563.5076 | 0 | 563.5076 | 0 | 0 | 55.5095 | 44.4905 | 0 | 55.5095 | 44.4905 | 0
254 | 17 | September | 4.1 | 5.0477 | 173.4 | 132.4657 | 305.8657 | 0 | 305.8657 | 0 | 0 | 56.6915 | 43.3085 | 0 | 56.6915 | 43.3085 | 0
254 | 18 | September | 2.6 | 3.201 | 0 | 54.243 | 54.243 | 0 | 54.243 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
254 | 19 | September | 2.6 | 3.201 | 0 | 2.646 | 2.646 | 0 | 2.646 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
254 | 20 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
254 | 21 | September | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
254 | 22 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
254 | 23 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
254 | 24 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
255 | 1 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
255 | 2 | September | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
255 | 3 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
255 | 4 | September | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
255 | 5 | September | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
255 | 6 | September | 3.1 | 3.8165 | 0 | 10.584 | 10.584 | 0 | 10.584 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
255 | 7 | September | 2.6 | 3.201 | 0 | 163.9996 | 163.9996 | 0 | 163.9996 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
255 | 8 | September | 1.5 | 1.8467 | 0 | 291.5872 | 291.5872 | 0 | 291.5872 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
255 | 9 | September | 3.6 | 4.4321 | 75.65 | 718.6301 | 794.2801 | 0 | 794.2801 | 0 | 0 | 9.5243 | 90.4757 | 0 | 9.5243 | 90.4757 | 0
255 | 10 | September | 5.7 | 7.0175 | 504.9 | 593.8558 | 1098.7558 | 0 | 1098.7558 | 0 | 0 | 45.952 | 54.048 | 0 | 45.952 | 54.048 | 0
255 | 11 | September | 6.2 | 7.6331 | 625.6 | 684.8846 | 1310.4846 | 0 | 1310.4846 | 0 | 0 | 47.7381 | 52.2619 | 0 | 47.7381 | 52.2619 | 0
255 | 12 | September | 6.2 | 7.6331 | 625.6 | 518.8932 | 1144.4932 | 0 | 1144.4932 | 0 | 0 | 54.6617 | 45.3383 | 0 | 54.6617 | 45.3383 | 0
255 | 13 | September | 6.4 | 7.8793 | 625.6 | 888.786 | 1514.386 | 0 | 1514.386 | 0 | 0 | 41.3105 | 58.6895 | 0 | 41.3105 | 58.6895 | 0
255 | 14 | September | 6.5 | 8.0024 | 761.6 | 993.965 | 1755.565 | 0 | 1755.565 | 0 | 0 | 43.382 | 56.618 | 0 | 43.382 | 56.618 | 0
255 | 15 | September | 6.7 | 8.2487 | 761.6 | 830.2126 | 1591.8126 | 0 | 1591.8126 | 0 | 0 | 47.8448 | 52.1552 | 0 | 47.8448 | 52.1552 | 0
255 | 16 | September | 5.1 | 6.2788 | 312.8 | 516.2211 | 829.0211 | 0 | 829.0211 | 0 | 0 | 37.7312 | 62.2688 | 0 | 37.7312 | 62.2688 | 0
255 | 17 | September | 5.1 | 6.2788 | 312.8 | 227.4477 | 540.2477 | 0 | 540.2477 | 0 | 0 | 57.8994 | 42.1006 | 0 | 57.8994 | 42.1006 | 0
255 | 18 | September | 2.6 | 3.201 | 0 | 50.274 | 50.274 | 0 | 50.274 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
255 | 19 | September | 3.1 | 3.8165 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
255 | 20 | September | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
255 | 21 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
255 | 22 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
255 | 23 | September | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
255 | 24 | September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256 | 1 | September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256 | 2 | September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256 | 3 | September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256 | 4 | September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256 | 5 | September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256 | 6 | September | 0 | 0 | 0 | 9.261 | 9.261 | 0 | 9.261 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
256 | 7 | September | 1.5 | 1.8467 | 0 | 81.1644 | 81.1644 | 0 | 81.1644 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
256 | 8 | September | 0 | 0 | 0 | 254.1802 | 254.1802 | 0 | 254.1802 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
256 | 9 | September | 0 | 0 | 0 | 432.4538 | 432.4538 | 0 | 432.4538 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
256 | 10 | September | 1.5 | 1.8467 | 0 | 544.9374 | 544.9374 | 0 | 544.9374 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
256 | 11 | September | 1 | 1.2311 | 0 | 681.7744 | 681.7744 | 0 | 681.7744 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
256 | 12 | September | 3.1 | 3.8165 | 0 | 723.002 | 723.002 | 0 | 723.002 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
256 | 13 | September | 3.6 | 4.4321 | 75.65 | 1045.2231 | 1120.8731 | 0 | 1120.8731 | 0 | 0 | 6.7492 | 93.2508 | 0 | 6.7492 | 93.2508 | 0
256 | 14 | September | 4.1 | 5.0477 | 173.4 | 1017.2571 | 1190.6571 | 0 | 1190.6571 | 0 | 0 | 14.5634 | 85.4366 | 0 | 14.5634 | 85.4366 | 0
256 | 15 | September | 4.1 | 5.0477 | 173.4 | 809.0183 | 982.4183 | 0 | 982.4183 | 0 | 0 | 17.6503 | 82.3497 | 0 | 17.6503 | 82.3497 | 0
256 | 16 | September | 5.1 | 6.2788 | 312.8 | 502.7931 | 815.5931 | 0 | 815.5931 | 0 | 0 | 38.3525 | 61.6475 | 0 | 38.3525 | 61.6475 | 0
256 | 17 | September | 3.1 | 3.8165 | 0 | 217.8398 | 217.8398 | 0 | 217.8398 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
256 | 18 | September | 3.1 | 3.8165 | 0 | 47.628 | 47.628 | 0 | 47.628 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
256 | 19 | September | 1.5 | 1.8467 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
256 | 20 | September | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256 | 21 | September | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256 | 22 | September | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256 | 23 | September | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256 | 24 | September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257 | 1 | September | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257 | 2 | September | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257 | 3 | September | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257 | 4 | September | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257 | 5 | September | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257 | 6 | September | 2.1 | 2.5854 | 0 | 7.938 | 7.938 | 0 | 7.938 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
257 | 7 | September | 1.5 | 1.8467 | 0 | 153.3154 | 153.3154 | 0 | 153.3154 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
257 | 8 | September | 0 | 0 | 0 | 443.3932 | 443.3932 | 0 | 443.3932 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
257 | 9 | September | 2.1 | 2.5854 | 0 | 774.4107 | 774.4107 | 0 | 774.4107 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
257 | 10 | September | 2.6 | 3.201 | 0 | 1006.2172 | 1006.2172 | 0 | 1006.2172 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
257 | 11 | September | 2.1 | 2.5854 | 0 | 1049.2217 | 1049.2217 | 0 | 1049.2217 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
257 | 12 | September | 3.6 | 4.4321 | 75.65 | 1195.4959 | 1271.1459 | 0 | 1271.1459 | 0 | 0 | 5.9513 | 94.0487 | 0 | 5.9513 | 94.0487 | 0
257 | 13 | September | 1 | 1.2311 | 0 | 1219.6762 | 1219.6762 | 0 | 1219.6762 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
257 | 14 | September | 0 | 0 | 0 | 917.017 | 917.017 | 0 | 917.017 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
257 | 15 | September | 4.1 | 5.0477 | 173.4 | 765.6449 | 939.0449 | 0 | 939.0449 | 0 | 0 | 18.4656 | 81.5344 | 0 | 18.4656 | 81.5344 | 0
257 | 16 | September | 3.6 | 4.4321 | 75.65 | 494.0898 | 569.7398 | 0 | 569.7398 | 0 | 0 | 13.278 | 86.722 | 0 | 13.278 | 86.722 | 0
257 | 17 | September | 3.1 | 3.8165 | 0 | 178.5203 | 178.5203 | 0 | 178.5203 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
257 | 18 | September | 2.6 | 3.201 | 0 | 26.46 | 26.46 | 0 | 26.46 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
257 | 19 | September | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257 | 20 | September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257 | 21 | September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257 | 22 | September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257 | 23 | September | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257 | 24 | September | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
258 | 1 | September | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
258 | 2 | September | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
258 | 3 | September | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
258 | 4 | September | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
258 | 5 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
258 | 6 | September | 3.6 | 4.4321 | 75.65 | 3.969 | 79.619 | 0 | 79.619 | 0 | 0 | 95.015 | 4.985 | 0 | 95.015 | 4.985 | 0
258 | 7 | September | 3.1 | 3.8165 | 0 | 54.243 | 54.243 | 0 | 54.243 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
258 | 8 | September | 4.1 | 5.0477 | 173.4 | 163.645 | 337.045 | 0 | 337.045 | 0 | 0 | 51.4471 | 48.5529 | 0 | 51.4471 | 48.5529 | 0
258 | 9 | September | 6.7 | 8.2487 | 761.6 | 168.021 | 929.621 | 0 | 929.621 | 0 | 0 | 81.9259 | 18.0741 | 0 | 81.9259 | 18.0741 | 0
258 | 10 | September | 3.1 | 3.8165 | 0 | 399.8652 | 399.8652 | 0 | 399.8652 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
258 | 11 | September | 5.7 | 7.0175 | 504.9 | 470.9759 | 975.8759 | 0 | 975.8759 | 0 | 0 | 51.7381 | 48.2619 | 0 | 51.7381 | 48.2619 | 0
258 | 12 | September | 6.7 | 8.2487 | 761.6 | 501.1559 | 1262.7559 | 0 | 1262.7559 | 0 | 0 | 60.3125 | 39.6875 | 0 | 60.3125 | 39.6875 | 0
258 | 13 | September | 7.7 | 9.4798 | 1059.95 | 489.4097 | 1549.3597 | 0 | 1549.3597 | 0 | 0 | 68.4121 | 31.5879 | 0 | 68.4121 | 31.5879 | 0
258 | 14 | September | 8.2 | 10.0954 | 1359.15 | 436.9126 | 1796.0626 | 0 | 1796.0626 | 0 | 0 | 75.6739 | 24.3261 | 0 | 75.6739 | 24.3261 | 0
258 | 15 | September | 5.7 | 7.0175 | 504.9 | 334.2235 | 839.1235 | 0 | 839.1235 | 0 | 0 | 60.1699 | 39.8301 | 0 | 60.1699 | 39.8301 | 0
258 | 16 | September | 2.1 | 2.5854 | 0 | 230.7983 | 230.7983 | 0 | 230.7983 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
258 | 17 | September | 2.1 | 2.5854 | 0 | 116.079 | 116.079 | 0 | 116.079 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
258 | 18 | September | 0 | 0 | 0 | 23.814 | 23.814 | 0 | 23.814 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
258 | 19 | September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
258 | 20 | September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
258 | 21 | September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
258 | 22 | September | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
258 | 23 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
258 | 24 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
259 | 1 | September | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
259 | 2 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
259 | 3 | September | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
259 | 4 | September | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
259 | 5 | September | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
259 | 6 | September | 3.1 | 3.8165 | 0 | 3.969 | 3.969 | 0 | 3.969 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
259 | 7 | September | 4.6 | 5.6633 | 237.15 | 86.7394 | 323.8894 | 0 | 323.8894 | 0 | 0 | 73.2194 | 26.7806 | 0 | 73.2194 | 26.7806 | 0
259 | 8 | September | 4.6 | 5.6633 | 237.15 | 409.3862 | 646.5362 | 0 | 646.5362 | 0 | 0 | 36.6801 | 63.3199 | 0 | 36.6801 | 63.3199 | 0
259 | 9 | September | 4.1 | 5.0477 | 173.4 | 774.1089 | 947.5089 | 0 | 947.5089 | 0 | 0 | 18.3006 | 81.6994 | 0 | 18.3006 | 81.6994 | 0
259 | 10 | September | 4.1 | 5.0477 | 173.4 | 1063.8351 | 1237.2351 | 0 | 1237.2351 | 0 | 0 | 14.0151 | 85.9849 | 0 | 14.0151 | 85.9849 | 0
259 | 11 | September | 5.1 | 6.2788 | 312.8 | 1155.9417 | 1468.7417 | 0 | 1468.7417 | 0 | 0 | 21.2971 | 78.7029 | 0 | 21.2971 | 78.7029 | 0
259 | 12 | September | 5.7 | 7.0175 | 504.9 | 1258.0967 | 1762.9967 | 0 | 1762.9967 | 0 | 0 | 28.6387 | 71.3613 | 0 | 28.6387 | 71.3613 | 0
259 | 13 | September | 5.1 | 6.2788 | 312.8 | 873.2436 | 1186.0436 | 0 | 1186.0436 | 0 | 0 | 26.3734 | 73.6266 | 0 | 26.3734 | 73.6266 | 0
259 | 14 | September | 4.1 | 5.0477 | 173.4 | 608.8807 | 782.2807 | 0 | 782.2807 | 0 | 0 | 22.166 | 77.834 | 0 | 22.166 | 77.834 | 0
259 | 15 | September | 4.1 | 5.0477 | 173.4 | 455.86 | 629.26 | 0 | 629.26 | 0 | 0 | 27.5562 | 72.4438 | 0 | 27.5562 | 72.4438 | 0
259 | 16 | September | 5.1 | 6.2788 | 312.8 | 300.5694 | 613.3694 | 0 | 613.3694 | 0 | 0 | 50.997 | 49.003 | 0 | 50.997 | 49.003 | 0
259 | 17 | September | 3.6 | 4.4321 | 75.65 | 112.0908 | 187.7408 | 0 | 187.7408 | 0 | 0 | 40.2949 | 59.7051 | 0 | 40.2949 | 59.7051 | 0
259 | 18 | September | 3.1 | 3.8165 | 0 | 21.168 | 21.168 | 0 | 21.168 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
259 | 19 | September | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
259 | 20 | September | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
259 | 21 | September | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
259 | 22 | September | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
259 | 23 | September | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
259 | 24 | September | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
260 | 1 | September | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
260 | 2 | September | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
260 | 3 | September | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
260 | 4 | September | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
260 | 5 | September | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
260 | 6 | September | 4.6 | 5.6633 | 237.15 | 3.969 | 241.119 | 0 | 241.119 | 0 | 0 | 98.3539 | 1.6461 | 0 | 98.3539 | 1.6461 | 0
260 | 7 | September | 4.6 | 5.6633 | 237.15 | 48.951 | 286.101 | 0 | 286.101 | 0 | 0 | 82.8903 | 17.1097 | 0 | 82.8903 | 17.1097 | 0
260 | 8 | September | 4.6 | 5.6633 | 237.15 | 155.5324 | 392.6824 | 0 | 392.6824 | 0 | 0 | 60.3923 | 39.6077 | 0 | 60.3923 | 39.6077 | 0
260 | 9 | September | 5.1 | 6.2788 | 312.8 | 276.859 | 589.659 | 0 | 589.659 | 0 | 0 | 53.0476 | 46.9524 | 0 | 53.0476 | 46.9524 | 0
260 | 10 | September | 5.1 | 6.2788 | 312.8 | 378.3477 | 691.1477 | 0 | 691.1477 | 0 | 0 | 45.2581 | 54.7419 | 0 | 45.2581 | 54.7419 | 0
260 | 11 | September | 6.2 | 7.6331 | 625.6 | 463.8861 | 1089.4861 | 0 | 1089.4861 | 0 | 0 | 57.4216 | 42.5784 | 0 | 57.4216 | 42.5784 | 0
260 | 12 | September | 5.1 | 6.2788 | 312.8 | 493.9644 | 806.7644 | 0 | 806.7644 | 0 | 0 | 38.7722 | 61.2278 | 0 | 38.7722 | 61.2278 | 0
260 | 13 | September | 6.2 | 7.6331 | 625.6 | 682.382 | 1307.982 | 0 | 1307.982 | 0 | 0 | 47.8294 | 52.1706 | 0 | 47.8294 | 52.1706 | 0
260 | 14 | September | 6.7 | 8.2487 | 761.6 | 596.9307 | 1358.5307 | 0 | 1358.5307 | 0 | 0 | 56.0606 | 43.9394 | 0 | 56.0606 | 43.9394 | 0
260 | 15 | September | 6.2 | 7.6331 | 625.6 | 591.9258 | 1217.5258 | 0 | 1217.5258 | 0 | 0 | 51.3829 | 48.6171 | 0 | 51.3829 | 48.6171 | 0
260 | 16 | September | 7.2 | 8.8642 | 908.65 | 302.6991 | 1211.3491 | 0 | 1211.3491 | 0 | 0 | 75.0114 | 24.9886 | 0 | 75.0114 | 24.9886 | 0
260 | 17 | September | 6.2 | 7.6331 | 625.6 | 107.7893 | 733.3893 | 0 | 733.3893 | 0 | 0 | 85.3026 | 14.6974 | 0 | 85.3026 | 14.6974 | 0
260 | 18 | September | 5.1 | 6.2788 | 312.8 | 25.137 | 337.937 | 0 | 337.937 | 0 | 0 | 92.5616 | 7.4384 | 0 | 92.5616 | 7.4384 | 0
260 | 19 | September | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
260 | 20 | September | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
260 | 21 | September | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
260 | 22 | September | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
260 | 23 | September | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
260 | 24 | September | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
261 | 1 | September | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
261 | 2 | September | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
261 | 3 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
261 | 4 | September | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
261 | 5 | September | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
261 | 6 | September | 4.6 | 5.6633 | 237.15 | 5.292 | 242.442 | 0 | 242.442 | 0 | 0 | 97.8172 | 2.1828 | 0 | 97.8172 | 2.1828 | 0
261 | 7 | September | 4.6 | 5.6633 | 237.15 | 108.463 | 345.613 | 0 | 345.613 | 0 | 0 | 68.6172 | 31.3828 | 0 | 68.6172 | 31.3828 | 0
261 | 8 | September | 5.1 | 6.2788 | 312.8 | 406.1283 | 718.9283 | 0 | 718.9283 | 0 | 0 | 43.5092 | 56.4908 | 0 | 43.5092 | 56.4908 | 0
261 | 9 | September | 5.7 | 7.0175 | 504.9 | 754.1382 | 1259.0382 | 0 | 1259.0382 | 0 | 0 | 40.102 | 59.898 | 0 | 40.102 | 59.898 | 0
261 | 10 | September | 6.2 | 7.6331 | 625.6 | 1043.9758 | 1669.5758 | 0 | 1669.5758 | 0 | 0 | 37.4706 | 62.5294 | 0 | 37.4706 | 62.5294 | 0
261 | 11 | September | 6.7 | 8.2487 | 761.6 | 1206.0243 | 1967.6243 | 0 | 1967.6243 | 0 | 0 | 38.7066 | 61.2934 | 0 | 38.7066 | 61.2934 | 0
261 | 12 | September | 7.2 | 8.8642 | 908.65 | 1267.6461 | 2176.2961 | 1 | 2000 | 176.2961 | 8.8148 | 41.7521 | 54.5675 | 13.9074 | 36.6177 | 58.2479 | 19.402
261 | 13 | September | 7.7 | 9.4798 | 1059.95 | 1184.9004 | 2244.8504 | 1 | 2000 | 244.8504 | 12.2425 | 47.217 | 47.0025 | 20.6642 | 40.755 | 52.783 | 23.1002
261 | 14 | September | 8.2 | 10.0954 | 1359.15 | 587.12 | 1946.27 | 0 | 1946.27 | 0 | 0 | 69.8336 | 30.1664 | 0 | 69.8336 | 30.1664 | 0
261 | 15 | September | 7.2 | 8.8642 | 908.65 | 327.7485 | 1236.3985 | 0 | 1236.3985 | 0 | 0 | 73.4917 | 26.5083 | 0 | 73.4917 | 26.5083 | 0
261 | 16 | September | 6.7 | 8.2487 | 761.6 | 215.788 | 977.388 | 0 | 977.388 | 0 | 0 | 77.922 | 22.078 | 0 | 77.922 | 22.078 | 0
261 | 17 | September | 5.1 | 6.2788 | 312.8 | 64.827 | 377.627 | 0 | 377.627 | 0 | 0 | 82.8331 | 17.1669 | 0 | 82.8331 | 17.1669 | 0
261 | 18 | September | 5.7 | 7.0175 | 504.9 | 10.584 | 515.484 | 0 | 515.484 | 0 | 0 | 97.9468 | 2.0532 | 0 | 97.9468 | 2.0532 | 0
261 | 19 | September | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
261 | 20 | September | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
261 | 21 | September | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
261 | 22 | September | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
261 | 23 | September | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
261 | 24 | September | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
262 | 1 | September | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
262 | 2 | September | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
262 | 3 | September | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
262 | 4 | September | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
262 | 5 | September | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
262 | 6 | September | 6.7 | 8.2487 | 761.6 | 2.646 | 764.246 | 0 | 764.246 | 0 | 0 | 99.6538 | 0.34622 | 0 | 99.6538 | 0.34622 | 0
262 | 7 | September | 9.8 | 12.0652 | 1683.85 | 44.982 | 1728.832 | 0 | 1728.832 | 0 | 0 | 97.3981 | 2.6019 | 0 | 97.3981 | 2.6019 | 0
262 | 8 | September | 8.7 | 10.711 | 1490.05 | 91.287 | 1581.337 | 0 | 1581.337 | 0 | 0 | 94.2272 | 5.7728 | 0 | 94.2272 | 5.7728 | 0
262 | 9 | September | 8.2 | 10.0954 | 1359.15 | 274.726 | 1633.876 | 0 | 1633.876 | 0 | 0 | 83.1856 | 16.8144 | 0 | 83.1856 | 16.8144 | 0
262 | 10 | September | 9.8 | 12.0652 | 1683.85 | 371.4947 | 2055.3447 | 1 | 2000 | 55.3447 | 2.7672 | 81.9254 | 15.8075 | 14.8978 | 81.4253 | 18.0746 | 3.2868
262 | 11 | September | 9.8 | 12.0652 | 1683.85 | 259.781 | 1943.631 | 0 | 1943.631 | 0 | 0 | 86.6342 | 13.3658 | 0 | 86.6342 | 13.3658 | 0
262 | 12 | September | 8.7 | 10.711 | 1490.05 | 278.5572 | 1768.6072 | 0 | 1768.6072 | 0 | 0 | 84.2499 | 15.7501 | 0 | 84.2499 | 15.7501 | 0
262 | 13 | September | 8.2 | 10.0954 | 1359.15 | 472.1264 | 1831.2764 | 0 | 1831.2764 | 0 | 0 | 74.2187 | 25.7813 | 0 | 74.2187 | 25.7813 | 0
262 | 14 | September | 7.2 | 8.8642 | 908.65 | 409.6711 | 1318.3211 | 0 | 1318.3211 | 0 | 0 | 68.9248 | 31.0752 | 0 | 68.9248 | 31.0752 | 0
262 | 15 | September | 8.7 | 10.711 | 1490.05 | 458.5835 | 1948.6335 | 0 | 1948.6335 | 0 | 0 | 76.4664 | 23.5336 | 0 | 76.4664 | 23.5336 | 0
262 | 16 | September | 8.7 | 10.711 | 1490.05 | 349.9514 | 1840.0014 | 0 | 1840.0014 | 0 | 0 | 80.9809 | 19.0191 | 0 | 80.9809 | 19.0191 | 0
262 | 17 | September | 7.7 | 9.4798 | 1059.95 | 172.3167 | 1232.2667 | 0 | 1232.2667 | 0 | 0 | 86.0163 | 13.9837 | 0 | 86.0163 | 13.9837 | 0
262 | 18 | September | 9.3 | 11.4496 | 1598.85 | 29.106 | 1627.956 | 0 | 1627.956 | 0 | 0 | 98.2121 | 1.7879 | 0 | 98.2121 | 1.7879 | 0
262 | 19 | September | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
262 | 20 | September | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
262 | 21 | September | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
262 | 22 | September | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
262 | 23 | September | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
262 | 24 | September | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
263 | 1 | September | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
263 | 2 | September | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
263 | 3 | September | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
263 | 4 | September | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
263 | 5 | September | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
263 | 6 | September | 7.2 | 8.8642 | 908.65 | 3.969 | 912.619 | 0 | 912.619 | 0 | 0 | 99.5651 | 0.4349 | 0 | 99.5651 | 0.4349 | 0
263 | 7 | September | 7.7 | 9.4798 | 1059.95 | 83.1305 | 1143.0805 | 0 | 1143.0805 | 0 | 0 | 92.7275 | 7.2725 | 0 | 92.7275 | 7.2725 | 0
263 | 8 | September | 7.7 | 9.4798 | 1059.95 | 349.2487 | 1409.1987 | 0 | 1409.1987 | 0 | 0 | 75.2165 | 24.7835 | 0 | 75.2165 | 24.7835 | 0
263 | 9 | September | 8.2 | 10.0954 | 1359.15 | 409.8809 | 1769.0309 | 0 | 1769.0309 | 0 | 0 | 76.8302 | 23.1698 | 0 | 76.8302 | 23.1698 | 0
263 | 10 | September | 7.7 | 9.4798 | 1059.95 | 386.9929 | 1446.9429 | 0 | 1446.9429 | 0 | 0 | 73.2544 | 26.7456 | 0 | 73.2544 | 26.7456 | 0
263 | 11 | September | 7.7 | 9.4798 | 1059.95 | 464.8531 | 1524.8031 | 0 | 1524.8031 | 0 | 0 | 69.5139 | 30.4861 | 0 | 69.5139 | 30.4861 | 0
263 | 12 | September | 9.3 | 11.4496 | 1598.85 | 482.4749 | 2081.3249 | 1 | 2000 | 81.3249 | 4.0662 | 76.8189 | 20.0575 | 16.8558 | 75.8763 | 23.1811 | 5.0865
263 | 13 | September | 10.3 | 12.6808 | 1694.9 | 470.5985 | 2165.4985 | 1 | 2000 | 165.4985 | 8.2749 | 78.2684 | 15.255 | 35.1677 | 76.4701 | 21.7316 | 9.7645
263 | 14 | September | 10.3 | 12.6808 | 1694.9 | 243.0334 | 1937.9334 | 0 | 1937.9334 | 0 | 0 | 87.4591 | 12.5409 | 0 | 87.4591 | 12.5409 | 0
263 | 15 | September | 9.8 | 12.0652 | 1683.85 | 589.8322 | 2273.6822 | 1 | 2000 | 273.6822 | 13.6841 | 74.0583 | 15.8075 | 46.4 | 70.5084 | 25.9417 | 16.2534
263 | 16 | September | 8.7 | 10.711 | 1490.05 | 288.8589 | 1778.9089 | 0 | 1778.9089 | 0 | 0 | 83.762 | 16.238 | 0 | 83.762 | 16.238 | 0
263 | 17 | September | 6.7 | 8.2487 | 761.6 | 166.785 | 928.385 | 0 | 928.385 | 0 | 0 | 82.0349 | 17.9651 | 0 | 82.0349 | 17.9651 | 0
263 | 18 | September | 7.2 | 8.8642 | 908.65 | 22.491 | 931.141 | 0 | 931.141 | 0 | 0 | 97.5846 | 2.4154 | 0 | 97.5846 | 2.4154 | 0
263 | 19 | September | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
263 | 20 | September | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
263 | 21 | September | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
263 | 22 | September | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
263 | 23 | September | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
263 | 24 | September | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
264 | 1 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
264 | 2 | September | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
264 | 3 | September | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
264 | 4 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
264 | 5 | September | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
264 | 6 | September | 2.6 | 3.201 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
264 | 7 | September | 2.6 | 3.201 | 0 | 41.013 | 41.013 | 0 | 41.013 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
264 | 8 | September | 2.1 | 2.5854 | 0 | 145.1647 | 145.1647 | 0 | 145.1647 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
264 | 9 | September | 2.1 | 2.5854 | 0 | 254.1741 | 254.1741 | 0 | 254.1741 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
264 | 10 | September | 2.6 | 3.201 | 0 | 372.426 | 372.426 | 0 | 372.426 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
264 | 11 | September | 2.1 | 2.5854 | 0 | 460.5671 | 460.5671 | 0 | 460.5671 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
264 | 12 | September | 2.1 | 2.5854 | 0 | 489.5069 | 489.5069 | 0 | 489.5069 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
264 | 13 | September | 3.1 | 3.8165 | 0 | 666.6979 | 666.6979 | 0 | 666.6979 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
264 | 14 | September | 3.6 | 4.4321 | 75.65 | 549.8264 | 625.4764 | 0 | 625.4764 | 0 | 0 | 12.0948 | 87.9052 | 0 | 12.0948 | 87.9052 | 0
264 | 15 | September | 3.1 | 3.8165 | 0 | 318.9278 | 318.9278 | 0 | 318.9278 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
264 | 16 | September | 2.6 | 3.201 | 0 | 202.8186 | 202.8186 | 0 | 202.8186 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
264 | 17 | September | 2.1 | 2.5854 | 0 | 91.287 | 91.287 | 0 | 91.287 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
264 | 18 | September | 1.5 | 1.8467 | 0 | 14.553 | 14.553 | 0 | 14.553 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
264 | 19 | September | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
264 | 20 | September | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
264 | 21 | September | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
264 | 22 | September | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
264 | 23 | September | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
264 | 24 | September | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
265 | 1 | September | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
265 | 2 | September | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
265 | 3 | September | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
265 | 4 | September | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
265 | 5 | September | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
265 | 6 | September | 2.1 | 2.5854 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
265 | 7 | September | 2.6 | 3.201 | 0 | 38.367 | 38.367 | 0 | 38.367 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
265 | 8 | September | 3.6 | 4.4321 | 75.65 | 139.2678 | 214.9178 | 0 | 214.9178 | 0 | 0 | 35.1995 | 64.8005 | 0 | 35.1995 | 64.8005 | 0
265 | 9 | September | 4.1 | 5.0477 | 173.4 | 258.6489 | 432.0489 | 0 | 432.0489 | 0 | 0 | 40.1343 | 59.8657 | 0 | 40.1343 | 59.8657 | 0
265 | 10 | September | 3.6 | 4.4321 | 75.65 | 361.8554 | 437.5054 | 0 | 437.5054 | 0 | 0 | 17.2912 | 82.7088 | 0 | 17.2912 | 82.7088 | 0
265 | 11 | September | 3.6 | 4.4321 | 75.65 | 446.7308 | 522.3808 | 0 | 522.3808 | 0 | 0 | 14.4818 | 85.5182 | 0 | 14.4818 | 85.5182 | 0
265 | 12 | September | 4.6 | 5.6633 | 237.15 | 476.6854 | 713.8354 | 0 | 713.8354 | 0 | 0 | 33.2219 | 66.7781 | 0 | 33.2219 | 66.7781 | 0
265 | 13 | September | 4.6 | 5.6633 | 237.15 | 470.6972 | 707.8472 | 0 | 707.8472 | 0 | 0 | 33.503 | 66.497 | 0 | 33.503 | 66.497 | 0
265 | 14 | September | 3.6 | 4.4321 | 75.65 | 397.2122 | 472.8622 | 0 | 472.8622 | 0 | 0 | 15.9983 | 84.0017 | 0 | 15.9983 | 84.0017 | 0
265 | 15 | September | 5.7 | 7.0175 | 504.9 | 313.3487 | 818.2487 | 0 | 818.2487 | 0 | 0 | 61.705 | 38.295 | 0 | 61.705 | 38.295 | 0
265 | 16 | September | 3.6 | 4.4321 | 75.65 | 197.5069 | 273.1569 | 0 | 273.1569 | 0 | 0 | 27.6947 | 72.3053 | 0 | 27.6947 | 72.3053 | 0
265 | 17 | September | 1.5 | 1.8467 | 0 | 87.318 | 87.318 | 0 | 87.318 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
265 | 18 | September | 2.6 | 3.201 | 0 | 13.23 | 13.23 | 0 | 13.23 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
265 | 19 | September | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
265 | 20 | September | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
265 | 21 | September | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
265 | 22 | September | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
265 | 23 | September | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
265 | 24 | September | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
266 | 1 | September | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
266 | 2 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
266 | 3 | September | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
266 | 4 | September | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
266 | 5 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
266 | 6 | September | 3.6 | 4.4321 | 75.65 | 2.646 | 78.296 | 0 | 78.296 | 0 | 0 | 96.6205 | 3.3795 | 0 | 96.6205 | 3.3795 | 0
266 | 7 | September | 2.6 | 3.201 | 0 | 58.455 | 58.455 | 0 | 58.455 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
266 | 8 | September | 2.6 | 3.201 | 0 | 200.673 | 200.673 | 0 | 200.673 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
266 | 9 | September | 2.6 | 3.201 | 0 | 513.3523 | 513.3523 | 0 | 513.3523 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
266 | 10 | September | 3.6 | 4.4321 | 75.65 | 723.3677 | 799.0177 | 0 | 799.0177 | 0 | 0 | 9.4679 | 90.5321 | 0 | 9.4679 | 90.5321 | 0
266 | 11 | September | 3.6 | 4.4321 | 75.65 | 980.2388 | 1055.8888 | 0 | 1055.8888 | 0 | 0 | 7.1646 | 92.8354 | 0 | 7.1646 | 92.8354 | 0
266 | 12 | September | 3.1 | 3.8165 | 0 | 1078.1899 | 1078.1899 | 0 | 1078.1899 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
266 | 13 | September | 3.6 | 4.4321 | 75.65 | 1019.0213 | 1094.6713 | 0 | 1094.6713 | 0 | 0 | 6.9108 | 93.0892 | 0 | 6.9108 | 93.0892 | 0
266 | 14 | September | 1.5 | 1.8467 | 0 | 942.9445 | 942.9445 | 0 | 942.9445 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
266 | 15 | September | 2.1 | 2.5854 | 0 | 688.8731 | 688.8731 | 0 | 688.8731 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
266 | 16 | September | 4.1 | 5.0477 | 173.4 | 403.2761 | 576.6761 | 0 | 576.6761 | 0 | 0 | 30.0689 | 69.9311 | 0 | 30.0689 | 69.9311 | 0
266 | 17 | September | 3.6 | 4.4321 | 75.65 | 151.2081 | 226.8581 | 0 | 226.8581 | 0 | 0 | 33.3468 | 66.6532 | 0 | 33.3468 | 66.6532 | 0
266 | 18 | September | 3.1 | 3.8165 | 0 | 21.168 | 21.168 | 0 | 21.168 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
266 | 19 | September | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
266 | 20 | September | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
266 | 21 | September | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
266 | 22 | September | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
266 | 23 | September | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
266 | 24 | September | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
267 | 1 | September | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
267 | 2 | September | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
267 | 3 | September | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
267 | 4 | September | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
267 | 5 | September | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
267 | 6 | September | 7.7 | 9.4798 | 1059.95 | 1.323 | 1061.273 | 0 | 1061.273 | 0 | 0 | 99.8753 | 0.12466 | 0 | 99.8753 | 0.12466 | 0
267 | 7 | September | 7.2 | 8.8642 | 908.65 | 21.168 | 929.818 | 0 | 929.818 | 0 | 0 | 97.7234 | 2.2766 | 0 | 97.7234 | 2.2766 | 0
267 | 8 | September | 7.2 | 8.8642 | 908.65 | 82.026 | 990.676 | 0 | 990.676 | 0 | 0 | 91.7202 | 8.2798 | 0 | 91.7202 | 8.2798 | 0
267 | 9 | September | 9.8 | 12.0652 | 1683.85 | 148.176 | 1832.026 | 0 | 1832.026 | 0 | 0 | 91.9119 | 8.0881 | 0 | 91.9119 | 8.0881 | 0
267 | 10 | September | 7.2 | 8.8642 | 908.65 | 206.388 | 1115.038 | 0 | 1115.038 | 0 | 0 | 81.4905 | 18.5095 | 0 | 81.4905 | 18.5095 | 0
267 | 11 | September | 4.6 | 5.6633 | 237.15 | 247.5995 | 484.7495 | 0 | 484.7495 | 0 | 0 | 48.9222 | 51.0778 | 0 | 48.9222 | 51.0778 | 0
267 | 12 | September | 5.1 | 6.2788 | 312.8 | 265.0936 | 577.8936 | 0 | 577.8936 | 0 | 0 | 54.1276 | 45.8724 | 0 | 54.1276 | 45.8724 | 0
267 | 13 | September | 6.2 | 7.6331 | 625.6 | 259.4999 | 885.0999 | 0 | 885.0999 | 0 | 0 | 70.6813 | 29.3187 | 0 | 70.6813 | 29.3187 | 0
267 | 14 | September | 6.7 | 8.2487 | 761.6 | 228.7571 | 990.3571 | 0 | 990.3571 | 0 | 0 | 76.9016 | 23.0984 | 0 | 76.9016 | 23.0984 | 0
267 | 15 | September | 7.7 | 9.4798 | 1059.95 | 302.9353 | 1362.8853 | 0 | 1362.8853 | 0 | 0 | 77.7725 | 22.2275 | 0 | 77.7725 | 22.2275 | 0
267 | 16 | September | 9.8 | 12.0652 | 1683.85 | 324.5331 | 2008.3831 | 1 | 2000 | 8.3831 | 0.41915 | 83.8411 | 15.8075 | 2.5831 | 83.7733 | 16.1589 | 0.49785
267 | 17 | September | 7.7 | 9.4798 | 1059.95 | 132.7652 | 1192.7152 | 0 | 1192.7152 | 0 | 0 | 88.8687 | 11.1313 | 0 | 88.8687 | 11.1313 | 0
267 | 18 | September | 6.7 | 8.2487 | 761.6 | 18.522 | 780.122 | 0 | 780.122 | 0 | 0 | 97.6258 | 2.3742 | 0 | 97.6258 | 2.3742 | 0
267 | 19 | September | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
267 | 20 | September | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
267 | 21 | September | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
267 | 22 | September | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
267 | 23 | September | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
267 | 24 | September | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
268 | 1 | September | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
268 | 2 | September | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
268 | 3 | September | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
268 | 4 | September | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
268 | 5 | September | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
268 | 6 | September | 4.1 | 5.0477 | 173.4 | 1.323 | 174.723 | 0 | 174.723 | 0 | 0 | 99.2428 | 0.7572 | 0 | 99.2428 | 0.7572 | 0
268 | 7 | September | 3.6 | 4.4321 | 75.65 | 70.7918 | 146.4418 | 0 | 146.4418 | 0 | 0 | 51.6587 | 48.3413 | 0 | 51.6587 | 48.3413 | 0
268 | 8 | September | 3.1 | 3.8165 | 0 | 349.898 | 349.898 | 0 | 349.898 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
268 | 9 | September | 4.6 | 5.6633 | 237.15 | 713.6322 | 950.7822 | 0 | 950.7822 | 0 | 0 | 24.9426 | 75.0574 | 0 | 24.9426 | 75.0574 | 0
268 | 10 | September | 5.1 | 6.2788 | 312.8 | 704.2719 | 1017.0719 | 0 | 1017.0719 | 0 | 0 | 30.755 | 69.245 | 0 | 30.755 | 69.245 | 0
268 | 11 | September | 5.7 | 7.0175 | 504.9 | 811.6236 | 1316.5236 | 0 | 1316.5236 | 0 | 0 | 38.351 | 61.649 | 0 | 38.351 | 61.649 | 0
268 | 12 | September | 7.2 | 8.8642 | 908.65 | 482.391 | 1391.041 | 0 | 1391.041 | 0 | 0 | 65.3216 | 34.6784 | 0 | 65.3216 | 34.6784 | 0
268 | 13 | September | 6.2 | 7.6331 | 625.6 | 462.89 | 1088.49 | 0 | 1088.49 | 0 | 0 | 57.4741 | 42.5259 | 0 | 57.4741 | 42.5259 | 0
268 | 14 | September | 8.7 | 10.711 | 1490.05 | 385.7408 | 1875.7908 | 0 | 1875.7908 | 0 | 0 | 79.4358 | 20.5642 | 0 | 79.4358 | 20.5642 | 0
268 | 15 | September | 8.2 | 10.0954 | 1359.15 | 424.4196 | 1783.5696 | 0 | 1783.5696 | 0 | 0 | 76.2039 | 23.7961 | 0 | 76.2039 | 23.7961 | 0
268 | 16 | September | 7.2 | 8.8642 | 908.65 | 387.5456 | 1296.1956 | 0 | 1296.1956 | 0 | 0 | 70.1013 | 29.8987 | 0 | 70.1013 | 29.8987 | 0
268 | 17 | September | 7.2 | 8.8642 | 908.65 | 133.4465 | 1042.0965 | 0 | 1042.0965 | 0 | 0 | 87.1944 | 12.8056 | 0 | 87.1944 | 12.8056 | 0
268 | 18 | September | 8.7 | 10.711 | 1490.05 | 17.199 | 1507.249 | 0 | 1507.249 | 0 | 0 | 98.8589 | 1.1411 | 0 | 98.8589 | 1.1411 | 0
268 | 19 | September | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
268 | 20 | September | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
268 | 21 | September | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
268 | 22 | September | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
268 | 23 | September | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
268 | 24 | September | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
269 | 1 | September | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
269 | 2 | September | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
269 | 3 | September | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
269 | 4 | September | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
269 | 5 | September | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
269 | 6 | September | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
269 | 7 | September | 7.2 | 8.8642 | 908.65 | 18.522 | 927.172 | 0 | 927.172 | 0 | 0 | 98.0023 | 1.9977 | 0 | 98.0023 | 1.9977 | 0
269 | 8 | September | 5.7 | 7.0175 | 504.9 | 78.057 | 582.957 | 0 | 582.957 | 0 | 0 | 86.6102 | 13.3898 | 0 | 86.6102 | 13.3898 | 0
269 | 9 | September | 5.1 | 6.2788 | 312.8 | 144.207 | 457.007 | 0 | 457.007 | 0 | 0 | 68.4453 | 31.5547 | 0 | 68.4453 | 31.5547 | 0
269 | 10 | September | 4.1 | 5.0477 | 173.4 | 199.773 | 373.173 | 0 | 373.173 | 0 | 0 | 46.4664 | 53.5336 | 0 | 46.4664 | 53.5336 | 0
269 | 11 | September | 5.1 | 6.2788 | 312.8 | 240.8771 | 553.6771 | 0 | 553.6771 | 0 | 0 | 56.495 | 43.505 | 0 | 56.495 | 43.505 | 0
269 | 12 | September | 4.6 | 5.6633 | 237.15 | 261.0874 | 498.2374 | 0 | 498.2374 | 0 | 0 | 47.5978 | 52.4022 | 0 | 47.5978 | 52.4022 | 0
269 | 13 | September | 3.6 | 4.4321 | 75.65 | 252.8057 | 328.4557 | 0 | 328.4557 | 0 | 0 | 23.032 | 76.968 | 0 | 23.032 | 76.968 | 0
269 | 14 | September | 3.1 | 3.8165 | 0 | 223.4537 | 223.4537 | 0 | 223.4537 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
269 | 15 | September | 3.6 | 4.4321 | 75.65 | 173.313 | 248.963 | 0 | 248.963 | 0 | 0 | 30.386 | 69.614 | 0 | 30.386 | 69.614 | 0
269 | 16 | September | 2.1 | 2.5854 | 0 | 111.132 | 111.132 | 0 | 111.132 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
269 | 17 | September | 3.6 | 4.4321 | 75.65 | 44.982 | 120.632 | 0 | 120.632 | 0 | 0 | 62.7114 | 37.2886 | 0 | 62.7114 | 37.2886 | 0
269 | 18 | September | 3.6 | 4.4321 | 75.65 | 5.292 | 80.942 | 0 | 80.942 | 0 | 0 | 93.462 | 6.538 | 0 | 93.462 | 6.538 | 0
269 | 19 | September | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
269 | 20 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
269 | 21 | September | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
269 | 22 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
269 | 23 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
269 | 24 | September | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
270 | 1 | September | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
270 | 2 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
270 | 3 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
270 | 4 | September | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
270 | 5 | September | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
270 | 6 | September | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
270 | 7 | September | 4.6 | 5.6633 | 237.15 | 27.783 | 264.933 | 0 | 264.933 | 0 | 0 | 89.5132 | 10.4868 | 0 | 89.5132 | 10.4868 | 0
270 | 8 | September | 5.1 | 6.2788 | 312.8 | 124.6286 | 437.4286 | 0 | 437.4286 | 0 | 0 | 71.5088 | 28.4912 | 0 | 71.5088 | 28.4912 | 0
270 | 9 | September | 5.7 | 7.0175 | 504.9 | 233.0598 | 737.9598 | 0 | 737.9598 | 0 | 0 | 68.4184 | 31.5816 | 0 | 68.4184 | 31.5816 | 0
270 | 10 | September | 7.7 | 9.4798 | 1059.95 | 524.52 | 1584.47 | 0 | 1584.47 | 0 | 0 | 66.8962 | 33.1038 | 0 | 66.8962 | 33.1038 | 0
270 | 11 | September | 12.3 | 15.1431 | 1700 | 429.6226 | 2129.6226 | 1 | 2000 | 129.6226 | 6.4811 | 79.8264 | 15 | 30.1713 | 78.5189 | 20.1736 | 7.6249
270 | 12 | September | 11.8 | 14.5275 | 1700 | 999.6345 | 2699.6345 | 1 | 2000 | 699.6345 | 34.9817 | 62.9715 | 15 | 69.989 | 50.0183 | 37.0285 | 41.155
270 | 13 | September | 11.3 | 13.9119 | 1700 | 1113.4647 | 2813.4647 | 1 | 2000 | 813.4647 | 40.6732 | 60.4237 | 15 | 73.0571 | 44.3268 | 39.5763 | 47.8509
270 | 14 | September | 16.4 | 20.1908 | 1700 | 923.6893 | 2623.6893 | 1 | 2000 | 623.6893 | 31.1845 | 64.7943 | 15 | 67.5215 | 53.8155 | 35.2057 | 36.6876
270 | 15 | September | 13.4 | 16.4973 | 1700 | 663.9425 | 2363.9425 | 1 | 2000 | 363.9425 | 18.1971 | 71.9138 | 15 | 54.8154 | 66.8029 | 28.0862 | 21.4084
270 | 16 | September | 14.4 | 17.7285 | 1700 | 389.9768 | 2089.9768 | 1 | 2000 | 89.9768 | 4.4988 | 81.3406 | 15 | 23.0723 | 80.5012 | 18.6594 | 5.2928
270 | 17 | September | 11.3 | 13.9119 | 1700 | 126.5095 | 1826.5095 | 0 | 1826.5095 | 0 | 0 | 93.0737 | 6.9263 | 0 | 93.0737 | 6.9263 | 0
270 | 18 | September | 12.3 | 15.1431 | 1700 | 13.23 | 1713.23 | 0 | 1713.23 | 0 | 0 | 99.2278 | 0.77223 | 0 | 99.2278 | 0.77223 | 0
270 | 19 | September | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
270 | 20 | September | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
270 | 21 | September | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
270 | 22 | September | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
270 | 23 | September | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
270 | 24 | September | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
271 | 1 | September | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
271 | 2 | September | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
271 | 3 | September | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
271 | 4 | September | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
271 | 5 | September | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
271 | 6 | September | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
271 | 7 | September | 5.7 | 7.0175 | 504.9 | 44.1374 | 549.0374 | 0 | 549.0374 | 0 | 0 | 91.961 | 8.039 | 0 | 91.961 | 8.039 | 0
271 | 8 | September | 6.7 | 8.2487 | 761.6 | 283.7379 | 1045.3379 | 0 | 1045.3379 | 0 | 0 | 72.8568 | 27.1432 | 0 | 72.8568 | 27.1432 | 0
271 | 9 | September | 6.7 | 8.2487 | 761.6 | 687.0618 | 1448.6618 | 0 | 1448.6618 | 0 | 0 | 52.5727 | 47.4273 | 0 | 52.5727 | 47.4273 | 0
271 | 10 | September | 6.7 | 8.2487 | 761.6 | 987.8247 | 1749.4247 | 0 | 1749.4247 | 0 | 0 | 43.5343 | 56.4657 | 0 | 43.5343 | 56.4657 | 0
271 | 11 | September | 7.7 | 9.4798 | 1059.95 | 1155.9374 | 2215.8874 | 1 | 2000 | 215.8874 | 10.7944 | 47.8341 | 47.0025 | 18.6764 | 42.2031 | 52.1659 | 20.3677
271 | 12 | September | 5.7 | 7.0175 | 504.9 | 1228.8477 | 1733.7477 | 0 | 1733.7477 | 0 | 0 | 29.1219 | 70.8781 | 0 | 29.1219 | 70.8781 | 0
271 | 13 | September | 6.7 | 8.2487 | 761.6 | 1162.1334 | 1923.7334 | 0 | 1923.7334 | 0 | 0 | 39.5897 | 60.4103 | 0 | 39.5897 | 60.4103 | 0
271 | 14 | September | 6.7 | 8.2487 | 761.6 | 982.231 | 1743.831 | 0 | 1743.831 | 0 | 0 | 43.674 | 56.326 | 0 | 43.674 | 56.326 | 0
271 | 15 | September | 5.1 | 6.2788 | 312.8 | 689.3939 | 1002.1939 | 0 | 1002.1939 | 0 | 0 | 31.2115 | 68.7885 | 0 | 31.2115 | 68.7885 | 0
271 | 16 | September | 6.2 | 7.6331 | 625.6 | 297.2504 | 922.8504 | 0 | 922.8504 | 0 | 0 | 67.79 | 32.21 | 0 | 67.79 | 32.21 | 0
271 | 17 | September | 6.2 | 7.6331 | 625.6 | 119.2091 | 744.8091 | 0 | 744.8091 | 0 | 0 | 83.9947 | 16.0053 | 0 | 83.9947 | 16.0053 | 0
271 | 18 | September | 4.1 | 5.0477 | 173.4 | 11.907 | 185.307 | 0 | 185.307 | 0 | 0 | 93.5744 | 6.4256 | 0 | 93.5744 | 6.4256 | 0
271 | 19 | September | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
271 | 20 | September | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
271 | 21 | September | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
271 | 22 | September | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
271 | 23 | September | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
271 | 24 | September | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
272 | 1 | September | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
272 | 2 | September | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
272 | 3 | September | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
272 | 4 | September | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
272 | 5 | September | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
272 | 6 | September | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
272 | 7 | September | 5.1 | 6.2788 | 312.8 | 49.5045 | 362.3045 | 0 | 362.3045 | 0 | 0 | 86.3362 | 13.6638 | 0 | 86.3362 | 13.6638 | 0
272 | 8 | September | 5.1 | 6.2788 | 312.8 | 323.9415 | 636.7415 | 0 | 636.7415 | 0 | 0 | 49.1251 | 50.8749 | 0 | 49.1251 | 50.8749 | 0
272 | 9 | September | 6.2 | 7.6331 | 625.6 | 686.7237 | 1312.3237 | 0 | 1312.3237 | 0 | 0 | 47.6712 | 52.3288 | 0 | 47.6712 | 52.3288 | 0
272 | 10 | September | 6.2 | 7.6331 | 625.6 | 971.3633 | 1596.9633 | 0 | 1596.9633 | 0 | 0 | 39.1743 | 60.8257 | 0 | 39.1743 | 60.8257 | 0
272 | 11 | September | 6.7 | 8.2487 | 761.6 | 804.9271 | 1566.5271 | 0 | 1566.5271 | 0 | 0 | 48.6171 | 51.3829 | 0 | 48.6171 | 51.3829 | 0
272 | 12 | September | 8.2 | 10.0954 | 1359.15 | 1148.2264 | 2507.3764 | 1 | 2000 | 507.3764 | 25.3688 | 54.2061 | 32.0425 | 44.1878 | 42.5887 | 45.7939 | 37.3304
272 | 13 | September | 7.2 | 8.8642 | 908.65 | 1124.263 | 2032.913 | 1 | 2000 | 32.913 | 1.6456 | 44.6969 | 54.5675 | 2.9275 | 43.7869 | 55.3031 | 3.6222
272 | 14 | September | 5.7 | 7.0175 | 504.9 | 947.4612 | 1452.3612 | 0 | 1452.3612 | 0 | 0 | 34.7641 | 65.2359 | 0 | 34.7641 | 65.2359 | 0
272 | 15 | September | 6.7 | 8.2487 | 761.6 | 675.5738 | 1437.1738 | 0 | 1437.1738 | 0 | 0 | 52.9929 | 47.0071 | 0 | 52.9929 | 47.0071 | 0
272 | 16 | September | 4.1 | 5.0477 | 173.4 | 288.9692 | 462.3692 | 0 | 462.3692 | 0 | 0 | 37.5025 | 62.4975 | 0 | 37.5025 | 62.4975 | 0
272 | 17 | September | 3.1 | 3.8165 | 0 | 62.181 | 62.181 | 0 | 62.181 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
272 | 18 | September | 0 | 0 | 0 | 5.292 | 5.292 | 0 | 5.292 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
272 | 19 | September | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
272 | 20 | September | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
272 | 21 | September | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
272 | 22 | September | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
272 | 23 | September | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
272 | 24 | September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
273 | 1 | September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
273 | 2 | September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
273 | 3 | September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
273 | 4 | September | 0.5 | 0.61557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
273 | 5 | September | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
273 | 6 | September | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
273 | 7 | September | 1.5 | 1.8467 | 0 | 22.491 | 22.491 | 0 | 22.491 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
273 | 8 | September | 2.6 | 3.201 | 0 | 115.062 | 115.062 | 0 | 115.062 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
273 | 9 | September | 2.6 | 3.201 | 0 | 363.1231 | 363.1231 | 0 | 363.1231 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
273 | 10 | September | 3.6 | 4.4321 | 75.65 | 349.0702 | 424.7202 | 0 | 424.7202 | 0 | 0 | 17.8117 | 82.1883 | 0 | 17.8117 | 82.1883 | 0
273 | 11 | September | 4.1 | 5.0477 | 173.4 | 400.3091 | 573.7091 | 0 | 573.7091 | 0 | 0 | 30.2244 | 69.7756 | 0 | 30.2244 | 69.7756 | 0
273 | 12 | September | 2.6 | 3.201 | 0 | 427.9107 | 427.9107 | 0 | 427.9107 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
273 | 13 | September | 2.1 | 2.5854 | 0 | 414.8755 | 414.8755 | 0 | 414.8755 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
273 | 14 | September | 3.6 | 4.4321 | 75.65 | 359.5886 | 435.2386 | 0 | 435.2386 | 0 | 0 | 17.3813 | 82.6187 | 0 | 17.3813 | 82.6187 | 0
273 | 15 | September | 3.1 | 3.8165 | 0 | 275.2013 | 275.2013 | 0 | 275.2013 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
273 | 16 | September | 3.6 | 4.4321 | 75.65 | 160.7125 | 236.3625 | 0 | 236.3625 | 0 | 0 | 32.0059 | 67.9941 | 0 | 32.0059 | 67.9941 | 0
273 | 17 | September | 4.1 | 5.0477 | 173.4 | 74.1417 | 247.5417 | 0 | 247.5417 | 0 | 0 | 70.0488 | 29.9512 | 0 | 70.0488 | 29.9512 | 0
273 | 18 | September | 4.6 | 5.6633 | 237.15 | 2.646 | 239.796 | 0 | 239.796 | 0 | 0 | 98.8966 | 1.1034 | 0 | 98.8966 | 1.1034 | 0
273 | 19 | September | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
273 | 20 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
273 | 21 | September | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
273 | 22 | September | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
273 | 23 | September | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
273 | 24 | September | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
274 | 1 | October | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
274 | 2 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
274 | 3 | October | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
274 | 4 | October | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
274 | 5 | October | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
274 | 6 | October | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
274 | 7 | October | 5.1 | 6.2788 | 312.8 | 27.783 | 340.583 | 0 | 340.583 | 0 | 0 | 91.8425 | 8.1575 | 0 | 91.8425 | 8.1575 | 0
274 | 8 | October | 5.7 | 7.0175 | 504.9 | 176.7823 | 681.6823 | 0 | 681.6823 | 0 | 0 | 74.0668 | 25.9332 | 0 | 74.0668 | 25.9332 | 0
274 | 9 | October | 6.2 | 7.6331 | 625.6 | 219.7016 | 845.3016 | 0 | 845.3016 | 0 | 0 | 74.0091 | 25.9909 | 0 | 74.0091 | 25.9909 | 0
274 | 10 | October | 6.7 | 8.2487 | 761.6 | 642.3318 | 1403.9318 | 0 | 1403.9318 | 0 | 0 | 54.2476 | 45.7524 | 0 | 54.2476 | 45.7524 | 0
274 | 11 | October | 6.7 | 8.2487 | 761.6 | 773.4186 | 1535.0186 | 0 | 1535.0186 | 0 | 0 | 49.615 | 50.385 | 0 | 49.615 | 50.385 | 0
274 | 12 | October | 7.2 | 8.8642 | 908.65 | 638.8148 | 1547.4648 | 0 | 1547.4648 | 0 | 0 | 58.7186 | 41.2814 | 0 | 58.7186 | 41.2814 | 0
274 | 13 | October | 6.2 | 7.6331 | 625.6 | 567.638 | 1193.238 | 0 | 1193.238 | 0 | 0 | 52.4288 | 47.5712 | 0 | 52.4288 | 47.5712 | 0
274 | 14 | October | 6.2 | 7.6331 | 625.6 | 491.8794 | 1117.4794 | 0 | 1117.4794 | 0 | 0 | 55.9831 | 44.0169 | 0 | 55.9831 | 44.0169 | 0
274 | 15 | October | 6.7 | 8.2487 | 761.6 | 590.2412 | 1351.8412 | 0 | 1351.8412 | 0 | 0 | 56.338 | 43.662 | 0 | 56.338 | 43.662 | 0
274 | 16 | October | 6.7 | 8.2487 | 761.6 | 341.2836 | 1102.8836 | 0 | 1102.8836 | 0 | 0 | 69.0553 | 30.9447 | 0 | 69.0553 | 30.9447 | 0
274 | 17 | October | 6.7 | 8.2487 | 761.6 | 83.7646 | 845.3646 | 0 | 845.3646 | 0 | 0 | 90.0913 | 9.9087 | 0 | 90.0913 | 9.9087 | 0
274 | 18 | October | 4.1 | 5.0477 | 173.4 | 7.938 | 181.338 | 0 | 181.338 | 0 | 0 | 95.6225 | 4.3775 | 0 | 95.6225 | 4.3775 | 0
274 | 19 | October | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
274 | 20 | October | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
274 | 21 | October | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
274 | 22 | October | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
274 | 23 | October | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
274 | 24 | October | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
275 | 1 | October | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
275 | 2 | October | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
275 | 3 | October | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
275 | 4 | October | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
275 | 5 | October | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
275 | 6 | October | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
275 | 7 | October | 7.2 | 8.8642 | 908.65 | 37.9249 | 946.5749 | 0 | 946.5749 | 0 | 0 | 95.9935 | 4.0065 | 0 | 95.9935 | 4.0065 | 0
275 | 8 | October | 7.7 | 9.4798 | 1059.95 | 295.5548 | 1355.5048 | 0 | 1355.5048 | 0 | 0 | 78.196 | 21.804 | 0 | 78.196 | 21.804 | 0
275 | 9 | October | 8.2 | 10.0954 | 1359.15 | 649.8354 | 2008.9854 | 1 | 2000 | 8.9854 | 0.44927 | 67.6536 | 32.0425 | 1.3827 | 67.5082 | 32.3464 | 0.6611
275 | 10 | October | 8.2 | 10.0954 | 1359.15 | 659.1707 | 2018.3207 | 1 | 2000 | 18.3207 | 0.91603 | 67.3406 | 32.0425 | 2.7794 | 67.0415 | 32.6594 | 1.348
275 | 11 | October | 7.7 | 9.4798 | 1059.95 | 762.3356 | 1822.2856 | 0 | 1822.2856 | 0 | 0 | 58.166 | 41.834 | 0 | 58.166 | 41.834 | 0
275 | 12 | October | 7.7 | 9.4798 | 1059.95 | 801.3035 | 1861.2535 | 0 | 1861.2535 | 0 | 0 | 56.9482 | 43.0518 | 0 | 56.9482 | 43.0518 | 0
275 | 13 | October | 5.7 | 7.0175 | 504.9 | 605.689 | 1110.589 | 0 | 1110.589 | 0 | 0 | 45.4624 | 54.5376 | 0 | 45.4624 | 54.5376 | 0
275 | 14 | October | 7.2 | 8.8642 | 908.65 | 655.6143 | 1564.2643 | 0 | 1564.2643 | 0 | 0 | 58.088 | 41.912 | 0 | 58.088 | 41.912 | 0
275 | 15 | October | 6.7 | 8.2487 | 761.6 | 282.0523 | 1043.6523 | 0 | 1043.6523 | 0 | 0 | 72.9745 | 27.0255 | 0 | 72.9745 | 27.0255 | 0
275 | 16 | October | 6.7 | 8.2487 | 761.6 | 292.4854 | 1054.0854 | 0 | 1054.0854 | 0 | 0 | 72.2522 | 27.7478 | 0 | 72.2522 | 27.7478 | 0
275 | 17 | October | 6.2 | 7.6331 | 625.6 | 66.5625 | 692.1625 | 0 | 692.1625 | 0 | 0 | 90.3834 | 9.6166 | 0 | 90.3834 | 9.6166 | 0
275 | 18 | October | 6.2 | 7.6331 | 625.6 | 5.292 | 630.892 | 0 | 630.892 | 0 | 0 | 99.1612 | 0.83881 | 0 | 99.1612 | 0.83881 | 0
275 | 19 | October | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
275 | 20 | October | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
275 | 21 | October | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
275 | 22 | October | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
275 | 23 | October | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
275 | 24 | October | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
276 | 1 | October | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
276 | 2 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
276 | 3 | October | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
276 | 4 | October | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
276 | 5 | October | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
276 | 6 | October | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
276 | 7 | October | 7.7 | 9.4798 | 1059.95 | 31.752 | 1091.702 | 0 | 1091.702 | 0 | 0 | 97.0915 | 2.9085 | 0 | 97.0915 | 2.9085 | 0
276 | 8 | October | 8.2 | 10.0954 | 1359.15 | 219.0373 | 1578.1873 | 0 | 1578.1873 | 0 | 0 | 86.121 | 13.879 | 0 | 86.121 | 13.879 | 0
276 | 9 | October | 8.2 | 10.0954 | 1359.15 | 468.4976 | 1827.6476 | 0 | 1827.6476 | 0 | 0 | 74.3661 | 25.6339 | 0 | 74.3661 | 25.6339 | 0
276 | 10 | October | 7.2 | 8.8642 | 908.65 | 858.145 | 1766.795 | 0 | 1766.795 | 0 | 0 | 51.4293 | 48.5707 | 0 | 51.4293 | 48.5707 | 0
276 | 11 | October | 7.2 | 8.8642 | 908.65 | 1050.5636 | 1959.2136 | 0 | 1959.2136 | 0 | 0 | 46.3783 | 53.6217 | 0 | 46.3783 | 53.6217 | 0
276 | 12 | October | 7.7 | 9.4798 | 1059.95 | 1100.4595 | 2160.4095 | 1 | 2000 | 160.4095 | 8.0205 | 49.0625 | 47.0025 | 14.5766 | 44.977 | 50.9375 | 15.1337
276 | 13 | October | 7.2 | 8.8642 | 908.65 | 919.3346 | 1827.9846 | 0 | 1827.9846 | 0 | 0 | 49.7078 | 50.2922 | 0 | 49.7078 | 50.2922 | 0
276 | 14 | October | 6.2 | 7.6331 | 625.6 | 659.9505 | 1285.5505 | 0 | 1285.5505 | 0 | 0 | 48.664 | 51.336 | 0 | 48.664 | 51.336 | 0
276 | 15 | October | 6.7 | 8.2487 | 761.6 | 599.9902 | 1361.5902 | 0 | 1361.5902 | 0 | 0 | 55.9346 | 44.0654 | 0 | 55.9346 | 44.0654 | 0
276 | 16 | October | 6.7 | 8.2487 | 761.6 | 211.0709 | 972.6709 | 0 | 972.6709 | 0 | 0 | 78.2999 | 21.7001 | 0 | 78.2999 | 21.7001 | 0
276 | 17 | October | 6.2 | 7.6331 | 625.6 | 30.429 | 656.029 | 0 | 656.029 | 0 | 0 | 95.3616 | 4.6384 | 0 | 95.3616 | 4.6384 | 0
276 | 18 | October | 7.7 | 9.4798 | 1059.95 | 1.323 | 1061.273 | 0 | 1061.273 | 0 | 0 | 99.8753 | 0.12466 | 0 | 99.8753 | 0.12466 | 0
276 | 19 | October | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
276 | 20 | October | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
276 | 21 | October | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
276 | 22 | October | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
276 | 23 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
276 | 24 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
277 | 1 | October | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
277 | 2 | October | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
277 | 3 | October | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
277 | 4 | October | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
277 | 5 | October | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
277 | 6 | October | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
277 | 7 | October | 8.2 | 10.0954 | 1359.15 | 11.907 | 1371.057 | 0 | 1371.057 | 0 | 0 | 99.1315 | 0.86845 | 0 | 99.1315 | 0.86845 | 0
277 | 8 | October | 5.7 | 7.0175 | 504.9 | 104.8714 | 609.7714 | 0 | 609.7714 | 0 | 0 | 82.8015 | 17.1985 | 0 | 82.8015 | 17.1985 | 0
277 | 9 | October | 5.7 | 7.0175 | 504.9 | 345.2865 | 850.1865 | 0 | 850.1865 | 0 | 0 | 59.387 | 40.613 | 0 | 59.387 | 40.613 | 0
277 | 10 | October | 6.2 | 7.6331 | 625.6 | 320.0382 | 945.6382 | 0 | 945.6382 | 0 | 0 | 66.1564 | 33.8436 | 0 | 66.1564 | 33.8436 | 0
277 | 11 | October | 5.7 | 7.0175 | 504.9 | 221.0532 | 725.9532 | 0 | 725.9532 | 0 | 0 | 69.5499 | 30.4501 | 0 | 69.5499 | 30.4501 | 0
277 | 12 | October | 4.1 | 5.0477 | 173.4 | 423.443 | 596.843 | 0 | 596.843 | 0 | 0 | 29.0529 | 70.9471 | 0 | 29.0529 | 70.9471 | 0
277 | 13 | October | 5.1 | 6.2788 | 312.8 | 591.5174 | 904.3174 | 0 | 904.3174 | 0 | 0 | 34.5896 | 65.4104 | 0 | 34.5896 | 65.4104 | 0
277 | 14 | October | 3.1 | 3.8165 | 0 | 636.0982 | 636.0982 | 0 | 636.0982 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
277 | 15 | October | 5.7 | 7.0175 | 504.9 | 469.9851 | 974.8851 | 0 | 974.8851 | 0 | 0 | 51.7907 | 48.2093 | 0 | 51.7907 | 48.2093 | 0
277 | 16 | October | 4.1 | 5.0477 | 173.4 | 144.9664 | 318.3664 | 0 | 318.3664 | 0 | 0 | 54.4655 | 45.5345 | 0 | 54.4655 | 45.5345 | 0
277 | 17 | October | 3.6 | 4.4321 | 75.65 | 56.889 | 132.539 | 0 | 132.539 | 0 | 0 | 57.0775 | 42.9225 | 0 | 57.0775 | 42.9225 | 0
277 | 18 | October | 3.6 | 4.4321 | 75.65 | 2.646 | 78.296 | 0 | 78.296 | 0 | 0 | 96.6205 | 3.3795 | 0 | 96.6205 | 3.3795 | 0
277 | 19 | October | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
277 | 20 | October | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
277 | 21 | October | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
277 | 22 | October | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
277 | 23 | October | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
277 | 24 | October | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
278 | 1 | October | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
278 | 2 | October | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
278 | 3 | October | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
278 | 4 | October | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
278 | 5 | October | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
278 | 6 | October | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
278 | 7 | October | 2.6 | 3.201 | 0 | 10.584 | 10.584 | 0 | 10.584 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
278 | 8 | October | 5.7 | 7.0175 | 504.9 | 60.858 | 565.758 | 0 | 565.758 | 0 | 0 | 89.2431 | 10.7569 | 0 | 89.2431 | 10.7569 | 0
278 | 9 | October | 5.7 | 7.0175 | 504.9 | 124.362 | 629.262 | 0 | 629.262 | 0 | 0 | 80.2368 | 19.7632 | 0 | 80.2368 | 19.7632 | 0
278 | 10 | October | 3.1 | 3.8165 | 0 | 314.5571 | 314.5571 | 0 | 314.5571 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
278 | 11 | October | 5.1 | 6.2788 | 312.8 | 215.7004 | 528.5004 | 0 | 528.5004 | 0 | 0 | 59.1863 | 40.8137 | 0 | 59.1863 | 40.8137 | 0
278 | 12 | October | 5.7 | 7.0175 | 504.9 | 231.5945 | 736.4945 | 0 | 736.4945 | 0 | 0 | 68.5545 | 31.4455 | 0 | 68.5545 | 31.4455 | 0
278 | 13 | October | 5.1 | 6.2788 | 312.8 | 224.8986 | 537.6986 | 0 | 537.6986 | 0 | 0 | 58.1739 | 41.8261 | 0 | 58.1739 | 41.8261 | 0
278 | 14 | October | 5.1 | 6.2788 | 312.8 | 344.9449 | 657.7449 | 0 | 657.7449 | 0 | 0 | 47.5564 | 52.4436 | 0 | 47.5564 | 52.4436 | 0
278 | 15 | October | 5.7 | 7.0175 | 504.9 | 238.5692 | 743.4692 | 0 | 743.4692 | 0 | 0 | 67.9114 | 32.0886 | 0 | 67.9114 | 32.0886 | 0
278 | 16 | October | 4.1 | 5.0477 | 173.4 | 84.672 | 258.072 | 0 | 258.072 | 0 | 0 | 67.1906 | 32.8094 | 0 | 67.1906 | 32.8094 | 0
278 | 17 | October | 3.1 | 3.8165 | 0 | 25.137 | 25.137 | 0 | 25.137 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
278 | 18 | October | 3.6 | 4.4321 | 75.65 | 1.323 | 76.973 | 0 | 76.973 | 0 | 0 | 98.2812 | 1.7188 | 0 | 98.2812 | 1.7188 | 0
278 | 19 | October | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
278 | 20 | October | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
278 | 21 | October | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
278 | 22 | October | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
278 | 23 | October | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
278 | 24 | October | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
279 | 1 | October | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
279 | 2 | October | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
279 | 3 | October | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
279 | 4 | October | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
279 | 5 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
279 | 6 | October | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
279 | 7 | October | 4.1 | 5.0477 | 173.4 | 29.106 | 202.506 | 0 | 202.506 | 0 | 0 | 85.6271 | 14.3729 | 0 | 85.6271 | 14.3729 | 0
279 | 8 | October | 4.1 | 5.0477 | 173.4 | 266.2226 | 439.6226 | 0 | 439.6226 | 0 | 0 | 39.4429 | 60.5571 | 0 | 39.4429 | 60.5571 | 0
279 | 9 | October | 5.7 | 7.0175 | 504.9 | 612.0342 | 1116.9342 | 0 | 1116.9342 | 0 | 0 | 45.2041 | 54.7959 | 0 | 45.2041 | 54.7959 | 0
279 | 10 | October | 6.7 | 8.2487 | 761.6 | 483.6427 | 1245.2427 | 0 | 1245.2427 | 0 | 0 | 61.1608 | 38.8392 | 0 | 61.1608 | 38.8392 | 0
279 | 11 | October | 6.2 | 7.6331 | 625.6 | 389.5397 | 1015.1397 | 0 | 1015.1397 | 0 | 0 | 61.627 | 38.373 | 0 | 61.627 | 38.373 | 0
279 | 12 | October | 5.7 | 7.0175 | 504.9 | 399.9223 | 904.8223 | 0 | 904.8223 | 0 | 0 | 55.801 | 44.199 | 0 | 55.801 | 44.199 | 0
279 | 13 | October | 5.7 | 7.0175 | 504.9 | 384.2095 | 889.1095 | 0 | 889.1095 | 0 | 0 | 56.7872 | 43.2128 | 0 | 56.7872 | 43.2128 | 0
279 | 14 | October | 3.6 | 4.4321 | 75.65 | 331.3824 | 407.0324 | 0 | 407.0324 | 0 | 0 | 18.5857 | 81.4143 | 0 | 18.5857 | 81.4143 | 0
279 | 15 | October | 6.7 | 8.2487 | 761.6 | 244.9119 | 1006.5119 | 0 | 1006.5119 | 0 | 0 | 75.6673 | 24.3327 | 0 | 75.6673 | 24.3327 | 0
279 | 16 | October | 7.2 | 8.8642 | 908.65 | 134.8611 | 1043.5111 | 0 | 1043.5111 | 0 | 0 | 87.0762 | 12.9238 | 0 | 87.0762 | 12.9238 | 0
279 | 17 | October | 5.1 | 6.2788 | 312.8 | 57.8759 | 370.6759 | 0 | 370.6759 | 0 | 0 | 84.3864 | 15.6136 | 0 | 84.3864 | 15.6136 | 0
279 | 18 | October | 3.6 | 4.4321 | 75.65 | 2.646 | 78.296 | 0 | 78.296 | 0 | 0 | 96.6205 | 3.3795 | 0 | 96.6205 | 3.3795 | 0
279 | 19 | October | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
279 | 20 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
279 | 21 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
279 | 22 | October | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
279 | 23 | October | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
279 | 24 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
280 | 1 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
280 | 2 | October | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
280 | 3 | October | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
280 | 4 | October | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
280 | 5 | October | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
280 | 6 | October | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
280 | 7 | October | 4.1 | 5.0477 | 173.4 | 15.876 | 189.276 | 0 | 189.276 | 0 | 0 | 91.6122 | 8.3878 | 0 | 91.6122 | 8.3878 | 0
280 | 8 | October | 5.1 | 6.2788 | 312.8 | 92.61 | 405.41 | 0 | 405.41 | 0 | 0 | 77.1565 | 22.8435 | 0 | 77.1565 | 22.8435 | 0
280 | 9 | October | 6.7 | 8.2487 | 761.6 | 120.393 | 881.993 | 0 | 881.993 | 0 | 0 | 86.3499 | 13.6501 | 0 | 86.3499 | 13.6501 | 0
280 | 10 | October | 7.7 | 9.4798 | 1059.95 | 323.298 | 1383.248 | 0 | 1383.248 | 0 | 0 | 76.6276 | 23.3724 | 0 | 76.6276 | 23.3724 | 0
280 | 11 | October | 8.7 | 10.711 | 1490.05 | 213.045 | 1703.095 | 0 | 1703.095 | 0 | 0 | 87.4907 | 12.5093 | 0 | 87.4907 | 12.5093 | 0
280 | 12 | October | 10.8 | 13.2964 | 1698.3 | 229.0562 | 1927.3562 | 0 | 1927.3562 | 0 | 0 | 88.1155 | 11.8845 | 0 | 88.1155 | 11.8845 | 0
280 | 13 | October | 12.3 | 15.1431 | 1700 | 220.9183 | 1920.9183 | 0 | 1920.9183 | 0 | 0 | 88.4993 | 11.5007 | 0 | 88.4993 | 11.5007 | 0
280 | 14 | October | 10.3 | 12.6808 | 1694.9 | 189.189 | 1884.089 | 0 | 1884.089 | 0 | 0 | 89.9586 | 10.0414 | 0 | 89.9586 | 10.0414 | 0
280 | 15 | October | 10.8 | 13.2964 | 1698.3 | 140.238 | 1838.538 | 0 | 1838.538 | 0 | 0 | 92.3723 | 7.6277 | 0 | 92.3723 | 7.6277 | 0
280 | 16 | October | 10.3 | 12.6808 | 1694.9 | 79.38 | 1774.28 | 0 | 1774.28 | 0 | 0 | 95.5261 | 4.4739 | 0 | 95.5261 | 4.4739 | 0
280 | 17 | October | 10.8 | 13.2964 | 1698.3 | 21.168 | 1719.468 | 0 | 1719.468 | 0 | 0 | 98.7689 | 1.2311 | 0 | 98.7689 | 1.2311 | 0
280 | 18 | October | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
280 | 19 | October | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
280 | 20 | October | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
280 | 21 | October | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
280 | 22 | October | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
280 | 23 | October | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
280 | 24 | October | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
281 | 1 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
281 | 2 | October | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
281 | 3 | October | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
281 | 4 | October | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
281 | 5 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
281 | 6 | October | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
281 | 7 | October | 8.7 | 10.711 | 1490.05 | 14.553 | 1504.603 | 0 | 1504.603 | 0 | 0 | 99.0328 | 0.96723 | 0 | 99.0328 | 0.96723 | 0
281 | 8 | October | 10.3 | 12.6808 | 1694.9 | 89.964 | 1784.864 | 0 | 1784.864 | 0 | 0 | 94.9596 | 5.0404 | 0 | 94.9596 | 5.0404 | 0
281 | 9 | October | 10.8 | 13.2964 | 1698.3 | 202.8474 | 1901.1474 | 0 | 1901.1474 | 0 | 0 | 89.3303 | 10.6697 | 0 | 89.3303 | 10.6697 | 0
281 | 10 | October | 10.3 | 12.6808 | 1694.9 | 309.7725 | 2004.6725 | 1 | 2000 | 4.6725 | 0.23362 | 84.5475 | 15.255 | 1.5084 | 84.5114 | 15.4525 | 0.27568
281 | 11 | October | 11.8 | 14.5275 | 1700 | 368.18 | 2068.18 | 1 | 2000 | 68.18 | 3.409 | 82.1979 | 15 | 18.5181 | 81.591 | 17.8021 | 4.0106
281 | 12 | October | 10.8 | 13.2964 | 1698.3 | 395.5672 | 2093.8672 | 1 | 2000 | 93.8672 | 4.6934 | 81.1083 | 15.085 | 23.7298 | 80.2216 | 18.8917 | 5.5271
281 | 13 | October | 11.8 | 14.5275 | 1700 | 222.1225 | 1922.1225 | 0 | 1922.1225 | 0 | 0 | 88.4439 | 11.5561 | 0 | 88.4439 | 11.5561 | 0
281 | 14 | October | 10.3 | 12.6808 | 1694.9 | 189.189 | 1884.089 | 0 | 1884.089 | 0 | 0 | 89.9586 | 10.0414 | 0 | 89.9586 | 10.0414 | 0
281 | 15 | October | 12.9 | 15.8818 | 1700 | 140.238 | 1840.238 | 0 | 1840.238 | 0 | 0 | 92.3794 | 7.6206 | 0 | 92.3794 | 7.6206 | 0
281 | 16 | October | 11.3 | 13.9119 | 1700 | 127.6862 | 1827.6862 | 0 | 1827.6862 | 0 | 0 | 93.0138 | 6.9862 | 0 | 93.0138 | 6.9862 | 0
281 | 17 | October | 9.3 | 11.4496 | 1598.85 | 19.845 | 1618.695 | 0 | 1618.695 | 0 | 0 | 98.774 | 1.226 | 0 | 98.774 | 1.226 | 0
281 | 18 | October | 10.8 | 13.2964 | 1698.3 | 1.323 | 1699.623 | 0 | 1699.623 | 0 | 0 | 99.9222 | 0.077841 | 0 | 99.9222 | 0.077841 | 0
281 | 19 | October | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
281 | 20 | October | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
281 | 21 | October | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
281 | 22 | October | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
281 | 23 | October | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
281 | 24 | October | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
282 | 1 | October | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
282 | 2 | October | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
282 | 3 | October | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
282 | 4 | October | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
282 | 5 | October | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
282 | 6 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
282 | 7 | October | 5.7 | 7.0175 | 504.9 | 13.23 | 518.13 | 0 | 518.13 | 0 | 0 | 97.4466 | 2.5534 | 0 | 97.4466 | 2.5534 | 0
282 | 8 | October | 6.7 | 8.2487 | 761.6 | 85.995 | 847.595 | 0 | 847.595 | 0 | 0 | 89.8542 | 10.1458 | 0 | 89.8542 | 10.1458 | 0
282 | 9 | October | 6.7 | 8.2487 | 761.6 | 325.1415 | 1086.7415 | 0 | 1086.7415 | 0 | 0 | 70.0811 | 29.9189 | 0 | 70.0811 | 29.9189 | 0
282 | 10 | October | 7.2 | 8.8642 | 908.65 | 440.0639 | 1348.7139 | 0 | 1348.7139 | 0 | 0 | 67.3716 | 32.6284 | 0 | 67.3716 | 32.6284 | 0
282 | 11 | October | 6.7 | 8.2487 | 761.6 | 510.746 | 1272.346 | 0 | 1272.346 | 0 | 0 | 59.8579 | 40.1421 | 0 | 59.8579 | 40.1421 | 0
282 | 12 | October | 9.3 | 11.4496 | 1598.85 | 403.0378 | 2001.8878 | 1 | 2000 | 1.8878 | 0.09439 | 79.8671 | 20.0575 | 0.46839 | 79.8481 | 20.1329 | 0.11807
282 | 13 | October | 9.8 | 12.0652 | 1683.85 | 368.9116 | 2052.7616 | 1 | 2000 | 52.7616 | 2.6381 | 82.0285 | 15.8075 | 14.302 | 81.5544 | 17.9715 | 3.1334
282 | 14 | October | 9.8 | 12.0652 | 1683.85 | 183.897 | 1867.747 | 0 | 1867.747 | 0 | 0 | 90.1541 | 9.8459 | 0 | 90.1541 | 9.8459 | 0
282 | 15 | October | 10.3 | 12.6808 | 1694.9 | 134.946 | 1829.846 | 0 | 1829.846 | 0 | 0 | 92.6253 | 7.3747 | 0 | 92.6253 | 7.3747 | 0
282 | 16 | October | 10.3 | 12.6808 | 1694.9 | 121.2548 | 1816.1548 | 0 | 1816.1548 | 0 | 0 | 93.3235 | 6.6765 | 0 | 93.3235 | 6.6765 | 0
282 | 17 | October | 10.3 | 12.6808 | 1694.9 | 18.522 | 1713.422 | 0 | 1713.422 | 0 | 0 | 98.919 | 1.081 | 0 | 98.919 | 1.081 | 0
282 | 18 | October | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
282 | 19 | October | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
282 | 20 | October | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
282 | 21 | October | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
282 | 22 | October | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
282 | 23 | October | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
282 | 24 | October | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
283 | 1 | October | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
283 | 2 | October | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
283 | 3 | October | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
283 | 4 | October | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
283 | 5 | October | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
283 | 6 | October | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
283 | 7 | October | 7.7 | 9.4798 | 1059.95 | 7.938 | 1067.888 | 0 | 1067.888 | 0 | 0 | 99.2567 | 0.74334 | 0 | 99.2567 | 0.74334 | 0
283 | 8 | October | 7.7 | 9.4798 | 1059.95 | 51.597 | 1111.547 | 0 | 1111.547 | 0 | 0 | 95.3581 | 4.6419 | 0 | 95.3581 | 4.6419 | 0
283 | 9 | October | 8.2 | 10.0954 | 1359.15 | 112.455 | 1471.605 | 0 | 1471.605 | 0 | 0 | 92.3583 | 7.6417 | 0 | 92.3583 | 7.6417 | 0
283 | 10 | October | 10.3 | 12.6808 | 1694.9 | 457.541 | 2152.441 | 1 | 2000 | 152.441 | 7.6221 | 78.7432 | 15.255 | 33.3175 | 77.1229 | 21.2568 | 8.9941
283 | 11 | October | 8.7 | 10.711 | 1490.05 | 507.6242 | 1997.6742 | 0 | 1997.6742 | 0 | 0 | 74.5892 | 25.4108 | 0 | 74.5892 | 25.4108 | 0
283 | 12 | October | 9.3 | 11.4496 | 1598.85 | 400.0942 | 1998.9442 | 0 | 1998.9442 | 0 | 0 | 79.9847 | 20.0153 | 0 | 79.9847 | 20.0153 | 0
283 | 13 | October | 10.3 | 12.6808 | 1694.9 | 364.6081 | 2059.5081 | 1 | 2000 | 59.5081 | 2.9754 | 82.2964 | 15.255 | 16.3211 | 81.7696 | 17.7036 | 3.511
283 | 14 | October | 9.3 | 11.4496 | 1598.85 | 179.928 | 1778.778 | 0 | 1778.778 | 0 | 0 | 89.8847 | 10.1153 | 0 | 89.8847 | 10.1153 | 0
283 | 15 | October | 9.8 | 12.0652 | 1683.85 | 132.3 | 1816.15 | 0 | 1816.15 | 0 | 0 | 92.7154 | 7.2846 | 0 | 92.7154 | 7.2846 | 0
283 | 16 | October | 8.2 | 10.0954 | 1359.15 | 72.765 | 1431.915 | 0 | 1431.915 | 0 | 0 | 94.9183 | 5.0817 | 0 | 94.9183 | 5.0817 | 0
283 | 17 | October | 10.3 | 12.6808 | 1694.9 | 15.876 | 1710.776 | 0 | 1710.776 | 0 | 0 | 99.072 | 0.928 | 0 | 99.072 | 0.928 | 0
283 | 18 | October | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
283 | 19 | October | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
283 | 20 | October | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
283 | 21 | October | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
283 | 22 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
283 | 23 | October | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
283 | 24 | October | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
284 | 1 | October | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
284 | 2 | October | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
284 | 3 | October | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
284 | 4 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
284 | 5 | October | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
284 | 6 | October | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
284 | 7 | October | 4.6 | 5.6633 | 237.15 | 21.168 | 258.318 | 0 | 258.318 | 0 | 0 | 91.8054 | 8.1946 | 0 | 91.8054 | 8.1946 | 0
284 | 8 | October | 6.7 | 8.2487 | 761.6 | 230.4077 | 992.0077 | 0 | 992.0077 | 0 | 0 | 76.7736 | 23.2264 | 0 | 76.7736 | 23.2264 | 0
284 | 9 | October | 6.7 | 8.2487 | 761.6 | 595.7222 | 1357.3222 | 0 | 1357.3222 | 0 | 0 | 56.1105 | 43.8895 | 0 | 56.1105 | 43.8895 | 0
284 | 10 | October | 7.2 | 8.8642 | 908.65 | 877.8238 | 1786.4738 | 0 | 1786.4738 | 0 | 0 | 50.8628 | 49.1372 | 0 | 50.8628 | 49.1372 | 0
284 | 11 | October | 7.2 | 8.8642 | 908.65 | 1075.4819 | 1984.1319 | 0 | 1984.1319 | 0 | 0 | 45.7958 | 54.2042 | 0 | 45.7958 | 54.2042 | 0
284 | 12 | October | 7.2 | 8.8642 | 908.65 | 1105.1235 | 2013.7735 | 1 | 2000 | 13.7735 | 0.68867 | 45.1218 | 54.5675 | 1.2463 | 44.7438 | 54.8782 | 1.5158
284 | 13 | October | 6.2 | 7.6331 | 625.6 | 978.9883 | 1604.5883 | 0 | 1604.5883 | 0 | 0 | 38.9882 | 61.0118 | 0 | 38.9882 | 61.0118 | 0
284 | 14 | October | 4.6 | 5.6633 | 237.15 | 321.4399 | 558.5899 | 0 | 558.5899 | 0 | 0 | 42.4551 | 57.5449 | 0 | 42.4551 | 57.5449 | 0
284 | 15 | October | 5.7 | 7.0175 | 504.9 | 327.258 | 832.158 | 0 | 832.158 | 0 | 0 | 60.6736 | 39.3264 | 0 | 60.6736 | 39.3264 | 0
284 | 16 | October | 4.1 | 5.0477 | 173.4 | 238.4179 | 411.8179 | 0 | 411.8179 | 0 | 0 | 42.106 | 57.894 | 0 | 42.106 | 57.894 | 0
284 | 17 | October | 3.1 | 3.8165 | 0 | 35.721 | 35.721 | 0 | 35.721 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
284 | 18 | October | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
284 | 19 | October | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
284 | 20 | October | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
284 | 21 | October | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
284 | 22 | October | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
284 | 23 | October | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
284 | 24 | October | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
285 | 1 | October | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
285 | 2 | October | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
285 | 3 | October | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
285 | 4 | October | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
285 | 5 | October | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
285 | 6 | October | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
285 | 7 | October | 1.5 | 1.8467 | 0 | 18.522 | 18.522 | 0 | 18.522 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
285 | 8 | October | 2.6 | 3.201 | 0 | 225.0943 | 225.0943 | 0 | 225.0943 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
285 | 9 | October | 3.1 | 3.8165 | 0 | 593.3069 | 593.3069 | 0 | 593.3069 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
285 | 10 | October | 4.1 | 5.0477 | 173.4 | 303.4168 | 476.8168 | 0 | 476.8168 | 0 | 0 | 36.3662 | 63.6338 | 0 | 36.3662 | 63.6338 | 0
285 | 11 | October | 5.1 | 6.2788 | 312.8 | 547.1582 | 859.9582 | 0 | 859.9582 | 0 | 0 | 36.3739 | 63.6261 | 0 | 36.3739 | 63.6261 | 0
285 | 12 | October | 5.1 | 6.2788 | 312.8 | 530.8009 | 843.6009 | 0 | 843.6009 | 0 | 0 | 37.0791 | 62.9209 | 0 | 37.0791 | 62.9209 | 0
285 | 13 | October | 4.1 | 5.0477 | 173.4 | 373.4341 | 546.8341 | 0 | 546.8341 | 0 | 0 | 31.7098 | 68.2902 | 0 | 31.7098 | 68.2902 | 0
285 | 14 | October | 4.6 | 5.6633 | 237.15 | 661.7964 | 898.9464 | 0 | 898.9464 | 0 | 0 | 26.3809 | 73.6191 | 0 | 26.3809 | 73.6191 | 0
285 | 15 | October | 5.1 | 6.2788 | 312.8 | 564.0489 | 876.8489 | 0 | 876.8489 | 0 | 0 | 35.6732 | 64.3268 | 0 | 35.6732 | 64.3268 | 0
285 | 16 | October | 3.6 | 4.4321 | 75.65 | 266.329 | 341.979 | 0 | 341.979 | 0 | 0 | 22.1212 | 77.8788 | 0 | 22.1212 | 77.8788 | 0
285 | 17 | October | 2.6 | 3.201 | 0 | 40.2957 | 40.2957 | 0 | 40.2957 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
285 | 18 | October | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
285 | 19 | October | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
285 | 20 | October | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
285 | 21 | October | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
285 | 22 | October | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
285 | 23 | October | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
285 | 24 | October | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
286 | 1 | October | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
286 | 2 | October | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
286 | 3 | October | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
286 | 4 | October | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
286 | 5 | October | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
286 | 6 | October | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
286 | 7 | October | 1.5 | 1.8467 | 0 | 6.615 | 6.615 | 0 | 6.615 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
286 | 8 | October | 1.5 | 1.8467 | 0 | 74.088 | 74.088 | 0 | 74.088 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
286 | 9 | October | 0 | 0 | 0 | 303.7755 | 303.7755 | 0 | 303.7755 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
286 | 10 | October | 4.1 | 5.0477 | 173.4 | 669.8972 | 843.2972 | 0 | 843.2972 | 0 | 0 | 20.5621 | 79.4379 | 0 | 20.5621 | 79.4379 | 0
286 | 11 | October | 4.6 | 5.6633 | 237.15 | 721.5187 | 958.6687 | 0 | 958.6687 | 0 | 0 | 24.7374 | 75.2626 | 0 | 24.7374 | 75.2626 | 0
286 | 12 | October | 4.6 | 5.6633 | 237.15 | 734.0531 | 971.2031 | 0 | 971.2031 | 0 | 0 | 24.4182 | 75.5818 | 0 | 24.4182 | 75.5818 | 0
286 | 13 | October | 4.1 | 5.0477 | 173.4 | 539.2578 | 712.6578 | 0 | 712.6578 | 0 | 0 | 24.3315 | 75.6685 | 0 | 24.3315 | 75.6685 | 0
286 | 14 | October | 4.6 | 5.6633 | 237.15 | 415.9499 | 653.0999 | 0 | 653.0999 | 0 | 0 | 36.3114 | 63.6886 | 0 | 36.3114 | 63.6886 | 0
286 | 15 | October | 6.7 | 8.2487 | 761.6 | 472.2517 | 1233.8517 | 0 | 1233.8517 | 0 | 0 | 61.7254 | 38.2746 | 0 | 61.7254 | 38.2746 | 0
286 | 16 | October | 5.7 | 7.0175 | 504.9 | 243.2816 | 748.1816 | 0 | 748.1816 | 0 | 0 | 67.4836 | 32.5164 | 0 | 67.4836 | 32.5164 | 0
286 | 17 | October | 3.6 | 4.4321 | 75.65 | 36.6814 | 112.3314 | 0 | 112.3314 | 0 | 0 | 67.3454 | 32.6546 | 0 | 67.3454 | 32.6546 | 0
286 | 18 | October | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
286 | 19 | October | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
286 | 20 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
286 | 21 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
286 | 22 | October | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
286 | 23 | October | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
286 | 24 | October | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
287 | 1 | October | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
287 | 2 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
287 | 3 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
287 | 4 | October | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
287 | 5 | October | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
287 | 6 | October | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
287 | 7 | October | 4.1 | 5.0477 | 173.4 | 15.876 | 189.276 | 0 | 189.276 | 0 | 0 | 91.6122 | 8.3878 | 0 | 91.6122 | 8.3878 | 0
287 | 8 | October | 5.1 | 6.2788 | 312.8 | 208.053 | 520.853 | 0 | 520.853 | 0 | 0 | 60.0553 | 39.9447 | 0 | 60.0553 | 39.9447 | 0
287 | 9 | October | 4.6 | 5.6633 | 237.15 | 580.5098 | 817.6598 | 0 | 817.6598 | 0 | 0 | 29.0035 | 70.9965 | 0 | 29.0035 | 70.9965 | 0
287 | 10 | October | 5.7 | 7.0175 | 504.9 | 846.4376 | 1351.3376 | 0 | 1351.3376 | 0 | 0 | 37.363 | 62.637 | 0 | 37.363 | 62.637 | 0
287 | 11 | October | 6.2 | 7.6331 | 625.6 | 1047.6215 | 1673.2215 | 0 | 1673.2215 | 0 | 0 | 37.389 | 62.611 | 0 | 37.389 | 62.611 | 0
287 | 12 | October | 6.7 | 8.2487 | 761.6 | 1078.8677 | 1840.4677 | 0 | 1840.4677 | 0 | 0 | 41.3808 | 58.6192 | 0 | 41.3808 | 58.6192 | 0
287 | 13 | October | 6.7 | 8.2487 | 761.6 | 550.0017 | 1311.6017 | 0 | 1311.6017 | 0 | 0 | 58.0664 | 41.9336 | 0 | 58.0664 | 41.9336 | 0
287 | 14 | October | 5.7 | 7.0175 | 504.9 | 306.2079 | 811.1079 | 0 | 811.1079 | 0 | 0 | 62.2482 | 37.7518 | 0 | 62.2482 | 37.7518 | 0
287 | 15 | October | 4.6 | 5.6633 | 237.15 | 200.609 | 437.759 | 0 | 437.759 | 0 | 0 | 54.1736 | 45.8264 | 0 | 54.1736 | 45.8264 | 0
287 | 16 | October | 4.6 | 5.6633 | 237.15 | 100.748 | 337.898 | 0 | 337.898 | 0 | 0 | 70.1839 | 29.8161 | 0 | 70.1839 | 29.8161 | 0
287 | 17 | October | 3.1 | 3.8165 | 0 | 11.907 | 11.907 | 0 | 11.907 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
287 | 18 | October | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
287 | 19 | October | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
287 | 20 | October | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
287 | 21 | October | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
287 | 22 | October | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
287 | 23 | October | 11.8 | 14.5275 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
287 | 24 | October | 12.3 | 15.1431 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
288 | 1 | October | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
288 | 2 | October | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
288 | 3 | October | 11.8 | 14.5275 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
288 | 4 | October | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
288 | 5 | October | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
288 | 6 | October | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
288 | 7 | October | 10.3 | 12.6808 | 1694.9 | 10.584 | 1705.484 | 0 | 1705.484 | 0 | 0 | 99.3794 | 0.62059 | 0 | 99.3794 | 0.62059 | 0
288 | 8 | October | 7.7 | 9.4798 | 1059.95 | 68.796 | 1128.746 | 0 | 1128.746 | 0 | 0 | 93.9051 | 6.0949 | 0 | 93.9051 | 6.0949 | 0
288 | 9 | October | 10.3 | 12.6808 | 1694.9 | 174.3621 | 1869.2621 | 0 | 1869.2621 | 0 | 0 | 90.6721 | 9.3279 | 0 | 90.6721 | 9.3279 | 0
288 | 10 | October | 9.8 | 12.0652 | 1683.85 | 264.5287 | 1948.3787 | 0 | 1948.3787 | 0 | 0 | 86.4231 | 13.5769 | 0 | 86.4231 | 13.5769 | 0
288 | 11 | October | 8.7 | 10.711 | 1490.05 | 337.4677 | 1827.5177 | 0 | 1827.5177 | 0 | 0 | 81.5341 | 18.4659 | 0 | 81.5341 | 18.4659 | 0
288 | 12 | October | 7.7 | 9.4798 | 1059.95 | 361.9379 | 1421.8879 | 0 | 1421.8879 | 0 | 0 | 74.5453 | 25.4547 | 0 | 74.5453 | 25.4547 | 0
288 | 13 | October | 6.2 | 7.6331 | 625.6 | 344.8189 | 970.4189 | 0 | 970.4189 | 0 | 0 | 64.467 | 35.533 | 0 | 64.467 | 35.533 | 0
288 | 14 | October | 3.6 | 4.4321 | 75.65 | 168.021 | 243.671 | 0 | 243.671 | 0 | 0 | 31.046 | 68.954 | 0 | 31.046 | 68.954 | 0
288 | 15 | October | 1.5 | 1.8467 | 0 | 119.07 | 119.07 | 0 | 119.07 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
288 | 16 | October | 1 | 1.2311 | 0 | 59.535 | 59.535 | 0 | 59.535 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
288 | 17 | October | 6.2 | 7.6331 | 625.6 | 10.584 | 636.184 | 0 | 636.184 | 0 | 0 | 98.3363 | 1.6637 | 0 | 98.3363 | 1.6637 | 0
288 | 18 | October | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
288 | 19 | October | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
288 | 20 | October | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
288 | 21 | October | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
288 | 22 | October | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
288 | 23 | October | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
288 | 24 | October | 12.9 | 15.8818 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
289 | 1 | October | 13.4 | 16.4973 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
289 | 2 | October | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
289 | 3 | October | 13.4 | 16.4973 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
289 | 4 | October | 16.4 | 20.1908 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
289 | 5 | October | 23.1 | 28.4394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
289 | 6 | October | 22.6 | 27.8239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
289 | 7 | October | 22.6 | 27.8239 | 0 | 5.292 | 5.292 | 0 | 5.292 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
289 | 8 | October | 21.1 | 25.9771 | 0 | 41.013 | 41.013 | 0 | 41.013 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
289 | 9 | October | 14.9 | 18.3441 | 1700 | 291.7772 | 1991.7772 | 0 | 1991.7772 | 0 | 0 | 85.3509 | 14.6491 | 0 | 85.3509 | 14.6491 | 0
289 | 10 | October | 19 | 23.3917 | 1700 | 276.4693 | 1976.4693 | 0 | 1976.4693 | 0 | 0 | 86.012 | 13.988 | 0 | 86.012 | 13.988 | 0
289 | 11 | October | 14.9 | 18.3441 | 1700 | 789.9804 | 2489.9804 | 1 | 2000 | 489.9804 | 24.499 | 68.2736 | 15 | 62.0244 | 60.501 | 31.7264 | 28.8224
289 | 12 | October | 14.4 | 17.7285 | 1700 | 1032.3398 | 2732.3398 | 1 | 2000 | 732.3398 | 36.617 | 62.2177 | 15 | 70.9398 | 48.383 | 37.7823 | 43.0788
289 | 13 | October | 12.9 | 15.8818 | 1700 | 1005.0333 | 2705.0333 | 1 | 2000 | 705.0333 | 35.2517 | 62.8458 | 15 | 70.1502 | 49.7483 | 37.1542 | 41.4725
289 | 14 | October | 10.8 | 13.2964 | 1698.3 | 813.3456 | 2511.6456 | 1 | 2000 | 511.6456 | 25.5823 | 67.617 | 15.085 | 62.9063 | 59.3327 | 32.383 | 30.1269
289 | 15 | October | 5.7 | 7.0175 | 504.9 | 216.8012 | 721.7012 | 0 | 721.7012 | 0 | 0 | 69.9597 | 30.0403 | 0 | 69.9597 | 30.0403 | 0
289 | 16 | October | 5.7 | 7.0175 | 504.9 | 93.603 | 598.503 | 0 | 598.503 | 0 | 0 | 84.3605 | 15.6395 | 0 | 84.3605 | 15.6395 | 0
289 | 17 | October | 7.2 | 8.8642 | 908.65 | 15.876 | 924.526 | 0 | 924.526 | 0 | 0 | 98.2828 | 1.7172 | 0 | 98.2828 | 1.7172 | 0
289 | 18 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
289 | 19 | October | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
289 | 20 | October | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
289 | 21 | October | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
289 | 22 | October | 5.9 | 7.2638 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
289 | 23 | October | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
289 | 24 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
290 | 1 | October | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
290 | 2 | October | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
290 | 3 | October | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
290 | 4 | October | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
290 | 5 | October | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
290 | 6 | October | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
290 | 7 | October | 6.7 | 8.2487 | 761.6 | 3.969 | 765.569 | 0 | 765.569 | 0 | 0 | 99.4816 | 0.51844 | 0 | 99.4816 | 0.51844 | 0
290 | 8 | October | 2.1 | 2.5854 | 0 | 111.129 | 111.129 | 0 | 111.129 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
290 | 9 | October | 5.1 | 6.2788 | 312.8 | 352.0907 | 664.8907 | 0 | 664.8907 | 0 | 0 | 47.0453 | 52.9547 | 0 | 47.0453 | 52.9547 | 0
290 | 10 | October | 6.2 | 7.6331 | 625.6 | 765.7457 | 1391.3457 | 0 | 1391.3457 | 0 | 0 | 44.9637 | 55.0363 | 0 | 44.9637 | 55.0363 | 0
290 | 11 | October | 6.2 | 7.6331 | 625.6 | 346.0504 | 971.6504 | 0 | 971.6504 | 0 | 0 | 64.3853 | 35.6147 | 0 | 64.3853 | 35.6147 | 0
290 | 12 | October | 6.2 | 7.6331 | 625.6 | 544.773 | 1170.373 | 0 | 1170.373 | 0 | 0 | 53.453 | 46.547 | 0 | 53.453 | 46.547 | 0
290 | 13 | October | 5.1 | 6.2788 | 312.8 | 470.4066 | 783.2066 | 0 | 783.2066 | 0 | 0 | 39.9384 | 60.0616 | 0 | 39.9384 | 60.0616 | 0
290 | 14 | October | 6.2 | 7.6331 | 625.6 | 677.983 | 1303.583 | 0 | 1303.583 | 0 | 0 | 47.9908 | 52.0092 | 0 | 47.9908 | 52.0092 | 0
290 | 15 | October | 6.2 | 7.6331 | 625.6 | 480.4981 | 1106.0981 | 0 | 1106.0981 | 0 | 0 | 56.5592 | 43.4408 | 0 | 56.5592 | 43.4408 | 0
290 | 16 | October | 3.1 | 3.8165 | 0 | 222.5038 | 222.5038 | 0 | 222.5038 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
290 | 17 | October | 3.6 | 4.4321 | 75.65 | 26.46 | 102.11 | 0 | 102.11 | 0 | 0 | 74.0868 | 25.9132 | 0 | 74.0868 | 25.9132 | 0
290 | 18 | October | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
290 | 19 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
290 | 20 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
290 | 21 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
290 | 22 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
290 | 23 | October | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
290 | 24 | October | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
291 | 1 | October | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
291 | 2 | October | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
291 | 3 | October | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
291 | 4 | October | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
291 | 5 | October | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
291 | 6 | October | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
291 | 7 | October | 7.2 | 8.8642 | 908.65 | 6.615 | 915.265 | 0 | 915.265 | 0 | 0 | 99.2773 | 0.72274 | 0 | 99.2773 | 0.72274 | 0
291 | 8 | October | 8.2 | 10.0954 | 1359.15 | 59.535 | 1418.685 | 0 | 1418.685 | 0 | 0 | 95.8035 | 4.1965 | 0 | 95.8035 | 4.1965 | 0
291 | 9 | October | 9.3 | 11.4496 | 1598.85 | 161.5451 | 1760.3951 | 0 | 1760.3951 | 0 | 0 | 90.8234 | 9.1766 | 0 | 90.8234 | 9.1766 | 0
291 | 10 | October | 9.8 | 12.0652 | 1683.85 | 249.8654 | 1933.7154 | 0 | 1933.7154 | 0 | 0 | 87.0785 | 12.9215 | 0 | 87.0785 | 12.9215 | 0
291 | 11 | October | 10.3 | 12.6808 | 1694.9 | 320.9226 | 2015.8226 | 1 | 2000 | 15.8226 | 0.79113 | 84.0798 | 15.255 | 4.9303 | 83.9539 | 15.9202 | 0.93354
291 | 12 | October | 10.8 | 13.2964 | 1698.3 | 343.9693 | 2042.2693 | 1 | 2000 | 42.2693 | 2.1135 | 83.1575 | 15.085 | 12.2887 | 82.8015 | 16.8425 | 2.4889
291 | 13 | October | 10.8 | 13.2964 | 1698.3 | 506.3469 | 2204.6469 | 1 | 2000 | 204.6469 | 10.2323 | 77.0327 | 15.085 | 40.4163 | 74.6827 | 22.9673 | 12.0501
291 | 14 | October | 9.8 | 12.0652 | 1683.85 | 277.4357 | 1961.2857 | 0 | 1961.2857 | 0 | 0 | 85.8544 | 14.1456 | 0 | 85.8544 | 14.1456 | 0
291 | 15 | October | 10.3 | 12.6808 | 1694.9 | 181.414 | 1876.314 | 0 | 1876.314 | 0 | 0 | 90.3314 | 9.6686 | 0 | 90.3314 | 9.6686 | 0
291 | 16 | October | 9.3 | 11.4496 | 1598.85 | 84.672 | 1683.522 | 0 | 1683.522 | 0 | 0 | 94.9705 | 5.0295 | 0 | 94.9705 | 5.0295 | 0
291 | 17 | October | 9.8 | 12.0652 | 1683.85 | 13.23 | 1697.08 | 0 | 1697.08 | 0 | 0 | 99.2204 | 0.77957 | 0 | 99.2204 | 0.77957 | 0
291 | 18 | October | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
291 | 19 | October | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
291 | 20 | October | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
291 | 21 | October | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
291 | 22 | October | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
291 | 23 | October | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
291 | 24 | October | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
292 | 1 | October | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
292 | 2 | October | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
292 | 3 | October | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
292 | 4 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
292 | 5 | October | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
292 | 6 | October | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
292 | 7 | October | 5.7 | 7.0175 | 504.9 | 6.615 | 511.515 | 0 | 511.515 | 0 | 0 | 98.7068 | 1.2932 | 0 | 98.7068 | 1.2932 | 0
292 | 8 | October | 5.7 | 7.0175 | 504.9 | 56.889 | 561.789 | 0 | 561.789 | 0 | 0 | 89.8736 | 10.1264 | 0 | 89.8736 | 10.1264 | 0
292 | 9 | October | 6.7 | 8.2487 | 761.6 | 158.1762 | 919.7762 | 0 | 919.7762 | 0 | 0 | 82.8028 | 17.1972 | 0 | 82.8028 | 17.1972 | 0
292 | 10 | October | 7.2 | 8.8642 | 908.65 | 250.0553 | 1158.7053 | 0 | 1158.7053 | 0 | 0 | 78.4194 | 21.5806 | 0 | 78.4194 | 21.5806 | 0
292 | 11 | October | 6.7 | 8.2487 | 761.6 | 315.3886 | 1076.9886 | 0 | 1076.9886 | 0 | 0 | 70.7157 | 29.2843 | 0 | 70.7157 | 29.2843 | 0
292 | 12 | October | 7.7 | 9.4798 | 1059.95 | 341.0657 | 1401.0157 | 0 | 1401.0157 | 0 | 0 | 75.6558 | 24.3442 | 0 | 75.6558 | 24.3442 | 0
292 | 13 | October | 6.7 | 8.2487 | 761.6 | 322.7022 | 1084.3022 | 0 | 1084.3022 | 0 | 0 | 70.2387 | 29.7613 | 0 | 70.2387 | 29.7613 | 0
292 | 14 | October | 6.7 | 8.2487 | 761.6 | 256.0856 | 1017.6856 | 0 | 1017.6856 | 0 | 0 | 74.8365 | 25.1635 | 0 | 74.8365 | 25.1635 | 0
292 | 15 | October | 7.7 | 9.4798 | 1059.95 | 177.6372 | 1237.5872 | 0 | 1237.5872 | 0 | 0 | 85.6465 | 14.3535 | 0 | 85.6465 | 14.3535 | 0
292 | 16 | October | 6.2 | 7.6331 | 625.6 | 80.703 | 706.303 | 0 | 706.303 | 0 | 0 | 88.5739 | 11.4261 | 0 | 88.5739 | 11.4261 | 0
292 | 17 | October | 5.1 | 6.2788 | 312.8 | 11.907 | 324.707 | 0 | 324.707 | 0 | 0 | 96.333 | 3.667 | 0 | 96.333 | 3.667 | 0
292 | 18 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
292 | 19 | October | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
292 | 20 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
292 | 21 | October | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
292 | 22 | October | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
292 | 23 | October | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
292 | 24 | October | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
293 | 1 | October | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
293 | 2 | October | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
293 | 3 | October | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
293 | 4 | October | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
293 | 5 | October | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
293 | 6 | October | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
293 | 7 | October | 5.7 | 7.0175 | 504.9 | 5.292 | 510.192 | 0 | 510.192 | 0 | 0 | 98.9627 | 1.0373 | 0 | 98.9627 | 1.0373 | 0
293 | 8 | October | 6.7 | 8.2487 | 761.6 | 34.398 | 795.998 | 0 | 795.998 | 0 | 0 | 95.6786 | 4.3214 | 0 | 95.6786 | 4.3214 | 0
293 | 9 | October | 6.2 | 7.6331 | 625.6 | 89.964 | 715.564 | 0 | 715.564 | 0 | 0 | 87.4275 | 12.5725 | 0 | 87.4275 | 12.5725 | 0
293 | 10 | October | 5.7 | 7.0175 | 504.9 | 140.238 | 645.138 | 0 | 645.138 | 0 | 0 | 78.2623 | 21.7377 | 0 | 78.2623 | 21.7377 | 0
293 | 11 | October | 7.2 | 8.8642 | 908.65 | 175.959 | 1084.609 | 0 | 1084.609 | 0 | 0 | 83.7767 | 16.2233 | 0 | 83.7767 | 16.2233 | 0
293 | 12 | October | 5.7 | 7.0175 | 504.9 | 189.189 | 694.089 | 0 | 694.089 | 0 | 0 | 72.7428 | 27.2572 | 0 | 72.7428 | 27.2572 | 0
293 | 13 | October | 6.2 | 7.6331 | 625.6 | 181.251 | 806.851 | 0 | 806.851 | 0 | 0 | 77.536 | 22.464 | 0 | 77.536 | 22.464 | 0
293 | 14 | October | 7.2 | 8.8642 | 908.65 | 150.822 | 1059.472 | 0 | 1059.472 | 0 | 0 | 85.7644 | 14.2356 | 0 | 85.7644 | 14.2356 | 0
293 | 15 | October | 7.7 | 9.4798 | 1059.95 | 104.517 | 1164.467 | 0 | 1164.467 | 0 | 0 | 91.0245 | 8.9755 | 0 | 91.0245 | 8.9755 | 0
293 | 16 | October | 6.7 | 8.2487 | 761.6 | 76.734 | 838.334 | 0 | 838.334 | 0 | 0 | 90.8468 | 9.1532 | 0 | 90.8468 | 9.1532 | 0
293 | 17 | October | 6.2 | 7.6331 | 625.6 | 11.907 | 637.507 | 0 | 637.507 | 0 | 0 | 98.1323 | 1.8677 | 0 | 98.1323 | 1.8677 | 0
293 | 18 | October | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
293 | 19 | October | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
293 | 20 | October | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
293 | 21 | October | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
293 | 22 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
293 | 23 | October | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
293 | 24 | October | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
294 | 1 | October | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
294 | 2 | October | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
294 | 3 | October | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
294 | 4 | October | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
294 | 5 | October | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
294 | 6 | October | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
294 | 7 | October | 7.2 | 8.8642 | 908.65 | 2.646 | 911.296 | 0 | 911.296 | 0 | 0 | 99.7096 | 0.29036 | 0 | 99.7096 | 0.29036 | 0
294 | 8 | October | 5.7 | 7.0175 | 504.9 | 31.752 | 536.652 | 0 | 536.652 | 0 | 0 | 94.0833 | 5.9167 | 0 | 94.0833 | 5.9167 | 0
294 | 9 | October | 5.1 | 6.2788 | 312.8 | 155.6687 | 468.4687 | 0 | 468.4687 | 0 | 0 | 66.7707 | 33.2293 | 0 | 66.7707 | 33.2293 | 0
294 | 10 | October | 7.2 | 8.8642 | 908.65 | 397.2494 | 1305.8994 | 0 | 1305.8994 | 0 | 0 | 69.5804 | 30.4196 | 0 | 69.5804 | 30.4196 | 0
294 | 11 | October | 7.2 | 8.8642 | 908.65 | 654.5749 | 1563.2249 | 0 | 1563.2249 | 0 | 0 | 58.1266 | 41.8734 | 0 | 58.1266 | 41.8734 | 0
294 | 12 | October | 7.7 | 9.4798 | 1059.95 | 828.161 | 1888.111 | 0 | 1888.111 | 0 | 0 | 56.1381 | 43.8619 | 0 | 56.1381 | 43.8619 | 0
294 | 13 | October | 7.2 | 8.8642 | 908.65 | 742.3863 | 1651.0363 | 0 | 1651.0363 | 0 | 0 | 55.0351 | 44.9649 | 0 | 55.0351 | 44.9649 | 0
294 | 14 | October | 4.6 | 5.6633 | 237.15 | 407.275 | 644.425 | 0 | 644.425 | 0 | 0 | 36.8002 | 63.1998 | 0 | 36.8002 | 63.1998 | 0
294 | 15 | October | 6.7 | 8.2487 | 761.6 | 264.3595 | 1025.9595 | 0 | 1025.9595 | 0 | 0 | 74.233 | 25.767 | 0 | 74.233 | 25.767 | 0
294 | 16 | October | 7.2 | 8.8642 | 908.65 | 74.088 | 982.738 | 0 | 982.738 | 0 | 0 | 92.4611 | 7.5389 | 0 | 92.4611 | 7.5389 | 0
294 | 17 | October | 6.2 | 7.6331 | 625.6 | 13.23 | 638.83 | 0 | 638.83 | 0 | 0 | 97.929 | 2.071 | 0 | 97.929 | 2.071 | 0
294 | 18 | October | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
294 | 19 | October | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
294 | 20 | October | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
294 | 21 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
294 | 22 | October | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
294 | 23 | October | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
294 | 24 | October | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
295 | 1 | October | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
295 | 2 | October | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
295 | 3 | October | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
295 | 4 | October | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
295 | 5 | October | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
295 | 6 | October | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
295 | 7 | October | 3.6 | 4.4321 | 75.65 | 6.615 | 82.265 | 0 | 82.265 | 0 | 0 | 91.9589 | 8.0411 | 0 | 91.9589 | 8.0411 | 0
295 | 8 | October | 3.6 | 4.4321 | 75.65 | 160.8006 | 236.4506 | 0 | 236.4506 | 0 | 0 | 31.994 | 68.006 | 0 | 31.994 | 68.006 | 0
295 | 9 | October | 3.1 | 3.8165 | 0 | 426.1178 | 426.1178 | 0 | 426.1178 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
295 | 10 | October | 3.6 | 4.4321 | 75.65 | 650.0103 | 725.6603 | 0 | 725.6603 | 0 | 0 | 10.425 | 89.575 | 0 | 10.425 | 89.575 | 0
295 | 11 | October | 4.1 | 5.0477 | 173.4 | 878.0802 | 1051.4802 | 0 | 1051.4802 | 0 | 0 | 16.491 | 83.509 | 0 | 16.491 | 83.509 | 0
295 | 12 | October | 4.6 | 5.6633 | 237.15 | 997.3692 | 1234.5192 | 0 | 1234.5192 | 0 | 0 | 19.2099 | 80.7901 | 0 | 19.2099 | 80.7901 | 0
295 | 13 | October | 4.1 | 5.0477 | 173.4 | 871.4798 | 1044.8798 | 0 | 1044.8798 | 0 | 0 | 16.5952 | 83.4048 | 0 | 16.5952 | 83.4048 | 0
295 | 14 | October | 3.6 | 4.4321 | 75.65 | 655.6805 | 731.3305 | 0 | 731.3305 | 0 | 0 | 10.3442 | 89.6558 | 0 | 10.3442 | 89.6558 | 0
295 | 15 | October | 3.1 | 3.8165 | 0 | 403.3851 | 403.3851 | 0 | 403.3851 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
295 | 16 | October | 1.5 | 1.8467 | 0 | 169.121 | 169.121 | 0 | 169.121 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
295 | 17 | October | 0 | 0 | 0 | 15.876 | 15.876 | 0 | 15.876 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
295 | 18 | October | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
295 | 19 | October | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
295 | 20 | October | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
295 | 21 | October | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
295 | 22 | October | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
295 | 23 | October | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
295 | 24 | October | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
296 | 1 | October | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
296 | 2 | October | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
296 | 3 | October | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
296 | 4 | October | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
296 | 5 | October | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
296 | 6 | October | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
296 | 7 | October | 1 | 1.2311 | 0 | 5.292 | 5.292 | 0 | 5.292 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
296 | 8 | October | 1.5 | 1.8467 | 0 | 142.5879 | 142.5879 | 0 | 142.5879 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
296 | 9 | October | 1 | 1.2311 | 0 | 457.5564 | 457.5564 | 0 | 457.5564 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
296 | 10 | October | 4.1 | 5.0477 | 173.4 | 275.5896 | 448.9896 | 0 | 448.9896 | 0 | 0 | 38.62 | 61.38 | 0 | 38.62 | 61.38 | 0
296 | 11 | October | 4.1 | 5.0477 | 173.4 | 299.9917 | 473.3917 | 0 | 473.3917 | 0 | 0 | 36.6293 | 63.3707 | 0 | 36.6293 | 63.3707 | 0
296 | 12 | October | 4.6 | 5.6633 | 237.15 | 322.9223 | 560.0723 | 0 | 560.0723 | 0 | 0 | 42.3428 | 57.6572 | 0 | 42.3428 | 57.6572 | 0
296 | 13 | October | 4.6 | 5.6633 | 237.15 | 306.0512 | 543.2012 | 0 | 543.2012 | 0 | 0 | 43.6579 | 56.3421 | 0 | 43.6579 | 56.3421 | 0
296 | 14 | October | 4.1 | 5.0477 | 173.4 | 144.207 | 317.607 | 0 | 317.607 | 0 | 0 | 54.5958 | 45.4042 | 0 | 54.5958 | 45.4042 | 0
296 | 15 | October | 4.6 | 5.6633 | 237.15 | 96.579 | 333.729 | 0 | 333.729 | 0 | 0 | 71.0607 | 28.9393 | 0 | 71.0607 | 28.9393 | 0
296 | 16 | October | 3.6 | 4.4321 | 75.65 | 42.336 | 117.986 | 0 | 117.986 | 0 | 0 | 64.1178 | 35.8822 | 0 | 64.1178 | 35.8822 | 0
296 | 17 | October | 4.6 | 5.6633 | 237.15 | 5.292 | 242.442 | 0 | 242.442 | 0 | 0 | 97.8172 | 2.1828 | 0 | 97.8172 | 2.1828 | 0
296 | 18 | October | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
296 | 19 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
296 | 20 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
296 | 21 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
296 | 22 | October | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
296 | 23 | October | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
296 | 24 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
297 | 1 | October | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
297 | 2 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
297 | 3 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
297 | 4 | October | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
297 | 5 | October | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297 | 6 | October | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297 | 7 | October | 4.6 | 5.6633 | 237.15 | 2.646 | 239.796 | 0 | 239.796 | 0 | 0 | 98.8966 | 1.1034 | 0 | 98.8966 | 1.1034 | 0
297 | 8 | October | 4.1 | 5.0477 | 173.4 | 62.6667 | 236.0667 | 0 | 236.0667 | 0 | 0 | 73.4538 | 26.5462 | 0 | 73.4538 | 26.5462 | 0
297 | 9 | October | 5.1 | 6.2788 | 312.8 | 329.8774 | 642.6774 | 0 | 642.6774 | 0 | 0 | 48.6714 | 51.3286 | 0 | 48.6714 | 51.3286 | 0
297 | 10 | October | 5.1 | 6.2788 | 312.8 | 528.161 | 840.961 | 0 | 840.961 | 0 | 0 | 37.1955 | 62.8045 | 0 | 37.1955 | 62.8045 | 0
297 | 11 | October | 4.6 | 5.6633 | 237.15 | 469.7966 | 706.9466 | 0 | 706.9466 | 0 | 0 | 33.5457 | 66.4543 | 0 | 33.5457 | 66.4543 | 0
297 | 12 | October | 4.1 | 5.0477 | 173.4 | 834.9475 | 1008.3475 | 0 | 1008.3475 | 0 | 0 | 17.1965 | 82.8035 | 0 | 17.1965 | 82.8035 | 0
297 | 13 | October | 3.6 | 4.4321 | 75.65 | 899.421 | 975.071 | 0 | 975.071 | 0 | 0 | 7.7584 | 92.2416 | 0 | 7.7584 | 92.2416 | 0
297 | 14 | October | 4.1 | 5.0477 | 173.4 | 713.4869 | 886.8869 | 0 | 886.8869 | 0 | 0 | 19.5515 | 80.4485 | 0 | 19.5515 | 80.4485 | 0
297 | 15 | October | 4.1 | 5.0477 | 173.4 | 454.5756 | 627.9756 | 0 | 627.9756 | 0 | 0 | 27.6125 | 72.3875 | 0 | 27.6125 | 72.3875 | 0
297 | 16 | October | 3.1 | 3.8165 | 0 | 168.4004 | 168.4004 | 0 | 168.4004 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
297 | 17 | October | 1.5 | 1.8467 | 0 | 13.23 | 13.23 | 0 | 13.23 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
297 | 18 | October | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297 | 19 | October | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297 | 20 | October | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297 | 21 | October | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297 | 22 | October | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297 | 23 | October | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297 | 24 | October | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298 | 1 | October | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298 | 2 | October | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298 | 3 | October | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298 | 4 | October | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298 | 5 | October | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298 | 6 | October | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298 | 7 | October | 0 | 0 | 0 | 3.969 | 3.969 | 0 | 3.969 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
298 | 8 | October | 0 | 0 | 0 | 120.8681 | 120.8681 | 0 | 120.8681 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
298 | 9 | October | 1.5 | 1.8467 | 0 | 479.9279 | 479.9279 | 0 | 479.9279 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
298 | 10 | October | 1 | 1.2311 | 0 | 780.0347 | 780.0347 | 0 | 780.0347 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
298 | 11 | October | 1.5 | 1.8467 | 0 | 945.374 | 945.374 | 0 | 945.374 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
298 | 12 | October | 2.6 | 3.201 | 0 | 997.6822 | 997.6822 | 0 | 997.6822 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
298 | 13 | October | 4.1 | 5.0477 | 173.4 | 915.2171 | 1088.6171 | 0 | 1088.6171 | 0 | 0 | 15.9285 | 84.0715 | 0 | 15.9285 | 84.0715 | 0
298 | 14 | October | 4.1 | 5.0477 | 173.4 | 716.3945 | 889.7945 | 0 | 889.7945 | 0 | 0 | 19.4876 | 80.5124 | 0 | 19.4876 | 80.5124 | 0
298 | 15 | October | 3.6 | 4.4321 | 75.65 | 446.5814 | 522.2314 | 0 | 522.2314 | 0 | 0 | 14.4859 | 85.5141 | 0 | 14.4859 | 85.5141 | 0
298 | 16 | October | 3.1 | 3.8165 | 0 | 159.7901 | 159.7901 | 0 | 159.7901 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
298 | 17 | October | 3.1 | 3.8165 | 0 | 11.907 | 11.907 | 0 | 11.907 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
298 | 18 | October | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
298 | 19 | October | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298 | 20 | October | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298 | 21 | October | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298 | 22 | October | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298 | 23 | October | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298 | 24 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
299 | 1 | October | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
299 | 2 | October | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
299 | 3 | October | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
299 | 4 | October | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
299 | 5 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
299 | 6 | October | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
299 | 7 | October | 5.7 | 7.0175 | 504.9 | 2.646 | 507.546 | 0 | 507.546 | 0 | 0 | 99.4787 | 0.52133 | 0 | 99.4787 | 0.52133 | 0
299 | 8 | October | 5.7 | 7.0175 | 504.9 | 95.1636 | 600.0636 | 0 | 600.0636 | 0 | 0 | 84.1411 | 15.8589 | 0 | 84.1411 | 15.8589 | 0
299 | 9 | October | 6.2 | 7.6331 | 625.6 | 131.6113 | 757.2113 | 0 | 757.2113 | 0 | 0 | 82.619 | 17.381 | 0 | 82.619 | 17.381 | 0
299 | 10 | October | 6.2 | 7.6331 | 625.6 | 215.2092 | 840.8092 | 0 | 840.8092 | 0 | 0 | 74.4045 | 25.5955 | 0 | 74.4045 | 25.5955 | 0
299 | 11 | October | 7.2 | 8.8642 | 908.65 | 286.1526 | 1194.8026 | 0 | 1194.8026 | 0 | 0 | 76.0502 | 23.9498 | 0 | 76.0502 | 23.9498 | 0
299 | 12 | October | 6.7 | 8.2487 | 761.6 | 309.0205 | 1070.6205 | 0 | 1070.6205 | 0 | 0 | 71.1363 | 28.8637 | 0 | 71.1363 | 28.8637 | 0
299 | 13 | October | 5.7 | 7.0175 | 504.9 | 165.375 | 670.275 | 0 | 670.275 | 0 | 0 | 75.3273 | 24.6727 | 0 | 75.3273 | 24.6727 | 0
299 | 14 | October | 4.1 | 5.0477 | 173.4 | 136.269 | 309.669 | 0 | 309.669 | 0 | 0 | 55.9953 | 44.0047 | 0 | 55.9953 | 44.0047 | 0
299 | 15 | October | 4.1 | 5.0477 | 173.4 | 89.964 | 263.364 | 0 | 263.364 | 0 | 0 | 65.8404 | 34.1596 | 0 | 65.8404 | 34.1596 | 0
299 | 16 | October | 3.1 | 3.8165 | 0 | 56.889 | 56.889 | 0 | 56.889 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
299 | 17 | October | 4.1 | 5.0477 | 173.4 | 3.969 | 177.369 | 0 | 177.369 | 0 | 0 | 97.7623 | 2.2377 | 0 | 97.7623 | 2.2377 | 0
299 | 18 | October | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
299 | 19 | October | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
299 | 20 | October | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
299 | 21 | October | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
299 | 22 | October | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
299 | 23 | October | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
299 | 24 | October | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
300 | 1 | October | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
300 | 2 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
300 | 3 | October | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
300 | 4 | October | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
300 | 5 | October | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
300 | 6 | October | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
300 | 7 | October | 7.7 | 9.4798 | 1059.95 | 1.323 | 1061.273 | 0 | 1061.273 | 0 | 0 | 99.8753 | 0.12466 | 0 | 99.8753 | 0.12466 | 0
300 | 8 | October | 8.7 | 10.711 | 1490.05 | 22.491 | 1512.541 | 0 | 1512.541 | 0 | 0 | 98.513 | 1.487 | 0 | 98.513 | 1.487 | 0
300 | 9 | October | 8.7 | 10.711 | 1490.05 | 74.088 | 1564.138 | 0 | 1564.138 | 0 | 0 | 95.2633 | 4.7367 | 0 | 95.2633 | 4.7367 | 0
300 | 10 | October | 8.7 | 10.711 | 1490.05 | 123.039 | 1613.089 | 0 | 1613.089 | 0 | 0 | 92.3725 | 7.6275 | 0 | 92.3725 | 7.6275 | 0
300 | 11 | October | 8.2 | 10.0954 | 1359.15 | 156.114 | 1515.264 | 0 | 1515.264 | 0 | 0 | 89.6972 | 10.3028 | 0 | 89.6972 | 10.3028 | 0
300 | 12 | October | 8.2 | 10.0954 | 1359.15 | 318.2907 | 1677.4407 | 0 | 1677.4407 | 0 | 0 | 81.0252 | 18.9748 | 0 | 81.0252 | 18.9748 | 0
300 | 13 | October | 8.2 | 10.0954 | 1359.15 | 161.406 | 1520.556 | 0 | 1520.556 | 0 | 0 | 89.3851 | 10.6149 | 0 | 89.3851 | 10.6149 | 0
300 | 14 | October | 7.2 | 8.8642 | 908.65 | 132.3 | 1040.95 | 0 | 1040.95 | 0 | 0 | 87.2905 | 12.7095 | 0 | 87.2905 | 12.7095 | 0
300 | 15 | October | 6.7 | 8.2487 | 761.6 | 85.995 | 847.595 | 0 | 847.595 | 0 | 0 | 89.8542 | 10.1458 | 0 | 89.8542 | 10.1458 | 0
300 | 16 | October | 7.7 | 9.4798 | 1059.95 | 34.398 | 1094.348 | 0 | 1094.348 | 0 | 0 | 96.8568 | 3.1432 | 0 | 96.8568 | 3.1432 | 0
300 | 17 | October | 6.2 | 7.6331 | 625.6 | 2.646 | 628.246 | 0 | 628.246 | 0 | 0 | 99.5788 | 0.42117 | 0 | 99.5788 | 0.42117 | 0
300 | 18 | October | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
300 | 19 | October | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
300 | 20 | October | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
300 | 21 | October | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
300 | 22 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
300 | 23 | October | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
300 | 24 | October | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
301 | 1 | October | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
301 | 2 | October | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
301 | 3 | October | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
301 | 4 | October | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
301 | 5 | October | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
301 | 6 | October | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
301 | 7 | October | 5.1 | 6.2788 | 312.8 | 1.323 | 314.123 | 0 | 314.123 | 0 | 0 | 99.5788 | 0.42117 | 0 | 99.5788 | 0.42117 | 0
301 | 8 | October | 5.1 | 6.2788 | 312.8 | 21.168 | 333.968 | 0 | 333.968 | 0 | 0 | 93.6617 | 6.3383 | 0 | 93.6617 | 6.3383 | 0
301 | 9 | October | 4.6 | 5.6633 | 237.15 | 125.4614 | 362.6114 | 0 | 362.6114 | 0 | 0 | 65.4006 | 34.5994 | 0 | 65.4006 | 34.5994 | 0
301 | 10 | October | 6.2 | 7.6331 | 625.6 | 205.9289 | 831.5289 | 0 | 831.5289 | 0 | 0 | 75.2349 | 24.7651 | 0 | 75.2349 | 24.7651 | 0
301 | 11 | October | 6.2 | 7.6331 | 625.6 | 453.7393 | 1079.3393 | 0 | 1079.3393 | 0 | 0 | 57.9614 | 42.0386 | 0 | 57.9614 | 42.0386 | 0
301 | 12 | October | 6.2 | 7.6331 | 625.6 | 317.8336 | 943.4336 | 0 | 943.4336 | 0 | 0 | 66.311 | 33.689 | 0 | 66.311 | 33.689 | 0
301 | 13 | October | 6.2 | 7.6331 | 625.6 | 452.774 | 1078.374 | 0 | 1078.374 | 0 | 0 | 58.0133 | 41.9867 | 0 | 58.0133 | 41.9867 | 0
301 | 14 | October | 5.7 | 7.0175 | 504.9 | 328.7158 | 833.6158 | 0 | 833.6158 | 0 | 0 | 60.5675 | 39.4325 | 0 | 60.5675 | 39.4325 | 0
301 | 15 | October | 4.1 | 5.0477 | 173.4 | 300.6766 | 474.0766 | 0 | 474.0766 | 0 | 0 | 36.5764 | 63.4236 | 0 | 36.5764 | 63.4236 | 0
301 | 16 | October | 3.6 | 4.4321 | 75.65 | 92.812 | 168.462 | 0 | 168.462 | 0 | 0 | 44.9063 | 55.0937 | 0 | 44.9063 | 55.0937 | 0
301 | 17 | October | 3.1 | 3.8165 | 0 | 7.938 | 7.938 | 0 | 7.938 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
301 | 18 | October | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
301 | 19 | October | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
301 | 20 | October | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
301 | 21 | October | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
301 | 22 | October | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
301 | 23 | October | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
301 | 24 | October | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
302 | 1 | October | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
302 | 2 | October | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
302 | 3 | October | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
302 | 4 | October | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
302 | 5 | October | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
302 | 6 | October | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
302 | 7 | October | 0 | 0 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
302 | 8 | October | 0 | 0 | 0 | 56.5533 | 56.5533 | 0 | 56.5533 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
302 | 9 | October | 1 | 1.2311 | 0 | 212.6345 | 212.6345 | 0 | 212.6345 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
302 | 10 | October | 3.6 | 4.4321 | 75.65 | 633.6784 | 709.3284 | 0 | 709.3284 | 0 | 0 | 10.665 | 89.335 | 0 | 10.665 | 89.335 | 0
302 | 11 | October | 3.1 | 3.8165 | 0 | 890.5419 | 890.5419 | 0 | 890.5419 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
302 | 12 | October | 2.6 | 3.201 | 0 | 920.3061 | 920.3061 | 0 | 920.3061 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
302 | 13 | October | 3.6 | 4.4321 | 75.65 | 841.9925 | 917.6425 | 0 | 917.6425 | 0 | 0 | 8.244 | 91.756 | 0 | 8.244 | 91.756 | 0
302 | 14 | October | 2.6 | 3.201 | 0 | 652.8384 | 652.8384 | 0 | 652.8384 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
302 | 15 | October | 1.5 | 1.8467 | 0 | 404.8007 | 404.8007 | 0 | 404.8007 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
302 | 16 | October | 2.6 | 3.201 | 0 | 94.9803 | 94.9803 | 0 | 94.9803 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
302 | 17 | October | 2.1 | 2.5854 | 0 | 5.292 | 5.292 | 0 | 5.292 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
302 | 18 | October | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
302 | 19 | October | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
302 | 20 | October | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
302 | 21 | October | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
302 | 22 | October | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
302 | 23 | October | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
302 | 24 | October | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
303 | 1 | October | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
303 | 2 | October | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
303 | 3 | October | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
303 | 4 | October | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
303 | 5 | October | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
303 | 6 | October | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
303 | 7 | October | 2.6 | 3.201 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
303 | 8 | October | 2.1 | 2.5854 | 0 | 37.044 | 37.044 | 0 | 37.044 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
303 | 9 | October | 3.1 | 3.8165 | 0 | 191.1397 | 191.1397 | 0 | 191.1397 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
303 | 10 | October | 3.1 | 3.8165 | 0 | 199.9065 | 199.9065 | 0 | 199.9065 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
303 | 11 | October | 4.1 | 5.0477 | 173.4 | 265.6732 | 439.0732 | 0 | 439.0732 | 0 | 0 | 39.4923 | 60.5077 | 0 | 39.4923 | 60.5077 | 0
303 | 12 | October | 3.1 | 3.8165 | 0 | 162.729 | 162.729 | 0 | 162.729 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
303 | 13 | October | 3.1 | 3.8165 | 0 | 153.468 | 153.468 | 0 | 153.468 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
303 | 14 | October | 3.1 | 3.8165 | 0 | 124.362 | 124.362 | 0 | 124.362 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
303 | 15 | October | 3.6 | 4.4321 | 75.65 | 79.38 | 155.03 | 0 | 155.03 | 0 | 0 | 48.797 | 51.203 | 0 | 48.797 | 51.203 | 0
303 | 16 | October | 4.6 | 5.6633 | 237.15 | 29.106 | 266.256 | 0 | 266.256 | 0 | 0 | 89.0684 | 10.9316 | 0 | 89.0684 | 10.9316 | 0
303 | 17 | October | 3.1 | 3.8165 | 0 | 2.646 | 2.646 | 0 | 2.646 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
303 | 18 | October | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
303 | 19 | October | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
303 | 20 | October | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
303 | 21 | October | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
303 | 22 | October | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
303 | 23 | October | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
303 | 24 | October | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
304 | 1 | October | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
304 | 2 | October | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
304 | 3 | October | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
304 | 4 | October | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
304 | 5 | October | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
304 | 6 | October | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
304 | 7 | October | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
304 | 8 | October | 3.1 | 3.8165 | 0 | 15.876 | 15.876 | 0 | 15.876 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
304 | 9 | October | 3.6 | 4.4321 | 75.65 | 66.15 | 141.8 | 0 | 141.8 | 0 | 0 | 53.3498 | 46.6502 | 0 | 53.3498 | 46.6502 | 0
304 | 10 | October | 2.6 | 3.201 | 0 | 112.455 | 112.455 | 0 | 112.455 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
304 | 11 | October | 3.6 | 4.4321 | 75.65 | 146.853 | 222.503 | 0 | 222.503 | 0 | 0 | 33.9995 | 66.0005 | 0 | 33.9995 | 66.0005 | 0
304 | 12 | October | 3.6 | 4.4321 | 75.65 | 160.083 | 235.733 | 0 | 235.733 | 0 | 0 | 32.0914 | 67.9086 | 0 | 32.0914 | 67.9086 | 0
304 | 13 | October | 4.1 | 5.0477 | 173.4 | 150.822 | 324.222 | 0 | 324.222 | 0 | 0 | 53.4819 | 46.5181 | 0 | 53.4819 | 46.5181 | 0
304 | 14 | October | 3.1 | 3.8165 | 0 | 121.716 | 121.716 | 0 | 121.716 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
304 | 15 | October | 3.1 | 3.8165 | 0 | 76.734 | 76.734 | 0 | 76.734 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
304 | 16 | October | 2.6 | 3.201 | 0 | 26.46 | 26.46 | 0 | 26.46 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
304 | 17 | October | 1.5 | 1.8467 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
304 | 18 | October | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
304 | 19 | October | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
304 | 20 | October | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
304 | 21 | October | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
304 | 22 | October | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
304 | 23 | October | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
304 | 24 | October | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305 | 1 | November | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
305 | 2 | November | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305 | 3 | November | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
305 | 4 | November | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305 | 5 | November | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
305 | 6 | November | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
305 | 7 | November | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305 | 8 | November | 3.6 | 4.4321 | 75.65 | 15.876 | 91.526 | 0 | 91.526 | 0 | 0 | 82.6541 | 17.3459 | 0 | 82.6541 | 17.3459 | 0
305 | 9 | November | 2.1 | 2.5854 | 0 | 63.504 | 63.504 | 0 | 63.504 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
305 | 10 | November | 2.6 | 3.201 | 0 | 111.132 | 111.132 | 0 | 111.132 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
305 | 11 | November | 5.1 | 6.2788 | 312.8 | 144.207 | 457.007 | 0 | 457.007 | 0 | 0 | 68.4453 | 31.5547 | 0 | 68.4453 | 31.5547 | 0
305 | 12 | November | 4.6 | 5.6633 | 237.15 | 300.4693 | 537.6193 | 0 | 537.6193 | 0 | 0 | 44.1111 | 55.8889 | 0 | 44.1111 | 55.8889 | 0
305 | 13 | November | 5.1 | 6.2788 | 312.8 | 263.6321 | 576.4321 | 0 | 576.4321 | 0 | 0 | 54.2649 | 45.7351 | 0 | 54.2649 | 45.7351 | 0
305 | 14 | November | 3.6 | 4.4321 | 75.65 | 207.5786 | 283.2286 | 0 | 283.2286 | 0 | 0 | 26.7099 | 73.2901 | 0 | 26.7099 | 73.2901 | 0
305 | 15 | November | 4.1 | 5.0477 | 173.4 | 123.622 | 297.022 | 0 | 297.022 | 0 | 0 | 58.3795 | 41.6205 | 0 | 58.3795 | 41.6205 | 0
305 | 16 | November | 4.1 | 5.0477 | 173.4 | 41.013 | 214.413 | 0 | 214.413 | 0 | 0 | 80.872 | 19.128 | 0 | 80.872 | 19.128 | 0
305 | 17 | November | 3.1 | 3.8165 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
305 | 18 | November | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
305 | 19 | November | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
305 | 20 | November | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305 | 21 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305 | 22 | November | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305 | 23 | November | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305 | 24 | November | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
306 | 1 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
306 | 2 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
306 | 3 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
306 | 4 | November | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
306 | 5 | November | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
306 | 6 | November | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
306 | 7 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
306 | 8 | November | 0 | 0 | 0 | 14.553 | 14.553 | 0 | 14.553 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
306 | 9 | November | 1 | 1.2311 | 0 | 62.181 | 62.181 | 0 | 62.181 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
306 | 10 | November | 1 | 1.2311 | 0 | 109.809 | 109.809 | 0 | 109.809 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
306 | 11 | November | 1 | 1.2311 | 0 | 520.0168 | 520.0168 | 0 | 520.0168 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
306 | 12 | November | 1 | 1.2311 | 0 | 154.791 | 154.791 | 0 | 154.791 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
306 | 13 | November | 2 | 2.4623 | 0 | 146.853 | 146.853 | 0 | 146.853 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
306 | 14 | November | 3.1 | 3.8165 | 0 | 117.747 | 117.747 | 0 | 117.747 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
306 | 15 | November | 1 | 1.2311 | 0 | 72.765 | 72.765 | 0 | 72.765 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
306 | 16 | November | 2.1 | 2.5854 | 0 | 23.814 | 23.814 | 0 | 23.814 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
306 | 17 | November | 0 | 0 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
306 | 18 | November | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
306 | 19 | November | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
306 | 20 | November | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
306 | 21 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
306 | 22 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
306 | 23 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
306 | 24 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
307 | 1 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
307 | 2 | November | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
307 | 3 | November | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
307 | 4 | November | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
307 | 5 | November | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
307 | 6 | November | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
307 | 7 | November | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
307 | 8 | November | 5.1 | 6.2788 | 312.8 | 14.553 | 327.353 | 0 | 327.353 | 0 | 0 | 95.5543 | 4.4457 | 0 | 95.5543 | 4.4457 | 0
307 | 9 | November | 6.7 | 8.2487 | 761.6 | 59.535 | 821.135 | 0 | 821.135 | 0 | 0 | 92.7497 | 7.2503 | 0 | 92.7497 | 7.2503 | 0
307 | 10 | November | 3.6 | 4.4321 | 75.65 | 105.84 | 181.49 | 0 | 181.49 | 0 | 0 | 41.6827 | 58.3173 | 0 | 41.6827 | 58.3173 | 0
307 | 11 | November | 3.1 | 3.8165 | 0 | 138.915 | 138.915 | 0 | 138.915 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
307 | 12 | November | 3.6 | 4.4321 | 75.65 | 291.917 | 367.567 | 0 | 367.567 | 0 | 0 | 20.5813 | 79.4187 | 0 | 20.5813 | 79.4187 | 0
307 | 13 | November | 4.1 | 5.0477 | 173.4 | 255.4763 | 428.8763 | 0 | 428.8763 | 0 | 0 | 40.4312 | 59.5688 | 0 | 40.4312 | 59.5688 | 0
307 | 14 | November | 3.6 | 4.4321 | 75.65 | 199.7234 | 275.3734 | 0 | 275.3734 | 0 | 0 | 27.4718 | 72.5282 | 0 | 27.4718 | 72.5282 | 0
307 | 15 | November | 4.1 | 5.0477 | 173.4 | 116.2128 | 289.6128 | 0 | 289.6128 | 0 | 0 | 59.873 | 40.127 | 0 | 59.873 | 40.127 | 0
307 | 16 | November | 5.1 | 6.2788 | 312.8 | 35.721 | 348.521 | 0 | 348.521 | 0 | 0 | 89.7507 | 10.2493 | 0 | 89.7507 | 10.2493 | 0
307 | 17 | November | 5.7 | 7.0175 | 504.9 | 1.323 | 506.223 | 0 | 506.223 | 0 | 0 | 99.7387 | 0.26135 | 0 | 99.7387 | 0.26135 | 0
307 | 18 | November | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
307 | 19 | November | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
307 | 20 | November | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
307 | 21 | November | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
307 | 22 | November | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
307 | 23 | November | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
307 | 24 | November | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
308 | 1 | November | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
308 | 2 | November | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
308 | 3 | November | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
308 | 4 | November | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
308 | 5 | November | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
308 | 6 | November | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
308 | 7 | November | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
308 | 8 | November | 5.7 | 7.0175 | 504.9 | 13.23 | 518.13 | 0 | 518.13 | 0 | 0 | 97.4466 | 2.5534 | 0 | 97.4466 | 2.5534 | 0
308 | 9 | November | 4.1 | 5.0477 | 173.4 | 58.212 | 231.612 | 0 | 231.612 | 0 | 0 | 74.8666 | 25.1334 | 0 | 74.8666 | 25.1334 | 0
308 | 10 | November | 5.7 | 7.0175 | 504.9 | 104.517 | 609.417 | 0 | 609.417 | 0 | 0 | 82.8497 | 17.1503 | 0 | 82.8497 | 17.1503 | 0
308 | 11 | November | 4.1 | 5.0477 | 173.4 | 137.592 | 310.992 | 0 | 310.992 | 0 | 0 | 55.7571 | 44.2429 | 0 | 55.7571 | 44.2429 | 0
308 | 12 | November | 4.1 | 5.0477 | 173.4 | 150.822 | 324.222 | 0 | 324.222 | 0 | 0 | 53.4819 | 46.5181 | 0 | 53.4819 | 46.5181 | 0
308 | 13 | November | 4.6 | 5.6633 | 237.15 | 141.561 | 378.711 | 0 | 378.711 | 0 | 0 | 62.6203 | 37.3797 | 0 | 62.6203 | 37.3797 | 0
308 | 14 | November | 5.1 | 6.2788 | 312.8 | 198.5526 | 511.3526 | 0 | 511.3526 | 0 | 0 | 61.1711 | 38.8289 | 0 | 61.1711 | 38.8289 | 0
308 | 15 | November | 3.6 | 4.4321 | 75.65 | 113.538 | 189.188 | 0 | 189.188 | 0 | 0 | 39.9867 | 60.0133 | 0 | 39.9867 | 60.0133 | 0
308 | 16 | November | 5.1 | 6.2788 | 312.8 | 33.075 | 345.875 | 0 | 345.875 | 0 | 0 | 90.4373 | 9.5627 | 0 | 90.4373 | 9.5627 | 0
308 | 17 | November | 4.1 | 5.0477 | 173.4 | 1.323 | 174.723 | 0 | 174.723 | 0 | 0 | 99.2428 | 0.7572 | 0 | 99.2428 | 0.7572 | 0
308 | 18 | November | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
308 | 19 | November | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
308 | 20 | November | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
308 | 21 | November | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
308 | 22 | November | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
308 | 23 | November | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
308 | 24 | November | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
309 | 1 | November | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
309 | 2 | November | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
309 | 3 | November | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
309 | 4 | November | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
309 | 5 | November | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
309 | 6 | November | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
309 | 7 | November | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
309 | 8 | November | 3.6 | 4.4321 | 75.65 | 11.907 | 87.557 | 0 | 87.557 | 0 | 0 | 86.4009 | 13.5991 | 0 | 86.4009 | 13.5991 | 0
309 | 9 | November | 5.1 | 6.2788 | 312.8 | 55.566 | 368.366 | 0 | 368.366 | 0 | 0 | 84.9155 | 15.0845 | 0 | 84.9155 | 15.0845 | 0
309 | 10 | November | 5.1 | 6.2788 | 312.8 | 101.871 | 414.671 | 0 | 414.671 | 0 | 0 | 75.4333 | 24.5667 | 0 | 75.4333 | 24.5667 | 0
309 | 11 | November | 4.6 | 5.6633 | 237.15 | 134.946 | 372.096 | 0 | 372.096 | 0 | 0 | 63.7336 | 36.2664 | 0 | 63.7336 | 36.2664 | 0
309 | 12 | November | 4.1 | 5.0477 | 173.4 | 148.176 | 321.576 | 0 | 321.576 | 0 | 0 | 53.9219 | 46.0781 | 0 | 53.9219 | 46.0781 | 0
309 | 13 | November | 3.6 | 4.4321 | 75.65 | 140.238 | 215.888 | 0 | 215.888 | 0 | 0 | 35.0413 | 64.9587 | 0 | 35.0413 | 64.9587 | 0
309 | 14 | November | 4.1 | 5.0477 | 173.4 | 111.132 | 284.532 | 0 | 284.532 | 0 | 0 | 60.9422 | 39.0578 | 0 | 60.9422 | 39.0578 | 0
309 | 15 | November | 3.1 | 3.8165 | 0 | 67.473 | 67.473 | 0 | 67.473 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
309 | 16 | November | 2.6 | 3.201 | 0 | 19.845 | 19.845 | 0 | 19.845 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
309 | 17 | November | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
309 | 18 | November | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
309 | 19 | November | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
309 | 20 | November | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
309 | 21 | November | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
309 | 22 | November | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
309 | 23 | November | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
309 | 24 | November | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
310 | 1 | November | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
310 | 2 | November | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310 | 3 | November | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310 | 4 | November | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310 | 5 | November | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310 | 6 | November | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310 | 7 | November | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310 | 8 | November | 2.1 | 2.5854 | 0 | 18.522 | 18.522 | 0 | 18.522 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
310 | 9 | November | 2.1 | 2.5854 | 0 | 92.8792 | 92.8792 | 0 | 92.8792 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
310 | 10 | November | 2.6 | 3.201 | 0 | 170.0413 | 170.0413 | 0 | 170.0413 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
310 | 11 | November | 2.1 | 2.5854 | 0 | 238.0643 | 238.0643 | 0 | 238.0643 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
310 | 12 | November | 3.1 | 3.8165 | 0 | 260.6605 | 260.6605 | 0 | 260.6605 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
310 | 13 | November | 3.1 | 3.8165 | 0 | 245.6683 | 245.6683 | 0 | 245.6683 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
310 | 14 | November | 4.6 | 5.6633 | 237.15 | 299.3455 | 536.4955 | 0 | 536.4955 | 0 | 0 | 44.2035 | 55.7965 | 0 | 44.2035 | 55.7965 | 0
310 | 15 | November | 2.1 | 2.5854 | 0 | 109.0092 | 109.0092 | 0 | 109.0092 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
310 | 16 | November | 1.5 | 1.8467 | 0 | 29.106 | 29.106 | 0 | 29.106 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
310 | 17 | November | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310 | 18 | November | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310 | 19 | November | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310 | 20 | November | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310 | 21 | November | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310 | 22 | November | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310 | 23 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310 | 24 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311 | 1 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311 | 2 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311 | 3 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311 | 4 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311 | 5 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311 | 6 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311 | 7 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311 | 8 | November | 0 | 0 | 0 | 10.584 | 10.584 | 0 | 10.584 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
311 | 9 | November | 1.5 | 1.8467 | 0 | 87.4683 | 87.4683 | 0 | 87.4683 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
311 | 10 | November | 2.6 | 3.201 | 0 | 167.3199 | 167.3199 | 0 | 167.3199 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
311 | 11 | November | 3.6 | 4.4321 | 75.65 | 380.6139 | 456.2639 | 0 | 456.2639 | 0 | 0 | 16.5803 | 83.4197 | 0 | 16.5803 | 83.4197 | 0
311 | 12 | November | 3.6 | 4.4321 | 75.65 | 274.0148 | 349.6648 | 0 | 349.6648 | 0 | 0 | 21.635 | 78.365 | 0 | 21.635 | 78.365 | 0
311 | 13 | November | 3.1 | 3.8165 | 0 | 240.3894 | 240.3894 | 0 | 240.3894 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
311 | 14 | November | 3.6 | 4.4321 | 75.65 | 107.163 | 182.813 | 0 | 182.813 | 0 | 0 | 41.3811 | 58.6189 | 0 | 41.3811 | 58.6189 | 0
311 | 15 | November | 2.6 | 3.201 | 0 | 63.504 | 63.504 | 0 | 63.504 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
311 | 16 | November | 1 | 1.2311 | 0 | 17.199 | 17.199 | 0 | 17.199 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
311 | 17 | November | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311 | 18 | November | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311 | 19 | November | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311 | 20 | November | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311 | 21 | November | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311 | 22 | November | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311 | 23 | November | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
311 | 24 | November | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
312 | 1 | November | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312 | 2 | November | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312 | 3 | November | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312 | 4 | November | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
312 | 5 | November | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
312 | 6 | November | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
312 | 7 | November | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
312 | 8 | November | 3.1 | 3.8165 | 0 | 10.584 | 10.584 | 0 | 10.584 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
312 | 9 | November | 3.6 | 4.4321 | 75.65 | 50.274 | 125.924 | 0 | 125.924 | 0 | 0 | 60.0759 | 39.9241 | 0 | 60.0759 | 39.9241 | 0
312 | 10 | November | 3.6 | 4.4321 | 75.65 | 96.579 | 172.229 | 0 | 172.229 | 0 | 0 | 43.9241 | 56.0759 | 0 | 43.9241 | 56.0759 | 0
312 | 11 | November | 4.1 | 5.0477 | 173.4 | 128.331 | 301.731 | 0 | 301.731 | 0 | 0 | 57.4684 | 42.5316 | 0 | 57.4684 | 42.5316 | 0
312 | 12 | November | 3.6 | 4.4321 | 75.65 | 141.561 | 217.211 | 0 | 217.211 | 0 | 0 | 34.8279 | 65.1721 | 0 | 34.8279 | 65.1721 | 0
312 | 13 | November | 4.1 | 5.0477 | 173.4 | 133.623 | 307.023 | 0 | 307.023 | 0 | 0 | 56.4779 | 43.5221 | 0 | 56.4779 | 43.5221 | 0
312 | 14 | November | 1.5 | 1.8467 | 0 | 105.84 | 105.84 | 0 | 105.84 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
312 | 15 | November | 1.5 | 1.8467 | 0 | 62.181 | 62.181 | 0 | 62.181 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
312 | 16 | November | 1 | 1.2311 | 0 | 15.876 | 15.876 | 0 | 15.876 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
312 | 17 | November | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312 | 18 | November | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312 | 19 | November | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312 | 20 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312 | 21 | November | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312 | 22 | November | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312 | 23 | November | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312 | 24 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313 | 1 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313 | 2 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313 | 3 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313 | 4 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313 | 5 | November | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313 | 6 | November | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313 | 7 | November | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
313 | 8 | November | 1 | 1.2311 | 0 | 9.261 | 9.261 | 0 | 9.261 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
313 | 9 | November | 1 | 1.2311 | 0 | 48.951 | 48.951 | 0 | 48.951 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
313 | 10 | November | 1 | 1.2311 | 0 | 93.933 | 93.933 | 0 | 93.933 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
313 | 11 | November | 0 | 0 | 0 | 125.685 | 125.685 | 0 | 125.685 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
313 | 12 | November | 1 | 1.2311 | 0 | 138.915 | 138.915 | 0 | 138.915 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
313 | 13 | November | 0 | 0 | 0 | 130.977 | 130.977 | 0 | 130.977 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
313 | 14 | November | 3.1 | 3.8165 | 0 | 101.871 | 101.871 | 0 | 101.871 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
313 | 15 | November | 3.6 | 4.4321 | 75.65 | 98.8529 | 174.5029 | 0 | 174.5029 | 0 | 0 | 43.3517 | 56.6483 | 0 | 43.3517 | 56.6483 | 0
313 | 16 | November | 4.6 | 5.6633 | 237.15 | 15.876 | 253.026 | 0 | 253.026 | 0 | 0 | 93.7255 | 6.2745 | 0 | 93.7255 | 6.2745 | 0
313 | 17 | November | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
313 | 18 | November | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
313 | 19 | November | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
313 | 20 | November | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
313 | 21 | November | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
313 | 22 | November | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
313 | 23 | November | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
313 | 24 | November | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
314 | 1 | November | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
314 | 2 | November | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
314 | 3 | November | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
314 | 4 | November | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
314 | 5 | November | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
314 | 6 | November | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
314 | 7 | November | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314 | 8 | November | 3.1 | 3.8165 | 0 | 9.261 | 9.261 | 0 | 9.261 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
314 | 9 | November | 3.1 | 3.8165 | 0 | 46.305 | 46.305 | 0 | 46.305 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
314 | 10 | November | 2.1 | 2.5854 | 0 | 91.287 | 91.287 | 0 | 91.287 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
314 | 11 | November | 3.1 | 3.8165 | 0 | 123.039 | 123.039 | 0 | 123.039 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
314 | 12 | November | 1 | 1.2311 | 0 | 136.269 | 136.269 | 0 | 136.269 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
314 | 13 | November | 0 | 0 | 0 | 128.331 | 128.331 | 0 | 128.331 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
314 | 14 | November | 0 | 0 | 0 | 100.548 | 100.548 | 0 | 100.548 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
314 | 15 | November | 1.5 | 1.8467 | 0 | 58.212 | 58.212 | 0 | 58.212 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
314 | 16 | November | 1.5 | 1.8467 | 0 | 14.553 | 14.553 | 0 | 14.553 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
314 | 17 | November | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314 | 18 | November | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314 | 19 | November | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314 | 20 | November | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314 | 21 | November | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314 | 22 | November | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314 | 23 | November | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314 | 24 | November | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
315 | 1 | November | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
315 | 2 | November | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
315 | 3 | November | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
315 | 4 | November | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
315 | 5 | November | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
315 | 6 | November | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
315 | 7 | November | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
315 | 8 | November | 3.1 | 3.8165 | 0 | 22.491 | 22.491 | 0 | 22.491 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
315 | 9 | November | 2.6 | 3.201 | 0 | 71.442 | 71.442 | 0 | 71.442 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
315 | 10 | November | 3.6 | 4.4321 | 75.65 | 151.632 | 227.282 | 0 | 227.282 | 0 | 0 | 33.2846 | 66.7154 | 0 | 33.2846 | 66.7154 | 0
315 | 11 | November | 4.1 | 5.0477 | 173.4 | 120.393 | 293.793 | 0 | 293.793 | 0 | 0 | 59.0211 | 40.9789 | 0 | 59.0211 | 40.9789 | 0
315 | 12 | November | 5.1 | 6.2788 | 312.8 | 133.623 | 446.423 | 0 | 446.423 | 0 | 0 | 70.0681 | 29.9319 | 0 | 70.0681 | 29.9319 | 0
315 | 13 | November | 6.2 | 7.6331 | 625.6 | 125.685 | 751.285 | 0 | 751.285 | 0 | 0 | 83.2707 | 16.7293 | 0 | 83.2707 | 16.7293 | 0
315 | 14 | November | 9.3 | 11.4496 | 1598.85 | 97.902 | 1696.752 | 0 | 1696.752 | 0 | 0 | 94.23 | 5.77 | 0 | 94.23 | 5.77 | 0
315 | 15 | November | 8.7 | 10.711 | 1490.05 | 55.566 | 1545.616 | 0 | 1545.616 | 0 | 0 | 96.4049 | 3.5951 | 0 | 96.4049 | 3.5951 | 0
315 | 16 | November | 8.7 | 10.711 | 1490.05 | 13.23 | 1503.28 | 0 | 1503.28 | 0 | 0 | 99.1199 | 0.88008 | 0 | 99.1199 | 0.88008 | 0
315 | 17 | November | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
315 | 18 | November | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
315 | 19 | November | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
315 | 20 | November | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
315 | 21 | November | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
315 | 22 | November | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
315 | 23 | November | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
315 | 24 | November | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
316 | 1 | November | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
316 | 2 | November | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
316 | 3 | November | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
316 | 4 | November | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
316 | 5 | November | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
316 | 6 | November | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
316 | 7 | November | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
316 | 8 | November | 4.1 | 5.0477 | 173.4 | 11.907 | 185.307 | 0 | 185.307 | 0 | 0 | 93.5744 | 6.4256 | 0 | 93.5744 | 6.4256 | 0
316 | 9 | November | 8.2 | 10.0954 | 1359.15 | 202.5295 | 1561.6795 | 0 | 1561.6795 | 0 | 0 | 87.0313 | 12.9687 | 0 | 87.0313 | 12.9687 | 0
316 | 10 | November | 10.3 | 12.6808 | 1694.9 | 571.4484 | 2266.3484 | 1 | 2000 | 266.3484 | 13.3174 | 74.7855 | 15.255 | 46.6093 | 71.4276 | 25.2145 | 15.7147
316 | 11 | November | 10.3 | 12.6808 | 1694.9 | 641.3466 | 2336.2466 | 1 | 2000 | 336.2466 | 16.8123 | 72.548 | 15.255 | 52.4282 | 67.9327 | 27.452 | 19.8387
316 | 12 | November | 10.3 | 12.6808 | 1694.9 | 575.4274 | 2270.3274 | 1 | 2000 | 270.3274 | 13.5164 | 74.6544 | 15.255 | 46.9785 | 71.2286 | 25.3456 | 15.9495
316 | 13 | November | 10.3 | 12.6808 | 1694.9 | 360.583 | 2055.483 | 1 | 2000 | 55.483 | 2.7742 | 82.4575 | 15.255 | 15.387 | 81.9708 | 17.5425 | 3.2735
316 | 14 | November | 13.4 | 16.4973 | 1700 | 399.6743 | 2099.6743 | 1 | 2000 | 99.6743 | 4.9837 | 80.9649 | 15 | 24.9389 | 80.0163 | 19.0351 | 5.8632
316 | 15 | November | 8.7 | 10.711 | 1490.05 | 145.1477 | 1635.1977 | 0 | 1635.1977 | 0 | 0 | 91.1235 | 8.8765 | 0 | 91.1235 | 8.8765 | 0
316 | 16 | November | 8.7 | 10.711 | 1490.05 | 39.6162 | 1529.6662 | 0 | 1529.6662 | 0 | 0 | 97.4101 | 2.5899 | 0 | 97.4101 | 2.5899 | 0
316 | 17 | November | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
316 | 18 | November | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
316 | 19 | November | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
316 | 20 | November | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
316 | 21 | November | 11.8 | 14.5275 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
316 | 22 | November | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
316 | 23 | November | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
316 | 24 | November | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
317 | 1 | November | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
317 | 2 | November | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
317 | 3 | November | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
317 | 4 | November | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
317 | 5 | November | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
317 | 6 | November | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
317 | 7 | November | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
317 | 8 | November | 6.2 | 7.6331 | 625.6 | 19.845 | 645.445 | 0 | 645.445 | 0 | 0 | 96.9254 | 3.0746 | 0 | 96.9254 | 3.0746 | 0
317 | 9 | November | 6.2 | 7.6331 | 625.6 | 232.6151 | 858.2151 | 0 | 858.2151 | 0 | 0 | 72.8955 | 27.1045 | 0 | 72.8955 | 27.1045 | 0
317 | 10 | November | 5.1 | 6.2788 | 312.8 | 398.156 | 710.956 | 0 | 710.956 | 0 | 0 | 43.9971 | 56.0029 | 0 | 43.9971 | 56.0029 | 0
317 | 11 | November | 4.1 | 5.0477 | 173.4 | 701.5032 | 874.9032 | 0 | 874.9032 | 0 | 0 | 19.8193 | 80.1807 | 0 | 19.8193 | 80.1807 | 0
317 | 12 | November | 4.1 | 5.0477 | 173.4 | 413.2451 | 586.6451 | 0 | 586.6451 | 0 | 0 | 29.5579 | 70.4421 | 0 | 29.5579 | 70.4421 | 0
317 | 13 | November | 2.6 | 3.201 | 0 | 338.883 | 338.883 | 0 | 338.883 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
317 | 14 | November | 3.1 | 3.8165 | 0 | 256.7824 | 256.7824 | 0 | 256.7824 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
317 | 15 | November | 3.6 | 4.4321 | 75.65 | 147.2812 | 222.9312 | 0 | 222.9312 | 0 | 0 | 33.9342 | 66.0658 | 0 | 33.9342 | 66.0658 | 0
317 | 16 | November | 3.1 | 3.8165 | 0 | 30.429 | 30.429 | 0 | 30.429 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
317 | 17 | November | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
317 | 18 | November | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
317 | 19 | November | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
317 | 20 | November | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
317 | 21 | November | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
317 | 22 | November | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
317 | 23 | November | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
317 | 24 | November | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
318 | 1 | November | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
318 | 2 | November | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
318 | 3 | November | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
318 | 4 | November | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
318 | 5 | November | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
318 | 6 | November | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
318 | 7 | November | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
318 | 8 | November | 7.2 | 8.8642 | 908.65 | 18.522 | 927.172 | 0 | 927.172 | 0 | 0 | 98.0023 | 1.9977 | 0 | 98.0023 | 1.9977 | 0
318 | 9 | November | 6.7 | 8.2487 | 761.6 | 228.2834 | 989.8834 | 0 | 989.8834 | 0 | 0 | 76.9384 | 23.0616 | 0 | 76.9384 | 23.0616 | 0
318 | 10 | November | 7.2 | 8.8642 | 908.65 | 568.8672 | 1477.5172 | 0 | 1477.5172 | 0 | 0 | 61.4984 | 38.5016 | 0 | 61.4984 | 38.5016 | 0
318 | 11 | November | 7.7 | 9.4798 | 1059.95 | 642.1586 | 1702.1086 | 0 | 1702.1086 | 0 | 0 | 62.2728 | 37.7272 | 0 | 62.2728 | 37.7272 | 0
318 | 12 | November | 7.7 | 9.4798 | 1059.95 | 553.5134 | 1613.4634 | 0 | 1613.4634 | 0 | 0 | 65.6941 | 34.3059 | 0 | 65.6941 | 34.3059 | 0
318 | 13 | November | 9.8 | 12.0652 | 1683.85 | 673.6656 | 2357.5156 | 1 | 2000 | 357.5156 | 17.8758 | 71.4248 | 15.8075 | 53.0702 | 66.3167 | 28.5752 | 21.232
318 | 14 | November | 9.3 | 11.4496 | 1598.85 | 378.5674 | 1977.4174 | 0 | 1977.4174 | 0 | 0 | 80.8555 | 19.1445 | 0 | 80.8555 | 19.1445 | 0
318 | 15 | November | 6.7 | 8.2487 | 761.6 | 284.9326 | 1046.5326 | 0 | 1046.5326 | 0 | 0 | 72.7737 | 27.2263 | 0 | 72.7737 | 27.2263 | 0
318 | 16 | November | 4.6 | 5.6633 | 237.15 | 30.429 | 267.579 | 0 | 267.579 | 0 | 0 | 88.628 | 11.372 | 0 | 88.628 | 11.372 | 0
318 | 17 | November | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
318 | 18 | November | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
318 | 19 | November | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
318 | 20 | November | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
318 | 21 | November | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
318 | 22 | November | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
318 | 23 | November | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
318 | 24 | November | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
319 | 1 | November | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
319 | 2 | November | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
319 | 3 | November | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
319 | 4 | November | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
319 | 5 | November | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
319 | 6 | November | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
319 | 7 | November | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
319 | 8 | November | 5.1 | 6.2788 | 312.8 | 5.292 | 318.092 | 0 | 318.092 | 0 | 0 | 98.3363 | 1.6637 | 0 | 98.3363 | 1.6637 | 0
319 | 9 | November | 5.7 | 7.0175 | 504.9 | 38.367 | 543.267 | 0 | 543.267 | 0 | 0 | 92.9377 | 7.0623 | 0 | 92.9377 | 7.0623 | 0
319 | 10 | November | 6.2 | 7.6331 | 625.6 | 80.703 | 706.303 | 0 | 706.303 | 0 | 0 | 88.5739 | 11.4261 | 0 | 88.5739 | 11.4261 | 0
319 | 11 | November | 9.3 | 11.4496 | 1598.85 | 112.455 | 1711.305 | 0 | 1711.305 | 0 | 0 | 93.4287 | 6.5713 | 0 | 93.4287 | 6.5713 | 0
319 | 12 | November | 10.8 | 13.2964 | 1698.3 | 125.685 | 1823.985 | 0 | 1823.985 | 0 | 0 | 93.1093 | 6.8907 | 0 | 93.1093 | 6.8907 | 0
319 | 13 | November | 9.3 | 11.4496 | 1598.85 | 117.747 | 1716.597 | 0 | 1716.597 | 0 | 0 | 93.1407 | 6.8593 | 0 | 93.1407 | 6.8593 | 0
319 | 14 | November | 9.3 | 11.4496 | 1598.85 | 91.287 | 1690.137 | 0 | 1690.137 | 0 | 0 | 94.5988 | 5.4012 | 0 | 94.5988 | 5.4012 | 0
319 | 15 | November | 7.2 | 8.8642 | 908.65 | 50.274 | 958.924 | 0 | 958.924 | 0 | 0 | 94.7572 | 5.2428 | 0 | 94.7572 | 5.2428 | 0
319 | 16 | November | 6.2 | 7.6331 | 625.6 | 10.584 | 636.184 | 0 | 636.184 | 0 | 0 | 98.3363 | 1.6637 | 0 | 98.3363 | 1.6637 | 0
319 | 17 | November | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
319 | 18 | November | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
319 | 19 | November | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
319 | 20 | November | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
319 | 21 | November | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
319 | 22 | November | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
319 | 23 | November | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
319 | 24 | November | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
320 | 1 | November | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
320 | 2 | November | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
320 | 3 | November | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
320 | 4 | November | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
320 | 5 | November | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
320 | 6 | November | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
320 | 7 | November | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
320 | 8 | November | 5.1 | 6.2788 | 312.8 | 13.23 | 326.03 | 0 | 326.03 | 0 | 0 | 95.9421 | 4.0579 | 0 | 95.9421 | 4.0579 | 0
320 | 9 | November | 5.7 | 7.0175 | 504.9 | 207.1311 | 712.0311 | 0 | 712.0311 | 0 | 0 | 70.9098 | 29.0902 | 0 | 70.9098 | 29.0902 | 0
320 | 10 | November | 7.7 | 9.4798 | 1059.95 | 258.9914 | 1318.9414 | 0 | 1318.9414 | 0 | 0 | 80.3637 | 19.6363 | 0 | 80.3637 | 19.6363 | 0
320 | 11 | November | 8.2 | 10.0954 | 1359.15 | 593.0434 | 1952.1934 | 0 | 1952.1934 | 0 | 0 | 69.6217 | 30.3783 | 0 | 69.6217 | 30.3783 | 0
320 | 12 | November | 9.8 | 12.0652 | 1683.85 | 775.1554 | 2459.0054 | 1 | 2000 | 459.0054 | 22.9503 | 68.4769 | 15.8075 | 59.2146 | 61.2422 | 31.5231 | 27.2593
320 | 13 | November | 10.3 | 12.6808 | 1694.9 | 661.2384 | 2356.1384 | 1 | 2000 | 356.1384 | 17.8069 | 71.9355 | 15.255 | 53.8593 | 66.9381 | 28.0645 | 21.0124
320 | 14 | November | 9.3 | 11.4496 | 1598.85 | 366.3253 | 1965.1753 | 0 | 1965.1753 | 0 | 0 | 81.3592 | 18.6408 | 0 | 81.3592 | 18.6408 | 0
320 | 15 | November | 7.2 | 8.8642 | 908.65 | 128.2068 | 1036.8568 | 0 | 1036.8568 | 0 | 0 | 87.6351 | 12.3649 | 0 | 87.6351 | 12.3649 | 0
320 | 16 | November | 6.7 | 8.2487 | 761.6 | 29.106 | 790.706 | 0 | 790.706 | 0 | 0 | 96.319 | 3.681 | 0 | 96.319 | 3.681 | 0
320 | 17 | November | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
320 | 18 | November | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
320 | 19 | November | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
320 | 20 | November | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
320 | 21 | November | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
320 | 22 | November | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
320 | 23 | November | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
320 | 24 | November | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
321 | 1 | November | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
321 | 2 | November | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
321 | 3 | November | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
321 | 4 | November | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
321 | 5 | November | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
321 | 6 | November | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
321 | 7 | November | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
321 | 8 | November | 5.1 | 6.2788 | 312.8 | 13.23 | 326.03 | 0 | 326.03 | 0 | 0 | 95.9421 | 4.0579 | 0 | 95.9421 | 4.0579 | 0
321 | 9 | November | 7.2 | 8.8642 | 908.65 | 196.4724 | 1105.1224 | 0 | 1105.1224 | 0 | 0 | 82.2217 | 17.7783 | 0 | 82.2217 | 17.7783 | 0
321 | 10 | November | 8.7 | 10.711 | 1490.05 | 533.6101 | 2023.6601 | 1 | 2000 | 23.6601 | 1.183 | 73.6314 | 25.4975 | 4.434 | 73.3195 | 26.3686 | 1.5879
321 | 11 | November | 8.7 | 10.711 | 1490.05 | 489.1224 | 1979.1724 | 0 | 1979.1724 | 0 | 0 | 75.2865 | 24.7135 | 0 | 75.2865 | 24.7135 | 0
321 | 12 | November | 7.2 | 8.8642 | 908.65 | 362.3264 | 1270.9764 | 0 | 1270.9764 | 0 | 0 | 71.4923 | 28.5077 | 0 | 71.4923 | 28.5077 | 0
321 | 13 | November | 7.2 | 8.8642 | 908.65 | 319.5422 | 1228.1922 | 0 | 1228.1922 | 0 | 0 | 73.9827 | 26.0173 | 0 | 73.9827 | 26.0173 | 0
321 | 14 | November | 6.7 | 8.2487 | 761.6 | 153.55 | 915.15 | 0 | 915.15 | 0 | 0 | 83.2213 | 16.7787 | 0 | 83.2213 | 16.7787 | 0
321 | 15 | November | 6.2 | 7.6331 | 625.6 | 76.0899 | 701.6899 | 0 | 701.6899 | 0 | 0 | 89.1562 | 10.8438 | 0 | 89.1562 | 10.8438 | 0
321 | 16 | November | 5.1 | 6.2788 | 312.8 | 15.876 | 328.676 | 0 | 328.676 | 0 | 0 | 95.1697 | 4.8303 | 0 | 95.1697 | 4.8303 | 0
321 | 17 | November | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
321 | 18 | November | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
321 | 19 | November | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
321 | 20 | November | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
321 | 21 | November | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
321 | 22 | November | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
321 | 23 | November | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
321 | 24 | November | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
322 | 1 | November | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322 | 2 | November | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
322 | 3 | November | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322 | 4 | November | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322 | 5 | November | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322 | 6 | November | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322 | 7 | November | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322 | 8 | November | 2.1 | 2.5854 | 0 | 10.584 | 10.584 | 0 | 10.584 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
322 | 9 | November | 3.6 | 4.4321 | 75.65 | 114.135 | 189.785 | 0 | 189.785 | 0 | 0 | 39.8609 | 60.1391 | 0 | 39.8609 | 60.1391 | 0
322 | 10 | November | 4.6 | 5.6633 | 237.15 | 217.2986 | 454.4486 | 0 | 454.4486 | 0 | 0 | 52.1841 | 47.8159 | 0 | 52.1841 | 47.8159 | 0
322 | 11 | November | 5.1 | 6.2788 | 312.8 | 192.0443 | 504.8443 | 0 | 504.8443 | 0 | 0 | 61.9597 | 38.0403 | 0 | 61.9597 | 38.0403 | 0
322 | 12 | November | 5.7 | 7.0175 | 504.9 | 220.0261 | 724.9261 | 0 | 724.9261 | 0 | 0 | 69.6485 | 30.3515 | 0 | 69.6485 | 30.3515 | 0
322 | 13 | November | 5.1 | 6.2788 | 312.8 | 197.1749 | 509.9749 | 0 | 509.9749 | 0 | 0 | 61.3364 | 38.6636 | 0 | 61.3364 | 38.6636 | 0
322 | 14 | November | 5.1 | 6.2788 | 312.8 | 147.1508 | 459.9508 | 0 | 459.9508 | 0 | 0 | 68.0073 | 31.9927 | 0 | 68.0073 | 31.9927 | 0
322 | 15 | November | 4.6 | 5.6633 | 237.15 | 72.765 | 309.915 | 0 | 309.915 | 0 | 0 | 76.521 | 23.479 | 0 | 76.521 | 23.479 | 0
322 | 16 | November | 4.6 | 5.6633 | 237.15 | 14.553 | 251.703 | 0 | 251.703 | 0 | 0 | 94.2182 | 5.7818 | 0 | 94.2182 | 5.7818 | 0
322 | 17 | November | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
322 | 18 | November | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
322 | 19 | November | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
322 | 20 | November | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
322 | 21 | November | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
322 | 22 | November | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
322 | 23 | November | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
322 | 24 | November | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
323 | 1 | November | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
323 | 2 | November | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
323 | 3 | November | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
323 | 4 | November | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
323 | 5 | November | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
323 | 6 | November | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
323 | 7 | November | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
323 | 8 | November | 3.1 | 3.8165 | 0 | 3.969 | 3.969 | 0 | 3.969 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
323 | 9 | November | 4.1 | 5.0477 | 173.4 | 31.752 | 205.152 | 0 | 205.152 | 0 | 0 | 84.5227 | 15.4773 | 0 | 84.5227 | 15.4773 | 0
323 | 10 | November | 3.1 | 3.8165 | 0 | 72.765 | 72.765 | 0 | 72.765 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
323 | 11 | November | 5.1 | 6.2788 | 312.8 | 103.194 | 415.994 | 0 | 415.994 | 0 | 0 | 75.1934 | 24.8066 | 0 | 75.1934 | 24.8066 | 0
323 | 12 | November | 2.6 | 3.201 | 0 | 116.424 | 116.424 | 0 | 116.424 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
323 | 13 | November | 4.1 | 5.0477 | 173.4 | 109.809 | 283.209 | 0 | 283.209 | 0 | 0 | 61.2269 | 38.7731 | 0 | 61.2269 | 38.7731 | 0
323 | 14 | November | 5.1 | 6.2788 | 312.8 | 84.672 | 397.472 | 0 | 397.472 | 0 | 0 | 78.6974 | 21.3026 | 0 | 78.6974 | 21.3026 | 0
323 | 15 | November | 4.1 | 5.0477 | 173.4 | 44.982 | 218.382 | 0 | 218.382 | 0 | 0 | 79.4021 | 20.5979 | 0 | 79.4021 | 20.5979 | 0
323 | 16 | November | 5.7 | 7.0175 | 504.9 | 9.261 | 514.161 | 0 | 514.161 | 0 | 0 | 98.1988 | 1.8012 | 0 | 98.1988 | 1.8012 | 0
323 | 17 | November | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
323 | 18 | November | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
323 | 19 | November | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
323 | 20 | November | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
323 | 21 | November | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
323 | 22 | November | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
323 | 23 | November | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
323 | 24 | November | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
324 | 1 | November | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
324 | 2 | November | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
324 | 3 | November | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
324 | 4 | November | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
324 | 5 | November | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
324 | 6 | November | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
324 | 7 | November | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
324 | 8 | November | 10.3 | 12.6808 | 1694.9 | 9.261 | 1704.161 | 0 | 1704.161 | 0 | 0 | 99.4566 | 0.54343 | 0 | 99.4566 | 0.54343 | 0
324 | 9 | November | 10.8 | 13.2964 | 1698.3 | 204.4336 | 1902.7336 | 0 | 1902.7336 | 0 | 0 | 89.2558 | 10.7442 | 0 | 89.2558 | 10.7442 | 0
324 | 10 | November | 11.3 | 13.9119 | 1700 | 509.9136 | 2209.9136 | 1 | 2000 | 209.9136 | 10.4957 | 76.9261 | 15 | 41.1665 | 74.5043 | 23.0739 | 12.3479
324 | 11 | November | 12.3 | 15.1431 | 1700 | 710.111 | 2410.111 | 1 | 2000 | 410.111 | 20.5055 | 70.5362 | 15 | 57.7531 | 64.4945 | 29.4638 | 24.1242
324 | 12 | November | 12.3 | 15.1431 | 1700 | 745.4822 | 2445.4822 | 1 | 2000 | 445.4822 | 22.2741 | 69.5159 | 15 | 59.7576 | 62.7259 | 30.4841 | 26.2048
324 | 13 | November | 12.9 | 15.8818 | 1700 | 679.3365 | 2379.3365 | 1 | 2000 | 379.3365 | 18.9668 | 71.4485 | 15 | 55.8393 | 66.0332 | 28.5515 | 22.3139
324 | 14 | November | 10.8 | 13.2964 | 1698.3 | 511.3637 | 2209.6637 | 1 | 2000 | 209.6637 | 10.4832 | 76.8578 | 15.085 | 41.0009 | 74.4318 | 23.1422 | 12.3455
324 | 15 | November | 11.8 | 14.5275 | 1700 | 248.2222 | 1948.2222 | 0 | 1948.2222 | 0 | 0 | 87.259 | 12.741 | 0 | 87.259 | 12.741 | 0
324 | 16 | November | 7.2 | 8.8642 | 908.65 | 23.814 | 932.464 | 0 | 932.464 | 0 | 0 | 97.4461 | 2.5539 | 0 | 97.4461 | 2.5539 | 0
324 | 17 | November | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
324 | 18 | November | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
324 | 19 | November | 12.9 | 15.8818 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
324 | 20 | November | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
324 | 21 | November | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
324 | 22 | November | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
324 | 23 | November | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
324 | 24 | November | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
325 | 1 | November | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
325 | 2 | November | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
325 | 3 | November | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
325 | 4 | November | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
325 | 5 | November | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
325 | 6 | November | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
325 | 7 | November | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
325 | 8 | November | 5.1 | 6.2788 | 312.8 | 5.292 | 318.092 | 0 | 318.092 | 0 | 0 | 98.3363 | 1.6637 | 0 | 98.3363 | 1.6637 | 0
325 | 9 | November | 4.6 | 5.6633 | 237.15 | 29.106 | 266.256 | 0 | 266.256 | 0 | 0 | 89.0684 | 10.9316 | 0 | 89.0684 | 10.9316 | 0
325 | 10 | November | 3.6 | 4.4321 | 75.65 | 127.5368 | 203.1868 | 0 | 203.1868 | 0 | 0 | 37.2318 | 62.7682 | 0 | 37.2318 | 62.7682 | 0
325 | 11 | November | 5.1 | 6.2788 | 312.8 | 175.3255 | 488.1255 | 0 | 488.1255 | 0 | 0 | 64.0819 | 35.9181 | 0 | 64.0819 | 35.9181 | 0
325 | 12 | November | 4.6 | 5.6633 | 237.15 | 113.778 | 350.928 | 0 | 350.928 | 0 | 0 | 67.578 | 32.422 | 0 | 67.578 | 32.422 | 0
325 | 13 | November | 5.7 | 7.0175 | 504.9 | 107.163 | 612.063 | 0 | 612.063 | 0 | 0 | 82.4915 | 17.5085 | 0 | 82.4915 | 17.5085 | 0
325 | 14 | November | 5.7 | 7.0175 | 504.9 | 82.026 | 586.926 | 0 | 586.926 | 0 | 0 | 86.0245 | 13.9755 | 0 | 86.0245 | 13.9755 | 0
325 | 15 | November | 5.1 | 6.2788 | 312.8 | 42.336 | 355.136 | 0 | 355.136 | 0 | 0 | 88.0789 | 11.9211 | 0 | 88.0789 | 11.9211 | 0
325 | 16 | November | 6.2 | 7.6331 | 625.6 | 7.938 | 633.538 | 0 | 633.538 | 0 | 0 | 98.747 | 1.253 | 0 | 98.747 | 1.253 | 0
325 | 17 | November | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
325 | 18 | November | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
325 | 19 | November | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
325 | 20 | November | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
325 | 21 | November | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
325 | 22 | November | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
325 | 23 | November | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
325 | 24 | November | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
326 | 1 | November | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
326 | 2 | November | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
326 | 3 | November | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
326 | 4 | November | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
326 | 5 | November | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
326 | 6 | November | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
326 | 7 | November | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
326 | 8 | November | 5.1 | 6.2788 | 312.8 | 3.969 | 316.769 | 0 | 316.769 | 0 | 0 | 98.747 | 1.253 | 0 | 98.747 | 1.253 | 0
326 | 9 | November | 5.1 | 6.2788 | 312.8 | 43.659 | 356.459 | 0 | 356.459 | 0 | 0 | 87.752 | 12.248 | 0 | 87.752 | 12.248 | 0
326 | 10 | November | 6.2 | 7.6331 | 625.6 | 67.473 | 693.073 | 0 | 693.073 | 0 | 0 | 90.2647 | 9.7353 | 0 | 90.2647 | 9.7353 | 0
326 | 11 | November | 5.7 | 7.0175 | 504.9 | 99.225 | 604.125 | 0 | 604.125 | 0 | 0 | 83.5754 | 16.4246 | 0 | 83.5754 | 16.4246 | 0
326 | 12 | November | 6.2 | 7.6331 | 625.6 | 112.455 | 738.055 | 0 | 738.055 | 0 | 0 | 84.7633 | 15.2367 | 0 | 84.7633 | 15.2367 | 0
326 | 13 | November | 4.1 | 5.0477 | 173.4 | 105.84 | 279.24 | 0 | 279.24 | 0 | 0 | 62.0971 | 37.9029 | 0 | 62.0971 | 37.9029 | 0
326 | 14 | November | 7.7 | 9.4798 | 1059.95 | 140.8264 | 1200.7764 | 0 | 1200.7764 | 0 | 0 | 88.2721 | 11.7279 | 0 | 88.2721 | 11.7279 | 0
326 | 15 | November | 5.7 | 7.0175 | 504.9 | 64.827 | 569.727 | 0 | 569.727 | 0 | 0 | 88.6214 | 11.3786 | 0 | 88.6214 | 11.3786 | 0
326 | 16 | November | 4.6 | 5.6633 | 237.15 | 11.907 | 249.057 | 0 | 249.057 | 0 | 0 | 95.2192 | 4.7808 | 0 | 95.2192 | 4.7808 | 0
326 | 17 | November | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
326 | 18 | November | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
326 | 19 | November | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
326 | 20 | November | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
326 | 21 | November | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
326 | 22 | November | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
326 | 23 | November | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
326 | 24 | November | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327 | 1 | November | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327 | 2 | November | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327 | 3 | November | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327 | 4 | November | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327 | 5 | November | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327 | 6 | November | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
327 | 7 | November | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327 | 8 | November | 1.5 | 1.8467 | 0 | 6.615 | 6.615 | 0 | 6.615 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
327 | 9 | November | 3.6 | 4.4321 | 75.65 | 132.4267 | 208.0767 | 0 | 208.0767 | 0 | 0 | 36.3568 | 63.6432 | 0 | 36.3568 | 63.6432 | 0
327 | 10 | November | 3.1 | 3.8165 | 0 | 325.6413 | 325.6413 | 0 | 325.6413 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
327 | 11 | November | 3.1 | 3.8165 | 0 | 554.9741 | 554.9741 | 0 | 554.9741 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
327 | 12 | November | 3.1 | 3.8165 | 0 | 338.4184 | 338.4184 | 0 | 338.4184 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
327 | 13 | November | 3.1 | 3.8165 | 0 | 296.9367 | 296.9367 | 0 | 296.9367 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
327 | 14 | November | 4.1 | 5.0477 | 173.4 | 218.5239 | 391.9239 | 0 | 391.9239 | 0 | 0 | 44.2433 | 55.7567 | 0 | 44.2433 | 55.7567 | 0
327 | 15 | November | 3.1 | 3.8165 | 0 | 195.4291 | 195.4291 | 0 | 195.4291 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
327 | 16 | November | 2.6 | 3.201 | 0 | 11.907 | 11.907 | 0 | 11.907 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
327 | 17 | November | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
327 | 18 | November | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327 | 19 | November | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327 | 20 | November | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
327 | 21 | November | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
327 | 22 | November | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
327 | 23 | November | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
327 | 24 | November | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
328 | 1 | November | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
328 | 2 | November | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
328 | 3 | November | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
328 | 4 | November | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
328 | 5 | November | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
328 | 6 | November | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
328 | 7 | November | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
328 | 8 | November | 5.1 | 6.2788 | 312.8 | 2.646 | 315.446 | 0 | 315.446 | 0 | 0 | 99.1612 | 0.83881 | 0 | 99.1612 | 0.83881 | 0
328 | 9 | November | 5.1 | 6.2788 | 312.8 | 62.1887 | 374.9887 | 0 | 374.9887 | 0 | 0 | 83.4159 | 16.5841 | 0 | 83.4159 | 16.5841 | 0
328 | 10 | November | 6.7 | 8.2487 | 761.6 | 111.7711 | 873.3711 | 0 | 873.3711 | 0 | 0 | 87.2023 | 12.7977 | 0 | 87.2023 | 12.7977 | 0
328 | 11 | November | 8.2 | 10.0954 | 1359.15 | 298.6949 | 1657.8449 | 0 | 1657.8449 | 0 | 0 | 81.9829 | 18.0171 | 0 | 81.9829 | 18.0171 | 0
328 | 12 | November | 8.2 | 10.0954 | 1359.15 | 207.6626 | 1566.8126 | 0 | 1566.8126 | 0 | 0 | 86.7462 | 13.2538 | 0 | 86.7462 | 13.2538 | 0
328 | 13 | November | 7.2 | 8.8642 | 908.65 | 101.871 | 1010.521 | 0 | 1010.521 | 0 | 0 | 89.919 | 10.081 | 0 | 89.919 | 10.081 | 0
328 | 14 | November | 7.2 | 8.8642 | 908.65 | 76.734 | 985.384 | 0 | 985.384 | 0 | 0 | 92.2128 | 7.7872 | 0 | 92.2128 | 7.7872 | 0
328 | 15 | November | 8.2 | 10.0954 | 1359.15 | 62.181 | 1421.331 | 0 | 1421.331 | 0 | 0 | 95.6252 | 4.3748 | 0 | 95.6252 | 4.3748 | 0
328 | 16 | November | 7.2 | 8.8642 | 908.65 | 14.553 | 923.203 | 0 | 923.203 | 0 | 0 | 98.4236 | 1.5764 | 0 | 98.4236 | 1.5764 | 0
328 | 17 | November | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
328 | 18 | November | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
328 | 19 | November | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
328 | 20 | November | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
328 | 21 | November | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
328 | 22 | November | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
328 | 23 | November | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
328 | 24 | November | 11.8 | 14.5275 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
329 | 1 | November | 12.3 | 15.1431 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
329 | 2 | November | 12.3 | 15.1431 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
329 | 3 | November | 12.3 | 15.1431 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
329 | 4 | November | 12.3 | 15.1431 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
329 | 5 | November | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
329 | 6 | November | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
329 | 7 | November | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
329 | 8 | November | 10.8 | 13.2964 | 1698.3 | 1.323 | 1699.623 | 0 | 1699.623 | 0 | 0 | 99.9222 | 0.077841 | 0 | 99.9222 | 0.077841 | 0
329 | 9 | November | 10.3 | 12.6808 | 1694.9 | 38.367 | 1733.267 | 0 | 1733.267 | 0 | 0 | 97.7864 | 2.2136 | 0 | 97.7864 | 2.2136 | 0
329 | 10 | November | 11.8 | 14.5275 | 1700 | 63.504 | 1763.504 | 0 | 1763.504 | 0 | 0 | 96.399 | 3.601 | 0 | 96.399 | 3.601 | 0
329 | 11 | November | 11.3 | 13.9119 | 1700 | 95.256 | 1795.256 | 0 | 1795.256 | 0 | 0 | 94.694 | 5.306 | 0 | 94.694 | 5.306 | 0
329 | 12 | November | 10.3 | 12.6808 | 1694.9 | 214.7839 | 1909.6839 | 0 | 1909.6839 | 0 | 0 | 88.7529 | 11.2471 | 0 | 88.7529 | 11.2471 | 0
329 | 13 | November | 10.3 | 12.6808 | 1694.9 | 101.871 | 1796.771 | 0 | 1796.771 | 0 | 0 | 94.3303 | 5.6697 | 0 | 94.3303 | 5.6697 | 0
329 | 14 | November | 10.8 | 13.2964 | 1698.3 | 76.734 | 1775.034 | 0 | 1775.034 | 0 | 0 | 95.677 | 4.323 | 0 | 95.677 | 4.323 | 0
329 | 15 | November | 11.3 | 13.9119 | 1700 | 38.367 | 1738.367 | 0 | 1738.367 | 0 | 0 | 97.7929 | 2.2071 | 0 | 97.7929 | 2.2071 | 0
329 | 16 | November | 10.8 | 13.2964 | 1698.3 | 10.584 | 1708.884 | 0 | 1708.884 | 0 | 0 | 99.3806 | 0.61935 | 0 | 99.3806 | 0.61935 | 0
329 | 17 | November | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
329 | 18 | November | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
329 | 19 | November | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
329 | 20 | November | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
329 | 21 | November | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
329 | 22 | November | 12.9 | 15.8818 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
329 | 23 | November | 11.8 | 14.5275 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
329 | 24 | November | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
330 | 1 | November | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
330 | 2 | November | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
330 | 3 | November | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
330 | 4 | November | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
330 | 5 | November | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
330 | 6 | November | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
330 | 7 | November | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
330 | 8 | November | 10.3 | 12.6808 | 1694.9 | 1.323 | 1696.223 | 0 | 1696.223 | 0 | 0 | 99.922 | 0.077997 | 0 | 99.922 | 0.077997 | 0
330 | 9 | November | 10.3 | 12.6808 | 1694.9 | 22.491 | 1717.391 | 0 | 1717.391 | 0 | 0 | 98.6904 | 1.3096 | 0 | 98.6904 | 1.3096 | 0
330 | 10 | November | 8.7 | 10.711 | 1490.05 | 111.4488 | 1601.4988 | 0 | 1601.4988 | 0 | 0 | 93.041 | 6.959 | 0 | 93.041 | 6.959 | 0
330 | 11 | November | 9.8 | 12.0652 | 1683.85 | 159.5012 | 1843.3512 | 0 | 1843.3512 | 0 | 0 | 91.3472 | 8.6528 | 0 | 91.3472 | 8.6528 | 0
330 | 12 | November | 11.3 | 13.9119 | 1700 | 198.0707 | 1898.0707 | 0 | 1898.0707 | 0 | 0 | 89.5646 | 10.4354 | 0 | 89.5646 | 10.4354 | 0
330 | 13 | November | 9.3 | 11.4496 | 1598.85 | 178.2239 | 1777.0739 | 0 | 1777.0739 | 0 | 0 | 89.9709 | 10.0291 | 0 | 89.9709 | 10.0291 | 0
330 | 14 | November | 10.3 | 12.6808 | 1694.9 | 75.411 | 1770.311 | 0 | 1770.311 | 0 | 0 | 95.7402 | 4.2598 | 0 | 95.7402 | 4.2598 | 0
330 | 15 | November | 8.7 | 10.711 | 1490.05 | 59.535 | 1549.585 | 0 | 1549.585 | 0 | 0 | 96.158 | 3.842 | 0 | 96.158 | 3.842 | 0
330 | 16 | November | 8.7 | 10.711 | 1490.05 | 6.615 | 1496.665 | 0 | 1496.665 | 0 | 0 | 99.558 | 0.44198 | 0 | 99.558 | 0.44198 | 0
330 | 17 | November | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
330 | 18 | November | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
330 | 19 | November | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
330 | 20 | November | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
330 | 21 | November | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
330 | 22 | November | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
330 | 23 | November | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
330 | 24 | November | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
331 | 1 | November | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
331 | 2 | November | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
331 | 3 | November | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
331 | 4 | November | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
331 | 5 | November | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
331 | 6 | November | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
331 | 7 | November | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
331 | 8 | November | 8.2 | 10.0954 | 1359.15 | 3.969 | 1363.119 | 0 | 1363.119 | 0 | 0 | 99.7088 | 0.29117 | 0 | 99.7088 | 0.29117 | 0
331 | 9 | November | 8.2 | 10.0954 | 1359.15 | 34.398 | 1393.548 | 0 | 1393.548 | 0 | 0 | 97.5316 | 2.4684 | 0 | 97.5316 | 2.4684 | 0
331 | 10 | November | 7.7 | 9.4798 | 1059.95 | 105.3366 | 1165.2866 | 0 | 1165.2866 | 0 | 0 | 90.9605 | 9.0395 | 0 | 90.9605 | 9.0395 | 0
331 | 11 | November | 7.7 | 9.4798 | 1059.95 | 159.2378 | 1219.1878 | 0 | 1219.1878 | 0 | 0 | 86.939 | 13.061 | 0 | 86.939 | 13.061 | 0
331 | 12 | November | 8.2 | 10.0954 | 1359.15 | 196.629 | 1555.779 | 0 | 1555.779 | 0 | 0 | 87.3614 | 12.6386 | 0 | 87.3614 | 12.6386 | 0
331 | 13 | November | 7.2 | 8.8642 | 908.65 | 175.5097 | 1084.1597 | 0 | 1084.1597 | 0 | 0 | 83.8115 | 16.1885 | 0 | 83.8115 | 16.1885 | 0
331 | 14 | November | 7.7 | 9.4798 | 1059.95 | 128.6431 | 1188.5931 | 0 | 1188.5931 | 0 | 0 | 89.1769 | 10.8231 | 0 | 89.1769 | 10.8231 | 0
331 | 15 | November | 6.7 | 8.2487 | 761.6 | 58.212 | 819.812 | 0 | 819.812 | 0 | 0 | 92.8993 | 7.1007 | 0 | 92.8993 | 7.1007 | 0
331 | 16 | November | 6.2 | 7.6331 | 625.6 | 15.876 | 641.476 | 0 | 641.476 | 0 | 0 | 97.5251 | 2.4749 | 0 | 97.5251 | 2.4749 | 0
331 | 17 | November | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
331 | 18 | November | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
331 | 19 | November | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
331 | 20 | November | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
331 | 21 | November | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
331 | 22 | November | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
331 | 23 | November | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
331 | 24 | November | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332 | 1 | November | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332 | 2 | November | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332 | 3 | November | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332 | 4 | November | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
332 | 5 | November | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332 | 6 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332 | 7 | November | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332 | 8 | November | 0 | 0 | 0 | 2.646 | 2.646 | 0 | 2.646 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
332 | 9 | November | 1.5 | 1.8467 | 0 | 74.4545 | 74.4545 | 0 | 74.4545 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
332 | 10 | November | 2.6 | 3.201 | 0 | 382.7614 | 382.7614 | 0 | 382.7614 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
332 | 11 | November | 2.6 | 3.201 | 0 | 639.2223 | 639.2223 | 0 | 639.2223 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
332 | 12 | November | 3.1 | 3.8165 | 0 | 719.9967 | 719.9967 | 0 | 719.9967 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
332 | 13 | November | 3.1 | 3.8165 | 0 | 542.9247 | 542.9247 | 0 | 542.9247 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
332 | 14 | November | 3.1 | 3.8165 | 0 | 316.3515 | 316.3515 | 0 | 316.3515 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
332 | 15 | November | 3.1 | 3.8165 | 0 | 205.9987 | 205.9987 | 0 | 205.9987 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
332 | 16 | November | 2.6 | 3.201 | 0 | 15.876 | 15.876 | 0 | 15.876 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
332 | 17 | November | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332 | 18 | November | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332 | 19 | November | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332 | 20 | November | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332 | 21 | November | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332 | 22 | November | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332 | 23 | November | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332 | 24 | November | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333 | 1 | November | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333 | 2 | November | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333 | 3 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333 | 4 | November | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333 | 5 | November | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333 | 6 | November | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333 | 7 | November | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333 | 8 | November | 1.5 | 1.8467 | 0 | 2.646 | 2.646 | 0 | 2.646 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
333 | 9 | November | 1.5 | 1.8467 | 0 | 125.9053 | 125.9053 | 0 | 125.9053 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
333 | 10 | November | 0 | 0 | 0 | 401.3884 | 401.3884 | 0 | 401.3884 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
333 | 11 | November | 0 | 0 | 0 | 661.1233 | 661.1233 | 0 | 661.1233 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
333 | 12 | November | 0 | 0 | 0 | 712.1932 | 712.1932 | 0 | 712.1932 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
333 | 13 | November | 1.5 | 1.8467 | 0 | 636.8158 | 636.8158 | 0 | 636.8158 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
333 | 14 | November | 1.5 | 1.8467 | 0 | 472.2142 | 472.2142 | 0 | 472.2142 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
333 | 15 | November | 1.5 | 1.8467 | 0 | 209.0824 | 209.0824 | 0 | 209.0824 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
333 | 16 | November | 1 | 1.2311 | 0 | 15.876 | 15.876 | 0 | 15.876 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
333 | 17 | November | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333 | 18 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333 | 19 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333 | 20 | November | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333 | 21 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333 | 22 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333 | 23 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333 | 24 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
334 | 1 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
334 | 2 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
334 | 3 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
334 | 4 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
334 | 5 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
334 | 6 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
334 | 7 | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
334 | 8 | November | 0 | 0 | 0 | 1.323 | 1.323 | 0 | 1.323 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
334 | 9 | November | 0 | 0 | 0 | 116.151 | 116.151 | 0 | 116.151 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
334 | 10 | November | 0 | 0 | 0 | 333.3902 | 333.3902 | 0 | 333.3902 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
334 | 11 | November | 1 | 1.2311 | 0 | 644.1167 | 644.1167 | 0 | 644.1167 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
334 | 12 | November | 1 | 1.2311 | 0 | 686.6677 | 686.6677 | 0 | 686.6677 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
334 | 13 | November | 2.6 | 3.201 | 0 | 625.1796 | 625.1796 | 0 | 625.1796 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
334 | 14 | November | 2.1 | 2.5854 | 0 | 452.3269 | 452.3269 | 0 | 452.3269 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
334 | 15 | November | 3.1 | 3.8165 | 0 | 191.787 | 191.787 | 0 | 191.787 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
334 | 16 | November | 2.6 | 3.201 | 0 | 7.938 | 7.938 | 0 | 7.938 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
334 | 17 | November | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
334 | 18 | November | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
334 | 19 | November | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
334 | 20 | November | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
334 | 21 | November | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
334 | 22 | November | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
334 | 23 | November | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
334 | 24 | November | 2.8 | 3.4472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335 | 1 | December | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335 | 2 | December | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
335 | 3 | December | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335 | 4 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
335 | 5 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
335 | 6 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
335 | 7 | December | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
335 | 8 | December | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
335 | 9 | December | 4.6 | 5.6633 | 237.15 | 15.876 | 253.026 | 0 | 253.026 | 0 | 0 | 93.7255 | 6.2745 | 0 | 93.7255 | 6.2745 | 0
335 | 10 | December | 4.6 | 5.6633 | 237.15 | 50.274 | 287.424 | 0 | 287.424 | 0 | 0 | 82.5088 | 17.4912 | 0 | 82.5088 | 17.4912 | 0
335 | 11 | December | 6.2 | 7.6331 | 625.6 | 80.703 | 706.303 | 0 | 706.303 | 0 | 0 | 88.5739 | 11.4261 | 0 | 88.5739 | 11.4261 | 0
335 | 12 | December | 5.7 | 7.0175 | 504.9 | 362.2958 | 867.1958 | 0 | 867.1958 | 0 | 0 | 58.2221 | 41.7779 | 0 | 58.2221 | 41.7779 | 0
335 | 13 | December | 6.2 | 7.6331 | 625.6 | 467.9752 | 1093.5752 | 0 | 1093.5752 | 0 | 0 | 57.2069 | 42.7931 | 0 | 57.2069 | 42.7931 | 0
335 | 14 | December | 4.6 | 5.6633 | 237.15 | 385.5826 | 622.7326 | 0 | 622.7326 | 0 | 0 | 38.0822 | 61.9178 | 0 | 38.0822 | 61.9178 | 0
335 | 15 | December | 4.6 | 5.6633 | 237.15 | 136.478 | 373.628 | 0 | 373.628 | 0 | 0 | 63.4722 | 36.5278 | 0 | 63.4722 | 36.5278 | 0
335 | 16 | December | 5.7 | 7.0175 | 504.9 | 3.969 | 508.869 | 0 | 508.869 | 0 | 0 | 99.22 | 0.77996 | 0 | 99.22 | 0.77996 | 0
335 | 17 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
335 | 18 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
335 | 19 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
335 | 20 | December | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
335 | 21 | December | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
335 | 22 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
335 | 23 | December | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
335 | 24 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
336 | 1 | December | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
336 | 2 | December | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
336 | 3 | December | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
336 | 4 | December | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
336 | 5 | December | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
336 | 6 | December | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
336 | 7 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
336 | 8 | December | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
336 | 9 | December | 9.3 | 11.4496 | 1598.85 | 23.814 | 1622.664 | 0 | 1622.664 | 0 | 0 | 98.5324 | 1.4676 | 0 | 98.5324 | 1.4676 | 0
336 | 10 | December | 9.3 | 11.4496 | 1598.85 | 78.057 | 1676.907 | 0 | 1676.907 | 0 | 0 | 95.3452 | 4.6548 | 0 | 95.3452 | 4.6548 | 0
336 | 11 | December | 9.8 | 12.0652 | 1683.85 | 131.8477 | 1815.6977 | 0 | 1815.6977 | 0 | 0 | 92.7385 | 7.2615 | 0 | 92.7385 | 7.2615 | 0
336 | 12 | December | 9.3 | 11.4496 | 1598.85 | 160.4337 | 1759.2837 | 0 | 1759.2837 | 0 | 0 | 90.8807 | 9.1193 | 0 | 90.8807 | 9.1193 | 0
336 | 13 | December | 8.2 | 10.0954 | 1359.15 | 149.1108 | 1508.2608 | 0 | 1508.2608 | 0 | 0 | 90.1137 | 9.8863 | 0 | 90.1137 | 9.8863 | 0
336 | 14 | December | 7.7 | 9.4798 | 1059.95 | 104.1161 | 1164.0661 | 0 | 1164.0661 | 0 | 0 | 91.0558 | 8.9442 | 0 | 91.0558 | 8.9442 | 0
336 | 15 | December | 7.2 | 8.8642 | 908.65 | 46.305 | 954.955 | 0 | 954.955 | 0 | 0 | 95.1511 | 4.8489 | 0 | 95.1511 | 4.8489 | 0
336 | 16 | December | 6.2 | 7.6331 | 625.6 | 6.615 | 632.215 | 0 | 632.215 | 0 | 0 | 98.9537 | 1.0463 | 0 | 98.9537 | 1.0463 | 0
336 | 17 | December | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
336 | 18 | December | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
336 | 19 | December | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
336 | 20 | December | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
336 | 21 | December | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
336 | 22 | December | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
336 | 23 | December | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
336 | 24 | December | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
337 | 1 | December | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
337 | 2 | December | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
337 | 3 | December | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
337 | 4 | December | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
337 | 5 | December | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
337 | 6 | December | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
337 | 7 | December | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
337 | 8 | December | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
337 | 9 | December | 7.2 | 8.8642 | 908.65 | 22.491 | 931.141 | 0 | 931.141 | 0 | 0 | 97.5846 | 2.4154 | 0 | 97.5846 | 2.4154 | 0
337 | 10 | December | 7.2 | 8.8642 | 908.65 | 76.734 | 985.384 | 0 | 985.384 | 0 | 0 | 92.2128 | 7.7872 | 0 | 92.2128 | 7.7872 | 0
337 | 11 | December | 9.3 | 11.4496 | 1598.85 | 130.5009 | 1729.3509 | 0 | 1729.3509 | 0 | 0 | 92.4538 | 7.5462 | 0 | 92.4538 | 7.5462 | 0
337 | 12 | December | 8.2 | 10.0954 | 1359.15 | 159.0676 | 1518.2176 | 0 | 1518.2176 | 0 | 0 | 89.5227 | 10.4773 | 0 | 89.5227 | 10.4773 | 0
337 | 13 | December | 7.7 | 9.4798 | 1059.95 | 149.083 | 1209.033 | 0 | 1209.033 | 0 | 0 | 87.6692 | 12.3308 | 0 | 87.6692 | 12.3308 | 0
337 | 14 | December | 9.3 | 11.4496 | 1598.85 | 102.7889 | 1701.6389 | 0 | 1701.6389 | 0 | 0 | 93.9594 | 6.0406 | 0 | 93.9594 | 6.0406 | 0
337 | 15 | December | 7.2 | 8.8642 | 908.65 | 44.982 | 953.632 | 0 | 953.632 | 0 | 0 | 95.2831 | 4.7169 | 0 | 95.2831 | 4.7169 | 0
337 | 16 | December | 5.1 | 6.2788 | 312.8 | 6.615 | 319.415 | 0 | 319.415 | 0 | 0 | 97.929 | 2.071 | 0 | 97.929 | 2.071 | 0
337 | 17 | December | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
337 | 18 | December | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
337 | 19 | December | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
337 | 20 | December | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
337 | 21 | December | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
337 | 22 | December | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
337 | 23 | December | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
337 | 24 | December | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
338 | 1 | December | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
338 | 2 | December | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
338 | 3 | December | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
338 | 4 | December | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
338 | 5 | December | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
338 | 6 | December | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
338 | 7 | December | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
338 | 8 | December | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
338 | 9 | December | 9.8 | 12.0652 | 1683.85 | 21.168 | 1705.018 | 0 | 1705.018 | 0 | 0 | 98.7585 | 1.2415 | 0 | 98.7585 | 1.2415 | 0
338 | 10 | December | 9.8 | 12.0652 | 1683.85 | 168.7601 | 1852.6101 | 0 | 1852.6101 | 0 | 0 | 90.8907 | 9.1093 | 0 | 90.8907 | 9.1093 | 0
338 | 11 | December | 10.3 | 12.6808 | 1694.9 | 244.3838 | 1939.2838 | 0 | 1939.2838 | 0 | 0 | 87.3982 | 12.6018 | 0 | 87.3982 | 12.6018 | 0
338 | 12 | December | 9.3 | 11.4496 | 1598.85 | 157.4981 | 1756.3481 | 0 | 1756.3481 | 0 | 0 | 91.0326 | 8.9674 | 0 | 91.0326 | 8.9674 | 0
338 | 13 | December | 11.3 | 13.9119 | 1700 | 147.7343 | 1847.7343 | 0 | 1847.7343 | 0 | 0 | 92.0046 | 7.9954 | 0 | 92.0046 | 7.9954 | 0
338 | 14 | December | 10.8 | 13.2964 | 1698.3 | 101.4622 | 1799.7622 | 0 | 1799.7622 | 0 | 0 | 94.3625 | 5.6375 | 0 | 94.3625 | 5.6375 | 0
338 | 15 | December | 9.8 | 12.0652 | 1683.85 | 152.0063 | 1835.8563 | 0 | 1835.8563 | 0 | 0 | 91.7201 | 8.2799 | 0 | 91.7201 | 8.2799 | 0
338 | 16 | December | 6.7 | 8.2487 | 761.6 | 10.584 | 772.184 | 0 | 772.184 | 0 | 0 | 98.6293 | 1.3707 | 0 | 98.6293 | 1.3707 | 0
338 | 17 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
338 | 18 | December | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
338 | 19 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
338 | 20 | December | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
338 | 21 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
338 | 22 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
338 | 23 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
338 | 24 | December | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
339 | 1 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
339 | 2 | December | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
339 | 3 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
339 | 4 | December | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
339 | 5 | December | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
339 | 6 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
339 | 7 | December | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
339 | 8 | December | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
339 | 9 | December | 8.7 | 10.711 | 1490.05 | 55.553 | 1545.603 | 0 | 1545.603 | 0 | 0 | 96.4057 | 3.5943 | 0 | 96.4057 | 3.5943 | 0
339 | 10 | December | 7.2 | 8.8642 | 908.65 | 266.304 | 1174.954 | 0 | 1174.954 | 0 | 0 | 77.3349 | 22.6651 | 0 | 77.3349 | 22.6651 | 0
339 | 11 | December | 8.2 | 10.0954 | 1359.15 | 528.7492 | 1887.8992 | 0 | 1887.8992 | 0 | 0 | 71.9927 | 28.0073 | 0 | 71.9927 | 28.0073 | 0
339 | 12 | December | 7.7 | 9.4798 | 1059.95 | 548.1297 | 1608.0797 | 0 | 1608.0797 | 0 | 0 | 65.914 | 34.086 | 0 | 65.914 | 34.086 | 0
339 | 13 | December | 7.2 | 8.8642 | 908.65 | 501.0864 | 1409.7364 | 0 | 1409.7364 | 0 | 0 | 64.4553 | 35.5447 | 0 | 64.4553 | 35.5447 | 0
339 | 14 | December | 7.7 | 9.4798 | 1059.95 | 380.3233 | 1440.2733 | 0 | 1440.2733 | 0 | 0 | 73.5937 | 26.4063 | 0 | 73.5937 | 26.4063 | 0
339 | 15 | December | 6.7 | 8.2487 | 761.6 | 146.7628 | 908.3628 | 0 | 908.3628 | 0 | 0 | 83.8432 | 16.1568 | 0 | 83.8432 | 16.1568 | 0
339 | 16 | December | 4.6 | 5.6633 | 237.15 | 10.584 | 247.734 | 0 | 247.734 | 0 | 0 | 95.7277 | 4.2723 | 0 | 95.7277 | 4.2723 | 0
339 | 17 | December | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
339 | 18 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
339 | 19 | December | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
339 | 20 | December | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
339 | 21 | December | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
339 | 22 | December | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
339 | 23 | December | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
339 | 24 | December | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
340 | 1 | December | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
340 | 2 | December | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
340 | 3 | December | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
340 | 4 | December | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
340 | 5 | December | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
340 | 6 | December | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
340 | 7 | December | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
340 | 8 | December | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
340 | 9 | December | 4.1 | 5.0477 | 173.4 | 19.845 | 193.245 | 0 | 193.245 | 0 | 0 | 89.7307 | 10.2693 | 0 | 89.7307 | 10.2693 | 0
340 | 10 | December | 5.1 | 6.2788 | 312.8 | 44.982 | 357.782 | 0 | 357.782 | 0 | 0 | 87.4275 | 12.5725 | 0 | 87.4275 | 12.5725 | 0
340 | 11 | December | 5.7 | 7.0175 | 504.9 | 133.3958 | 638.2958 | 0 | 638.2958 | 0 | 0 | 79.1013 | 20.8987 | 0 | 79.1013 | 20.8987 | 0
340 | 12 | December | 5.7 | 7.0175 | 504.9 | 153.8699 | 658.7699 | 0 | 658.7699 | 0 | 0 | 76.6429 | 23.3571 | 0 | 76.6429 | 23.3571 | 0
340 | 13 | December | 6.2 | 7.6331 | 625.6 | 143.9989 | 769.5989 | 0 | 769.5989 | 0 | 0 | 81.2891 | 18.7109 | 0 | 81.2891 | 18.7109 | 0
340 | 14 | December | 6.2 | 7.6331 | 625.6 | 99.2449 | 724.8449 | 0 | 724.8449 | 0 | 0 | 86.3081 | 13.6919 | 0 | 86.3081 | 13.6919 | 0
340 | 15 | December | 6.2 | 7.6331 | 625.6 | 42.336 | 667.936 | 0 | 667.936 | 0 | 0 | 93.6617 | 6.3383 | 0 | 93.6617 | 6.3383 | 0
340 | 16 | December | 5.7 | 7.0175 | 504.9 | 5.292 | 510.192 | 0 | 510.192 | 0 | 0 | 98.9627 | 1.0373 | 0 | 98.9627 | 1.0373 | 0
340 | 17 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
340 | 18 | December | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
340 | 19 | December | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
340 | 20 | December | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
340 | 21 | December | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
340 | 22 | December | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
340 | 23 | December | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
340 | 24 | December | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
341 | 1 | December | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
341 | 2 | December | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
341 | 3 | December | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
341 | 4 | December | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
341 | 5 | December | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
341 | 6 | December | 11.8 | 14.5275 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
341 | 7 | December | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
341 | 8 | December | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
341 | 9 | December | 6.7 | 8.2487 | 761.6 | 19.845 | 781.445 | 0 | 781.445 | 0 | 0 | 97.4605 | 2.5395 | 0 | 97.4605 | 2.5395 | 0
341 | 10 | December | 8.2 | 10.0954 | 1359.15 | 71.442 | 1430.592 | 0 | 1430.592 | 0 | 0 | 95.0061 | 4.9939 | 0 | 95.0061 | 4.9939 | 0
341 | 11 | December | 8.2 | 10.0954 | 1359.15 | 123.8 | 1482.95 | 0 | 1482.95 | 0 | 0 | 91.6518 | 8.3482 | 0 | 91.6518 | 8.3482 | 0
341 | 12 | December | 8.2 | 10.0954 | 1359.15 | 153.6262 | 1512.7762 | 0 | 1512.7762 | 0 | 0 | 89.8447 | 10.1553 | 0 | 89.8447 | 10.1553 | 0
341 | 13 | December | 6.7 | 8.2487 | 761.6 | 244.7759 | 1006.3759 | 0 | 1006.3759 | 0 | 0 | 75.6775 | 24.3225 | 0 | 75.6775 | 24.3225 | 0
341 | 14 | December | 9.8 | 12.0652 | 1683.85 | 337.2101 | 2021.0601 | 1 | 2000 | 21.0601 | 1.053 | 83.3152 | 15.8075 | 6.2454 | 83.1395 | 16.6848 | 1.2507
341 | 15 | December | 8.7 | 10.711 | 1490.05 | 108.1313 | 1598.1813 | 0 | 1598.1813 | 0 | 0 | 93.2341 | 6.7659 | 0 | 93.2341 | 6.7659 | 0
341 | 16 | December | 7.2 | 8.8642 | 908.65 | 10.584 | 919.234 | 0 | 919.234 | 0 | 0 | 98.8486 | 1.1514 | 0 | 98.8486 | 1.1514 | 0
341 | 17 | December | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
341 | 18 | December | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
341 | 19 | December | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
341 | 20 | December | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
341 | 21 | December | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
341 | 22 | December | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
341 | 23 | December | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
341 | 24 | December | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
342 | 1 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
342 | 2 | December | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
342 | 3 | December | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
342 | 4 | December | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
342 | 5 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
342 | 6 | December | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
342 | 7 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
342 | 8 | December | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
342 | 9 | December | 5.7 | 7.0175 | 504.9 | 11.907 | 516.807 | 0 | 516.807 | 0 | 0 | 97.696 | 2.304 | 0 | 97.696 | 2.304 | 0
342 | 10 | December | 5.7 | 7.0175 | 504.9 | 43.659 | 548.559 | 0 | 548.559 | 0 | 0 | 92.0411 | 7.9589 | 0 | 92.0411 | 7.9589 | 0
342 | 11 | December | 6.2 | 7.6331 | 625.6 | 72.765 | 698.365 | 0 | 698.365 | 0 | 0 | 89.5807 | 10.4193 | 0 | 89.5807 | 10.4193 | 0
342 | 12 | December | 8.2 | 10.0954 | 1359.15 | 85.995 | 1445.145 | 0 | 1445.145 | 0 | 0 | 94.0494 | 5.9506 | 0 | 94.0494 | 5.9506 | 0
342 | 13 | December | 6.7 | 8.2487 | 761.6 | 82.026 | 843.626 | 0 | 843.626 | 0 | 0 | 90.277 | 9.723 | 0 | 90.277 | 9.723 | 0
342 | 14 | December | 7.7 | 9.4798 | 1059.95 | 59.535 | 1119.485 | 0 | 1119.485 | 0 | 0 | 94.6819 | 5.3181 | 0 | 94.6819 | 5.3181 | 0
342 | 15 | December | 8.2 | 10.0954 | 1359.15 | 26.46 | 1385.61 | 0 | 1385.61 | 0 | 0 | 98.0904 | 1.9096 | 0 | 98.0904 | 1.9096 | 0
342 | 16 | December | 9.7 | 11.9421 | 1658.35 | 3.969 | 1662.319 | 0 | 1662.319 | 0 | 0 | 99.7612 | 0.23876 | 0 | 99.7612 | 0.23876 | 0
342 | 17 | December | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
342 | 18 | December | 12.3 | 15.1431 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
342 | 19 | December | 14.4 | 17.7285 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
342 | 20 | December | 14.4 | 17.7285 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
342 | 21 | December | 14.9 | 18.3441 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
342 | 22 | December | 14.9 | 18.3441 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
342 | 23 | December | 14.9 | 18.3441 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
342 | 24 | December | 15.9 | 19.5752 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
343 | 1 | December | 17 | 20.9295 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
343 | 2 | December | 16.4 | 20.1908 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
343 | 3 | December | 17 | 20.9295 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
343 | 4 | December | 19 | 23.3917 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
343 | 5 | December | 18.5 | 22.7762 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
343 | 6 | December | 20.6 | 25.3616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343 | 7 | December | 21.6 | 26.5927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343 | 8 | December | 18 | 22.1606 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
343 | 9 | December | 17.5 | 21.545 | 1700 | 37.9124 | 1737.9124 | 0 | 1737.9124 | 0 | 0 | 97.8185 | 2.1815 | 0 | 97.8185 | 2.1815 | 0
343 | 10 | December | 16.7 | 20.5601 | 1700 | 231.474 | 1931.474 | 0 | 1931.474 | 0 | 0 | 88.0157 | 11.9843 | 0 | 88.0157 | 11.9843 | 0
343 | 11 | December | 15.9 | 19.5752 | 1700 | 385.7853 | 2085.7853 | 1 | 2000 | 85.7853 | 4.2893 | 81.5041 | 15 | 22.2365 | 80.7107 | 18.4959 | 5.0462
343 | 12 | December | 17 | 20.9295 | 1700 | 584.5004 | 2284.5004 | 1 | 2000 | 284.5004 | 14.225 | 74.4145 | 15 | 48.6741 | 70.775 | 25.5855 | 16.7353
343 | 13 | December | 17 | 20.9295 | 1700 | 487.4318 | 2187.4318 | 1 | 2000 | 187.4318 | 9.3716 | 77.7167 | 15 | 38.4529 | 75.6284 | 22.2833 | 11.0254
343 | 14 | December | 15.9 | 19.5752 | 1700 | 379.344 | 2079.344 | 1 | 2000 | 79.344 | 3.9672 | 81.7566 | 15 | 20.9161 | 81.0328 | 18.2434 | 4.6673
343 | 15 | December | 13.9 | 17.1129 | 1700 | 145.5685 | 1845.5685 | 0 | 1845.5685 | 0 | 0 | 92.1125 | 7.8875 | 0 | 92.1125 | 7.8875 | 0
343 | 16 | December | 9.8 | 12.0652 | 1683.85 | 9.261 | 1693.111 | 0 | 1693.111 | 0 | 0 | 99.453 | 0.54698 | 0 | 99.453 | 0.54698 | 0
343 | 17 | December | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
343 | 18 | December | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
343 | 19 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
343 | 20 | December | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
343 | 21 | December | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
343 | 22 | December | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
343 | 23 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
343 | 24 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
344 | 1 | December | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
344 | 2 | December | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
344 | 3 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
344 | 4 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
344 | 5 | December | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
344 | 6 | December | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
344 | 7 | December | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
344 | 8 | December | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
344 | 9 | December | 9.3 | 11.4496 | 1598.85 | 31.752 | 1630.602 | 0 | 1630.602 | 0 | 0 | 98.0527 | 1.9473 | 0 | 98.0527 | 1.9473 | 0
344 | 10 | December | 11.8 | 14.5275 | 1700 | 67.473 | 1767.473 | 0 | 1767.473 | 0 | 0 | 96.1825 | 3.8175 | 0 | 96.1825 | 3.8175 | 0
344 | 11 | December | 10.3 | 12.6808 | 1694.9 | 119.7769 | 1814.6769 | 0 | 1814.6769 | 0 | 0 | 93.3995 | 6.6005 | 0 | 93.3995 | 6.6005 | 0
344 | 12 | December | 10.8 | 13.2964 | 1698.3 | 150.8933 | 1849.1933 | 0 | 1849.1933 | 0 | 0 | 91.84 | 8.16 | 0 | 91.84 | 8.16 | 0
344 | 13 | December | 11.8 | 14.5275 | 1700 | 475.6209 | 2175.6209 | 1 | 2000 | 175.6209 | 8.781 | 78.1386 | 15 | 36.9246 | 76.219 | 21.8614 | 10.3306
344 | 14 | December | 10.8 | 13.2964 | 1698.3 | 349.513 | 2047.813 | 1 | 2000 | 47.813 | 2.3906 | 82.9324 | 15.085 | 13.6799 | 82.5244 | 17.0676 | 2.8153
344 | 15 | December | 9.8 | 12.0652 | 1683.85 | 143.667 | 1827.517 | 0 | 1827.517 | 0 | 0 | 92.1387 | 7.8613 | 0 | 92.1387 | 7.8613 | 0
344 | 16 | December | 8.7 | 10.711 | 1490.05 | 9.261 | 1499.311 | 0 | 1499.311 | 0 | 0 | 99.3823 | 0.61768 | 0 | 99.3823 | 0.61768 | 0
344 | 17 | December | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
344 | 18 | December | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
344 | 19 | December | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
344 | 20 | December | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
344 | 21 | December | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
344 | 22 | December | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
344 | 23 | December | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
344 | 24 | December | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
345 | 1 | December | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
345 | 2 | December | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
345 | 3 | December | 11.8 | 14.5275 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
345 | 4 | December | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
345 | 5 | December | 12.3 | 15.1431 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
345 | 6 | December | 11.8 | 14.5275 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
345 | 7 | December | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
345 | 8 | December | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
345 | 9 | December | 9.8 | 12.0652 | 1683.85 | 29.106 | 1712.956 | 0 | 1712.956 | 0 | 0 | 98.3008 | 1.6992 | 0 | 98.3008 | 1.6992 | 0
345 | 10 | December | 9.8 | 12.0652 | 1683.85 | 148.7792 | 1832.6292 | 0 | 1832.6292 | 0 | 0 | 91.8817 | 8.1183 | 0 | 91.8817 | 8.1183 | 0
345 | 11 | December | 10.3 | 12.6808 | 1694.9 | 463.6935 | 2158.5935 | 1 | 2000 | 158.5935 | 7.9297 | 78.5187 | 15.255 | 34.2022 | 76.8153 | 21.4813 | 9.3571
345 | 12 | December | 11.3 | 13.9119 | 1700 | 147.5538 | 1847.5538 | 0 | 1847.5538 | 0 | 0 | 92.0136 | 7.9864 | 0 | 92.0136 | 7.9864 | 0
345 | 13 | December | 10.3 | 12.6808 | 1694.9 | 143.8381 | 1838.7381 | 0 | 1838.7381 | 0 | 0 | 92.1773 | 7.8227 | 0 | 92.1773 | 7.8227 | 0
345 | 14 | December | 6.7 | 8.2487 | 761.6 | 159.9805 | 921.5805 | 0 | 921.5805 | 0 | 0 | 82.6406 | 17.3594 | 0 | 82.6406 | 17.3594 | 0
345 | 15 | December | 8.2 | 10.0954 | 1359.15 | 41.013 | 1400.163 | 0 | 1400.163 | 0 | 0 | 97.0708 | 2.9292 | 0 | 97.0708 | 2.9292 | 0
345 | 16 | December | 7.2 | 8.8642 | 908.65 | 5.292 | 913.942 | 0 | 913.942 | 0 | 0 | 99.421 | 0.57903 | 0 | 99.421 | 0.57903 | 0
345 | 17 | December | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
345 | 18 | December | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
345 | 19 | December | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
345 | 20 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
345 | 21 | December | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
345 | 22 | December | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
345 | 23 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
345 | 24 | December | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
346 | 1 | December | 11.8 | 14.5275 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
346 | 2 | December | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
346 | 3 | December | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
346 | 4 | December | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
346 | 5 | December | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
346 | 6 | December | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
346 | 7 | December | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
346 | 8 | December | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346 | 9 | December | 1.5 | 1.8467 | 0 | 10.584 | 10.584 | 0 | 10.584 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
346 | 10 | December | 2.6 | 3.201 | 0 | 64.827 | 64.827 | 0 | 64.827 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
346 | 11 | December | 2.6 | 3.201 | 0 | 70.119 | 70.119 | 0 | 70.119 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
346 | 12 | December | 2.6 | 3.201 | 0 | 84.672 | 84.672 | 0 | 84.672 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
346 | 13 | December | 3.6 | 4.4321 | 75.65 | 80.703 | 156.353 | 0 | 156.353 | 0 | 0 | 48.3841 | 51.6159 | 0 | 48.3841 | 51.6159 | 0
346 | 14 | December | 5.7 | 7.0175 | 504.9 | 58.212 | 563.112 | 0 | 563.112 | 0 | 0 | 89.6624 | 10.3376 | 0 | 89.6624 | 10.3376 | 0
346 | 15 | December | 9.3 | 11.4496 | 1598.85 | 25.137 | 1623.987 | 0 | 1623.987 | 0 | 0 | 98.4521 | 1.5479 | 0 | 98.4521 | 1.5479 | 0
346 | 16 | December | 11.8 | 14.5275 | 1700 | 2.646 | 1702.646 | 0 | 1702.646 | 0 | 0 | 99.8446 | 0.15541 | 0 | 99.8446 | 0.15541 | 0
346 | 17 | December | 12.9 | 15.8818 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
346 | 18 | December | 11.8 | 14.5275 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
346 | 19 | December | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
346 | 20 | December | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
346 | 21 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
346 | 22 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
346 | 23 | December | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
346 | 24 | December | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
347 | 1 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
347 | 2 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
347 | 3 | December | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
347 | 4 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
347 | 5 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
347 | 6 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
347 | 7 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
347 | 8 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
347 | 9 | December | 5.1 | 6.2788 | 312.8 | 15.876 | 328.676 | 0 | 328.676 | 0 | 0 | 95.1697 | 4.8303 | 0 | 95.1697 | 4.8303 | 0
347 | 10 | December | 5.7 | 7.0175 | 504.9 | 63.504 | 568.404 | 0 | 568.404 | 0 | 0 | 88.8277 | 11.1723 | 0 | 88.8277 | 11.1723 | 0
347 | 11 | December | 4.6 | 5.6633 | 237.15 | 114.688 | 351.838 | 0 | 351.838 | 0 | 0 | 67.4032 | 32.5968 | 0 | 67.4032 | 32.5968 | 0
347 | 12 | December | 5.1 | 6.2788 | 312.8 | 144.6537 | 457.4537 | 0 | 457.4537 | 0 | 0 | 68.3785 | 31.6215 | 0 | 68.3785 | 31.6215 | 0
347 | 13 | December | 5.1 | 6.2788 | 312.8 | 137.3026 | 450.1026 | 0 | 450.1026 | 0 | 0 | 69.4953 | 30.5047 | 0 | 69.4953 | 30.5047 | 0
347 | 14 | December | 4.1 | 5.0477 | 173.4 | 93.9513 | 267.3513 | 0 | 267.3513 | 0 | 0 | 64.8585 | 35.1415 | 0 | 64.8585 | 35.1415 | 0
347 | 15 | December | 3.1 | 3.8165 | 0 | 39.69 | 39.69 | 0 | 39.69 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
347 | 16 | December | 4.6 | 5.6633 | 237.15 | 5.292 | 242.442 | 0 | 242.442 | 0 | 0 | 97.8172 | 2.1828 | 0 | 97.8172 | 2.1828 | 0
347 | 17 | December | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347 | 18 | December | 12.9 | 15.8818 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
347 | 19 | December | 13.9 | 17.1129 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
347 | 20 | December | 13.9 | 17.1129 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
347 | 21 | December | 12.3 | 15.1431 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
347 | 22 | December | 12.3 | 15.1431 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
347 | 23 | December | 13.4 | 16.4973 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
347 | 24 | December | 13.4 | 16.4973 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
348 | 1 | December | 11.8 | 14.5275 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
348 | 2 | December | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
348 | 3 | December | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
348 | 4 | December | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
348 | 5 | December | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
348 | 6 | December | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
348 | 7 | December | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
348 | 8 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
348 | 9 | December | 3.6 | 4.4321 | 75.65 | 15.876 | 91.526 | 0 | 91.526 | 0 | 0 | 82.6541 | 17.3459 | 0 | 82.6541 | 17.3459 | 0
348 | 10 | December | 1.5 | 1.8467 | 0 | 62.181 | 62.181 | 0 | 62.181 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
348 | 11 | December | 2.1 | 2.5854 | 0 | 115.9997 | 115.9997 | 0 | 115.9997 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
348 | 12 | December | 3.1 | 3.8165 | 0 | 151.2506 | 151.2506 | 0 | 151.2506 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
348 | 13 | December | 3.6 | 4.4321 | 75.65 | 142.4939 | 218.1439 | 0 | 218.1439 | 0 | 0 | 34.6789 | 65.3211 | 0 | 34.6789 | 65.3211 | 0
348 | 14 | December | 4.6 | 5.6633 | 237.15 | 96.1643 | 333.3143 | 0 | 333.3143 | 0 | 0 | 71.1491 | 28.8509 | 0 | 71.1491 | 28.8509 | 0
348 | 15 | December | 4.6 | 5.6633 | 237.15 | 39.69 | 276.84 | 0 | 276.84 | 0 | 0 | 85.6632 | 14.3368 | 0 | 85.6632 | 14.3368 | 0
348 | 16 | December | 4.6 | 5.6633 | 237.15 | 5.292 | 242.442 | 0 | 242.442 | 0 | 0 | 97.8172 | 2.1828 | 0 | 97.8172 | 2.1828 | 0
348 | 17 | December | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
348 | 18 | December | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
348 | 19 | December | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
348 | 20 | December | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
348 | 21 | December | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
348 | 22 | December | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
348 | 23 | December | 12.3 | 15.1431 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
348 | 24 | December | 14.9 | 18.3441 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
349 | 1 | December | 13.9 | 17.1129 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
349 | 2 | December | 13.4 | 16.4973 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
349 | 3 | December | 13.9 | 17.1129 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
349 | 4 | December | 12.9 | 15.8818 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
349 | 5 | December | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
349 | 6 | December | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
349 | 7 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
349 | 8 | December | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
349 | 9 | December | 6.7 | 8.2487 | 761.6 | 26.46 | 788.06 | 0 | 788.06 | 0 | 0 | 96.6424 | 3.3576 | 0 | 96.6424 | 3.3576 | 0
349 | 10 | December | 5.1 | 6.2788 | 312.8 | 225.5767 | 538.3767 | 0 | 538.3767 | 0 | 0 | 58.1006 | 41.8994 | 0 | 58.1006 | 41.8994 | 0
349 | 11 | December | 7.2 | 8.8642 | 908.65 | 493.5752 | 1402.2252 | 0 | 1402.2252 | 0 | 0 | 64.8006 | 35.1994 | 0 | 64.8006 | 35.1994 | 0
349 | 12 | December | 6.2 | 7.6331 | 625.6 | 516.3639 | 1141.9639 | 0 | 1141.9639 | 0 | 0 | 54.7828 | 45.2172 | 0 | 54.7828 | 45.2172 | 0
349 | 13 | December | 6.7 | 8.2487 | 761.6 | 328.8238 | 1090.4238 | 0 | 1090.4238 | 0 | 0 | 69.8444 | 30.1556 | 0 | 69.8444 | 30.1556 | 0
349 | 14 | December | 4.6 | 5.6633 | 237.15 | 97.0774 | 334.2274 | 0 | 334.2274 | 0 | 0 | 70.9547 | 29.0453 | 0 | 70.9547 | 29.0453 | 0
349 | 15 | December | 5.1 | 6.2788 | 312.8 | 141.6899 | 454.4899 | 0 | 454.4899 | 0 | 0 | 68.8244 | 31.1756 | 0 | 68.8244 | 31.1756 | 0
349 | 16 | December | 6.2 | 7.6331 | 625.6 | 9.261 | 634.861 | 0 | 634.861 | 0 | 0 | 98.5413 | 1.4587 | 0 | 98.5413 | 1.4587 | 0
349 | 17 | December | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
349 | 18 | December | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
349 | 19 | December | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
349 | 20 | December | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
349 | 21 | December | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
349 | 22 | December | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
349 | 23 | December | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
349 | 24 | December | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
350 | 1 | December | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
350 | 2 | December | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
350 | 3 | December | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
350 | 4 | December | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
350 | 5 | December | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
350 | 6 | December | 12.9 | 15.8818 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
350 | 7 | December | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
350 | 8 | December | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
350 | 9 | December | 9.8 | 12.0652 | 1683.85 | 14.553 | 1698.403 | 0 | 1698.403 | 0 | 0 | 99.1431 | 0.85686 | 0 | 99.1431 | 0.85686 | 0
350 | 10 | December | 9.8 | 12.0652 | 1683.85 | 60.858 | 1744.708 | 0 | 1744.708 | 0 | 0 | 96.5119 | 3.4881 | 0 | 96.5119 | 3.4881 | 0
350 | 11 | December | 10.8 | 13.2964 | 1698.3 | 113.3341 | 1811.6341 | 0 | 1811.6341 | 0 | 0 | 93.7441 | 6.2559 | 0 | 93.7441 | 6.2559 | 0
350 | 12 | December | 11.3 | 13.9119 | 1700 | 144.3936 | 1844.3936 | 0 | 1844.3936 | 0 | 0 | 92.1712 | 7.8288 | 0 | 92.1712 | 7.8288 | 0
350 | 13 | December | 10.3 | 12.6808 | 1694.9 | 135.9764 | 1830.8764 | 0 | 1830.8764 | 0 | 0 | 92.5732 | 7.4268 | 0 | 92.5732 | 7.4268 | 0
350 | 14 | December | 11.3 | 13.9119 | 1700 | 95.7367 | 1795.7367 | 0 | 1795.7367 | 0 | 0 | 94.6687 | 5.3313 | 0 | 94.6687 | 5.3313 | 0
350 | 15 | December | 11.3 | 13.9119 | 1700 | 76.1431 | 1776.1431 | 0 | 1776.1431 | 0 | 0 | 95.713 | 4.287 | 0 | 95.713 | 4.287 | 0
350 | 16 | December | 11.3 | 13.9119 | 1700 | 9.261 | 1709.261 | 0 | 1709.261 | 0 | 0 | 99.4582 | 0.54181 | 0 | 99.4582 | 0.54181 | 0
350 | 17 | December | 11.8 | 14.5275 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
350 | 18 | December | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
350 | 19 | December | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
350 | 20 | December | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
350 | 21 | December | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
350 | 22 | December | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
350 | 23 | December | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
350 | 24 | December | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
351 | 1 | December | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
351 | 2 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
351 | 3 | December | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
351 | 4 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
351 | 5 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
351 | 6 | December | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
351 | 7 | December | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
351 | 8 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
351 | 9 | December | 4.1 | 5.0477 | 173.4 | 21.168 | 194.568 | 0 | 194.568 | 0 | 0 | 89.1205 | 10.8795 | 0 | 89.1205 | 10.8795 | 0
351 | 10 | December | 5.1 | 6.2788 | 312.8 | 59.535 | 372.335 | 0 | 372.335 | 0 | 0 | 84.0104 | 15.9896 | 0 | 84.0104 | 15.9896 | 0
351 | 11 | December | 4.6 | 5.6633 | 237.15 | 112.0026 | 349.1526 | 0 | 349.1526 | 0 | 0 | 67.9216 | 32.0784 | 0 | 67.9216 | 32.0784 | 0
351 | 12 | December | 5.7 | 7.0175 | 504.9 | 144.3851 | 649.2851 | 0 | 649.2851 | 0 | 0 | 77.7624 | 22.2376 | 0 | 77.7624 | 22.2376 | 0
351 | 13 | December | 4.6 | 5.6633 | 237.15 | 319.8101 | 556.9601 | 0 | 556.9601 | 0 | 0 | 42.5794 | 57.4206 | 0 | 42.5794 | 57.4206 | 0
351 | 14 | December | 3.1 | 3.8165 | 0 | 245.3727 | 245.3727 | 0 | 245.3727 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
351 | 15 | December | 3.6 | 4.4321 | 75.65 | 39.69 | 115.34 | 0 | 115.34 | 0 | 0 | 65.5887 | 34.4113 | 0 | 65.5887 | 34.4113 | 0
351 | 16 | December | 2.1 | 2.5854 | 0 | 2.646 | 2.646 | 0 | 2.646 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
351 | 17 | December | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
351 | 18 | December | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
351 | 19 | December | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
351 | 20 | December | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
351 | 21 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
351 | 22 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
351 | 23 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
351 | 24 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
352 | 1 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
352 | 2 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
352 | 3 | December | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
352 | 4 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
352 | 5 | December | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
352 | 6 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
352 | 7 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
352 | 8 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
352 | 9 | December | 6.7 | 8.2487 | 761.6 | 13.23 | 774.83 | 0 | 774.83 | 0 | 0 | 98.2925 | 1.7075 | 0 | 98.2925 | 1.7075 | 0
352 | 10 | December | 7.7 | 9.4798 | 1059.95 | 58.212 | 1118.162 | 0 | 1118.162 | 0 | 0 | 94.794 | 5.206 | 0 | 94.794 | 5.206 | 0
352 | 11 | December | 9.3 | 11.4496 | 1598.85 | 109.6039 | 1708.4539 | 0 | 1708.4539 | 0 | 0 | 93.5846 | 6.4154 | 0 | 93.5846 | 6.4154 | 0
352 | 12 | December | 9.3 | 11.4496 | 1598.85 | 80.703 | 1679.553 | 0 | 1679.553 | 0 | 0 | 95.195 | 4.805 | 0 | 95.195 | 4.805 | 0
352 | 13 | December | 10.3 | 12.6808 | 1694.9 | 76.734 | 1771.634 | 0 | 1771.634 | 0 | 0 | 95.6687 | 4.3313 | 0 | 95.6687 | 4.3313 | 0
352 | 14 | December | 10.3 | 12.6808 | 1694.9 | 56.889 | 1751.789 | 0 | 1751.789 | 0 | 0 | 96.7525 | 3.2475 | 0 | 96.7525 | 3.2475 | 0
352 | 15 | December | 9.8 | 12.0652 | 1683.85 | 25.137 | 1708.987 | 0 | 1708.987 | 0 | 0 | 98.5291 | 1.4709 | 0 | 98.5291 | 1.4709 | 0
352 | 16 | December | 10.8 | 13.2964 | 1698.3 | 2.646 | 1700.946 | 0 | 1700.946 | 0 | 0 | 99.8444 | 0.15556 | 0 | 99.8444 | 0.15556 | 0
352 | 17 | December | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
352 | 18 | December | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
352 | 19 | December | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
352 | 20 | December | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
352 | 21 | December | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
352 | 22 | December | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
352 | 23 | December | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
352 | 24 | December | 11.8 | 14.5275 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
353 | 1 | December | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
353 | 2 | December | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
353 | 3 | December | 12.9 | 15.8818 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
353 | 4 | December | 13.9 | 17.1129 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
353 | 5 | December | 12.9 | 15.8818 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
353 | 6 | December | 12.9 | 15.8818 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
353 | 7 | December | 11.8 | 14.5275 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
353 | 8 | December | 12.3 | 15.1431 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
353 | 9 | December | 12.3 | 15.1431 | 1700 | 13.23 | 1713.23 | 0 | 1713.23 | 0 | 0 | 99.2278 | 0.77223 | 0 | 99.2278 | 0.77223 | 0
353 | 10 | December | 12.3 | 15.1431 | 1700 | 58.212 | 1758.212 | 0 | 1758.212 | 0 | 0 | 96.6891 | 3.3109 | 0 | 96.6891 | 3.3109 | 0
353 | 11 | December | 12.9 | 15.8818 | 1700 | 107.2079 | 1807.2079 | 0 | 1807.2079 | 0 | 0 | 94.0678 | 5.9322 | 0 | 94.0678 | 5.9322 | 0
353 | 12 | December | 14.9 | 18.3441 | 1700 | 139.5304 | 1839.5304 | 0 | 1839.5304 | 0 | 0 | 92.4149 | 7.5851 | 0 | 92.4149 | 7.5851 | 0
353 | 13 | December | 17.5 | 21.545 | 1700 | 133.6293 | 1833.6293 | 0 | 1833.6293 | 0 | 0 | 92.7123 | 7.2877 | 0 | 92.7123 | 7.2877 | 0
353 | 14 | December | 13.4 | 16.4973 | 1700 | 160.8425 | 1860.8425 | 0 | 1860.8425 | 0 | 0 | 91.3565 | 8.6435 | 0 | 91.3565 | 8.6435 | 0
353 | 15 | December | 13.4 | 16.4973 | 1700 | 55.6087 | 1755.6087 | 0 | 1755.6087 | 0 | 0 | 96.8325 | 3.1675 | 0 | 96.8325 | 3.1675 | 0
353 | 16 | December | 10.8 | 13.2964 | 1698.3 | 6.615 | 1704.915 | 0 | 1704.915 | 0 | 0 | 99.612 | 0.388 | 0 | 99.612 | 0.388 | 0
353 | 17 | December | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
353 | 18 | December | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
353 | 19 | December | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
353 | 20 | December | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
353 | 21 | December | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
353 | 22 | December | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
353 | 23 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
353 | 24 | December | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
354 | 1 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
354 | 2 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
354 | 3 | December | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
354 | 4 | December | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
354 | 5 | December | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
354 | 6 | December | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
354 | 7 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
354 | 8 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
354 | 9 | December | 3.1 | 3.8165 | 0 | 7.938 | 7.938 | 0 | 7.938 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
354 | 10 | December | 2.1 | 2.5854 | 0 | 35.721 | 35.721 | 0 | 35.721 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
354 | 11 | December | 2.6 | 3.201 | 0 | 115.4803 | 115.4803 | 0 | 115.4803 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
354 | 12 | December | 2.1 | 2.5854 | 0 | 80.703 | 80.703 | 0 | 80.703 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
354 | 13 | December | 1.5 | 1.8467 | 0 | 78.057 | 78.057 | 0 | 78.057 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
354 | 14 | December | 1 | 1.2311 | 0 | 96.6528 | 96.6528 | 0 | 96.6528 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
354 | 15 | December | 0 | 0 | 0 | 25.137 | 25.137 | 0 | 25.137 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
354 | 16 | December | 1 | 1.2311 | 0 | 3.969 | 3.969 | 0 | 3.969 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
354 | 17 | December | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
354 | 18 | December | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
354 | 19 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
354 | 20 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
354 | 21 | December | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
354 | 22 | December | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
354 | 23 | December | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
354 | 24 | December | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
355 | 1 | December | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
355 | 2 | December | 12.3 | 15.1431 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
355 | 3 | December | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
355 | 4 | December | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
355 | 5 | December | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
355 | 6 | December | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
355 | 7 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
355 | 8 | December | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
355 | 9 | December | 7.2 | 8.8642 | 908.65 | 13.23 | 921.88 | 0 | 921.88 | 0 | 0 | 98.5649 | 1.4351 | 0 | 98.5649 | 1.4351 | 0
355 | 10 | December | 4.6 | 5.6633 | 237.15 | 56.889 | 294.039 | 0 | 294.039 | 0 | 0 | 80.6526 | 19.3474 | 0 | 80.6526 | 19.3474 | 0
355 | 11 | December | 4.6 | 5.6633 | 237.15 | 109.5897 | 346.7397 | 0 | 346.7397 | 0 | 0 | 68.3943 | 31.6057 | 0 | 68.3943 | 31.6057 | 0
355 | 12 | December | 7.7 | 9.4798 | 1059.95 | 145.0272 | 1204.9772 | 0 | 1204.9772 | 0 | 0 | 87.9643 | 12.0357 | 0 | 87.9643 | 12.0357 | 0
355 | 13 | December | 6.2 | 7.6331 | 625.6 | 138.8557 | 764.4557 | 0 | 764.4557 | 0 | 0 | 81.836 | 18.164 | 0 | 81.836 | 18.164 | 0
355 | 14 | December | 6.2 | 7.6331 | 625.6 | 158.7293 | 784.3293 | 0 | 784.3293 | 0 | 0 | 79.7624 | 20.2376 | 0 | 79.7624 | 20.2376 | 0
355 | 15 | December | 6.7 | 8.2487 | 761.6 | 134.9166 | 896.5166 | 0 | 896.5166 | 0 | 0 | 84.951 | 15.049 | 0 | 84.951 | 15.049 | 0
355 | 16 | December | 7.2 | 8.8642 | 908.65 | 9.261 | 917.911 | 0 | 917.911 | 0 | 0 | 98.9911 | 1.0089 | 0 | 98.9911 | 1.0089 | 0
355 | 17 | December | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
355 | 18 | December | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
355 | 19 | December | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
355 | 20 | December | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
355 | 21 | December | 10.8 | 13.2964 | 1698.3 | 0 | 1698.3 | 0 | 1698.3 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
355 | 22 | December | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
355 | 23 | December | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
355 | 24 | December | 10.3 | 12.6808 | 1694.9 | 0 | 1694.9 | 0 | 1694.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
356 | 1 | December | 9.8 | 12.0652 | 1683.85 | 0 | 1683.85 | 0 | 1683.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
356 | 2 | December | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
356 | 3 | December | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
356 | 4 | December | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
356 | 5 | December | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
356 | 6 | December | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
356 | 7 | December | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
356 | 8 | December | 7.7 | 9.4798 | 1059.95 | 0 | 1059.95 | 0 | 1059.95 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
356 | 9 | December | 8.7 | 10.711 | 1490.05 | 11.907 | 1501.957 | 0 | 1501.957 | 0 | 0 | 99.2072 | 0.79277 | 0 | 99.2072 | 0.79277 | 0
356 | 10 | December | 7.2 | 8.8642 | 908.65 | 35.721 | 944.371 | 0 | 944.371 | 0 | 0 | 96.2175 | 3.7825 | 0 | 96.2175 | 3.7825 | 0
356 | 11 | December | 8.7 | 10.711 | 1490.05 | 64.827 | 1554.877 | 0 | 1554.877 | 0 | 0 | 95.8307 | 4.1693 | 0 | 95.8307 | 4.1693 | 0
356 | 12 | December | 7.7 | 9.4798 | 1059.95 | 80.703 | 1140.653 | 0 | 1140.653 | 0 | 0 | 92.9248 | 7.0752 | 0 | 92.9248 | 7.0752 | 0
356 | 13 | December | 6.7 | 8.2487 | 761.6 | 78.057 | 839.657 | 0 | 839.657 | 0 | 0 | 90.7037 | 9.2963 | 0 | 90.7037 | 9.2963 | 0
356 | 14 | December | 6.2 | 7.6331 | 625.6 | 58.212 | 683.812 | 0 | 683.812 | 0 | 0 | 91.4871 | 8.5129 | 0 | 91.4871 | 8.5129 | 0
356 | 15 | December | 6.2 | 7.6331 | 625.6 | 41.013 | 666.613 | 0 | 666.613 | 0 | 0 | 93.8476 | 6.1524 | 0 | 93.8476 | 6.1524 | 0
356 | 16 | December | 6.2 | 7.6331 | 625.6 | 5.292 | 630.892 | 0 | 630.892 | 0 | 0 | 99.1612 | 0.83881 | 0 | 99.1612 | 0.83881 | 0
356 | 17 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
356 | 18 | December | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
356 | 19 | December | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
356 | 20 | December | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
356 | 21 | December | 12.9 | 15.8818 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
356 | 22 | December | 11.3 | 13.9119 | 1700 | 0 | 1700 | 0 | 1700 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
356 | 23 | December | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
356 | 24 | December | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
357 | 1 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
357 | 2 | December | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
357 | 3 | December | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
357 | 4 | December | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
357 | 5 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
357 | 6 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
357 | 7 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
357 | 8 | December | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
357 | 9 | December | 5.1 | 6.2788 | 312.8 | 11.907 | 324.707 | 0 | 324.707 | 0 | 0 | 96.333 | 3.667 | 0 | 96.333 | 3.667 | 0
357 | 10 | December | 5.1 | 6.2788 | 312.8 | 56.889 | 369.689 | 0 | 369.689 | 0 | 0 | 84.6117 | 15.3883 | 0 | 84.6117 | 15.3883 | 0
357 | 11 | December | 5.1 | 6.2788 | 312.8 | 201.6619 | 514.4619 | 0 | 514.4619 | 0 | 0 | 60.8014 | 39.1986 | 0 | 60.8014 | 39.1986 | 0
357 | 12 | December | 5.1 | 6.2788 | 312.8 | 379.5378 | 692.3378 | 0 | 692.3378 | 0 | 0 | 45.1803 | 54.8197 | 0 | 45.1803 | 54.8197 | 0
357 | 13 | December | 4.6 | 5.6633 | 237.15 | 142.7866 | 379.9366 | 0 | 379.9366 | 0 | 0 | 62.4183 | 37.5817 | 0 | 62.4183 | 37.5817 | 0
357 | 14 | December | 5.7 | 7.0175 | 504.9 | 252.5776 | 757.4776 | 0 | 757.4776 | 0 | 0 | 66.6554 | 33.3446 | 0 | 66.6554 | 33.3446 | 0
357 | 15 | December | 5.1 | 6.2788 | 312.8 | 42.336 | 355.136 | 0 | 355.136 | 0 | 0 | 88.0789 | 11.9211 | 0 | 88.0789 | 11.9211 | 0
357 | 16 | December | 5.1 | 6.2788 | 312.8 | 5.292 | 318.092 | 0 | 318.092 | 0 | 0 | 98.3363 | 1.6637 | 0 | 98.3363 | 1.6637 | 0
357 | 17 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
357 | 18 | December | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
357 | 19 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
357 | 20 | December | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
357 | 21 | December | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
357 | 22 | December | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
357 | 23 | December | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
357 | 24 | December | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
358 | 1 | December | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
358 | 2 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
358 | 3 | December | 5.9 | 7.2638 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
358 | 4 | December | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
358 | 5 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
358 | 6 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
358 | 7 | December | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
358 | 8 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
358 | 9 | December | 6.2 | 7.6331 | 625.6 | 11.907 | 637.507 | 0 | 637.507 | 0 | 0 | 98.1323 | 1.8677 | 0 | 98.1323 | 1.8677 | 0
358 | 10 | December | 6.7 | 8.2487 | 761.6 | 35.721 | 797.321 | 0 | 797.321 | 0 | 0 | 95.5199 | 4.4801 | 0 | 95.5199 | 4.4801 | 0
358 | 11 | December | 7.2 | 8.8642 | 908.65 | 115.4556 | 1024.1056 | 0 | 1024.1056 | 0 | 0 | 88.7262 | 11.2738 | 0 | 88.7262 | 11.2738 | 0
358 | 12 | December | 5.7 | 7.0175 | 504.9 | 141.9692 | 646.8692 | 0 | 646.8692 | 0 | 0 | 78.0529 | 21.9471 | 0 | 78.0529 | 21.9471 | 0
358 | 13 | December | 8.2 | 10.0954 | 1359.15 | 137.105 | 1496.255 | 0 | 1496.255 | 0 | 0 | 90.8368 | 9.1632 | 0 | 90.8368 | 9.1632 | 0
358 | 14 | December | 7.7 | 9.4798 | 1059.95 | 96.6918 | 1156.6418 | 0 | 1156.6418 | 0 | 0 | 91.6403 | 8.3597 | 0 | 91.6403 | 8.3597 | 0
358 | 15 | December | 9.8 | 12.0652 | 1683.85 | 26.46 | 1710.31 | 0 | 1710.31 | 0 | 0 | 98.4529 | 1.5471 | 0 | 98.4529 | 1.5471 | 0
358 | 16 | December | 9.3 | 11.4496 | 1598.85 | 3.969 | 1602.819 | 0 | 1602.819 | 0 | 0 | 99.7524 | 0.24763 | 0 | 99.7524 | 0.24763 | 0
358 | 17 | December | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
358 | 18 | December | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
358 | 19 | December | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
358 | 20 | December | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
358 | 21 | December | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
358 | 22 | December | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
358 | 23 | December | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
358 | 24 | December | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
359 | 1 | December | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
359 | 2 | December | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
359 | 3 | December | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
359 | 4 | December | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
359 | 5 | December | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
359 | 6 | December | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
359 | 7 | December | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
359 | 8 | December | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
359 | 9 | December | 1 | 1.2311 | 0 | 11.907 | 11.907 | 0 | 11.907 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
359 | 10 | December | 1 | 1.2311 | 0 | 35.721 | 35.721 | 0 | 35.721 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
359 | 11 | December | 1 | 1.2311 | 0 | 111.7119 | 111.7119 | 0 | 111.7119 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
359 | 12 | December | 1 | 1.2311 | 0 | 146.1616 | 146.1616 | 0 | 146.1616 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
359 | 13 | December | 2.6 | 3.201 | 0 | 138.4492 | 138.4492 | 0 | 138.4492 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
359 | 14 | December | 2.6 | 3.201 | 0 | 98.9292 | 98.9292 | 0 | 98.9292 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
359 | 15 | December | 3.1 | 3.8165 | 0 | 43.659 | 43.659 | 0 | 43.659 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
359 | 16 | December | 1 | 1.2311 | 0 | 7.938 | 7.938 | 0 | 7.938 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
359 | 17 | December | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
359 | 18 | December | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
359 | 19 | December | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
359 | 20 | December | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
359 | 21 | December | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
359 | 22 | December | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
359 | 23 | December | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
359 | 24 | December | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
360 | 1 | December | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
360 | 2 | December | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
360 | 3 | December | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
360 | 4 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
360 | 5 | December | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
360 | 6 | December | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
360 | 7 | December | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
360 | 8 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
360 | 9 | December | 7.2 | 8.8642 | 908.65 | 15.876 | 924.526 | 0 | 924.526 | 0 | 0 | 98.2828 | 1.7172 | 0 | 98.2828 | 1.7172 | 0
360 | 10 | December | 8.7 | 10.711 | 1490.05 | 236.2906 | 1726.3406 | 0 | 1726.3406 | 0 | 0 | 86.3126 | 13.6874 | 0 | 86.3126 | 13.6874 | 0
360 | 11 | December | 8.7 | 10.711 | 1490.05 | 110.3892 | 1600.4392 | 0 | 1600.4392 | 0 | 0 | 93.1026 | 6.8974 | 0 | 93.1026 | 6.8974 | 0
360 | 12 | December | 9.8 | 12.0652 | 1683.85 | 239.1828 | 1923.0328 | 0 | 1923.0328 | 0 | 0 | 87.5622 | 12.4378 | 0 | 87.5622 | 12.4378 | 0
360 | 13 | December | 9.8 | 12.0652 | 1683.85 | 479.5009 | 2163.3509 | 1 | 2000 | 163.3509 | 8.1675 | 77.8353 | 15.8075 | 34.0669 | 76.025 | 22.1647 | 9.701
360 | 14 | December | 8.2 | 10.0954 | 1359.15 | 99.3619 | 1458.5119 | 0 | 1458.5119 | 0 | 0 | 93.1874 | 6.8126 | 0 | 93.1874 | 6.8126 | 0
360 | 15 | December | 8.7 | 10.711 | 1490.05 | 43.659 | 1533.709 | 0 | 1533.709 | 0 | 0 | 97.1534 | 2.8466 | 0 | 97.1534 | 2.8466 | 0
360 | 16 | December | 8.2 | 10.0954 | 1359.15 | 6.615 | 1365.765 | 0 | 1365.765 | 0 | 0 | 99.5157 | 0.48434 | 0 | 99.5157 | 0.48434 | 0
360 | 17 | December | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
360 | 18 | December | 8.2 | 10.0954 | 1359.15 | 0 | 1359.15 | 0 | 1359.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
360 | 19 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
360 | 20 | December | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
360 | 21 | December | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
360 | 22 | December | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
360 | 23 | December | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
360 | 24 | December | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
361 | 1 | December | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
361 | 2 | December | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
361 | 3 | December | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
361 | 4 | December | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
361 | 5 | December | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
361 | 6 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
361 | 7 | December | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
361 | 8 | December | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
361 | 9 | December | 3.1 | 3.8165 | 0 | 11.907 | 11.907 | 0 | 11.907 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
361 | 10 | December | 3.1 | 3.8165 | 0 | 55.566 | 55.566 | 0 | 55.566 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
361 | 11 | December | 3.1 | 3.8165 | 0 | 109.3258 | 109.3258 | 0 | 109.3258 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
361 | 12 | December | 4.6 | 5.6633 | 237.15 | 143.1088 | 380.2588 | 0 | 380.2588 | 0 | 0 | 62.3654 | 37.6346 | 0 | 62.3654 | 37.6346 | 0
361 | 13 | December | 4.1 | 5.0477 | 173.4 | 242.1583 | 415.5583 | 0 | 415.5583 | 0 | 0 | 41.727 | 58.273 | 0 | 41.727 | 58.273 | 0
361 | 14 | December | 3.6 | 4.4321 | 75.65 | 184.9762 | 260.6262 | 0 | 260.6262 | 0 | 0 | 29.0262 | 70.9738 | 0 | 29.0262 | 70.9738 | 0
361 | 15 | December | 3.6 | 4.4321 | 75.65 | 44.982 | 120.632 | 0 | 120.632 | 0 | 0 | 62.7114 | 37.2886 | 0 | 62.7114 | 37.2886 | 0
361 | 16 | December | 2.6 | 3.201 | 0 | 6.615 | 6.615 | 0 | 6.615 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0
361 | 17 | December | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
361 | 18 | December | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
361 | 19 | December | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
361 | 20 | December | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
361 | 21 | December | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
361 | 22 | December | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
361 | 23 | December | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
361 | 24 | December | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
362 | 1 | December | 1.5 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
362 | 2 | December | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
362 | 3 | December | 1 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
362 | 4 | December | 2.1 | 2.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
362 | 5 | December | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
362 | 6 | December | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
362 | 7 | December | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
362 | 8 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
362 | 9 | December | 4.1 | 5.0477 | 173.4 | 7.938 | 181.338 | 0 | 181.338 | 0 | 0 | 95.6225 | 4.3775 | 0 | 95.6225 | 4.3775 | 0
362 | 10 | December | 6.7 | 8.2487 | 761.6 | 35.721 | 797.321 | 0 | 797.321 | 0 | 0 | 95.5199 | 4.4801 | 0 | 95.5199 | 4.4801 | 0
362 | 11 | December | 6.2 | 7.6331 | 625.6 | 66.15 | 691.75 | 0 | 691.75 | 0 | 0 | 90.4373 | 9.5627 | 0 | 90.4373 | 9.5627 | 0
362 | 12 | December | 7.2 | 8.8642 | 908.65 | 82.026 | 990.676 | 0 | 990.676 | 0 | 0 | 91.7202 | 8.2798 | 0 | 91.7202 | 8.2798 | 0
362 | 13 | December | 9.3 | 11.4496 | 1598.85 | 80.703 | 1679.553 | 0 | 1679.553 | 0 | 0 | 95.195 | 4.805 | 0 | 95.195 | 4.805 | 0
362 | 14 | December | 9.8 | 12.0652 | 1683.85 | 60.858 | 1744.708 | 0 | 1744.708 | 0 | 0 | 96.5119 | 3.4881 | 0 | 96.5119 | 3.4881 | 0
362 | 15 | December | 9.8 | 12.0652 | 1683.85 | 29.106 | 1712.956 | 0 | 1712.956 | 0 | 0 | 98.3008 | 1.6992 | 0 | 98.3008 | 1.6992 | 0
362 | 16 | December | 7.7 | 9.4798 | 1059.95 | 3.969 | 1063.919 | 0 | 1063.919 | 0 | 0 | 99.6269 | 0.37305 | 0 | 99.6269 | 0.37305 | 0
362 | 17 | December | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
362 | 18 | December | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
362 | 19 | December | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
362 | 20 | December | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
362 | 21 | December | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
362 | 22 | December | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
362 | 23 | December | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
362 | 24 | December | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
363 | 1 | December | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
363 | 2 | December | 2.6 | 3.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
363 | 3 | December | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
363 | 4 | December | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
363 | 5 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
363 | 6 | December | 6.7 | 8.2487 | 761.6 | 0 | 761.6 | 0 | 761.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
363 | 7 | December | 8.7 | 10.711 | 1490.05 | 0 | 1490.05 | 0 | 1490.05 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
363 | 8 | December | 9.3 | 11.4496 | 1598.85 | 0 | 1598.85 | 0 | 1598.85 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
363 | 9 | December | 9.3 | 11.4496 | 1598.85 | 7.938 | 1606.788 | 0 | 1606.788 | 0 | 0 | 99.506 | 0.49403 | 0 | 99.506 | 0.49403 | 0
363 | 10 | December | 10.8 | 13.2964 | 1698.3 | 34.398 | 1732.698 | 0 | 1732.698 | 0 | 0 | 98.0148 | 1.9852 | 0 | 98.0148 | 1.9852 | 0
363 | 11 | December | 11.8 | 14.5275 | 1700 | 64.827 | 1764.827 | 0 | 1764.827 | 0 | 0 | 96.3267 | 3.6733 | 0 | 96.3267 | 3.6733 | 0
363 | 12 | December | 9.3 | 11.4496 | 1598.85 | 82.026 | 1680.876 | 0 | 1680.876 | 0 | 0 | 95.12 | 4.88 | 0 | 95.12 | 4.88 | 0
363 | 13 | December | 7.2 | 8.8642 | 908.65 | 80.703 | 989.353 | 0 | 989.353 | 0 | 0 | 91.8429 | 8.1571 | 0 | 91.8429 | 8.1571 | 0
363 | 14 | December | 5.7 | 7.0175 | 504.9 | 102.5503 | 607.4503 | 0 | 607.4503 | 0 | 0 | 83.1179 | 16.8821 | 0 | 83.1179 | 16.8821 | 0
363 | 15 | December | 6.7 | 8.2487 | 761.6 | 46.305 | 807.905 | 0 | 807.905 | 0 | 0 | 94.2685 | 5.7315 | 0 | 94.2685 | 5.7315 | 0
363 | 16 | December | 5.7 | 7.0175 | 504.9 | 13.23 | 518.13 | 0 | 518.13 | 0 | 0 | 97.4466 | 2.5534 | 0 | 97.4466 | 2.5534 | 0
363 | 17 | December | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
363 | 18 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
363 | 19 | December | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
363 | 20 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
363 | 21 | December | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
363 | 22 | December | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
363 | 23 | December | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
363 | 24 | December | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
364 | 1 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
364 | 2 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
364 | 3 | December | 5.9 | 7.2638 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
364 | 4 | December | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
364 | 5 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
364 | 6 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
364 | 7 | December | 7.2 | 8.8642 | 908.65 | 0 | 908.65 | 0 | 908.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
364 | 8 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
364 | 9 | December | 6.2 | 7.6331 | 625.6 | 11.907 | 637.507 | 0 | 637.507 | 0 | 0 | 98.1323 | 1.8677 | 0 | 98.1323 | 1.8677 | 0
364 | 10 | December | 6.2 | 7.6331 | 625.6 | 56.889 | 682.489 | 0 | 682.489 | 0 | 0 | 91.6645 | 8.3355 | 0 | 91.6645 | 8.3355 | 0
364 | 11 | December | 6.2 | 7.6331 | 625.6 | 110.6586 | 736.2586 | 0 | 736.2586 | 0 | 0 | 84.9701 | 15.0299 | 0 | 84.9701 | 15.0299 | 0
364 | 12 | December | 5.7 | 7.0175 | 504.9 | 82.026 | 586.926 | 0 | 586.926 | 0 | 0 | 86.0245 | 13.9755 | 0 | 86.0245 | 13.9755 | 0
364 | 13 | December | 7.2 | 8.8642 | 908.65 | 80.703 | 989.353 | 0 | 989.353 | 0 | 0 | 91.8429 | 8.1571 | 0 | 91.8429 | 8.1571 | 0
364 | 14 | December | 6.2 | 7.6331 | 625.6 | 62.181 | 687.781 | 0 | 687.781 | 0 | 0 | 90.9592 | 9.0408 | 0 | 90.9592 | 9.0408 | 0
364 | 15 | December | 5.1 | 6.2788 | 312.8 | 29.106 | 341.906 | 0 | 341.906 | 0 | 0 | 91.4871 | 8.5129 | 0 | 91.4871 | 8.5129 | 0
364 | 16 | December | 3.6 | 4.4321 | 75.65 | 5.292 | 80.942 | 0 | 80.942 | 0 | 0 | 93.462 | 6.538 | 0 | 93.462 | 6.538 | 0
364 | 17 | December | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
364 | 18 | December | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
364 | 19 | December | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
364 | 20 | December | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
364 | 21 | December | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
364 | 22 | December | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
364 | 23 | December | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
364 | 24 | December | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
365 | 1 | December | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
365 | 2 | December | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
365 | 3 | December | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
365 | 4 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
365 | 5 | December | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
365 | 6 | December | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
365 | 7 | December | 5.1 | 6.2788 | 312.8 | 0 | 312.8 | 0 | 312.8 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
365 | 8 | December | 6.2 | 7.6331 | 625.6 | 0 | 625.6 | 0 | 625.6 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
365 | 9 | December | 6.7 | 8.2487 | 761.6 | 19.845 | 781.445 | 0 | 781.445 | 0 | 0 | 97.4605 | 2.5395 | 0 | 97.4605 | 2.5395 | 0
365 | 10 | December | 6.2 | 7.6331 | 625.6 | 279.1672 | 904.7672 | 0 | 904.7672 | 0 | 0 | 69.1449 | 30.8551 | 0 | 69.1449 | 30.8551 | 0
365 | 11 | December | 7.7 | 9.4798 | 1059.95 | 404.4642 | 1464.4142 | 0 | 1464.4142 | 0 | 0 | 72.3805 | 27.6195 | 0 | 72.3805 | 27.6195 | 0
365 | 12 | December | 7.2 | 8.8642 | 908.65 | 553.4082 | 1462.0582 | 0 | 1462.0582 | 0 | 0 | 62.1487 | 37.8513 | 0 | 62.1487 | 37.8513 | 0
365 | 13 | December | 6.7 | 8.2487 | 761.6 | 468.2449 | 1229.8449 | 0 | 1229.8449 | 0 | 0 | 61.9265 | 38.0735 | 0 | 61.9265 | 38.0735 | 0
365 | 14 | December | 5.7 | 7.0175 | 504.9 | 353.2443 | 858.1443 | 0 | 858.1443 | 0 | 0 | 58.8363 | 41.1637 | 0 | 58.8363 | 41.1637 | 0
365 | 15 | December | 5.7 | 7.0175 | 504.9 | 180.4035 | 685.3035 | 0 | 685.3035 | 0 | 0 | 73.6754 | 26.3246 | 0 | 73.6754 | 26.3246 | 0
365 | 16 | December | 5.1 | 6.2788 | 312.8 | 7.938 | 320.738 | 0 | 320.738 | 0 | 0 | 97.5251 | 2.4749 | 0 | 97.5251 | 2.4749 | 0
365 | 17 | December | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
365 | 18 | December | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
365 | 19 | December | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
365 | 20 | December | 5.7 | 7.0175 | 504.9 | 0 | 504.9 | 0 | 504.9 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
365 | 21 | December | 4.6 | 5.6633 | 237.15 | 0 | 237.15 | 0 | 237.15 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
365 | 22 | December | 3.1 | 3.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
365 | 23 | December | 4.1 | 5.0477 | 173.4 | 0 | 173.4 | 0 | 173.4 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
365 | 24 | December | 3.6 | 4.4321 | 75.65 | 0 | 75.65 | 0 | 75.65 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4.1
3.6
4.6
4.1
3.6
4.6
5.1
4.1
4.1
5.1
6.2
6.7
6.2
7.7
7.2
6.7
5.7
5.7
5.1
4.6
3.6
4.6
5.7
4.6
3.1
4.1
3.6
Note on H3: Jenny MacLean: Do NOT enter data here - informatin pulled from PV data sheet

## PV data and calcs
Location Data: | HEMSBY |  |  | Panel Data: | (Degrees) | (Rads) |  | Output Summary:
| (Degrees) | (Rads) |  | Orientation, ψ | 0 | 0 | (S=0 SE=-45 E=-90 NE=-135 | Total electrical output (MWh) |  | 1628.9844
latitude, φ: | 52.68 | 0.91944 |  | Tilt, β | 30 | 0.5236 | SW=45 W=90 N=180, etc) | Mean solar | (kW) | 185.9571
longitude, long: | 1.68 | 0.029322 |  | Panel efficiency, r | 0.15 |  |  | Mean insolation (W/m2) |  | 117.131
ref longitude, LSTM: | 0 | 0 |  | Performance factor | 0.9
Daylight hours | 3157 | α >=12.5 |  | Area (m^2), A | 11760
Date | Time | direct solar | diffuse solar |  | Declination angle | Day angle (use in EoT) | Equation of time | Time correction factor | Local solar time | Hour angle | Solar elevation | Direct solar radiation received | Diffuse solar radiation received | Total solar | Solar panel hourly energy | Daylight hour?
[5 empty] | (Rads) | (Rads) |  | (hours) | (hours) | (RADS) | (Degrees) | (W/m^2) | (W/m^2) | (W/m^2) | (kWh) | α >=12.5
DOY | hours | W/m^2 | W/m^2 |  | δ | B | EoT | TC | LST | HRA | α | Bm | D |  | Pvout
1 | 1 | 0 | 0 |  | -0.40119 | -1.3771 | -3.7052 | 3.0148 | 1.0502 | -2.8666 | -57.9646 | 0 | 0 | 0 | 0 | 0
1 | 2 | 0 | 0 |  | -0.40119 | -1.3771 | -3.7052 | 3.0148 | 2.0502 | -2.6048 | -52.204 | 0 | 0 | 0 | 0 | 0
1 | 3 | 0 | 0 |  | -0.40119 | -1.3771 | -3.7052 | 3.0148 | 3.0502 | -2.343 | -44.426 | 0 | 0 | 0 | 0 | 0
1 | 4 | 0 | 0 |  | -0.40119 | -1.3771 | -3.7052 | 3.0148 | 4.0502 | -2.0812 | -35.6787 | 0 | 0 | 0 | 0 | 0
1 | 5 | 0 | 0 |  | -0.40119 | -1.3771 | -3.7052 | 3.0148 | 5.0502 | -1.8194 | -26.6095 | 0 | 0 | 0 | 0 | 0
1 | 6 | 0 | 0 |  | -0.40119 | -1.3771 | -3.7052 | 3.0148 | 6.0502 | -1.5576 | -17.6508 | 0 | 0 | 0 | 0 | 0
1 | 7 | 0 | 0 |  | -0.40119 | -1.3771 | -3.7052 | 3.0148 | 7.0502 | -1.2958 | -9.1503 | 0 | 0 | 0 | 0 | 0
1 | 8 | 0 | 0 |  | -0.40119 | -1.3771 | -3.7052 | 3.0148 | 8.0502 | -1.034 | -1.4417 | 0 | 0 | 0 | 0 | 0
1 | 9 | 0 | 18 |  | -0.40119 | -1.3771 | -3.7052 | 3.0148 | 9.0502 | -0.77224 | 5.1208 | 0 | 15 | 15 | 23.814 | 0
1 | 10 | 60 | 75 |  | -0.40119 | -1.3771 | -3.7052 | 3.0148 | 10.0502 | -0.51044 | 10.1616 | 35.4336 | 62.5 | 97.9336 | 155.4795 | 0
1 | 11 | 406 | 63 |  | -0.40119 | -1.3771 | -3.7052 | 3.0148 | 11.0502 | -0.24864 | 13.321 | 273.1223 | 52.5 | 325.6223 | 516.958 | 1
1 | 12 | 513 | 64 |  | -0.40119 | -1.3771 | -3.7052 | 3.0148 | 12.0502 | 0.013155 | 14.3309 | 358.4658 | 53.3333 | 411.7991 | 653.7723 | 1
1 | 13 | 61 | 90 |  | -0.40119 | -1.3771 | -3.7052 | 3.0148 | 13.0502 | 0.27495 | 13.0973 | 40.6828 | 75 | 115.6828 | 183.658 | 1
1 | 14 | 351 | 69 |  | -0.40119 | -1.3771 | -3.7052 | 3.0148 | 14.0502 | 0.53675 | 9.7345 | 203.365 | 57.5 | 260.865 | 414.1492 | 0
1 | 15 | 44 | 47 |  | -0.40119 | -1.3771 | -3.7052 | 3.0148 | 15.0502 | 0.79855 | 4.5238 | 19.4523 | 39.1667 | 58.619 | 93.0635 | 0
1 | 16 | 0 | 7 |  | -0.40119 | -1.3771 | -3.7052 | 3.0148 | 16.0502 | 1.0604 | -2.1706 | 0 | 5.8333 | 5.8333 | 9.261 | 0
1 | 17 | 0 | 0 |  | -0.40119 | -1.3771 | -3.7052 | 3.0148 | 17.0502 | 1.3222 | -9.9744 | 0 | 0 | 0 | 0 | 0
1 | 18 | 0 | 0 |  | -0.40119 | -1.3771 | -3.7052 | 3.0148 | 18.0502 | 1.584 | -18.5359 | 0 | 0 | 0 | 0 | 0
1 | 19 | 0 | 0 |  | -0.40119 | -1.3771 | -3.7052 | 3.0148 | 19.0502 | 1.8458 | -27.5221 | 0 | 0 | 0 | 0 | 0
1 | 20 | 0 | 0 |  | -0.40119 | -1.3771 | -3.7052 | 3.0148 | 20.0502 | 2.1075 | -36.5808 | 0 | 0 | 0 | 0 | 0
1 | 21 | 0 | 0 |  | -0.40119 | -1.3771 | -3.7052 | 3.0148 | 21.0502 | 2.3693 | -45.2651 | 0 | 0 | 0 | 0 | 0
1 | 22 | 0 | 0 |  | -0.40119 | -1.3771 | -3.7052 | 3.0148 | 22.0502 | 2.6311 | -52.8958 | 0 | 0 | 0 | 0 | 0
1 | 23 | 0 | 0 |  | -0.40119 | -1.3771 | -3.7052 | 3.0148 | 23.0502 | 2.8929 | -58.3775 | 0 | 0 | 0 | 0 | 0
1 | 24 | 0 | 0 |  | -0.40119 | -1.3771 | -3.7052 | 3.0148 | 24.0502 | 3.1547 | -60.3006 | 0 | 0 | 0 | 0 | 0
2 | 1 | 0 | 0 |  | -0.39969 | -1.3599 | -4.1497 | 2.5703 | 1.0428 | -2.8686 | -57.9148 | 0 | 0 | 0 | 0 | 0
2 | 2 | 0 | 0 |  | -0.39969 | -1.3599 | -4.1497 | 2.5703 | 2.0428 | -2.6068 | -52.1817 | 0 | 0 | 0 | 0 | 0
2 | 3 | 0 | 0 |  | -0.39969 | -1.3599 | -4.1497 | 2.5703 | 3.0428 | -2.345 | -44.4202 | 0 | 0 | 0 | 0 | 0
2 | 4 | 0 | 0 |  | -0.39969 | -1.3599 | -4.1497 | 2.5703 | 4.0428 | -2.0832 | -35.6803 | 0 | 0 | 0 | 0 | 0
2 | 5 | 0 | 0 |  | -0.39969 | -1.3599 | -4.1497 | 2.5703 | 5.0428 | -1.8214 | -26.6122 | 0 | 0 | 0 | 0 | 0
2 | 6 | 0 | 0 |  | -0.39969 | -1.3599 | -4.1497 | 2.5703 | 6.0428 | -1.5596 | -17.6499 | 0 | 0 | 0 | 0 | 0
2 | 7 | 0 | 0 |  | -0.39969 | -1.3599 | -4.1497 | 2.5703 | 7.0428 | -1.2978 | -9.1417 | 0 | 0 | 0 | 0 | 0
2 | 8 | 0 | 0 |  | -0.39969 | -1.3599 | -4.1497 | 2.5703 | 8.0428 | -1.036 | -1.422 | 0 | 0 | 0 | 0 | 0
2 | 9 | 0 | 10 |  | -0.39969 | -1.3599 | -4.1497 | 2.5703 | 9.0428 | -0.77418 | 5.1548 | 0 | 8.3333 | 8.3333 | 13.23 | 0
2 | 10 | 286 | 31 |  | -0.39969 | -1.3599 | -4.1497 | 2.5703 | 10.0428 | -0.51238 | 10.2124 | 168.9555 | 25.8333 | 194.7888 | 309.2467 | 0
2 | 11 | 224 | 81 |  | -0.39969 | -1.3599 | -4.1497 | 2.5703 | 11.0428 | -0.25058 | 13.3898 | 150.8325 | 67.5 | 218.3325 | 346.6247 | 1
2 | 12 | 113 | 110 |  | -0.39969 | -1.3599 | -4.1497 | 2.5703 | 12.0428 | 0.011215 | 14.4173 | 79.0833 | 91.6667 | 170.7499 | 271.0826 | 1
2 | 13 | 385 | 79 |  | -0.39969 | -1.3599 | -4.1497 | 2.5703 | 13.0428 | 0.27301 | 13.199 | 257.3438 | 65.8333 | 323.1771 | 513.076 | 1
2 | 14 | 239 | 74 |  | -0.39969 | -1.3599 | -4.1497 | 2.5703 | 14.0428 | 0.53481 | 9.8479 | 138.9119 | 61.6667 | 200.5786 | 318.4386 | 0
2 | 15 | 238 | 44 |  | -0.39969 | -1.3599 | -4.1497 | 2.5703 | 15.0428 | 0.79661 | 4.6454 | 105.7156 | 36.6667 | 142.3823 | 226.0461 | 0
2 | 16 | 0 | 13 |  | -0.39969 | -1.3599 | -4.1497 | 2.5703 | 16.0428 | 1.0584 | -2.0438 | 0 | 10.8333 | 10.8333 | 17.199 | 0
2 | 17 | 0 | 0 |  | -0.39969 | -1.3599 | -4.1497 | 2.5703 | 17.0428 | 1.3202 | -9.8446 | 0 | 0 | 0 | 0 | 0
2 | 18 | 0 | 0 |  | -0.39969 | -1.3599 | -4.1497 | 2.5703 | 18.0428 | 1.582 | -18.4047 | 0 | 0 | 0 | 0 | 0
2 | 19 | 0 | 0 |  | -0.39969 | -1.3599 | -4.1497 | 2.5703 | 19.0428 | 1.8438 | -27.3903 | 0 | 0 | 0 | 0 | 0
2 | 20 | 0 | 0 |  | -0.39969 | -1.3599 | -4.1497 | 2.5703 | 20.0428 | 2.1056 | -36.4492 | 0 | 0 | 0 | 0 | 0
2 | 21 | 0 | 0 |  | -0.39969 | -1.3599 | -4.1497 | 2.5703 | 21.0428 | 2.3674 | -45.1351 | 0 | 0 | 0 | 0 | 0
2 | 22 | 0 | 0 |  | -0.39969 | -1.3599 | -4.1497 | 2.5703 | 22.0428 | 2.6292 | -52.7709 | 0 | 0 | 0 | 0 | 0
2 | 23 | 0 | 0 |  | -0.39969 | -1.3599 | -4.1497 | 2.5703 | 23.0428 | 2.891 | -58.2662 | 0 | 0 | 0 | 0 | 0
2 | 24 | 0 | 0 |  | -0.39969 | -1.3599 | -4.1497 | 2.5703 | 24.0428 | 3.1528 | -60.2165 | 0 | 0 | 0 | 0 | 0
3 | 1 | 0 | 0 |  | -0.39807 | -1.3427 | -4.5894 | 2.1306 | 1.0355 | -2.8705 | -57.8576 | 0 | 0 | 0 | 0 | 0
3 | 2 | 0 | 0 |  | -0.39807 | -1.3427 | -4.5894 | 2.1306 | 2.0355 | -2.6087 | -52.1525 | 0 | 0 | 0 | 0 | 0
3 | 3 | 0 | 0 |  | -0.39807 | -1.3427 | -4.5894 | 2.1306 | 3.0355 | -2.3469 | -44.4079 | 0 | 0 | 0 | 0 | 0
3 | 4 | 0 | 0 |  | -0.39807 | -1.3427 | -4.5894 | 2.1306 | 4.0355 | -2.0851 | -35.6757 | 0 | 0 | 0 | 0 | 0
3 | 5 | 0 | 0 |  | -0.39807 | -1.3427 | -4.5894 | 2.1306 | 5.0355 | -1.8233 | -26.6088 | 0 | 0 | 0 | 0 | 0
3 | 6 | 0 | 0 |  | -0.39807 | -1.3427 | -4.5894 | 2.1306 | 6.0355 | -1.5615 | -17.6428 | 0 | 0 | 0 | 0 | 0
3 | 7 | 0 | 0 |  | -0.39807 | -1.3427 | -4.5894 | 2.1306 | 7.0355 | -1.2997 | -9.1268 | 0 | 0 | 0 | 0 | 0
3 | 8 | 0 | 0 |  | -0.39807 | -1.3427 | -4.5894 | 2.1306 | 8.0355 | -1.0379 | -1.3958 | 0 | 0 | 0 | 0 | 0
3 | 9 | 0 | 18 |  | -0.39807 | -1.3427 | -4.5894 | 2.1306 | 9.0355 | -0.7761 | 5.1955 | 0 | 15 | 15 | 23.814 | 0
3 | 10 | 291 | 30 |  | -0.39807 | -1.3427 | -4.5894 | 2.1306 | 10.0355 | -0.5143 | 10.2701 | 171.9905 | 25 | 196.9905 | 312.7422 | 0
3 | 11 | 313 | 88 |  | -0.39807 | -1.3427 | -4.5894 | 2.1306 | 11.0355 | -0.2525 | 13.4657 | 210.9903 | 73.3333 | 284.3236 | 451.3921 | 1
3 | 12 | 498 | 70 |  | -0.39807 | -1.3427 | -4.5894 | 2.1306 | 12.0355 | 0.0092964 | 14.5107 | 349.1098 | 58.3333 | 407.4431 | 646.8567 | 1
3 | 13 | 493 | 70 |  | -0.39807 | -1.3427 | -4.5894 | 2.1306 | 13.0355 | 0.2711 | 13.3073 | 330.3088 | 58.3333 | 388.6421 | 617.0082 | 1
3 | 14 | 395 | 62 |  | -0.39807 | -1.3427 | -4.5894 | 2.1306 | 14.0355 | 0.5329 | 9.9677 | 230.3348 | 51.6667 | 282.0014 | 447.7055 | 0
3 | 15 | 214 | 46 |  | -0.39807 | -1.3427 | -4.5894 | 2.1306 | 15.0355 | 0.79469 | 4.773 | 95.5145 | 38.3333 | 133.8478 | 212.4968 | 0
3 | 16 | 0 | 10 |  | -0.39807 | -1.3427 | -4.5894 | 2.1306 | 16.0355 | 1.0565 | -1.9116 | 0 | 8.3333 | 8.3333 | 13.23 | 0
3 | 17 | 0 | 0 |  | -0.39807 | -1.3427 | -4.5894 | 2.1306 | 17.0355 | 1.3183 | -9.7098 | 0 | 0 | 0 | 0 | 0
3 | 18 | 0 | 0 |  | -0.39807 | -1.3427 | -4.5894 | 2.1306 | 18.0355 | 1.5801 | -18.2686 | 0 | 0 | 0 | 0 | 0
3 | 19 | 0 | 0 |  | -0.39807 | -1.3427 | -4.5894 | 2.1306 | 19.0355 | 1.8419 | -27.2538 | 0 | 0 | 0 | 0 | 0
3 | 20 | 0 | 0 |  | -0.39807 | -1.3427 | -4.5894 | 2.1306 | 20.0355 | 2.1037 | -36.3129 | 0 | 0 | 0 | 0 | 0
3 | 21 | 0 | 0 |  | -0.39807 | -1.3427 | -4.5894 | 2.1306 | 21.0355 | 2.3655 | -45.0002 | 0 | 0 | 0 | 0 | 0
3 | 22 | 0 | 0 |  | -0.39807 | -1.3427 | -4.5894 | 2.1306 | 22.0355 | 2.6273 | -52.6404 | 0 | 0 | 0 | 0 | 0
3 | 23 | 0 | 0 |  | -0.39807 | -1.3427 | -4.5894 | 2.1306 | 23.0355 | 2.8891 | -58.1484 | 0 | 0 | 0 | 0 | 0
3 | 24 | 0 | 0 |  | -0.39807 | -1.3427 | -4.5894 | 2.1306 | 24.0355 | 3.1509 | -60.1251 | 0 | 0 | 0 | 0 | 0
4 | 1 | 0 | 0 |  | -0.39633 | -1.3255 | -5.0239 | 1.6961 | 1.0283 | -2.8724 | -57.7929 | 0 | 0 | 0 | 0 | 0
4 | 2 | 0 | 0 |  | -0.39633 | -1.3255 | -5.0239 | 1.6961 | 2.0283 | -2.6106 | -52.1163 | 0 | 0 | 0 | 0 | 0
4 | 3 | 0 | 0 |  | -0.39633 | -1.3255 | -5.0239 | 1.6961 | 3.0283 | -2.3488 | -44.389 | 0 | 0 | 0 | 0 | 0
4 | 4 | 0 | 0 |  | -0.39633 | -1.3255 | -5.0239 | 1.6961 | 4.0283 | -2.087 | -35.6648 | 0 | 0 | 0 | 0 | 0
4 | 5 | 0 | 0 |  | -0.39633 | -1.3255 | -5.0239 | 1.6961 | 5.0283 | -1.8252 | -26.5993 | 0 | 0 | 0 | 0 | 0
4 | 6 | 0 | 0 |  | -0.39633 | -1.3255 | -5.0239 | 1.6961 | 6.0283 | -1.5634 | -17.6295 | 0 | 0 | 0 | 0 | 0
4 | 7 | 0 | 0 |  | -0.39633 | -1.3255 | -5.0239 | 1.6961 | 7.0283 | -1.3016 | -9.1057 | 0 | 0 | 0 | 0 | 0
4 | 8 | 0 | 0 |  | -0.39633 | -1.3255 | -5.0239 | 1.6961 | 8.0283 | -1.0398 | -1.363 | 0 | 0 | 0 | 0 | 0
4 | 9 | 0 | 18 |  | -0.39633 | -1.3255 | -5.0239 | 1.6961 | 9.0283 | -0.778 | 5.243 | 0 | 15 | 15 | 23.814 | 0
4 | 10 | 46 | 72 |  | -0.39633 | -1.3255 | -5.0239 | 1.6961 | 10.0283 | -0.5162 | 10.3348 | 27.2043 | 60 | 87.2043 | 138.4456 | 0
4 | 11 | 96 | 92 |  | -0.39633 | -1.3255 | -5.0239 | 1.6961 | 11.0283 | -0.2544 | 13.5487 | 64.7911 | 76.6667 | 141.4577 | 224.5783 | 1
4 | 12 | 427 | 82 |  | -0.39633 | -1.3255 | -5.0239 | 1.6961 | 12.0283 | 0.0074006 | 14.611 | 299.8728 | 68.3333 | 368.2062 | 584.5641 | 1
4 | 13 | 361 | 97 |  | -0.39633 | -1.3255 | -5.0239 | 1.6961 | 13.0283 | 0.2692 | 13.4224 | 242.4644 | 80.8333 | 323.2977 | 513.2675 | 1
4 | 14 | 208 | 83 |  | -0.39633 | -1.3255 | -5.0239 | 1.6961 | 14.0283 | 0.531 | 10.0938 | 121.7007 | 69.1667 | 190.8673 | 303.021 | 0
4 | 15 | 0 | 44 |  | -0.39633 | -1.3255 | -5.0239 | 1.6961 | 15.0283 | 0.7928 | 4.9063 | 0 | 36.6667 | 36.6667 | 58.212 | 0
4 | 16 | 0 | 8 |  | -0.39633 | -1.3255 | -5.0239 | 1.6961 | 16.0283 | 1.0546 | -1.7739 | 0 | 6.6667 | 6.6667 | 10.584 | 0
4 | 17 | 0 | 0 |  | -0.39633 | -1.3255 | -5.0239 | 1.6961 | 17.0283 | 1.3164 | -9.5699 | 0 | 0 | 0 | 0 | 0
4 | 18 | 0 | 0 |  | -0.39633 | -1.3255 | -5.0239 | 1.6961 | 18.0283 | 1.5782 | -18.1278 | 0 | 0 | 0 | 0 | 0
4 | 19 | 0 | 0 |  | -0.39633 | -1.3255 | -5.0239 | 1.6961 | 19.0283 | 1.84 | -27.1128 | 0 | 0 | 0 | 0 | 0
4 | 20 | 0 | 0 |  | -0.39633 | -1.3255 | -5.0239 | 1.6961 | 20.0283 | 2.1018 | -36.172 | 0 | 0 | 0 | 0 | 0
4 | 21 | 0 | 0 |  | -0.39633 | -1.3255 | -5.0239 | 1.6961 | 21.0283 | 2.3636 | -44.8602 | 0 | 0 | 0 | 0 | 0
4 | 22 | 0 | 0 |  | -0.39633 | -1.3255 | -5.0239 | 1.6961 | 22.0283 | 2.6254 | -52.5042 | 0 | 0 | 0 | 0 | 0
4 | 23 | 0 | 0 |  | -0.39633 | -1.3255 | -5.0239 | 1.6961 | 23.0283 | 2.8872 | -58.024 | 0 | 0 | 0 | 0 | 0
4 | 24 | 0 | 0 |  | -0.39633 | -1.3255 | -5.0239 | 1.6961 | 24.0283 | 3.149 | -60.0263 | 0 | 0 | 0 | 0 | 0
5 | 1 | 0 | 0 |  | -0.39447 | -1.3083 | -5.4528 | 1.2672 | 1.0211 | -2.8743 | -57.7209 | 0 | 0 | 0 | 0 | 0
5 | 2 | 0 | 0 |  | -0.39447 | -1.3083 | -5.4528 | 1.2672 | 2.0211 | -2.6125 | -52.0731 | 0 | 0 | 0 | 0 | 0
5 | 3 | 0 | 0 |  | -0.39447 | -1.3083 | -5.4528 | 1.2672 | 3.0211 | -2.3507 | -44.3635 | 0 | 0 | 0 | 0 | 0
5 | 4 | 0 | 0 |  | -0.39447 | -1.3083 | -5.4528 | 1.2672 | 4.0211 | -2.0889 | -35.6477 | 0 | 0 | 0 | 0 | 0
5 | 5 | 0 | 0 |  | -0.39447 | -1.3083 | -5.4528 | 1.2672 | 5.0211 | -1.8271 | -26.5835 | 0 | 0 | 0 | 0 | 0
5 | 6 | 0 | 0 |  | -0.39447 | -1.3083 | -5.4528 | 1.2672 | 6.0211 | -1.5653 | -17.61 | 0 | 0 | 0 | 0 | 0
5 | 7 | 0 | 0 |  | -0.39447 | -1.3083 | -5.4528 | 1.2672 | 7.0211 | -1.3035 | -9.0781 | 0 | 0 | 0 | 0 | 0
5 | 8 | 0 | 0 |  | -0.39447 | -1.3083 | -5.4528 | 1.2672 | 8.0211 | -1.0417 | -1.3238 | 0 | 0 | 0 | 0 | 0
5 | 9 | 0 | 11 |  | -0.39447 | -1.3083 | -5.4528 | 1.2672 | 9.0211 | -0.77987 | 5.2973 | 0 | 9.1667 | 9.1667 | 14.553 | 0
5 | 10 | 7 | 47 |  | -0.39447 | -1.3083 | -5.4528 | 1.2672 | 10.0211 | -0.51807 | 10.4064 | 4.143 | 39.1667 | 43.3096 | 68.7583 | 0
5 | 11 | 13 | 85 |  | -0.39447 | -1.3083 | -5.4528 | 1.2672 | 11.0211 | -0.25627 | 13.6386 | 8.7855 | 70.8333 | 79.6189 | 126.4029 | 1
5 | 12 | 0 | 69 |  | -0.39447 | -1.3083 | -5.4528 | 1.2672 | 12.0211 | 0.0055293 | 14.7183 | 0 | 57.5 | 57.5 | 91.287 | 1
5 | 13 | 0 | 68 |  | -0.39447 | -1.3083 | -5.4528 | 1.2672 | 13.0211 | 0.26733 | 13.5441 | 0 | 56.6667 | 56.6667 | 89.964 | 1
5 | 14 | 0 | 54 |  | -0.39447 | -1.3083 | -5.4528 | 1.2672 | 14.0211 | 0.52913 | 10.2261 | 0 | 45 | 45 | 71.442 | 0
5 | 15 | 0 | 28 |  | -0.39447 | -1.3083 | -5.4528 | 1.2672 | 15.0211 | 0.79093 | 5.0455 | 0 | 23.3333 | 23.3333 | 37.044 | 0
5 | 16 | 0 | 6 |  | -0.39447 | -1.3083 | -5.4528 | 1.2672 | 16.0211 | 1.0527 | -1.631 | 0 | 5 | 5 | 7.938 | 0
5 | 17 | 0 | 0 |  | -0.39447 | -1.3083 | -5.4528 | 1.2672 | 17.0211 | 1.3145 | -9.4252 | 0 | 0 | 0 | 0 | 0
5 | 18 | 0 | 0 |  | -0.39447 | -1.3083 | -5.4528 | 1.2672 | 18.0211 | 1.5763 | -17.9825 | 0 | 0 | 0 | 0 | 0
5 | 19 | 0 | 0 |  | -0.39447 | -1.3083 | -5.4528 | 1.2672 | 19.0211 | 1.8381 | -26.9672 | 0 | 0 | 0 | 0 | 0
5 | 20 | 0 | 0 |  | -0.39447 | -1.3083 | -5.4528 | 1.2672 | 20.0211 | 2.0999 | -36.0265 | 0 | 0 | 0 | 0 | 0
5 | 21 | 0 | 0 |  | -0.39447 | -1.3083 | -5.4528 | 1.2672 | 21.0211 | 2.3617 | -44.7154 | 0 | 0 | 0 | 0 | 0
5 | 22 | 0 | 0 |  | -0.39447 | -1.3083 | -5.4528 | 1.2672 | 22.0211 | 2.6235 | -52.3625 | 0 | 0 | 0 | 0 | 0
5 | 23 | 0 | 0 |  | -0.39447 | -1.3083 | -5.4528 | 1.2672 | 23.0211 | 2.8853 | -57.8931 | 0 | 0 | 0 | 0 | 0
5 | 24 | 0 | 0 |  | -0.39447 | -1.3083 | -5.4528 | 1.2672 | 24.0211 | 3.1471 | -59.9202 | 0 | 0 | 0 | 0 | 0
6 | 1 | 0 | 0 |  | -0.39248 | -1.2911 | -5.8756 | 0.84438 | 1.0141 | -2.8761 | -57.6414 | 0 | 0 | 0 | 0 | 0
6 | 2 | 0 | 0 |  | -0.39248 | -1.2911 | -5.8756 | 0.84438 | 2.0141 | -2.6143 | -52.0229 | 0 | 0 | 0 | 0 | 0
6 | 3 | 0 | 0 |  | -0.39248 | -1.2911 | -5.8756 | 0.84438 | 3.0141 | -2.3525 | -44.3315 | 0 | 0 | 0 | 0 | 0
6 | 4 | 0 | 0 |  | -0.39248 | -1.2911 | -5.8756 | 0.84438 | 4.0141 | -2.0907 | -35.6242 | 0 | 0 | 0 | 0 | 0
6 | 5 | 0 | 0 |  | -0.39248 | -1.2911 | -5.8756 | 0.84438 | 5.0141 | -1.8289 | -26.5616 | 0 | 0 | 0 | 0 | 0
6 | 6 | 0 | 0 |  | -0.39248 | -1.2911 | -5.8756 | 0.84438 | 6.0141 | -1.5671 | -17.5843 | 0 | 0 | 0 | 0 | 0
6 | 7 | 0 | 0 |  | -0.39248 | -1.2911 | -5.8756 | 0.84438 | 7.0141 | -1.3053 | -9.0443 | 0 | 0 | 0 | 0 | 0
6 | 8 | 0 | 0 |  | -0.39248 | -1.2911 | -5.8756 | 0.84438 | 8.0141 | -1.0435 | -1.278 | 0 | 0 | 0 | 0 | 0
6 | 9 | 0 | 11 |  | -0.39248 | -1.2911 | -5.8756 | 0.84438 | 9.0141 | -0.78171 | 5.3583 | 0 | 9.1667 | 9.1667 | 14.553 | 0
6 | 10 | 124 | 45 |  | -0.39248 | -1.2911 | -5.8756 | 0.84438 | 10.0141 | -0.51991 | 10.4849 | 73.4561 | 37.5 | 110.9561 | 176.1539 | 0
6 | 11 | 144 | 83 |  | -0.39248 | -1.2911 | -5.8756 | 0.84438 | 11.0141 | -0.25812 | 13.7354 | 97.4587 | 69.1667 | 166.6253 | 264.5344 | 1
6 | 12 | 363 | 106 |  | -0.39248 | -1.2911 | -5.8756 | 0.84438 | 12.0141 | 0.0036843 | 14.8324 | 255.9266 | 88.3333 | 344.26 | 546.5471 | 1
6 | 13 | 501 | 71 |  | -0.39248 | -1.2911 | -5.8756 | 0.84438 | 13.0141 | 0.26548 | 13.6724 | 338.2604 | 59.1667 | 397.4271 | 630.9552 | 1
6 | 14 | 139 | 82 |  | -0.39248 | -1.2911 | -5.8756 | 0.84438 | 14.0141 | 0.52728 | 10.3647 | 81.9053 | 68.3333 | 150.2386 | 238.5189 | 0
6 | 15 | 36 | 54 |  | -0.39248 | -1.2911 | -5.8756 | 0.84438 | 15.0141 | 0.78908 | 5.1903 | 16.3122 | 45 | 61.3122 | 97.3392 | 0
6 | 16 | 0 | 14 |  | -0.39248 | -1.2911 | -5.8756 | 0.84438 | 16.0141 | 1.0509 | -1.4828 | 0 | 11.6667 | 11.6667 | 18.522 | 0
6 | 17 | 0 | 0 |  | -0.39248 | -1.2911 | -5.8756 | 0.84438 | 17.0141 | 1.3127 | -9.2756 | 0 | 0 | 0 | 0 | 0
6 | 18 | 0 | 0 |  | -0.39248 | -1.2911 | -5.8756 | 0.84438 | 18.0141 | 1.5745 | -17.8325 | 0 | 0 | 0 | 0 | 0
6 | 19 | 0 | 0 |  | -0.39248 | -1.2911 | -5.8756 | 0.84438 | 19.0141 | 1.8363 | -26.8173 | 0 | 0 | 0 | 0 | 0
6 | 20 | 0 | 0 |  | -0.39248 | -1.2911 | -5.8756 | 0.84438 | 20.0141 | 2.0981 | -35.8766 | 0 | 0 | 0 | 0 | 0
6 | 21 | 0 | 0 |  | -0.39248 | -1.2911 | -5.8756 | 0.84438 | 21.0141 | 2.3599 | -44.5657 | 0 | 0 | 0 | 0 | 0
6 | 22 | 0 | 0 |  | -0.39248 | -1.2911 | -5.8756 | 0.84438 | 22.0141 | 2.6217 | -52.2154 | 0 | 0 | 0 | 0 | 0
6 | 23 | 0 | 0 |  | -0.39248 | -1.2911 | -5.8756 | 0.84438 | 23.0141 | 2.8835 | -57.7559 | 0 | 0 | 0 | 0 | 0
6 | 24 | 0 | 0 |  | -0.39248 | -1.2911 | -5.8756 | 0.84438 | 24.0141 | 3.1453 | -59.807 | 0 | 0 | 0 | 0 | 0
7 | 1 | 0 | 0 |  | -0.39037 | -1.2739 | -6.2921 | 0.42793 | 1.0071 | -2.8779 | -57.5545 | 0 | 0 | 0 | 0 | 0
7 | 2 | 0 | 0 |  | -0.39037 | -1.2739 | -6.2921 | 0.42793 | 2.0071 | -2.6161 | -51.9655 | 0 | 0 | 0 | 0 | 0
7 | 3 | 0 | 0 |  | -0.39037 | -1.2739 | -6.2921 | 0.42793 | 3.0071 | -2.3543 | -44.2928 | 0 | 0 | 0 | 0 | 0
7 | 4 | 0 | 0 |  | -0.39037 | -1.2739 | -6.2921 | 0.42793 | 4.0071 | -2.0925 | -35.5944 | 0 | 0 | 0 | 0 | 0
7 | 5 | 0 | 0 |  | -0.39037 | -1.2739 | -6.2921 | 0.42793 | 5.0071 | -1.8307 | -26.5334 | 0 | 0 | 0 | 0 | 0
7 | 6 | 0 | 0 |  | -0.39037 | -1.2739 | -6.2921 | 0.42793 | 6.0071 | -1.5689 | -17.5523 | 0 | 0 | 0 | 0 | 0
7 | 7 | 0 | 0 |  | -0.39037 | -1.2739 | -6.2921 | 0.42793 | 7.0071 | -1.3071 | -9.004 | 0 | 0 | 0 | 0 | 0
7 | 8 | 0 | 0 |  | -0.39037 | -1.2739 | -6.2921 | 0.42793 | 8.0071 | -1.0453 | -1.2256 | 0 | 0 | 0 | 0 | 0
7 | 9 | 0 | 14 |  | -0.39037 | -1.2739 | -6.2921 | 0.42793 | 9.0071 | -0.78353 | 5.426 | 0 | 11.6667 | 11.6667 | 18.522 | 0
7 | 10 | 156 | 41 |  | -0.39037 | -1.2739 | -6.2921 | 0.42793 | 10.0071 | -0.52173 | 10.5703 | 92.5097 | 34.1667 | 126.6764 | 201.1115 | 0
7 | 11 | 16 | 86 |  | -0.39037 | -1.2739 | -6.2921 | 0.42793 | 11.0071 | -0.25993 | 13.8392 | 10.8459 | 71.6667 | 82.5125 | 130.9969 | 1
7 | 12 | 36 | 103 |  | -0.39037 | -1.2739 | -6.2921 | 0.42793 | 12.0071 | 0.0018672 | 14.9533 | 25.4351 | 85.8333 | 111.2684 | 176.6497 | 1
7 | 13 | 36 | 102 |  | -0.39037 | -1.2739 | -6.2921 | 0.42793 | 13.0071 | 0.26367 | 13.8073 | 24.3735 | 85 | 109.3735 | 173.6414 | 1
7 | 14 | 19 | 84 |  | -0.39037 | -1.2739 | -6.2921 | 0.42793 | 14.0071 | 0.52547 | 10.5093 | 11.2369 | 70 | 81.2369 | 128.9718 | 0
7 | 15 | 0 | 48 |  | -0.39037 | -1.2739 | -6.2921 | 0.42793 | 15.0071 | 0.78727 | 5.3408 | 0 | 40 | 40 | 63.504 | 0
7 | 16 | 0 | 10 |  | -0.39037 | -1.2739 | -6.2921 | 0.42793 | 16.0071 | 1.0491 | -1.3295 | 0 | 8.3333 | 8.3333 | 13.23 | 0
7 | 17 | 0 | 0 |  | -0.39037 | -1.2739 | -6.2921 | 0.42793 | 17.0071 | 1.3109 | -9.1214 | 0 | 0 | 0 | 0 | 0
7 | 18 | 0 | 0 |  | -0.39037 | -1.2739 | -6.2921 | 0.42793 | 18.0071 | 1.5727 | -17.6781 | 0 | 0 | 0 | 0 | 0
7 | 19 | 0 | 0 |  | -0.39037 | -1.2739 | -6.2921 | 0.42793 | 19.0071 | 1.8345 | -26.663 | 0 | 0 | 0 | 0 | 0
7 | 20 | 0 | 0 |  | -0.39037 | -1.2739 | -6.2921 | 0.42793 | 20.0071 | 2.0963 | -35.7223 | 0 | 0 | 0 | 0 | 0
7 | 21 | 0 | 0 |  | -0.39037 | -1.2739 | -6.2921 | 0.42793 | 21.0071 | 2.3581 | -44.4114 | 0 | 0 | 0 | 0 | 0
7 | 22 | 0 | 0 |  | -0.39037 | -1.2739 | -6.2921 | 0.42793 | 22.0071 | 2.6199 | -52.063 | 0 | 0 | 0 | 0 | 0
7 | 23 | 0 | 0 |  | -0.39037 | -1.2739 | -6.2921 | 0.42793 | 23.0071 | 2.8817 | -57.6124 | 0 | 0 | 0 | 0 | 0
7 | 24 | 0 | 0 |  | -0.39037 | -1.2739 | -6.2921 | 0.42793 | 24.0071 | 3.1435 | -59.6866 | 0 | 0 | 0 | 0 | 0
8 | 1 | 0 | 0 |  | -0.38814 | -1.2566 | -6.7018 | 0.018246 | 1.0003 | -2.8797 | -57.4603 | 0 | 0 | 0 | 0 | 0
8 | 2 | 0 | 0 |  | -0.38814 | -1.2566 | -6.7018 | 0.018246 | 2.0003 | -2.6179 | -51.9011 | 0 | 0 | 0 | 0 | 0
8 | 3 | 0 | 0 |  | -0.38814 | -1.2566 | -6.7018 | 0.018246 | 3.0003 | -2.3561 | -44.2474 | 0 | 0 | 0 | 0 | 0
8 | 4 | 0 | 0 |  | -0.38814 | -1.2566 | -6.7018 | 0.018246 | 4.0003 | -2.0943 | -35.5582 | 0 | 0 | 0 | 0 | 0
8 | 5 | 0 | 0 |  | -0.38814 | -1.2566 | -6.7018 | 0.018246 | 5.0003 | -1.8325 | -26.499 | 0 | 0 | 0 | 0 | 0
8 | 6 | 0 | 0 |  | -0.38814 | -1.2566 | -6.7018 | 0.018246 | 6.0003 | -1.5707 | -17.514 | 0 | 0 | 0 | 0 | 0
8 | 7 | 0 | 0 |  | -0.38814 | -1.2566 | -6.7018 | 0.018246 | 7.0003 | -1.3089 | -8.9574 | 0 | 0 | 0 | 0 | 0
8 | 8 | 0 | 0 |  | -0.38814 | -1.2566 | -6.7018 | 0.018246 | 8.0003 | -1.0471 | -1.1667 | 0 | 0 | 0 | 0 | 0
8 | 9 | 0 | 7 |  | -0.38814 | -1.2566 | -6.7018 | 0.018246 | 9.0003 | -0.78532 | 5.5004 | 0 | 5.8333 | 5.8333 | 9.261 | 0
8 | 10 | 0 | 31 |  | -0.38814 | -1.2566 | -6.7018 | 0.018246 | 10.0003 | -0.52352 | 10.6625 | 0 | 25.8333 | 25.8333 | 41.013 | 0
8 | 11 | 0 | 56 |  | -0.38814 | -1.2566 | -6.7018 | 0.018246 | 11.0003 | -0.26172 | 13.9499 | 0 | 46.6667 | 46.6667 | 74.088 | 1
8 | 12 | 0 | 70 |  | -0.38814 | -1.2566 | -6.7018 | 0.018246 | 12.0003 | 7.9615e-05 | 15.081 | 0 | 58.3333 | 58.3333 | 92.61 | 1
8 | 13 | 0 | 70 |  | -0.38814 | -1.2566 | -6.7018 | 0.018246 | 13.0003 | 0.26188 | 13.9486 | 0 | 58.3333 | 58.3333 | 92.61 | 1
8 | 14 | 21 | 84 |  | -0.38814 | -1.2566 | -6.7018 | 0.018246 | 14.0003 | 0.52368 | 10.6599 | 12.4667 | 70 | 82.4667 | 130.9241 | 0
8 | 15 | 0 | 49 |  | -0.38814 | -1.2566 | -6.7018 | 0.018246 | 15.0003 | 0.78548 | 5.4968 | 0 | 40.8333 | 40.8333 | 64.827 | 0
8 | 16 | 0 | 16 |  | -0.38814 | -1.2566 | -6.7018 | 0.018246 | 16.0003 | 1.0473 | -1.1711 | 0 | 13.3333 | 13.3333 | 21.168 | 0
8 | 17 | 0 | 0 |  | -0.38814 | -1.2566 | -6.7018 | 0.018246 | 17.0003 | 1.3091 | -8.9624 | 0 | 0 | 0 | 0 | 0
8 | 18 | 0 | 0 |  | -0.38814 | -1.2566 | -6.7018 | 0.018246 | 18.0003 | 1.5709 | -17.5194 | 0 | 0 | 0 | 0 | 0
8 | 19 | 0 | 0 |  | -0.38814 | -1.2566 | -6.7018 | 0.018246 | 19.0003 | 1.8327 | -26.5045 | 0 | 0 | 0 | 0 | 0
8 | 20 | 0 | 0 |  | -0.38814 | -1.2566 | -6.7018 | 0.018246 | 20.0003 | 2.0945 | -35.5636 | 0 | 0 | 0 | 0 | 0
8 | 21 | 0 | 0 |  | -0.38814 | -1.2566 | -6.7018 | 0.018246 | 21.0003 | 2.3563 | -44.2525 | 0 | 0 | 0 | 0 | 0
8 | 22 | 0 | 0 |  | -0.38814 | -1.2566 | -6.7018 | 0.018246 | 22.0003 | 2.6181 | -51.9053 | 0 | 0 | 0 | 0 | 0
8 | 23 | 0 | 0 |  | -0.38814 | -1.2566 | -6.7018 | 0.018246 | 23.0003 | 2.8799 | -57.4628 | 0 | 0 | 0 | 0 | 0
8 | 24 | 0 | 0 |  | -0.38814 | -1.2566 | -6.7018 | 0.018246 | 24.0003 | 3.1417 | -59.559 | 0 | 0 | 0 | 0 | 0
9 | 1 | 0 | 0 |  | -0.3858 | -1.2394 | -7.1043 | -0.38429 | 0.9936 | -2.8815 | -57.3587 | 0 | 0 | 0 | 0 | 0
9 | 2 | 0 | 0 |  | -0.3858 | -1.2394 | -7.1043 | -0.38429 | 1.9936 | -2.6197 | -51.8296 | 0 | 0 | 0 | 0 | 0
9 | 3 | 0 | 0 |  | -0.3858 | -1.2394 | -7.1043 | -0.38429 | 2.9936 | -2.3579 | -44.1953 | 0 | 0 | 0 | 0 | 0
9 | 4 | 0 | 0 |  | -0.3858 | -1.2394 | -7.1043 | -0.38429 | 3.9936 | -2.0961 | -35.5155 | 0 | 0 | 0 | 0 | 0
9 | 5 | 0 | 0 |  | -0.3858 | -1.2394 | -7.1043 | -0.38429 | 4.9936 | -1.8343 | -26.4582 | 0 | 0 | 0 | 0 | 0
9 | 6 | 0 | 0 |  | -0.3858 | -1.2394 | -7.1043 | -0.38429 | 5.9936 | -1.5725 | -17.4695 | 0 | 0 | 0 | 0 | 0
9 | 7 | 0 | 0 |  | -0.3858 | -1.2394 | -7.1043 | -0.38429 | 6.9936 | -1.3107 | -8.9044 | 0 | 0 | 0 | 0 | 0
9 | 8 | 0 | 0 |  | -0.3858 | -1.2394 | -7.1043 | -0.38429 | 7.9936 | -1.0489 | -1.1013 | 0 | 0 | 0 | 0 | 0
9 | 9 | 0 | 20 |  | -0.3858 | -1.2394 | -7.1043 | -0.38429 | 8.9936 | -0.78707 | 5.5815 | 0 | 16.6667 | 16.6667 | 26.46 | 0
9 | 10 | 7 | 50 |  | -0.3858 | -1.2394 | -7.1043 | -0.38429 | 9.9936 | -0.52528 | 10.7616 | 4.1616 | 41.6667 | 45.8283 | 72.7569 | 0
9 | 11 | 0 | 57 |  | -0.3858 | -1.2394 | -7.1043 | -0.38429 | 10.9936 | -0.26348 | 14.0675 | 0 | 47.5 | 47.5 | 75.411 | 1
9 | 12 | 0 | 71 |  | -0.3858 | -1.2394 | -7.1043 | -0.38429 | 11.9936 | -0.0016768 | 15.2153 | 0 | 59.1667 | 59.1667 | 93.933 | 1
9 | 13 | 0 | 71 |  | -0.3858 | -1.2394 | -7.1043 | -0.38429 | 12.9936 | 0.26012 | 14.0963 | 0 | 59.1667 | 59.1667 | 93.933 | 1
9 | 14 | 0 | 57 |  | -0.3858 | -1.2394 | -7.1043 | -0.38429 | 13.9936 | 0.52192 | 10.8165 | 0 | 47.5 | 47.5 | 75.411 | 0
9 | 15 | 0 | 31 |  | -0.3858 | -1.2394 | -7.1043 | -0.38429 | 14.9936 | 0.78372 | 5.6582 | 0 | 25.8333 | 25.8333 | 41.013 | 0
9 | 16 | 0 | 11 |  | -0.3858 | -1.2394 | -7.1043 | -0.38429 | 15.9936 | 1.0455 | -1.0078 | 0 | 9.1667 | 9.1667 | 14.553 | 0
9 | 17 | 0 | 0 |  | -0.3858 | -1.2394 | -7.1043 | -0.38429 | 16.9936 | 1.3073 | -8.7989 | 0 | 0 | 0 | 0 | 0
9 | 18 | 0 | 0 |  | -0.3858 | -1.2394 | -7.1043 | -0.38429 | 17.9936 | 1.5691 | -17.3564 | 0 | 0 | 0 | 0 | 0
9 | 19 | 0 | 0 |  | -0.3858 | -1.2394 | -7.1043 | -0.38429 | 18.9936 | 1.8309 | -26.3419 | 0 | 0 | 0 | 0 | 0
9 | 20 | 0 | 0 |  | -0.3858 | -1.2394 | -7.1043 | -0.38429 | 19.9936 | 2.0927 | -35.4008 | 0 | 0 | 0 | 0 | 0
9 | 21 | 0 | 0 |  | -0.3858 | -1.2394 | -7.1043 | -0.38429 | 20.9936 | 2.3545 | -44.089 | 0 | 0 | 0 | 0 | 0
9 | 22 | 0 | 0 |  | -0.3858 | -1.2394 | -7.1043 | -0.38429 | 21.9936 | 2.6163 | -51.7424 | 0 | 0 | 0 | 0 | 0
9 | 23 | 0 | 0 |  | -0.3858 | -1.2394 | -7.1043 | -0.38429 | 22.9936 | 2.8781 | -57.307 | 0 | 0 | 0 | 0 | 0
9 | 24 | 0 | 0 |  | -0.3858 | -1.2394 | -7.1043 | -0.38429 | 23.9936 | 3.1399 | -59.4245 | 0 | 0 | 0 | 0 | 0
10 | 1 | 0 | 0 |  | -0.38333 | -1.2222 | -7.4993 | -0.77932 | 0.98701 | -2.8832 | -57.2498 | 0 | 0 | 0 | 0 | 0
10 | 2 | 0 | 0 |  | -0.38333 | -1.2222 | -7.4993 | -0.77932 | 1.987 | -2.6214 | -51.7511 | 0 | 0 | 0 | 0 | 0
10 | 3 | 0 | 0 |  | -0.38333 | -1.2222 | -7.4993 | -0.77932 | 2.987 | -2.3596 | -44.1365 | 0 | 0 | 0 | 0 | 0
10 | 4 | 0 | 0 |  | -0.38333 | -1.2222 | -7.4993 | -0.77932 | 3.987 | -2.0978 | -35.4664 | 0 | 0 | 0 | 0 | 0
10 | 5 | 0 | 0 |  | -0.38333 | -1.2222 | -7.4993 | -0.77932 | 4.987 | -1.836 | -26.4112 | 0 | 0 | 0 | 0 | 0
10 | 6 | 0 | 0 |  | -0.38333 | -1.2222 | -7.4993 | -0.77932 | 5.987 | -1.5742 | -17.4186 | 0 | 0 | 0 | 0 | 0
10 | 7 | 0 | 0 |  | -0.38333 | -1.2222 | -7.4993 | -0.77932 | 6.987 | -1.3124 | -8.845 | 0 | 0 | 0 | 0 | 0
10 | 8 | 0 | 0 |  | -0.38333 | -1.2222 | -7.4993 | -0.77932 | 7.987 | -1.0506 | -1.0293 | 0 | 0 | 0 | 0 | 0
10 | 9 | 0 | 20 |  | -0.38333 | -1.2222 | -7.4993 | -0.77932 | 8.987 | -0.7888 | 5.6694 | 0 | 16.6667 | 16.6667 | 26.46 | 0
10 | 10 | 138 | 46 |  | -0.38333 | -1.2222 | -7.4993 | -0.77932 | 9.987 | -0.527 | 10.8674 | 82.164 | 38.3333 | 120.4974 | 191.3016 | 0
10 | 11 | 151 | 86 |  | -0.38333 | -1.2222 | -7.4993 | -0.77932 | 10.987 | -0.2652 | 14.1918 | 102.9183 | 71.6667 | 174.585 | 277.1712 | 1
10 | 12 | 0 | 72 |  | -0.38333 | -1.2222 | -7.4993 | -0.77932 | 11.987 | -0.0034004 | 15.3564 | 0 | 60 | 60 | 95.256 | 1
10 | 13 | 0 | 72 |  | -0.38333 | -1.2222 | -7.4993 | -0.77932 | 12.987 | 0.2584 | 14.2503 | 0 | 60 | 60 | 95.256 | 1
10 | 14 | 0 | 58 |  | -0.38333 | -1.2222 | -7.4993 | -0.77932 | 13.987 | 0.5202 | 10.979 | 0 | 48.3333 | 48.3333 | 76.734 | 0
10 | 15 | 0 | 32 |  | -0.38333 | -1.2222 | -7.4993 | -0.77932 | 14.987 | 0.782 | 5.8251 | 0 | 26.6667 | 26.6667 | 42.336 | 0
10 | 16 | 0 | 7 |  | -0.38333 | -1.2222 | -7.4993 | -0.77932 | 15.987 | 1.0438 | -0.83957 | 0 | 5.8333 | 5.8333 | 9.261 | 0
10 | 17 | 0 | 0 |  | -0.38333 | -1.2222 | -7.4993 | -0.77932 | 16.987 | 1.3056 | -8.6309 | 0 | 0 | 0 | 0 | 0
10 | 18 | 0 | 0 |  | -0.38333 | -1.2222 | -7.4993 | -0.77932 | 17.987 | 1.5674 | -17.1892 | 0 | 0 | 0 | 0 | 0
10 | 19 | 0 | 0 |  | -0.38333 | -1.2222 | -7.4993 | -0.77932 | 18.987 | 1.8292 | -26.1752 | 0 | 0 | 0 | 0 | 0
10 | 20 | 0 | 0 |  | -0.38333 | -1.2222 | -7.4993 | -0.77932 | 19.987 | 2.091 | -35.2338 | 0 | 0 | 0 | 0 | 0
10 | 21 | 0 | 0 |  | -0.38333 | -1.2222 | -7.4993 | -0.77932 | 20.987 | 2.3528 | -43.9211 | 0 | 0 | 0 | 0 | 0
10 | 22 | 0 | 0 |  | -0.38333 | -1.2222 | -7.4993 | -0.77932 | 21.987 | 2.6146 | -51.5745 | 0 | 0 | 0 | 0 | 0
10 | 23 | 0 | 0 |  | -0.38333 | -1.2222 | -7.4993 | -0.77932 | 22.987 | 2.8764 | -57.1452 | 0 | 0 | 0 | 0 | 0
10 | 24 | 0 | 0 |  | -0.38333 | -1.2222 | -7.4993 | -0.77932 | 23.987 | 3.1382 | -59.283 | 0 | 0 | 0 | 0 | 0
11 | 1 | 0 | 0 |  | -0.38075 | -1.205 | -7.8865 | -1.1665 | 0.98056 | -2.8849 | -57.1337 | 0 | 0 | 0 | 0 | 0
11 | 2 | 0 | 0 |  | -0.38075 | -1.205 | -7.8865 | -1.1665 | 1.9806 | -2.6231 | -51.6654 | 0 | 0 | 0 | 0 | 0
11 | 3 | 0 | 0 |  | -0.38075 | -1.205 | -7.8865 | -1.1665 | 2.9806 | -2.3613 | -44.071 | 0 | 0 | 0 | 0 | 0
11 | 4 | 0 | 0 |  | -0.38075 | -1.205 | -7.8865 | -1.1665 | 3.9806 | -2.0995 | -35.4109 | 0 | 0 | 0 | 0 | 0
11 | 5 | 0 | 0 |  | -0.38075 | -1.205 | -7.8865 | -1.1665 | 4.9806 | -1.8377 | -26.3578 | 0 | 0 | 0 | 0 | 0
11 | 6 | 0 | 0 |  | -0.38075 | -1.205 | -7.8865 | -1.1665 | 5.9806 | -1.5759 | -17.3615 | 0 | 0 | 0 | 0 | 0
11 | 7 | 0 | 0 |  | -0.38075 | -1.205 | -7.8865 | -1.1665 | 6.9806 | -1.3141 | -8.7792 | 0 | 0 | 0 | 0 | 0
11 | 8 | 0 | 0 |  | -0.38075 | -1.205 | -7.8865 | -1.1665 | 7.9806 | -1.0523 | -0.95087 | 0 | 0 | 0 | 0 | 0
11 | 9 | 0 | 21 |  | -0.38075 | -1.205 | -7.8865 | -1.1665 | 8.9806 | -0.79049 | 5.7638 | 0 | 17.5 | 17.5 | 27.783 | 0
11 | 10 | 141 | 47 |  | -0.38075 | -1.205 | -7.8865 | -1.1665 | 9.9806 | -0.52869 | 10.9801 | 84.0859 | 39.1667 | 123.2525 | 195.6757 | 0
11 | 11 | 335 | 79 |  | -0.38075 | -1.205 | -7.8865 | -1.1665 | 10.9806 | -0.26689 | 14.3229 | 228.7978 | 65.8333 | 294.6311 | 467.7563 | 1
11 | 12 | 147 | 112 |  | -0.38075 | -1.205 | -7.8865 | -1.1665 | 11.9806 | -0.0050898 | 15.5041 | 104.8542 | 93.3333 | 198.1876 | 314.6426 | 1
11 | 13 | 125 | 118 |  | -0.38075 | -1.205 | -7.8865 | -1.1665 | 12.9806 | 0.25671 | 14.4106 | 85.6544 | 98.3333 | 183.9877 | 292.0989 | 1
11 | 14 | 393 | 75 |  | -0.38075 | -1.205 | -7.8865 | -1.1665 | 13.9806 | 0.51851 | 11.1473 | 236.0804 | 62.5 | 298.5804 | 474.0263 | 0
11 | 15 | 179 | 57 |  | -0.38075 | -1.205 | -7.8865 | -1.1665 | 14.9806 | 0.78031 | 5.9972 | 83.3226 | 47.5 | 130.8226 | 207.6939 | 0
11 | 16 | 0 | 16 |  | -0.38075 | -1.205 | -7.8865 | -1.1665 | 15.9806 | 1.0421 | -0.66654 | 0 | 13.3333 | 13.3333 | 21.168 | 0
11 | 17 | 0 | 0 |  | -0.38075 | -1.205 | -7.8865 | -1.1665 | 16.9806 | 1.3039 | -8.4585 | 0 | 0 | 0 | 0 | 0
11 | 18 | 0 | 0 |  | -0.38075 | -1.205 | -7.8865 | -1.1665 | 17.9806 | 1.5657 | -17.0179 | 0 | 0 | 0 | 0 | 0
11 | 19 | 0 | 0 |  | -0.38075 | -1.205 | -7.8865 | -1.1665 | 18.9806 | 1.8275 | -26.0045 | 0 | 0 | 0 | 0 | 0
11 | 20 | 0 | 0 |  | -0.38075 | -1.205 | -7.8865 | -1.1665 | 19.9806 | 2.0893 | -35.0628 | 0 | 0 | 0 | 0 | 0
11 | 21 | 0 | 0 |  | -0.38075 | -1.205 | -7.8865 | -1.1665 | 20.9806 | 2.3511 | -43.7488 | 0 | 0 | 0 | 0 | 0
11 | 22 | 0 | 0 |  | -0.38075 | -1.205 | -7.8865 | -1.1665 | 21.9806 | 2.6129 | -51.4015 | 0 | 0 | 0 | 0 | 0
11 | 23 | 0 | 0 |  | -0.38075 | -1.205 | -7.8865 | -1.1665 | 22.9806 | 2.8747 | -56.9774 | 0 | 0 | 0 | 0 | 0
11 | 24 | 0 | 0 |  | -0.38075 | -1.205 | -7.8865 | -1.1665 | 23.9806 | 3.1365 | -59.1347 | 0 | 0 | 0 | 0 | 0
12 | 1 | 0 | 0 |  | -0.37806 | -1.1878 | -8.2655 | -1.5455 | 0.97424 | -2.8865 | -57.0103 | 0 | 0 | 0 | 0 | 0
12 | 2 | 0 | 0 |  | -0.37806 | -1.1878 | -8.2655 | -1.5455 | 1.9742 | -2.6247 | -51.5726 | 0 | 0 | 0 | 0 | 0
12 | 3 | 0 | 0 |  | -0.37806 | -1.1878 | -8.2655 | -1.5455 | 2.9742 | -2.3629 | -43.9987 | 0 | 0 | 0 | 0 | 0
12 | 4 | 0 | 0 |  | -0.37806 | -1.1878 | -8.2655 | -1.5455 | 3.9742 | -2.1011 | -35.3489 | 0 | 0 | 0 | 0 | 0
12 | 5 | 0 | 0 |  | -0.37806 | -1.1878 | -8.2655 | -1.5455 | 4.9742 | -1.8393 | -26.2981 | 0 | 0 | 0 | 0 | 0
12 | 6 | 0 | 0 |  | -0.37806 | -1.1878 | -8.2655 | -1.5455 | 5.9742 | -1.5775 | -17.298 | 0 | 0 | 0 | 0 | 0
12 | 7 | 0 | 0 |  | -0.37806 | -1.1878 | -8.2655 | -1.5455 | 6.9742 | -1.3157 | -8.7071 | 0 | 0 | 0 | 0 | 0
12 | 8 | 0 | 0 |  | -0.37806 | -1.1878 | -8.2655 | -1.5455 | 7.9742 | -1.0539 | -0.8659 | 0 | 0 | 0 | 0 | 0
12 | 9 | 0 | 22 |  | -0.37806 | -1.1878 | -8.2655 | -1.5455 | 8.9742 | -0.79214 | 5.865 | 0 | 18.3333 | 18.3333 | 29.106 | 0
12 | 10 | 194 | 63 |  | -0.37806 | -1.1878 | -8.2655 | -1.5455 | 9.9742 | -0.53034 | 11.0994 | 115.8955 | 52.5 | 168.3955 | 267.3446 | 0
12 | 11 | 125 | 94 |  | -0.37806 | -1.1878 | -8.2655 | -1.5455 | 10.9742 | -0.26854 | 14.4608 | 85.5573 | 78.3333 | 163.8906 | 260.1928 | 1
12 | 12 | 313 | 95 |  | -0.37806 | -1.1878 | -8.2655 | -1.5455 | 11.9742 | -0.0067434 | 15.6583 | 223.8493 | 79.1667 | 303.016 | 481.0682 | 1
12 | 13 | 432 | 80 |  | -0.37806 | -1.1878 | -8.2655 | -1.5455 | 12.9742 | 0.25506 | 14.5772 | 296.9791 | 66.6667 | 363.6458 | 577.324 | 1
12 | 14 | 156 | 88 |  | -0.37806 | -1.1878 | -8.2655 | -1.5455 | 13.9742 | 0.51686 | 11.3214 | 94.0964 | 73.3333 | 167.4297 | 265.8114 | 0
12 | 15 | 261 | 58 |  | -0.37806 | -1.1878 | -8.2655 | -1.5455 | 14.9742 | 0.77865 | 6.1745 | 122.1759 | 48.3333 | 170.5093 | 270.7005 | 0
12 | 16 | 0 | 23 |  | -0.37806 | -1.1878 | -8.2655 | -1.5455 | 15.9742 | 1.0405 | -0.4888 | 0 | 19.1667 | 19.1667 | 30.429 | 0
12 | 17 | 0 | 0 |  | -0.37806 | -1.1878 | -8.2655 | -1.5455 | 16.9742 | 1.3023 | -8.2819 | 0 | 0 | 0 | 0 | 0
12 | 18 | 0 | 0 |  | -0.37806 | -1.1878 | -8.2655 | -1.5455 | 17.9742 | 1.5641 | -16.8426 | 0 | 0 | 0 | 0 | 0
12 | 19 | 0 | 0 |  | -0.37806 | -1.1878 | -8.2655 | -1.5455 | 18.9742 | 1.8259 | -25.8299 | 0 | 0 | 0 | 0 | 0
12 | 20 | 0 | 0 |  | -0.37806 | -1.1878 | -8.2655 | -1.5455 | 19.9742 | 2.0877 | -34.8879 | 0 | 0 | 0 | 0 | 0
12 | 21 | 0 | 0 |  | -0.37806 | -1.1878 | -8.2655 | -1.5455 | 20.9742 | 2.3495 | -43.5722 | 0 | 0 | 0 | 0 | 0
12 | 22 | 0 | 0 |  | -0.37806 | -1.1878 | -8.2655 | -1.5455 | 21.9742 | 2.6113 | -51.2237 | 0 | 0 | 0 | 0 | 0
12 | 23 | 0 | 0 |  | -0.37806 | -1.1878 | -8.2655 | -1.5455 | 22.9742 | 2.873 | -56.8039 | 0 | 0 | 0 | 0 | 0
12 | 24 | 0 | 0 |  | -0.37806 | -1.1878 | -8.2655 | -1.5455 | 23.9742 | 3.1348 | -58.9796 | 0 | 0 | 0 | 0 | 0
13 | 1 | 0 | 0 |  | -0.37524 | -1.1706 | -8.6359 | -1.9159 | 0.96807 | -2.8882 | -56.8797 | 0 | 0 | 0 | 0 | 0
13 | 2 | 0 | 0 |  | -0.37524 | -1.1706 | -8.6359 | -1.9159 | 1.9681 | -2.6264 | -51.4728 | 0 | 0 | 0 | 0 | 0
13 | 3 | 0 | 0 |  | -0.37524 | -1.1706 | -8.6359 | -1.9159 | 2.9681 | -2.3646 | -43.9196 | 0 | 0 | 0 | 0 | 0
13 | 4 | 0 | 0 |  | -0.37524 | -1.1706 | -8.6359 | -1.9159 | 3.9681 | -2.1028 | -35.2803 | 0 | 0 | 0 | 0 | 0
13 | 5 | 0 | 0 |  | -0.37524 | -1.1706 | -8.6359 | -1.9159 | 4.9681 | -1.841 | -26.232 | 0 | 0 | 0 | 0 | 0
13 | 6 | 0 | 0 |  | -0.37524 | -1.1706 | -8.6359 | -1.9159 | 5.9681 | -1.5792 | -17.2282 | 0 | 0 | 0 | 0 | 0
13 | 7 | 0 | 0 |  | -0.37524 | -1.1706 | -8.6359 | -1.9159 | 6.9681 | -1.3174 | -8.6285 | 0 | 0 | 0 | 0 | 0
13 | 8 | 0 | 0 |  | -0.37524 | -1.1706 | -8.6359 | -1.9159 | 7.9681 | -1.0556 | -0.77444 | 0 | 0 | 0 | 0 | 0
13 | 9 | 0 | 8 |  | -0.37524 | -1.1706 | -8.6359 | -1.9159 | 8.9681 | -0.79376 | 5.9727 | 0 | 6.6667 | 6.6667 | 10.584 | 0
13 | 10 | 0 | 35 |  | -0.37524 | -1.1706 | -8.6359 | -1.9159 | 9.9681 | -0.53196 | 11.2255 | 0 | 29.1667 | 29.1667 | 46.305 | 0
13 | 11 | 0 | 61 |  | -0.37524 | -1.1706 | -8.6359 | -1.9159 | 10.9681 | -0.27016 | 14.6052 | 0 | 50.8333 | 50.8333 | 80.703 | 1
13 | 12 | 0 | 76 |  | -0.37524 | -1.1706 | -8.6359 | -1.9159 | 11.9681 | -0.0083598 | 15.8189 | 0 | 63.3333 | 63.3333 | 100.548 | 1
13 | 13 | 0 | 76 |  | -0.37524 | -1.1706 | -8.6359 | -1.9159 | 12.9681 | 0.25344 | 14.7498 | 0 | 63.3333 | 63.3333 | 100.548 | 1
13 | 14 | 0 | 61 |  | -0.37524 | -1.1706 | -8.6359 | -1.9159 | 13.9681 | 0.51524 | 11.5011 | 0 | 50.8333 | 50.8333 | 80.703 | 0
13 | 15 | 6 | 56 |  | -0.37524 | -1.1706 | -8.6359 | -1.9159 | 14.9681 | 0.77704 | 6.357 | 2.8246 | 46.6667 | 49.4913 | 78.5724 | 0
13 | 16 | 0 | 14 |  | -0.37524 | -1.1706 | -8.6359 | -1.9159 | 15.9681 | 1.0388 | -0.30644 | 0 | 11.6667 | 11.6667 | 18.522 | 0
13 | 17 | 0 | 0 |  | -0.37524 | -1.1706 | -8.6359 | -1.9159 | 16.9681 | 1.3006 | -8.101 | 0 | 0 | 0 | 0 | 0
13 | 18 | 0 | 0 |  | -0.37524 | -1.1706 | -8.6359 | -1.9159 | 17.9681 | 1.5624 | -16.6633 | 0 | 0 | 0 | 0 | 0
13 | 19 | 0 | 0 |  | -0.37524 | -1.1706 | -8.6359 | -1.9159 | 18.9681 | 1.8242 | -25.6516 | 0 | 0 | 0 | 0 | 0
13 | 20 | 0 | 0 |  | -0.37524 | -1.1706 | -8.6359 | -1.9159 | 19.9681 | 2.086 | -34.7091 | 0 | 0 | 0 | 0 | 0
13 | 21 | 0 | 0 |  | -0.37524 | -1.1706 | -8.6359 | -1.9159 | 20.9681 | 2.3478 | -43.3915 | 0 | 0 | 0 | 0 | 0
13 | 22 | 0 | 0 |  | -0.37524 | -1.1706 | -8.6359 | -1.9159 | 21.9681 | 2.6096 | -51.041 | 0 | 0 | 0 | 0 | 0
13 | 23 | 0 | 0 |  | -0.37524 | -1.1706 | -8.6359 | -1.9159 | 22.9681 | 2.8714 | -56.6246 | 0 | 0 | 0 | 0 | 0
13 | 24 | 0 | 0 |  | -0.37524 | -1.1706 | -8.6359 | -1.9159 | 23.9681 | 3.1332 | -58.8177 | 0 | 0 | 0 | 0 | 0
14 | 1 | 0 | 0 |  | -0.37232 | -1.1534 | -8.9975 | -2.2775 | 0.96204 | -2.8897 | -56.7419 | 0 | 0 | 0 | 0 | 0
14 | 2 | 0 | 0 |  | -0.37232 | -1.1534 | -8.9975 | -2.2775 | 1.962 | -2.6279 | -51.3658 | 0 | 0 | 0 | 0 | 0
14 | 3 | 0 | 0 |  | -0.37232 | -1.1534 | -8.9975 | -2.2775 | 2.962 | -2.3661 | -43.8338 | 0 | 0 | 0 | 0 | 0
14 | 4 | 0 | 0 |  | -0.37232 | -1.1534 | -8.9975 | -2.2775 | 3.962 | -2.1043 | -35.2053 | 0 | 0 | 0 | 0 | 0
14 | 5 | 0 | 0 |  | -0.37232 | -1.1534 | -8.9975 | -2.2775 | 4.962 | -1.8425 | -26.1596 | 0 | 0 | 0 | 0 | 0
14 | 6 | 0 | 0 |  | -0.37232 | -1.1534 | -8.9975 | -2.2775 | 5.962 | -1.5807 | -17.1521 | 0 | 0 | 0 | 0 | 0
14 | 7 | 0 | 0 |  | -0.37232 | -1.1534 | -8.9975 | -2.2775 | 6.962 | -1.3189 | -8.5436 | 0 | 0 | 0 | 0 | 0
14 | 8 | 0 | 0 |  | -0.37232 | -1.1534 | -8.9975 | -2.2775 | 7.962 | -1.0571 | -0.6765 | 0 | 0 | 0 | 0 | 0
14 | 9 | 0 | 17 |  | -0.37232 | -1.1534 | -8.9975 | -2.2775 | 8.962 | -0.79534 | 6.087 | 0 | 14.1667 | 14.1667 | 22.491 | 0
14 | 10 | 15 | 53 |  | -0.37232 | -1.1534 | -8.9975 | -2.2775 | 9.962 | -0.53354 | 11.3582 | 8.9961 | 44.1667 | 53.1627 | 84.4012 | 0
14 | 11 | 15 | 94 |  | -0.37232 | -1.1534 | -8.9975 | -2.2775 | 10.962 | -0.27174 | 14.7564 | 10.3148 | 78.3333 | 88.6481 | 140.7378 | 1
14 | 12 | 39 | 111 |  | -0.37232 | -1.1534 | -8.9975 | -2.2775 | 11.962 | -0.0099376 | 15.9861 | 28.0468 | 92.5 | 120.5468 | 191.3801 | 1
14 | 13 | 39 | 111 |  | -0.37232 | -1.1534 | -8.9975 | -2.2775 | 12.962 | 0.25186 | 14.9286 | 26.9909 | 92.5 | 119.4909 | 189.7038 | 1
14 | 14 | 23 | 94 |  | -0.37232 | -1.1534 | -8.9975 | -2.2775 | 13.962 | 0.51366 | 11.6863 | 13.9904 | 78.3333 | 92.3238 | 146.5732 | 0
14 | 15 | 4 | 57 |  | -0.37232 | -1.1534 | -8.9975 | -2.2775 | 14.962 | 0.77546 | 6.5445 | 1.8939 | 47.5 | 49.3939 | 78.4177 | 0
14 | 16 | 0 | 15 |  | -0.37232 | -1.1534 | -8.9975 | -2.2775 | 15.962 | 1.0373 | -0.11956 | 0 | 12.5 | 12.5 | 19.845 | 0
14 | 17 | 0 | 0 |  | -0.37232 | -1.1534 | -8.9975 | -2.2775 | 16.962 | 1.2991 | -7.916 | 0 | 0 | 0 | 0 | 0
14 | 18 | 0 | 0 |  | -0.37232 | -1.1534 | -8.9975 | -2.2775 | 17.962 | 1.5609 | -16.4803 | 0 | 0 | 0 | 0 | 0
14 | 19 | 0 | 0 |  | -0.37232 | -1.1534 | -8.9975 | -2.2775 | 18.962 | 1.8227 | -25.4696 | 0 | 0 | 0 | 0 | 0
14 | 20 | 0 | 0 |  | -0.37232 | -1.1534 | -8.9975 | -2.2775 | 19.962 | 2.0845 | -34.5265 | 0 | 0 | 0 | 0 | 0
14 | 21 | 0 | 0 |  | -0.37232 | -1.1534 | -8.9975 | -2.2775 | 20.962 | 2.3463 | -43.2067 | 0 | 0 | 0 | 0 | 0
14 | 22 | 0 | 0 |  | -0.37232 | -1.1534 | -8.9975 | -2.2775 | 21.962 | 2.6081 | -50.8537 | 0 | 0 | 0 | 0 | 0
14 | 23 | 0 | 0 |  | -0.37232 | -1.1534 | -8.9975 | -2.2775 | 22.962 | 2.8699 | -56.4396 | 0 | 0 | 0 | 0 | 0
14 | 24 | 0 | 0 |  | -0.37232 | -1.1534 | -8.9975 | -2.2775 | 23.962 | 3.1317 | -58.6492 | 0 | 0 | 0 | 0 | 0
15 | 1 | 0 | 0 |  | -0.36928 | -1.1361 | -9.3499 | -2.6299 | 0.95617 | -2.8913 | -56.597 | 0 | 0 | 0 | 0 | 0
15 | 2 | 0 | 0 |  | -0.36928 | -1.1361 | -9.3499 | -2.6299 | 1.9562 | -2.6295 | -51.2518 | 0 | 0 | 0 | 0 | 0
15 | 3 | 0 | 0 |  | -0.36928 | -1.1361 | -9.3499 | -2.6299 | 2.9562 | -2.3677 | -43.7412 | 0 | 0 | 0 | 0 | 0
15 | 4 | 0 | 0 |  | -0.36928 | -1.1361 | -9.3499 | -2.6299 | 3.9562 | -2.1059 | -35.1237 | 0 | 0 | 0 | 0 | 0
15 | 5 | 0 | 0 |  | -0.36928 | -1.1361 | -9.3499 | -2.6299 | 4.9562 | -1.8441 | -26.0808 | 0 | 0 | 0 | 0 | 0
15 | 6 | 0 | 0 |  | -0.36928 | -1.1361 | -9.3499 | -2.6299 | 5.9562 | -1.5823 | -17.0696 | 0 | 0 | 0 | 0 | 0
15 | 7 | 0 | 0 |  | -0.36928 | -1.1361 | -9.3499 | -2.6299 | 6.9562 | -1.3205 | -8.4524 | 0 | 0 | 0 | 0 | 0
15 | 8 | 0 | 0 |  | -0.36928 | -1.1361 | -9.3499 | -2.6299 | 7.9562 | -1.0587 | -0.57212 | 0 | 0 | 0 | 0 | 0
15 | 9 | 0 | 9 |  | -0.36928 | -1.1361 | -9.3499 | -2.6299 | 8.9562 | -0.79687 | 6.2078 | 0 | 7.5 | 7.5 | 11.907 | 0
15 | 10 | 0 | 35 |  | -0.36928 | -1.1361 | -9.3499 | -2.6299 | 9.9562 | -0.53507 | 11.4975 | 0 | 29.1667 | 29.1667 | 46.305 | 0
15 | 11 | 0 | 62 |  | -0.36928 | -1.1361 | -9.3499 | -2.6299 | 10.9562 | -0.27327 | 14.914 | 0 | 51.6667 | 51.6667 | 82.026 | 1
15 | 12 | 0 | 77 |  | -0.36928 | -1.1361 | -9.3499 | -2.6299 | 11.9562 | -0.011475 | 16.1595 | 0 | 64.1667 | 64.1667 | 101.871 | 1
15 | 13 | 229 | 121 |  | -0.36928 | -1.1361 | -9.3499 | -2.6299 | 12.9562 | 0.25032 | 15.1133 | 159.0357 | 100.8333 | 259.869 | 412.5681 | 1
15 | 14 | 35 | 93 |  | -0.36928 | -1.1361 | -9.3499 | -2.6299 | 13.9562 | 0.51212 | 11.8771 | 21.3817 | 77.5 | 98.8817 | 156.9845 | 0
15 | 15 | 252 | 62 |  | -0.36928 | -1.1361 | -9.3499 | -2.6299 | 14.9562 | 0.77392 | 6.7369 | 120.0058 | 51.6667 | 171.6725 | 272.5472 | 0
15 | 16 | 0 | 16 |  | -0.36928 | -1.1361 | -9.3499 | -2.6299 | 15.9562 | 1.0357 | 0.071754 | 0 | 13.3333 | 13.3333 | 21.168 | 0
15 | 17 | 0 | 0 |  | -0.36928 | -1.1361 | -9.3499 | -2.6299 | 16.9562 | 1.2975 | -7.727 | 0 | 0 | 0 | 0 | 0
15 | 18 | 0 | 0 |  | -0.36928 | -1.1361 | -9.3499 | -2.6299 | 17.9562 | 1.5593 | -16.2935 | 0 | 0 | 0 | 0 | 0
15 | 19 | 0 | 0 |  | -0.36928 | -1.1361 | -9.3499 | -2.6299 | 18.9562 | 1.8211 | -25.2839 | 0 | 0 | 0 | 0 | 0
15 | 20 | 0 | 0 |  | -0.36928 | -1.1361 | -9.3499 | -2.6299 | 19.9562 | 2.0829 | -34.3403 | 0 | 0 | 0 | 0 | 0
15 | 21 | 0 | 0 |  | -0.36928 | -1.1361 | -9.3499 | -2.6299 | 20.9562 | 2.3447 | -43.0179 | 0 | 0 | 0 | 0 | 0
15 | 22 | 0 | 0 |  | -0.36928 | -1.1361 | -9.3499 | -2.6299 | 21.9562 | 2.6065 | -50.6617 | 0 | 0 | 0 | 0 | 0
15 | 23 | 0 | 0 |  | -0.36928 | -1.1361 | -9.3499 | -2.6299 | 22.9562 | 2.8683 | -56.2491 | 0 | 0 | 0 | 0 | 0
15 | 24 | 0 | 0 |  | -0.36928 | -1.1361 | -9.3499 | -2.6299 | 23.9562 | 3.1301 | -58.4742 | 0 | 0 | 0 | 0 | 0
16 | 1 | 0 | 0 |  | -0.36613 | -1.1189 | -9.6929 | -2.9729 | 0.95045 | -2.8928 | -56.4451 | 0 | 0 | 0 | 0 | 0
16 | 2 | 0 | 0 |  | -0.36613 | -1.1189 | -9.6929 | -2.9729 | 1.9505 | -2.631 | -51.1308 | 0 | 0 | 0 | 0 | 0
16 | 3 | 0 | 0 |  | -0.36613 | -1.1189 | -9.6929 | -2.9729 | 2.9505 | -2.3692 | -43.6418 | 0 | 0 | 0 | 0 | 0
16 | 4 | 0 | 0 |  | -0.36613 | -1.1189 | -9.6929 | -2.9729 | 3.9505 | -2.1074 | -35.0356 | 0 | 0 | 0 | 0 | 0
16 | 5 | 0 | 0 |  | -0.36613 | -1.1189 | -9.6929 | -2.9729 | 4.9505 | -1.8456 | -25.9956 | 0 | 0 | 0 | 0 | 0
16 | 6 | 0 | 0 |  | -0.36613 | -1.1189 | -9.6929 | -2.9729 | 5.9505 | -1.5838 | -16.9809 | 0 | 0 | 0 | 0 | 0
16 | 7 | 0 | 0 |  | -0.36613 | -1.1189 | -9.6929 | -2.9729 | 6.9505 | -1.322 | -8.3547 | 0 | 0 | 0 | 0 | 0
16 | 8 | 0 | 0 |  | -0.36613 | -1.1189 | -9.6929 | -2.9729 | 7.9505 | -1.0602 | -0.4613 | 0 | 0 | 0 | 0 | 0
16 | 9 | 0 | 15 |  | -0.36613 | -1.1189 | -9.6929 | -2.9729 | 8.9505 | -0.79837 | 6.3352 | 0 | 12.5 | 12.5 | 19.845 | 0
16 | 10 | 161 | 50 |  | -0.36613 | -1.1189 | -9.6929 | -2.9729 | 9.9505 | -0.53657 | 11.6434 | 96.987 | 41.6667 | 138.6536 | 220.1265 | 0
16 | 11 | 285 | 84 |  | -0.36613 | -1.1189 | -9.6929 | -2.9729 | 10.9505 | -0.27477 | 15.0782 | 196.9799 | 70 | 266.9799 | 423.8573 | 1
16 | 12 | 61 | 109 |  | -0.36613 | -1.1189 | -9.6929 | -2.9729 | 11.9505 | -0.012972 | 16.3393 | 44.1276 | 90.8333 | 134.9609 | 214.2639 | 1
16 | 13 | 42 | 115 |  | -0.36613 | -1.1189 | -9.6929 | -2.9729 | 12.9505 | 0.24883 | 15.3039 | 29.2716 | 95.8333 | 125.1049 | 198.6165 | 1
16 | 14 | 33 | 96 |  | -0.36613 | -1.1189 | -9.6929 | -2.9729 | 13.9505 | 0.51063 | 12.0733 | 20.2481 | 80 | 100.2481 | 159.1539 | 0
16 | 15 | 6 | 61 |  | -0.36613 | -1.1189 | -9.6929 | -2.9729 | 14.9505 | 0.77243 | 6.9342 | 2.874 | 50.8333 | 53.7073 | 85.2657 | 0
16 | 16 | 0 | 11 |  | -0.36613 | -1.1189 | -9.6929 | -2.9729 | 15.9505 | 1.0342 | 0.26741 | 0 | 9.1667 | 9.1667 | 14.553 | 0
16 | 17 | 0 | 0 |  | -0.36613 | -1.1189 | -9.6929 | -2.9729 | 16.9505 | 1.296 | -7.5341 | 0 | 0 | 0 | 0 | 0
16 | 18 | 0 | 0 |  | -0.36613 | -1.1189 | -9.6929 | -2.9729 | 17.9505 | 1.5578 | -16.1031 | 0 | 0 | 0 | 0 | 0
16 | 19 | 0 | 0 |  | -0.36613 | -1.1189 | -9.6929 | -2.9729 | 18.9505 | 1.8196 | -25.0948 | 0 | 0 | 0 | 0 | 0
16 | 20 | 0 | 0 |  | -0.36613 | -1.1189 | -9.6929 | -2.9729 | 19.9505 | 2.0814 | -34.1504 | 0 | 0 | 0 | 0 | 0
16 | 21 | 0 | 0 |  | -0.36613 | -1.1189 | -9.6929 | -2.9729 | 20.9505 | 2.3432 | -42.8252 | 0 | 0 | 0 | 0 | 0
16 | 22 | 0 | 0 |  | -0.36613 | -1.1189 | -9.6929 | -2.9729 | 21.9505 | 2.605 | -50.4652 | 0 | 0 | 0 | 0 | 0
16 | 23 | 0 | 0 |  | -0.36613 | -1.1189 | -9.6929 | -2.9729 | 22.9505 | 2.8668 | -56.0532 | 0 | 0 | 0 | 0 | 0
16 | 24 | 0 | 0 |  | -0.36613 | -1.1189 | -9.6929 | -2.9729 | 23.9505 | 3.1286 | -58.2926 | 0 | 0 | 0 | 0 | 0
17 | 1 | 0 | 0 |  | -0.36287 | -1.1017 | -10.0261 | -3.3061 | 0.9449 | -2.8942 | -56.2863 | 0 | 0 | 0 | 0 | 0
17 | 2 | 0 | 0 |  | -0.36287 | -1.1017 | -10.0261 | -3.3061 | 1.9449 | -2.6324 | -51.0028 | 0 | 0 | 0 | 0 | 0
17 | 3 | 0 | 0 |  | -0.36287 | -1.1017 | -10.0261 | -3.3061 | 2.9449 | -2.3706 | -43.5357 | 0 | 0 | 0 | 0 | 0
17 | 4 | 0 | 0 |  | -0.36287 | -1.1017 | -10.0261 | -3.3061 | 3.9449 | -2.1088 | -34.941 | 0 | 0 | 0 | 0 | 0
17 | 5 | 0 | 0 |  | -0.36287 | -1.1017 | -10.0261 | -3.3061 | 4.9449 | -1.847 | -25.9041 | 0 | 0 | 0 | 0 | 0
17 | 6 | 0 | 0 |  | -0.36287 | -1.1017 | -10.0261 | -3.3061 | 5.9449 | -1.5852 | -16.8858 | 0 | 0 | 0 | 0 | 0
17 | 7 | 0 | 0 |  | -0.36287 | -1.1017 | -10.0261 | -3.3061 | 6.9449 | -1.3234 | -8.2508 | 0 | 0 | 0 | 0 | 0
17 | 8 | 0 | 0 |  | -0.36287 | -1.1017 | -10.0261 | -3.3061 | 7.9449 | -1.0616 | -0.34408 | 0 | 0 | 0 | 0 | 0
17 | 9 | 0 | 10 |  | -0.36287 | -1.1017 | -10.0261 | -3.3061 | 8.9449 | -0.79982 | 6.4691 | 0 | 8.3333 | 8.3333 | 13.23 | 0
17 | 10 | 0 | 37 |  | -0.36287 | -1.1017 | -10.0261 | -3.3061 | 9.9449 | -0.53802 | 11.7958 | 0 | 30.8333 | 30.8333 | 48.951 | 0
17 | 11 | 0 | 64 |  | -0.36287 | -1.1017 | -10.0261 | -3.3061 | 10.9449 | -0.27622 | 15.2489 | 0 | 53.3333 | 53.3333 | 84.672 | 1
17 | 12 | 0 | 80 |  | -0.36287 | -1.1017 | -10.0261 | -3.3061 | 11.9449 | -0.014426 | 16.5253 | 0 | 66.6667 | 66.6667 | 105.84 | 1
17 | 13 | 0 | 80 |  | -0.36287 | -1.1017 | -10.0261 | -3.3061 | 12.9449 | 0.24737 | 15.5003 | 0 | 66.6667 | 66.6667 | 105.84 | 1
17 | 14 | 0 | 66 |  | -0.36287 | -1.1017 | -10.0261 | -3.3061 | 13.9449 | 0.50917 | 12.2748 | 0 | 55 | 55 | 87.318 | 0
17 | 15 | 0 | 40 |  | -0.36287 | -1.1017 | -10.0261 | -3.3061 | 14.9449 | 0.77097 | 7.1363 | 0 | 33.3333 | 33.3333 | 52.92 | 0
17 | 16 | 0 | 11 |  | -0.36287 | -1.1017 | -10.0261 | -3.3061 | 15.9449 | 1.0328 | 0.4673 | 0 | 9.1667 | 9.1667 | 14.553 | 0
17 | 17 | 0 | 0 |  | -0.36287 | -1.1017 | -10.0261 | -3.3061 | 16.9449 | 1.2946 | -7.3374 | 0 | 0 | 0 | 0 | 0
17 | 18 | 0 | 0 |  | -0.36287 | -1.1017 | -10.0261 | -3.3061 | 17.9449 | 1.5564 | -15.9091 | 0 | 0 | 0 | 0 | 0
17 | 19 | 0 | 0 |  | -0.36287 | -1.1017 | -10.0261 | -3.3061 | 18.9449 | 1.8182 | -24.9022 | 0 | 0 | 0 | 0 | 0
17 | 20 | 0 | 0 |  | -0.36287 | -1.1017 | -10.0261 | -3.3061 | 19.9449 | 2.08 | -33.9571 | 0 | 0 | 0 | 0 | 0
17 | 21 | 0 | 0 |  | -0.36287 | -1.1017 | -10.0261 | -3.3061 | 20.9449 | 2.3418 | -42.6286 | 0 | 0 | 0 | 0 | 0
17 | 22 | 0 | 0 |  | -0.36287 | -1.1017 | -10.0261 | -3.3061 | 21.9449 | 2.6036 | -50.2642 | 0 | 0 | 0 | 0 | 0
17 | 23 | 0 | 0 |  | -0.36287 | -1.1017 | -10.0261 | -3.3061 | 22.9449 | 2.8654 | -55.8518 | 0 | 0 | 0 | 0 | 0
17 | 24 | 0 | 0 |  | -0.36287 | -1.1017 | -10.0261 | -3.3061 | 23.9449 | 3.1272 | -58.1048 | 0 | 0 | 0 | 0 | 0
18 | 1 | 0 | 0 |  | -0.35951 | -1.0845 | -10.3492 | -3.6292 | 0.93951 | -2.8956 | -56.1204 | 0 | 0 | 0 | 0 | 0
18 | 2 | 0 | 0 |  | -0.35951 | -1.0845 | -10.3492 | -3.6292 | 1.9395 | -2.6338 | -50.8678 | 0 | 0 | 0 | 0 | 0
18 | 3 | 0 | 0 |  | -0.35951 | -1.0845 | -10.3492 | -3.6292 | 2.9395 | -2.372 | -43.4228 | 0 | 0 | 0 | 0 | 0
18 | 4 | 0 | 0 |  | -0.35951 | -1.0845 | -10.3492 | -3.6292 | 3.9395 | -2.1102 | -34.8398 | 0 | 0 | 0 | 0 | 0
18 | 5 | 0 | 0 |  | -0.35951 | -1.0845 | -10.3492 | -3.6292 | 4.9395 | -1.8484 | -25.8061 | 0 | 0 | 0 | 0 | 0
18 | 6 | 0 | 0 |  | -0.35951 | -1.0845 | -10.3492 | -3.6292 | 5.9395 | -1.5866 | -16.7843 | 0 | 0 | 0 | 0 | 0
18 | 7 | 0 | 0 |  | -0.35951 | -1.0845 | -10.3492 | -3.6292 | 6.9395 | -1.3248 | -8.1405 | 0 | 0 | 0 | 0 | 0
18 | 8 | 0 | 0 |  | -0.35951 | -1.0845 | -10.3492 | -3.6292 | 7.9395 | -1.063 | -0.22048 | 0 | 0 | 0 | 0 | 0
18 | 9 | 0 | 16 |  | -0.35951 | -1.0845 | -10.3492 | -3.6292 | 8.9395 | -0.80123 | 6.6094 | 0 | 13.3333 | 13.3333 | 21.168 | 0
18 | 10 | 25 | 57 |  | -0.35951 | -1.0845 | -10.3492 | -3.6292 | 9.9395 | -0.53943 | 11.9546 | 15.1347 | 47.5 | 62.6347 | 99.4389 | 0
18 | 11 | 135 | 102 |  | -0.35951 | -1.0845 | -10.3492 | -3.6292 | 10.9395 | -0.27763 | 15.4259 | 93.8195 | 85 | 178.8195 | 283.8938 | 1
18 | 12 | 396 | 118 |  | -0.35951 | -1.0845 | -10.3492 | -3.6292 | 11.9395 | -0.015836 | 16.7175 | 288.2581 | 98.3333 | 386.5914 | 613.7525 | 1
18 | 13 | 553 | 76 |  | -0.35951 | -1.0845 | -10.3492 | -3.6292 | 12.9395 | 0.24596 | 15.7026 | 388.2273 | 63.3333 | 451.5606 | 716.8976 | 1
18 | 14 | 472 | 70 |  | -0.35951 | -1.0845 | -10.3492 | -3.6292 | 13.9395 | 0.50776 | 12.4815 | 292.1987 | 58.3333 | 350.5321 | 556.5047 | 0
18 | 15 | 303 | 65 |  | -0.35951 | -1.0845 | -10.3492 | -3.6292 | 14.9395 | 0.76956 | 7.343 | 146.8517 | 54.1667 | 201.0183 | 319.1367 | 0
18 | 16 | 113 | 26 |  | -0.35951 | -1.0845 | -10.3492 | -3.6292 | 15.9395 | 1.0314 | 0.67134 | 34.8017 | 21.6667 | 56.4683 | 89.6491 | 0
18 | 17 | 0 | 0 |  | -0.35951 | -1.0845 | -10.3492 | -3.6292 | 16.9395 | 1.2932 | -7.1369 | 0 | 0 | 0 | 0 | 0
18 | 18 | 0 | 0 |  | -0.35951 | -1.0845 | -10.3492 | -3.6292 | 17.9395 | 1.555 | -15.7117 | 0 | 0 | 0 | 0 | 0
18 | 19 | 0 | 0 |  | -0.35951 | -1.0845 | -10.3492 | -3.6292 | 18.9395 | 1.8168 | -24.7063 | 0 | 0 | 0 | 0 | 0
18 | 20 | 0 | 0 |  | -0.35951 | -1.0845 | -10.3492 | -3.6292 | 19.9395 | 2.0786 | -33.7603 | 0 | 0 | 0 | 0 | 0
18 | 21 | 0 | 0 |  | -0.35951 | -1.0845 | -10.3492 | -3.6292 | 20.9395 | 2.3404 | -42.4283 | 0 | 0 | 0 | 0 | 0
18 | 22 | 0 | 0 |  | -0.35951 | -1.0845 | -10.3492 | -3.6292 | 21.9395 | 2.6022 | -50.0589 | 0 | 0 | 0 | 0 | 0
18 | 23 | 0 | 0 |  | -0.35951 | -1.0845 | -10.3492 | -3.6292 | 22.9395 | 2.864 | -55.6453 | 0 | 0 | 0 | 0 | 0
18 | 24 | 0 | 0 |  | -0.35951 | -1.0845 | -10.3492 | -3.6292 | 23.9395 | 3.1258 | -57.9106 | 0 | 0 | 0 | 0 | 0
19 | 1 | 0 | 0 |  | -0.35603 | -1.0673 | -10.6621 | -3.9421 | 0.9343 | -2.897 | -55.9478 | 0 | 0 | 0 | 0 | 0
19 | 2 | 0 | 0 |  | -0.35603 | -1.0673 | -10.6621 | -3.9421 | 1.9343 | -2.6352 | -50.7258 | 0 | 0 | 0 | 0 | 0
19 | 3 | 0 | 0 |  | -0.35603 | -1.0673 | -10.6621 | -3.9421 | 2.9343 | -2.3734 | -43.3031 | 0 | 0 | 0 | 0 | 0
19 | 4 | 0 | 0 |  | -0.35603 | -1.0673 | -10.6621 | -3.9421 | 3.9343 | -2.1116 | -34.7322 | 0 | 0 | 0 | 0 | 0
19 | 5 | 0 | 0 |  | -0.35603 | -1.0673 | -10.6621 | -3.9421 | 4.9343 | -1.8498 | -25.7018 | 0 | 0 | 0 | 0 | 0
19 | 6 | 0 | 0 |  | -0.35603 | -1.0673 | -10.6621 | -3.9421 | 5.9343 | -1.588 | -16.6766 | 0 | 0 | 0 | 0 | 0
19 | 7 | 0 | 0 |  | -0.35603 | -1.0673 | -10.6621 | -3.9421 | 6.9343 | -1.3262 | -8.0239 | 0 | 0 | 0 | 0 | 0
19 | 8 | 0 | 0 |  | -0.35603 | -1.0673 | -10.6621 | -3.9421 | 7.9343 | -1.0644 | -0.090535 | 0 | 0 | 0 | 0 | 0
19 | 9 | 72 | 25 |  | -0.35603 | -1.0673 | -10.6621 | -3.9421 | 8.9343 | -0.8026 | 6.7561 | 33.5883 | 20.8333 | 54.4217 | 86.3999 | 0
19 | 10 | 138 | 71 |  | -0.35603 | -1.0673 | -10.6621 | -3.9421 | 9.9343 | -0.5408 | 12.1199 | 83.7659 | 59.1667 | 142.9326 | 226.9197 | 0
19 | 11 | 49 | 94 |  | -0.35603 | -1.0673 | -10.6621 | -3.9421 | 10.9343 | -0.279 | 15.6092 | 34.1515 | 78.3333 | 112.4848 | 178.5809 | 1
19 | 12 | 0 | 82 |  | -0.35603 | -1.0673 | -10.6621 | -3.9421 | 11.9343 | -0.0172 | 16.9157 | 0 | 68.3333 | 68.3333 | 108.486 | 1
19 | 13 | 0 | 83 |  | -0.35603 | -1.0673 | -10.6621 | -3.9421 | 12.9343 | 0.2446 | 15.9104 | 0 | 69.1667 | 69.1667 | 109.809 | 1
19 | 14 | 0 | 69 |  | -0.35603 | -1.0673 | -10.6621 | -3.9421 | 13.9343 | 0.5064 | 12.6933 | 0 | 57.5 | 57.5 | 91.287 | 1
19 | 15 | 0 | 42 |  | -0.35603 | -1.0673 | -10.6621 | -3.9421 | 14.9343 | 0.7682 | 7.5543 | 0 | 35 | 35 | 55.566 | 0
19 | 16 | 0 | 12 |  | -0.35603 | -1.0673 | -10.6621 | -3.9421 | 15.9343 | 1.03 | 0.87942 | 0 | 10 | 10 | 15.876 | 0
19 | 17 | 0 | 0 |  | -0.35603 | -1.0673 | -10.6621 | -3.9421 | 16.9343 | 1.2918 | -6.9328 | 0 | 0 | 0 | 0 | 0
19 | 18 | 0 | 0 |  | -0.35603 | -1.0673 | -10.6621 | -3.9421 | 17.9343 | 1.5536 | -15.511 | 0 | 0 | 0 | 0 | 0
19 | 19 | 0 | 0 |  | -0.35603 | -1.0673 | -10.6621 | -3.9421 | 18.9343 | 1.8154 | -24.5071 | 0 | 0 | 0 | 0 | 0
19 | 20 | 0 | 0 |  | -0.35603 | -1.0673 | -10.6621 | -3.9421 | 19.9343 | 2.0772 | -33.5602 | 0 | 0 | 0 | 0 | 0
19 | 21 | 0 | 0 |  | -0.35603 | -1.0673 | -10.6621 | -3.9421 | 20.9343 | 2.339 | -42.2244 | 0 | 0 | 0 | 0 | 0
19 | 22 | 0 | 0 |  | -0.35603 | -1.0673 | -10.6621 | -3.9421 | 21.9343 | 2.6008 | -49.8493 | 0 | 0 | 0 | 0 | 0
19 | 23 | 0 | 0 |  | -0.35603 | -1.0673 | -10.6621 | -3.9421 | 22.9343 | 2.8626 | -55.4335 | 0 | 0 | 0 | 0 | 0
19 | 24 | 0 | 0 |  | -0.35603 | -1.0673 | -10.6621 | -3.9421 | 23.9343 | 3.1244 | -57.7102 | 0 | 0 | 0 | 0 | 0
20 | 1 | 0 | 0 |  | -0.35246 | -1.0501 | -10.9643 | -4.2443 | 0.92926 | -2.8983 | -55.7683 | 0 | 0 | 0 | 0 | 0
20 | 2 | 0 | 0 |  | -0.35246 | -1.0501 | -10.9643 | -4.2443 | 1.9293 | -2.6365 | -50.5769 | 0 | 0 | 0 | 0 | 0
20 | 3 | 0 | 0 |  | -0.35246 | -1.0501 | -10.9643 | -4.2443 | 2.9293 | -2.3747 | -43.1767 | 0 | 0 | 0 | 0 | 0
20 | 4 | 0 | 0 |  | -0.35246 | -1.0501 | -10.9643 | -4.2443 | 3.9293 | -2.1129 | -34.618 | 0 | 0 | 0 | 0 | 0
20 | 5 | 0 | 0 |  | -0.35246 | -1.0501 | -10.9643 | -4.2443 | 4.9293 | -1.8511 | -25.5912 | 0 | 0 | 0 | 0 | 0
20 | 6 | 0 | 0 |  | -0.35246 | -1.0501 | -10.9643 | -4.2443 | 5.9293 | -1.5893 | -16.5627 | 0 | 0 | 0 | 0 | 0
20 | 7 | 0 | 0 |  | -0.35246 | -1.0501 | -10.9643 | -4.2443 | 6.9293 | -1.3275 | -7.901 | 0 | 0 | 0 | 0 | 0
20 | 8 | 0 | 0 |  | -0.35246 | -1.0501 | -10.9643 | -4.2443 | 7.9293 | -1.0657 | 0.045725 | 0 | 0 | 0 | 0 | 0
20 | 9 | 56 | 25 |  | -0.35246 | -1.0501 | -10.9643 | -4.2443 | 8.9293 | -0.80392 | 6.9092 | 26.1953 | 20.8333 | 47.0286 | 74.6627 | 0
20 | 10 | 141 | 72 |  | -0.35246 | -1.0501 | -10.9643 | -4.2443 | 9.9293 | -0.54212 | 12.2916 | 85.8249 | 60 | 145.8249 | 231.5116 | 0
20 | 11 | 301 | 87 |  | -0.35246 | -1.0501 | -10.9643 | -4.2443 | 10.9293 | -0.28032 | 15.7989 | 210.4137 | 72.5 | 282.9137 | 449.1538 | 1
20 | 12 | 64 | 115 |  | -0.35246 | -1.0501 | -10.9643 | -4.2443 | 11.9293 | -0.018519 | 17.12 | 46.8929 | 95.8333 | 142.7262 | 226.5921 | 1
20 | 13 | 266 | 162 |  | -0.35246 | -1.0501 | -10.9643 | -4.2443 | 12.9293 | 0.24328 | 16.1239 | 188.155 | 135 | 323.155 | 513.0409 | 1
20 | 14 | 493 | 69 |  | -0.35246 | -1.0501 | -10.9643 | -4.2443 | 13.9293 | 0.50508 | 12.9102 | 307.9884 | 57.5 | 365.4884 | 580.2494 | 1
20 | 15 | 213 | 66 |  | -0.35246 | -1.0501 | -10.9643 | -4.2443 | 14.9293 | 0.76688 | 7.77 | 104.4662 | 55 | 159.4662 | 253.1685 | 0
20 | 16 | 25 | 29 |  | -0.35246 | -1.0501 | -10.9643 | -4.2443 | 15.9293 | 1.0287 | 1.0915 | 7.8421 | 24.1667 | 32.0088 | 50.8172 | 0
20 | 17 | 0 | 0 |  | -0.35246 | -1.0501 | -10.9643 | -4.2443 | 16.9293 | 1.2905 | -6.7252 | 0 | 0 | 0 | 0 | 0
20 | 18 | 0 | 0 |  | -0.35246 | -1.0501 | -10.9643 | -4.2443 | 17.9293 | 1.5523 | -15.3069 | 0 | 0 | 0 | 0 | 0
20 | 19 | 0 | 0 |  | -0.35246 | -1.0501 | -10.9643 | -4.2443 | 18.9293 | 1.8141 | -24.3048 | 0 | 0 | 0 | 0 | 0
20 | 20 | 0 | 0 |  | -0.35246 | -1.0501 | -10.9643 | -4.2443 | 19.9293 | 2.0759 | -33.3568 | 0 | 0 | 0 | 0 | 0
20 | 21 | 0 | 0 |  | -0.35246 | -1.0501 | -10.9643 | -4.2443 | 20.9293 | 2.3377 | -42.0169 | 0 | 0 | 0 | 0 | 0
20 | 22 | 0 | 0 |  | -0.35246 | -1.0501 | -10.9643 | -4.2443 | 21.9293 | 2.5995 | -49.6356 | 0 | 0 | 0 | 0 | 0
20 | 23 | 0 | 0 |  | -0.35246 | -1.0501 | -10.9643 | -4.2443 | 22.9293 | 2.8613 | -55.2166 | 0 | 0 | 0 | 0 | 0
20 | 24 | 0 | 0 |  | -0.35246 | -1.0501 | -10.9643 | -4.2443 | 23.9293 | 3.1231 | -57.5038 | 0 | 0 | 0 | 0 | 0
21 | 1 | 0 | 0 |  | -0.34877 | -1.0329 | -11.2557 | -4.5357 | 0.9244 | -2.8996 | -55.5821 | 0 | 0 | 0 | 0 | 0
21 | 2 | 0 | 0 |  | -0.34877 | -1.0329 | -11.2557 | -4.5357 | 1.9244 | -2.6378 | -50.4211 | 0 | 0 | 0 | 0 | 0
21 | 3 | 0 | 0 |  | -0.34877 | -1.0329 | -11.2557 | -4.5357 | 2.9244 | -2.376 | -43.0436 | 0 | 0 | 0 | 0 | 0
21 | 4 | 0 | 0 |  | -0.34877 | -1.0329 | -11.2557 | -4.5357 | 3.9244 | -2.1142 | -34.4973 | 0 | 0 | 0 | 0 | 0
21 | 5 | 0 | 0 |  | -0.34877 | -1.0329 | -11.2557 | -4.5357 | 4.9244 | -1.8524 | -25.4742 | 0 | 0 | 0 | 0 | 0
21 | 6 | 0 | 0 |  | -0.34877 | -1.0329 | -11.2557 | -4.5357 | 5.9244 | -1.5906 | -16.4424 | 0 | 0 | 0 | 0 | 0
21 | 7 | 0 | 0 |  | -0.34877 | -1.0329 | -11.2557 | -4.5357 | 6.9244 | -1.3288 | -7.7719 | 0 | 0 | 0 | 0 | 0
21 | 8 | 0 | 0 |  | -0.34877 | -1.0329 | -11.2557 | -4.5357 | 7.9244 | -1.067 | 0.18826 | 0 | 0 | 0 | 0 | 0
21 | 9 | 0 | 18 |  | -0.34877 | -1.0329 | -11.2557 | -4.5357 | 8.9244 | -0.80519 | 7.0685 | 0 | 15 | 15 | 23.814 | 0
21 | 10 | 31 | 60 |  | -0.34877 | -1.0329 | -11.2557 | -4.5357 | 9.9244 | -0.54339 | 12.4695 | 18.924 | 50 | 68.924 | 109.4237 | 0
21 | 11 | 51 | 97 |  | -0.34877 | -1.0329 | -11.2557 | -4.5357 | 10.9244 | -0.28159 | 15.9947 | 35.7611 | 80.8333 | 116.5945 | 185.1054 | 1
21 | 12 | 0 | 85 |  | -0.34877 | -1.0329 | -11.2557 | -4.5357 | 11.9244 | -0.019791 | 17.3301 | 0 | 70.8333 | 70.8333 | 112.455 | 1
21 | 13 | 0 | 86 |  | -0.34877 | -1.0329 | -11.2557 | -4.5357 | 12.9244 | 0.24201 | 16.3429 | 0 | 71.6667 | 71.6667 | 113.778 | 1
21 | 14 | 0 | 72 |  | -0.34877 | -1.0329 | -11.2557 | -4.5357 | 13.9244 | 0.50381 | 13.132 | 0 | 60 | 60 | 95.256 | 1
21 | 15 | 0 | 45 |  | -0.34877 | -1.0329 | -11.2557 | -4.5357 | 14.9244 | 0.76561 | 7.9901 | 0 | 37.5 | 37.5 | 59.535 | 0
21 | 16 | 0 | 14 |  | -0.34877 | -1.0329 | -11.2557 | -4.5357 | 15.9244 | 1.0274 | 1.3073 | 0 | 11.6667 | 11.6667 | 18.522 | 0
21 | 17 | 0 | 1 |  | -0.34877 | -1.0329 | -11.2557 | -4.5357 | 16.9244 | 1.2892 | -6.5141 | 0 | 0.83333 | 0.83333 | 1.323 | 0
21 | 18 | 0 | 0 |  | -0.34877 | -1.0329 | -11.2557 | -4.5357 | 17.9244 | 1.551 | -15.0998 | 0 | 0 | 0 | 0 | 0
21 | 19 | 0 | 0 |  | -0.34877 | -1.0329 | -11.2557 | -4.5357 | 18.9244 | 1.8128 | -24.0995 | 0 | 0 | 0 | 0 | 0
21 | 20 | 0 | 0 |  | -0.34877 | -1.0329 | -11.2557 | -4.5357 | 19.9244 | 2.0746 | -33.1503 | 0 | 0 | 0 | 0 | 0
21 | 21 | 0 | 0 |  | -0.34877 | -1.0329 | -11.2557 | -4.5357 | 20.9244 | 2.3364 | -41.8058 | 0 | 0 | 0 | 0 | 0
21 | 22 | 0 | 0 |  | -0.34877 | -1.0329 | -11.2557 | -4.5357 | 21.9244 | 2.5982 | -49.4177 | 0 | 0 | 0 | 0 | 0
21 | 23 | 0 | 0 |  | -0.34877 | -1.0329 | -11.2557 | -4.5357 | 22.9244 | 2.86 | -54.9948 | 0 | 0 | 0 | 0 | 0
21 | 24 | 0 | 0 |  | -0.34877 | -1.0329 | -11.2557 | -4.5357 | 23.9244 | 3.1218 | -57.2913 | 0 | 0 | 0 | 0 | 0
22 | 1 | 0 | 0 |  | -0.34499 | -1.0156 | -11.5361 | -4.8161 | 0.91973 | -2.9008 | -55.3892 | 0 | 0 | 0 | 0 | 0
22 | 2 | 0 | 0 |  | -0.34499 | -1.0156 | -11.5361 | -4.8161 | 1.9197 | -2.639 | -50.2585 | 0 | 0 | 0 | 0 | 0
22 | 3 | 0 | 0 |  | -0.34499 | -1.0156 | -11.5361 | -4.8161 | 2.9197 | -2.3772 | -42.9038 | 0 | 0 | 0 | 0 | 0
22 | 4 | 0 | 0 |  | -0.34499 | -1.0156 | -11.5361 | -4.8161 | 3.9197 | -2.1154 | -34.3701 | 0 | 0 | 0 | 0 | 0
22 | 5 | 0 | 0 |  | -0.34499 | -1.0156 | -11.5361 | -4.8161 | 4.9197 | -1.8536 | -25.3508 | 0 | 0 | 0 | 0 | 0
22 | 6 | 0 | 0 |  | -0.34499 | -1.0156 | -11.5361 | -4.8161 | 5.9197 | -1.5918 | -16.3159 | 0 | 0 | 0 | 0 | 0
22 | 7 | 0 | 0 |  | -0.34499 | -1.0156 | -11.5361 | -4.8161 | 6.9197 | -1.33 | -7.6366 | 0 | 0 | 0 | 0 | 0
22 | 8 | 0 | 0 |  | -0.34499 | -1.0156 | -11.5361 | -4.8161 | 7.9197 | -1.0682 | 0.33704 | 0 | 0 | 0 | 0 | 0
22 | 9 | 0 | 19 |  | -0.34499 | -1.0156 | -11.5361 | -4.8161 | 8.9197 | -0.80641 | 7.2342 | 0 | 15.8333 | 15.8333 | 25.137 | 0
22 | 10 | 33 | 61 |  | -0.34499 | -1.0156 | -11.5361 | -4.8161 | 9.9197 | -0.54461 | 12.6537 | 20.2056 | 50.8333 | 71.0389 | 112.7814 | 1
22 | 11 | 52 | 99 |  | -0.34499 | -1.0156 | -11.5361 | -4.8161 | 10.9197 | -0.28281 | 16.1967 | 36.5777 | 82.5 | 119.0777 | 189.0477 | 1
22 | 12 | 45 | 124 |  | -0.34499 | -1.0156 | -11.5361 | -4.8161 | 11.9197 | -0.021014 | 17.5462 | 33.1974 | 103.3333 | 136.5307 | 216.7561 | 1
22 | 13 | 0 | 87 |  | -0.34499 | -1.0156 | -11.5361 | -4.8161 | 12.9197 | 0.24079 | 16.5673 | 0 | 72.5 | 72.5 | 115.101 | 1
22 | 14 | 0 | 73 |  | -0.34499 | -1.0156 | -11.5361 | -4.8161 | 13.9197 | 0.50258 | 13.3587 | 0 | 60.8333 | 60.8333 | 96.579 | 1
22 | 15 | 0 | 46 |  | -0.34499 | -1.0156 | -11.5361 | -4.8161 | 14.9197 | 0.76438 | 8.2145 | 0 | 38.3333 | 38.3333 | 60.858 | 0
22 | 16 | 0 | 14 |  | -0.34499 | -1.0156 | -11.5361 | -4.8161 | 15.9197 | 1.0262 | 1.527 | 0 | 11.6667 | 11.6667 | 18.522 | 0
22 | 17 | 0 | 0 |  | -0.34499 | -1.0156 | -11.5361 | -4.8161 | 16.9197 | 1.288 | -6.2997 | 0 | 0 | 0 | 0 | 0
22 | 18 | 0 | 0 |  | -0.34499 | -1.0156 | -11.5361 | -4.8161 | 17.9197 | 1.5498 | -14.8895 | 0 | 0 | 0 | 0 | 0
22 | 19 | 0 | 0 |  | -0.34499 | -1.0156 | -11.5361 | -4.8161 | 18.9197 | 1.8116 | -23.8911 | 0 | 0 | 0 | 0 | 0
22 | 20 | 0 | 0 |  | -0.34499 | -1.0156 | -11.5361 | -4.8161 | 19.9197 | 2.0734 | -32.9408 | 0 | 0 | 0 | 0 | 0
22 | 21 | 0 | 0 |  | -0.34499 | -1.0156 | -11.5361 | -4.8161 | 20.9197 | 2.3352 | -41.5914 | 0 | 0 | 0 | 0 | 0
22 | 22 | 0 | 0 |  | -0.34499 | -1.0156 | -11.5361 | -4.8161 | 21.9197 | 2.597 | -49.1958 | 0 | 0 | 0 | 0 | 0
22 | 23 | 0 | 0 |  | -0.34499 | -1.0156 | -11.5361 | -4.8161 | 22.9197 | 2.8588 | -54.7681 | 0 | 0 | 0 | 0 | 0
22 | 24 | 0 | 0 |  | -0.34499 | -1.0156 | -11.5361 | -4.8161 | 23.9197 | 3.1206 | -57.073 | 0 | 0 | 0 | 0 | 0
23 | 1 | 0 | 0 |  | -0.3411 | -0.99842 | -11.8052 | -5.0852 | 0.91525 | -2.902 | -55.1898 | 0 | 0 | 0 | 0 | 0
23 | 2 | 0 | 0 |  | -0.3411 | -0.99842 | -11.8052 | -5.0852 | 1.9152 | -2.6402 | -50.089 | 0 | 0 | 0 | 0 | 0
23 | 3 | 0 | 0 |  | -0.3411 | -0.99842 | -11.8052 | -5.0852 | 2.9152 | -2.3784 | -42.7573 | 0 | 0 | 0 | 0 | 0
23 | 4 | 0 | 0 |  | -0.3411 | -0.99842 | -11.8052 | -5.0852 | 3.9152 | -2.1166 | -34.2365 | 0 | 0 | 0 | 0 | 0
23 | 5 | 0 | 0 |  | -0.3411 | -0.99842 | -11.8052 | -5.0852 | 4.9152 | -1.8548 | -25.2212 | 0 | 0 | 0 | 0 | 0
23 | 6 | 0 | 0 |  | -0.3411 | -0.99842 | -11.8052 | -5.0852 | 5.9152 | -1.593 | -16.1832 | 0 | 0 | 0 | 0 | 0
23 | 7 | 0 | 0 |  | -0.3411 | -0.99842 | -11.8052 | -5.0852 | 6.9152 | -1.3312 | -7.4951 | 0 | 0 | 0 | 0 | 0
23 | 8 | 0 | 0 |  | -0.3411 | -0.99842 | -11.8052 | -5.0852 | 7.9152 | -1.0694 | 0.49203 | 0 | 0 | 0 | 0 | 0
23 | 9 | 0 | 19 |  | -0.3411 | -0.99842 | -11.8052 | -5.0852 | 8.9152 | -0.80759 | 7.4061 | 0 | 15.8333 | 15.8333 | 25.137 | 0
23 | 10 | 145 | 63 |  | -0.3411 | -0.99842 | -11.8052 | -5.0852 | 9.9152 | -0.54579 | 12.8441 | 89.0597 | 52.5 | 141.5597 | 224.7401 | 1
23 | 11 | 259 | 104 |  | -0.3411 | -0.99842 | -11.8052 | -5.0852 | 10.9152 | -0.28399 | 16.4047 | 182.7765 | 86.6667 | 269.4432 | 427.768 | 1
23 | 12 | 489 | 96 |  | -0.3411 | -0.99842 | -11.8052 | -5.0852 | 11.9152 | -0.022188 | 17.768 | 362.0139 | 80 | 442.0139 | 701.7412 | 1
23 | 13 | 607 | 69 |  | -0.3411 | -0.99842 | -11.8052 | -5.0852 | 12.9152 | 0.23961 | 16.797 | 434.422 | 57.5 | 491.922 | 780.9753 | 1
23 | 14 | 537 | 72 |  | -0.3411 | -0.99842 | -11.8052 | -5.0852 | 13.9152 | 0.50141 | 13.5902 | 340.1874 | 60 | 400.1874 | 635.3375 | 1
23 | 15 | 100 | 79 |  | -0.3411 | -0.99842 | -11.8052 | -5.0852 | 14.9152 | 0.76321 | 8.4431 | 49.9343 | 65.8333 | 115.7677 | 183.7927 | 0
23 | 16 | 0 | 28 |  | -0.3411 | -0.99842 | -11.8052 | -5.0852 | 15.9152 | 1.025 | 1.7502 | 0 | 23.3333 | 23.3333 | 37.044 | 0
23 | 17 | 0 | 1 |  | -0.3411 | -0.99842 | -11.8052 | -5.0852 | 16.9152 | 1.2868 | -6.0821 | 0 | 0.83333 | 0.83333 | 1.323 | 0
23 | 18 | 0 | 0 |  | -0.3411 | -0.99842 | -11.8052 | -5.0852 | 17.9152 | 1.5486 | -14.6763 | 0 | 0 | 0 | 0 | 0
23 | 19 | 0 | 0 |  | -0.3411 | -0.99842 | -11.8052 | -5.0852 | 18.9152 | 1.8104 | -23.6799 | 0 | 0 | 0 | 0 | 0
23 | 20 | 0 | 0 |  | -0.3411 | -0.99842 | -11.8052 | -5.0852 | 19.9152 | 2.0722 | -32.7282 | 0 | 0 | 0 | 0 | 0
23 | 21 | 0 | 0 |  | -0.3411 | -0.99842 | -11.8052 | -5.0852 | 20.9152 | 2.334 | -41.3737 | 0 | 0 | 0 | 0 | 0
23 | 22 | 0 | 0 |  | -0.3411 | -0.99842 | -11.8052 | -5.0852 | 21.9152 | 2.5958 | -48.97 | 0 | 0 | 0 | 0 | 0
23 | 23 | 0 | 0 |  | -0.3411 | -0.99842 | -11.8052 | -5.0852 | 22.9152 | 2.8576 | -54.5366 | 0 | 0 | 0 | 0 | 0
23 | 24 | 0 | 0 |  | -0.3411 | -0.99842 | -11.8052 | -5.0852 | 23.9152 | 3.1194 | -56.8488 | 0 | 0 | 0 | 0 | 0
24 | 1 | 0 | 0 |  | -0.33711 | -0.98121 | -12.0628 | -5.3428 | 0.91095 | -2.9031 | -54.984 | 0 | 0 | 0 | 0 | 0
24 | 2 | 0 | 0 |  | -0.33711 | -0.98121 | -12.0628 | -5.3428 | 1.911 | -2.6413 | -49.9129 | 0 | 0 | 0 | 0 | 0
24 | 3 | 0 | 0 |  | -0.33711 | -0.98121 | -12.0628 | -5.3428 | 2.911 | -2.3795 | -42.6041 | 0 | 0 | 0 | 0 | 0
24 | 4 | 0 | 0 |  | -0.33711 | -0.98121 | -12.0628 | -5.3428 | 3.911 | -2.1177 | -34.0964 | 0 | 0 | 0 | 0 | 0
24 | 5 | 0 | 0 |  | -0.33711 | -0.98121 | -12.0628 | -5.3428 | 4.911 | -1.8559 | -25.0853 | 0 | 0 | 0 | 0 | 0
24 | 6 | 0 | 0 |  | -0.33711 | -0.98121 | -12.0628 | -5.3428 | 5.911 | -1.5941 | -16.0443 | 0 | 0 | 0 | 0 | 0
24 | 7 | 0 | 0 |  | -0.33711 | -0.98121 | -12.0628 | -5.3428 | 6.911 | -1.3323 | -7.3474 | 0 | 0 | 0 | 0 | 0
24 | 8 | 0 | 0 |  | -0.33711 | -0.98121 | -12.0628 | -5.3428 | 7.911 | -1.0705 | 0.65317 | 0 | 0 | 0 | 0 | 0
24 | 9 | 95 | 28 |  | -0.33711 | -0.98121 | -12.0628 | -5.3428 | 8.911 | -0.80871 | 7.5841 | 44.9966 | 23.3333 | 68.33 | 108.4807 | 0
24 | 10 | 149 | 64 |  | -0.33711 | -0.98121 | -12.0628 | -5.3428 | 9.911 | -0.54691 | 13.0407 | 91.8125 | 53.3333 | 145.1459 | 230.4336 | 1
24 | 11 | 37 | 107 |  | -0.33711 | -0.98121 | -12.0628 | -5.3428 | 10.911 | -0.28511 | 16.6187 | 26.1979 | 89.1667 | 115.3645 | 183.1527 | 1
24 | 12 | 57 | 125 |  | -0.33711 | -0.98121 | -12.0628 | -5.3428 | 11.911 | -0.023312 | 17.9955 | 42.349 | 104.1667 | 146.5157 | 232.6083 | 1
24 | 13 | 58 | 127 |  | -0.33711 | -0.98121 | -12.0628 | -5.3428 | 12.911 | 0.23849 | 17.0319 | 41.6763 | 105.8333 | 147.5096 | 234.1863 | 1
24 | 14 | 49 | 109 |  | -0.33711 | -0.98121 | -12.0628 | -5.3428 | 13.911 | 0.50029 | 13.8263 | 31.1879 | 90.8333 | 122.0213 | 193.721 | 1
24 | 15 | 0 | 49 |  | -0.33711 | -0.98121 | -12.0628 | -5.3428 | 14.911 | 0.76209 | 8.6757 | 0 | 40.8333 | 40.8333 | 64.827 | 0
24 | 16 | 0 | 16 |  | -0.33711 | -0.98121 | -12.0628 | -5.3428 | 15.911 | 1.0239 | 1.9771 | 0 | 13.3333 | 13.3333 | 21.168 | 0
24 | 17 | 0 | 1 |  | -0.33711 | -0.98121 | -12.0628 | -5.3428 | 16.911 | 1.2857 | -5.8613 | 0 | 0.83333 | 0.83333 | 1.323 | 0
24 | 18 | 0 | 0 |  | -0.33711 | -0.98121 | -12.0628 | -5.3428 | 17.911 | 1.5475 | -14.4602 | 0 | 0 | 0 | 0 | 0
24 | 19 | 0 | 0 |  | -0.33711 | -0.98121 | -12.0628 | -5.3428 | 18.911 | 1.8093 | -23.4658 | 0 | 0 | 0 | 0 | 0
24 | 20 | 0 | 0 |  | -0.33711 | -0.98121 | -12.0628 | -5.3428 | 19.911 | 2.0711 | -32.5127 | 0 | 0 | 0 | 0 | 0
24 | 21 | 0 | 0 |  | -0.33711 | -0.98121 | -12.0628 | -5.3428 | 20.911 | 2.3329 | -41.1527 | 0 | 0 | 0 | 0 | 0
24 | 22 | 0 | 0 |  | -0.33711 | -0.98121 | -12.0628 | -5.3428 | 21.911 | 2.5947 | -48.7404 | 0 | 0 | 0 | 0 | 0
24 | 23 | 0 | 0 |  | -0.33711 | -0.98121 | -12.0628 | -5.3428 | 22.911 | 2.8565 | -54.3004 | 0 | 0 | 0 | 0 | 0
24 | 24 | 0 | 0 |  | -0.33711 | -0.98121 | -12.0628 | -5.3428 | 23.911 | 3.1183 | -56.6189 | 0 | 0 | 0 | 0 | 0
25 | 1 | 0 | 0 |  | -0.33303 | -0.964 | -12.3087 | -5.5887 | 0.90685 | -2.9042 | -54.7717 | 0 | 0 | 0 | 0 | 0
25 | 2 | 0 | 0 |  | -0.33303 | -0.964 | -12.3087 | -5.5887 | 1.9069 | -2.6424 | -49.7301 | 0 | 0 | 0 | 0 | 0
25 | 3 | 0 | 0 |  | -0.33303 | -0.964 | -12.3087 | -5.5887 | 2.9069 | -2.3806 | -42.4444 | 0 | 0 | 0 | 0 | 0
25 | 4 | 0 | 0 |  | -0.33303 | -0.964 | -12.3087 | -5.5887 | 3.9069 | -2.1188 | -33.9498 | 0 | 0 | 0 | 0 | 0
25 | 5 | 0 | 0 |  | -0.33303 | -0.964 | -12.3087 | -5.5887 | 4.9069 | -1.857 | -24.9431 | 0 | 0 | 0 | 0 | 0
25 | 6 | 0 | 0 |  | -0.33303 | -0.964 | -12.3087 | -5.5887 | 5.9069 | -1.5952 | -15.8992 | 0 | 0 | 0 | 0 | 0
25 | 7 | 0 | 0 |  | -0.33303 | -0.964 | -12.3087 | -5.5887 | 6.9069 | -1.3334 | -7.1936 | 0 | 0 | 0 | 0 | 0
25 | 8 | 0 | 0 |  | -0.33303 | -0.964 | -12.3087 | -5.5887 | 7.9069 | -1.0716 | 0.82043 | 0 | 0 | 0 | 0 | 0
25 | 9 | 0 | 21 |  | -0.33303 | -0.964 | -12.3087 | -5.5887 | 8.9069 | -0.80978 | 7.7683 | 0 | 17.5 | 17.5 | 27.783 | 0
25 | 10 | 0 | 45 |  | -0.33303 | -0.964 | -12.3087 | -5.5887 | 9.9069 | -0.54798 | 13.2433 | 0 | 37.5 | 37.5 | 59.535 | 1
25 | 11 | 0 | 74 |  | -0.33303 | -0.964 | -12.3087 | -5.5887 | 10.9069 | -0.28618 | 16.8386 | 0 | 61.6667 | 61.6667 | 97.902 | 1
25 | 12 | 0 | 90 |  | -0.33303 | -0.964 | -12.3087 | -5.5887 | 11.9069 | -0.024385 | 18.2287 | 0 | 75 | 75 | 119.07 | 1
25 | 13 | 0 | 92 |  | -0.33303 | -0.964 | -12.3087 | -5.5887 | 12.9069 | 0.23741 | 17.272 | 0 | 76.6667 | 76.6667 | 121.716 | 1
25 | 14 | 0 | 78 |  | -0.33303 | -0.964 | -12.3087 | -5.5887 | 13.9069 | 0.49921 | 14.067 | 0 | 65 | 65 | 103.194 | 1
25 | 15 | 0 | 51 |  | -0.33303 | -0.964 | -12.3087 | -5.5887 | 14.9069 | 0.76101 | 8.9124 | 0 | 42.5 | 42.5 | 67.473 | 0
25 | 16 | 0 | 17 |  | -0.33303 | -0.964 | -12.3087 | -5.5887 | 15.9069 | 1.0228 | 2.2074 | 0 | 14.1667 | 14.1667 | 22.491 | 0
25 | 17 | 0 | 1 |  | -0.33303 | -0.964 | -12.3087 | -5.5887 | 16.9069 | 1.2846 | -5.6374 | 0 | 0.83333 | 0.83333 | 1.323 | 0
25 | 18 | 0 | 0 |  | -0.33303 | -0.964 | -12.3087 | -5.5887 | 17.9069 | 1.5464 | -14.2412 | 0 | 0 | 0 | 0 | 0
25 | 19 | 0 | 0 |  | -0.33303 | -0.964 | -12.3087 | -5.5887 | 18.9069 | 1.8082 | -23.2491 | 0 | 0 | 0 | 0 | 0
25 | 20 | 0 | 0 |  | -0.33303 | -0.964 | -12.3087 | -5.5887 | 19.9069 | 2.07 | -32.2944 | 0 | 0 | 0 | 0 | 0
25 | 21 | 0 | 0 |  | -0.33303 | -0.964 | -12.3087 | -5.5887 | 20.9069 | 2.3318 | -40.9286 | 0 | 0 | 0 | 0 | 0
25 | 22 | 0 | 0 |  | -0.33303 | -0.964 | -12.3087 | -5.5887 | 21.9069 | 2.5936 | -48.507 | 0 | 0 | 0 | 0 | 0
25 | 23 | 0 | 0 |  | -0.33303 | -0.964 | -12.3087 | -5.5887 | 22.9069 | 2.8554 | -54.0596 | 0 | 0 | 0 | 0 | 0
25 | 24 | 0 | 0 |  | -0.33303 | -0.964 | -12.3087 | -5.5887 | 23.9069 | 3.1172 | -56.3834 | 0 | 0 | 0 | 0 | 0
26 | 1 | 0 | 0 |  | -0.32885 | -0.94678 | -12.5428 | -5.8228 | 0.90295 | -2.9052 | -54.5531 | 0 | 0 | 0 | 0 | 0
26 | 2 | 0 | 0 |  | -0.32885 | -0.94678 | -12.5428 | -5.8228 | 1.903 | -2.6434 | -49.5406 | 0 | 0 | 0 | 0 | 0
26 | 3 | 0 | 0 |  | -0.32885 | -0.94678 | -12.5428 | -5.8228 | 2.903 | -2.3816 | -42.2781 | 0 | 0 | 0 | 0 | 0
26 | 4 | 0 | 0 |  | -0.32885 | -0.94678 | -12.5428 | -5.8228 | 3.903 | -2.1198 | -33.7969 | 0 | 0 | 0 | 0 | 0
26 | 5 | 0 | 0 |  | -0.32885 | -0.94678 | -12.5428 | -5.8228 | 4.903 | -1.858 | -24.7946 | 0 | 0 | 0 | 0 | 0
26 | 6 | 0 | 0 |  | -0.32885 | -0.94678 | -12.5428 | -5.8228 | 5.903 | -1.5962 | -15.748 | 0 | 0 | 0 | 0 | 0
26 | 7 | 0 | 0 |  | -0.32885 | -0.94678 | -12.5428 | -5.8228 | 6.903 | -1.3344 | -7.0337 | 0 | 0 | 0 | 0 | 0
26 | 8 | 0 | 0 |  | -0.32885 | -0.94678 | -12.5428 | -5.8228 | 7.903 | -1.0726 | 0.99375 | 0 | 0 | 0 | 0 | 0
26 | 9 | 0 | 14 |  | -0.32885 | -0.94678 | -12.5428 | -5.8228 | 8.903 | -0.8108 | 7.9585 | 0 | 11.6667 | 11.6667 | 18.522 | 0
26 | 10 | 0 | 46 |  | -0.32885 | -0.94678 | -12.5428 | -5.8228 | 9.903 | -0.54901 | 13.4519 | 0 | 38.3333 | 38.3333 | 60.858 | 1
26 | 11 | 0 | 75 |  | -0.32885 | -0.94678 | -12.5428 | -5.8228 | 10.903 | -0.28721 | 17.0644 | 0 | 62.5 | 62.5 | 99.225 | 1
26 | 12 | 0 | 92 |  | -0.32885 | -0.94678 | -12.5428 | -5.8228 | 11.903 | -0.025407 | 18.4673 | 0 | 76.6667 | 76.6667 | 121.716 | 1
26 | 13 | 0 | 94 |  | -0.32885 | -0.94678 | -12.5428 | -5.8228 | 12.903 | 0.23639 | 17.5172 | 0 | 78.3333 | 78.3333 | 124.362 | 1
26 | 14 | 0 | 80 |  | -0.32885 | -0.94678 | -12.5428 | -5.8228 | 13.903 | 0.49819 | 14.3122 | 0 | 66.6667 | 66.6667 | 105.84 | 1
26 | 15 | 14 | 81 |  | -0.32885 | -0.94678 | -12.5428 | -5.8228 | 14.903 | 0.75999 | 9.1529 | 7.118 | 67.5 | 74.618 | 118.4636 | 0
26 | 16 | 0 | 30 |  | -0.32885 | -0.94678 | -12.5428 | -5.8228 | 15.903 | 1.0218 | 2.441 | 0 | 25 | 25 | 39.69 | 0
26 | 17 | 0 | 2 |  | -0.32885 | -0.94678 | -12.5428 | -5.8228 | 16.903 | 1.2836 | -5.4107 | 0 | 1.6667 | 1.6667 | 2.646 | 0
26 | 18 | 0 | 0 |  | -0.32885 | -0.94678 | -12.5428 | -5.8228 | 17.903 | 1.5454 | -14.0196 | 0 | 0 | 0 | 0 | 0
26 | 19 | 0 | 0 |  | -0.32885 | -0.94678 | -12.5428 | -5.8228 | 18.903 | 1.8072 | -23.0297 | 0 | 0 | 0 | 0 | 0
26 | 20 | 0 | 0 |  | -0.32885 | -0.94678 | -12.5428 | -5.8228 | 19.903 | 2.069 | -32.0733 | 0 | 0 | 0 | 0 | 0
26 | 21 | 0 | 0 |  | -0.32885 | -0.94678 | -12.5428 | -5.8228 | 20.903 | 2.3308 | -40.7013 | 0 | 0 | 0 | 0 | 0
26 | 22 | 0 | 0 |  | -0.32885 | -0.94678 | -12.5428 | -5.8228 | 21.903 | 2.5926 | -48.27 | 0 | 0 | 0 | 0 | 0
26 | 23 | 0 | 0 |  | -0.32885 | -0.94678 | -12.5428 | -5.8228 | 22.903 | 2.8544 | -53.8143 | 0 | 0 | 0 | 0 | 0
26 | 24 | 0 | 0 |  | -0.32885 | -0.94678 | -12.5428 | -5.8228 | 23.903 | 3.1162 | -56.1424 | 0 | 0 | 0 | 0 | 0
27 | 1 | 0 | 0 |  | -0.32457 | -0.92957 | -12.7648 | -6.0448 | 0.89925 | -2.9062 | -54.3282 | 0 | 0 | 0 | 0 | 0
27 | 2 | 0 | 0 |  | -0.32457 | -0.92957 | -12.7648 | -6.0448 | 1.8993 | -2.6444 | -49.3446 | 0 | 0 | 0 | 0 | 0
27 | 3 | 0 | 0 |  | -0.32457 | -0.92957 | -12.7648 | -6.0448 | 2.8993 | -2.3826 | -42.1053 | 0 | 0 | 0 | 0 | 0
27 | 4 | 0 | 0 |  | -0.32457 | -0.92957 | -12.7648 | -6.0448 | 3.8993 | -2.1208 | -33.6377 | 0 | 0 | 0 | 0 | 0
27 | 5 | 0 | 0 |  | -0.32457 | -0.92957 | -12.7648 | -6.0448 | 4.8993 | -1.859 | -24.64 | 0 | 0 | 0 | 0 | 0
27 | 6 | 0 | 0 |  | -0.32457 | -0.92957 | -12.7648 | -6.0448 | 5.8993 | -1.5972 | -15.5907 | 0 | 0 | 0 | 0 | 0
27 | 7 | 0 | 0 |  | -0.32457 | -0.92957 | -12.7648 | -6.0448 | 6.8993 | -1.3354 | -6.8678 | 0 | 0 | 0 | 0 | 0
27 | 8 | 0 | 1 |  | -0.32457 | -0.92957 | -12.7648 | -6.0448 | 7.8993 | -1.0736 | 1.1731 | 0 | 0.83333 | 0.83333 | 1.323 | 0
27 | 9 | 0 | 14 |  | -0.32457 | -0.92957 | -12.7648 | -6.0448 | 8.8993 | -0.81177 | 8.1547 | 0 | 11.6667 | 11.6667 | 18.522 | 0
27 | 10 | 0 | 48 |  | -0.32457 | -0.92957 | -12.7648 | -6.0448 | 9.8993 | -0.54997 | 13.6664 | 0 | 40 | 40 | 63.504 | 1
27 | 11 | 0 | 77 |  | -0.32457 | -0.92957 | -12.7648 | -6.0448 | 10.8993 | -0.28817 | 17.296 | 0 | 64.1667 | 64.1667 | 101.871 | 1
27 | 12 | 0 | 94 |  | -0.32457 | -0.92957 | -12.7648 | -6.0448 | 11.8993 | -0.026375 | 18.7115 | 0 | 78.3333 | 78.3333 | 124.362 | 1
27 | 13 | 0 | 96 |  | -0.32457 | -0.92957 | -12.7648 | -6.0448 | 12.8993 | 0.23542 | 17.7673 | 0 | 80 | 80 | 127.008 | 1
27 | 14 | 0 | 82 |  | -0.32457 | -0.92957 | -12.7648 | -6.0448 | 13.8993 | 0.49722 | 14.5617 | 0 | 68.3333 | 68.3333 | 108.486 | 1
27 | 15 | 0 | 54 |  | -0.32457 | -0.92957 | -12.7648 | -6.0448 | 14.8993 | 0.75902 | 9.3971 | 0 | 45 | 45 | 71.442 | 0
27 | 16 | 0 | 20 |  | -0.32457 | -0.92957 | -12.7648 | -6.0448 | 15.8993 | 1.0208 | 2.6778 | 0 | 16.6667 | 16.6667 | 26.46 | 0
27 | 17 | 0 | 1 |  | -0.32457 | -0.92957 | -12.7648 | -6.0448 | 16.8993 | 1.2826 | -5.181 | 0 | 0.83333 | 0.83333 | 1.323 | 0
27 | 18 | 0 | 0 |  | -0.32457 | -0.92957 | -12.7648 | -6.0448 | 17.8993 | 1.5444 | -13.7954 | 0 | 0 | 0 | 0 | 0
27 | 19 | 0 | 0 |  | -0.32457 | -0.92957 | -12.7648 | -6.0448 | 18.8993 | 1.8062 | -22.8078 | 0 | 0 | 0 | 0 | 0
27 | 20 | 0 | 0 |  | -0.32457 | -0.92957 | -12.7648 | -6.0448 | 19.8993 | 2.068 | -31.8496 | 0 | 0 | 0 | 0 | 0
27 | 21 | 0 | 0 |  | -0.32457 | -0.92957 | -12.7648 | -6.0448 | 20.8993 | 2.3298 | -40.4711 | 0 | 0 | 0 | 0 | 0
27 | 22 | 0 | 0 |  | -0.32457 | -0.92957 | -12.7648 | -6.0448 | 21.8993 | 2.5916 | -48.0294 | 0 | 0 | 0 | 0 | 0
27 | 23 | 0 | 0 |  | -0.32457 | -0.92957 | -12.7648 | -6.0448 | 22.8993 | 2.8534 | -53.5646 | 0 | 0 | 0 | 0 | 0
27 | 24 | 0 | 0 |  | -0.32457 | -0.92957 | -12.7648 | -6.0448 | 23.8993 | 3.1152 | -55.896 | 0 | 0 | 0 | 0 | 0
28 | 1 | 0 | 0 |  | -0.3202 | -0.91235 | -12.9746 | -6.2546 | 0.89576 | -2.9071 | -54.0973 | 0 | 0 | 0 | 0 | 0
28 | 2 | 0 | 0 |  | -0.3202 | -0.91235 | -12.9746 | -6.2546 | 1.8958 | -2.6453 | -49.1421 | 0 | 0 | 0 | 0 | 0
28 | 3 | 0 | 0 |  | -0.3202 | -0.91235 | -12.9746 | -6.2546 | 2.8958 | -2.3835 | -41.926 | 0 | 0 | 0 | 0 | 0
28 | 4 | 0 | 0 |  | -0.3202 | -0.91235 | -12.9746 | -6.2546 | 3.8958 | -2.1217 | -33.4721 | 0 | 0 | 0 | 0 | 0
28 | 5 | 0 | 0 |  | -0.3202 | -0.91235 | -12.9746 | -6.2546 | 4.8958 | -1.8599 | -24.4792 | 0 | 0 | 0 | 0 | 0
28 | 6 | 0 | 0 |  | -0.3202 | -0.91235 | -12.9746 | -6.2546 | 5.8958 | -1.5981 | -15.4273 | 0 | 0 | 0 | 0 | 0
28 | 7 | 0 | 0 |  | -0.3202 | -0.91235 | -12.9746 | -6.2546 | 6.8958 | -1.3363 | -6.6958 | 0 | 0 | 0 | 0 | 0
28 | 8 | 0 | 0 |  | -0.3202 | -0.91235 | -12.9746 | -6.2546 | 7.8958 | -1.0745 | 1.3584 | 0 | 0 | 0 | 0 | 0
28 | 9 | 0 | 24 |  | -0.3202 | -0.91235 | -12.9746 | -6.2546 | 8.8958 | -0.81269 | 8.3568 | 0 | 20 | 20 | 31.752 | 0
28 | 10 | 287 | 82 |  | -0.3202 | -0.91235 | -12.9746 | -6.2546 | 9.8958 | -0.55089 | 13.8868 | 179.3314 | 68.3333 | 247.6647 | 393.1925 | 1
28 | 11 | 555 | 68 |  | -0.3202 | -0.91235 | -12.9746 | -6.2546 | 10.8958 | -0.28909 | 17.5332 | 398.5285 | 56.6667 | 455.1952 | 722.6679 | 1
28 | 12 | 586 | 83 |  | -0.3202 | -0.91235 | -12.9746 | -6.2546 | 11.8958 | -0.027291 | 18.9609 | 441.8937 | 69.1667 | 511.0604 | 811.3595 | 1
28 | 13 | 590 | 83 |  | -0.3202 | -0.91235 | -12.9746 | -6.2546 | 12.8958 | 0.23451 | 18.0223 | 430.9595 | 69.1667 | 500.1262 | 794.0003 | 1
28 | 14 | 55 | 116 |  | -0.3202 | -0.91235 | -12.9746 | -6.2546 | 13.8958 | 0.49631 | 14.8155 | 35.681 | 96.6667 | 132.3477 | 210.1152 | 1
28 | 15 | 19 | 84 |  | -0.3202 | -0.91235 | -12.9746 | -6.2546 | 14.8958 | 0.75811 | 9.6451 | 9.7768 | 70 | 79.7768 | 126.6537 | 0
28 | 16 | 0 | 33 |  | -0.3202 | -0.91235 | -12.9746 | -6.2546 | 15.8958 | 1.0199 | 2.9179 | 0 | 27.5 | 27.5 | 43.659 | 0
28 | 17 | 0 | 2 |  | -0.3202 | -0.91235 | -12.9746 | -6.2546 | 16.8958 | 1.2817 | -4.9487 | 0 | 1.6667 | 1.6667 | 2.646 | 0
28 | 18 | 0 | 0 |  | -0.3202 | -0.91235 | -12.9746 | -6.2546 | 17.8958 | 1.5435 | -13.5687 | 0 | 0 | 0 | 0 | 0
28 | 19 | 0 | 0 |  | -0.3202 | -0.91235 | -12.9746 | -6.2546 | 18.8958 | 1.8053 | -22.5834 | 0 | 0 | 0 | 0 | 0
28 | 20 | 0 | 0 |  | -0.3202 | -0.91235 | -12.9746 | -6.2546 | 19.8958 | 2.0671 | -31.6233 | 0 | 0 | 0 | 0 | 0
28 | 21 | 0 | 0 |  | -0.3202 | -0.91235 | -12.9746 | -6.2546 | 20.8958 | 2.3289 | -40.238 | 0 | 0 | 0 | 0 | 0
28 | 22 | 0 | 0 |  | -0.3202 | -0.91235 | -12.9746 | -6.2546 | 21.8958 | 2.5907 | -47.7853 | 0 | 0 | 0 | 0 | 0
28 | 23 | 0 | 0 |  | -0.3202 | -0.91235 | -12.9746 | -6.2546 | 22.8958 | 2.8525 | -53.3105 | 0 | 0 | 0 | 0 | 0
28 | 24 | 0 | 0 |  | -0.3202 | -0.91235 | -12.9746 | -6.2546 | 23.8958 | 3.1143 | -55.6443 | 0 | 0 | 0 | 0 | 0
29 | 1 | 0 | 0 |  | -0.31574 | -0.89514 | -13.1721 | -6.4521 | 0.89246 | -2.9079 | -53.8602 | 0 | 0 | 0 | 0 | 0
29 | 2 | 0 | 0 |  | -0.31574 | -0.89514 | -13.1721 | -6.4521 | 1.8925 | -2.6461 | -48.9332 | 0 | 0 | 0 | 0 | 0
29 | 3 | 0 | 0 |  | -0.31574 | -0.89514 | -13.1721 | -6.4521 | 2.8925 | -2.3843 | -41.7403 | 0 | 0 | 0 | 0 | 0
29 | 4 | 0 | 0 |  | -0.31574 | -0.89514 | -13.1721 | -6.4521 | 3.8925 | -2.1225 | -33.3002 | 0 | 0 | 0 | 0 | 0
29 | 5 | 0 | 0 |  | -0.31574 | -0.89514 | -13.1721 | -6.4521 | 4.8925 | -1.8607 | -24.3123 | 0 | 0 | 0 | 0 | 0
29 | 6 | 0 | 0 |  | -0.31574 | -0.89514 | -13.1721 | -6.4521 | 5.8925 | -1.5989 | -15.2579 | 0 | 0 | 0 | 0 | 0
29 | 7 | 0 | 0 |  | -0.31574 | -0.89514 | -13.1721 | -6.4521 | 6.8925 | -1.3371 | -6.518 | 0 | 0 | 0 | 0 | 0
29 | 8 | 0 | 1 |  | -0.31574 | -0.89514 | -13.1721 | -6.4521 | 7.8925 | -1.0754 | 1.5496 | 0 | 0.83333 | 0.83333 | 1.323 | 0
29 | 9 | 0 | 25 |  | -0.31574 | -0.89514 | -13.1721 | -6.4521 | 8.8925 | -0.81355 | 8.5648 | 0 | 20.8333 | 20.8333 | 33.075 | 0
29 | 10 | 14 | 77 |  | -0.31574 | -0.89514 | -13.1721 | -6.4521 | 9.8925 | -0.55175 | 14.1131 | 8.7806 | 64.1667 | 72.9472 | 115.811 | 1
29 | 11 | 58 | 111 |  | -0.31574 | -0.89514 | -13.1721 | -6.4521 | 10.8925 | -0.28995 | 17.7761 | 41.8018 | 92.5 | 134.3018 | 213.2176 | 1
29 | 12 | 48 | 138 |  | -0.31574 | -0.89514 | -13.1721 | -6.4521 | 11.8925 | -0.028153 | 19.2157 | 36.3353 | 115 | 151.3353 | 240.2599 | 1
29 | 13 | 0 | 98 |  | -0.31574 | -0.89514 | -13.1721 | -6.4521 | 12.8925 | 0.23365 | 18.2821 | 0 | 81.6667 | 81.6667 | 129.654 | 1
29 | 14 | 49 | 119 |  | -0.31574 | -0.89514 | -13.1721 | -6.4521 | 13.8925 | 0.49545 | 15.0735 | 31.9417 | 99.1667 | 131.1084 | 208.1476 | 1
29 | 15 | 19 | 86 |  | -0.31574 | -0.89514 | -13.1721 | -6.4521 | 14.8925 | 0.75725 | 9.8966 | 9.8355 | 71.6667 | 81.5022 | 129.3928 | 0
29 | 16 | 0 | 35 |  | -0.31574 | -0.89514 | -13.1721 | -6.4521 | 15.8925 | 1.019 | 3.1609 | 0 | 29.1667 | 29.1667 | 46.305 | 0
29 | 17 | 0 | 3 |  | -0.31574 | -0.89514 | -13.1721 | -6.4521 | 16.8925 | 1.2808 | -4.7137 | 0 | 2.5 | 2.5 | 3.969 | 0
29 | 18 | 0 | 0 |  | -0.31574 | -0.89514 | -13.1721 | -6.4521 | 17.8925 | 1.5426 | -13.3395 | 0 | 0 | 0 | 0 | 0
29 | 19 | 0 | 0 |  | -0.31574 | -0.89514 | -13.1721 | -6.4521 | 18.8925 | 1.8044 | -22.3567 | 0 | 0 | 0 | 0 | 0
29 | 20 | 0 | 0 |  | -0.31574 | -0.89514 | -13.1721 | -6.4521 | 19.8925 | 2.0662 | -31.3945 | 0 | 0 | 0 | 0 | 0
29 | 21 | 0 | 0 |  | -0.31574 | -0.89514 | -13.1721 | -6.4521 | 20.8925 | 2.328 | -40.002 | 0 | 0 | 0 | 0 | 0
29 | 22 | 0 | 0 |  | -0.31574 | -0.89514 | -13.1721 | -6.4521 | 21.8925 | 2.5898 | -47.5377 | 0 | 0 | 0 | 0 | 0
29 | 23 | 0 | 0 |  | -0.31574 | -0.89514 | -13.1721 | -6.4521 | 22.8925 | 2.8516 | -53.0522 | 0 | 0 | 0 | 0 | 0
29 | 24 | 0 | 0 |  | -0.31574 | -0.89514 | -13.1721 | -6.4521 | 23.8925 | 3.1134 | -55.3874 | 0 | 0 | 0 | 0 | 0
30 | 1 | 0 | 0 |  | -0.31119 | -0.87792 | -13.3571 | -6.6371 | 0.88938 | -2.9088 | -53.6173 | 0 | 0 | 0 | 0 | 0
30 | 2 | 0 | 0 |  | -0.31119 | -0.87792 | -13.3571 | -6.6371 | 1.8894 | -2.647 | -48.7179 | 0 | 0 | 0 | 0 | 0
30 | 3 | 0 | 0 |  | -0.31119 | -0.87792 | -13.3571 | -6.6371 | 2.8894 | -2.3852 | -41.5482 | 0 | 0 | 0 | 0 | 0
30 | 4 | 0 | 0 |  | -0.31119 | -0.87792 | -13.3571 | -6.6371 | 3.8894 | -2.1234 | -33.1221 | 0 | 0 | 0 | 0 | 0
30 | 5 | 0 | 0 |  | -0.31119 | -0.87792 | -13.3571 | -6.6371 | 4.8894 | -1.8616 | -24.1393 | 0 | 0 | 0 | 0 | 0
30 | 6 | 0 | 0 |  | -0.31119 | -0.87792 | -13.3571 | -6.6371 | 5.8894 | -1.5998 | -15.0826 | 0 | 0 | 0 | 0 | 0
30 | 7 | 0 | 0 |  | -0.31119 | -0.87792 | -13.3571 | -6.6371 | 6.8894 | -1.338 | -6.3342 | 0 | 0 | 0 | 0 | 0
30 | 8 | 0 | 2 |  | -0.31119 | -0.87792 | -13.3571 | -6.6371 | 7.8894 | -1.0762 | 1.7467 | 0 | 1.6667 | 1.6667 | 2.646 | 0
30 | 9 | 131 | 35 |  | -0.31119 | -0.87792 | -13.3571 | -6.6371 | 8.8894 | -0.81436 | 8.7787 | 63.5071 | 29.1667 | 92.6738 | 147.1289 | 0
30 | 10 | 348 | 75 |  | -0.31119 | -0.87792 | -13.3571 | -6.6371 | 9.8894 | -0.55256 | 14.345 | 219.095 | 62.5 | 281.595 | 447.0603 | 1
30 | 11 | 278 | 116 |  | -0.31119 | -0.87792 | -13.3571 | -6.6371 | 10.8894 | -0.29076 | 18.0245 | 201.1133 | 96.6667 | 297.7799 | 472.7554 | 1
30 | 12 | 523 | 110 |  | -0.31119 | -0.87792 | -13.3571 | -6.6371 | 11.8894 | -0.02896 | 19.4757 | 397.4426 | 91.6667 | 489.1093 | 776.5099 | 1
30 | 13 | 647 | 75 |  | -0.31119 | -0.87792 | -13.3571 | -6.6371 | 12.8894 | 0.23284 | 18.5465 | 476.5766 | 62.5 | 539.0766 | 855.8381 | 1
30 | 14 | 598 | 71 |  | -0.31119 | -0.87792 | -13.3571 | -6.6371 | 13.8894 | 0.49464 | 15.3356 | 391.7002 | 59.1667 | 450.8669 | 715.7963 | 1
30 | 15 | 484 | 60 |  | -0.31119 | -0.87792 | -13.3571 | -6.6371 | 14.8894 | 0.75644 | 10.1515 | 252.0458 | 50 | 302.0458 | 479.5278 | 0
30 | 16 | 189 | 44 |  | -0.31119 | -0.87792 | -13.3571 | -6.6371 | 15.8894 | 1.0182 | 3.4069 | 64.8194 | 36.6667 | 101.4861 | 161.1193 | 0
30 | 17 | 0 | 5 |  | -0.31119 | -0.87792 | -13.3571 | -6.6371 | 16.8894 | 1.28 | -4.4761 | 0 | 4.1667 | 4.1667 | 6.615 | 0
30 | 18 | 0 | 0 |  | -0.31119 | -0.87792 | -13.3571 | -6.6371 | 17.8894 | 1.5418 | -13.108 | 0 | 0 | 0 | 0 | 0
30 | 19 | 0 | 0 |  | -0.31119 | -0.87792 | -13.3571 | -6.6371 | 18.8894 | 1.8036 | -22.1276 | 0 | 0 | 0 | 0 | 0
30 | 20 | 0 | 0 |  | -0.31119 | -0.87792 | -13.3571 | -6.6371 | 19.8894 | 2.0654 | -31.1633 | 0 | 0 | 0 | 0 | 0
30 | 21 | 0 | 0 |  | -0.31119 | -0.87792 | -13.3571 | -6.6371 | 20.8894 | 2.3272 | -39.7632 | 0 | 0 | 0 | 0 | 0
30 | 22 | 0 | 0 |  | -0.31119 | -0.87792 | -13.3571 | -6.6371 | 21.8894 | 2.589 | -47.2868 | 0 | 0 | 0 | 0 | 0
30 | 23 | 0 | 0 |  | -0.31119 | -0.87792 | -13.3571 | -6.6371 | 22.8894 | 2.8508 | -52.7898 | 0 | 0 | 0 | 0 | 0
30 | 24 | 0 | 0 |  | -0.31119 | -0.87792 | -13.3571 | -6.6371 | 23.8894 | 3.1126 | -55.1254 | 0 | 0 | 0 | 0 | 0
31 | 1 | 0 | 0 |  | -0.30655 | -0.86071 | -13.5296 | -6.8096 | 0.88651 | -2.9095 | -53.3685 | 0 | 0 | 0 | 0 | 0
31 | 2 | 0 | 0 |  | -0.30655 | -0.86071 | -13.5296 | -6.8096 | 1.8865 | -2.6477 | -48.4964 | 0 | 0 | 0 | 0 | 0
31 | 3 | 0 | 0 |  | -0.30655 | -0.86071 | -13.5296 | -6.8096 | 2.8865 | -2.3859 | -41.3498 | 0 | 0 | 0 | 0 | 0
31 | 4 | 0 | 0 |  | -0.30655 | -0.86071 | -13.5296 | -6.8096 | 3.8865 | -2.1241 | -32.9378 | 0 | 0 | 0 | 0 | 0
31 | 5 | 0 | 0 |  | -0.30655 | -0.86071 | -13.5296 | -6.8096 | 4.8865 | -1.8623 | -23.9602 | 0 | 0 | 0 | 0 | 0
31 | 6 | 0 | 0 |  | -0.30655 | -0.86071 | -13.5296 | -6.8096 | 5.8865 | -1.6005 | -14.9013 | 0 | 0 | 0 | 0 | 0
31 | 7 | 0 | 0 |  | -0.30655 | -0.86071 | -13.5296 | -6.8096 | 6.8865 | -1.3387 | -6.1446 | 0 | 0 | 0 | 0 | 0
31 | 8 | 0 | 1 |  | -0.30655 | -0.86071 | -13.5296 | -6.8096 | 7.8865 | -1.0769 | 1.9496 | 0 | 0.83333 | 0.83333 | 1.323 | 0
31 | 9 | 0 | 18 |  | -0.30655 | -0.86071 | -13.5296 | -6.8096 | 8.8865 | -0.81511 | 8.9982 | 0 | 15 | 15 | 23.814 | 0
31 | 10 | 0 | 53 |  | -0.30655 | -0.86071 | -13.5296 | -6.8096 | 9.8865 | -0.55331 | 14.5826 | 0 | 44.1667 | 44.1667 | 70.119 | 1
31 | 11 | 0 | 83 |  | -0.30655 | -0.86071 | -13.5296 | -6.8096 | 10.8865 | -0.29151 | 18.2784 | 0 | 69.1667 | 69.1667 | 109.809 | 1
31 | 12 | 0 | 100 |  | -0.30655 | -0.86071 | -13.5296 | -6.8096 | 11.8865 | -0.029712 | 19.7407 | 0 | 83.3333 | 83.3333 | 132.3 | 1
31 | 13 | 0 | 101 |  | -0.30655 | -0.86071 | -13.5296 | -6.8096 | 12.8865 | 0.23209 | 18.8155 | 0 | 84.1667 | 84.1667 | 133.623 | 1
31 | 14 | 0 | 87 |  | -0.30655 | -0.86071 | -13.5296 | -6.8096 | 13.8865 | 0.49389 | 15.6016 | 0 | 72.5 | 72.5 | 115.101 | 1
31 | 15 | 0 | 60 |  | -0.30655 | -0.86071 | -13.5296 | -6.8096 | 14.8865 | 0.75569 | 10.4098 | 0 | 50 | 50 | 79.38 | 0
31 | 16 | 0 | 25 |  | -0.30655 | -0.86071 | -13.5296 | -6.8096 | 15.8865 | 1.0175 | 3.6557 | 0 | 20.8333 | 20.8333 | 33.075 | 0
31 | 17 | 0 | 2 |  | -0.30655 | -0.86071 | -13.5296 | -6.8096 | 16.8865 | 1.2793 | -4.236 | 0 | 1.6667 | 1.6667 | 2.646 | 0
31 | 18 | 0 | 0 |  | -0.30655 | -0.86071 | -13.5296 | -6.8096 | 17.8865 | 1.5411 | -12.8743 | 0 | 0 | 0 | 0 | 0
31 | 19 | 0 | 0 |  | -0.30655 | -0.86071 | -13.5296 | -6.8096 | 18.8865 | 1.8029 | -21.8964 | 0 | 0 | 0 | 0 | 0
31 | 20 | 0 | 0 |  | -0.30655 | -0.86071 | -13.5296 | -6.8096 | 19.8865 | 2.0647 | -30.9297 | 0 | 0 | 0 | 0 | 0
31 | 21 | 0 | 0 |  | -0.30655 | -0.86071 | -13.5296 | -6.8096 | 20.8865 | 2.3265 | -39.5217 | 0 | 0 | 0 | 0 | 0
31 | 22 | 0 | 0 |  | -0.30655 | -0.86071 | -13.5296 | -6.8096 | 21.8865 | 2.5883 | -47.0327 | 0 | 0 | 0 | 0 | 0
31 | 23 | 0 | 0 |  | -0.30655 | -0.86071 | -13.5296 | -6.8096 | 22.8865 | 2.8501 | -52.5233 | 0 | 0 | 0 | 0 | 0
31 | 24 | 0 | 0 |  | -0.30655 | -0.86071 | -13.5296 | -6.8096 | 23.8865 | 3.1119 | -54.8583 | 0 | 0 | 0 | 0 | 0
32 | 1 | 0 | 0 |  | -0.30182 | -0.8435 | -13.6893 | -6.9693 | 0.88384 | -2.9102 | -53.1139 | 0 | 0 | 0 | 0 | 0
32 | 2 | 0 | 0 |  | -0.30182 | -0.8435 | -13.6893 | -6.9693 | 1.8838 | -2.6484 | -48.2686 | 0 | 0 | 0 | 0 | 0
32 | 3 | 0 | 0 |  | -0.30182 | -0.8435 | -13.6893 | -6.9693 | 2.8838 | -2.3866 | -41.1452 | 0 | 0 | 0 | 0 | 0
32 | 4 | 0 | 0 |  | -0.30182 | -0.8435 | -13.6893 | -6.9693 | 3.8838 | -2.1248 | -32.7474 | 0 | 0 | 0 | 0 | 0
32 | 5 | 0 | 0 |  | -0.30182 | -0.8435 | -13.6893 | -6.9693 | 4.8838 | -1.863 | -23.7751 | 0 | 0 | 0 | 0 | 0
32 | 6 | 0 | 0 |  | -0.30182 | -0.8435 | -13.6893 | -6.9693 | 5.8838 | -1.6012 | -14.7142 | 0 | 0 | 0 | 0 | 0
32 | 7 | 0 | 0 |  | -0.30182 | -0.8435 | -13.6893 | -6.9693 | 6.8838 | -1.3394 | -5.9492 | 0 | 0 | 0 | 0 | 0
32 | 8 | 0 | 1 |  | -0.30182 | -0.8435 | -13.6893 | -6.9693 | 7.8838 | -1.0776 | 2.1581 | 0 | 0.83333 | 0.83333 | 1.323 | 0
32 | 9 | 0 | 19 |  | -0.30182 | -0.8435 | -13.6893 | -6.9693 | 8.8838 | -0.81581 | 9.2235 | 0 | 15.8333 | 15.8333 | 25.137 | 0
32 | 10 | 0 | 55 |  | -0.30182 | -0.8435 | -13.6893 | -6.9693 | 9.8838 | -0.55401 | 14.8257 | 0 | 45.8333 | 45.8333 | 72.765 | 1
32 | 11 | 0 | 85 |  | -0.30182 | -0.8435 | -13.6893 | -6.9693 | 10.8838 | -0.29221 | 18.5376 | 0 | 70.8333 | 70.8333 | 112.455 | 1
32 | 12 | 77 | 138 |  | -0.30182 | -0.8435 | -13.6893 | -6.9693 | 11.8838 | -0.03041 | 20.0108 | 58.9775 | 115 | 173.9775 | 276.2066 | 1
32 | 13 | 53 | 148 |  | -0.30182 | -0.8435 | -13.6893 | -6.9693 | 12.8838 | 0.23139 | 19.089 | 39.3721 | 123.3333 | 162.7054 | 258.3111 | 1
32 | 14 | 0 | 90 |  | -0.30182 | -0.8435 | -13.6893 | -6.9693 | 13.8838 | 0.49319 | 15.8715 | 0 | 75 | 75 | 119.07 | 1
32 | 15 | 0 | 63 |  | -0.30182 | -0.8435 | -13.6893 | -6.9693 | 14.8838 | 0.75499 | 10.6714 | 0 | 52.5 | 52.5 | 83.349 | 0
32 | 16 | 0 | 27 |  | -0.30182 | -0.8435 | -13.6893 | -6.9693 | 15.8838 | 1.0168 | 3.9073 | 0 | 22.5 | 22.5 | 35.721 | 0
32 | 17 | 0 | 3 |  | -0.30182 | -0.8435 | -13.6893 | -6.9693 | 16.8838 | 1.2786 | -3.9936 | 0 | 2.5 | 2.5 | 3.969 | 0
32 | 18 | 0 | 0 |  | -0.30182 | -0.8435 | -13.6893 | -6.9693 | 17.8838 | 1.5404 | -12.6384 | 0 | 0 | 0 | 0 | 0
32 | 19 | 0 | 0 |  | -0.30182 | -0.8435 | -13.6893 | -6.9693 | 18.8838 | 1.8022 | -21.663 | 0 | 0 | 0 | 0 | 0
32 | 20 | 0 | 0 |  | -0.30182 | -0.8435 | -13.6893 | -6.9693 | 19.8838 | 2.064 | -30.6939 | 0 | 0 | 0 | 0 | 0
32 | 21 | 0 | 0 |  | -0.30182 | -0.8435 | -13.6893 | -6.9693 | 20.8838 | 2.3258 | -39.2777 | 0 | 0 | 0 | 0 | 0
32 | 22 | 0 | 0 |  | -0.30182 | -0.8435 | -13.6893 | -6.9693 | 21.8838 | 2.5876 | -46.7753 | 0 | 0 | 0 | 0 | 0
32 | 23 | 0 | 0 |  | -0.30182 | -0.8435 | -13.6893 | -6.9693 | 22.8838 | 2.8494 | -52.2529 | 0 | 0 | 0 | 0 | 0
32 | 24 | 0 | 0 |  | -0.30182 | -0.8435 | -13.6893 | -6.9693 | 23.8838 | 3.1112 | -54.5864 | 0 | 0 | 0 | 0 | 0
33 | 1 | 0 | 0 |  | -0.29701 | -0.82628 | -13.8363 | -7.1163 | 0.88139 | -2.9108 | -52.8537 | 0 | 0 | 0 | 0 | 0
33 | 2 | 0 | 0 |  | -0.29701 | -0.82628 | -13.8363 | -7.1163 | 1.8814 | -2.649 | -48.0348 | 0 | 0 | 0 | 0 | 0
33 | 3 | 0 | 0 |  | -0.29701 | -0.82628 | -13.8363 | -7.1163 | 2.8814 | -2.3872 | -40.9344 | 0 | 0 | 0 | 0 | 0
33 | 4 | 0 | 0 |  | -0.29701 | -0.82628 | -13.8363 | -7.1163 | 3.8814 | -2.1254 | -32.5508 | 0 | 0 | 0 | 0 | 0
33 | 5 | 0 | 0 |  | -0.29701 | -0.82628 | -13.8363 | -7.1163 | 4.8814 | -1.8636 | -23.5841 | 0 | 0 | 0 | 0 | 0
33 | 6 | 0 | 0 |  | -0.29701 | -0.82628 | -13.8363 | -7.1163 | 5.8814 | -1.6018 | -14.5212 | 0 | 0 | 0 | 0 | 0
33 | 7 | 0 | 0 |  | -0.29701 | -0.82628 | -13.8363 | -7.1163 | 6.8814 | -1.34 | -5.748 | 0 | 0 | 0 | 0 | 0
33 | 8 | 0 | 3 |  | -0.29701 | -0.82628 | -13.8363 | -7.1163 | 7.8814 | -1.0782 | 2.3724 | 0 | 2.5 | 2.5 | 3.969 | 0
33 | 9 | 0 | 21 |  | -0.29701 | -0.82628 | -13.8363 | -7.1163 | 8.8814 | -0.81645 | 9.4543 | 0 | 17.5 | 17.5 | 27.783 | 0
33 | 10 | 43 | 82 |  | -0.29701 | -0.82628 | -13.8363 | -7.1163 | 9.8814 | -0.55465 | 15.0744 | 27.3981 | 68.3333 | 95.7314 | 151.9832 | 1
33 | 11 | 48 | 126 |  | -0.29701 | -0.82628 | -13.8363 | -7.1163 | 10.8814 | -0.29285 | 18.8021 | 35.1297 | 105 | 140.1297 | 222.4699 | 1
33 | 12 | 186 | 153 |  | -0.29701 | -0.82628 | -13.8363 | -7.1163 | 11.8814 | -0.031051 | 20.2858 | 143.0351 | 127.5 | 270.5351 | 429.5015 | 1
33 | 13 | 140 | 172 |  | -0.29701 | -0.82628 | -13.8363 | -7.1163 | 12.8814 | 0.23075 | 19.3669 | 104.4466 | 143.3333 | 247.7799 | 393.3754 | 1
33 | 14 | 183 | 135 |  | -0.29701 | -0.82628 | -13.8363 | -7.1163 | 13.8814 | 0.49255 | 16.1451 | 121.6137 | 112.5 | 234.1137 | 371.6789 | 1
33 | 15 | 35 | 96 |  | -0.29701 | -0.82628 | -13.8363 | -7.1163 | 14.8814 | 0.75435 | 10.9361 | 18.553 | 80 | 98.553 | 156.4628 | 0
33 | 16 | 1 | 46 |  | -0.29701 | -0.82628 | -13.8363 | -7.1163 | 15.8814 | 1.0161 | 4.1615 | 0.3518 | 38.3333 | 38.6851 | 61.4165 | 0
33 | 17 | 0 | 5 |  | -0.29701 | -0.82628 | -13.8363 | -7.1163 | 16.8814 | 1.2779 | -3.7489 | 0 | 4.1667 | 4.1667 | 6.615 | 0
33 | 18 | 0 | 0 |  | -0.29701 | -0.82628 | -13.8363 | -7.1163 | 17.8814 | 1.5397 | -12.4004 | 0 | 0 | 0 | 0 | 0
33 | 19 | 0 | 0 |  | -0.29701 | -0.82628 | -13.8363 | -7.1163 | 18.8814 | 1.8015 | -21.4276 | 0 | 0 | 0 | 0 | 0
33 | 20 | 0 | 0 |  | -0.29701 | -0.82628 | -13.8363 | -7.1163 | 19.8814 | 2.0633 | -30.4559 | 0 | 0 | 0 | 0 | 0
33 | 21 | 0 | 0 |  | -0.29701 | -0.82628 | -13.8363 | -7.1163 | 20.8814 | 2.3251 | -39.031 | 0 | 0 | 0 | 0 | 0
33 | 22 | 0 | 0 |  | -0.29701 | -0.82628 | -13.8363 | -7.1163 | 21.8814 | 2.5869 | -46.5149 | 0 | 0 | 0 | 0 | 0
33 | 23 | 0 | 0 |  | -0.29701 | -0.82628 | -13.8363 | -7.1163 | 22.8814 | 2.8487 | -51.9785 | 0 | 0 | 0 | 0 | 0
33 | 24 | 0 | 0 |  | -0.29701 | -0.82628 | -13.8363 | -7.1163 | 23.8814 | 3.1105 | -54.3097 | 0 | 0 | 0 | 0 | 0
34 | 1 | 0 | 0 |  | -0.29211 | -0.80907 | -13.9705 | -7.2505 | 0.87916 | -2.9114 | -52.588 | 0 | 0 | 0 | 0 | 0
34 | 2 | 0 | 0 |  | -0.29211 | -0.80907 | -13.9705 | -7.2505 | 1.8792 | -2.6496 | -47.7949 | 0 | 0 | 0 | 0 | 0
34 | 3 | 0 | 0 |  | -0.29211 | -0.80907 | -13.9705 | -7.2505 | 2.8792 | -2.3878 | -40.7174 | 0 | 0 | 0 | 0 | 0
34 | 4 | 0 | 0 |  | -0.29211 | -0.80907 | -13.9705 | -7.2505 | 3.8792 | -2.126 | -32.3483 | 0 | 0 | 0 | 0 | 0
34 | 5 | 0 | 0 |  | -0.29211 | -0.80907 | -13.9705 | -7.2505 | 4.8792 | -1.8642 | -23.3872 | 0 | 0 | 0 | 0 | 0
34 | 6 | 0 | 0 |  | -0.29211 | -0.80907 | -13.9705 | -7.2505 | 5.8792 | -1.6024 | -14.3224 | 0 | 0 | 0 | 0 | 0
34 | 7 | 0 | 0 |  | -0.29211 | -0.80907 | -13.9705 | -7.2505 | 6.8792 | -1.3406 | -5.5412 | 0 | 0 | 0 | 0 | 0
34 | 8 | 0 | 3 |  | -0.29211 | -0.80907 | -13.9705 | -7.2505 | 7.8792 | -1.0788 | 2.5923 | 0 | 2.5 | 2.5 | 3.969 | 0
34 | 9 | 0 | 35 |  | -0.29211 | -0.80907 | -13.9705 | -7.2505 | 8.8792 | -0.81703 | 9.6907 | 0 | 29.1667 | 29.1667 | 46.305 | 0
34 | 10 | 31 | 87 |  | -0.29211 | -0.80907 | -13.9705 | -7.2505 | 9.8792 | -0.55523 | 15.3285 | 19.8342 | 72.5 | 92.3342 | 146.5898 | 1
34 | 11 | 60 | 125 |  | -0.29211 | -0.80907 | -13.9705 | -7.2505 | 10.8792 | -0.29344 | 19.0718 | 44.0869 | 104.1667 | 148.2535 | 235.3673 | 1
34 | 12 | 49 | 154 |  | -0.29211 | -0.80907 | -13.9705 | -7.2505 | 11.8792 | -0.031636 | 20.5656 | 37.8332 | 128.3333 | 166.1666 | 263.8061 | 1
34 | 13 | 49 | 157 |  | -0.29211 | -0.80907 | -13.9705 | -7.2505 | 12.8792 | 0.23016 | 19.6491 | 36.7132 | 130.8333 | 167.5465 | 265.9968 | 1
34 | 14 | 52 | 135 |  | -0.29211 | -0.80907 | -13.9705 | -7.2505 | 13.8792 | 0.49196 | 16.4224 | 34.7236 | 112.5 | 147.2236 | 233.7323 | 1
34 | 15 | 37 | 98 |  | -0.29211 | -0.80907 | -13.9705 | -7.2505 | 14.8792 | 0.75376 | 11.2039 | 19.7285 | 81.6667 | 101.3952 | 160.975 | 0
34 | 16 | 2 | 48 |  | -0.29211 | -0.80907 | -13.9705 | -7.2505 | 15.8792 | 1.0156 | 4.4182 | 0.70948 | 40 | 40.7095 | 64.6304 | 0
34 | 17 | 0 | 6 |  | -0.29211 | -0.80907 | -13.9705 | -7.2505 | 16.8792 | 1.2774 | -3.5021 | 0 | 5 | 5 | 7.938 | 0
34 | 18 | 0 | 0 |  | -0.29211 | -0.80907 | -13.9705 | -7.2505 | 17.8792 | 1.5392 | -12.1604 | 0 | 0 | 0 | 0 | 0
34 | 19 | 0 | 0 |  | -0.29211 | -0.80907 | -13.9705 | -7.2505 | 18.8792 | 1.801 | -21.1903 | 0 | 0 | 0 | 0 | 0
34 | 20 | 0 | 0 |  | -0.29211 | -0.80907 | -13.9705 | -7.2505 | 19.8792 | 2.0628 | -30.2157 | 0 | 0 | 0 | 0 | 0
34 | 21 | 0 | 0 |  | -0.29211 | -0.80907 | -13.9705 | -7.2505 | 20.8792 | 2.3246 | -38.7819 | 0 | 0 | 0 | 0 | 0
34 | 22 | 0 | 0 |  | -0.29211 | -0.80907 | -13.9705 | -7.2505 | 21.8792 | 2.5864 | -46.2514 | 0 | 0 | 0 | 0 | 0
34 | 23 | 0 | 0 |  | -0.29211 | -0.80907 | -13.9705 | -7.2505 | 22.8792 | 2.8482 | -51.7004 | 0 | 0 | 0 | 0 | 0
34 | 24 | 0 | 0 |  | -0.29211 | -0.80907 | -13.9705 | -7.2505 | 23.8792 | 3.11 | -54.0283 | 0 | 0 | 0 | 0 | 0
35 | 1 | 0 | 0 |  | -0.28713 | -0.79185 | -14.0917 | -7.3717 | 0.87714 | -2.912 | -52.3168 | 0 | 0 | 0 | 0 | 0
35 | 2 | 0 | 0 |  | -0.28713 | -0.79185 | -14.0917 | -7.3717 | 1.8771 | -2.6502 | -47.5491 | 0 | 0 | 0 | 0 | 0
35 | 3 | 0 | 0 |  | -0.28713 | -0.79185 | -14.0917 | -7.3717 | 2.8771 | -2.3884 | -40.4944 | 0 | 0 | 0 | 0 | 0
35 | 4 | 0 | 0 |  | -0.28713 | -0.79185 | -14.0917 | -7.3717 | 3.8771 | -2.1266 | -32.1398 | 0 | 0 | 0 | 0 | 0
35 | 5 | 0 | 0 |  | -0.28713 | -0.79185 | -14.0917 | -7.3717 | 4.8771 | -1.8648 | -23.1845 | 0 | 0 | 0 | 0 | 0
35 | 6 | 0 | 0 |  | -0.28713 | -0.79185 | -14.0917 | -7.3717 | 5.8771 | -1.603 | -14.118 | 0 | 0 | 0 | 0 | 0
35 | 7 | 0 | 0 |  | -0.28713 | -0.79185 | -14.0917 | -7.3717 | 6.8771 | -1.3412 | -5.3288 | 0 | 0 | 0 | 0 | 0
35 | 8 | 0 | 2 |  | -0.28713 | -0.79185 | -14.0917 | -7.3717 | 7.8771 | -1.0794 | 2.8177 | 0 | 1.6667 | 1.6667 | 2.646 | 0
35 | 9 | 0 | 37 |  | -0.28713 | -0.79185 | -14.0917 | -7.3717 | 8.8771 | -0.81756 | 9.9326 | 0 | 30.8333 | 30.8333 | 48.951 | 0
35 | 10 | 31 | 89 |  | -0.28713 | -0.79185 | -14.0917 | -7.3717 | 9.8771 | -0.55576 | 15.5879 | 19.9181 | 74.1667 | 94.0848 | 149.369 | 1
35 | 11 | 171 | 135 |  | -0.28713 | -0.79185 | -14.0917 | -7.3717 | 10.8771 | -0.29396 | 19.3466 | 126.1536 | 112.5 | 238.6536 | 378.8864 | 1
35 | 12 | 550 | 119 |  | -0.28713 | -0.79185 | -14.0917 | -7.3717 | 11.8771 | -0.032165 | 20.8501 | 426.3833 | 99.1667 | 525.55 | 834.3632 | 1
35 | 13 | 705 | 67 |  | -0.28713 | -0.79185 | -14.0917 | -7.3717 | 12.8771 | 0.22963 | 19.9355 | 530.4923 | 55.8333 | 586.3256 | 930.8505 | 1
35 | 14 | 620 | 78 |  | -0.28713 | -0.79185 | -14.0917 | -7.3717 | 13.8771 | 0.49143 | 16.7033 | 416.0069 | 65 | 481.0069 | 763.6465 | 1
35 | 15 | 529 | 62 |  | -0.28713 | -0.79185 | -14.0917 | -7.3717 | 14.8771 | 0.75323 | 11.4746 | 283.7125 | 51.6667 | 335.3792 | 532.448 | 0
35 | 16 | 235 | 49 |  | -0.28713 | -0.79185 | -14.0917 | -7.3717 | 15.8771 | 1.015 | 4.6774 | 84.0518 | 40.8333 | 124.8852 | 198.2677 | 0
35 | 17 | 0 | 10 |  | -0.28713 | -0.79185 | -14.0917 | -7.3717 | 16.8771 | 1.2768 | -3.2531 | 0 | 8.3333 | 8.3333 | 13.23 | 0
35 | 18 | 0 | 0 |  | -0.28713 | -0.79185 | -14.0917 | -7.3717 | 17.8771 | 1.5386 | -11.9186 | 0 | 0 | 0 | 0 | 0
35 | 19 | 0 | 0 |  | -0.28713 | -0.79185 | -14.0917 | -7.3717 | 18.8771 | 1.8004 | -20.951 | 0 | 0 | 0 | 0 | 0
35 | 20 | 0 | 0 |  | -0.28713 | -0.79185 | -14.0917 | -7.3717 | 19.8771 | 2.0622 | -29.9735 | 0 | 0 | 0 | 0 | 0
35 | 21 | 0 | 0 |  | -0.28713 | -0.79185 | -14.0917 | -7.3717 | 20.8771 | 2.324 | -38.5304 | 0 | 0 | 0 | 0 | 0
35 | 22 | 0 | 0 |  | -0.28713 | -0.79185 | -14.0917 | -7.3717 | 21.8771 | 2.5858 | -45.9849 | 0 | 0 | 0 | 0 | 0
35 | 23 | 0 | 0 |  | -0.28713 | -0.79185 | -14.0917 | -7.3717 | 22.8771 | 2.8476 | -51.4186 | 0 | 0 | 0 | 0 | 0
35 | 24 | 0 | 0 |  | -0.28713 | -0.79185 | -14.0917 | -7.3717 | 23.8771 | 3.1094 | -53.7423 | 0 | 0 | 0 | 0 | 0
36 | 1 | 0 | 0 |  | -0.28207 | -0.77464 | -14.2 | -7.48 | 0.87533 | -2.9124 | -52.0403 | 0 | 0 | 0 | 0 | 0
36 | 2 | 0 | 0 |  | -0.28207 | -0.77464 | -14.2 | -7.48 | 1.8753 | -2.6506 | -47.2975 | 0 | 0 | 0 | 0 | 0
36 | 3 | 0 | 0 |  | -0.28207 | -0.77464 | -14.2 | -7.48 | 2.8753 | -2.3888 | -40.2655 | 0 | 0 | 0 | 0 | 0
36 | 4 | 0 | 0 |  | -0.28207 | -0.77464 | -14.2 | -7.48 | 3.8753 | -2.127 | -31.9254 | 0 | 0 | 0 | 0 | 0
36 | 5 | 0 | 0 |  | -0.28207 | -0.77464 | -14.2 | -7.48 | 4.8753 | -1.8652 | -22.976 | 0 | 0 | 0 | 0 | 0
36 | 6 | 0 | 0 |  | -0.28207 | -0.77464 | -14.2 | -7.48 | 5.8753 | -1.6034 | -13.9079 | 0 | 0 | 0 | 0 | 0
36 | 7 | 0 | 0 |  | -0.28207 | -0.77464 | -14.2 | -7.48 | 6.8753 | -1.3416 | -5.1108 | 0 | 0 | 0 | 0 | 0
36 | 8 | 0 | 3 |  | -0.28207 | -0.77464 | -14.2 | -7.48 | 7.8753 | -1.0798 | 3.0486 | 0 | 2.5 | 2.5 | 3.969 | 0
36 | 9 | 0 | 38 |  | -0.28207 | -0.77464 | -14.2 | -7.48 | 8.8753 | -0.81804 | 10.1798 | 0 | 31.6667 | 31.6667 | 50.274 | 0
36 | 10 | 31 | 91 |  | -0.28207 | -0.77464 | -14.2 | -7.48 | 9.8753 | -0.55624 | 15.8526 | 20.0038 | 75.8333 | 95.8372 | 152.1511 | 1
36 | 11 | 49 | 133 |  | -0.28207 | -0.77464 | -14.2 | -7.48 | 10.8753 | -0.29444 | 19.6265 | 36.2965 | 110.8333 | 147.1298 | 233.5833 | 1
36 | 12 | 210 | 152 |  | -0.28207 | -0.77464 | -14.2 | -7.48 | 11.8753 | -0.032638 | 21.1393 | 163.4661 | 126.6667 | 290.1328 | 460.6148 | 1
36 | 13 | 75 | 152 |  | -0.28207 | -0.77464 | -14.2 | -7.48 | 12.8753 | 0.22916 | 20.226 | 56.6786 | 126.6667 | 183.3452 | 291.0789 | 1
36 | 14 | 51 | 140 |  | -0.28207 | -0.77464 | -14.2 | -7.48 | 13.8753 | 0.49096 | 16.9876 | 34.3844 | 116.6667 | 151.051 | 239.8086 | 1
36 | 15 | 37 | 102 |  | -0.28207 | -0.77464 | -14.2 | -7.48 | 14.8753 | 0.75276 | 11.7481 | 19.959 | 85 | 104.959 | 166.6329 | 0
36 | 16 | 3 | 52 |  | -0.28207 | -0.77464 | -14.2 | -7.48 | 15.8753 | 1.0146 | 4.939 | 1.0818 | 43.3333 | 44.4151 | 70.5134 | 0
36 | 17 | 0 | 8 |  | -0.28207 | -0.77464 | -14.2 | -7.48 | 16.8753 | 1.2764 | -3.0022 | 0 | 6.6667 | 6.6667 | 10.584 | 0
36 | 18 | 0 | 0 |  | -0.28207 | -0.77464 | -14.2 | -7.48 | 17.8753 | 1.5382 | -11.6749 | 0 | 0 | 0 | 0 | 0
36 | 19 | 0 | 0 |  | -0.28207 | -0.77464 | -14.2 | -7.48 | 18.8753 | 1.8 | -20.71 | 0 | 0 | 0 | 0 | 0
36 | 20 | 0 | 0 |  | -0.28207 | -0.77464 | -14.2 | -7.48 | 19.8753 | 2.0618 | -29.7293 | 0 | 0 | 0 | 0 | 0
36 | 21 | 0 | 0 |  | -0.28207 | -0.77464 | -14.2 | -7.48 | 20.8753 | 2.3236 | -38.2765 | 0 | 0 | 0 | 0 | 0
36 | 22 | 0 | 0 |  | -0.28207 | -0.77464 | -14.2 | -7.48 | 21.8753 | 2.5854 | -45.7156 | 0 | 0 | 0 | 0 | 0
36 | 23 | 0 | 0 |  | -0.28207 | -0.77464 | -14.2 | -7.48 | 22.8753 | 2.8472 | -51.1332 | 0 | 0 | 0 | 0 | 0
36 | 24 | 0 | 0 |  | -0.28207 | -0.77464 | -14.2 | -7.48 | 23.8753 | 3.109 | -53.4518 | 0 | 0 | 0 | 0 | 0
37 | 1 | 0 | 0 |  | -0.27694 | -0.75743 | -14.2953 | -7.5753 | 0.87374 | -2.9128 | -51.7585 | 0 | 0 | 0 | 0 | 0
37 | 2 | 0 | 0 |  | -0.27694 | -0.75743 | -14.2953 | -7.5753 | 1.8737 | -2.651 | -47.0401 | 0 | 0 | 0 | 0 | 0
37 | 3 | 0 | 0 |  | -0.27694 | -0.75743 | -14.2953 | -7.5753 | 2.8737 | -2.3892 | -40.0306 | 0 | 0 | 0 | 0 | 0
37 | 4 | 0 | 0 |  | -0.27694 | -0.75743 | -14.2953 | -7.5753 | 3.8737 | -2.1274 | -31.7051 | 0 | 0 | 0 | 0 | 0
37 | 5 | 0 | 0 |  | -0.27694 | -0.75743 | -14.2953 | -7.5753 | 4.8737 | -1.8656 | -22.7618 | 0 | 0 | 0 | 0 | 0
37 | 6 | 0 | 0 |  | -0.27694 | -0.75743 | -14.2953 | -7.5753 | 5.8737 | -1.6038 | -13.6922 | 0 | 0 | 0 | 0 | 0
37 | 7 | 0 | 0 |  | -0.27694 | -0.75743 | -14.2953 | -7.5753 | 6.8737 | -1.3421 | -4.8874 | 0 | 0 | 0 | 0 | 0
37 | 8 | 0 | 6 |  | -0.27694 | -0.75743 | -14.2953 | -7.5753 | 7.8737 | -1.0803 | 3.2848 | 0 | 5 | 5 | 7.938 | 0
37 | 9 | 227 | 44 |  | -0.27694 | -0.75743 | -14.2953 | -7.5753 | 8.8737 | -0.81845 | 10.4323 | 113.7413 | 36.6667 | 150.408 | 238.7877 | 0
37 | 10 | 524 | 57 |  | -0.27694 | -0.75743 | -14.2953 | -7.5753 | 9.8737 | -0.55665 | 16.1224 | 339.6062 | 47.5 | 387.1062 | 614.5698 | 1
37 | 11 | 492 | 91 |  | -0.27694 | -0.75743 | -14.2953 | -7.5753 | 10.8737 | -0.29485 | 19.9113 | 365.9458 | 75.8333 | 441.7791 | 701.3685 | 1
37 | 12 | 211 | 154 |  | -0.27694 | -0.75743 | -14.2953 | -7.5753 | 11.8737 | -0.033054 | 21.433 | 164.9193 | 128.3333 | 293.2527 | 465.568 | 1
37 | 13 | 75 | 155 |  | -0.27694 | -0.75743 | -14.2953 | -7.5753 | 12.8737 | 0.22875 | 20.5204 | 56.9231 | 129.1667 | 186.0898 | 295.4361 | 1
37 | 14 | 51 | 142 |  | -0.27694 | -0.75743 | -14.2953 | -7.5753 | 13.8737 | 0.49055 | 17.2753 | 34.5491 | 118.3333 | 152.8825 | 242.7162 | 1
37 | 15 | 38 | 104 |  | -0.27694 | -0.75743 | -14.2953 | -7.5753 | 14.8737 | 0.75234 | 12.0244 | 20.6166 | 86.6667 | 107.2833 | 170.3229 | 0
37 | 16 | 4 | 54 |  | -0.27694 | -0.75743 | -14.2953 | -7.5753 | 15.8737 | 1.0141 | 5.2027 | 1.454 | 45 | 46.454 | 73.7503 | 0
37 | 17 | 0 | 8 |  | -0.27694 | -0.75743 | -14.2953 | -7.5753 | 16.8737 | 1.2759 | -2.7493 | 0 | 6.6667 | 6.6667 | 10.584 | 0
37 | 18 | 0 | 0 |  | -0.27694 | -0.75743 | -14.2953 | -7.5753 | 17.8737 | 1.5377 | -11.4295 | 0 | 0 | 0 | 0 | 0
37 | 19 | 0 | 0 |  | -0.27694 | -0.75743 | -14.2953 | -7.5753 | 18.8737 | 1.7995 | -20.4671 | 0 | 0 | 0 | 0 | 0
37 | 20 | 0 | 0 |  | -0.27694 | -0.75743 | -14.2953 | -7.5753 | 19.8737 | 2.0613 | -29.4831 | 0 | 0 | 0 | 0 | 0
37 | 21 | 0 | 0 |  | -0.27694 | -0.75743 | -14.2953 | -7.5753 | 20.8737 | 2.3231 | -38.0204 | 0 | 0 | 0 | 0 | 0
37 | 22 | 0 | 0 |  | -0.27694 | -0.75743 | -14.2953 | -7.5753 | 21.8737 | 2.5849 | -45.4434 | 0 | 0 | 0 | 0 | 0
37 | 23 | 0 | 0 |  | -0.27694 | -0.75743 | -14.2953 | -7.5753 | 22.8737 | 2.8467 | -50.8443 | 0 | 0 | 0 | 0 | 0
37 | 24 | 0 | 0 |  | -0.27694 | -0.75743 | -14.2953 | -7.5753 | 23.8737 | 3.1085 | -53.1569 | 0 | 0 | 0 | 0 | 0
38 | 1 | 0 | 0 |  | -0.27173 | -0.74021 | -14.3777 | -7.6577 | 0.87237 | -2.9132 | -51.4716 | 0 | 0 | 0 | 0 | 0
38 | 2 | 0 | 0 |  | -0.27173 | -0.74021 | -14.3777 | -7.6577 | 1.8724 | -2.6514 | -46.777 | 0 | 0 | 0 | 0 | 0
38 | 3 | 0 | 0 |  | -0.27173 | -0.74021 | -14.3777 | -7.6577 | 2.8724 | -2.3896 | -39.7899 | 0 | 0 | 0 | 0 | 0
38 | 4 | 0 | 0 |  | -0.27173 | -0.74021 | -14.3777 | -7.6577 | 3.8724 | -2.1278 | -31.4791 | 0 | 0 | 0 | 0 | 0
38 | 5 | 0 | 0 |  | -0.27173 | -0.74021 | -14.3777 | -7.6577 | 4.8724 | -1.866 | -22.542 | 0 | 0 | 0 | 0 | 0
38 | 6 | 0 | 0 |  | -0.27173 | -0.74021 | -14.3777 | -7.6577 | 5.8724 | -1.6042 | -13.471 | 0 | 0 | 0 | 0 | 0
38 | 7 | 0 | 0 |  | -0.27173 | -0.74021 | -14.3777 | -7.6577 | 6.8724 | -1.3424 | -4.6585 | 0 | 0 | 0 | 0 | 0
38 | 8 | 0 | 4 |  | -0.27173 | -0.74021 | -14.3777 | -7.6577 | 7.8724 | -1.0806 | 3.5264 | 0 | 3.3333 | 3.3333 | 5.292 | 0
38 | 9 | 0 | 43 |  | -0.27173 | -0.74021 | -14.3777 | -7.6577 | 8.8724 | -0.81881 | 10.69 | 0 | 35.8333 | 35.8333 | 56.889 | 0
38 | 10 | 49 | 92 |  | -0.27173 | -0.74021 | -14.3777 | -7.6577 | 9.8724 | -0.55701 | 16.3973 | 31.8978 | 76.6667 | 108.5645 | 172.357 | 1
38 | 11 | 52 | 138 |  | -0.27173 | -0.74021 | -14.3777 | -7.6577 | 10.8724 | -0.29521 | 20.2009 | 38.8378 | 115 | 153.8378 | 244.2329 | 1
38 | 12 | 50 | 165 |  | -0.27173 | -0.74021 | -14.3777 | -7.6577 | 11.8724 | -0.033413 | 21.7312 | 39.2417 | 137.5 | 176.7417 | 280.5952 | 1
38 | 13 | 50 | 167 |  | -0.27173 | -0.74021 | -14.3777 | -7.6577 | 12.8724 | 0.22839 | 20.8188 | 38.1125 | 139.1667 | 177.2792 | 281.4485 | 1
38 | 14 | 0 | 102 |  | -0.27173 | -0.74021 | -14.3777 | -7.6577 | 13.8724 | 0.49019 | 17.5662 | 0 | 85 | 85 | 134.946 | 1
38 | 15 | 0 | 73 |  | -0.27173 | -0.74021 | -14.3777 | -7.6577 | 14.8724 | 0.75199 | 12.3034 | 0 | 60.8333 | 60.8333 | 96.579 | 0
38 | 16 | 0 | 36 |  | -0.27173 | -0.74021 | -14.3777 | -7.6577 | 15.8724 | 1.0138 | 5.4686 | 0 | 30 | 30 | 47.628 | 0
38 | 17 | 0 | 6 |  | -0.27173 | -0.74021 | -14.3777 | -7.6577 | 16.8724 | 1.2756 | -2.4947 | 0 | 5 | 5 | 7.938 | 0
38 | 18 | 0 | 0 |  | -0.27173 | -0.74021 | -14.3777 | -7.6577 | 17.8724 | 1.5374 | -11.1824 | 0 | 0 | 0 | 0 | 0
38 | 19 | 0 | 0 |  | -0.27173 | -0.74021 | -14.3777 | -7.6577 | 18.8724 | 1.7992 | -20.2227 | 0 | 0 | 0 | 0 | 0
38 | 20 | 0 | 0 |  | -0.27173 | -0.74021 | -14.3777 | -7.6577 | 19.8724 | 2.061 | -29.2351 | 0 | 0 | 0 | 0 | 0
38 | 21 | 0 | 0 |  | -0.27173 | -0.74021 | -14.3777 | -7.6577 | 20.8724 | 2.3228 | -37.762 | 0 | 0 | 0 | 0 | 0
38 | 22 | 0 | 0 |  | -0.27173 | -0.74021 | -14.3777 | -7.6577 | 21.8724 | 2.5846 | -45.1685 | 0 | 0 | 0 | 0 | 0
38 | 23 | 0 | 0 |  | -0.27173 | -0.74021 | -14.3777 | -7.6577 | 22.8724 | 2.8464 | -50.5519 | 0 | 0 | 0 | 0 | 0
38 | 24 | 0 | 0 |  | -0.27173 | -0.74021 | -14.3777 | -7.6577 | 23.8724 | 3.1082 | -52.8578 | 0 | 0 | 0 | 0 | 0
39 | 1 | 0 | 0 |  | -0.26644 | -0.723 | -14.447 | -7.727 | 0.87122 | -2.9135 | -51.1797 | 0 | 0 | 0 | 0 | 0
39 | 2 | 0 | 0 |  | -0.26644 | -0.723 | -14.447 | -7.727 | 1.8712 | -2.6517 | -46.5084 | 0 | 0 | 0 | 0 | 0
39 | 3 | 0 | 0 |  | -0.26644 | -0.723 | -14.447 | -7.727 | 2.8712 | -2.3899 | -39.5435 | 0 | 0 | 0 | 0 | 0
39 | 4 | 0 | 0 |  | -0.26644 | -0.723 | -14.447 | -7.727 | 3.8712 | -2.1281 | -31.2474 | 0 | 0 | 0 | 0 | 0
39 | 5 | 0 | 0 |  | -0.26644 | -0.723 | -14.447 | -7.727 | 4.8712 | -1.8663 | -22.3166 | 0 | 0 | 0 | 0 | 0
39 | 6 | 0 | 0 |  | -0.26644 | -0.723 | -14.447 | -7.727 | 5.8712 | -1.6045 | -13.2444 | 0 | 0 | 0 | 0 | 0
39 | 7 | 0 | 0 |  | -0.26644 | -0.723 | -14.447 | -7.727 | 6.8712 | -1.3427 | -4.4244 | 0 | 0 | 0 | 0 | 0
39 | 8 | 0 | 7 |  | -0.26644 | -0.723 | -14.447 | -7.727 | 7.8712 | -1.0809 | 3.7732 | 0 | 5.8333 | 5.8333 | 9.261 | 0
39 | 9 | 2 | 45 |  | -0.26644 | -0.723 | -14.447 | -7.727 | 8.8712 | -0.81911 | 10.9529 | 1.0126 | 37.5 | 38.5126 | 61.1426 | 0
39 | 10 | 323 | 97 |  | -0.26644 | -0.723 | -14.447 | -7.727 | 9.8712 | -0.55731 | 16.6773 | 211.2096 | 80.8333 | 292.043 | 463.6474 | 1
39 | 11 | 506 | 94 |  | -0.26644 | -0.723 | -14.447 | -7.727 | 10.8712 | -0.29551 | 20.4953 | 379.5045 | 78.3333 | 457.8378 | 726.8633 | 1
39 | 12 | 665 | 86 |  | -0.26644 | -0.723 | -14.447 | -7.727 | 11.8712 | -0.033715 | 22.0337 | 524.0781 | 71.6667 | 595.7448 | 945.8044 | 1
39 | 13 | 391 | 138 |  | -0.26644 | -0.723 | -14.447 | -7.727 | 12.8712 | 0.22808 | 21.1209 | 299.3263 | 115 | 414.3263 | 657.7845 | 1
39 | 14 | 63 | 146 |  | -0.26644 | -0.723 | -14.447 | -7.727 | 13.8712 | 0.48988 | 17.8602 | 43.086 | 121.6667 | 164.7527 | 261.5613 | 1
39 | 15 | 51 | 108 |  | -0.26644 | -0.723 | -14.447 | -7.727 | 14.8712 | 0.75168 | 12.5848 | 27.9859 | 90 | 117.9859 | 187.3144 | 1
39 | 16 | 0 | 38 |  | -0.26644 | -0.723 | -14.447 | -7.727 | 15.8712 | 1.0135 | 5.7366 | 0 | 31.6667 | 31.6667 | 50.274 | 0
39 | 17 | 0 | 6 |  | -0.26644 | -0.723 | -14.447 | -7.727 | 16.8712 | 1.2753 | -2.2383 | 0 | 5 | 5 | 7.938 | 0
39 | 18 | 0 | 0 |  | -0.26644 | -0.723 | -14.447 | -7.727 | 17.8712 | 1.5371 | -10.9338 | 0 | 0 | 0 | 0 | 0
39 | 19 | 0 | 0 |  | -0.26644 | -0.723 | -14.447 | -7.727 | 18.8712 | 1.7989 | -19.9766 | 0 | 0 | 0 | 0 | 0
39 | 20 | 0 | 0 |  | -0.26644 | -0.723 | -14.447 | -7.727 | 19.8712 | 2.0607 | -28.9854 | 0 | 0 | 0 | 0 | 0
39 | 21 | 0 | 0 |  | -0.26644 | -0.723 | -14.447 | -7.727 | 20.8712 | 2.3225 | -37.5015 | 0 | 0 | 0 | 0 | 0
39 | 22 | 0 | 0 |  | -0.26644 | -0.723 | -14.447 | -7.727 | 21.8712 | 2.5843 | -44.891 | 0 | 0 | 0 | 0 | 0
39 | 23 | 0 | 0 |  | -0.26644 | -0.723 | -14.447 | -7.727 | 22.8712 | 2.8461 | -50.2562 | 0 | 0 | 0 | 0 | 0
39 | 24 | 0 | 0 |  | -0.26644 | -0.723 | -14.447 | -7.727 | 23.8712 | 3.1079 | -52.5544 | 0 | 0 | 0 | 0 | 0
40 | 1 | 0 | 0 |  | -0.26108 | -0.70578 | -14.5033 | -7.7833 | 0.87028 | -2.9138 | -50.8829 | 0 | 0 | 0 | 0 | 0
40 | 2 | 0 | 0 |  | -0.26108 | -0.70578 | -14.5033 | -7.7833 | 1.8703 | -2.652 | -46.2343 | 0 | 0 | 0 | 0 | 0
40 | 3 | 0 | 0 |  | -0.26108 | -0.70578 | -14.5033 | -7.7833 | 2.8703 | -2.3902 | -39.2915 | 0 | 0 | 0 | 0 | 0
40 | 4 | 0 | 0 |  | -0.26108 | -0.70578 | -14.5033 | -7.7833 | 3.8703 | -2.1284 | -31.0101 | 0 | 0 | 0 | 0 | 0
40 | 5 | 0 | 0 |  | -0.26108 | -0.70578 | -14.5033 | -7.7833 | 4.8703 | -1.8666 | -22.0857 | 0 | 0 | 0 | 0 | 0
40 | 6 | 0 | 0 |  | -0.26108 | -0.70578 | -14.5033 | -7.7833 | 5.8703 | -1.6048 | -13.0124 | 0 | 0 | 0 | 0 | 0
40 | 7 | 0 | 0 |  | -0.26108 | -0.70578 | -14.5033 | -7.7833 | 6.8703 | -1.343 | -4.1849 | 0 | 0 | 0 | 0 | 0
40 | 8 | 0 | 5 |  | -0.26108 | -0.70578 | -14.5033 | -7.7833 | 7.8703 | -1.0812 | 4.0251 | 0 | 4.1667 | 4.1667 | 6.615 | 0
40 | 9 | 2 | 46 |  | -0.26108 | -0.70578 | -14.5033 | -7.7833 | 8.8703 | -0.81936 | 11.2209 | 1.0181 | 38.3333 | 39.3514 | 62.4743 | 0
40 | 10 | 51 | 96 |  | -0.26108 | -0.70578 | -14.5033 | -7.7833 | 9.8703 | -0.55756 | 16.9621 | 33.5006 | 80 | 113.5006 | 180.1935 | 1
40 | 11 | 51 | 142 |  | -0.26108 | -0.70578 | -14.5033 | -7.7833 | 10.8703 | -0.29576 | 20.7944 | 38.4119 | 118.3333 | 156.7452 | 248.8487 | 1
40 | 12 | 0 | 118 |  | -0.26108 | -0.70578 | -14.5033 | -7.7833 | 11.8703 | -0.033961 | 22.3405 | 0 | 98.3333 | 98.3333 | 156.114 | 1
40 | 13 | 0 | 120 |  | -0.26108 | -0.70578 | -14.5033 | -7.7833 | 12.8703 | 0.22784 | 21.4267 | 0 | 100 | 100 | 158.76 | 1
40 | 14 | 0 | 105 |  | -0.26108 | -0.70578 | -14.5033 | -7.7833 | 13.8703 | 0.48964 | 18.1573 | 0 | 87.5 | 87.5 | 138.915 | 1
40 | 15 | 183 | 108 |  | -0.26108 | -0.70578 | -14.5033 | -7.7833 | 14.8703 | 0.75144 | 12.8687 | 100.985 | 90 | 190.985 | 303.2077 | 1
40 | 16 | 55 | 71 |  | -0.26108 | -0.70578 | -14.5033 | -7.7833 | 15.8703 | 1.0132 | 6.0065 | 20.4672 | 59.1667 | 79.6339 | 126.4267 | 0
40 | 17 | 0 | 17 |  | -0.26108 | -0.70578 | -14.5033 | -7.7833 | 16.8703 | 1.275 | -1.9803 | 0 | 14.1667 | 14.1667 | 22.491 | 0
40 | 18 | 0 | 0 |  | -0.26108 | -0.70578 | -14.5033 | -7.7833 | 17.8703 | 1.5368 | -10.6836 | 0 | 0 | 0 | 0 | 0
40 | 19 | 0 | 0 |  | -0.26108 | -0.70578 | -14.5033 | -7.7833 | 18.8703 | 1.7986 | -19.729 | 0 | 0 | 0 | 0 | 0
40 | 20 | 0 | 0 |  | -0.26108 | -0.70578 | -14.5033 | -7.7833 | 19.8703 | 2.0604 | -28.7339 | 0 | 0 | 0 | 0 | 0
40 | 21 | 0 | 0 |  | -0.26108 | -0.70578 | -14.5033 | -7.7833 | 20.8703 | 2.3222 | -37.2389 | 0 | 0 | 0 | 0 | 0
40 | 22 | 0 | 0 |  | -0.26108 | -0.70578 | -14.5033 | -7.7833 | 21.8703 | 2.584 | -44.6108 | 0 | 0 | 0 | 0 | 0
40 | 23 | 0 | 0 |  | -0.26108 | -0.70578 | -14.5033 | -7.7833 | 22.8703 | 2.8458 | -49.9572 | 0 | 0 | 0 | 0 | 0
40 | 24 | 0 | 0 |  | -0.26108 | -0.70578 | -14.5033 | -7.7833 | 23.8703 | 3.1076 | -52.247 | 0 | 0 | 0 | 0 | 0
41 | 1 | 0 | 0 |  | -0.25564 | -0.68857 | -14.5467 | -7.8267 | 0.86956 | -2.9139 | -50.5813 | 0 | 0 | 0 | 0 | 0
41 | 2 | 0 | 0 |  | -0.25564 | -0.68857 | -14.5467 | -7.8267 | 1.8696 | -2.6521 | -45.9549 | 0 | 0 | 0 | 0 | 0
41 | 3 | 0 | 0 |  | -0.25564 | -0.68857 | -14.5467 | -7.8267 | 2.8696 | -2.3903 | -39.0339 | 0 | 0 | 0 | 0 | 0
41 | 4 | 0 | 0 |  | -0.25564 | -0.68857 | -14.5467 | -7.8267 | 3.8696 | -2.1285 | -30.7673 | 0 | 0 | 0 | 0 | 0
41 | 5 | 0 | 0 |  | -0.25564 | -0.68857 | -14.5467 | -7.8267 | 4.8696 | -1.8667 | -21.8494 | 0 | 0 | 0 | 0 | 0
41 | 6 | 0 | 0 |  | -0.25564 | -0.68857 | -14.5467 | -7.8267 | 5.8696 | -1.6049 | -12.7751 | 0 | 0 | 0 | 0 | 0
41 | 7 | 0 | 0 |  | -0.25564 | -0.68857 | -14.5467 | -7.8267 | 6.8696 | -1.3431 | -3.9403 | 0 | 0 | 0 | 0 | 0
41 | 8 | 0 | 6 |  | -0.25564 | -0.68857 | -14.5467 | -7.8267 | 7.8696 | -1.0813 | 4.2822 | 0 | 5 | 5 | 7.938 | 0
41 | 9 | 8 | 48 |  | -0.25564 | -0.68857 | -14.5467 | -7.8267 | 8.8696 | -0.81955 | 11.4938 | 4.0944 | 40 | 44.0944 | 70.0043 | 0
41 | 10 | 54 | 98 |  | -0.25564 | -0.68857 | -14.5467 | -7.8267 | 9.8696 | -0.55775 | 17.2518 | 35.6344 | 81.6667 | 117.3011 | 186.2271 | 1
41 | 11 | 53 | 145 |  | -0.25564 | -0.68857 | -14.5467 | -7.8267 | 10.8696 | -0.29595 | 21.098 | 40.0879 | 120.8333 | 160.9212 | 255.4785 | 1
41 | 12 | 218 | 164 |  | -0.25564 | -0.68857 | -14.5467 | -7.8267 | 11.8696 | -0.03415 | 22.6514 | 173.2366 | 136.6667 | 309.9033 | 492.0024 | 1
41 | 13 | 79 | 165 |  | -0.25564 | -0.68857 | -14.5467 | -7.8267 | 12.8696 | 0.22765 | 21.7361 | 61 | 137.5 | 198.5 | 315.1386 | 1
41 | 14 | 47 | 156 |  | -0.25564 | -0.68857 | -14.5467 | -7.8267 | 13.8696 | 0.48945 | 18.4573 | 32.4477 | 130 | 162.4477 | 257.9019 | 1
41 | 15 | 42 | 115 |  | -0.25564 | -0.68857 | -14.5467 | -7.8267 | 14.8696 | 0.75125 | 13.1549 | 23.3061 | 95.8333 | 119.1394 | 189.1457 | 1
41 | 16 | 7 | 64 |  | -0.25564 | -0.68857 | -14.5467 | -7.8267 | 15.8696 | 1.013 | 6.2783 | 2.6248 | 53.3333 | 55.9582 | 88.8392 | 0
41 | 17 | 0 | 16 |  | -0.25564 | -0.68857 | -14.5467 | -7.8267 | 16.8696 | 1.2748 | -1.7207 | 0 | 13.3333 | 13.3333 | 21.168 | 0
41 | 18 | 0 | 0 |  | -0.25564 | -0.68857 | -14.5467 | -7.8267 | 17.8696 | 1.5366 | -10.4321 | 0 | 0 | 0 | 0 | 0
41 | 19 | 0 | 0 |  | -0.25564 | -0.68857 | -14.5467 | -7.8267 | 18.8696 | 1.7984 | -19.48 | 0 | 0 | 0 | 0 | 0
41 | 20 | 0 | 0 |  | -0.25564 | -0.68857 | -14.5467 | -7.8267 | 19.8696 | 2.0602 | -28.4807 | 0 | 0 | 0 | 0 | 0
41 | 21 | 0 | 0 |  | -0.25564 | -0.68857 | -14.5467 | -7.8267 | 20.8696 | 2.322 | -36.9743 | 0 | 0 | 0 | 0 | 0
41 | 22 | 0 | 0 |  | -0.25564 | -0.68857 | -14.5467 | -7.8267 | 21.8696 | 2.5838 | -44.3281 | 0 | 0 | 0 | 0 | 0
41 | 23 | 0 | 0 |  | -0.25564 | -0.68857 | -14.5467 | -7.8267 | 22.8696 | 2.8456 | -49.655 | 0 | 0 | 0 | 0 | 0
41 | 24 | 0 | 0 |  | -0.25564 | -0.68857 | -14.5467 | -7.8267 | 23.8696 | 3.1074 | -51.9356 | 0 | 0 | 0 | 0 | 0
42 | 1 | 0 | 0 |  | -0.25014 | -0.67135 | -14.5771 | -7.8571 | 0.86905 | -2.9141 | -50.275 | 0 | 0 | 0 | 0 | 0
42 | 2 | 0 | 0 |  | -0.25014 | -0.67135 | -14.5771 | -7.8571 | 1.869 | -2.6523 | -45.6703 | 0 | 0 | 0 | 0 | 0
42 | 3 | 0 | 0 |  | -0.25014 | -0.67135 | -14.5771 | -7.8571 | 2.869 | -2.3905 | -38.7708 | 0 | 0 | 0 | 0 | 0
42 | 4 | 0 | 0 |  | -0.25014 | -0.67135 | -14.5771 | -7.8571 | 3.869 | -2.1287 | -30.519 | 0 | 0 | 0 | 0 | 0
42 | 5 | 0 | 0 |  | -0.25014 | -0.67135 | -14.5771 | -7.8571 | 4.869 | -1.8669 | -21.6077 | 0 | 0 | 0 | 0 | 0
42 | 6 | 0 | 0 |  | -0.25014 | -0.67135 | -14.5771 | -7.8571 | 5.869 | -1.6051 | -12.5326 | 0 | 0 | 0 | 0 | 0
42 | 7 | 0 | 0 |  | -0.25014 | -0.67135 | -14.5771 | -7.8571 | 6.869 | -1.3433 | -3.6906 | 0 | 0 | 0 | 0 | 0
42 | 8 | 0 | 12 |  | -0.25014 | -0.67135 | -14.5771 | -7.8571 | 7.869 | -1.0815 | 4.5442 | 0 | 10 | 10 | 15.876 | 0
42 | 9 | 11 | 50 |  | -0.25014 | -0.67135 | -14.5771 | -7.8571 | 8.869 | -0.81968 | 11.7716 | 5.661 | 41.6667 | 47.3277 | 75.1374 | 0
42 | 10 | 0 | 72 |  | -0.25014 | -0.67135 | -14.5771 | -7.8571 | 9.869 | -0.55788 | 17.5461 | 0 | 60 | 60 | 95.256 | 1
42 | 11 | 0 | 104 |  | -0.25014 | -0.67135 | -14.5771 | -7.8571 | 10.869 | -0.29608 | 21.4061 | 0 | 86.6667 | 86.6667 | 137.592 | 1
42 | 12 | 84 | 162 |  | -0.25014 | -0.67135 | -14.5771 | -7.8571 | 11.869 | -0.034283 | 22.9664 | 67.0305 | 135 | 202.0305 | 320.7437 | 1
42 | 13 | 51 | 178 |  | -0.25014 | -0.67135 | -14.5771 | -7.8571 | 12.869 | 0.22752 | 22.0489 | 39.549 | 148.3333 | 187.8823 | 298.282 | 1
42 | 14 | 47 | 159 |  | -0.25014 | -0.67135 | -14.5771 | -7.8571 | 13.869 | 0.48932 | 18.7602 | 32.5995 | 132.5 | 165.0995 | 262.112 | 1
42 | 15 | 0 | 81 |  | -0.25014 | -0.67135 | -14.5771 | -7.8571 | 14.869 | 0.75111 | 13.4434 | 0 | 67.5 | 67.5 | 107.163 | 1
42 | 16 | 0 | 42 |  | -0.25014 | -0.67135 | -14.5771 | -7.8571 | 15.869 | 1.0129 | 6.5518 | 0 | 35 | 35 | 55.566 | 0
42 | 17 | 0 | 8 |  | -0.25014 | -0.67135 | -14.5771 | -7.8571 | 16.869 | 1.2747 | -1.4597 | 0 | 6.6667 | 6.6667 | 10.584 | 0
42 | 18 | 0 | 0 |  | -0.25014 | -0.67135 | -14.5771 | -7.8571 | 17.869 | 1.5365 | -10.1792 | 0 | 0 | 0 | 0 | 0
42 | 19 | 0 | 0 |  | -0.25014 | -0.67135 | -14.5771 | -7.8571 | 18.869 | 1.7983 | -19.2295 | 0 | 0 | 0 | 0 | 0
42 | 20 | 0 | 0 |  | -0.25014 | -0.67135 | -14.5771 | -7.8571 | 19.869 | 2.0601 | -28.226 | 0 | 0 | 0 | 0 | 0
42 | 21 | 0 | 0 |  | -0.25014 | -0.67135 | -14.5771 | -7.8571 | 20.869 | 2.3219 | -36.7077 | 0 | 0 | 0 | 0 | 0
42 | 22 | 0 | 0 |  | -0.25014 | -0.67135 | -14.5771 | -7.8571 | 21.869 | 2.5837 | -44.0429 | 0 | 0 | 0 | 0 | 0
42 | 23 | 0 | 0 |  | -0.25014 | -0.67135 | -14.5771 | -7.8571 | 22.869 | 2.8455 | -49.3496 | 0 | 0 | 0 | 0 | 0
42 | 24 | 0 | 0 |  | -0.25014 | -0.67135 | -14.5771 | -7.8571 | 23.869 | 3.1073 | -51.6203 | 0 | 0 | 0 | 0 | 0
43 | 1 | 0 | 0 |  | -0.24457 | -0.65414 | -14.5947 | -7.8747 | 0.86875 | -2.9142 | -49.9642 | 0 | 0 | 0 | 0 | 0
43 | 2 | 0 | 0 |  | -0.24457 | -0.65414 | -14.5947 | -7.8747 | 1.8688 | -2.6524 | -45.3805 | 0 | 0 | 0 | 0 | 0
43 | 3 | 0 | 0 |  | -0.24457 | -0.65414 | -14.5947 | -7.8747 | 2.8688 | -2.3906 | -38.5024 | 0 | 0 | 0 | 0 | 0
43 | 4 | 0 | 0 |  | -0.24457 | -0.65414 | -14.5947 | -7.8747 | 3.8688 | -2.1288 | -30.2653 | 0 | 0 | 0 | 0 | 0
43 | 5 | 0 | 0 |  | -0.24457 | -0.65414 | -14.5947 | -7.8747 | 4.8688 | -1.867 | -21.3608 | 0 | 0 | 0 | 0 | 0
43 | 6 | 0 | 0 |  | -0.24457 | -0.65414 | -14.5947 | -7.8747 | 5.8688 | -1.6052 | -12.285 | 0 | 0 | 0 | 0 | 0
43 | 7 | 0 | 0 |  | -0.24457 | -0.65414 | -14.5947 | -7.8747 | 6.8688 | -1.3434 | -3.4359 | 0 | 0 | 0 | 0 | 0
43 | 8 | 0 | 7 |  | -0.24457 | -0.65414 | -14.5947 | -7.8747 | 7.8688 | -1.0816 | 4.8111 | 0 | 5.8333 | 5.8333 | 9.261 | 0
43 | 9 | 16 | 52 |  | -0.24457 | -0.65414 | -14.5947 | -7.8747 | 8.8688 | -0.81976 | 12.0542 | 8.2804 | 43.3333 | 51.6138 | 81.942 | 0
43 | 10 | 57 | 103 |  | -0.24457 | -0.65414 | -14.5947 | -7.8747 | 9.8688 | -0.55796 | 17.8452 | 37.9664 | 85.8333 | 123.7998 | 196.5445 | 1
43 | 11 | 47 | 153 |  | -0.24457 | -0.65414 | -14.5947 | -7.8747 | 10.8688 | -0.29616 | 21.7186 | 35.8551 | 127.5 | 163.3551 | 259.3426 | 1
43 | 12 | 51 | 179 |  | -0.24457 | -0.65414 | -14.5947 | -7.8747 | 11.8688 | -0.03436 | 23.2853 | 40.8673 | 149.1667 | 190.034 | 301.698 | 1
43 | 13 | 52 | 182 |  | -0.24457 | -0.65414 | -14.5947 | -7.8747 | 12.8688 | 0.22744 | 22.3652 | 40.4973 | 151.6667 | 192.1639 | 305.0795 | 1
43 | 14 | 48 | 161 |  | -0.24457 | -0.65414 | -14.5947 | -7.8747 | 13.8688 | 0.48924 | 19.0658 | 33.4479 | 134.1667 | 167.6146 | 266.1049 | 1
43 | 15 | 44 | 120 |  | -0.24457 | -0.65414 | -14.5947 | -7.8747 | 14.8688 | 0.75104 | 13.7339 | 24.6848 | 100 | 124.6848 | 197.9496 | 1
43 | 16 | 9 | 69 |  | -0.24457 | -0.65414 | -14.5947 | -7.8747 | 15.8688 | 1.0128 | 6.827 | 3.4255 | 57.5 | 60.9255 | 96.7253 | 0
43 | 17 | 0 | 14 |  | -0.24457 | -0.65414 | -14.5947 | -7.8747 | 16.8688 | 1.2746 | -1.1972 | 0 | 11.6667 | 11.6667 | 18.522 | 0
43 | 18 | 0 | 0 |  | -0.24457 | -0.65414 | -14.5947 | -7.8747 | 17.8688 | 1.5364 | -9.925 | 0 | 0 | 0 | 0 | 0
43 | 19 | 0 | 0 |  | -0.24457 | -0.65414 | -14.5947 | -7.8747 | 18.8688 | 1.7982 | -18.9778 | 0 | 0 | 0 | 0 | 0
43 | 20 | 0 | 0 |  | -0.24457 | -0.65414 | -14.5947 | -7.8747 | 19.8688 | 2.06 | -27.9697 | 0 | 0 | 0 | 0 | 0
43 | 21 | 0 | 0 |  | -0.24457 | -0.65414 | -14.5947 | -7.8747 | 20.8688 | 2.3218 | -36.4392 | 0 | 0 | 0 | 0 | 0
43 | 22 | 0 | 0 |  | -0.24457 | -0.65414 | -14.5947 | -7.8747 | 21.8688 | 2.5836 | -43.7553 | 0 | 0 | 0 | 0 | 0
43 | 23 | 0 | 0 |  | -0.24457 | -0.65414 | -14.5947 | -7.8747 | 22.8688 | 2.8454 | -49.0413 | 0 | 0 | 0 | 0 | 0
43 | 24 | 0 | 0 |  | -0.24457 | -0.65414 | -14.5947 | -7.8747 | 23.8688 | 3.1072 | -51.3012 | 0 | 0 | 0 | 0 | 0
44 | 1 | 0 | 0 |  | -0.23894 | -0.63693 | -14.5995 | -7.8795 | 0.86867 | -2.9142 | -49.6488 | 0 | 0 | 0 | 0 | 0
44 | 2 | 0 | 0 |  | -0.23894 | -0.63693 | -14.5995 | -7.8795 | 1.8687 | -2.6524 | -45.0856 | 0 | 0 | 0 | 0 | 0
44 | 3 | 0 | 0 |  | -0.23894 | -0.63693 | -14.5995 | -7.8795 | 2.8687 | -2.3906 | -38.2287 | 0 | 0 | 0 | 0 | 0
44 | 4 | 0 | 0 |  | -0.23894 | -0.63693 | -14.5995 | -7.8795 | 3.8687 | -2.1288 | -30.0064 | 0 | 0 | 0 | 0 | 0
44 | 5 | 0 | 0 |  | -0.23894 | -0.63693 | -14.5995 | -7.8795 | 4.8687 | -1.867 | -21.1087 | 0 | 0 | 0 | 0 | 0
44 | 6 | 0 | 0 |  | -0.23894 | -0.63693 | -14.5995 | -7.8795 | 5.8687 | -1.6052 | -12.0323 | 0 | 0 | 0 | 0 | 0
44 | 7 | 0 | 0 |  | -0.23894 | -0.63693 | -14.5995 | -7.8795 | 6.8687 | -1.3434 | -3.1763 | 0 | 0 | 0 | 0 | 0
44 | 8 | 0 | 8 |  | -0.23894 | -0.63693 | -14.5995 | -7.8795 | 7.8687 | -1.0816 | 5.0829 | 0 | 6.6667 | 6.6667 | 10.584 | 0
44 | 9 | 0 | 35 |  | -0.23894 | -0.63693 | -14.5995 | -7.8795 | 8.8687 | -0.81978 | 12.3414 | 0 | 29.1667 | 29.1667 | 46.305 | 0
44 | 10 | 0 | 75 |  | -0.23894 | -0.63693 | -14.5995 | -7.8795 | 9.8687 | -0.55798 | 18.1487 | 0 | 62.5 | 62.5 | 99.225 | 1
44 | 11 | 0 | 108 |  | -0.23894 | -0.63693 | -14.5995 | -7.8795 | 10.8687 | -0.29618 | 22.0354 | 0 | 90 | 90 | 142.884 | 1
44 | 12 | 0 | 126 |  | -0.23894 | -0.63693 | -14.5995 | -7.8795 | 11.8687 | -0.034381 | 23.6081 | 0 | 105 | 105 | 166.698 | 1
44 | 13 | 0 | 128 |  | -0.23894 | -0.63693 | -14.5995 | -7.8795 | 12.8687 | 0.22742 | 22.6847 | 0 | 106.6667 | 106.6667 | 169.344 | 1
44 | 14 | 0 | 114 |  | -0.23894 | -0.63693 | -14.5995 | -7.8795 | 13.8687 | 0.48922 | 19.374 | 0 | 95 | 95 | 150.822 | 1
44 | 15 | 0 | 85 |  | -0.23894 | -0.63693 | -14.5995 | -7.8795 | 14.8687 | 0.75102 | 14.0266 | 0 | 70.8333 | 70.8333 | 112.455 | 1
44 | 16 | 0 | 46 |  | -0.23894 | -0.63693 | -14.5995 | -7.8795 | 15.8687 | 1.0128 | 7.1038 | 0 | 38.3333 | 38.3333 | 60.858 | 0
44 | 17 | 0 | 15 |  | -0.23894 | -0.63693 | -14.5995 | -7.8795 | 16.8687 | 1.2746 | -0.93351 | 0 | 12.5 | 12.5 | 19.845 | 0
44 | 18 | 0 | 0 |  | -0.23894 | -0.63693 | -14.5995 | -7.8795 | 17.8687 | 1.5364 | -9.6697 | 0 | 0 | 0 | 0 | 0
44 | 19 | 0 | 0 |  | -0.23894 | -0.63693 | -14.5995 | -7.8795 | 18.8687 | 1.7982 | -18.7248 | 0 | 0 | 0 | 0 | 0
44 | 20 | 0 | 0 |  | -0.23894 | -0.63693 | -14.5995 | -7.8795 | 19.8687 | 2.06 | -27.712 | 0 | 0 | 0 | 0 | 0
44 | 21 | 0 | 0 |  | -0.23894 | -0.63693 | -14.5995 | -7.8795 | 20.8687 | 2.3218 | -36.1689 | 0 | 0 | 0 | 0 | 0
44 | 22 | 0 | 0 |  | -0.23894 | -0.63693 | -14.5995 | -7.8795 | 21.8687 | 2.5836 | -43.4653 | 0 | 0 | 0 | 0 | 0
44 | 23 | 0 | 0 |  | -0.23894 | -0.63693 | -14.5995 | -7.8795 | 22.8687 | 2.8454 | -48.73 | 0 | 0 | 0 | 0 | 0
44 | 24 | 0 | 0 |  | -0.23894 | -0.63693 | -14.5995 | -7.8795 | 23.8687 | 3.1072 | -50.9784 | 0 | 0 | 0 | 0 | 0
45 | 1 | 0 | 0 |  | -0.23324 | -0.61971 | -14.5916 | -7.8716 | 0.86881 | -2.9141 | -49.3291 | 0 | 0 | 0 | 0 | 0
45 | 2 | 0 | 0 |  | -0.23324 | -0.61971 | -14.5916 | -7.8716 | 1.8688 | -2.6523 | -44.7859 | 0 | 0 | 0 | 0 | 0
45 | 3 | 0 | 0 |  | -0.23324 | -0.61971 | -14.5916 | -7.8716 | 2.8688 | -2.3905 | -37.9499 | 0 | 0 | 0 | 0 | 0
45 | 4 | 0 | 0 |  | -0.23324 | -0.61971 | -14.5916 | -7.8716 | 3.8688 | -2.1287 | -29.7423 | 0 | 0 | 0 | 0 | 0
45 | 5 | 0 | 0 |  | -0.23324 | -0.61971 | -14.5916 | -7.8716 | 4.8688 | -1.8669 | -20.8515 | 0 | 0 | 0 | 0 | 0
45 | 6 | 0 | 0 |  | -0.23324 | -0.61971 | -14.5916 | -7.8716 | 5.8688 | -1.6051 | -11.7747 | 0 | 0 | 0 | 0 | 0
45 | 7 | 0 | 0 |  | -0.23324 | -0.61971 | -14.5916 | -7.8716 | 6.8688 | -1.3433 | -2.9118 | 0 | 0 | 0 | 0 | 0
45 | 8 | 0 | 16 |  | -0.23324 | -0.61971 | -14.5916 | -7.8716 | 7.8688 | -1.0815 | 5.3593 | 0 | 13.3333 | 13.3333 | 21.168 | 0
45 | 9 | 241 | 67 |  | -0.23324 | -0.61971 | -14.5916 | -7.8716 | 8.8688 | -0.81974 | 12.6333 | 126.1565 | 55.8333 | 181.9899 | 288.9271 | 1
45 | 10 | 600 | 59 |  | -0.23324 | -0.61971 | -14.5916 | -7.8716 | 9.8688 | -0.55795 | 18.4567 | 403.4586 | 49.1667 | 452.6252 | 718.5878 | 1
45 | 11 | 692 | 70 |  | -0.23324 | -0.61971 | -14.5916 | -7.8716 | 10.8688 | -0.29615 | 22.3563 | 532.4887 | 58.3333 | 590.822 | 937.989 | 1
45 | 12 | 752 | 69 |  | -0.23324 | -0.61971 | -14.5916 | -7.8716 | 11.8688 | -0.034346 | 23.9347 | 607.6466 | 57.5 | 665.1466 | 1055.9868 | 1
45 | 13 | 749 | 71 |  | -0.23324 | -0.61971 | -14.5916 | -7.8716 | 12.8688 | 0.22745 | 23.0074 | 588.3014 | 59.1667 | 647.4681 | 1027.9204 | 1
45 | 14 | 640 | 84 |  | -0.23324 | -0.61971 | -14.5916 | -7.8716 | 13.8688 | 0.48925 | 19.6847 | 450.0846 | 70 | 520.0846 | 825.6863 | 1
45 | 15 | 584 | 75 |  | -0.23324 | -0.61971 | -14.5916 | -7.8716 | 14.8688 | 0.75105 | 14.3211 | 331.1666 | 62.5 | 393.6666 | 624.9851 | 1
45 | 16 | 435 | 53 |  | -0.23324 | -0.61971 | -14.5916 | -7.8716 | 15.8688 | 1.0129 | 7.382 | 167.9783 | 44.1667 | 212.145 | 336.8013 | 0
45 | 17 | 85 | 24 |  | -0.23324 | -0.61971 | -14.5916 | -7.8716 | 16.8688 | 1.2747 | -0.66856 | 14.693 | 20 | 34.693 | 55.0786 | 0
45 | 18 | 0 | 0 |  | -0.23324 | -0.61971 | -14.5916 | -7.8716 | 17.8688 | 1.5364 | -9.4132 | 0 | 0 | 0 | 0 | 0
45 | 19 | 0 | 0 |  | -0.23324 | -0.61971 | -14.5916 | -7.8716 | 18.8688 | 1.7982 | -18.4706 | 0 | 0 | 0 | 0 | 0
45 | 20 | 0 | 0 |  | -0.23324 | -0.61971 | -14.5916 | -7.8716 | 19.8688 | 2.06 | -27.4528 | 0 | 0 | 0 | 0 | 0
45 | 21 | 0 | 0 |  | -0.23324 | -0.61971 | -14.5916 | -7.8716 | 20.8688 | 2.3218 | -35.8967 | 0 | 0 | 0 | 0 | 0
45 | 22 | 0 | 0 |  | -0.23324 | -0.61971 | -14.5916 | -7.8716 | 21.8688 | 2.5836 | -43.1731 | 0 | 0 | 0 | 0 | 0
45 | 23 | 0 | 0 |  | -0.23324 | -0.61971 | -14.5916 | -7.8716 | 22.8688 | 2.8454 | -48.4158 | 0 | 0 | 0 | 0 | 0
45 | 24 | 0 | 0 |  | -0.23324 | -0.61971 | -14.5916 | -7.8716 | 23.8688 | 3.1072 | -50.6521 | 0 | 0 | 0 | 0 | 0
46 | 1 | 0 | 0 |  | -0.22747 | -0.6025 | -14.5711 | -7.8511 | 0.86915 | -2.914 | -49.0052 | 0 | 0 | 0 | 0 | 0
46 | 2 | 0 | 0 |  | -0.22747 | -0.6025 | -14.5711 | -7.8511 | 1.8691 | -2.6523 | -44.4813 | 0 | 0 | 0 | 0 | 0
46 | 3 | 0 | 0 |  | -0.22747 | -0.6025 | -14.5711 | -7.8511 | 2.8691 | -2.3905 | -37.666 | 0 | 0 | 0 | 0 | 0
46 | 4 | 0 | 0 |  | -0.22747 | -0.6025 | -14.5711 | -7.8511 | 3.8691 | -2.1287 | -29.4732 | 0 | 0 | 0 | 0 | 0
46 | 5 | 0 | 0 |  | -0.22747 | -0.6025 | -14.5711 | -7.8511 | 4.8691 | -1.8669 | -20.5894 | 0 | 0 | 0 | 0 | 0
46 | 6 | 0 | 0 |  | -0.22747 | -0.6025 | -14.5711 | -7.8511 | 5.8691 | -1.6051 | -11.5121 | 0 | 0 | 0 | 0 | 0
46 | 7 | 0 | 0 |  | -0.22747 | -0.6025 | -14.5711 | -7.8511 | 6.8691 | -1.3433 | -2.6426 | 0 | 0 | 0 | 0 | 0
46 | 8 | 0 | 13 |  | -0.22747 | -0.6025 | -14.5711 | -7.8511 | 7.8691 | -1.0815 | 5.6404 | 0 | 10.8333 | 10.8333 | 17.199 | 0
46 | 9 | 0 | 39 |  | -0.22747 | -0.6025 | -14.5711 | -7.8511 | 8.8691 | -0.81965 | 12.9297 | 0 | 32.5 | 32.5 | 51.597 | 1
46 | 10 | 0 | 80 |  | -0.22747 | -0.6025 | -14.5711 | -7.8511 | 9.8691 | -0.55786 | 18.7691 | 0 | 66.6667 | 66.6667 | 105.84 | 1
46 | 11 | 0 | 113 |  | -0.22747 | -0.6025 | -14.5711 | -7.8511 | 10.8691 | -0.29606 | 22.6813 | 0 | 94.1667 | 94.1667 | 149.499 | 1
46 | 12 | 0 | 131 |  | -0.22747 | -0.6025 | -14.5711 | -7.8511 | 11.8691 | -0.034257 | 24.2649 | 0 | 109.1667 | 109.1667 | 173.313 | 1
46 | 13 | 0 | 134 |  | -0.22747 | -0.6025 | -14.5711 | -7.8511 | 12.8691 | 0.22754 | 23.3332 | 0 | 111.6667 | 111.6667 | 177.282 | 1
46 | 14 | 0 | 119 |  | -0.22747 | -0.6025 | -14.5711 | -7.8511 | 13.8691 | 0.48934 | 19.9979 | 0 | 99.1667 | 99.1667 | 157.437 | 1
46 | 15 | 0 | 89 |  | -0.22747 | -0.6025 | -14.5711 | -7.8511 | 14.8691 | 0.75114 | 14.6175 | 0 | 74.1667 | 74.1667 | 117.747 | 1
46 | 16 | 0 | 49 |  | -0.22747 | -0.6025 | -14.5711 | -7.8511 | 15.8691 | 1.0129 | 7.6617 | 0 | 40.8333 | 40.8333 | 64.827 | 0
46 | 17 | 0 | 11 |  | -0.22747 | -0.6025 | -14.5711 | -7.8511 | 16.8691 | 1.2747 | -0.40247 | 0 | 9.1667 | 9.1667 | 14.553 | 0
46 | 18 | 0 | 0 |  | -0.22747 | -0.6025 | -14.5711 | -7.8511 | 17.8691 | 1.5365 | -9.1556 | 0 | 0 | 0 | 0 | 0
46 | 19 | 0 | 0 |  | -0.22747 | -0.6025 | -14.5711 | -7.8511 | 18.8691 | 1.7983 | -18.2152 | 0 | 0 | 0 | 0 | 0
46 | 20 | 0 | 0 |  | -0.22747 | -0.6025 | -14.5711 | -7.8511 | 19.8691 | 2.0601 | -27.1922 | 0 | 0 | 0 | 0 | 0
46 | 21 | 0 | 0 |  | -0.22747 | -0.6025 | -14.5711 | -7.8511 | 20.8691 | 2.3219 | -35.6229 | 0 | 0 | 0 | 0 | 0
46 | 22 | 0 | 0 |  | -0.22747 | -0.6025 | -14.5711 | -7.8511 | 21.8691 | 2.5837 | -42.8786 | 0 | 0 | 0 | 0 | 0
46 | 23 | 0 | 0 |  | -0.22747 | -0.6025 | -14.5711 | -7.8511 | 22.8691 | 2.8455 | -48.0988 | 0 | 0 | 0 | 0 | 0
46 | 24 | 0 | 0 |  | -0.22747 | -0.6025 | -14.5711 | -7.8511 | 23.8691 | 3.1073 | -50.3222 | 0 | 0 | 0 | 0 | 0
47 | 1 | 0 | 0 |  | -0.22165 | -0.58528 | -14.538 | -7.818 | 0.8697 | -2.9139 | -48.6772 | 0 | 0 | 0 | 0 | 0
47 | 2 | 0 | 0 |  | -0.22165 | -0.58528 | -14.538 | -7.818 | 1.8697 | -2.6521 | -44.1721 | 0 | 0 | 0 | 0 | 0
47 | 3 | 0 | 0 |  | -0.22165 | -0.58528 | -14.538 | -7.818 | 2.8697 | -2.3903 | -37.3771 | 0 | 0 | 0 | 0 | 0
47 | 4 | 0 | 0 |  | -0.22165 | -0.58528 | -14.538 | -7.818 | 3.8697 | -2.1285 | -29.199 | 0 | 0 | 0 | 0 | 0
47 | 5 | 0 | 0 |  | -0.22165 | -0.58528 | -14.538 | -7.818 | 4.8697 | -1.8667 | -20.3223 | 0 | 0 | 0 | 0 | 0
47 | 6 | 0 | 0 |  | -0.22165 | -0.58528 | -14.538 | -7.818 | 5.8697 | -1.6049 | -11.2449 | 0 | 0 | 0 | 0 | 0
47 | 7 | 0 | 0 |  | -0.22165 | -0.58528 | -14.538 | -7.818 | 6.8697 | -1.3431 | -2.3687 | 0 | 0 | 0 | 0 | 0
47 | 8 | 0 | 7 |  | -0.22165 | -0.58528 | -14.538 | -7.818 | 7.8697 | -1.0813 | 5.9261 | 0 | 5.8333 | 5.8333 | 9.261 | 0
47 | 9 | 0 | 41 |  | -0.22165 | -0.58528 | -14.538 | -7.818 | 8.8697 | -0.81951 | 13.2305 | 0 | 34.1667 | 34.1667 | 54.243 | 1
47 | 10 | 0 | 82 |  | -0.22165 | -0.58528 | -14.538 | -7.818 | 9.8697 | -0.55771 | 19.0857 | 0 | 68.3333 | 68.3333 | 108.486 | 1
47 | 11 | 0 | 115 |  | -0.22165 | -0.58528 | -14.538 | -7.818 | 10.8697 | -0.29591 | 23.0103 | 0 | 95.8333 | 95.8333 | 152.145 | 1
47 | 12 | 0 | 134 |  | -0.22165 | -0.58528 | -14.538 | -7.818 | 11.8697 | -0.034112 | 24.5986 | 0 | 111.6667 | 111.6667 | 177.282 | 1
47 | 13 | 0 | 136 |  | -0.22165 | -0.58528 | -14.538 | -7.818 | 12.8697 | 0.22769 | 23.6619 | 0 | 113.3333 | 113.3333 | 179.928 | 1
47 | 14 | 0 | 122 |  | -0.22165 | -0.58528 | -14.538 | -7.818 | 13.8697 | 0.48949 | 20.3133 | 0 | 101.6667 | 101.6667 | 161.406 | 1
47 | 15 | 0 | 92 |  | -0.22165 | -0.58528 | -14.538 | -7.818 | 14.8697 | 0.75129 | 14.9156 | 0 | 76.6667 | 76.6667 | 121.716 | 1
47 | 16 | 0 | 51 |  | -0.22165 | -0.58528 | -14.538 | -7.818 | 15.8697 | 1.0131 | 7.9427 | 0 | 42.5 | 42.5 | 67.473 | 0
47 | 17 | 0 | 12 |  | -0.22165 | -0.58528 | -14.538 | -7.818 | 16.8697 | 1.2749 | -0.13531 | 0 | 10 | 10 | 15.876 | 0
47 | 18 | 0 | 0 |  | -0.22165 | -0.58528 | -14.538 | -7.818 | 17.8697 | 1.5367 | -8.8971 | 0 | 0 | 0 | 0 | 0
47 | 19 | 0 | 0 |  | -0.22165 | -0.58528 | -14.538 | -7.818 | 18.8697 | 1.7985 | -17.9588 | 0 | 0 | 0 | 0 | 0
47 | 20 | 0 | 0 |  | -0.22165 | -0.58528 | -14.538 | -7.818 | 19.8697 | 2.0603 | -26.9304 | 0 | 0 | 0 | 0 | 0
47 | 21 | 0 | 0 |  | -0.22165 | -0.58528 | -14.538 | -7.818 | 20.8697 | 2.3221 | -35.3473 | 0 | 0 | 0 | 0 | 0
47 | 22 | 0 | 0 |  | -0.22165 | -0.58528 | -14.538 | -7.818 | 21.8697 | 2.5839 | -42.582 | 0 | 0 | 0 | 0 | 0
47 | 23 | 0 | 0 |  | -0.22165 | -0.58528 | -14.538 | -7.818 | 22.8697 | 2.8457 | -47.7791 | 0 | 0 | 0 | 0 | 0
47 | 24 | 0 | 0 |  | -0.22165 | -0.58528 | -14.538 | -7.818 | 23.8697 | 3.1075 | -49.989 | 0 | 0 | 0 | 0 | 0
48 | 1 | 0 | 0 |  | -0.21577 | -0.56807 | -14.4926 | -7.7726 | 0.87046 | -2.9137 | -48.3451 | 0 | 0 | 0 | 0 | 0
48 | 2 | 0 | 0 |  | -0.21577 | -0.56807 | -14.4926 | -7.7726 | 1.8705 | -2.6519 | -43.8583 | 0 | 0 | 0 | 0 | 0
48 | 3 | 0 | 0 |  | -0.21577 | -0.56807 | -14.4926 | -7.7726 | 2.8705 | -2.3901 | -37.0834 | 0 | 0 | 0 | 0 | 0
48 | 4 | 0 | 0 |  | -0.21577 | -0.56807 | -14.4926 | -7.7726 | 3.8705 | -2.1283 | -28.92 | 0 | 0 | 0 | 0 | 0
48 | 5 | 0 | 0 |  | -0.21577 | -0.56807 | -14.4926 | -7.7726 | 4.8705 | -1.8665 | -20.0504 | 0 | 0 | 0 | 0 | 0
48 | 6 | 0 | 0 |  | -0.21577 | -0.56807 | -14.4926 | -7.7726 | 5.8705 | -1.6047 | -10.9729 | 0 | 0 | 0 | 0 | 0
48 | 7 | 0 | 0 |  | -0.21577 | -0.56807 | -14.4926 | -7.7726 | 6.8705 | -1.3429 | -2.0903 | 0 | 0 | 0 | 0 | 0
48 | 8 | 0 | 7 |  | -0.21577 | -0.56807 | -14.4926 | -7.7726 | 7.8705 | -1.0811 | 6.2161 | 0 | 5.8333 | 5.8333 | 9.261 | 0
48 | 9 | 0 | 42 |  | -0.21577 | -0.56807 | -14.4926 | -7.7726 | 8.8705 | -0.81931 | 13.5356 | 0 | 35 | 35 | 55.566 | 1
48 | 10 | 0 | 84 |  | -0.21577 | -0.56807 | -14.4926 | -7.7726 | 9.8705 | -0.55751 | 19.4065 | 0 | 70 | 70 | 111.132 | 1
48 | 11 | 0 | 118 |  | -0.21577 | -0.56807 | -14.4926 | -7.7726 | 10.8705 | -0.29571 | 23.3432 | 0 | 98.3333 | 98.3333 | 156.114 | 1
48 | 12 | 0 | 136 |  | -0.21577 | -0.56807 | -14.4926 | -7.7726 | 11.8705 | -0.033914 | 24.9358 | 0 | 113.3333 | 113.3333 | 179.928 | 1
48 | 13 | 0 | 139 |  | -0.21577 | -0.56807 | -14.4926 | -7.7726 | 12.8705 | 0.22789 | 23.9935 | 0 | 115.8333 | 115.8333 | 183.897 | 1
48 | 14 | 0 | 124 |  | -0.21577 | -0.56807 | -14.4926 | -7.7726 | 13.8705 | 0.48968 | 20.631 | 0 | 103.3333 | 103.3333 | 164.052 | 1
48 | 15 | 0 | 94 |  | -0.21577 | -0.56807 | -14.4926 | -7.7726 | 14.8705 | 0.75148 | 15.2154 | 0 | 78.3333 | 78.3333 | 124.362 | 1
48 | 16 | 0 | 53 |  | -0.21577 | -0.56807 | -14.4926 | -7.7726 | 15.8705 | 1.0133 | 8.2249 | 0 | 44.1667 | 44.1667 | 70.119 | 0
48 | 17 | 0 | 13 |  | -0.21577 | -0.56807 | -14.4926 | -7.7726 | 16.8705 | 1.2751 | 0.13284 | 0 | 10.8333 | 10.8333 | 17.199 | 0
48 | 18 | 0 | 0 |  | -0.21577 | -0.56807 | -14.4926 | -7.7726 | 17.8705 | 1.5369 | -8.6376 | 0 | 0 | 0 | 0 | 0
48 | 19 | 0 | 0 |  | -0.21577 | -0.56807 | -14.4926 | -7.7726 | 18.8705 | 1.7987 | -17.7013 | 0 | 0 | 0 | 0 | 0
48 | 20 | 0 | 0 |  | -0.21577 | -0.56807 | -14.4926 | -7.7726 | 19.8705 | 2.0605 | -26.6672 | 0 | 0 | 0 | 0 | 0
48 | 21 | 0 | 0 |  | -0.21577 | -0.56807 | -14.4926 | -7.7726 | 20.8705 | 2.3223 | -35.0701 | 0 | 0 | 0 | 0 | 0
48 | 22 | 0 | 0 |  | -0.21577 | -0.56807 | -14.4926 | -7.7726 | 21.8705 | 2.5841 | -42.2833 | 0 | 0 | 0 | 0 | 0
48 | 23 | 0 | 0 |  | -0.21577 | -0.56807 | -14.4926 | -7.7726 | 22.8705 | 2.8459 | -47.4568 | 0 | 0 | 0 | 0 | 0
48 | 24 | 0 | 0 |  | -0.21577 | -0.56807 | -14.4926 | -7.7726 | 23.8705 | 3.1077 | -49.6525 | 0 | 0 | 0 | 0 | 0
49 | 1 | 0 | 0 |  | -0.20983 | -0.55085 | -14.4349 | -7.7149 | 0.87142 | -2.9135 | -48.0091 | 0 | 0 | 0 | 0 | 0
49 | 2 | 0 | 0 |  | -0.20983 | -0.55085 | -14.4349 | -7.7149 | 1.8714 | -2.6517 | -43.54 | 0 | 0 | 0 | 0 | 0
49 | 3 | 0 | 0 |  | -0.20983 | -0.55085 | -14.4349 | -7.7149 | 2.8714 | -2.3899 | -36.785 | 0 | 0 | 0 | 0 | 0
49 | 4 | 0 | 0 |  | -0.20983 | -0.55085 | -14.4349 | -7.7149 | 3.8714 | -2.1281 | -28.6362 | 0 | 0 | 0 | 0 | 0
49 | 5 | 0 | 0 |  | -0.20983 | -0.55085 | -14.4349 | -7.7149 | 4.8714 | -1.8663 | -19.7739 | 0 | 0 | 0 | 0 | 0
49 | 6 | 0 | 0 |  | -0.20983 | -0.55085 | -14.4349 | -7.7149 | 5.8714 | -1.6045 | -10.6964 | 0 | 0 | 0 | 0 | 0
49 | 7 | 0 | 0 |  | -0.20983 | -0.55085 | -14.4349 | -7.7149 | 6.8714 | -1.3427 | -1.8074 | 0 | 0 | 0 | 0 | 0
49 | 8 | 0 | 8 |  | -0.20983 | -0.55085 | -14.4349 | -7.7149 | 7.8714 | -1.0809 | 6.5105 | 0 | 6.6667 | 6.6667 | 10.584 | 0
49 | 9 | 0 | 44 |  | -0.20983 | -0.55085 | -14.4349 | -7.7149 | 8.8714 | -0.81906 | 13.845 | 0 | 36.6667 | 36.6667 | 58.212 | 1
49 | 10 | 0 | 86 |  | -0.20983 | -0.55085 | -14.4349 | -7.7149 | 9.8714 | -0.55726 | 19.7313 | 0 | 71.6667 | 71.6667 | 113.778 | 1
49 | 11 | 0 | 119 |  | -0.20983 | -0.55085 | -14.4349 | -7.7149 | 10.8714 | -0.29546 | 23.6799 | 0 | 99.1667 | 99.1667 | 157.437 | 1
49 | 12 | 0 | 138 |  | -0.20983 | -0.55085 | -14.4349 | -7.7149 | 11.8714 | -0.033662 | 25.2764 | 0 | 115 | 115 | 182.574 | 1
49 | 13 | 0 | 140 |  | -0.20983 | -0.55085 | -14.4349 | -7.7149 | 12.8714 | 0.22814 | 24.3278 | 0 | 116.6667 | 116.6667 | 185.22 | 1
49 | 14 | 0 | 125 |  | -0.20983 | -0.55085 | -14.4349 | -7.7149 | 13.8714 | 0.48994 | 20.9508 | 0 | 104.1667 | 104.1667 | 165.375 | 1
49 | 15 | 0 | 95 |  | -0.20983 | -0.55085 | -14.4349 | -7.7149 | 14.8714 | 0.75174 | 15.5167 | 0 | 79.1667 | 79.1667 | 125.685 | 1
49 | 16 | 0 | 55 |  | -0.20983 | -0.55085 | -14.4349 | -7.7149 | 15.8714 | 1.0135 | 8.5083 | 0 | 45.8333 | 45.8333 | 72.765 | 0
49 | 17 | 0 | 14 |  | -0.20983 | -0.55085 | -14.4349 | -7.7149 | 16.8714 | 1.2753 | 0.40191 | 0 | 11.6667 | 11.6667 | 18.522 | 0
49 | 18 | 0 | 0 |  | -0.20983 | -0.55085 | -14.4349 | -7.7149 | 17.8714 | 1.5371 | -8.3772 | 0 | 0 | 0 | 0 | 0
49 | 19 | 0 | 0 |  | -0.20983 | -0.55085 | -14.4349 | -7.7149 | 18.8714 | 1.7989 | -17.4429 | 0 | 0 | 0 | 0 | 0
49 | 20 | 0 | 0 |  | -0.20983 | -0.55085 | -14.4349 | -7.7149 | 19.8714 | 2.0607 | -26.4029 | 0 | 0 | 0 | 0 | 0
49 | 21 | 0 | 0 |  | -0.20983 | -0.55085 | -14.4349 | -7.7149 | 20.8714 | 2.3225 | -34.7914 | 0 | 0 | 0 | 0 | 0
49 | 22 | 0 | 0 |  | -0.20983 | -0.55085 | -14.4349 | -7.7149 | 21.8714 | 2.5843 | -41.9825 | 0 | 0 | 0 | 0 | 0
49 | 23 | 0 | 0 |  | -0.20983 | -0.55085 | -14.4349 | -7.7149 | 22.8714 | 2.8461 | -47.1318 | 0 | 0 | 0 | 0 | 0
49 | 24 | 0 | 0 |  | -0.20983 | -0.55085 | -14.4349 | -7.7149 | 23.8714 | 3.1079 | -49.3128 | 0 | 0 | 0 | 0 | 0
50 | 1 | 0 | 0 |  | -0.20383 | -0.53364 | -14.3651 | -7.6451 | 0.87258 | -2.9132 | -47.6694 | 0 | 0 | 0 | 0 | 0
50 | 2 | 0 | 0 |  | -0.20383 | -0.53364 | -14.3651 | -7.6451 | 1.8726 | -2.6514 | -43.2173 | 0 | 0 | 0 | 0 | 0
50 | 3 | 0 | 0 |  | -0.20383 | -0.53364 | -14.3651 | -7.6451 | 2.8726 | -2.3896 | -36.4819 | 0 | 0 | 0 | 0 | 0
50 | 4 | 0 | 0 |  | -0.20383 | -0.53364 | -14.3651 | -7.6451 | 3.8726 | -2.1278 | -28.3477 | 0 | 0 | 0 | 0 | 0
50 | 5 | 0 | 0 |  | -0.20383 | -0.53364 | -14.3651 | -7.6451 | 4.8726 | -1.866 | -19.4927 | 0 | 0 | 0 | 0 | 0
50 | 6 | 0 | 0 |  | -0.20383 | -0.53364 | -14.3651 | -7.6451 | 5.8726 | -1.6042 | -10.4153 | 0 | 0 | 0 | 0 | 0
50 | 7 | 0 | 0 |  | -0.20383 | -0.53364 | -14.3651 | -7.6451 | 6.8726 | -1.3424 | -1.5201 | 0 | 0 | 0 | 0 | 0
50 | 8 | 0 | 9 |  | -0.20383 | -0.53364 | -14.3651 | -7.6451 | 7.8726 | -1.0806 | 6.8092 | 0 | 7.5 | 7.5 | 11.907 | 0
50 | 9 | 0 | 46 |  | -0.20383 | -0.53364 | -14.3651 | -7.6451 | 8.8726 | -0.81876 | 14.1584 | 0 | 38.3333 | 38.3333 | 60.858 | 1
50 | 10 | 0 | 89 |  | -0.20383 | -0.53364 | -14.3651 | -7.6451 | 9.8726 | -0.55696 | 20.06 | 0 | 74.1667 | 74.1667 | 117.747 | 1
50 | 11 | 0 | 122 |  | -0.20383 | -0.53364 | -14.3651 | -7.6451 | 10.8726 | -0.29516 | 24.0203 | 0 | 101.6667 | 101.6667 | 161.406 | 1
50 | 12 | 0 | 141 |  | -0.20383 | -0.53364 | -14.3651 | -7.6451 | 11.8726 | -0.033358 | 25.6202 | 0 | 117.5 | 117.5 | 186.543 | 1
50 | 13 | 0 | 143 |  | -0.20383 | -0.53364 | -14.3651 | -7.6451 | 12.8726 | 0.22844 | 24.6649 | 0 | 119.1667 | 119.1667 | 189.189 | 1
50 | 14 | 0 | 128 |  | -0.20383 | -0.53364 | -14.3651 | -7.6451 | 13.8726 | 0.49024 | 21.2726 | 0 | 106.6667 | 106.6667 | 169.344 | 1
50 | 15 | 59 | 137 |  | -0.20383 | -0.53364 | -14.3651 | -7.6451 | 14.8726 | 0.75204 | 15.8195 | 34.3276 | 114.1667 | 148.4942 | 235.7495 | 1
50 | 16 | 24 | 85 |  | -0.20383 | -0.53364 | -14.3651 | -7.6451 | 15.8726 | 1.0138 | 8.7927 | 9.5899 | 70.8333 | 80.4233 | 127.68 | 0
50 | 17 | 0 | 14 |  | -0.20383 | -0.53364 | -14.3651 | -7.6451 | 16.8726 | 1.2756 | 0.67182 | 0 | 11.6667 | 11.6667 | 18.522 | 0
50 | 18 | 0 | 0 |  | -0.20383 | -0.53364 | -14.3651 | -7.6451 | 17.8726 | 1.5374 | -8.1161 | 0 | 0 | 0 | 0 | 0
50 | 19 | 0 | 0 |  | -0.20383 | -0.53364 | -14.3651 | -7.6451 | 18.8726 | 1.7992 | -17.1835 | 0 | 0 | 0 | 0 | 0
50 | 20 | 0 | 0 |  | -0.20383 | -0.53364 | -14.3651 | -7.6451 | 19.8726 | 2.061 | -26.1374 | 0 | 0 | 0 | 0 | 0
50 | 21 | 0 | 0 |  | -0.20383 | -0.53364 | -14.3651 | -7.6451 | 20.8726 | 2.3228 | -34.5111 | 0 | 0 | 0 | 0 | 0
50 | 22 | 0 | 0 |  | -0.20383 | -0.53364 | -14.3651 | -7.6451 | 21.8726 | 2.5846 | -41.6797 | 0 | 0 | 0 | 0 | 0
50 | 23 | 0 | 0 |  | -0.20383 | -0.53364 | -14.3651 | -7.6451 | 22.8726 | 2.8464 | -46.8044 | 0 | 0 | 0 | 0 | 0
50 | 24 | 0 | 0 |  | -0.20383 | -0.53364 | -14.3651 | -7.6451 | 23.8726 | 3.1082 | -48.97 | 0 | 0 | 0 | 0 | 0
51 | 1 | 0 | 0 |  | -0.19778 | -0.51643 | -14.2833 | -7.5633 | 0.87394 | -2.9128 | -47.326 | 0 | 0 | 0 | 0 | 0
51 | 2 | 0 | 0 |  | -0.19778 | -0.51643 | -14.2833 | -7.5633 | 1.8739 | -2.651 | -42.8905 | 0 | 0 | 0 | 0 | 0
51 | 3 | 0 | 0 |  | -0.19778 | -0.51643 | -14.2833 | -7.5633 | 2.8739 | -2.3892 | -36.1743 | 0 | 0 | 0 | 0 | 0
51 | 4 | 0 | 0 |  | -0.19778 | -0.51643 | -14.2833 | -7.5633 | 3.8739 | -2.1274 | -28.0547 | 0 | 0 | 0 | 0 | 0
51 | 5 | 0 | 0 |  | -0.19778 | -0.51643 | -14.2833 | -7.5633 | 4.8739 | -1.8656 | -19.207 | 0 | 0 | 0 | 0 | 0
51 | 6 | 0 | 0 |  | -0.19778 | -0.51643 | -14.2833 | -7.5633 | 5.8739 | -1.6038 | -10.1299 | 0 | 0 | 0 | 0 | 0
51 | 7 | 0 | 0 |  | -0.19778 | -0.51643 | -14.2833 | -7.5633 | 6.8739 | -1.342 | -1.2286 | 0 | 0 | 0 | 0 | 0
51 | 8 | 0 | 10 |  | -0.19778 | -0.51643 | -14.2833 | -7.5633 | 7.8739 | -1.0802 | 7.1119 | 0 | 8.3333 | 8.3333 | 13.23 | 0
51 | 9 | 0 | 48 |  | -0.19778 | -0.51643 | -14.2833 | -7.5633 | 8.8739 | -0.8184 | 14.4759 | 0 | 40 | 40 | 63.504 | 1
51 | 10 | 0 | 91 |  | -0.19778 | -0.51643 | -14.2833 | -7.5633 | 9.8739 | -0.5566 | 20.3926 | 0 | 75.8333 | 75.8333 | 120.393 | 1
51 | 11 | 0 | 124 |  | -0.19778 | -0.51643 | -14.2833 | -7.5633 | 10.8739 | -0.2948 | 24.3642 | 0 | 103.3333 | 103.3333 | 164.052 | 1
51 | 12 | 0 | 143 |  | -0.19778 | -0.51643 | -14.2833 | -7.5633 | 11.8739 | -0.033001 | 25.9672 | 0 | 119.1667 | 119.1667 | 189.189 | 1
51 | 13 | 87 | 194 |  | -0.19778 | -0.51643 | -14.2833 | -7.5633 | 12.8739 | 0.2288 | 25.0044 | 70.0648 | 161.6667 | 231.7314 | 367.8968 | 1
51 | 14 | 75 | 178 |  | -0.19778 | -0.51643 | -14.2833 | -7.5633 | 13.8739 | 0.4906 | 21.5964 | 54.1659 | 148.3333 | 202.4993 | 321.4878 | 1
51 | 15 | 63 | 139 |  | -0.19778 | -0.51643 | -14.2833 | -7.5633 | 14.8739 | 0.7524 | 16.1236 | 36.8362 | 115.8333 | 152.6695 | 242.3781 | 1
51 | 16 | 103 | 97 |  | -0.19778 | -0.51643 | -14.2833 | -7.5633 | 15.8739 | 1.0142 | 9.0781 | 41.4246 | 80.8333 | 122.258 | 194.0968 | 0
51 | 17 | 0 | 25 |  | -0.19778 | -0.51643 | -14.2833 | -7.5633 | 16.8739 | 1.276 | 0.94251 | 0 | 20.8333 | 20.8333 | 33.075 | 0
51 | 18 | 0 | 0 |  | -0.19778 | -0.51643 | -14.2833 | -7.5633 | 17.8739 | 1.5378 | -7.8542 | 0 | 0 | 0 | 0 | 0
51 | 19 | 0 | 0 |  | -0.19778 | -0.51643 | -14.2833 | -7.5633 | 18.8739 | 1.7996 | -16.9233 | 0 | 0 | 0 | 0 | 0
51 | 20 | 0 | 0 |  | -0.19778 | -0.51643 | -14.2833 | -7.5633 | 19.8739 | 2.0614 | -25.8707 | 0 | 0 | 0 | 0 | 0
51 | 21 | 0 | 0 |  | -0.19778 | -0.51643 | -14.2833 | -7.5633 | 20.8739 | 2.3232 | -34.2293 | 0 | 0 | 0 | 0 | 0
51 | 22 | 0 | 0 |  | -0.19778 | -0.51643 | -14.2833 | -7.5633 | 21.8739 | 2.585 | -41.3751 | 0 | 0 | 0 | 0 | 0
51 | 23 | 0 | 0 |  | -0.19778 | -0.51643 | -14.2833 | -7.5633 | 22.8739 | 2.8468 | -46.4746 | 0 | 0 | 0 | 0 | 0
51 | 24 | 0 | 0 |  | -0.19778 | -0.51643 | -14.2833 | -7.5633 | 23.8739 | 3.1086 | -48.6241 | 0 | 0 | 0 | 0 | 0
52 | 1 | 0 | 0 |  | -0.19168 | -0.49921 | -14.1898 | -7.4698 | 0.8755 | -2.9124 | -46.979 | 0 | 0 | 0 | 0 | 0
52 | 2 | 0 | 0 |  | -0.19168 | -0.49921 | -14.1898 | -7.4698 | 1.8755 | -2.6506 | -42.5595 | 0 | 0 | 0 | 0 | 0
52 | 3 | 0 | 0 |  | -0.19168 | -0.49921 | -14.1898 | -7.4698 | 2.8755 | -2.3888 | -35.8624 | 0 | 0 | 0 | 0 | 0
52 | 4 | 0 | 0 |  | -0.19168 | -0.49921 | -14.1898 | -7.4698 | 3.8755 | -2.127 | -27.7572 | 0 | 0 | 0 | 0 | 0
52 | 5 | 0 | 0 |  | -0.19168 | -0.49921 | -14.1898 | -7.4698 | 4.8755 | -1.8652 | -18.917 | 0 | 0 | 0 | 0 | 0
52 | 6 | 0 | 0 |  | -0.19168 | -0.49921 | -14.1898 | -7.4698 | 5.8755 | -1.6034 | -9.8402 | 0 | 0 | 0 | 0 | 0
52 | 7 | 0 | 0 |  | -0.19168 | -0.49921 | -14.1898 | -7.4698 | 6.8755 | -1.3416 | -0.93299 | 0 | 0 | 0 | 0 | 0
52 | 8 | 70 | 25 |  | -0.19168 | -0.49921 | -14.1898 | -7.4698 | 7.8755 | -1.0798 | 7.4187 | 24.7538 | 20.8333 | 45.5871 | 72.3741 | 0
52 | 9 | 291 | 84 |  | -0.19168 | -0.49921 | -14.1898 | -7.4698 | 8.8755 | -0.81799 | 14.7972 | 158.8304 | 70 | 228.8304 | 363.2911 | 1
52 | 10 | 614 | 74 |  | -0.19168 | -0.49921 | -14.1898 | -7.4698 | 9.8755 | -0.55619 | 20.729 | 427.215 | 61.6667 | 488.8817 | 776.1486 | 1
52 | 11 | 728 | 74 |  | -0.19168 | -0.49921 | -14.1898 | -7.4698 | 10.8755 | -0.29439 | 24.7116 | 577.5574 | 61.6667 | 639.224 | 1014.8321 | 1
52 | 12 | 786 | 71 |  | -0.19168 | -0.49921 | -14.1898 | -7.4698 | 11.8755 | -0.032593 | 26.3172 | 653.8221 | 59.1667 | 712.9888 | 1131.9409 | 1
52 | 13 | 789 | 71 |  | -0.19168 | -0.49921 | -14.1898 | -7.4698 | 12.8755 | 0.22921 | 25.3464 | 638.0068 | 59.1667 | 697.1735 | 1106.8326 | 1
52 | 14 | 759 | 69 |  | -0.19168 | -0.49921 | -14.1898 | -7.4698 | 13.8755 | 0.49101 | 21.9219 | 550.508 | 57.5 | 608.008 | 965.2735 | 1
52 | 15 | 650 | 74 |  | -0.19168 | -0.49921 | -14.1898 | -7.4698 | 14.8755 | 0.7528 | 16.429 | 381.9089 | 61.6667 | 443.5756 | 704.2206 | 1
52 | 16 | 494 | 60 |  | -0.19168 | -0.49921 | -14.1898 | -7.4698 | 15.8755 | 1.0146 | 9.3644 | 199.9469 | 50 | 249.9469 | 396.8156 | 0
52 | 17 | 134 | 35 |  | -0.19168 | -0.49921 | -14.1898 | -7.4698 | 16.8755 | 1.2764 | 1.2139 | 25.3742 | 29.1667 | 54.5409 | 86.5892 | 0
52 | 18 | 0 | 1 |  | -0.19168 | -0.49921 | -14.1898 | -7.4698 | 17.8755 | 1.5382 | -7.5916 | 0 | 0.83333 | 0.83333 | 1.323 | 0
52 | 19 | 0 | 0 |  | -0.19168 | -0.49921 | -14.1898 | -7.4698 | 18.8755 | 1.8 | -16.6623 | 0 | 0 | 0 | 0 | 0
52 | 20 | 0 | 0 |  | -0.19168 | -0.49921 | -14.1898 | -7.4698 | 19.8755 | 2.0618 | -25.603 | 0 | 0 | 0 | 0 | 0
52 | 21 | 0 | 0 |  | -0.19168 | -0.49921 | -14.1898 | -7.4698 | 20.8755 | 2.3236 | -33.946 | 0 | 0 | 0 | 0 | 0
52 | 22 | 0 | 0 |  | -0.19168 | -0.49921 | -14.1898 | -7.4698 | 21.8755 | 2.5854 | -41.0685 | 0 | 0 | 0 | 0 | 0
52 | 23 | 0 | 0 |  | -0.19168 | -0.49921 | -14.1898 | -7.4698 | 22.8755 | 2.8472 | -46.1424 | 0 | 0 | 0 | 0 | 0
52 | 24 | 0 | 0 |  | -0.19168 | -0.49921 | -14.1898 | -7.4698 | 23.8755 | 3.109 | -48.2754 | 0 | 0 | 0 | 0 | 0
53 | 1 | 0 | 0 |  | -0.18553 | -0.482 | -14.0848 | -7.3648 | 0.87725 | -2.9119 | -46.6286 | 0 | 0 | 0 | 0 | 0
53 | 2 | 0 | 0 |  | -0.18553 | -0.482 | -14.0848 | -7.3648 | 1.8773 | -2.6501 | -42.2246 | 0 | 0 | 0 | 0 | 0
53 | 3 | 0 | 0 |  | -0.18553 | -0.482 | -14.0848 | -7.3648 | 2.8773 | -2.3883 | -35.5462 | 0 | 0 | 0 | 0 | 0
53 | 4 | 0 | 0 |  | -0.18553 | -0.482 | -14.0848 | -7.3648 | 3.8773 | -2.1265 | -27.4554 | 0 | 0 | 0 | 0 | 0
53 | 5 | 0 | 0 |  | -0.18553 | -0.482 | -14.0848 | -7.3648 | 4.8773 | -1.8647 | -18.6227 | 0 | 0 | 0 | 0 | 0
53 | 6 | 0 | 0 |  | -0.18553 | -0.482 | -14.0848 | -7.3648 | 5.8773 | -1.6029 | -9.5464 | 0 | 0 | 0 | 0 | 0
53 | 7 | 0 | 0 |  | -0.18553 | -0.482 | -14.0848 | -7.3648 | 6.8773 | -1.3411 | -0.6333 | 0 | 0 | 0 | 0 | 0
53 | 8 | 96 | 25 |  | -0.18553 | -0.482 | -14.0848 | -7.3648 | 7.8773 | -1.0793 | 7.7295 | 34.2551 | 20.8333 | 55.0884 | 87.4584 | 0
53 | 9 | 295 | 86 |  | -0.18553 | -0.482 | -14.0848 | -7.3648 | 8.8773 | -0.81753 | 15.1224 | 162.005 | 71.6667 | 233.6717 | 370.9772 | 1
53 | 10 | 616 | 75 |  | -0.18553 | -0.482 | -14.0848 | -7.3648 | 9.8773 | -0.55573 | 21.0689 | 430.7337 | 62.5 | 493.2337 | 783.0578 | 1
53 | 11 | 734 | 74 |  | -0.18553 | -0.482 | -14.0848 | -7.3648 | 10.8773 | -0.29393 | 25.0624 | 584.8635 | 61.6667 | 646.5302 | 1026.4313 | 1
53 | 12 | 789 | 71 |  | -0.18553 | -0.482 | -14.0848 | -7.3648 | 11.8773 | -0.032135 | 26.6701 | 659.0056 | 59.1667 | 718.1723 | 1140.1703 | 1
53 | 13 | 793 | 72 |  | -0.18553 | -0.482 | -14.0848 | -7.3648 | 12.8773 | 0.22966 | 25.6908 | 643.8357 | 60 | 703.8357 | 1117.4095 | 1
53 | 14 | 762 | 70 |  | -0.18553 | -0.482 | -14.0848 | -7.3648 | 13.8773 | 0.49146 | 22.2492 | 555.0248 | 58.3333 | 613.3582 | 973.7674 | 1
53 | 15 | 656 | 74 |  | -0.18553 | -0.482 | -14.0848 | -7.3648 | 14.8773 | 0.75326 | 16.7356 | 387.2855 | 61.6667 | 448.9522 | 712.7565 | 1
53 | 16 | 500 | 61 |  | -0.18553 | -0.482 | -14.0848 | -7.3648 | 15.8773 | 1.0151 | 9.6515 | 203.6446 | 50.8333 | 254.4779 | 404.0091 | 0
53 | 17 | 143 | 37 |  | -0.18553 | -0.482 | -14.0848 | -7.3648 | 16.8773 | 1.2769 | 1.4859 | 27.3989 | 30.8333 | 58.2322 | 92.4495 | 0
53 | 18 | 0 | 1 |  | -0.18553 | -0.482 | -14.0848 | -7.3648 | 17.8773 | 1.5387 | -7.3284 | 0 | 0.83333 | 0.83333 | 1.323 | 0
53 | 19 | 0 | 0 |  | -0.18553 | -0.482 | -14.0848 | -7.3648 | 18.8773 | 1.8005 | -16.4005 | 0 | 0 | 0 | 0 | 0
53 | 20 | 0 | 0 |  | -0.18553 | -0.482 | -14.0848 | -7.3648 | 19.8773 | 2.0623 | -25.3343 | 0 | 0 | 0 | 0 | 0
53 | 21 | 0 | 0 |  | -0.18553 | -0.482 | -14.0848 | -7.3648 | 20.8773 | 2.3241 | -33.6614 | 0 | 0 | 0 | 0 | 0
53 | 22 | 0 | 0 |  | -0.18553 | -0.482 | -14.0848 | -7.3648 | 21.8773 | 2.5859 | -40.7601 | 0 | 0 | 0 | 0 | 0
53 | 23 | 0 | 0 |  | -0.18553 | -0.482 | -14.0848 | -7.3648 | 22.8773 | 2.8477 | -45.8079 | 0 | 0 | 0 | 0 | 0
53 | 24 | 0 | 0 |  | -0.18553 | -0.482 | -14.0848 | -7.3648 | 23.8773 | 3.1095 | -47.9239 | 0 | 0 | 0 | 0 | 0
54 | 1 | 0 | 0 |  | -0.17933 | -0.46478 | -13.9683 | -7.2483 | 0.8792 | -2.9114 | -46.2748 | 0 | 0 | 0 | 0 | 0
54 | 2 | 0 | 0 |  | -0.17933 | -0.46478 | -13.9683 | -7.2483 | 1.8792 | -2.6496 | -41.8858 | 0 | 0 | 0 | 0 | 0
54 | 3 | 0 | 0 |  | -0.17933 | -0.46478 | -13.9683 | -7.2483 | 2.8792 | -2.3878 | -35.2258 | 0 | 0 | 0 | 0 | 0
54 | 4 | 0 | 0 |  | -0.17933 | -0.46478 | -13.9683 | -7.2483 | 3.8792 | -2.126 | -27.1493 | 0 | 0 | 0 | 0 | 0
54 | 5 | 0 | 0 |  | -0.17933 | -0.46478 | -13.9683 | -7.2483 | 4.8792 | -1.8642 | -18.3242 | 0 | 0 | 0 | 0 | 0
54 | 6 | 0 | 0 |  | -0.17933 | -0.46478 | -13.9683 | -7.2483 | 5.8792 | -1.6024 | -9.2485 | 0 | 0 | 0 | 0 | 0
54 | 7 | 0 | 0 |  | -0.17933 | -0.46478 | -13.9683 | -7.2483 | 6.8792 | -1.3406 | -0.32967 | 0 | 0 | 0 | 0 | 0
54 | 8 | 97 | 27 |  | -0.17933 | -0.46478 | -13.9683 | -7.2483 | 7.8792 | -1.0788 | 8.044 | 34.9269 | 22.5 | 57.4269 | 91.171 | 0
54 | 9 | 300 | 89 |  | -0.17933 | -0.46478 | -13.9683 | -7.2483 | 8.8792 | -0.81702 | 15.4512 | 165.7701 | 74.1667 | 239.9367 | 380.9235 | 1
54 | 10 | 619 | 76 |  | -0.17933 | -0.46478 | -13.9683 | -7.2483 | 9.8792 | -0.55523 | 21.4124 | 434.9829 | 63.3333 | 498.3163 | 791.1269 | 1
54 | 11 | 735 | 75 |  | -0.17933 | -0.46478 | -13.9683 | -7.2483 | 10.8792 | -0.29343 | 25.4164 | 588.2165 | 62.5 | 650.7165 | 1033.0775 | 1
54 | 12 | 784 | 74 |  | -0.17933 | -0.46478 | -13.9683 | -7.2483 | 11.8792 | -0.031627 | 27.0258 | 657.4972 | 61.6667 | 719.1639 | 1141.7446 | 1
54 | 13 | 788 | 74 |  | -0.17933 | -0.46478 | -13.9683 | -7.2483 | 12.8792 | 0.23017 | 26.0374 | 642.3422 | 61.6667 | 704.0088 | 1117.6844 | 1
54 | 14 | 757 | 72 |  | -0.17933 | -0.46478 | -13.9683 | -7.2483 | 13.8792 | 0.49197 | 22.5781 | 553.6903 | 60 | 613.6903 | 974.2947 | 1
54 | 15 | 672 | 70 |  | -0.17933 | -0.46478 | -13.9683 | -7.2483 | 14.8792 | 0.75377 | 17.0433 | 398.6079 | 58.3333 | 456.9412 | 725.4399 | 1
54 | 16 | 500 | 62 |  | -0.17933 | -0.46478 | -13.9683 | -7.2483 | 15.8792 | 1.0156 | 9.9394 | 204.8978 | 51.6667 | 256.5645 | 407.3217 | 0
54 | 17 | 153 | 39 |  | -0.17933 | -0.46478 | -13.9683 | -7.2483 | 16.8792 | 1.2774 | 1.7586 | 29.653 | 32.5 | 62.153 | 98.6742 | 0
54 | 18 | 0 | 2 |  | -0.17933 | -0.46478 | -13.9683 | -7.2483 | 17.8792 | 1.5392 | -7.0646 | 0 | 1.6667 | 1.6667 | 2.646 | 0
54 | 19 | 0 | 0 |  | -0.17933 | -0.46478 | -13.9683 | -7.2483 | 18.8792 | 1.801 | -16.138 | 0 | 0 | 0 | 0 | 0
54 | 20 | 0 | 0 |  | -0.17933 | -0.46478 | -13.9683 | -7.2483 | 19.8792 | 2.0628 | -25.0645 | 0 | 0 | 0 | 0 | 0
54 | 21 | 0 | 0 |  | -0.17933 | -0.46478 | -13.9683 | -7.2483 | 20.8792 | 2.3246 | -33.3755 | 0 | 0 | 0 | 0 | 0
54 | 22 | 0 | 0 |  | -0.17933 | -0.46478 | -13.9683 | -7.2483 | 21.8792 | 2.5864 | -40.45 | 0 | 0 | 0 | 0 | 0
54 | 23 | 0 | 0 |  | -0.17933 | -0.46478 | -13.9683 | -7.2483 | 22.8792 | 2.8482 | -45.4713 | 0 | 0 | 0 | 0 | 0
54 | 24 | 0 | 0 |  | -0.17933 | -0.46478 | -13.9683 | -7.2483 | 23.8792 | 3.11 | -47.5696 | 0 | 0 | 0 | 0 | 0
55 | 1 | 0 | 0 |  | -0.17309 | -0.44757 | -13.8407 | -7.1207 | 0.88132 | -2.9109 | -45.9179 | 0 | 0 | 0 | 0 | 0
55 | 2 | 0 | 0 |  | -0.17309 | -0.44757 | -13.8407 | -7.1207 | 1.8813 | -2.6491 | -41.5432 | 0 | 0 | 0 | 0 | 0
55 | 3 | 0 | 0 |  | -0.17309 | -0.44757 | -13.8407 | -7.1207 | 2.8813 | -2.3873 | -34.9014 | 0 | 0 | 0 | 0 | 0
55 | 4 | 0 | 0 |  | -0.17309 | -0.44757 | -13.8407 | -7.1207 | 3.8813 | -2.1255 | -26.8392 | 0 | 0 | 0 | 0 | 0
55 | 5 | 0 | 0 |  | -0.17309 | -0.44757 | -13.8407 | -7.1207 | 4.8813 | -1.8637 | -18.0216 | 0 | 0 | 0 | 0 | 0
55 | 6 | 0 | 0 |  | -0.17309 | -0.44757 | -13.8407 | -7.1207 | 5.8813 | -1.6019 | -8.9466 | 0 | 0 | 0 | 0 | 0
55 | 7 | 0 | 0 |  | -0.17309 | -0.44757 | -13.8407 | -7.1207 | 6.8813 | -1.3401 | -0.022225 | 0 | 0 | 0 | 0 | 0
55 | 8 | 0 | 20 |  | -0.17309 | -0.44757 | -13.8407 | -7.1207 | 7.8813 | -1.0783 | 8.3622 | 0 | 16.6667 | 16.6667 | 26.46 | 0
55 | 9 | 163 | 96 |  | -0.17309 | -0.44757 | -13.8407 | -7.1207 | 8.8813 | -0.81647 | 15.7836 | 90.6278 | 80 | 170.6278 | 270.8886 | 1
55 | 10 | 57 | 139 |  | -0.17309 | -0.44757 | -13.8407 | -7.1207 | 9.8813 | -0.55467 | 21.7594 | 40.2543 | 115.8333 | 156.0876 | 247.8047 | 1
55 | 11 | 183 | 197 |  | -0.17309 | -0.44757 | -13.8407 | -7.1207 | 10.8813 | -0.29287 | 25.7736 | 147.0916 | 164.1667 | 311.2583 | 494.1536 | 1
55 | 12 | 71 | 210 |  | -0.17309 | -0.44757 | -13.8407 | -7.1207 | 11.8813 | -0.03107 | 27.3843 | 59.7849 | 175 | 234.7849 | 372.7446 | 1
55 | 13 | 79 | 209 |  | -0.17309 | -0.44757 | -13.8407 | -7.1207 | 12.8813 | 0.23073 | 26.3862 | 64.6532 | 174.1667 | 238.8198 | 379.1503 | 1
55 | 14 | 0 | 138 |  | -0.17309 | -0.44757 | -13.8407 | -7.1207 | 13.8813 | 0.49253 | 22.9085 | 0 | 115 | 115 | 182.574 | 1
55 | 15 | 71 | 147 |  | -0.17309 | -0.44757 | -13.8407 | -7.1207 | 14.8813 | 0.75433 | 17.352 | 42.3109 | 122.5 | 164.8109 | 261.6538 | 1
55 | 16 | 28 | 98 |  | -0.17309 | -0.44757 | -13.8407 | -7.1207 | 15.8813 | 1.0161 | 10.2279 | 11.5435 | 81.6667 | 93.2102 | 147.9805 | 0
55 | 17 | 0 | 33 |  | -0.17309 | -0.44757 | -13.8407 | -7.1207 | 16.8813 | 1.2779 | 2.0317 | 0 | 27.5 | 27.5 | 43.659 | 0
55 | 18 | 0 | 1 |  | -0.17309 | -0.44757 | -13.8407 | -7.1207 | 17.8813 | 1.5397 | -6.8003 | 0 | 0.83333 | 0.83333 | 1.323 | 0
55 | 19 | 0 | 0 |  | -0.17309 | -0.44757 | -13.8407 | -7.1207 | 18.8813 | 1.8015 | -15.8748 | 0 | 0 | 0 | 0 | 0
55 | 20 | 0 | 0 |  | -0.17309 | -0.44757 | -13.8407 | -7.1207 | 19.8813 | 2.0633 | -24.7939 | 0 | 0 | 0 | 0 | 0
55 | 21 | 0 | 0 |  | -0.17309 | -0.44757 | -13.8407 | -7.1207 | 20.8813 | 2.3251 | -33.0882 | 0 | 0 | 0 | 0 | 0
55 | 22 | 0 | 0 |  | -0.17309 | -0.44757 | -13.8407 | -7.1207 | 21.8813 | 2.5869 | -40.1382 | 0 | 0 | 0 | 0 | 0
55 | 23 | 0 | 0 |  | -0.17309 | -0.44757 | -13.8407 | -7.1207 | 22.8813 | 2.8487 | -45.1325 | 0 | 0 | 0 | 0 | 0
55 | 24 | 0 | 0 |  | -0.17309 | -0.44757 | -13.8407 | -7.1207 | 23.8813 | 3.1105 | -47.2127 | 0 | 0 | 0 | 0 | 0
56 | 1 | 0 | 0 |  | -0.16679 | -0.43036 | -13.7021 | -6.9821 | 0.88363 | -2.9103 | -45.5578 | 0 | 0 | 0 | 0 | 0
56 | 2 | 0 | 0 |  | -0.16679 | -0.43036 | -13.7021 | -6.9821 | 1.8836 | -2.6485 | -41.1971 | 0 | 0 | 0 | 0 | 0
56 | 3 | 0 | 0 |  | -0.16679 | -0.43036 | -13.7021 | -6.9821 | 2.8836 | -2.3867 | -34.5731 | 0 | 0 | 0 | 0 | 0
56 | 4 | 0 | 0 |  | -0.16679 | -0.43036 | -13.7021 | -6.9821 | 3.8836 | -2.1249 | -26.5251 | 0 | 0 | 0 | 0 | 0
56 | 5 | 0 | 0 |  | -0.16679 | -0.43036 | -13.7021 | -6.9821 | 4.8836 | -1.8631 | -17.7151 | 0 | 0 | 0 | 0 | 0
56 | 6 | 0 | 0 |  | -0.16679 | -0.43036 | -13.7021 | -6.9821 | 5.8836 | -1.6013 | -8.6409 | 0 | 0 | 0 | 0 | 0
56 | 7 | 0 | 0 |  | -0.16679 | -0.43036 | -13.7021 | -6.9821 | 6.8836 | -1.3395 | 0.28893 | 0 | 0 | 0 | 0 | 0
56 | 8 | 26 | 30 |  | -0.16679 | -0.43036 | -13.7021 | -6.9821 | 7.8836 | -1.0777 | 8.6841 | 9.5344 | 25 | 34.5344 | 54.8267 | 0
56 | 9 | 129 | 62 |  | -0.16679 | -0.43036 | -13.7021 | -6.9821 | 8.8836 | -0.81586 | 16.1195 | 72.1707 | 51.6667 | 123.8373 | 196.6042 | 1
56 | 10 | 44 | 147 |  | -0.16679 | -0.43036 | -13.7021 | -6.9821 | 9.8836 | -0.55406 | 22.1096 | 31.2281 | 122.5 | 153.7281 | 244.0588 | 1
56 | 11 | 74 | 185 |  | -0.16679 | -0.43036 | -13.7021 | -6.9821 | 10.8836 | -0.29226 | 26.1338 | 59.7379 | 154.1667 | 213.9046 | 339.5949 | 1
56 | 12 | 79 | 210 |  | -0.16679 | -0.43036 | -13.7021 | -6.9821 | 11.8836 | -0.030465 | 27.7455 | 66.789 | 175 | 241.789 | 383.8642 | 1
56 | 13 | 80 | 213 |  | -0.16679 | -0.43036 | -13.7021 | -6.9821 | 12.8836 | 0.23133 | 26.737 | 65.7292 | 177.5 | 243.2292 | 386.1507 | 1
56 | 14 | 76 | 193 |  | -0.16679 | -0.43036 | -13.7021 | -6.9821 | 13.8836 | 0.49313 | 23.2404 | 56.0458 | 160.8333 | 216.8792 | 344.3174 | 1
56 | 15 | 169 | 165 |  | -0.16679 | -0.43036 | -13.7021 | -6.9821 | 14.8836 | 0.75493 | 17.6617 | 101.1731 | 137.5 | 238.6731 | 378.9174 | 1
56 | 16 | 99 | 114 |  | -0.16679 | -0.43036 | -13.7021 | -6.9821 | 15.8836 | 1.0167 | 10.517 | 41.0562 | 95 | 136.0562 | 216.0029 | 0
56 | 17 | 167 | 43 |  | -0.16679 | -0.43036 | -13.7021 | -6.9821 | 16.8836 | 1.2785 | 2.3053 | 33.0889 | 35.8333 | 68.9222 | 109.4209 | 0
56 | 18 | 0 | 2 |  | -0.16679 | -0.43036 | -13.7021 | -6.9821 | 17.8836 | 1.5403 | -6.5356 | 0 | 1.6667 | 1.6667 | 2.646 | 0
56 | 19 | 0 | 0 |  | -0.16679 | -0.43036 | -13.7021 | -6.9821 | 18.8836 | 1.8021 | -15.611 | 0 | 0 | 0 | 0 | 0
56 | 20 | 0 | 0 |  | -0.16679 | -0.43036 | -13.7021 | -6.9821 | 19.8836 | 2.0639 | -24.5223 | 0 | 0 | 0 | 0 | 0
56 | 21 | 0 | 0 |  | -0.16679 | -0.43036 | -13.7021 | -6.9821 | 20.8836 | 2.3257 | -32.7996 | 0 | 0 | 0 | 0 | 0
56 | 22 | 0 | 0 |  | -0.16679 | -0.43036 | -13.7021 | -6.9821 | 21.8836 | 2.5875 | -39.8247 | 0 | 0 | 0 | 0 | 0
56 | 23 | 0 | 0 |  | -0.16679 | -0.43036 | -13.7021 | -6.9821 | 22.8836 | 2.8493 | -44.7916 | 0 | 0 | 0 | 0 | 0
56 | 24 | 0 | 0 |  | -0.16679 | -0.43036 | -13.7021 | -6.9821 | 23.8836 | 3.1111 | -46.8533 | 0 | 0 | 0 | 0 | 0
57 | 1 | 0 | 0 |  | -0.16046 | -0.41314 | -13.5528 | -6.8328 | 0.88612 | -2.9096 | -45.1947 | 0 | 0 | 0 | 0 | 0
57 | 2 | 0 | 0 |  | -0.16046 | -0.41314 | -13.5528 | -6.8328 | 1.8861 | -2.6478 | -40.8474 | 0 | 0 | 0 | 0 | 0
57 | 3 | 0 | 0 |  | -0.16046 | -0.41314 | -13.5528 | -6.8328 | 2.8861 | -2.386 | -34.241 | 0 | 0 | 0 | 0 | 0
57 | 4 | 0 | 0 |  | -0.16046 | -0.41314 | -13.5528 | -6.8328 | 3.8861 | -2.1242 | -26.2071 | 0 | 0 | 0 | 0 | 0
57 | 5 | 0 | 0 |  | -0.16046 | -0.41314 | -13.5528 | -6.8328 | 4.8861 | -1.8624 | -17.4048 | 0 | 0 | 0 | 0 | 0
57 | 6 | 0 | 0 |  | -0.16046 | -0.41314 | -13.5528 | -6.8328 | 5.8861 | -1.6006 | -8.3315 | 0 | 0 | 0 | 0 | 0
57 | 7 | 0 | 0 |  | -0.16046 | -0.41314 | -13.5528 | -6.8328 | 6.8861 | -1.3388 | 0.60368 | 0 | 0 | 0 | 0 | 0
57 | 8 | 0 | 23 |  | -0.16046 | -0.41314 | -13.5528 | -6.8328 | 7.8861 | -1.077 | 9.0094 | 0 | 19.1667 | 19.1667 | 30.429 | 0
57 | 9 | 17 | 90 |  | -0.16046 | -0.41314 | -13.5528 | -6.8328 | 8.8861 | -0.81521 | 16.4587 | 9.5703 | 75 | 84.5703 | 134.2638 | 1
57 | 10 | 45 | 150 |  | -0.16046 | -0.41314 | -13.5528 | -6.8328 | 9.8861 | -0.55341 | 22.463 | 32.0968 | 125 | 157.0968 | 249.4069 | 1
57 | 11 | 76 | 188 |  | -0.16046 | -0.41314 | -13.5528 | -6.8328 | 10.8861 | -0.29161 | 26.497 | 61.6178 | 156.6667 | 218.2845 | 346.5485 | 1
57 | 12 | 1 | 157 |  | -0.16046 | -0.41314 | -13.5528 | -6.8328 | 11.8861 | -0.029814 | 28.1091 | 0.84881 | 130.8333 | 131.6821 | 209.0586 | 1
57 | 13 | 1 | 159 |  | -0.16046 | -0.41314 | -13.5528 | -6.8328 | 12.8861 | 0.23199 | 27.0897 | 0.82482 | 132.5 | 133.3248 | 211.6665 | 1
57 | 14 | 0 | 143 |  | -0.16046 | -0.41314 | -13.5528 | -6.8328 | 13.8861 | 0.49379 | 23.5736 | 0 | 119.1667 | 119.1667 | 189.189 | 1
57 | 15 | 0 | 112 |  | -0.16046 | -0.41314 | -13.5528 | -6.8328 | 14.8861 | 0.75558 | 17.9721 | 0 | 93.3333 | 93.3333 | 148.176 | 1
57 | 16 | 0 | 69 |  | -0.16046 | -0.41314 | -13.5528 | -6.8328 | 15.8861 | 1.0174 | 10.8067 | 0 | 57.5 | 57.5 | 91.287 | 0
57 | 17 | 0 | 23 |  | -0.16046 | -0.41314 | -13.5528 | -6.8328 | 16.8861 | 1.2792 | 2.5792 | 0 | 19.1667 | 19.1667 | 30.429 | 0
57 | 18 | 0 | 1 |  | -0.16046 | -0.41314 | -13.5528 | -6.8328 | 17.8861 | 1.541 | -6.2704 | 0 | 0.83333 | 0.83333 | 1.323 | 0
57 | 19 | 0 | 0 |  | -0.16046 | -0.41314 | -13.5528 | -6.8328 | 18.8861 | 1.8028 | -15.3466 | 0 | 0 | 0 | 0 | 0
57 | 20 | 0 | 0 |  | -0.16046 | -0.41314 | -13.5528 | -6.8328 | 19.8861 | 2.0646 | -24.2498 | 0 | 0 | 0 | 0 | 0
57 | 21 | 0 | 0 |  | -0.16046 | -0.41314 | -13.5528 | -6.8328 | 20.8861 | 2.3264 | -32.5099 | 0 | 0 | 0 | 0 | 0
57 | 22 | 0 | 0 |  | -0.16046 | -0.41314 | -13.5528 | -6.8328 | 21.8861 | 2.5882 | -39.5096 | 0 | 0 | 0 | 0 | 0
57 | 23 | 0 | 0 |  | -0.16046 | -0.41314 | -13.5528 | -6.8328 | 22.8861 | 2.85 | -44.4488 | 0 | 0 | 0 | 0 | 0
57 | 24 | 0 | 0 |  | -0.16046 | -0.41314 | -13.5528 | -6.8328 | 23.8861 | 3.1118 | -46.4915 | 0 | 0 | 0 | 0 | 0
58 | 1 | 0 | 0 |  | -0.15408 | -0.39593 | -13.393 | -6.673 | 0.88878 | -2.9089 | -44.8288 | 0 | 0 | 0 | 0 | 0
58 | 2 | 0 | 0 |  | -0.15408 | -0.39593 | -13.393 | -6.673 | 1.8888 | -2.6471 | -40.4944 | 0 | 0 | 0 | 0 | 0
58 | 3 | 0 | 0 |  | -0.15408 | -0.39593 | -13.393 | -6.673 | 2.8888 | -2.3853 | -33.9052 | 0 | 0 | 0 | 0 | 0
58 | 4 | 0 | 0 |  | -0.15408 | -0.39593 | -13.393 | -6.673 | 3.8888 | -2.1235 | -25.8853 | 0 | 0 | 0 | 0 | 0
58 | 5 | 0 | 0 |  | -0.15408 | -0.39593 | -13.393 | -6.673 | 4.8888 | -1.8617 | -17.0908 | 0 | 0 | 0 | 0 | 0
58 | 6 | 0 | 0 |  | -0.15408 | -0.39593 | -13.393 | -6.673 | 5.8888 | -1.5999 | -8.0185 | 0 | 0 | 0 | 0 | 0
58 | 7 | 0 | 0 |  | -0.15408 | -0.39593 | -13.393 | -6.673 | 6.8888 | -1.3381 | 0.92191 | 0 | 0 | 0 | 0 | 0
58 | 8 | 0 | 16 |  | -0.15408 | -0.39593 | -13.393 | -6.673 | 7.8888 | -1.0763 | 9.338 | 0 | 13.3333 | 13.3333 | 21.168 | 0
58 | 9 | 0 | 60 |  | -0.15408 | -0.39593 | -13.393 | -6.673 | 8.8888 | -0.81451 | 16.8012 | 0 | 50 | 50 | 79.38 | 1
58 | 10 | 0 | 104 |  | -0.15408 | -0.39593 | -13.393 | -6.673 | 9.8888 | -0.55272 | 22.8195 | 0 | 86.6667 | 86.6667 | 137.592 | 1
58 | 11 | 0 | 138 |  | -0.15408 | -0.39593 | -13.393 | -6.673 | 10.8888 | -0.29092 | 26.863 | 0 | 115 | 115 | 182.574 | 1
58 | 12 | 91 | 208 |  | -0.15408 | -0.39593 | -13.393 | -6.673 | 11.8888 | -0.029117 | 28.4751 | 77.5482 | 173.3333 | 250.8815 | 398.2995 | 1
58 | 13 | 4 | 157 |  | -0.15408 | -0.39593 | -13.393 | -6.673 | 12.8888 | 0.23268 | 27.4443 | 3.312 | 130.8333 | 134.1453 | 212.9691 | 1
58 | 14 | 87 | 190 |  | -0.15408 | -0.39593 | -13.393 | -6.673 | 13.8888 | 0.49448 | 23.908 | 64.6715 | 158.3333 | 223.0049 | 354.0425 | 1
58 | 15 | 45 | 163 |  | -0.15408 | -0.39593 | -13.393 | -6.673 | 14.8888 | 0.75628 | 18.2834 | 27.1808 | 135.8333 | 163.0141 | 258.8012 | 1
58 | 16 | 16 | 107 |  | -0.15408 | -0.39593 | -13.393 | -6.673 | 15.8888 | 1.0181 | 11.0968 | 6.7118 | 89.1667 | 95.8785 | 152.2166 | 0
58 | 17 | 0 | 24 |  | -0.15408 | -0.39593 | -13.393 | -6.673 | 16.8888 | 1.2799 | 2.8535 | 0 | 20 | 20 | 31.752 | 0
58 | 18 | 0 | 1 |  | -0.15408 | -0.39593 | -13.393 | -6.673 | 17.8888 | 1.5417 | -6.0048 | 0 | 0.83333 | 0.83333 | 1.323 | 0
58 | 19 | 0 | 0 |  | -0.15408 | -0.39593 | -13.393 | -6.673 | 18.8888 | 1.8035 | -15.0816 | 0 | 0 | 0 | 0 | 0
58 | 20 | 0 | 0 |  | -0.15408 | -0.39593 | -13.393 | -6.673 | 19.8888 | 2.0653 | -23.9766 | 0 | 0 | 0 | 0 | 0
58 | 21 | 0 | 0 |  | -0.15408 | -0.39593 | -13.393 | -6.673 | 20.8888 | 2.3271 | -32.2189 | 0 | 0 | 0 | 0 | 0
58 | 22 | 0 | 0 |  | -0.15408 | -0.39593 | -13.393 | -6.673 | 21.8888 | 2.5889 | -39.1929 | 0 | 0 | 0 | 0 | 0
58 | 23 | 0 | 0 |  | -0.15408 | -0.39593 | -13.393 | -6.673 | 22.8888 | 2.8507 | -44.104 | 0 | 0 | 0 | 0 | 0
58 | 24 | 0 | 0 |  | -0.15408 | -0.39593 | -13.393 | -6.673 | 23.8888 | 3.1125 | -46.1273 | 0 | 0 | 0 | 0 | 0
59 | 1 | 0 | 0 |  | -0.14767 | -0.37871 | -13.2231 | -6.5031 | 0.89162 | -2.9082 | -44.4601 | 0 | 0 | 0 | 0 | 0
59 | 2 | 0 | 0 |  | -0.14767 | -0.37871 | -13.2231 | -6.5031 | 1.8916 | -2.6464 | -40.1382 | 0 | 0 | 0 | 0 | 0
59 | 3 | 0 | 0 |  | -0.14767 | -0.37871 | -13.2231 | -6.5031 | 2.8916 | -2.3846 | -33.566 | 0 | 0 | 0 | 0 | 0
59 | 4 | 0 | 0 |  | -0.14767 | -0.37871 | -13.2231 | -6.5031 | 3.8916 | -2.1228 | -25.5599 | 0 | 0 | 0 | 0 | 0
59 | 5 | 0 | 0 |  | -0.14767 | -0.37871 | -13.2231 | -6.5031 | 4.8916 | -1.861 | -16.7732 | 0 | 0 | 0 | 0 | 0
59 | 6 | 0 | 0 |  | -0.14767 | -0.37871 | -13.2231 | -6.5031 | 5.8916 | -1.5992 | -7.702 | 0 | 0 | 0 | 0 | 0
59 | 7 | 0 | 0 |  | -0.14767 | -0.37871 | -13.2231 | -6.5031 | 6.8916 | -1.3374 | 1.2435 | 0 | 0 | 0 | 0 | 0
59 | 8 | 0 | 17 |  | -0.14767 | -0.37871 | -13.2231 | -6.5031 | 7.8916 | -1.0756 | 9.6699 | 0 | 14.1667 | 14.1667 | 22.491 | 0
59 | 9 | 30 | 92 |  | -0.14767 | -0.37871 | -13.2231 | -6.5031 | 8.8916 | -0.81377 | 17.1468 | 17.1008 | 76.6667 | 93.7675 | 148.8653 | 1
59 | 10 | 51 | 151 |  | -0.14767 | -0.37871 | -13.2231 | -6.5031 | 9.8916 | -0.55197 | 23.1789 | 36.7387 | 125.8333 | 162.572 | 258.0993 | 1
59 | 11 | 50 | 201 |  | -0.14767 | -0.37871 | -13.2231 | -6.5031 | 10.8916 | -0.29017 | 27.2317 | 40.8873 | 167.5 | 208.3873 | 330.8357 | 1
59 | 12 | 4 | 157 |  | -0.14767 | -0.37871 | -13.2231 | -6.5031 | 11.8916 | -0.028375 | 28.8435 | 3.4221 | 130.8333 | 134.2555 | 213.144 | 1
59 | 13 | 2 | 159 |  | -0.14767 | -0.37871 | -13.2231 | -6.5031 | 12.8916 | 0.23342 | 27.8007 | 1.6623 | 132.5 | 134.1623 | 212.9961 | 1
59 | 14 | 0 | 145 |  | -0.14767 | -0.37871 | -13.2231 | -6.5031 | 13.8916 | 0.49522 | 24.2436 | 0 | 120.8333 | 120.8333 | 191.835 | 1
59 | 15 | 0 | 114 |  | -0.14767 | -0.37871 | -13.2231 | -6.5031 | 14.8916 | 0.75702 | 18.5953 | 0 | 95 | 95 | 150.822 | 1
59 | 16 | 27 | 107 |  | -0.14767 | -0.37871 | -13.2231 | -6.5031 | 15.8916 | 1.0188 | 11.3873 | 11.3892 | 89.1667 | 100.5559 | 159.6426 | 0
59 | 17 | 0 | 41 |  | -0.14767 | -0.37871 | -13.2231 | -6.5031 | 16.8916 | 1.2806 | 3.1281 | 0 | 34.1667 | 34.1667 | 54.243 | 0
59 | 18 | 0 | 2 |  | -0.14767 | -0.37871 | -13.2231 | -6.5031 | 17.8916 | 1.5424 | -5.7389 | 0 | 1.6667 | 1.6667 | 2.646 | 0
59 | 19 | 0 | 0 |  | -0.14767 | -0.37871 | -13.2231 | -6.5031 | 18.8916 | 1.8042 | -14.8161 | 0 | 0 | 0 | 0 | 0
59 | 20 | 0 | 0 |  | -0.14767 | -0.37871 | -13.2231 | -6.5031 | 19.8916 | 2.066 | -23.7025 | 0 | 0 | 0 | 0 | 0
59 | 21 | 0 | 0 |  | -0.14767 | -0.37871 | -13.2231 | -6.5031 | 20.8916 | 2.3278 | -31.9269 | 0 | 0 | 0 | 0 | 0
59 | 22 | 0 | 0 |  | -0.14767 | -0.37871 | -13.2231 | -6.5031 | 21.8916 | 2.5896 | -38.8748 | 0 | 0 | 0 | 0 | 0
59 | 23 | 0 | 0 |  | -0.14767 | -0.37871 | -13.2231 | -6.5031 | 22.8916 | 2.8514 | -43.7574 | 0 | 0 | 0 | 0 | 0
59 | 24 | 0 | 0 |  | -0.14767 | -0.37871 | -13.2231 | -6.5031 | 23.8916 | 3.1132 | -45.7609 | 0 | 0 | 0 | 0 | 0
60 | 1 | 0 | 0 |  | -0.14121 | -0.3615 | -13.0431 | -6.3231 | 0.89461 | -2.9074 | -44.0888 | 0 | 0 | 0 | 0 | 0
60 | 2 | 0 | 0 |  | -0.14121 | -0.3615 | -13.0431 | -6.3231 | 1.8946 | -2.6456 | -39.7788 | 0 | 0 | 0 | 0 | 0
60 | 3 | 0 | 0 |  | -0.14121 | -0.3615 | -13.0431 | -6.3231 | 2.8946 | -2.3838 | -33.2233 | 0 | 0 | 0 | 0 | 0
60 | 4 | 0 | 0 |  | -0.14121 | -0.3615 | -13.0431 | -6.3231 | 3.8946 | -2.122 | -25.2311 | 0 | 0 | 0 | 0 | 0
60 | 5 | 0 | 0 |  | -0.14121 | -0.3615 | -13.0431 | -6.3231 | 4.8946 | -1.8602 | -16.4522 | 0 | 0 | 0 | 0 | 0
60 | 6 | 0 | 0 |  | -0.14121 | -0.3615 | -13.0431 | -6.3231 | 5.8946 | -1.5984 | -7.3822 | 0 | 0 | 0 | 0 | 0
60 | 7 | 0 | 2 |  | -0.14121 | -0.3615 | -13.0431 | -6.3231 | 6.8946 | -1.3366 | 1.5683 | 0 | 1.6667 | 1.6667 | 2.646 | 0
60 | 8 | 53 | 42 |  | -0.14121 | -0.3615 | -13.0431 | -6.3231 | 7.8946 | -1.0748 | 10.0049 | 20.1653 | 35 | 55.1653 | 87.5805 | 0
60 | 9 | 130 | 104 |  | -0.14121 | -0.3615 | -13.0431 | -6.3231 | 8.8946 | -0.81299 | 17.4954 | 74.568 | 86.6667 | 161.2347 | 255.9762 | 1
60 | 10 | 513 | 129 |  | -0.14121 | -0.3615 | -13.0431 | -6.3231 | 9.8946 | -0.55119 | 23.5413 | 371.3782 | 107.5 | 478.8782 | 760.267 | 1
60 | 11 | 348 | 193 |  | -0.14121 | -0.3615 | -13.0431 | -6.3231 | 10.8946 | -0.28939 | 27.6031 | 285.7898 | 160.8333 | 446.6231 | 709.0589 | 1
60 | 12 | 387 | 203 |  | -0.14121 | -0.3615 | -13.0431 | -6.3231 | 11.8946 | -0.02759 | 29.214 | 332.3834 | 169.1667 | 501.55 | 796.2608 | 1
60 | 13 | 655 | 148 |  | -0.14121 | -0.3615 | -13.0431 | -6.3231 | 12.8946 | 0.23421 | 28.1587 | 546.453 | 123.3333 | 669.7863 | 1063.3528 | 1
60 | 14 | 698 | 95 |  | -0.14121 | -0.3615 | -13.0431 | -6.3231 | 13.8946 | 0.49601 | 24.5803 | 522.8955 | 79.1667 | 602.0622 | 955.8339 | 1
60 | 15 | 504 | 118 |  | -0.14121 | -0.3615 | -13.0431 | -6.3231 | 14.8946 | 0.75781 | 18.9077 | 307.0559 | 98.3333 | 405.3893 | 643.596 | 1
60 | 16 | 522 | 71 |  | -0.14121 | -0.3615 | -13.0431 | -6.3231 | 15.8946 | 1.0196 | 11.6781 | 221.3933 | 59.1667 | 280.56 | 445.417 | 0
60 | 17 | 160 | 53 |  | -0.14121 | -0.3615 | -13.0431 | -6.3231 | 16.8946 | 1.2814 | 3.4029 | 33.0257 | 44.1667 | 77.1923 | 122.5505 | 0
60 | 18 | 0 | 5 |  | -0.14121 | -0.3615 | -13.0431 | -6.3231 | 17.8946 | 1.5432 | -5.4727 | 0 | 4.1667 | 4.1667 | 6.615 | 0
60 | 19 | 0 | 0 |  | -0.14121 | -0.3615 | -13.0431 | -6.3231 | 18.8946 | 1.805 | -14.5501 | 0 | 0 | 0 | 0 | 0
60 | 20 | 0 | 0 |  | -0.14121 | -0.3615 | -13.0431 | -6.3231 | 19.8946 | 2.0668 | -23.4276 | 0 | 0 | 0 | 0 | 0
60 | 21 | 0 | 0 |  | -0.14121 | -0.3615 | -13.0431 | -6.3231 | 20.8946 | 2.3286 | -31.6337 | 0 | 0 | 0 | 0 | 0
60 | 22 | 0 | 0 |  | -0.14121 | -0.3615 | -13.0431 | -6.3231 | 21.8946 | 2.5904 | -38.5551 | 0 | 0 | 0 | 0 | 0
60 | 23 | 0 | 0 |  | -0.14121 | -0.3615 | -13.0431 | -6.3231 | 22.8946 | 2.8522 | -43.409 | 0 | 0 | 0 | 0 | 0
60 | 24 | 0 | 0 |  | -0.14121 | -0.3615 | -13.0431 | -6.3231 | 23.8946 | 3.114 | -45.3923 | 0 | 0 | 0 | 0 | 0
61 | 1 | 0 | 0 |  | -0.13472 | -0.34428 | -12.8536 | -6.1336 | 0.89777 | -2.9066 | -43.715 | 0 | 0 | 0 | 0 | 0
61 | 2 | 0 | 0 |  | -0.13472 | -0.34428 | -12.8536 | -6.1336 | 1.8978 | -2.6448 | -39.4165 | 0 | 0 | 0 | 0 | 0
61 | 3 | 0 | 0 |  | -0.13472 | -0.34428 | -12.8536 | -6.1336 | 2.8978 | -2.383 | -32.8774 | 0 | 0 | 0 | 0 | 0
61 | 4 | 0 | 0 |  | -0.13472 | -0.34428 | -12.8536 | -6.1336 | 3.8978 | -2.1212 | -24.8989 | 0 | 0 | 0 | 0 | 0
61 | 5 | 0 | 0 |  | -0.13472 | -0.34428 | -12.8536 | -6.1336 | 4.8978 | -1.8594 | -16.1278 | 0 | 0 | 0 | 0 | 0
61 | 6 | 0 | 0 |  | -0.13472 | -0.34428 | -12.8536 | -6.1336 | 5.8978 | -1.5976 | -7.0591 | 0 | 0 | 0 | 0 | 0
61 | 7 | 0 | 2 |  | -0.13472 | -0.34428 | -12.8536 | -6.1336 | 6.8978 | -1.3358 | 1.8963 | 0 | 1.6667 | 1.6667 | 2.646 | 0
61 | 8 | 0 | 35 |  | -0.13472 | -0.34428 | -12.8536 | -6.1336 | 7.8978 | -1.074 | 10.3429 | 0 | 29.1667 | 29.1667 | 46.305 | 0
61 | 9 | 123 | 109 |  | -0.13472 | -0.34428 | -12.8536 | -6.1336 | 8.8978 | -0.81216 | 17.8468 | 70.9948 | 90.8333 | 161.8282 | 256.9184 | 1
61 | 10 | 313 | 156 |  | -0.13472 | -0.34428 | -12.8536 | -6.1336 | 9.8978 | -0.55036 | 23.9063 | 227.7107 | 130 | 357.7107 | 567.9015 | 1
61 | 11 | 327 | 205 |  | -0.13472 | -0.34428 | -12.8536 | -6.1336 | 10.8978 | -0.28856 | 27.9769 | 269.6829 | 170.8333 | 440.5163 | 699.3636 | 1
61 | 12 | 192 | 248 |  | -0.13472 | -0.34428 | -12.8536 | -6.1336 | 11.8978 | -0.026763 | 29.5867 | 165.5413 | 206.6667 | 372.2079 | 590.9173 | 1
61 | 13 | 72 | 235 |  | -0.13472 | -0.34428 | -12.8536 | -6.1336 | 12.8978 | 0.23504 | 28.5182 | 60.2916 | 195.8333 | 256.1249 | 406.6239 | 1
61 | 14 | 77 | 210 |  | -0.13472 | -0.34428 | -12.8536 | -6.1336 | 13.8978 | 0.49684 | 24.9179 | 57.9022 | 175 | 232.9022 | 369.7555 | 1
61 | 15 | 68 | 169 |  | -0.13472 | -0.34428 | -12.8536 | -6.1336 | 14.8978 | 0.75864 | 19.2208 | 41.602 | 140.8333 | 182.4354 | 289.6344 | 1
61 | 16 | 119 | 127 |  | -0.13472 | -0.34428 | -12.8536 | -6.1336 | 15.8978 | 1.0204 | 11.9691 | 50.7405 | 105.8333 | 156.5738 | 248.5766 | 0
61 | 17 | 0 | 30 |  | -0.13472 | -0.34428 | -12.8536 | -6.1336 | 16.8978 | 1.2822 | 3.6779 | 0 | 25 | 25 | 39.69 | 0
61 | 18 | 0 | 4 |  | -0.13472 | -0.34428 | -12.8536 | -6.1336 | 17.8978 | 1.544 | -5.2062 | 0 | 3.3333 | 3.3333 | 5.292 | 0
61 | 19 | 0 | 0 |  | -0.13472 | -0.34428 | -12.8536 | -6.1336 | 18.8978 | 1.8058 | -14.2837 | 0 | 0 | 0 | 0 | 0
61 | 20 | 0 | 0 |  | -0.13472 | -0.34428 | -12.8536 | -6.1336 | 19.8978 | 2.0676 | -23.1521 | 0 | 0 | 0 | 0 | 0
61 | 21 | 0 | 0 |  | -0.13472 | -0.34428 | -12.8536 | -6.1336 | 20.8978 | 2.3294 | -31.3395 | 0 | 0 | 0 | 0 | 0
61 | 22 | 0 | 0 |  | -0.13472 | -0.34428 | -12.8536 | -6.1336 | 21.8978 | 2.5912 | -38.2341 | 0 | 0 | 0 | 0 | 0
61 | 23 | 0 | 0 |  | -0.13472 | -0.34428 | -12.8536 | -6.1336 | 22.8978 | 2.853 | -43.0589 | 0 | 0 | 0 | 0 | 0
61 | 24 | 0 | 0 |  | -0.13472 | -0.34428 | -12.8536 | -6.1336 | 23.8978 | 3.1148 | -45.0217 | 0 | 0 | 0 | 0 | 0
62 | 1 | 0 | 0 |  | -0.1282 | -0.32707 | -12.6546 | -5.9346 | 0.90109 | -2.9057 | -43.3387 | 0 | 0 | 0 | 0 | 0
62 | 2 | 0 | 0 |  | -0.1282 | -0.32707 | -12.6546 | -5.9346 | 1.9011 | -2.6439 | -39.0513 | 0 | 0 | 0 | 0 | 0
62 | 3 | 0 | 0 |  | -0.1282 | -0.32707 | -12.6546 | -5.9346 | 2.9011 | -2.3821 | -32.5283 | 0 | 0 | 0 | 0 | 0
62 | 4 | 0 | 0 |  | -0.1282 | -0.32707 | -12.6546 | -5.9346 | 3.9011 | -2.1203 | -24.5634 | 0 | 0 | 0 | 0 | 0
62 | 5 | 0 | 0 |  | -0.1282 | -0.32707 | -12.6546 | -5.9346 | 4.9011 | -1.8585 | -15.8003 | 0 | 0 | 0 | 0 | 0
62 | 6 | 0 | 0 |  | -0.1282 | -0.32707 | -12.6546 | -5.9346 | 5.9011 | -1.5967 | -6.7329 | 0 | 0 | 0 | 0 | 0
62 | 7 | 0 | 1 |  | -0.1282 | -0.32707 | -12.6546 | -5.9346 | 6.9011 | -1.3349 | 2.2272 | 0 | 0.83333 | 0.83333 | 1.323 | 0
62 | 8 | 0 | 23 |  | -0.1282 | -0.32707 | -12.6546 | -5.9346 | 7.9011 | -1.0731 | 10.6838 | 0 | 19.1667 | 19.1667 | 30.429 | 0
62 | 9 | 0 | 70 |  | -0.1282 | -0.32707 | -12.6546 | -5.9346 | 8.9011 | -0.81129 | 18.2011 | 0 | 58.3333 | 58.3333 | 92.61 | 1
62 | 10 | 0 | 116 |  | -0.1282 | -0.32707 | -12.6546 | -5.9346 | 9.9011 | -0.54949 | 24.274 | 0 | 96.6667 | 96.6667 | 153.468 | 1
62 | 11 | 1 | 150 |  | -0.1282 | -0.32707 | -12.6546 | -5.9346 | 10.9011 | -0.28769 | 28.3532 | 0.82819 | 125 | 125.8282 | 199.7648 | 1
62 | 12 | 3 | 167 |  | -0.1282 | -0.32707 | -12.6546 | -5.9346 | 11.9011 | -0.025894 | 29.9614 | 2.5965 | 139.1667 | 141.7632 | 225.0632 | 1
62 | 13 | 94 | 225 |  | -0.1282 | -0.32707 | -12.6546 | -5.9346 | 12.9011 | 0.2359 | 28.8791 | 79.0032 | 187.5 | 266.5032 | 423.1004 | 1
62 | 14 | 492 | 196 |  | -0.1282 | -0.32707 | -12.6546 | -5.9346 | 13.9011 | 0.4977 | 25.2564 | 371.3544 | 163.3333 | 534.6877 | 848.8702 | 1
62 | 15 | 73 | 168 |  | -0.1282 | -0.32707 | -12.6546 | -5.9346 | 14.9011 | 0.7595 | 19.5342 | 44.845 | 140 | 184.845 | 293.4599 | 1
62 | 16 | 54 | 112 |  | -0.1282 | -0.32707 | -12.6546 | -5.9346 | 15.9011 | 1.0213 | 12.2603 | 23.1455 | 93.3333 | 116.4788 | 184.9217 | 0
62 | 17 | 35 | 60 |  | -0.1282 | -0.32707 | -12.6546 | -5.9346 | 16.9011 | 1.2831 | 3.953 | 7.3625 | 50 | 57.3625 | 91.0686 | 0
62 | 18 | 0 | 5 |  | -0.1282 | -0.32707 | -12.6546 | -5.9346 | 17.9011 | 1.5449 | -4.9396 | 0 | 4.1667 | 4.1667 | 6.615 | 0
62 | 19 | 0 | 0 |  | -0.1282 | -0.32707 | -12.6546 | -5.9346 | 18.9011 | 1.8067 | -14.0169 | 0 | 0 | 0 | 0 | 0
62 | 20 | 0 | 0 |  | -0.1282 | -0.32707 | -12.6546 | -5.9346 | 19.9011 | 2.0685 | -22.8758 | 0 | 0 | 0 | 0 | 0
62 | 21 | 0 | 0 |  | -0.1282 | -0.32707 | -12.6546 | -5.9346 | 20.9011 | 2.3303 | -31.0442 | 0 | 0 | 0 | 0 | 0
62 | 22 | 0 | 0 |  | -0.1282 | -0.32707 | -12.6546 | -5.9346 | 21.9011 | 2.5921 | -37.9118 | 0 | 0 | 0 | 0 | 0
62 | 23 | 0 | 0 |  | -0.1282 | -0.32707 | -12.6546 | -5.9346 | 22.9011 | 2.8539 | -42.7072 | 0 | 0 | 0 | 0 | 0
62 | 24 | 0 | 0 |  | -0.1282 | -0.32707 | -12.6546 | -5.9346 | 23.9011 | 3.1157 | -44.6491 | 0 | 0 | 0 | 0 | 0
63 | 1 | 0 | 0 |  | -0.12164 | -0.30986 | -12.4465 | -5.7265 | 0.90456 | -2.9048 | -42.9602 | 0 | 0 | 0 | 0 | 0
63 | 2 | 0 | 0 |  | -0.12164 | -0.30986 | -12.4465 | -5.7265 | 1.9046 | -2.643 | -38.6834 | 0 | 0 | 0 | 0 | 0
63 | 3 | 0 | 0 |  | -0.12164 | -0.30986 | -12.4465 | -5.7265 | 2.9046 | -2.3812 | -32.1762 | 0 | 0 | 0 | 0 | 0
63 | 4 | 0 | 0 |  | -0.12164 | -0.30986 | -12.4465 | -5.7265 | 3.9046 | -2.1194 | -24.2249 | 0 | 0 | 0 | 0 | 0
63 | 5 | 0 | 0 |  | -0.12164 | -0.30986 | -12.4465 | -5.7265 | 4.9046 | -1.8576 | -15.4696 | 0 | 0 | 0 | 0 | 0
63 | 6 | 0 | 0 |  | -0.12164 | -0.30986 | -12.4465 | -5.7265 | 5.9046 | -1.5958 | -6.4038 | 0 | 0 | 0 | 0 | 0
63 | 7 | 0 | 4 |  | -0.12164 | -0.30986 | -12.4465 | -5.7265 | 6.9046 | -1.334 | 2.561 | 0 | 3.3333 | 3.3333 | 5.292 | 0
63 | 8 | 70 | 51 |  | -0.12164 | -0.30986 | -12.4465 | -5.7265 | 7.9046 | -1.0722 | 11.0274 | 27.3826 | 42.5 | 69.8826 | 110.9457 | 0
63 | 9 | 348 | 113 |  | -0.12164 | -0.30986 | -12.4465 | -5.7265 | 8.9046 | -0.81038 | 18.5579 | 203.3841 | 94.1667 | 297.5508 | 472.3917 | 1
63 | 10 | 316 | 162 |  | -0.12164 | -0.30986 | -12.4465 | -5.7265 | 9.9046 | -0.54859 | 24.6442 | 232.158 | 135 | 367.158 | 582.9 | 1
63 | 11 | 589 | 148 |  | -0.12164 | -0.30986 | -12.4465 | -5.7265 | 10.9046 | -0.28679 | 28.7317 | 489.8486 | 123.3333 | 613.182 | 973.4877 | 1
63 | 12 | 14 | 165 |  | -0.12164 | -0.30986 | -12.4465 | -5.7265 | 11.9046 | -0.024987 | 30.3379 | 12.1629 | 137.5 | 149.6629 | 237.6049 | 1
63 | 13 | 88 | 233 |  | -0.12164 | -0.30986 | -12.4465 | -5.7265 | 12.9046 | 0.23681 | 29.2415 | 74.2285 | 194.1667 | 268.3952 | 426.1042 | 1
63 | 14 | 76 | 216 |  | -0.12164 | -0.30986 | -12.4465 | -5.7265 | 13.9046 | 0.49861 | 25.5957 | 57.5745 | 180 | 237.5745 | 377.1732 | 1
63 | 15 | 172 | 189 |  | -0.12164 | -0.30986 | -12.4465 | -5.7265 | 14.9046 | 0.76041 | 19.848 | 106.0891 | 157.5 | 263.5891 | 418.474 | 1
63 | 16 | 106 | 136 |  | -0.12164 | -0.30986 | -12.4465 | -5.7265 | 15.9046 | 1.0222 | 12.5517 | 45.6661 | 113.3333 | 158.9995 | 252.4276 | 1
63 | 17 | 0 | 53 |  | -0.12164 | -0.30986 | -12.4465 | -5.7265 | 16.9046 | 1.284 | 4.2282 | 0 | 44.1667 | 44.1667 | 70.119 | 0
63 | 18 | 0 | 7 |  | -0.12164 | -0.30986 | -12.4465 | -5.7265 | 17.9046 | 1.5458 | -4.6727 | 0 | 5.8333 | 5.8333 | 9.261 | 0
63 | 19 | 0 | 0 |  | -0.12164 | -0.30986 | -12.4465 | -5.7265 | 18.9046 | 1.8076 | -13.7498 | 0 | 0 | 0 | 0 | 0
63 | 20 | 0 | 0 |  | -0.12164 | -0.30986 | -12.4465 | -5.7265 | 19.9046 | 2.0694 | -22.5989 | 0 | 0 | 0 | 0 | 0
63 | 21 | 0 | 0 |  | -0.12164 | -0.30986 | -12.4465 | -5.7265 | 20.9046 | 2.3312 | -30.7479 | 0 | 0 | 0 | 0 | 0
63 | 22 | 0 | 0 |  | -0.12164 | -0.30986 | -12.4465 | -5.7265 | 21.9046 | 2.593 | -37.5882 | 0 | 0 | 0 | 0 | 0
63 | 23 | 0 | 0 |  | -0.12164 | -0.30986 | -12.4465 | -5.7265 | 22.9046 | 2.8548 | -42.3539 | 0 | 0 | 0 | 0 | 0
63 | 24 | 0 | 0 |  | -0.12164 | -0.30986 | -12.4465 | -5.7265 | 23.9046 | 3.1166 | -44.2746 | 0 | 0 | 0 | 0 | 0
64 | 1 | 0 | 0 |  | -0.11505 | -0.29264 | -12.2297 | -5.5097 | 0.90817 | -2.9038 | -42.5795 | 0 | 0 | 0 | 0 | 0
64 | 2 | 0 | 0 |  | -0.11505 | -0.29264 | -12.2297 | -5.5097 | 1.9082 | -2.642 | -38.3129 | 0 | 0 | 0 | 0 | 0
64 | 3 | 0 | 0 |  | -0.11505 | -0.29264 | -12.2297 | -5.5097 | 2.9082 | -2.3802 | -31.8213 | 0 | 0 | 0 | 0 | 0
64 | 4 | 0 | 0 |  | -0.11505 | -0.29264 | -12.2297 | -5.5097 | 3.9082 | -2.1184 | -23.8834 | 0 | 0 | 0 | 0 | 0
64 | 5 | 0 | 0 |  | -0.11505 | -0.29264 | -12.2297 | -5.5097 | 4.9082 | -1.8566 | -15.136 | 0 | 0 | 0 | 0 | 0
64 | 6 | 0 | 0 |  | -0.11505 | -0.29264 | -12.2297 | -5.5097 | 5.9082 | -1.5948 | -6.0718 | 0 | 0 | 0 | 0 | 0
64 | 7 | 0 | 3 |  | -0.11505 | -0.29264 | -12.2297 | -5.5097 | 6.9082 | -1.333 | 2.8975 | 0 | 2.5 | 2.5 | 3.969 | 0
64 | 8 | 0 | 43 |  | -0.11505 | -0.29264 | -12.2297 | -5.5097 | 7.9082 | -1.0712 | 11.3737 | 0 | 35.8333 | 35.8333 | 56.889 | 0
64 | 9 | 132 | 118 |  | -0.11505 | -0.29264 | -12.2297 | -5.5097 | 8.9082 | -0.80944 | 18.9173 | 77.6269 | 98.3333 | 175.9602 | 279.3544 | 1
64 | 10 | 60 | 170 |  | -0.11505 | -0.29264 | -12.2297 | -5.5097 | 9.9082 | -0.54764 | 25.0168 | 44.2958 | 141.6667 | 185.9625 | 295.2341 | 1
64 | 11 | 190 | 231 |  | -0.11505 | -0.29264 | -12.2297 | -5.5097 | 10.9082 | -0.28584 | 29.1124 | 158.6723 | 192.5 | 351.1723 | 557.5211 | 1
64 | 12 | 215 | 248 |  | -0.11505 | -0.29264 | -12.2297 | -5.5097 | 11.9082 | -0.02404 | 30.7162 | 187.4891 | 206.6667 | 394.1557 | 625.7616 | 1
64 | 13 | 73 | 244 |  | -0.11505 | -0.29264 | -12.2297 | -5.5097 | 12.9082 | 0.23776 | 29.605 | 61.7961 | 203.3333 | 265.1295 | 420.9195 | 1
64 | 14 | 2 | 160 |  | -0.11505 | -0.29264 | -12.2297 | -5.5097 | 13.9082 | 0.49956 | 25.9356 | 1.5206 | 133.3333 | 134.8539 | 214.0941 | 1
64 | 15 | 0 | 129 |  | -0.11505 | -0.29264 | -12.2297 | -5.5097 | 14.9082 | 0.76136 | 20.1621 | 0 | 107.5 | 107.5 | 170.667 | 1
64 | 16 | 0 | 84 |  | -0.11505 | -0.29264 | -12.2297 | -5.5097 | 15.9082 | 1.0232 | 12.8431 | 0 | 70 | 70 | 111.132 | 1
64 | 17 | 0 | 35 |  | -0.11505 | -0.29264 | -12.2297 | -5.5097 | 16.9082 | 1.285 | 4.5034 | 0 | 29.1667 | 29.1667 | 46.305 | 0
64 | 18 | 0 | 4 |  | -0.11505 | -0.29264 | -12.2297 | -5.5097 | 17.9082 | 1.5468 | -4.4058 | 0 | 3.3333 | 3.3333 | 5.292 | 0
64 | 19 | 0 | 0 |  | -0.11505 | -0.29264 | -12.2297 | -5.5097 | 18.9082 | 1.8086 | -13.4822 | 0 | 0 | 0 | 0 | 0
64 | 20 | 0 | 0 |  | -0.11505 | -0.29264 | -12.2297 | -5.5097 | 19.9082 | 2.0704 | -22.3214 | 0 | 0 | 0 | 0 | 0
64 | 21 | 0 | 0 |  | -0.11505 | -0.29264 | -12.2297 | -5.5097 | 20.9082 | 2.3322 | -30.4508 | 0 | 0 | 0 | 0 | 0
64 | 22 | 0 | 0 |  | -0.11505 | -0.29264 | -12.2297 | -5.5097 | 21.9082 | 2.594 | -37.2633 | 0 | 0 | 0 | 0 | 0
64 | 23 | 0 | 0 |  | -0.11505 | -0.29264 | -12.2297 | -5.5097 | 22.9082 | 2.8558 | -41.999 | 0 | 0 | 0 | 0 | 0
64 | 24 | 0 | 0 |  | -0.11505 | -0.29264 | -12.2297 | -5.5097 | 23.9082 | 3.1176 | -43.8983 | 0 | 0 | 0 | 0 | 0
65 | 1 | 0 | 0 |  | -0.10844 | -0.27543 | -12.0044 | -5.2844 | 0.91193 | -2.9029 | -42.1967 | 0 | 0 | 0 | 0 | 0
65 | 2 | 0 | 0 |  | -0.10844 | -0.27543 | -12.0044 | -5.2844 | 1.9119 | -2.6411 | -37.9399 | 0 | 0 | 0 | 0 | 0
65 | 3 | 0 | 0 |  | -0.10844 | -0.27543 | -12.0044 | -5.2844 | 2.9119 | -2.3793 | -31.4636 | 0 | 0 | 0 | 0 | 0
65 | 4 | 0 | 0 |  | -0.10844 | -0.27543 | -12.0044 | -5.2844 | 3.9119 | -2.1175 | -23.539 | 0 | 0 | 0 | 0 | 0
65 | 5 | 0 | 0 |  | -0.10844 | -0.27543 | -12.0044 | -5.2844 | 4.9119 | -1.8557 | -14.7996 | 0 | 0 | 0 | 0 | 0
65 | 6 | 0 | 0 |  | -0.10844 | -0.27543 | -12.0044 | -5.2844 | 5.9119 | -1.5939 | -5.737 | 0 | 0 | 0 | 0 | 0
65 | 7 | 0 | 3 |  | -0.10844 | -0.27543 | -12.0044 | -5.2844 | 6.9119 | -1.3321 | 3.2367 | 0 | 2.5 | 2.5 | 3.969 | 0
65 | 8 | 0 | 45 |  | -0.10844 | -0.27543 | -12.0044 | -5.2844 | 7.9119 | -1.0703 | 11.7225 | 0 | 37.5 | 37.5 | 59.535 | 0
65 | 9 | 2 | 100 |  | -0.10844 | -0.27543 | -12.0044 | -5.2844 | 8.9119 | -0.80846 | 19.2791 | 1.1835 | 83.3333 | 84.5168 | 134.1789 | 1
65 | 10 | 0 | 122 |  | -0.10844 | -0.27543 | -12.0044 | -5.2844 | 9.9119 | -0.54666 | 25.3917 | 0 | 101.6667 | 101.6667 | 161.406 | 1
65 | 11 | 2 | 156 |  | -0.10844 | -0.27543 | -12.0044 | -5.2844 | 10.9119 | -0.28486 | 29.4951 | 1.6771 | 130 | 131.6771 | 209.0506 | 1
65 | 12 | 4 | 173 |  | -0.10844 | -0.27543 | -12.0044 | -5.2844 | 11.9119 | -0.023057 | 31.0963 | 3.5011 | 144.1667 | 147.6678 | 234.4374 | 1
65 | 13 | 4 | 174 |  | -0.10844 | -0.27543 | -12.0044 | -5.2844 | 12.9119 | 0.23874 | 29.9697 | 3.398 | 145 | 148.398 | 235.5967 | 1
65 | 14 | 2 | 160 |  | -0.10844 | -0.27543 | -12.0044 | -5.2844 | 13.9119 | 0.50054 | 26.2762 | 1.526 | 133.3333 | 134.8593 | 214.1027 | 1
65 | 15 | 0 | 129 |  | -0.10844 | -0.27543 | -12.0044 | -5.2844 | 14.9119 | 0.76234 | 20.4764 | 0 | 107.5 | 107.5 | 170.667 | 1
65 | 16 | 0 | 85 |  | -0.10844 | -0.27543 | -12.0044 | -5.2844 | 15.9119 | 1.0241 | 13.1346 | 0 | 70.8333 | 70.8333 | 112.455 | 1
65 | 17 | 2 | 57 |  | -0.10844 | -0.27543 | -12.0044 | -5.2844 | 16.9119 | 1.2859 | 4.7785 | 0.43207 | 47.5 | 47.9321 | 76.097 | 0
65 | 18 | 0 | 7 |  | -0.10844 | -0.27543 | -12.0044 | -5.2844 | 17.9119 | 1.5477 | -4.1387 | 0 | 5.8333 | 5.8333 | 9.261 | 0
65 | 19 | 0 | 0 |  | -0.10844 | -0.27543 | -12.0044 | -5.2844 | 18.9119 | 1.8095 | -13.2144 | 0 | 0 | 0 | 0 | 0
65 | 20 | 0 | 0 |  | -0.10844 | -0.27543 | -12.0044 | -5.2844 | 19.9119 | 2.0713 | -22.0432 | 0 | 0 | 0 | 0 | 0
65 | 21 | 0 | 0 |  | -0.10844 | -0.27543 | -12.0044 | -5.2844 | 20.9119 | 2.3331 | -30.1526 | 0 | 0 | 0 | 0 | 0
65 | 22 | 0 | 0 |  | -0.10844 | -0.27543 | -12.0044 | -5.2844 | 21.9119 | 2.5949 | -36.9372 | 0 | 0 | 0 | 0 | 0
65 | 23 | 0 | 0 |  | -0.10844 | -0.27543 | -12.0044 | -5.2844 | 22.9119 | 2.8567 | -41.6428 | 0 | 0 | 0 | 0 | 0
65 | 24 | 0 | 0 |  | -0.10844 | -0.27543 | -12.0044 | -5.2844 | 23.9119 | 3.1185 | -43.5204 | 0 | 0 | 0 | 0 | 0
66 | 1 | 0 | 0 |  | -0.10179 | -0.25821 | -11.7709 | -5.0509 | 0.91582 | -2.9018 | -41.8119 | 0 | 0 | 0 | 0 | 0
66 | 2 | 0 | 0 |  | -0.10179 | -0.25821 | -11.7709 | -5.0509 | 1.9158 | -2.64 | -37.5646 | 0 | 0 | 0 | 0 | 0
66 | 3 | 0 | 0 |  | -0.10179 | -0.25821 | -11.7709 | -5.0509 | 2.9158 | -2.3782 | -31.1033 | 0 | 0 | 0 | 0 | 0
66 | 4 | 0 | 0 |  | -0.10179 | -0.25821 | -11.7709 | -5.0509 | 3.9158 | -2.1164 | -23.192 | 0 | 0 | 0 | 0 | 0
66 | 5 | 0 | 0 |  | -0.10179 | -0.25821 | -11.7709 | -5.0509 | 4.9158 | -1.8546 | -14.4606 | 0 | 0 | 0 | 0 | 0
66 | 6 | 0 | 0 |  | -0.10179 | -0.25821 | -11.7709 | -5.0509 | 5.9158 | -1.5928 | -5.3997 | 0 | 0 | 0 | 0 | 0
66 | 7 | 0 | 5 |  | -0.10179 | -0.25821 | -11.7709 | -5.0509 | 6.9158 | -1.331 | 3.5783 | 0 | 4.1667 | 4.1667 | 6.615 | 0
66 | 8 | 103 | 57 |  | -0.10179 | -0.25821 | -11.7709 | -5.0509 | 7.9158 | -1.0692 | 12.0736 | 41.4201 | 47.5 | 88.9201 | 141.1696 | 0
66 | 9 | 30 | 118 |  | -0.10179 | -0.25821 | -11.7709 | -5.0509 | 8.9158 | -0.80744 | 19.6432 | 17.8622 | 98.3333 | 116.1956 | 184.4721 | 1
66 | 10 | 426 | 156 |  | -0.10179 | -0.25821 | -11.7709 | -5.0509 | 9.9158 | -0.54564 | 25.7687 | 317.5544 | 130 | 447.5544 | 710.5373 | 1
66 | 11 | 413 | 181 |  | -0.10179 | -0.25821 | -11.7709 | -5.0509 | 10.9158 | -0.28384 | 29.8798 | 347.7408 | 150.8333 | 498.5741 | 791.5362 | 1
66 | 12 | 388 | 221 |  | -0.10179 | -0.25821 | -11.7709 | -5.0509 | 11.9158 | -0.022039 | 31.4778 | 340.8547 | 184.1667 | 525.0214 | 833.524 | 1
66 | 13 | 644 | 154 |  | -0.10179 | -0.25821 | -11.7709 | -5.0509 | 12.9158 | 0.23976 | 30.3355 | 548.9829 | 128.3333 | 677.3162 | 1075.3072 | 1
66 | 14 | 84 | 220 |  | -0.10179 | -0.25821 | -11.7709 | -5.0509 | 13.9158 | 0.50156 | 26.6174 | 64.3155 | 183.3333 | 247.6488 | 393.1672 | 1
66 | 15 | 325 | 178 |  | -0.10179 | -0.25821 | -11.7709 | -5.0509 | 14.9158 | 0.76336 | 20.7909 | 202.8046 | 148.3333 | 351.138 | 557.4666 | 1
66 | 16 | 146 | 133 |  | -0.10179 | -0.25821 | -11.7709 | -5.0509 | 15.9158 | 1.0252 | 13.426 | 63.8272 | 110.8333 | 174.6605 | 277.291 | 1
66 | 17 | 4 | 59 |  | -0.10179 | -0.25821 | -11.7709 | -5.0509 | 16.9158 | 1.287 | 5.0537 | 0.87147 | 49.1667 | 50.0381 | 79.4405 | 0
66 | 18 | 0 | 12 |  | -0.10179 | -0.25821 | -11.7709 | -5.0509 | 17.9158 | 1.5488 | -3.8716 | 0 | 10 | 10 | 15.876 | 0
66 | 19 | 0 | 0 |  | -0.10179 | -0.25821 | -11.7709 | -5.0509 | 18.9158 | 1.8106 | -12.9463 | 0 | 0 | 0 | 0 | 0
66 | 20 | 0 | 0 |  | -0.10179 | -0.25821 | -11.7709 | -5.0509 | 19.9158 | 2.0724 | -21.7645 | 0 | 0 | 0 | 0 | 0
66 | 21 | 0 | 0 |  | -0.10179 | -0.25821 | -11.7709 | -5.0509 | 20.9158 | 2.3342 | -29.8537 | 0 | 0 | 0 | 0 | 0
66 | 22 | 0 | 0 |  | -0.10179 | -0.25821 | -11.7709 | -5.0509 | 21.9158 | 2.596 | -36.6099 | 0 | 0 | 0 | 0 | 0
66 | 23 | 0 | 0 |  | -0.10179 | -0.25821 | -11.7709 | -5.0509 | 22.9158 | 2.8578 | -41.2852 | 0 | 0 | 0 | 0 | 0
66 | 24 | 0 | 0 |  | -0.10179 | -0.25821 | -11.7709 | -5.0509 | 23.9158 | 3.1196 | -43.1408 | 0 | 0 | 0 | 0 | 0
67 | 1 | 0 | 0 |  | -0.095123 | -0.241 | -11.5296 | -4.8096 | 0.91984 | -2.9008 | -41.4253 | 0 | 0 | 0 | 0 | 0
67 | 2 | 0 | 0 |  | -0.095123 | -0.241 | -11.5296 | -4.8096 | 1.9198 | -2.639 | -37.187 | 0 | 0 | 0 | 0 | 0
67 | 3 | 0 | 0 |  | -0.095123 | -0.241 | -11.5296 | -4.8096 | 2.9198 | -2.3772 | -30.7406 | 0 | 0 | 0 | 0 | 0
67 | 4 | 0 | 0 |  | -0.095123 | -0.241 | -11.5296 | -4.8096 | 3.9198 | -2.1154 | -22.8424 | 0 | 0 | 0 | 0 | 0
67 | 5 | 0 | 0 |  | -0.095123 | -0.241 | -11.5296 | -4.8096 | 4.9198 | -1.8536 | -14.119 | 0 | 0 | 0 | 0 | 0
67 | 6 | 0 | 0 |  | -0.095123 | -0.241 | -11.5296 | -4.8096 | 5.9198 | -1.5918 | -5.06 | 0 | 0 | 0 | 0 | 0
67 | 7 | 0 | 6 |  | -0.095123 | -0.241 | -11.5296 | -4.8096 | 6.9198 | -1.33 | 3.9223 | 0 | 5 | 5 | 7.938 | 0
67 | 8 | 0 | 51 |  | -0.095123 | -0.241 | -11.5296 | -4.8096 | 7.9198 | -1.0682 | 12.427 | 0 | 42.5 | 42.5 | 67.473 | 0
67 | 9 | 26 | 122 |  | -0.095123 | -0.241 | -11.5296 | -4.8096 | 8.9198 | -0.80638 | 20.0094 | 15.5762 | 101.6667 | 117.2429 | 186.1348 | 1
67 | 10 | 57 | 180 |  | -0.095123 | -0.241 | -11.5296 | -4.8096 | 9.9198 | -0.54458 | 26.1477 | 42.6936 | 150 | 192.6936 | 305.9204 | 1
67 | 11 | 53 | 232 |  | -0.095123 | -0.241 | -11.5296 | -4.8096 | 10.9198 | -0.28279 | 30.2664 | 44.8061 | 193.3333 | 238.1394 | 378.0701 | 1
67 | 12 | 57 | 259 |  | -0.095123 | -0.241 | -11.5296 | -4.8096 | 11.9198 | -0.020986 | 31.8609 | 50.2556 | 215.8333 | 266.0889 | 422.4427 | 1
67 | 13 | 56 | 260 |  | -0.095123 | -0.241 | -11.5296 | -4.8096 | 12.9198 | 0.24081 | 30.7022 | 47.901 | 216.6667 | 264.5677 | 420.0276 | 1
67 | 14 | 486 | 190 |  | -0.095123 | -0.241 | -11.5296 | -4.8096 | 13.9198 | 0.50261 | 26.9589 | 373.3865 | 158.3333 | 531.7199 | 844.1584 | 1
67 | 15 | 82 | 178 |  | -0.095123 | -0.241 | -11.5296 | -4.8096 | 14.9198 | 0.76441 | 21.1054 | 51.36 | 148.3333 | 199.6934 | 317.0332 | 1
67 | 16 | 59 | 123 |  | -0.095123 | -0.241 | -11.5296 | -4.8096 | 15.9198 | 1.0262 | 13.7172 | 25.9139 | 102.5 | 128.4139 | 203.8699 | 1
67 | 17 | 4 | 62 |  | -0.095123 | -0.241 | -11.5296 | -4.8096 | 16.9198 | 1.288 | 5.3287 | 0.87867 | 51.6667 | 52.5453 | 83.421 | 0
67 | 18 | 0 | 8 |  | -0.095123 | -0.241 | -11.5296 | -4.8096 | 17.9198 | 1.5498 | -3.6045 | 0 | 6.6667 | 6.6667 | 10.584 | 0
67 | 19 | 0 | 0 |  | -0.095123 | -0.241 | -11.5296 | -4.8096 | 18.9198 | 1.8116 | -12.6779 | 0 | 0 | 0 | 0 | 0
67 | 20 | 0 | 0 |  | -0.095123 | -0.241 | -11.5296 | -4.8096 | 19.9198 | 2.0734 | -21.4853 | 0 | 0 | 0 | 0 | 0
67 | 21 | 0 | 0 |  | -0.095123 | -0.241 | -11.5296 | -4.8096 | 20.9198 | 2.3352 | -29.5538 | 0 | 0 | 0 | 0 | 0
67 | 22 | 0 | 0 |  | -0.095123 | -0.241 | -11.5296 | -4.8096 | 21.9198 | 2.597 | -36.2816 | 0 | 0 | 0 | 0 | 0
67 | 23 | 0 | 0 |  | -0.095123 | -0.241 | -11.5296 | -4.8096 | 22.9198 | 2.8588 | -40.9263 | 0 | 0 | 0 | 0 | 0
67 | 24 | 0 | 0 |  | -0.095123 | -0.241 | -11.5296 | -4.8096 | 23.9198 | 3.1206 | -42.7598 | 0 | 0 | 0 | 0 | 0
68 | 1 | 0 | 0 |  | -0.088429 | -0.22378 | -11.2808 | -4.5608 | 0.92399 | -2.8997 | -41.037 | 0 | 0 | 0 | 0 | 0
68 | 2 | 0 | 0 |  | -0.088429 | -0.22378 | -11.2808 | -4.5608 | 1.924 | -2.6379 | -36.8074 | 0 | 0 | 0 | 0 | 0
68 | 3 | 0 | 0 |  | -0.088429 | -0.22378 | -11.2808 | -4.5608 | 2.924 | -2.3761 | -30.3755 | 0 | 0 | 0 | 0 | 0
68 | 4 | 0 | 0 |  | -0.088429 | -0.22378 | -11.2808 | -4.5608 | 3.924 | -2.1143 | -22.4904 | 0 | 0 | 0 | 0 | 0
68 | 5 | 0 | 0 |  | -0.088429 | -0.22378 | -11.2808 | -4.5608 | 4.924 | -1.8525 | -13.775 | 0 | 0 | 0 | 0 | 0
68 | 6 | 0 | 0 |  | -0.088429 | -0.22378 | -11.2808 | -4.5608 | 5.924 | -1.5907 | -4.7179 | 0 | 0 | 0 | 0 | 0
68 | 7 | 0 | 6 |  | -0.088429 | -0.22378 | -11.2808 | -4.5608 | 6.924 | -1.3289 | 4.2684 | 0 | 5 | 5 | 7.938 | 0
68 | 8 | 0 | 54 |  | -0.088429 | -0.22378 | -11.2808 | -4.5608 | 7.924 | -1.0671 | 12.7824 | 0 | 45 | 45 | 71.442 | 1
68 | 9 | 26 | 125 |  | -0.088429 | -0.22378 | -11.2808 | -4.5608 | 8.924 | -0.8053 | 20.3776 | 15.6719 | 104.1667 | 119.8386 | 190.2557 | 1
68 | 10 | 56 | 183 |  | -0.088429 | -0.22378 | -11.2808 | -4.5608 | 9.924 | -0.5435 | 26.5287 | 42.1446 | 152.5 | 194.6446 | 309.0177 | 1
68 | 11 | 53 | 235 |  | -0.088429 | -0.22378 | -11.2808 | -4.5608 | 10.924 | -0.2817 | 30.6546 | 44.9859 | 195.8333 | 240.8192 | 382.3245 | 1
68 | 12 | 10 | 177 |  | -0.088429 | -0.22378 | -11.2808 | -4.5608 | 11.924 | -0.0199 | 32.2453 | 8.8483 | 147.5 | 156.3483 | 248.2186 | 1
68 | 13 | 93 | 242 |  | -0.088429 | -0.22378 | -11.2808 | -4.5608 | 12.924 | 0.2419 | 31.0698 | 79.8179 | 201.6667 | 281.4845 | 446.8848 | 1
68 | 14 | 6 | 164 |  | -0.088429 | -0.22378 | -11.2808 | -4.5608 | 13.924 | 0.5037 | 27.3009 | 4.6252 | 136.6667 | 141.2919 | 224.315 | 1
68 | 15 | 0 | 134 |  | -0.088429 | -0.22378 | -11.2808 | -4.5608 | 14.924 | 0.7655 | 21.4199 | 0 | 111.6667 | 111.6667 | 177.282 | 1
68 | 16 | 0 | 90 |  | -0.088429 | -0.22378 | -11.2808 | -4.5608 | 15.924 | 1.0273 | 14.0084 | 0 | 75 | 75 | 119.07 | 1
68 | 17 | 0 | 40 |  | -0.088429 | -0.22378 | -11.2808 | -4.5608 | 16.924 | 1.2891 | 5.6035 | 0 | 33.3333 | 33.3333 | 52.92 | 0
68 | 18 | 0 | 9 |  | -0.088429 | -0.22378 | -11.2808 | -4.5608 | 17.924 | 1.5509 | -3.3374 | 0 | 7.5 | 7.5 | 11.907 | 0
68 | 19 | 0 | 0 |  | -0.088429 | -0.22378 | -11.2808 | -4.5608 | 18.924 | 1.8127 | -12.4093 | 0 | 0 | 0 | 0 | 0
68 | 20 | 0 | 0 |  | -0.088429 | -0.22378 | -11.2808 | -4.5608 | 19.924 | 2.0745 | -21.2055 | 0 | 0 | 0 | 0 | 0
68 | 21 | 0 | 0 |  | -0.088429 | -0.22378 | -11.2808 | -4.5608 | 20.924 | 2.3363 | -29.2532 | 0 | 0 | 0 | 0 | 0
68 | 22 | 0 | 0 |  | -0.088429 | -0.22378 | -11.2808 | -4.5608 | 21.924 | 2.5981 | -35.9522 | 0 | 0 | 0 | 0 | 0
68 | 23 | 0 | 0 |  | -0.088429 | -0.22378 | -11.2808 | -4.5608 | 22.924 | 2.8599 | -40.5662 | 0 | 0 | 0 | 0 | 0
68 | 24 | 0 | 0 |  | -0.088429 | -0.22378 | -11.2808 | -4.5608 | 23.924 | 3.1217 | -42.3773 | 0 | 0 | 0 | 0 | 0
69 | 1 | 0 | 0 |  | -0.081712 | -0.20657 | -11.0249 | -4.3049 | 0.92825 | -2.8986 | -40.6471 | 0 | 0 | 0 | 0 | 0
69 | 2 | 0 | 0 |  | -0.081712 | -0.20657 | -11.0249 | -4.3049 | 1.9283 | -2.6368 | -36.4259 | 0 | 0 | 0 | 0 | 0
69 | 3 | 0 | 0 |  | -0.081712 | -0.20657 | -11.0249 | -4.3049 | 2.9283 | -2.375 | -30.0082 | 0 | 0 | 0 | 0 | 0
69 | 4 | 0 | 0 |  | -0.081712 | -0.20657 | -11.0249 | -4.3049 | 3.9283 | -2.1132 | -22.1361 | 0 | 0 | 0 | 0 | 0
69 | 5 | 0 | 0 |  | -0.081712 | -0.20657 | -11.0249 | -4.3049 | 4.9283 | -1.8514 | -13.4287 | 0 | 0 | 0 | 0 | 0
69 | 6 | 0 | 0 |  | -0.081712 | -0.20657 | -11.0249 | -4.3049 | 5.9283 | -1.5896 | -4.3736 | 0 | 0 | 0 | 0 | 0
69 | 7 | 0 | 4 |  | -0.081712 | -0.20657 | -11.0249 | -4.3049 | 6.9283 | -1.3278 | 4.6167 | 0 | 3.3333 | 3.3333 | 5.292 | 0
69 | 8 | 0 | 36 |  | -0.081712 | -0.20657 | -11.0249 | -4.3049 | 7.9283 | -1.066 | 13.1399 | 0 | 30 | 30 | 47.628 | 1
69 | 9 | 44 | 123 |  | -0.081712 | -0.20657 | -11.0249 | -4.3049 | 8.9283 | -0.80418 | 20.7477 | 26.6839 | 102.5 | 129.1839 | 205.0923 | 1
69 | 10 | 58 | 186 |  | -0.081712 | -0.20657 | -11.0249 | -4.3049 | 9.9283 | -0.54238 | 26.9114 | 43.8563 | 155 | 198.8563 | 315.7043 | 1
69 | 11 | 489 | 191 |  | -0.081712 | -0.20657 | -11.0249 | -4.3049 | 10.9283 | -0.28058 | 31.0445 | 416.7067 | 159.1667 | 575.8733 | 914.2565 | 1
69 | 12 | 634 | 140 |  | -0.081712 | -0.20657 | -11.0249 | -4.3049 | 11.9283 | -0.018784 | 32.631 | 562.9668 | 116.6667 | 679.6334 | 1078.986 | 1
69 | 13 | 432 | 209 |  | -0.081712 | -0.20657 | -11.0249 | -4.3049 | 12.9283 | 0.24302 | 31.4382 | 371.996 | 174.1667 | 546.1626 | 867.0878 | 1
69 | 14 | 92 | 225 |  | -0.081712 | -0.20657 | -11.0249 | -4.3049 | 13.9283 | 0.50481 | 27.6431 | 71.1543 | 187.5 | 258.6543 | 410.6395 | 1
69 | 15 | 49 | 198 |  | -0.081712 | -0.20657 | -11.0249 | -4.3049 | 14.9283 | 0.76661 | 21.7344 | 30.913 | 165 | 195.913 | 311.0315 | 1
69 | 16 | 60 | 128 |  | -0.081712 | -0.20657 | -11.0249 | -4.3049 | 15.9283 | 1.0284 | 14.2993 | 26.5922 | 106.6667 | 133.2588 | 211.5617 | 1
69 | 17 | 5 | 66 |  | -0.081712 | -0.20657 | -11.0249 | -4.3049 | 16.9283 | 1.2902 | 5.8782 | 1.1159 | 55 | 56.1159 | 89.0896 | 0
69 | 18 | 0 | 10 |  | -0.081712 | -0.20657 | -11.0249 | -4.3049 | 17.9283 | 1.552 | -3.0703 | 0 | 8.3333 | 8.3333 | 13.23 | 0
69 | 19 | 0 | 0 |  | -0.081712 | -0.20657 | -11.0249 | -4.3049 | 18.9283 | 1.8138 | -12.1405 | 0 | 0 | 0 | 0 | 0
69 | 20 | 0 | 0 |  | -0.081712 | -0.20657 | -11.0249 | -4.3049 | 19.9283 | 2.0756 | -20.9252 | 0 | 0 | 0 | 0 | 0
69 | 21 | 0 | 0 |  | -0.081712 | -0.20657 | -11.0249 | -4.3049 | 20.9283 | 2.3374 | -28.9518 | 0 | 0 | 0 | 0 | 0
69 | 22 | 0 | 0 |  | -0.081712 | -0.20657 | -11.0249 | -4.3049 | 21.9283 | 2.5992 | -35.6219 | 0 | 0 | 0 | 0 | 0
69 | 23 | 0 | 0 |  | -0.081712 | -0.20657 | -11.0249 | -4.3049 | 22.9283 | 2.861 | -40.205 | 0 | 0 | 0 | 0 | 0
69 | 24 | 0 | 0 |  | -0.081712 | -0.20657 | -11.0249 | -4.3049 | 23.9283 | 3.1228 | -41.9935 | 0 | 0 | 0 | 0 | 0
70 | 1 | 0 | 0 |  | -0.074975 | -0.18936 | -10.7622 | -4.0422 | 0.93263 | -2.8974 | -40.2557 | 0 | 0 | 0 | 0 | 0
70 | 2 | 0 | 0 |  | -0.074975 | -0.18936 | -10.7622 | -4.0422 | 1.9326 | -2.6356 | -36.0425 | 0 | 0 | 0 | 0 | 0
70 | 3 | 0 | 0 |  | -0.074975 | -0.18936 | -10.7622 | -4.0422 | 2.9326 | -2.3738 | -29.6389 | 0 | 0 | 0 | 0 | 0
70 | 4 | 0 | 0 |  | -0.074975 | -0.18936 | -10.7622 | -4.0422 | 3.9326 | -2.112 | -21.7796 | 0 | 0 | 0 | 0 | 0
70 | 5 | 0 | 0 |  | -0.074975 | -0.18936 | -10.7622 | -4.0422 | 4.9326 | -1.8502 | -13.0803 | 0 | 0 | 0 | 0 | 0
70 | 6 | 0 | 0 |  | -0.074975 | -0.18936 | -10.7622 | -4.0422 | 5.9326 | -1.5884 | -4.0273 | 0 | 0 | 0 | 0 | 0
70 | 7 | 0 | 7 |  | -0.074975 | -0.18936 | -10.7622 | -4.0422 | 6.9326 | -1.3266 | 4.9669 | 0 | 5.8333 | 5.8333 | 9.261 | 0
70 | 8 | 6 | 59 |  | -0.074975 | -0.18936 | -10.7622 | -4.0422 | 7.9326 | -1.0648 | 13.4992 | 2.5022 | 49.1667 | 51.6689 | 82.0295 | 1
70 | 9 | 0 | 88 |  | -0.074975 | -0.18936 | -10.7622 | -4.0422 | 8.9326 | -0.80304 | 21.1196 | 0 | 73.3333 | 73.3333 | 116.424 | 1
70 | 10 | 0 | 134 |  | -0.074975 | -0.18936 | -10.7622 | -4.0422 | 9.9326 | -0.54124 | 27.2959 | 0 | 111.6667 | 111.6667 | 177.282 | 1
70 | 11 | 91 | 223 |  | -0.074975 | -0.18936 | -10.7622 | -4.0422 | 10.9326 | -0.27944 | 31.4359 | 77.8514 | 185.8333 | 263.6847 | 418.6258 | 1
70 | 12 | 11 | 181 |  | -0.074975 | -0.18936 | -10.7622 | -4.0422 | 11.9326 | -0.017638 | 33.0178 | 9.8016 | 150.8333 | 160.6349 | 255.024 | 1
70 | 13 | 6 | 185 |  | -0.074975 | -0.18936 | -10.7622 | -4.0422 | 12.9326 | 0.24416 | 31.8072 | 5.1835 | 154.1667 | 159.3501 | 252.9843 | 1
70 | 14 | 4 | 170 |  | -0.074975 | -0.18936 | -10.7622 | -4.0422 | 13.9326 | 0.50596 | 27.9855 | 3.1037 | 141.6667 | 144.7704 | 229.8374 | 1
70 | 15 | 0 | 139 |  | -0.074975 | -0.18936 | -10.7622 | -4.0422 | 14.9326 | 0.76776 | 22.0487 | 0 | 115.8333 | 115.8333 | 183.897 | 1
70 | 16 | 0 | 94 |  | -0.074975 | -0.18936 | -10.7622 | -4.0422 | 15.9326 | 1.0296 | 14.59 | 0 | 78.3333 | 78.3333 | 124.362 | 1
70 | 17 | 0 | 43 |  | -0.074975 | -0.18936 | -10.7622 | -4.0422 | 16.9326 | 1.2914 | 6.1527 | 0 | 35.8333 | 35.8333 | 56.889 | 0
70 | 18 | 0 | 6 |  | -0.074975 | -0.18936 | -10.7622 | -4.0422 | 17.9326 | 1.5532 | -2.8032 | 0 | 5 | 5 | 7.938 | 0
70 | 19 | 0 | 0 |  | -0.074975 | -0.18936 | -10.7622 | -4.0422 | 18.9326 | 1.815 | -11.8715 | 0 | 0 | 0 | 0 | 0
70 | 20 | 0 | 0 |  | -0.074975 | -0.18936 | -10.7622 | -4.0422 | 19.9326 | 2.0768 | -20.6445 | 0 | 0 | 0 | 0 | 0
70 | 21 | 0 | 0 |  | -0.074975 | -0.18936 | -10.7622 | -4.0422 | 20.9326 | 2.3386 | -28.6497 | 0 | 0 | 0 | 0 | 0
70 | 22 | 0 | 0 |  | -0.074975 | -0.18936 | -10.7622 | -4.0422 | 21.9326 | 2.6004 | -35.2905 | 0 | 0 | 0 | 0 | 0
70 | 23 | 0 | 0 |  | -0.074975 | -0.18936 | -10.7622 | -4.0422 | 22.9326 | 2.8622 | -39.8426 | 0 | 0 | 0 | 0 | 0
70 | 24 | 0 | 0 |  | -0.074975 | -0.18936 | -10.7622 | -4.0422 | 23.9326 | 3.124 | -41.6085 | 0 | 0 | 0 | 0 | 0
71 | 1 | 0 | 0 |  | -0.068219 | -0.17214 | -10.4931 | -3.7731 | 0.93711 | -2.8963 | -39.863 | 0 | 0 | 0 | 0 | 0
71 | 2 | 0 | 0 |  | -0.068219 | -0.17214 | -10.4931 | -3.7731 | 1.9371 | -2.6345 | -35.6575 | 0 | 0 | 0 | 0 | 0
71 | 3 | 0 | 0 |  | -0.068219 | -0.17214 | -10.4931 | -3.7731 | 2.9371 | -2.3727 | -29.2677 | 0 | 0 | 0 | 0 | 0
71 | 4 | 0 | 0 |  | -0.068219 | -0.17214 | -10.4931 | -3.7731 | 3.9371 | -2.1109 | -21.4211 | 0 | 0 | 0 | 0 | 0
71 | 5 | 0 | 0 |  | -0.068219 | -0.17214 | -10.4931 | -3.7731 | 4.9371 | -1.8491 | -12.7299 | 0 | 0 | 0 | 0 | 0
71 | 6 | 0 | 0 |  | -0.068219 | -0.17214 | -10.4931 | -3.7731 | 5.9371 | -1.5873 | -3.679 | 0 | 0 | 0 | 0 | 0
71 | 7 | 0 | 5 |  | -0.068219 | -0.17214 | -10.4931 | -3.7731 | 6.9371 | -1.3255 | 5.3189 | 0 | 4.1667 | 4.1667 | 6.615 | 0
71 | 8 | 0 | 39 |  | -0.068219 | -0.17214 | -10.4931 | -3.7731 | 7.9371 | -1.0637 | 13.8602 | 0 | 32.5 | 32.5 | 51.597 | 1
71 | 9 | 0 | 90 |  | -0.068219 | -0.17214 | -10.4931 | -3.7731 | 8.9371 | -0.80186 | 21.4931 | 0 | 75 | 75 | 119.07 | 1
71 | 10 | 0 | 136 |  | -0.068219 | -0.17214 | -10.4931 | -3.7731 | 9.9371 | -0.54006 | 27.6818 | 0 | 113.3333 | 113.3333 | 179.928 | 1
71 | 11 | 92 | 226 |  | -0.068219 | -0.17214 | -10.4931 | -3.7731 | 10.9371 | -0.27826 | 31.8286 | 79.0127 | 188.3333 | 267.3461 | 424.4386 | 1
71 | 12 | 57 | 272 |  | -0.068219 | -0.17214 | -10.4931 | -3.7731 | 11.9371 | -0.016463 | 33.4057 | 50.9647 | 226.6667 | 277.6314 | 440.7676 | 1
71 | 13 | 57 | 273 |  | -0.068219 | -0.17214 | -10.4931 | -3.7731 | 12.9371 | 0.24534 | 32.1768 | 49.4007 | 227.5 | 276.9007 | 439.6075 | 1
71 | 14 | 2 | 174 |  | -0.068219 | -0.17214 | -10.4931 | -3.7731 | 13.9371 | 0.50714 | 28.328 | 1.5568 | 145 | 146.5568 | 232.6735 | 1
71 | 15 | 0 | 142 |  | -0.068219 | -0.17214 | -10.4931 | -3.7731 | 14.9371 | 0.76893 | 22.3629 | 0 | 118.3333 | 118.3333 | 187.866 | 1
71 | 16 | 51 | 137 |  | -0.068219 | -0.17214 | -10.4931 | -3.7731 | 15.9371 | 1.0307 | 14.8803 | 22.7991 | 114.1667 | 136.9658 | 217.4469 | 1
71 | 17 | 5 | 71 |  | -0.068219 | -0.17214 | -10.4931 | -3.7731 | 16.9371 | 1.2925 | 6.4269 | 1.1329 | 59.1667 | 60.2995 | 95.7315 | 0
71 | 18 | 0 | 7 |  | -0.068219 | -0.17214 | -10.4931 | -3.7731 | 17.9371 | 1.5543 | -2.5363 | 0 | 5.8333 | 5.8333 | 9.261 | 0
71 | 19 | 0 | 0 |  | -0.068219 | -0.17214 | -10.4931 | -3.7731 | 18.9371 | 1.8161 | -11.6024 | 0 | 0 | 0 | 0 | 0
71 | 20 | 0 | 0 |  | -0.068219 | -0.17214 | -10.4931 | -3.7731 | 19.9371 | 2.0779 | -20.3634 | 0 | 0 | 0 | 0 | 0
71 | 21 | 0 | 0 |  | -0.068219 | -0.17214 | -10.4931 | -3.7731 | 20.9371 | 2.3397 | -28.3469 | 0 | 0 | 0 | 0 | 0
71 | 22 | 0 | 0 |  | -0.068219 | -0.17214 | -10.4931 | -3.7731 | 21.9371 | 2.6015 | -34.9583 | 0 | 0 | 0 | 0 | 0
71 | 23 | 0 | 0 |  | -0.068219 | -0.17214 | -10.4931 | -3.7731 | 22.9371 | 2.8633 | -39.4793 | 0 | 0 | 0 | 0 | 0
71 | 24 | 0 | 0 |  | -0.068219 | -0.17214 | -10.4931 | -3.7731 | 23.9371 | 3.1251 | -41.2224 | 0 | 0 | 0 | 0 | 0
72 | 1 | 0 | 0 |  | -0.061446 | -0.15493 | -10.2179 | -3.4979 | 0.9417 | -2.8951 | -39.4689 | 0 | 0 | 0 | 0 | 0
72 | 2 | 0 | 0 |  | -0.061446 | -0.15493 | -10.2179 | -3.4979 | 1.9417 | -2.6333 | -35.2708 | 0 | 0 | 0 | 0 | 0
72 | 3 | 0 | 0 |  | -0.061446 | -0.15493 | -10.2179 | -3.4979 | 2.9417 | -2.3715 | -28.8947 | 0 | 0 | 0 | 0 | 0
72 | 4 | 0 | 0 |  | -0.061446 | -0.15493 | -10.2179 | -3.4979 | 3.9417 | -2.1097 | -21.0608 | 0 | 0 | 0 | 0 | 0
72 | 5 | 0 | 0 |  | -0.061446 | -0.15493 | -10.2179 | -3.4979 | 4.9417 | -1.8479 | -12.3776 | 0 | 0 | 0 | 0 | 0
72 | 6 | 0 | 0 |  | -0.061446 | -0.15493 | -10.2179 | -3.4979 | 5.9417 | -1.5861 | -3.329 | 0 | 0 | 0 | 0 | 0
72 | 7 | 0 | 6 |  | -0.061446 | -0.15493 | -10.2179 | -3.4979 | 6.9417 | -1.3243 | 5.6726 | 0 | 5 | 5 | 7.938 | 0
72 | 8 | 0 | 42 |  | -0.061446 | -0.15493 | -10.2179 | -3.4979 | 7.9417 | -1.0625 | 14.2228 | 0 | 35 | 35 | 55.566 | 1
72 | 9 | 0 | 93 |  | -0.061446 | -0.15493 | -10.2179 | -3.4979 | 8.9417 | -0.80066 | 21.8681 | 0 | 77.5 | 77.5 | 123.039 | 1
72 | 10 | 0 | 139 |  | -0.061446 | -0.15493 | -10.2179 | -3.4979 | 9.9417 | -0.53886 | 28.0692 | 0 | 115.8333 | 115.8333 | 183.897 | 1
72 | 11 | 4 | 171 |  | -0.061446 | -0.15493 | -10.2179 | -3.4979 | 10.9417 | -0.27706 | 32.2226 | 3.4485 | 142.5 | 145.9485 | 231.7079 | 1
72 | 12 | 93 | 253 |  | -0.061446 | -0.15493 | -10.2179 | -3.4979 | 11.9417 | -0.015263 | 33.7946 | 83.4346 | 210.8333 | 294.268 | 467.1798 | 1
72 | 13 | 56 | 276 |  | -0.061446 | -0.15493 | -10.2179 | -3.4979 | 12.9417 | 0.24654 | 32.5469 | 48.6869 | 230 | 278.6869 | 442.4432 | 1
72 | 14 | 9 | 172 |  | -0.061446 | -0.15493 | -10.2179 | -3.4979 | 13.9417 | 0.50834 | 28.6706 | 7.0273 | 143.3333 | 150.3606 | 238.7125 | 1
72 | 15 | 0 | 143 |  | -0.061446 | -0.15493 | -10.2179 | -3.4979 | 14.9417 | 0.77014 | 22.6768 | 0 | 119.1667 | 119.1667 | 189.189 | 1
72 | 16 | 0 | 98 |  | -0.061446 | -0.15493 | -10.2179 | -3.4979 | 15.9417 | 1.0319 | 15.1703 | 0 | 81.6667 | 81.6667 | 129.654 | 1
72 | 17 | 0 | 47 |  | -0.061446 | -0.15493 | -10.2179 | -3.4979 | 16.9417 | 1.2937 | 6.7008 | 0 | 39.1667 | 39.1667 | 62.181 | 0
72 | 18 | 0 | 8 |  | -0.061446 | -0.15493 | -10.2179 | -3.4979 | 17.9417 | 1.5555 | -2.2695 | 0 | 6.6667 | 6.6667 | 10.584 | 0
72 | 19 | 0 | 0 |  | -0.061446 | -0.15493 | -10.2179 | -3.4979 | 18.9417 | 1.8173 | -11.3331 | 0 | 0 | 0 | 0 | 0
72 | 20 | 0 | 0 |  | -0.061446 | -0.15493 | -10.2179 | -3.4979 | 19.9417 | 2.0791 | -20.0819 | 0 | 0 | 0 | 0 | 0
72 | 21 | 0 | 0 |  | -0.061446 | -0.15493 | -10.2179 | -3.4979 | 20.9417 | 2.3409 | -28.0434 | 0 | 0 | 0 | 0 | 0
72 | 22 | 0 | 0 |  | -0.061446 | -0.15493 | -10.2179 | -3.4979 | 21.9417 | 2.6027 | -34.6253 | 0 | 0 | 0 | 0 | 0
72 | 23 | 0 | 0 |  | -0.061446 | -0.15493 | -10.2179 | -3.4979 | 22.9417 | 2.8645 | -39.115 | 0 | 0 | 0 | 0 | 0
72 | 24 | 0 | 0 |  | -0.061446 | -0.15493 | -10.2179 | -3.4979 | 23.9417 | 3.1263 | -40.8352 | 0 | 0 | 0 | 0 | 0
73 | 1 | 0 | 0 |  | -0.054657 | -0.13771 | -9.937 | -3.217 | 0.94638 | -2.8938 | -39.0738 | 0 | 0 | 0 | 0 | 0
73 | 2 | 0 | 0 |  | -0.054657 | -0.13771 | -9.937 | -3.217 | 1.9464 | -2.632 | -34.8828 | 0 | 0 | 0 | 0 | 0
73 | 3 | 0 | 0 |  | -0.054657 | -0.13771 | -9.937 | -3.217 | 2.9464 | -2.3702 | -28.52 | 0 | 0 | 0 | 0 | 0
73 | 4 | 0 | 0 |  | -0.054657 | -0.13771 | -9.937 | -3.217 | 3.9464 | -2.1084 | -20.6987 | 0 | 0 | 0 | 0 | 0
73 | 5 | 0 | 0 |  | -0.054657 | -0.13771 | -9.937 | -3.217 | 4.9464 | -1.8466 | -12.0237 | 0 | 0 | 0 | 0 | 0
73 | 6 | 0 | 0 |  | -0.054657 | -0.13771 | -9.937 | -3.217 | 5.9464 | -1.5848 | -2.9774 | 0 | 0 | 0 | 0 | 0
73 | 7 | 0 | 10 |  | -0.054657 | -0.13771 | -9.937 | -3.217 | 6.9464 | -1.323 | 6.0278 | 0 | 8.3333 | 8.3333 | 13.23 | 0
73 | 8 | 40 | 62 |  | -0.054657 | -0.13771 | -9.937 | -3.217 | 7.9464 | -1.0612 | 14.5868 | 17.1335 | 51.6667 | 68.8002 | 109.2272 | 1
73 | 9 | 42 | 138 |  | -0.054657 | -0.13771 | -9.937 | -3.217 | 8.9464 | -0.79944 | 22.2445 | 26.0896 | 115 | 141.0896 | 223.9939 | 1
73 | 10 | 79 | 191 |  | -0.054657 | -0.13771 | -9.937 | -3.217 | 9.9464 | -0.53764 | 28.4579 | 60.8502 | 159.1667 | 220.0169 | 349.2988 | 1
73 | 11 | 77 | 241 |  | -0.054657 | -0.13771 | -9.937 | -3.217 | 10.9464 | -0.27584 | 32.6177 | 66.6361 | 200.8333 | 267.4694 | 424.6344 | 1
73 | 12 | 57 | 279 |  | -0.054657 | -0.13771 | -9.937 | -3.217 | 11.9464 | -0.014037 | 34.1842 | 51.308 | 232.5 | 283.808 | 450.5735 | 1
73 | 13 | 79 | 268 |  | -0.054657 | -0.13771 | -9.937 | -3.217 | 12.9464 | 0.24776 | 32.9174 | 68.8957 | 223.3333 | 292.229 | 463.9428 | 1
73 | 14 | 55 | 256 |  | -0.054657 | -0.13771 | -9.937 | -3.217 | 13.9464 | 0.50956 | 29.0131 | 43.0753 | 213.3333 | 256.4087 | 407.0744 | 1
73 | 15 | 51 | 210 |  | -0.054657 | -0.13771 | -9.937 | -3.217 | 14.9464 | 0.77136 | 22.9903 | 32.6129 | 175 | 207.6129 | 329.6063 | 1
73 | 16 | 0 | 100 |  | -0.054657 | -0.13771 | -9.937 | -3.217 | 15.9464 | 1.0332 | 15.4599 | 0 | 83.3333 | 83.3333 | 132.3 | 1
73 | 17 | 0 | 48 |  | -0.054657 | -0.13771 | -9.937 | -3.217 | 16.9464 | 1.295 | 6.9744 | 0 | 40 | 40 | 63.504 | 0
73 | 18 | 0 | 8 |  | -0.054657 | -0.13771 | -9.937 | -3.217 | 17.9464 | 1.5568 | -2.0028 | 0 | 6.6667 | 6.6667 | 10.584 | 0
73 | 19 | 0 | 0 |  | -0.054657 | -0.13771 | -9.937 | -3.217 | 18.9464 | 1.8186 | -11.0637 | 0 | 0 | 0 | 0 | 0
73 | 20 | 0 | 0 |  | -0.054657 | -0.13771 | -9.937 | -3.217 | 19.9464 | 2.0804 | -19.7999 | 0 | 0 | 0 | 0 | 0
73 | 21 | 0 | 0 |  | -0.054657 | -0.13771 | -9.937 | -3.217 | 20.9464 | 2.3422 | -27.7393 | 0 | 0 | 0 | 0 | 0
73 | 22 | 0 | 0 |  | -0.054657 | -0.13771 | -9.937 | -3.217 | 21.9464 | 2.604 | -34.2914 | 0 | 0 | 0 | 0 | 0
73 | 23 | 0 | 0 |  | -0.054657 | -0.13771 | -9.937 | -3.217 | 22.9464 | 2.8658 | -38.7499 | 0 | 0 | 0 | 0 | 0
73 | 24 | 0 | 0 |  | -0.054657 | -0.13771 | -9.937 | -3.217 | 23.9464 | 3.1276 | -40.4471 | 0 | 0 | 0 | 0 | 0
74 | 1 | 0 | 0 |  | -0.047855 | -0.1205 | -9.6508 | -2.9308 | 0.95115 | -2.8926 | -38.6775 | 0 | 0 | 0 | 0 | 0
74 | 2 | 0 | 0 |  | -0.047855 | -0.1205 | -9.6508 | -2.9308 | 1.9512 | -2.6308 | -34.4935 | 0 | 0 | 0 | 0 | 0
74 | 3 | 0 | 0 |  | -0.047855 | -0.1205 | -9.6508 | -2.9308 | 2.9512 | -2.369 | -28.1439 | 0 | 0 | 0 | 0 | 0
74 | 4 | 0 | 0 |  | -0.047855 | -0.1205 | -9.6508 | -2.9308 | 3.9512 | -2.1072 | -20.3351 | 0 | 0 | 0 | 0 | 0
74 | 5 | 0 | 0 |  | -0.047855 | -0.1205 | -9.6508 | -2.9308 | 4.9512 | -1.8454 | -11.6682 | 0 | 0 | 0 | 0 | 0
74 | 6 | 0 | 0 |  | -0.047855 | -0.1205 | -9.6508 | -2.9308 | 5.9512 | -1.5836 | -2.6243 | 0 | 0 | 0 | 0 | 0
74 | 7 | 0 | 7 |  | -0.047855 | -0.1205 | -9.6508 | -2.9308 | 6.9512 | -1.3218 | 6.3844 | 0 | 5.8333 | 5.8333 | 9.261 | 0
74 | 8 | 0 | 45 |  | -0.047855 | -0.1205 | -9.6508 | -2.9308 | 7.9512 | -1.06 | 14.9521 | 0 | 37.5 | 37.5 | 59.535 | 1
74 | 9 | 0 | 96 |  | -0.047855 | -0.1205 | -9.6508 | -2.9308 | 8.9512 | -0.79819 | 22.6221 | 0 | 80 | 80 | 127.008 | 1
74 | 10 | 0 | 142 |  | -0.047855 | -0.1205 | -9.6508 | -2.9308 | 9.9512 | -0.53639 | 28.8477 | 0 | 118.3333 | 118.3333 | 187.866 | 1
74 | 11 | 4 | 175 |  | -0.047855 | -0.1205 | -9.6508 | -2.9308 | 10.9512 | -0.27459 | 33.0139 | 3.4746 | 145.8333 | 149.3079 | 237.0412 | 1
74 | 12 | 6 | 192 |  | -0.047855 | -0.1205 | -9.6508 | -2.9308 | 11.9512 | -0.012788 | 34.5747 | 5.4186 | 160 | 165.4186 | 262.6185 | 1
74 | 13 | 6 | 192 |  | -0.047855 | -0.1205 | -9.6508 | -2.9308 | 12.9512 | 0.24901 | 33.2882 | 5.2485 | 160 | 165.2485 | 262.3485 | 1
74 | 14 | 4 | 177 |  | -0.047855 | -0.1205 | -9.6508 | -2.9308 | 13.9512 | 0.51081 | 29.3555 | 3.1421 | 147.5 | 150.6421 | 239.1594 | 1
74 | 15 | 0 | 146 |  | -0.047855 | -0.1205 | -9.6508 | -2.9308 | 14.9512 | 0.77261 | 23.3035 | 0 | 121.6667 | 121.6667 | 193.158 | 1
74 | 16 | 0 | 100 |  | -0.047855 | -0.1205 | -9.6508 | -2.9308 | 15.9512 | 1.0344 | 15.7491 | 0 | 83.3333 | 83.3333 | 132.3 | 1
74 | 17 | 252 | 87 |  | -0.047855 | -0.1205 | -9.6508 | -2.9308 | 16.9512 | 1.2962 | 7.2476 | 58.3257 | 72.5 | 130.8257 | 207.6988 | 0
74 | 18 | 8 | 24 |  | -0.047855 | -0.1205 | -9.6508 | -2.9308 | 17.9512 | 1.558 | -1.7363 | 0 | 20 | 20 | 31.752 | 0
74 | 19 | 0 | 0 |  | -0.047855 | -0.1205 | -9.6508 | -2.9308 | 18.9512 | 1.8198 | -10.7943 | 0 | 0 | 0 | 0 | 0
74 | 20 | 0 | 0 |  | -0.047855 | -0.1205 | -9.6508 | -2.9308 | 19.9512 | 2.0816 | -19.5177 | 0 | 0 | 0 | 0 | 0
74 | 21 | 0 | 0 |  | -0.047855 | -0.1205 | -9.6508 | -2.9308 | 20.9512 | 2.3434 | -27.4346 | 0 | 0 | 0 | 0 | 0
74 | 22 | 0 | 0 |  | -0.047855 | -0.1205 | -9.6508 | -2.9308 | 21.9512 | 2.6052 | -33.9569 | 0 | 0 | 0 | 0 | 0
74 | 23 | 0 | 0 |  | -0.047855 | -0.1205 | -9.6508 | -2.9308 | 22.9512 | 2.867 | -38.3839 | 0 | 0 | 0 | 0 | 0
74 | 24 | 0 | 0 |  | -0.047855 | -0.1205 | -9.6508 | -2.9308 | 23.9512 | 3.1288 | -40.0582 | 0 | 0 | 0 | 0 | 0
75 | 1 | 0 | 0 |  | -0.041041 | -0.10329 | -9.3596 | -2.6396 | 0.95601 | -2.8913 | -38.2804 | 0 | 0 | 0 | 0 | 0
75 | 2 | 0 | 0 |  | -0.041041 | -0.10329 | -9.3596 | -2.6396 | 1.956 | -2.6295 | -34.103 | 0 | 0 | 0 | 0 | 0
75 | 3 | 0 | 0 |  | -0.041041 | -0.10329 | -9.3596 | -2.6396 | 2.956 | -2.3677 | -27.7664 | 0 | 0 | 0 | 0 | 0
75 | 4 | 0 | 0 |  | -0.041041 | -0.10329 | -9.3596 | -2.6396 | 3.956 | -2.1059 | -19.97 | 0 | 0 | 0 | 0 | 0
75 | 5 | 0 | 0 |  | -0.041041 | -0.10329 | -9.3596 | -2.6396 | 4.956 | -1.8441 | -11.3112 | 0 | 0 | 0 | 0 | 0
75 | 6 | 0 | 0 |  | -0.041041 | -0.10329 | -9.3596 | -2.6396 | 5.956 | -1.5823 | -2.2698 | 0 | 0 | 0 | 0 | 0
75 | 7 | 0 | 16 |  | -0.041041 | -0.10329 | -9.3596 | -2.6396 | 6.956 | -1.3205 | 6.7422 | 0 | 13.3333 | 13.3333 | 21.168 | 0
75 | 8 | 23 | 70 |  | -0.041041 | -0.10329 | -9.3596 | -2.6396 | 7.956 | -1.0587 | 15.3186 | 10.0257 | 58.3333 | 68.3591 | 108.5269 | 1
75 | 9 | 41 | 144 |  | -0.041041 | -0.10329 | -9.3596 | -2.6396 | 8.956 | -0.79692 | 23.0008 | 25.7688 | 120 | 145.7688 | 231.4226 | 1
75 | 10 | 59 | 205 |  | -0.041041 | -0.10329 | -9.3596 | -2.6396 | 9.956 | -0.53512 | 29.2386 | 45.855 | 170.8333 | 216.6883 | 344.0144 | 1
75 | 11 | 351 | 241 |  | -0.041041 | -0.10329 | -9.3596 | -2.6396 | 10.956 | -0.27332 | 33.411 | 306.0213 | 200.8333 | 506.8547 | 804.6825 | 1
75 | 12 | 11 | 193 |  | -0.041041 | -0.10329 | -9.3596 | -2.6396 | 11.956 | -0.011517 | 34.9657 | 9.9662 | 160.8333 | 170.7995 | 271.1613 | 1
75 | 13 | 9 | 194 |  | -0.041041 | -0.10329 | -9.3596 | -2.6396 | 12.956 | 0.25028 | 33.6593 | 7.8962 | 161.6667 | 169.5628 | 269.198 | 1
75 | 14 | 247 | 240 |  | -0.041041 | -0.10329 | -9.3596 | -2.6396 | 13.956 | 0.51208 | 29.6977 | 194.5918 | 200 | 394.5918 | 626.4539 | 1
75 | 15 | 77 | 202 |  | -0.041041 | -0.10329 | -9.3596 | -2.6396 | 14.956 | 0.77388 | 23.6163 | 49.5513 | 168.3333 | 217.8846 | 345.9136 | 1
75 | 16 | 0 | 103 |  | -0.041041 | -0.10329 | -9.3596 | -2.6396 | 15.956 | 1.0357 | 16.0378 | 0 | 85.8333 | 85.8333 | 136.269 | 1
75 | 17 | 0 | 51 |  | -0.041041 | -0.10329 | -9.3596 | -2.6396 | 16.956 | 1.2975 | 7.5205 | 0 | 42.5 | 42.5 | 67.473 | 0
75 | 18 | 0 | 9 |  | -0.041041 | -0.10329 | -9.3596 | -2.6396 | 17.956 | 1.5593 | -1.4699 | 0 | 7.5 | 7.5 | 11.907 | 0
75 | 19 | 0 | 0 |  | -0.041041 | -0.10329 | -9.3596 | -2.6396 | 18.956 | 1.8211 | -10.5248 | 0 | 0 | 0 | 0 | 0
75 | 20 | 0 | 0 |  | -0.041041 | -0.10329 | -9.3596 | -2.6396 | 19.956 | 2.0829 | -19.2351 | 0 | 0 | 0 | 0 | 0
75 | 21 | 0 | 0 |  | -0.041041 | -0.10329 | -9.3596 | -2.6396 | 20.956 | 2.3447 | -27.1294 | 0 | 0 | 0 | 0 | 0
75 | 22 | 0 | 0 |  | -0.041041 | -0.10329 | -9.3596 | -2.6396 | 21.956 | 2.6065 | -33.6216 | 0 | 0 | 0 | 0 | 0
75 | 23 | 0 | 0 |  | -0.041041 | -0.10329 | -9.3596 | -2.6396 | 22.956 | 2.8683 | -38.0173 | 0 | 0 | 0 | 0 | 0
75 | 24 | 0 | 0 |  | -0.041041 | -0.10329 | -9.3596 | -2.6396 | 23.956 | 3.1301 | -39.6685 | 0 | 0 | 0 | 0 | 0
76 | 1 | 0 | 0 |  | -0.034216 | -0.086071 | -9.0638 | -2.3438 | 0.96094 | -2.89 | -37.8825 | 0 | 0 | 0 | 0 | 0
76 | 2 | 0 | 0 |  | -0.034216 | -0.086071 | -9.0638 | -2.3438 | 1.9609 | -2.6282 | -33.7115 | 0 | 0 | 0 | 0 | 0
76 | 3 | 0 | 0 |  | -0.034216 | -0.086071 | -9.0638 | -2.3438 | 2.9609 | -2.3664 | -27.3877 | 0 | 0 | 0 | 0 | 0
76 | 4 | 0 | 0 |  | -0.034216 | -0.086071 | -9.0638 | -2.3438 | 3.9609 | -2.1046 | -19.6037 | 0 | 0 | 0 | 0 | 0
76 | 5 | 0 | 0 |  | -0.034216 | -0.086071 | -9.0638 | -2.3438 | 4.9609 | -1.8428 | -10.953 | 0 | 0 | 0 | 0 | 0
76 | 6 | 0 | 0 |  | -0.034216 | -0.086071 | -9.0638 | -2.3438 | 5.9609 | -1.581 | -1.9142 | 0 | 0 | 0 | 0 | 0
76 | 7 | 0 | 17 |  | -0.034216 | -0.086071 | -9.0638 | -2.3438 | 6.9609 | -1.3192 | 7.1012 | 0 | 14.1667 | 14.1667 | 22.491 | 0
76 | 8 | 230 | 87 |  | -0.034216 | -0.086071 | -9.0638 | -2.3438 | 7.9609 | -1.0574 | 15.6862 | 101.1275 | 72.5 | 173.6275 | 275.6509 | 1
76 | 9 | 341 | 124 |  | -0.034216 | -0.086071 | -9.0638 | -2.3438 | 8.9609 | -0.79563 | 23.3804 | 215.5642 | 103.3333 | 318.8976 | 506.2818 | 1
76 | 10 | 584 | 139 |  | -0.034216 | -0.086071 | -9.0638 | -2.3438 | 9.9609 | -0.53383 | 29.6304 | 455.8953 | 115.8333 | 571.7287 | 907.6764 | 1
76 | 11 | 728 | 109 |  | -0.034216 | -0.086071 | -9.0638 | -2.3438 | 10.9609 | -0.27203 | 33.8089 | 637.0246 | 90.8333 | 727.8579 | 1155.5472 | 1
76 | 12 | 419 | 236 |  | -0.034216 | -0.086071 | -9.0638 | -2.3438 | 11.9609 | -0.010227 | 35.3573 | 380.8265 | 196.6667 | 577.4932 | 916.8282 | 1
76 | 13 | 474 | 205 |  | -0.034216 | -0.086071 | -9.0638 | -2.3438 | 12.9609 | 0.25157 | 34.0304 | 417.0799 | 170.8333 | 587.9132 | 933.371 | 1
76 | 14 | 190 | 277 |  | -0.034216 | -0.086071 | -9.0638 | -2.3438 | 13.9609 | 0.51337 | 30.0397 | 150.1139 | 230.8333 | 380.9472 | 604.7918 | 1
76 | 15 | 140 | 245 |  | -0.034216 | -0.086071 | -9.0638 | -2.3438 | 14.9609 | 0.77517 | 23.9286 | 90.3686 | 204.1667 | 294.5352 | 467.6042 | 1
76 | 16 | 139 | 166 |  | -0.034216 | -0.086071 | -9.0638 | -2.3438 | 15.9609 | 1.037 | 16.3259 | 63.3866 | 138.3333 | 201.7199 | 320.2505 | 1
76 | 17 | 13 | 81 |  | -0.034216 | -0.086071 | -9.0638 | -2.3438 | 16.9609 | 1.2988 | 7.7929 | 3.0494 | 67.5 | 70.5494 | 112.0043 | 0
76 | 18 | 0 | 15 |  | -0.034216 | -0.086071 | -9.0638 | -2.3438 | 17.9609 | 1.5606 | -1.2038 | 0 | 12.5 | 12.5 | 19.845 | 0
76 | 19 | 0 | 0 |  | -0.034216 | -0.086071 | -9.0638 | -2.3438 | 18.9609 | 1.8224 | -10.2552 | 0 | 0 | 0 | 0 | 0
76 | 20 | 0 | 0 |  | -0.034216 | -0.086071 | -9.0638 | -2.3438 | 19.9609 | 2.0842 | -18.9522 | 0 | 0 | 0 | 0 | 0
76 | 21 | 0 | 0 |  | -0.034216 | -0.086071 | -9.0638 | -2.3438 | 20.9609 | 2.346 | -26.8236 | 0 | 0 | 0 | 0 | 0
76 | 22 | 0 | 0 |  | -0.034216 | -0.086071 | -9.0638 | -2.3438 | 21.9609 | 2.6078 | -33.2857 | 0 | 0 | 0 | 0 | 0
76 | 23 | 0 | 0 |  | -0.034216 | -0.086071 | -9.0638 | -2.3438 | 22.9609 | 2.8696 | -37.65 | 0 | 0 | 0 | 0 | 0
76 | 24 | 0 | 0 |  | -0.034216 | -0.086071 | -9.0638 | -2.3438 | 23.9609 | 3.1314 | -39.2781 | 0 | 0 | 0 | 0 | 0
77 | 1 | 0 | 0 |  | -0.027383 | -0.068857 | -8.7639 | -2.0439 | 0.96594 | -2.8887 | -37.4839 | 0 | 0 | 0 | 0 | 0
77 | 2 | 0 | 0 |  | -0.027383 | -0.068857 | -8.7639 | -2.0439 | 1.9659 | -2.6269 | -33.319 | 0 | 0 | 0 | 0 | 0
77 | 3 | 0 | 0 |  | -0.027383 | -0.068857 | -8.7639 | -2.0439 | 2.9659 | -2.3651 | -27.0079 | 0 | 0 | 0 | 0 | 0
77 | 4 | 0 | 0 |  | -0.027383 | -0.068857 | -8.7639 | -2.0439 | 3.9659 | -2.1033 | -19.2361 | 0 | 0 | 0 | 0 | 0
77 | 5 | 0 | 0 |  | -0.027383 | -0.068857 | -8.7639 | -2.0439 | 4.9659 | -1.8415 | -10.5937 | 0 | 0 | 0 | 0 | 0
77 | 6 | 0 | 0 |  | -0.027383 | -0.068857 | -8.7639 | -2.0439 | 5.9659 | -1.5797 | -1.5574 | 0 | 0 | 0 | 0 | 0
77 | 7 | 23 | 24 |  | -0.027383 | -0.068857 | -8.7639 | -2.0439 | 6.9659 | -1.3179 | 7.4611 | 5.0647 | 20 | 25.0647 | 39.7927 | 0
77 | 8 | 236 | 90 |  | -0.027383 | -0.068857 | -8.7639 | -2.0439 | 7.9659 | -1.0561 | 16.0546 | 104.6576 | 75 | 179.6576 | 285.2244 | 1
77 | 9 | 518 | 102 |  | -0.027383 | -0.068857 | -8.7639 | -2.0439 | 8.9659 | -0.79432 | 23.7609 | 329.3362 | 85 | 414.3362 | 657.8002 | 1
77 | 10 | 669 | 103 |  | -0.027383 | -0.068857 | -8.7639 | -2.0439 | 9.9659 | -0.53252 | 30.023 | 524.534 | 85.8333 | 610.3673 | 969.0192 | 1
77 | 11 | 407 | 218 |  | -0.027383 | -0.068857 | -8.7639 | -2.0439 | 10.9659 | -0.27072 | 34.2075 | 357.4184 | 181.6667 | 539.085 | 855.8514 | 1
77 | 12 | 602 | 176 |  | -0.027383 | -0.068857 | -8.7639 | -2.0439 | 11.9659 | -0.0089182 | 35.7494 | 548.8632 | 146.6667 | 695.5299 | 1104.2233 | 1
77 | 13 | 252 | 270 |  | -0.027383 | -0.068857 | -8.7639 | -2.0439 | 12.9659 | 0.25288 | 34.4016 | 222.3738 | 225 | 447.3738 | 710.2506 | 1
77 | 14 | 86 | 251 |  | -0.027383 | -0.068857 | -8.7639 | -2.0439 | 13.9659 | 0.51468 | 30.3813 | 68.1363 | 209.1667 | 277.3029 | 440.2461 | 1
77 | 15 | 71 | 211 |  | -0.027383 | -0.068857 | -8.7639 | -2.0439 | 14.9659 | 0.77648 | 24.2403 | 45.9666 | 175.8333 | 221.7999 | 352.1295 | 1
77 | 16 | 0 | 107 |  | -0.027383 | -0.068857 | -8.7639 | -2.0439 | 15.9659 | 1.0383 | 16.6135 | 0 | 89.1667 | 89.1667 | 141.561 | 1
77 | 17 | 0 | 54 |  | -0.027383 | -0.068857 | -8.7639 | -2.0439 | 16.9659 | 1.3001 | 8.0649 | 0 | 45 | 45 | 71.442 | 0
77 | 18 | 0 | 10 |  | -0.027383 | -0.068857 | -8.7639 | -2.0439 | 17.9659 | 1.5619 | -0.93794 | 0 | 8.3333 | 8.3333 | 13.23 | 0
77 | 19 | 0 | 0 |  | -0.027383 | -0.068857 | -8.7639 | -2.0439 | 18.9659 | 1.8237 | -9.9857 | 0 | 0 | 0 | 0 | 0
77 | 20 | 0 | 0 |  | -0.027383 | -0.068857 | -8.7639 | -2.0439 | 19.9659 | 2.0855 | -18.669 | 0 | 0 | 0 | 0 | 0
77 | 21 | 0 | 0 |  | -0.027383 | -0.068857 | -8.7639 | -2.0439 | 20.9659 | 2.3473 | -26.5174 | 0 | 0 | 0 | 0 | 0
77 | 22 | 0 | 0 |  | -0.027383 | -0.068857 | -8.7639 | -2.0439 | 21.9659 | 2.6091 | -32.9492 | 0 | 0 | 0 | 0 | 0
77 | 23 | 0 | 0 |  | -0.027383 | -0.068857 | -8.7639 | -2.0439 | 22.9659 | 2.8709 | -37.2821 | 0 | 0 | 0 | 0 | 0
77 | 24 | 0 | 0 |  | -0.027383 | -0.068857 | -8.7639 | -2.0439 | 23.9659 | 3.1327 | -38.8872 | 0 | 0 | 0 | 0 | 0
78 | 1 | 0 | 0 |  | -0.020543 | -0.051643 | -8.4601 | -1.7401 | 0.971 | -2.8874 | -37.0847 | 0 | 0 | 0 | 0 | 0
78 | 2 | 0 | 0 |  | -0.020543 | -0.051643 | -8.4601 | -1.7401 | 1.971 | -2.6256 | -32.9259 | 0 | 0 | 0 | 0 | 0
78 | 3 | 0 | 0 |  | -0.020543 | -0.051643 | -8.4601 | -1.7401 | 2.971 | -2.3638 | -26.6271 | 0 | 0 | 0 | 0 | 0
78 | 4 | 0 | 0 |  | -0.020543 | -0.051643 | -8.4601 | -1.7401 | 3.971 | -2.102 | -18.8676 | 0 | 0 | 0 | 0 | 0
78 | 5 | 0 | 0 |  | -0.020543 | -0.051643 | -8.4601 | -1.7401 | 4.971 | -1.8402 | -10.2333 | 0 | 0 | 0 | 0 | 0
78 | 6 | 0 | 0 |  | -0.020543 | -0.051643 | -8.4601 | -1.7401 | 5.971 | -1.5784 | -1.1998 | 0 | 0 | 0 | 0 | 0
78 | 7 | 0 | 10 |  | -0.020543 | -0.051643 | -8.4601 | -1.7401 | 6.971 | -1.3166 | 7.8219 | 0 | 8.3333 | 8.3333 | 13.23 | 0
78 | 8 | 0 | 53 |  | -0.020543 | -0.051643 | -8.4601 | -1.7401 | 7.971 | -1.0548 | 16.4237 | 0 | 44.1667 | 44.1667 | 70.119 | 1
78 | 9 | 0 | 105 |  | -0.020543 | -0.051643 | -8.4601 | -1.7401 | 8.971 | -0.79299 | 24.1421 | 0 | 87.5 | 87.5 | 138.915 | 1
78 | 10 | 0 | 151 |  | -0.020543 | -0.051643 | -8.4601 | -1.7401 | 9.971 | -0.53119 | 30.4163 | 0 | 125.8333 | 125.8333 | 199.773 | 1
78 | 11 | 88 | 247 |  | -0.020543 | -0.051643 | -8.4601 | -1.7401 | 10.971 | -0.26939 | 34.6067 | 77.5532 | 205.8333 | 283.3865 | 449.9044 | 1
78 | 12 | 8 | 199 |  | -0.020543 | -0.051643 | -8.4601 | -1.7401 | 11.971 | -0.0075928 | 36.1417 | 7.3162 | 165.8333 | 173.1496 | 274.8923 | 1
78 | 13 | 9 | 198 |  | -0.020543 | -0.051643 | -8.4601 | -1.7401 | 12.971 | 0.25421 | 34.7727 | 7.9642 | 165 | 172.9642 | 274.598 | 1
78 | 14 | 88 | 249 |  | -0.020543 | -0.051643 | -8.4601 | -1.7401 | 13.971 | 0.51601 | 30.7225 | 69.9114 | 207.5 | 277.4114 | 440.4183 | 1
78 | 15 | 2 | 152 |  | -0.020543 | -0.051643 | -8.4601 | -1.7401 | 14.971 | 0.77781 | 24.5514 | 1.2986 | 126.6667 | 127.9653 | 203.1577 | 1
78 | 16 | 0 | 107 |  | -0.020543 | -0.051643 | -8.4601 | -1.7401 | 15.971 | 1.0396 | 16.9005 | 0 | 89.1667 | 89.1667 | 141.561 | 1
78 | 17 | 0 | 55 |  | -0.020543 | -0.051643 | -8.4601 | -1.7401 | 16.971 | 1.3014 | 8.3364 | 0 | 45.8333 | 45.8333 | 72.765 | 0
78 | 18 | 0 | 17 |  | -0.020543 | -0.051643 | -8.4601 | -1.7401 | 17.971 | 1.5632 | -0.67232 | 0 | 14.1667 | 14.1667 | 22.491 | 0
78 | 19 | 0 | 0 |  | -0.020543 | -0.051643 | -8.4601 | -1.7401 | 18.971 | 1.825 | -9.7161 | 0 | 0 | 0 | 0 | 0
78 | 20 | 0 | 0 |  | -0.020543 | -0.051643 | -8.4601 | -1.7401 | 19.971 | 2.0868 | -18.3856 | 0 | 0 | 0 | 0 | 0
78 | 21 | 0 | 0 |  | -0.020543 | -0.051643 | -8.4601 | -1.7401 | 20.971 | 2.3486 | -26.2107 | 0 | 0 | 0 | 0 | 0
78 | 22 | 0 | 0 |  | -0.020543 | -0.051643 | -8.4601 | -1.7401 | 21.971 | 2.6104 | -32.6123 | 0 | 0 | 0 | 0 | 0
78 | 23 | 0 | 0 |  | -0.020543 | -0.051643 | -8.4601 | -1.7401 | 22.971 | 2.8722 | -36.9138 | 0 | 0 | 0 | 0 | 0
78 | 24 | 0 | 0 |  | -0.020543 | -0.051643 | -8.4601 | -1.7401 | 23.971 | 3.134 | -38.4958 | 0 | 0 | 0 | 0 | 0
79 | 1 | 0 | 0 |  | -0.013698 | -0.034428 | -8.153 | -1.433 | 0.97612 | -2.886 | -36.6851 | 0 | 0 | 0 | 0 | 0
79 | 2 | 0 | 0 |  | -0.013698 | -0.034428 | -8.153 | -1.433 | 1.9761 | -2.6242 | -32.532 | 0 | 0 | 0 | 0 | 0
79 | 3 | 0 | 0 |  | -0.013698 | -0.034428 | -8.153 | -1.433 | 2.9761 | -2.3624 | -26.2456 | 0 | 0 | 0 | 0 | 0
79 | 4 | 0 | 0 |  | -0.013698 | -0.034428 | -8.153 | -1.433 | 3.9761 | -2.1006 | -18.4982 | 0 | 0 | 0 | 0 | 0
79 | 5 | 0 | 0 |  | -0.013698 | -0.034428 | -8.153 | -1.433 | 4.9761 | -1.8388 | -9.8721 | 0 | 0 | 0 | 0 | 0
79 | 6 | 0 | 0 |  | -0.013698 | -0.034428 | -8.153 | -1.433 | 5.9761 | -1.577 | -0.84135 | 0 | 0 | 0 | 0 | 0
79 | 7 | 37 | 27 |  | -0.013698 | -0.034428 | -8.153 | -1.433 | 6.9761 | -1.3152 | 8.1833 | 8.4332 | 22.5 | 30.9332 | 49.1096 | 0
79 | 8 | 261 | 95 |  | -0.013698 | -0.034428 | -8.153 | -1.433 | 7.9761 | -1.0535 | 16.7935 | 117.7127 | 79.1667 | 196.8794 | 312.5657 | 1
79 | 9 | 510 | 109 |  | -0.013698 | -0.034428 | -8.153 | -1.433 | 8.9761 | -0.79165 | 24.5239 | 327.9267 | 90.8333 | 418.76 | 664.8234 | 1
79 | 10 | 684 | 111 |  | -0.013698 | -0.034428 | -8.153 | -1.433 | 9.9761 | -0.52985 | 30.8101 | 540.9082 | 92.5 | 633.4082 | 1005.5988 | 1
79 | 11 | 395 | 227 |  | -0.013698 | -0.034428 | -8.153 | -1.433 | 10.9761 | -0.26805 | 35.0063 | 349.3213 | 189.1667 | 538.4879 | 854.9035 | 1
79 | 12 | 454 | 218 |  | -0.013698 | -0.034428 | -8.153 | -1.433 | 11.9761 | -0.0062526 | 36.5343 | 416.448 | 181.6667 | 598.1147 | 949.5669 | 1
79 | 13 | 106 | 265 |  | -0.013698 | -0.034428 | -8.153 | -1.433 | 12.9761 | 0.25555 | 35.1437 | 94.0584 | 220.8333 | 314.8918 | 499.9222 | 1
79 | 14 | 53 | 272 |  | -0.013698 | -0.034428 | -8.153 | -1.433 | 13.9761 | 0.51735 | 31.0632 | 42.2182 | 226.6667 | 268.8849 | 426.8816 | 1
79 | 15 | 49 | 225 |  | -0.013698 | -0.034428 | -8.153 | -1.433 | 14.9761 | 0.77915 | 24.8619 | 31.9064 | 187.5 | 219.4064 | 348.3296 | 1
79 | 16 | 0 | 109 |  | -0.013698 | -0.034428 | -8.153 | -1.433 | 15.9761 | 1.0409 | 17.1868 | 0 | 90.8333 | 90.8333 | 144.207 | 1
79 | 17 | 0 | 57 |  | -0.013698 | -0.034428 | -8.153 | -1.433 | 16.9761 | 1.3027 | 8.6074 | 0 | 47.5 | 47.5 | 75.411 | 0
79 | 18 | 0 | 11 |  | -0.013698 | -0.034428 | -8.153 | -1.433 | 17.9761 | 1.5645 | -0.40699 | 0 | 9.1667 | 9.1667 | 14.553 | 0
79 | 19 | 0 | 0 |  | -0.013698 | -0.034428 | -8.153 | -1.433 | 18.9761 | 1.8263 | -9.4466 | 0 | 0 | 0 | 0 | 0
79 | 20 | 0 | 0 |  | -0.013698 | -0.034428 | -8.153 | -1.433 | 19.9761 | 2.0881 | -18.102 | 0 | 0 | 0 | 0 | 0
79 | 21 | 0 | 0 |  | -0.013698 | -0.034428 | -8.153 | -1.433 | 20.9761 | 2.3499 | -25.9037 | 0 | 0 | 0 | 0 | 0
79 | 22 | 0 | 0 |  | -0.013698 | -0.034428 | -8.153 | -1.433 | 21.9761 | 2.6117 | -32.2748 | 0 | 0 | 0 | 0 | 0
79 | 23 | 0 | 0 |  | -0.013698 | -0.034428 | -8.153 | -1.433 | 22.9761 | 2.8735 | -36.545 | 0 | 0 | 0 | 0 | 0
79 | 24 | 0 | 0 |  | -0.013698 | -0.034428 | -8.153 | -1.433 | 23.9761 | 3.1353 | -38.104 | 0 | 0 | 0 | 0 | 0
80 | 1 | 0 | 0 |  | -0.0068501 | -0.017214 | -7.8428 | -1.1228 | 0.98129 | -2.8847 | -36.2851 | 0 | 0 | 0 | 0 | 0
80 | 2 | 0 | 0 |  | -0.0068501 | -0.017214 | -7.8428 | -1.1228 | 1.9813 | -2.6229 | -32.1377 | 0 | 0 | 0 | 0 | 0
80 | 3 | 0 | 0 |  | -0.0068501 | -0.017214 | -7.8428 | -1.1228 | 2.9813 | -2.3611 | -25.8634 | 0 | 0 | 0 | 0 | 0
80 | 4 | 0 | 0 |  | -0.0068501 | -0.017214 | -7.8428 | -1.1228 | 3.9813 | -2.0993 | -18.1281 | 0 | 0 | 0 | 0 | 0
80 | 5 | 0 | 0 |  | -0.0068501 | -0.017214 | -7.8428 | -1.1228 | 4.9813 | -1.8375 | -9.5103 | 0 | 0 | 0 | 0 | 0
80 | 6 | 0 | 0 |  | -0.0068501 | -0.017214 | -7.8428 | -1.1228 | 5.9813 | -1.5757 | -0.4823 | 0 | 0 | 0 | 0 | 0
80 | 7 | 0 | 11 |  | -0.0068501 | -0.017214 | -7.8428 | -1.1228 | 6.9813 | -1.3139 | 8.5453 | 0 | 9.1667 | 9.1667 | 14.553 | 0
80 | 8 | 0 | 57 |  | -0.0068501 | -0.017214 | -7.8428 | -1.1228 | 7.9813 | -1.0521 | 17.1637 | 0 | 47.5 | 47.5 | 75.411 | 1
80 | 9 | 0 | 110 |  | -0.0068501 | -0.017214 | -7.8428 | -1.1228 | 8.9813 | -0.7903 | 24.9061 | 0 | 91.6667 | 91.6667 | 145.53 | 1
80 | 10 | 82 | 210 |  | -0.0068501 | -0.017214 | -7.8428 | -1.1228 | 9.9813 | -0.5285 | 31.2043 | 65.1185 | 175 | 240.1185 | 381.2122 | 1
80 | 11 | 53 | 274 |  | -0.0068501 | -0.017214 | -7.8428 | -1.1228 | 10.9813 | -0.2667 | 35.4063 | 47.0317 | 228.3333 | 275.365 | 437.1695 | 1
80 | 12 | 8 | 203 |  | -0.0068501 | -0.017214 | -7.8428 | -1.1228 | 11.9813 | -0.0048992 | 36.927 | 7.36 | 169.1667 | 176.5267 | 280.2537 | 1
80 | 13 | 106 | 268 |  | -0.0068501 | -0.017214 | -7.8428 | -1.1228 | 12.9813 | 0.2569 | 35.5145 | 94.3114 | 223.3333 | 317.6448 | 504.2928 | 1
80 | 14 | 53 | 275 |  | -0.0068501 | -0.017214 | -7.8428 | -1.1228 | 13.9813 | 0.5187 | 31.4034 | 42.3284 | 229.1667 | 271.495 | 431.0255 | 1
80 | 15 | 3 | 156 |  | -0.0068501 | -0.017214 | -7.8428 | -1.1228 | 14.9813 | 0.7805 | 25.1717 | 1.9589 | 130 | 131.9589 | 209.4979 | 1
80 | 16 | 59 | 155 |  | -0.0068501 | -0.017214 | -7.8428 | -1.1228 | 15.9813 | 1.0423 | 17.4724 | 27.293 | 129.1667 | 156.4597 | 248.3954 | 1
80 | 17 | 9 | 91 |  | -0.0068501 | -0.017214 | -7.8428 | -1.1228 | 16.9813 | 1.3041 | 8.8779 | 2.1647 | 75.8333 | 77.998 | 123.8297 | 0
80 | 18 | 0 | 19 |  | -0.0068501 | -0.017214 | -7.8428 | -1.1228 | 17.9813 | 1.5659 | -0.14195 | 0 | 15.8333 | 15.8333 | 25.137 | 0
80 | 19 | 0 | 0 |  | -0.0068501 | -0.017214 | -7.8428 | -1.1228 | 18.9813 | 1.8277 | -9.1771 | 0 | 0 | 0 | 0 | 0
80 | 20 | 0 | 0 |  | -0.0068501 | -0.017214 | -7.8428 | -1.1228 | 19.9813 | 2.0895 | -17.8182 | 0 | 0 | 0 | 0 | 0
80 | 21 | 0 | 0 |  | -0.0068501 | -0.017214 | -7.8428 | -1.1228 | 20.9813 | 2.3513 | -25.5963 | 0 | 0 | 0 | 0 | 0
80 | 22 | 0 | 0 |  | -0.0068501 | -0.017214 | -7.8428 | -1.1228 | 21.9813 | 2.6131 | -31.9369 | 0 | 0 | 0 | 0 | 0
80 | 23 | 0 | 0 |  | -0.0068501 | -0.017214 | -7.8428 | -1.1228 | 22.9813 | 2.8749 | -36.1759 | 0 | 0 | 0 | 0 | 0
80 | 24 | 0 | 0 |  | -0.0068501 | -0.017214 | -7.8428 | -1.1228 | 23.9813 | 3.1367 | -37.712 | 0 | 0 | 0 | 0 | 0
81 | 1 | 0 | 0 |  | 0 | 0 | -7.53 | -0.81 | 0.9865 | -2.8833 | -35.8849 | 0 | 0 | 0 | 0 | 0
81 | 2 | 0 | 0 |  | 0 | 0 | -7.53 | -0.81 | 1.9865 | -2.6215 | -31.743 | 0 | 0 | 0 | 0 | 0
81 | 3 | 0 | 0 |  | 0 | 0 | -7.53 | -0.81 | 2.9865 | -2.3597 | -25.4807 | 0 | 0 | 0 | 0 | 0
81 | 4 | 0 | 0 |  | 0 | 0 | -7.53 | -0.81 | 3.9865 | -2.0979 | -17.7574 | 0 | 0 | 0 | 0 | 0
81 | 5 | 0 | 0 |  | 0 | 0 | -7.53 | -0.81 | 4.9865 | -1.8361 | -9.1478 | 0 | 0 | 0 | 0 | 0
81 | 6 | 0 | 0 |  | 0 | 0 | -7.53 | -0.81 | 5.9865 | -1.5743 | -0.12277 | 0 | 0 | 0 | 0 | 0
81 | 7 | 43 | 31 |  | 0 | 0 | -7.53 | -0.81 | 6.9865 | -1.3125 | 8.9077 | 10.1331 | 25.8333 | 35.9665 | 57.1003 | 0
81 | 8 | 312 | 94 |  | 0 | 0 | -7.53 | -0.81 | 7.9865 | -1.0507 | 17.5342 | 143.0549 | 78.3333 | 221.3883 | 351.476 | 1
81 | 9 | 560 | 105 |  | 0 | 0 | -7.53 | -0.81 | 8.9865 | -0.78893 | 25.2885 | 364.0662 | 87.5 | 451.5662 | 716.9065 | 1
81 | 10 | 668 | 110 |  | 0 | 0 | -7.53 | -0.81 | 9.9865 | -0.52713 | 31.5987 | 532.6783 | 91.6667 | 624.3449 | 991.21 | 1
81 | 11 | 767 | 107 |  | 0 | 0 | -7.53 | -0.81 | 10.9865 | -0.26533 | 35.8065 | 682.9244 | 89.1667 | 772.0911 | 1225.7718 | 1
81 | 12 | 405 | 254 |  | 0 | 0 | -7.53 | -0.81 | 11.9865 | -0.0035343 | 37.3197 | 373.6801 | 211.6667 | 585.3468 | 929.2966 | 1
81 | 13 | 591 | 189 |  | 0 | 0 | -7.53 | -0.81 | 12.9865 | 0.25827 | 35.8849 | 527.2145 | 157.5 | 684.7145 | 1087.0527 | 1
81 | 14 | 712 | 125 |  | 0 | 0 | -7.53 | -0.81 | 13.9865 | 0.52006 | 31.743 | 570.0867 | 104.1667 | 674.2533 | 1070.4446 | 1
81 | 15 | 229 | 215 |  | 0 | 0 | -7.53 | -0.81 | 14.9865 | 0.78186 | 25.4807 | 149.9332 | 179.1667 | 329.0998 | 522.4789 | 1
81 | 16 | 61 | 157 |  | 0 | 0 | -7.53 | -0.81 | 15.9865 | 1.0437 | 17.7574 | 28.3136 | 130.8333 | 159.1469 | 252.6617 | 1
81 | 17 | 9 | 93 |  | 0 | 0 | -7.53 | -0.81 | 16.9865 | 1.3055 | 9.1478 | 2.1776 | 77.5 | 79.6776 | 126.4961 | 0
81 | 18 | 0 | 20 |  | 0 | 0 | -7.53 | -0.81 | 17.9865 | 1.5673 | 0.12277 | 0 | 16.6667 | 16.6667 | 26.46 | 0
81 | 19 | 0 | 0 |  | 0 | 0 | -7.53 | -0.81 | 18.9865 | 1.8291 | -8.9077 | 0 | 0 | 0 | 0 | 0
81 | 20 | 0 | 0 |  | 0 | 0 | -7.53 | -0.81 | 19.9865 | 2.0909 | -17.5342 | 0 | 0 | 0 | 0 | 0
81 | 21 | 0 | 0 |  | 0 | 0 | -7.53 | -0.81 | 20.9865 | 2.3527 | -25.2885 | 0 | 0 | 0 | 0 | 0
81 | 22 | 0 | 0 |  | 0 | 0 | -7.53 | -0.81 | 21.9865 | 2.6145 | -31.5987 | 0 | 0 | 0 | 0 | 0
81 | 23 | 0 | 0 |  | 0 | 0 | -7.53 | -0.81 | 22.9865 | 2.8763 | -35.8065 | 0 | 0 | 0 | 0 | 0
81 | 24 | 0 | 0 |  | 0 | 0 | -7.53 | -0.81 | 23.9865 | 3.1381 | -37.3197 | 0 | 0 | 0 | 0 | 0
82 | 1 | 0 | 0 |  | 0.0068501 | 0.017214 | -7.215 | -0.49496 | 0.99175 | -2.882 | -35.4846 | 0 | 0 | 0 | 0 | 0
82 | 2 | 0 | 0 |  | 0.0068501 | 0.017214 | -7.215 | -0.49496 | 1.9918 | -2.6202 | -31.348 | 0 | 0 | 0 | 0 | 0
82 | 3 | 0 | 0 |  | 0.0068501 | 0.017214 | -7.215 | -0.49496 | 2.9918 | -2.3584 | -25.0976 | 0 | 0 | 0 | 0 | 0
82 | 4 | 0 | 0 |  | 0.0068501 | 0.017214 | -7.215 | -0.49496 | 3.9918 | -2.0966 | -17.3862 | 0 | 0 | 0 | 0 | 0
82 | 5 | 0 | 0 |  | 0.0068501 | 0.017214 | -7.215 | -0.49496 | 4.9918 | -1.8348 | -8.785 | 0 | 0 | 0 | 0 | 0
82 | 6 | 0 | 0 |  | 0.0068501 | 0.017214 | -7.215 | -0.49496 | 5.9918 | -1.573 | 0.23711 | 0 | 0 | 0 | 0 | 0
82 | 7 | 0 | 28 |  | 0.0068501 | 0.017214 | -7.215 | -0.49496 | 6.9918 | -1.3112 | 9.2703 | 0 | 23.3333 | 23.3333 | 37.044 | 0
82 | 8 | 15 | 94 |  | 0.0068501 | 0.017214 | -7.215 | -0.49496 | 7.9918 | -1.0494 | 17.905 | 6.9336 | 78.3333 | 85.2669 | 135.3698 | 1
82 | 9 | 49 | 165 |  | 0.0068501 | 0.017214 | -7.215 | -0.49496 | 8.9918 | -0.78756 | 25.6712 | 32.0285 | 137.5 | 169.5285 | 269.1435 | 1
82 | 10 | 50 | 233 |  | 0.0068501 | 0.017214 | -7.215 | -0.49496 | 9.9918 | -0.52576 | 31.9934 | 40.0341 | 194.1667 | 234.2008 | 371.8172 | 1
82 | 11 | 100 | 255 |  | 0.0068501 | 0.017214 | -7.215 | -0.49496 | 10.9918 | -0.26396 | 36.2068 | 89.3336 | 212.5 | 301.8336 | 479.191 | 1
82 | 12 | 102 | 278 |  | 0.0068501 | 0.017214 | -7.215 | -0.49496 | 11.9918 | -0.0021597 | 37.7124 | 94.3796 | 231.6667 | 326.0463 | 517.6311 | 1
82 | 13 | 101 | 278 |  | 0.0068501 | 0.017214 | -7.215 | -0.49496 | 12.9918 | 0.25964 | 36.255 | 90.3311 | 231.6667 | 321.9978 | 511.2037 | 1
82 | 14 | 391 | 242 |  | 0.0068501 | 0.017214 | -7.215 | -0.49496 | 13.9918 | 0.52144 | 32.0819 | 313.8459 | 201.6667 | 515.5126 | 818.4278 | 1
82 | 15 | 213 | 226 |  | 0.0068501 | 0.017214 | -7.215 | -0.49496 | 14.9918 | 0.78324 | 25.7889 | 139.8263 | 188.3333 | 328.1597 | 520.9863 | 1
82 | 16 | 142 | 182 |  | 0.0068501 | 0.017214 | -7.215 | -0.49496 | 15.9918 | 1.045 | 18.0416 | 66.1282 | 151.6667 | 217.7948 | 345.7711 | 1
82 | 17 | 81 | 106 |  | 0.0068501 | 0.017214 | -7.215 | -0.49496 | 16.9918 | 1.3068 | 9.4172 | 19.7126 | 88.3333 | 108.0459 | 171.5337 | 0
82 | 18 | 29 | 35 |  | 0.0068501 | 0.017214 | -7.215 | -0.49496 | 17.9918 | 1.5686 | 0.38714 | 0.13438 | 29.1667 | 29.301 | 46.5183 | 0
82 | 19 | 0 | 0 |  | 0.0068501 | 0.017214 | -7.215 | -0.49496 | 18.9918 | 1.8304 | -8.6383 | 0 | 0 | 0 | 0 | 0
82 | 20 | 0 | 0 |  | 0.0068501 | 0.017214 | -7.215 | -0.49496 | 19.9918 | 2.0922 | -17.2501 | 0 | 0 | 0 | 0 | 0
82 | 21 | 0 | 0 |  | 0.0068501 | 0.017214 | -7.215 | -0.49496 | 20.9918 | 2.354 | -24.9805 | 0 | 0 | 0 | 0 | 0
82 | 22 | 0 | 0 |  | 0.0068501 | 0.017214 | -7.215 | -0.49496 | 21.9918 | 2.6158 | -31.2602 | 0 | 0 | 0 | 0 | 0
82 | 23 | 0 | 0 |  | 0.0068501 | 0.017214 | -7.215 | -0.49496 | 22.9918 | 2.8776 | -35.4369 | 0 | 0 | 0 | 0 | 0
82 | 24 | 0 | 0 |  | 0.0068501 | 0.017214 | -7.215 | -0.49496 | 23.9918 | 3.1394 | -36.9274 | 0 | 0 | 0 | 0 | 0
83 | 1 | 0 | 0 |  | 0.013698 | 0.034428 | -6.8981 | -0.17809 | 0.99703 | -2.8806 | -35.0843 | 0 | 0 | 0 | 0 | 0
83 | 2 | 0 | 0 |  | 0.013698 | 0.034428 | -6.8981 | -0.17809 | 1.997 | -2.6188 | -30.953 | 0 | 0 | 0 | 0 | 0
83 | 3 | 0 | 0 |  | 0.013698 | 0.034428 | -6.8981 | -0.17809 | 2.997 | -2.357 | -24.7143 | 0 | 0 | 0 | 0 | 0
83 | 4 | 0 | 0 |  | 0.013698 | 0.034428 | -6.8981 | -0.17809 | 3.997 | -2.0952 | -17.0148 | 0 | 0 | 0 | 0 | 0
83 | 5 | 0 | 0 |  | 0.013698 | 0.034428 | -6.8981 | -0.17809 | 4.997 | -1.8334 | -8.4218 | 0 | 0 | 0 | 0 | 0
83 | 6 | 0 | 0 |  | 0.013698 | 0.034428 | -6.8981 | -0.17809 | 5.997 | -1.5716 | 0.59717 | 0 | 0 | 0 | 0 | 0
83 | 7 | 0 | 24 |  | 0.013698 | 0.034428 | -6.8981 | -0.17809 | 6.997 | -1.3098 | 9.633 | 0 | 20 | 20 | 31.752 | 0
83 | 8 | 0 | 63 |  | 0.013698 | 0.034428 | -6.8981 | -0.17809 | 7.997 | -1.048 | 18.2757 | 0 | 52.5 | 52.5 | 83.349 | 1
83 | 9 | 0 | 116 |  | 0.013698 | 0.034428 | -6.8981 | -0.17809 | 8.997 | -0.78618 | 26.0538 | 0 | 96.6667 | 96.6667 | 153.468 | 1
83 | 10 | 2 | 162 |  | 0.013698 | 0.034428 | -6.8981 | -0.17809 | 9.997 | -0.52438 | 32.388 | 1.6078 | 135 | 136.6078 | 216.8786 | 1
83 | 11 | 286 | 240 |  | 0.013698 | 0.034428 | -6.8981 | -0.17809 | 10.997 | -0.26258 | 36.6071 | 256.3263 | 200 | 456.3263 | 724.4636 | 1
83 | 12 | 276 | 272 |  | 0.013698 | 0.034428 | -6.8981 | -0.17809 | 11.997 | -0.00077707 | 38.1049 | 256.0915 | 226.6667 | 482.7581 | 766.4268 | 1
83 | 13 | 163 | 344 |  | 0.013698 | 0.034428 | -6.8981 | -0.17809 | 12.997 | 0.26102 | 36.6245 | 146.1485 | 286.6667 | 432.8152 | 687.1374 | 1
83 | 14 | 92 | 264 |  | 0.013698 | 0.034428 | -6.8981 | -0.17809 | 13.997 | 0.52282 | 32.42 | 74.0253 | 220 | 294.0253 | 466.7946 | 1
83 | 15 | 73 | 227 |  | 0.013698 | 0.034428 | -6.8981 | -0.17809 | 14.997 | 0.78462 | 26.0963 | 48.0453 | 189.1667 | 237.212 | 376.5978 | 1
83 | 16 | 66 | 162 |  | 0.013698 | 0.034428 | -6.8981 | -0.17809 | 15.997 | 1.0464 | 18.325 | 30.8349 | 135 | 165.8349 | 263.2795 | 1
83 | 17 | 100 | 104 |  | 0.013698 | 0.034428 | -6.8981 | -0.17809 | 16.997 | 1.3082 | 9.6859 | 24.4757 | 86.6667 | 111.1424 | 176.4496 | 0
83 | 18 | 0 | 15 |  | 0.013698 | 0.034428 | -6.8981 | -0.17809 | 17.997 | 1.57 | 0.65116 | 0 | 12.5 | 12.5 | 19.845 | 0
83 | 19 | 0 | 0 |  | 0.013698 | 0.034428 | -6.8981 | -0.17809 | 18.997 | 1.8318 | -8.3691 | 0 | 0 | 0 | 0 | 0
83 | 20 | 0 | 0 |  | 0.013698 | 0.034428 | -6.8981 | -0.17809 | 19.997 | 2.0936 | -16.9659 | 0 | 0 | 0 | 0 | 0
83 | 21 | 0 | 0 |  | 0.013698 | 0.034428 | -6.8981 | -0.17809 | 20.997 | 2.3554 | -24.6723 | 0 | 0 | 0 | 0 | 0
83 | 22 | 0 | 0 |  | 0.013698 | 0.034428 | -6.8981 | -0.17809 | 21.997 | 2.6172 | -30.9215 | 0 | 0 | 0 | 0 | 0
83 | 23 | 0 | 0 |  | 0.013698 | 0.034428 | -6.8981 | -0.17809 | 22.997 | 2.879 | -35.0672 | 0 | 0 | 0 | 0 | 0
83 | 24 | 0 | 0 |  | 0.013698 | 0.034428 | -6.8981 | -0.17809 | 23.997 | 3.1408 | -36.5351 | 0 | 0 | 0 | 0 | 0
84 | 1 | 0 | 0 |  | 0.020543 | 0.051643 | -6.5798 | 0.14022 | 1.0023 | -2.8792 | -34.6842 | 0 | 0 | 0 | 0 | 0
84 | 2 | 0 | 0 |  | 0.020543 | 0.051643 | -6.5798 | 0.14022 | 2.0023 | -2.6174 | -30.5579 | 0 | 0 | 0 | 0 | 0
84 | 3 | 0 | 0 |  | 0.020543 | 0.051643 | -6.5798 | 0.14022 | 3.0023 | -2.3556 | -24.3309 | 0 | 0 | 0 | 0 | 0
84 | 4 | 0 | 0 |  | 0.020543 | 0.051643 | -6.5798 | 0.14022 | 4.0023 | -2.0938 | -16.6432 | 0 | 0 | 0 | 0 | 0
84 | 5 | 0 | 0 |  | 0.020543 | 0.051643 | -6.5798 | 0.14022 | 5.0023 | -1.832 | -8.0586 | 0 | 0 | 0 | 0 | 0
84 | 6 | 0 | 0 |  | 0.020543 | 0.051643 | -6.5798 | 0.14022 | 6.0023 | -1.5702 | 0.95729 | 0 | 0 | 0 | 0 | 0
84 | 7 | 0 | 17 |  | 0.020543 | 0.051643 | -6.5798 | 0.14022 | 7.0023 | -1.3084 | 9.9957 | 0 | 14.1667 | 14.1667 | 22.491 | 0
84 | 8 | 0 | 65 |  | 0.020543 | 0.051643 | -6.5798 | 0.14022 | 8.0023 | -1.0466 | 18.6464 | 0 | 54.1667 | 54.1667 | 85.995 | 1
84 | 9 | 0 | 119 |  | 0.020543 | 0.051643 | -6.5798 | 0.14022 | 9.0023 | -0.78479 | 26.4363 | 0 | 99.1667 | 99.1667 | 157.437 | 1
84 | 10 | 3 | 165 |  | 0.020543 | 0.051643 | -6.5798 | 0.14022 | 10.0023 | -0.52299 | 32.7826 | 2.4213 | 137.5 | 139.9213 | 222.139 | 1
84 | 11 | 9 | 195 |  | 0.020543 | 0.051643 | -6.5798 | 0.14022 | 11.0023 | -0.26119 | 37.0073 | 8.092 | 162.5 | 170.592 | 270.8319 | 1
84 | 12 | 108 | 280 |  | 0.020543 | 0.051643 | -6.5798 | 0.14022 | 12.0023 | 0.00061184 | 38.497 | 100.483 | 233.3333 | 333.8164 | 529.9669 | 1
84 | 13 | 539 | 230 |  | 0.020543 | 0.051643 | -6.5798 | 0.14022 | 13.0023 | 0.26241 | 36.9935 | 484.4639 | 191.6667 | 676.1305 | 1073.4248 | 1
84 | 14 | 632 | 148 |  | 0.020543 | 0.051643 | -6.5798 | 0.14022 | 14.0023 | 0.52421 | 32.7573 | 509.7255 | 123.3333 | 633.0589 | 1005.0442 | 1
84 | 15 | 515 | 161 |  | 0.020543 | 0.051643 | -6.5798 | 0.14022 | 15.0023 | 0.78601 | 26.4028 | 339.8031 | 134.1667 | 473.9698 | 752.4745 | 1
84 | 16 | 386 | 141 |  | 0.020543 | 0.051643 | -6.5798 | 0.14022 | 16.0023 | 1.0478 | 18.6075 | 180.9069 | 117.5 | 298.4069 | 473.7508 | 1
84 | 17 | 315 | 88 |  | 0.020543 | 0.051643 | -6.5798 | 0.14022 | 17.0023 | 1.3096 | 9.954 | 77.5311 | 73.3333 | 150.8644 | 239.5123 | 0
84 | 18 | 0 | 32 |  | 0.020543 | 0.051643 | -6.5798 | 0.14022 | 18.0023 | 1.5714 | 0.91479 | 0 | 26.6667 | 26.6667 | 42.336 | 0
84 | 19 | 0 | 1 |  | 0.020543 | 0.051643 | -6.5798 | 0.14022 | 19.0023 | 1.8332 | -8.1 | 0 | 0.83333 | 0.83333 | 1.323 | 0
84 | 20 | 0 | 0 |  | 0.020543 | 0.051643 | -6.5798 | 0.14022 | 20.0023 | 2.095 | -16.6817 | 0 | 0 | 0 | 0 | 0
84 | 21 | 0 | 0 |  | 0.020543 | 0.051643 | -6.5798 | 0.14022 | 21.0023 | 2.3568 | -24.3639 | 0 | 0 | 0 | 0 | 0
84 | 22 | 0 | 0 |  | 0.020543 | 0.051643 | -6.5798 | 0.14022 | 22.0023 | 2.6186 | -30.5826 | 0 | 0 | 0 | 0 | 0
84 | 23 | 0 | 0 |  | 0.020543 | 0.051643 | -6.5798 | 0.14022 | 23.0023 | 2.8804 | -34.6975 | 0 | 0 | 0 | 0 | 0
84 | 24 | 0 | 0 |  | 0.020543 | 0.051643 | -6.5798 | 0.14022 | 24.0023 | 3.1422 | -36.1429 | 0 | 0 | 0 | 0 | 0
85 | 1 | 0 | 0 |  | 0.027383 | 0.068857 | -6.2604 | 0.45958 | 1.0077 | -2.8778 | -34.2842 | 0 | 0 | 0 | 0 | 0
85 | 2 | 0 | 0 |  | 0.027383 | 0.068857 | -6.2604 | 0.45958 | 2.0077 | -2.616 | -30.163 | 0 | 0 | 0 | 0 | 0
85 | 3 | 0 | 0 |  | 0.027383 | 0.068857 | -6.2604 | 0.45958 | 3.0077 | -2.3542 | -23.9475 | 0 | 0 | 0 | 0 | 0
85 | 4 | 0 | 0 |  | 0.027383 | 0.068857 | -6.2604 | 0.45958 | 4.0077 | -2.0924 | -16.2717 | 0 | 0 | 0 | 0 | 0
85 | 5 | 0 | 0 |  | 0.027383 | 0.068857 | -6.2604 | 0.45958 | 5.0077 | -1.8306 | -7.6954 | 0 | 0 | 0 | 0 | 0
85 | 6 | 0 | 0 |  | 0.027383 | 0.068857 | -6.2604 | 0.45958 | 6.0077 | -1.5688 | 1.3173 | 0 | 0 | 0 | 0 | 0
85 | 7 | 0 | 18 |  | 0.027383 | 0.068857 | -6.2604 | 0.45958 | 7.0077 | -1.307 | 10.3582 | 0 | 15 | 15 | 23.814 | 0
85 | 8 | 0 | 68 |  | 0.027383 | 0.068857 | -6.2604 | 0.45958 | 8.0077 | -1.0452 | 19.0168 | 0 | 56.6667 | 56.6667 | 89.964 | 1
85 | 9 | 0 | 122 |  | 0.027383 | 0.068857 | -6.2604 | 0.45958 | 9.0077 | -0.78339 | 26.8186 | 0 | 101.6667 | 101.6667 | 161.406 | 1
85 | 10 | 3 | 168 |  | 0.027383 | 0.068857 | -6.2604 | 0.45958 | 10.0077 | -0.52159 | 33.1769 | 2.4307 | 140 | 142.4307 | 226.123 | 1
85 | 11 | 4 | 201 |  | 0.027383 | 0.068857 | -6.2604 | 0.45958 | 11.0077 | -0.25979 | 37.4072 | 3.6077 | 167.5 | 171.1077 | 271.6506 | 1
85 | 12 | 5 | 219 |  | 0.027383 | 0.068857 | -6.2604 | 0.45958 | 12.0077 | 0.0020053 | 38.8889 | 4.6644 | 182.5 | 187.1644 | 297.1422 | 1
85 | 13 | 5 | 288 |  | 0.027383 | 0.068857 | -6.2604 | 0.45958 | 13.0077 | 0.2638 | 37.3619 | 4.5049 | 240 | 244.5049 | 388.1759 | 1
85 | 14 | 7 | 228 |  | 0.027383 | 0.068857 | -6.2604 | 0.45958 | 14.0077 | 0.5256 | 33.0937 | 5.6587 | 190 | 195.6587 | 310.6278 | 1
85 | 15 | 1 | 168 |  | 0.027383 | 0.068857 | -6.2604 | 0.45958 | 15.0077 | 0.7874 | 26.7083 | 0.66143 | 140 | 140.6614 | 223.3141 | 1
85 | 16 | 0 | 121 |  | 0.027383 | 0.068857 | -6.2604 | 0.45958 | 16.0077 | 1.0492 | 18.8893 | 0 | 100.8333 | 100.8333 | 160.083 | 1
85 | 17 | 0 | 84 |  | 0.027383 | 0.068857 | -6.2604 | 0.45958 | 17.0077 | 1.311 | 10.2215 | 0 | 70 | 70 | 111.132 | 0
85 | 18 | 0 | 17 |  | 0.027383 | 0.068857 | -6.2604 | 0.45958 | 18.0077 | 1.5728 | 1.178 | 0 | 14.1667 | 14.1667 | 22.491 | 0
85 | 19 | 0 | 1 |  | 0.027383 | 0.068857 | -6.2604 | 0.45958 | 19.0077 | 1.8346 | -7.8311 | 0 | 0.83333 | 0.83333 | 1.323 | 0
85 | 20 | 0 | 0 |  | 0.027383 | 0.068857 | -6.2604 | 0.45958 | 20.0077 | 2.0964 | -16.3974 | 0 | 0 | 0 | 0 | 0
85 | 21 | 0 | 0 |  | 0.027383 | 0.068857 | -6.2604 | 0.45958 | 21.0077 | 2.3582 | -24.0553 | 0 | 0 | 0 | 0 | 0
85 | 22 | 0 | 0 |  | 0.027383 | 0.068857 | -6.2604 | 0.45958 | 22.0077 | 2.62 | -30.2436 | 0 | 0 | 0 | 0 | 0
85 | 23 | 0 | 0 |  | 0.027383 | 0.068857 | -6.2604 | 0.45958 | 23.0077 | 2.8818 | -34.3279 | 0 | 0 | 0 | 0 | 0
85 | 24 | 0 | 0 |  | 0.027383 | 0.068857 | -6.2604 | 0.45958 | 24.0077 | 3.1436 | -35.751 | 0 | 0 | 0 | 0 | 0
86 | 1 | 0 | 0 |  | 0.034216 | 0.086071 | -5.9404 | 0.77959 | 1.013 | -2.8764 | -33.8847 | 0 | 0 | 0 | 0 | 0
86 | 2 | 0 | 0 |  | 0.034216 | 0.086071 | -5.9404 | 0.77959 | 2.013 | -2.6146 | -29.7684 | 0 | 0 | 0 | 0 | 0
86 | 3 | 0 | 0 |  | 0.034216 | 0.086071 | -5.9404 | 0.77959 | 3.013 | -2.3528 | -23.5643 | 0 | 0 | 0 | 0 | 0
86 | 4 | 0 | 0 |  | 0.034216 | 0.086071 | -5.9404 | 0.77959 | 4.013 | -2.091 | -15.9002 | 0 | 0 | 0 | 0 | 0
86 | 5 | 0 | 0 |  | 0.034216 | 0.086071 | -5.9404 | 0.77959 | 5.013 | -1.8292 | -7.3323 | 0 | 0 | 0 | 0 | 0
86 | 6 | 0 | 1 |  | 0.034216 | 0.086071 | -5.9404 | 0.77959 | 6.013 | -1.5674 | 1.6771 | 0 | 0.83333 | 0.83333 | 1.323 | 0
86 | 7 | 0 | 31 |  | 0.034216 | 0.086071 | -5.9404 | 0.77959 | 7.013 | -1.3056 | 10.7204 | 0 | 25.8333 | 25.8333 | 41.013 | 0
86 | 8 | 0 | 70 |  | 0.034216 | 0.086071 | -5.9404 | 0.77959 | 8.013 | -1.0438 | 19.3868 | 0 | 58.3333 | 58.3333 | 92.61 | 1
86 | 9 | 9 | 147 |  | 0.034216 | 0.086071 | -5.9404 | 0.77959 | 9.013 | -0.782 | 27.2004 | 6.0071 | 122.5 | 128.5071 | 204.0178 | 1
86 | 10 | 10 | 236 |  | 0.034216 | 0.086071 | -5.9404 | 0.77959 | 10.013 | -0.5202 | 33.5708 | 8.1334 | 196.6667 | 204.8001 | 325.1407 | 1
86 | 11 | 73 | 283 |  | 0.034216 | 0.086071 | -5.9404 | 0.77959 | 11.013 | -0.2584 | 37.8068 | 66.0438 | 235.8333 | 301.8771 | 479.2601 | 1
86 | 12 | 111 | 321 |  | 0.034216 | 0.086071 | -5.9404 | 0.77959 | 12.013 | 0.0034016 | 39.2802 | 103.8203 | 267.5 | 371.3203 | 589.5081 | 1
86 | 13 | 153 | 327 |  | 0.034216 | 0.086071 | -5.9404 | 0.77959 | 13.013 | 0.2652 | 37.7295 | 138.1721 | 272.5 | 410.6721 | 651.983 | 1
86 | 14 | 267 | 259 |  | 0.034216 | 0.086071 | -5.9404 | 0.77959 | 14.013 | 0.527 | 33.4292 | 216.3255 | 215.8333 | 432.1589 | 686.0954 | 1
86 | 15 | 527 | 169 |  | 0.034216 | 0.086071 | -5.9404 | 0.77959 | 15.013 | 0.7888 | 27.0128 | 349.409 | 140.8333 | 490.2423 | 778.3087 | 1
86 | 16 | 489 | 138 |  | 0.034216 | 0.086071 | -5.9404 | 0.77959 | 16.013 | 1.0506 | 19.1701 | 230.582 | 115 | 345.582 | 548.646 | 1
86 | 17 | 230 | 100 |  | 0.034216 | 0.086071 | -5.9404 | 0.77959 | 17.013 | 1.3124 | 10.4883 | 57.2297 | 83.3333 | 140.5631 | 223.1579 | 0
86 | 18 | 0 | 37 |  | 0.034216 | 0.086071 | -5.9404 | 0.77959 | 18.013 | 1.5742 | 1.4408 | 0 | 30.8333 | 30.8333 | 48.951 | 0
86 | 19 | 0 | 1 |  | 0.034216 | 0.086071 | -5.9404 | 0.77959 | 19.013 | 1.836 | -7.5624 | 0 | 0.83333 | 0.83333 | 1.323 | 0
86 | 20 | 0 | 0 |  | 0.034216 | 0.086071 | -5.9404 | 0.77959 | 20.013 | 2.0978 | -16.113 | 0 | 0 | 0 | 0 | 0
86 | 21 | 0 | 0 |  | 0.034216 | 0.086071 | -5.9404 | 0.77959 | 21.013 | 2.3596 | -23.7467 | 0 | 0 | 0 | 0 | 0
86 | 22 | 0 | 0 |  | 0.034216 | 0.086071 | -5.9404 | 0.77959 | 22.013 | 2.6214 | -29.9045 | 0 | 0 | 0 | 0 | 0
86 | 23 | 0 | 0 |  | 0.034216 | 0.086071 | -5.9404 | 0.77959 | 23.013 | 2.8832 | -33.9583 | 0 | 0 | 0 | 0 | 0
86 | 24 | 0 | 0 |  | 0.034216 | 0.086071 | -5.9404 | 0.77959 | 24.013 | 3.145 | -35.3593 | 0 | 0 | 0 | 0 | 0
87 | 1 | 0 | 0 |  | 0.041041 | 0.10329 | -5.6201 | 1.0999 | 1.0183 | -2.875 | -33.4856 | 0 | 0 | 0 | 0 | 0
87 | 2 | 0 | 0 |  | 0.041041 | 0.10329 | -5.6201 | 1.0999 | 2.0183 | -2.6132 | -29.3742 | 0 | 0 | 0 | 0 | 0
87 | 3 | 0 | 0 |  | 0.041041 | 0.10329 | -5.6201 | 1.0999 | 3.0183 | -2.3514 | -23.1815 | 0 | 0 | 0 | 0 | 0
87 | 4 | 0 | 0 |  | 0.041041 | 0.10329 | -5.6201 | 1.0999 | 4.0183 | -2.0896 | -15.5291 | 0 | 0 | 0 | 0 | 0
87 | 5 | 0 | 0 |  | 0.041041 | 0.10329 | -5.6201 | 1.0999 | 5.0183 | -1.8278 | -6.9696 | 0 | 0 | 0 | 0 | 0
87 | 6 | 0 | 2 |  | 0.041041 | 0.10329 | -5.6201 | 1.0999 | 6.0183 | -1.566 | 2.0365 | 0 | 1.6667 | 1.6667 | 2.646 | 0
87 | 7 | 71 | 46 |  | 0.041041 | 0.10329 | -5.6201 | 1.0999 | 7.0183 | -1.3042 | 11.0821 | 18.3674 | 38.3333 | 56.7007 | 90.018 | 0
87 | 8 | 96 | 122 |  | 0.041041 | 0.10329 | -5.6201 | 1.0999 | 8.0183 | -1.0424 | 19.7563 | 46.137 | 101.6667 | 147.8037 | 234.6532 | 1
87 | 9 | 92 | 203 |  | 0.041041 | 0.10329 | -5.6201 | 1.0999 | 9.0183 | -0.7806 | 27.5817 | 61.7154 | 169.1667 | 230.8821 | 366.5484 | 1
87 | 10 | 88 | 254 |  | 0.041041 | 0.10329 | -5.6201 | 1.0999 | 10.0183 | -0.5188 | 33.9643 | 71.8439 | 211.6667 | 283.5106 | 450.1014 | 1
87 | 11 | 14 | 219 |  | 0.041041 | 0.10329 | -5.6201 | 1.0999 | 11.0183 | -0.257 | 38.2059 | 12.7041 | 182.5 | 195.2041 | 309.9061 | 1
87 | 12 | 3 | 225 |  | 0.041041 | 0.10329 | -5.6201 | 1.0999 | 12.0183 | 0.004799 | 39.6709 | 2.8131 | 187.5 | 190.3131 | 302.1411 | 1
87 | 13 | 12 | 271 |  | 0.041041 | 0.10329 | -5.6201 | 1.0999 | 13.0183 | 0.2666 | 38.0963 | 10.8618 | 225.8333 | 236.6951 | 375.7772 | 1
87 | 14 | 3 | 203 |  | 0.041041 | 0.10329 | -5.6201 | 1.0999 | 14.0183 | 0.5284 | 33.7637 | 2.436 | 169.1667 | 171.6026 | 272.4363 | 1
87 | 15 | 103 | 232 |  | 0.041041 | 0.10329 | -5.6201 | 1.0999 | 15.0183 | 0.7902 | 27.3163 | 68.45 | 193.3333 | 261.7833 | 415.6072 | 1
87 | 16 | 61 | 190 |  | 0.041041 | 0.10329 | -5.6201 | 1.0999 | 16.0183 | 1.052 | 19.4501 | 28.8488 | 158.3333 | 187.1821 | 297.1704 | 1
87 | 17 | 5 | 97 |  | 0.041041 | 0.10329 | -5.6201 | 1.0999 | 17.0183 | 1.3138 | 10.7544 | 1.2507 | 80.8333 | 82.0841 | 130.3167 | 0
87 | 18 | 0 | 26 |  | 0.041041 | 0.10329 | -5.6201 | 1.0999 | 18.0183 | 1.5756 | 1.7032 | 0 | 21.6667 | 21.6667 | 34.398 | 0
87 | 19 | 0 | 2 |  | 0.041041 | 0.10329 | -5.6201 | 1.0999 | 19.0183 | 1.8374 | -7.2939 | 0 | 1.6667 | 1.6667 | 2.646 | 0
87 | 20 | 0 | 0 |  | 0.041041 | 0.10329 | -5.6201 | 1.0999 | 20.0183 | 2.0992 | -15.8287 | 0 | 0 | 0 | 0 | 0
87 | 21 | 0 | 0 |  | 0.041041 | 0.10329 | -5.6201 | 1.0999 | 21.0183 | 2.361 | -23.4379 | 0 | 0 | 0 | 0 | 0
87 | 22 | 0 | 0 |  | 0.041041 | 0.10329 | -5.6201 | 1.0999 | 22.0183 | 2.6228 | -29.5655 | 0 | 0 | 0 | 0 | 0
87 | 23 | 0 | 0 |  | 0.041041 | 0.10329 | -5.6201 | 1.0999 | 23.0183 | 2.8846 | -33.589 | 0 | 0 | 0 | 0 | 0
87 | 24 | 0 | 0 |  | 0.041041 | 0.10329 | -5.6201 | 1.0999 | 24.0183 | 3.1464 | -34.9681 | 0 | 0 | 0 | 0 | 0
88 | 1 | 0 | 0 |  | 0.047855 | 0.1205 | -5.3 | 1.42 | 1.0237 | -2.8736 | -33.0871 | 0 | 0 | 0 | 0 | 0
88 | 2 | 0 | 0 |  | 0.047855 | 0.1205 | -5.3 | 1.42 | 2.0237 | -2.6118 | -28.9805 | 0 | 0 | 0 | 0 | 0
88 | 3 | 0 | 0 |  | 0.047855 | 0.1205 | -5.3 | 1.42 | 3.0237 | -2.35 | -22.799 | 0 | 0 | 0 | 0 | 0
88 | 4 | 0 | 0 |  | 0.047855 | 0.1205 | -5.3 | 1.42 | 4.0237 | -2.0882 | -15.1584 | 0 | 0 | 0 | 0 | 0
88 | 5 | 0 | 0 |  | 0.047855 | 0.1205 | -5.3 | 1.42 | 5.0237 | -1.8264 | -6.6073 | 0 | 0 | 0 | 0 | 0
88 | 6 | 0 | 2 |  | 0.047855 | 0.1205 | -5.3 | 1.42 | 6.0237 | -1.5646 | 2.3954 | 0 | 1.6667 | 1.6667 | 2.646 | 0
88 | 7 | 81 | 49 |  | 0.047855 | 0.1205 | -5.3 | 1.42 | 7.0237 | -1.3028 | 11.4433 | 21.2615 | 40.8333 | 62.0949 | 98.5818 | 0
88 | 8 | 137 | 112 |  | 0.047855 | 0.1205 | -5.3 | 1.42 | 8.0237 | -1.041 | 20.1252 | 66.334 | 93.3333 | 159.6673 | 253.4878 | 1
88 | 9 | 176 | 189 |  | 0.047855 | 0.1205 | -5.3 | 1.42 | 9.0237 | -0.7792 | 27.9624 | 118.6507 | 157.5 | 276.1507 | 438.4168 | 1
88 | 10 | 168 | 270 |  | 0.047855 | 0.1205 | -5.3 | 1.42 | 10.0237 | -0.5174 | 34.3571 | 137.6639 | 225 | 362.6639 | 575.7652 | 1
88 | 11 | 90 | 279 |  | 0.047855 | 0.1205 | -5.3 | 1.42 | 11.0237 | -0.2556 | 38.6044 | 81.9107 | 232.5 | 314.4107 | 499.1584 | 1
88 | 12 | 102 | 295 |  | 0.047855 | 0.1205 | -5.3 | 1.42 | 12.0237 | 0.0061959 | 40.061 | 95.8845 | 245.8333 | 341.7178 | 542.5112 | 1
88 | 13 | 101 | 295 |  | 0.047855 | 0.1205 | -5.3 | 1.42 | 13.0237 | 0.268 | 38.4622 | 91.6235 | 245.8333 | 337.4568 | 535.7464 | 1
88 | 14 | 100 | 271 |  | 0.047855 | 0.1205 | -5.3 | 1.42 | 14.0237 | 0.52979 | 34.0971 | 81.3718 | 225.8333 | 307.2051 | 487.7188 | 1
88 | 15 | 51 | 249 |  | 0.047855 | 0.1205 | -5.3 | 1.42 | 15.0237 | 0.79159 | 27.6187 | 33.9699 | 207.5 | 241.4699 | 383.3576 | 1
88 | 16 | 0 | 125 |  | 0.047855 | 0.1205 | -5.3 | 1.42 | 16.0237 | 1.0534 | 19.7291 | 0 | 104.1667 | 104.1667 | 165.375 | 1
88 | 17 | 0 | 93 |  | 0.047855 | 0.1205 | -5.3 | 1.42 | 17.0237 | 1.3152 | 11.0198 | 0 | 77.5 | 77.5 | 123.039 | 0
88 | 18 | 0 | 32 |  | 0.047855 | 0.1205 | -5.3 | 1.42 | 18.0237 | 1.577 | 1.9651 | 0 | 26.6667 | 26.6667 | 42.336 | 0
88 | 19 | 0 | 1 |  | 0.047855 | 0.1205 | -5.3 | 1.42 | 19.0237 | 1.8388 | -7.0256 | 0 | 0.83333 | 0.83333 | 1.323 | 0
88 | 20 | 0 | 0 |  | 0.047855 | 0.1205 | -5.3 | 1.42 | 20.0237 | 2.1006 | -15.5445 | 0 | 0 | 0 | 0 | 0
88 | 21 | 0 | 0 |  | 0.047855 | 0.1205 | -5.3 | 1.42 | 21.0237 | 2.3624 | -23.1292 | 0 | 0 | 0 | 0 | 0
88 | 22 | 0 | 0 |  | 0.047855 | 0.1205 | -5.3 | 1.42 | 22.0237 | 2.6242 | -29.2265 | 0 | 0 | 0 | 0 | 0
88 | 23 | 0 | 0 |  | 0.047855 | 0.1205 | -5.3 | 1.42 | 23.0237 | 2.886 | -33.22 | 0 | 0 | 0 | 0 | 0
88 | 24 | 0 | 0 |  | 0.047855 | 0.1205 | -5.3 | 1.42 | 24.0237 | 3.1478 | -34.5773 | 0 | 0 | 0 | 0 | 0
89 | 1 | 0 | 0 |  | 0.054657 | 0.13771 | -4.9804 | 1.7396 | 1.029 | -2.8722 | -32.6892 | 0 | 0 | 0 | 0 | 0
89 | 2 | 0 | 0 |  | 0.054657 | 0.13771 | -4.9804 | 1.7396 | 2.029 | -2.6104 | -28.5875 | 0 | 0 | 0 | 0 | 0
89 | 3 | 0 | 0 |  | 0.054657 | 0.13771 | -4.9804 | 1.7396 | 3.029 | -2.3486 | -22.4172 | 0 | 0 | 0 | 0 | 0
89 | 4 | 0 | 0 |  | 0.054657 | 0.13771 | -4.9804 | 1.7396 | 4.029 | -2.0868 | -14.7882 | 0 | 0 | 0 | 0 | 0
89 | 5 | 0 | 0 |  | 0.054657 | 0.13771 | -4.9804 | 1.7396 | 5.029 | -1.825 | -6.2456 | 0 | 0 | 0 | 0 | 0
89 | 6 | 0 | 1 |  | 0.054657 | 0.13771 | -4.9804 | 1.7396 | 6.029 | -1.5632 | 2.7535 | 0 | 0.83333 | 0.83333 | 1.323 | 0
89 | 7 | 0 | 24 |  | 0.054657 | 0.13771 | -4.9804 | 1.7396 | 7.029 | -1.3014 | 11.8036 | 0 | 20 | 20 | 31.752 | 0
89 | 8 | 0 | 76 |  | 0.054657 | 0.13771 | -4.9804 | 1.7396 | 8.029 | -1.0396 | 20.4932 | 0 | 63.3333 | 63.3333 | 100.548 | 1
89 | 9 | 0 | 130 |  | 0.054657 | 0.13771 | -4.9804 | 1.7396 | 9.029 | -0.77781 | 28.3422 | 0 | 108.3333 | 108.3333 | 171.99 | 1
89 | 10 | 4 | 175 |  | 0.054657 | 0.13771 | -4.9804 | 1.7396 | 10.029 | -0.51601 | 34.7492 | 3.2896 | 145.8333 | 149.1229 | 236.7476 | 1
89 | 11 | 10 | 205 |  | 0.054657 | 0.13771 | -4.9804 | 1.7396 | 11.029 | -0.25421 | 39.0023 | 9.1275 | 170.8333 | 179.9608 | 285.7058 | 1
89 | 12 | 12 | 220 |  | 0.054657 | 0.13771 | -4.9804 | 1.7396 | 12.029 | 0.0075904 | 40.4503 | 11.308 | 183.3333 | 194.6413 | 309.0126 | 1
89 | 13 | 12 | 220 |  | 0.054657 | 0.13771 | -4.9804 | 1.7396 | 13.029 | 0.26939 | 38.8271 | 10.9096 | 183.3333 | 194.2429 | 308.38 | 1
89 | 14 | 10 | 203 |  | 0.054657 | 0.13771 | -4.9804 | 1.7396 | 14.029 | 0.53119 | 34.4294 | 8.1541 | 169.1667 | 177.3208 | 281.5144 | 1
89 | 15 | 4 | 173 |  | 0.054657 | 0.13771 | -4.9804 | 1.7396 | 15.029 | 0.79299 | 27.92 | 2.6702 | 144.1667 | 146.8369 | 233.1182 | 1
89 | 16 | 0 | 127 |  | 0.054657 | 0.13771 | -4.9804 | 1.7396 | 16.029 | 1.0548 | 20.0071 | 0 | 105.8333 | 105.8333 | 168.021 | 1
89 | 17 | 0 | 72 |  | 0.054657 | 0.13771 | -4.9804 | 1.7396 | 17.029 | 1.3166 | 11.2845 | 0 | 60 | 60 | 95.256 | 0
89 | 18 | 0 | 21 |  | 0.054657 | 0.13771 | -4.9804 | 1.7396 | 18.029 | 1.5784 | 2.2265 | 0 | 17.5 | 17.5 | 27.783 | 0
89 | 19 | 0 | 1 |  | 0.054657 | 0.13771 | -4.9804 | 1.7396 | 19.029 | 1.8402 | -6.7575 | 0 | 0.83333 | 0.83333 | 1.323 | 0
89 | 20 | 0 | 0 |  | 0.054657 | 0.13771 | -4.9804 | 1.7396 | 20.029 | 2.102 | -15.2604 | 0 | 0 | 0 | 0 | 0
89 | 21 | 0 | 0 |  | 0.054657 | 0.13771 | -4.9804 | 1.7396 | 21.029 | 2.3638 | -22.8206 | 0 | 0 | 0 | 0 | 0
89 | 22 | 0 | 0 |  | 0.054657 | 0.13771 | -4.9804 | 1.7396 | 22.029 | 2.6256 | -28.8877 | 0 | 0 | 0 | 0 | 0
89 | 23 | 0 | 0 |  | 0.054657 | 0.13771 | -4.9804 | 1.7396 | 23.029 | 2.8874 | -32.8513 | 0 | 0 | 0 | 0 | 0
89 | 24 | 0 | 0 |  | 0.054657 | 0.13771 | -4.9804 | 1.7396 | 24.029 | 3.1492 | -34.1872 | 0 | 0 | 0 | 0 | 0
90 | 1 | 0 | 0 |  | 0.061446 | 0.15493 | -4.6617 | 2.0583 | 1.0343 | -2.8708 | -32.2923 | 0 | 0 | 0 | 0 | 0
90 | 2 | 0 | 0 |  | 0.061446 | 0.15493 | -4.6617 | 2.0583 | 2.0343 | -2.609 | -28.1953 | 0 | 0 | 0 | 0 | 0
90 | 3 | 0 | 0 |  | 0.061446 | 0.15493 | -4.6617 | 2.0583 | 3.0343 | -2.3472 | -22.0361 | 0 | 0 | 0 | 0 | 0
90 | 4 | 0 | 0 |  | 0.061446 | 0.15493 | -4.6617 | 2.0583 | 4.0343 | -2.0854 | -14.4188 | 0 | 0 | 0 | 0 | 0
90 | 5 | 0 | 0 |  | 0.061446 | 0.15493 | -4.6617 | 2.0583 | 5.0343 | -1.8236 | -5.8847 | 0 | 0 | 0 | 0 | 0
90 | 6 | 0 | 3 |  | 0.061446 | 0.15493 | -4.6617 | 2.0583 | 6.0343 | -1.5618 | 3.1109 | 0 | 2.5 | 2.5 | 3.969 | 0
90 | 7 | 0 | 26 |  | 0.061446 | 0.15493 | -4.6617 | 2.0583 | 7.0343 | -1.3 | 12.1631 | 0 | 21.6667 | 21.6667 | 34.398 | 0
90 | 8 | 32 | 115 |  | 0.061446 | 0.15493 | -4.6617 | 2.0583 | 8.0343 | -1.0382 | 20.8603 | 15.7212 | 95.8333 | 111.5545 | 177.104 | 1
90 | 9 | 0 | 133 |  | 0.061446 | 0.15493 | -4.6617 | 2.0583 | 9.0343 | -0.77642 | 28.7211 | 0 | 110.8333 | 110.8333 | 175.959 | 1
90 | 10 | 4 | 177 |  | 0.061446 | 0.15493 | -4.6617 | 2.0583 | 10.0343 | -0.51462 | 35.1404 | 3.3013 | 147.5 | 150.8013 | 239.4122 | 1
90 | 11 | 10 | 207 |  | 0.061446 | 0.15493 | -4.6617 | 2.0583 | 11.0343 | -0.25282 | 39.3993 | 9.1533 | 172.5 | 181.6533 | 288.3928 | 1
90 | 12 | 109 | 296 |  | 0.061446 | 0.15493 | -4.6617 | 2.0583 | 12.0343 | 0.008981 | 40.8387 | 102.9583 | 246.6667 | 349.625 | 555.0647 | 1
90 | 13 | 102 | 300 |  | 0.061446 | 0.15493 | -4.6617 | 2.0583 | 13.0343 | 0.27078 | 39.191 | 92.9274 | 250 | 342.9274 | 544.4315 | 1
90 | 14 | 391 | 263 |  | 0.061446 | 0.15493 | -4.6617 | 2.0583 | 14.0343 | 0.53258 | 34.7605 | 319.4705 | 219.1667 | 538.6371 | 855.1403 | 1
90 | 15 | 360 | 228 |  | 0.061446 | 0.15493 | -4.6617 | 2.0583 | 15.0343 | 0.79438 | 28.2201 | 240.8399 | 190 | 430.8399 | 684.0015 | 1
90 | 16 | 465 | 139 |  | 0.061446 | 0.15493 | -4.6617 | 2.0583 | 16.0343 | 1.0562 | 20.2842 | 221.7873 | 115.8333 | 337.6207 | 536.0066 | 1
90 | 17 | 380 | 102 |  | 0.061446 | 0.15493 | -4.6617 | 2.0583 | 17.0343 | 1.318 | 11.5484 | 96.5328 | 85 | 181.5328 | 288.2014 | 0
90 | 18 | 106 | 50 |  | 0.061446 | 0.15493 | -4.6617 | 2.0583 | 18.0343 | 1.5798 | 2.4874 | 1.6331 | 41.6667 | 43.2998 | 68.7427 | 0
90 | 19 | 0 | 3 |  | 0.061446 | 0.15493 | -4.6617 | 2.0583 | 19.0343 | 1.8416 | -6.4898 | 0 | 2.5 | 2.5 | 3.969 | 0
90 | 20 | 0 | 0 |  | 0.061446 | 0.15493 | -4.6617 | 2.0583 | 20.0343 | 2.1034 | -14.9764 | 0 | 0 | 0 | 0 | 0
90 | 21 | 0 | 0 |  | 0.061446 | 0.15493 | -4.6617 | 2.0583 | 21.0343 | 2.3652 | -22.512 | 0 | 0 | 0 | 0 | 0
90 | 22 | 0 | 0 |  | 0.061446 | 0.15493 | -4.6617 | 2.0583 | 22.0343 | 2.627 | -28.5491 | 0 | 0 | 0 | 0 | 0
90 | 23 | 0 | 0 |  | 0.061446 | 0.15493 | -4.6617 | 2.0583 | 23.0343 | 2.8888 | -32.4831 | 0 | 0 | 0 | 0 | 0
90 | 24 | 0 | 0 |  | 0.061446 | 0.15493 | -4.6617 | 2.0583 | 24.0343 | 3.1506 | -33.7977 | 0 | 0 | 0 | 0 | 0
91 | 1 | 0 | 0 |  | 0.068219 | 0.17214 | -4.3443 | 2.3757 | 1.0396 | -2.8694 | -31.8962 | 0 | 0 | 0 | 0 | 0
91 | 2 | 0 | 0 |  | 0.068219 | 0.17214 | -4.3443 | 2.3757 | 2.0396 | -2.6076 | -27.804 | 0 | 0 | 0 | 0 | 0
91 | 3 | 0 | 0 |  | 0.068219 | 0.17214 | -4.3443 | 2.3757 | 3.0396 | -2.3458 | -21.6559 | 0 | 0 | 0 | 0 | 0
91 | 4 | 0 | 0 |  | 0.068219 | 0.17214 | -4.3443 | 2.3757 | 4.0396 | -2.084 | -14.0502 | 0 | 0 | 0 | 0 | 0
91 | 5 | 0 | 0 |  | 0.068219 | 0.17214 | -4.3443 | 2.3757 | 5.0396 | -1.8222 | -5.5246 | 0 | 0 | 0 | 0 | 0
91 | 6 | 0 | 5 |  | 0.068219 | 0.17214 | -4.3443 | 2.3757 | 6.0396 | -1.5604 | 3.4673 | 0 | 4.1667 | 4.1667 | 6.615 | 0
91 | 7 | 155 | 52 |  | 0.068219 | 0.17214 | -4.3443 | 2.3757 | 7.0396 | -1.2986 | 12.5215 | 42.4293 | 43.3333 | 85.7626 | 136.1568 | 1
91 | 8 | 457 | 88 |  | 0.068219 | 0.17214 | -4.3443 | 2.3757 | 8.0396 | -1.0368 | 21.2262 | 226.1171 | 73.3333 | 299.4505 | 475.4076 | 1
91 | 9 | 630 | 107 |  | 0.068219 | 0.17214 | -4.3443 | 2.3757 | 9.0396 | -0.77503 | 29.0989 | 430.8611 | 89.1667 | 520.0278 | 825.5961 | 1
91 | 10 | 769 | 97 |  | 0.068219 | 0.17214 | -4.3443 | 2.3757 | 10.0396 | -0.51323 | 35.5306 | 636.8945 | 80.8333 | 717.7278 | 1139.4646 | 1
91 | 11 | 842 | 90 |  | 0.068219 | 0.17214 | -4.3443 | 2.3757 | 11.0396 | -0.25143 | 39.7953 | 772.8431 | 75 | 847.8431 | 1346.0358 | 1
91 | 12 | 853 | 96 |  | 0.068219 | 0.17214 | -4.3443 | 2.3757 | 12.0396 | 0.010366 | 41.2262 | 807.587 | 80 | 887.587 | 1409.1331 | 1
91 | 13 | 858 | 94 |  | 0.068219 | 0.17214 | -4.3443 | 2.3757 | 13.0396 | 0.27217 | 39.5537 | 783.2911 | 78.3333 | 861.6244 | 1367.9149 | 1
91 | 14 | 833 | 91 |  | 0.068219 | 0.17214 | -4.3443 | 2.3757 | 14.0396 | 0.53396 | 35.0903 | 681.9515 | 75.8333 | 757.7848 | 1203.0592 | 1
91 | 15 | 770 | 93 |  | 0.068219 | 0.17214 | -4.3443 | 2.3757 | 15.0396 | 0.79576 | 28.5191 | 516.2173 | 77.5 | 593.7173 | 942.5856 | 1
91 | 16 | 654 | 92 |  | 0.068219 | 0.17214 | -4.3443 | 2.3757 | 16.0396 | 1.0576 | 20.5602 | 312.7812 | 76.6667 | 389.4478 | 618.2874 | 1
91 | 17 | 454 | 81 |  | 0.068219 | 0.17214 | -4.3443 | 2.3757 | 17.0396 | 1.3194 | 11.8115 | 115.9079 | 67.5 | 183.4079 | 291.1785 | 0
91 | 18 | 101 | 50 |  | 0.068219 | 0.17214 | -4.3443 | 2.3757 | 18.0396 | 1.5812 | 2.7478 | 1.6909 | 41.6667 | 43.3576 | 68.8345 | 0
91 | 19 | 0 | 3 |  | 0.068219 | 0.17214 | -4.3443 | 2.3757 | 19.0396 | 1.843 | -6.2223 | 0 | 2.5 | 2.5 | 3.969 | 0
91 | 20 | 0 | 0 |  | 0.068219 | 0.17214 | -4.3443 | 2.3757 | 20.0396 | 2.1048 | -14.6925 | 0 | 0 | 0 | 0 | 0
91 | 21 | 0 | 0 |  | 0.068219 | 0.17214 | -4.3443 | 2.3757 | 21.0396 | 2.3666 | -22.2036 | 0 | 0 | 0 | 0 | 0
91 | 22 | 0 | 0 |  | 0.068219 | 0.17214 | -4.3443 | 2.3757 | 22.0396 | 2.6284 | -28.2108 | 0 | 0 | 0 | 0 | 0
91 | 23 | 0 | 0 |  | 0.068219 | 0.17214 | -4.3443 | 2.3757 | 23.0396 | 2.8902 | -32.1155 | 0 | 0 | 0 | 0 | 0
91 | 24 | 0 | 0 |  | 0.068219 | 0.17214 | -4.3443 | 2.3757 | 24.0396 | 3.152 | -33.4091 | 0 | 0 | 0 | 0 | 0
92 | 1 | 0 | 0 |  | 0.074975 | 0.18936 | -4.0286 | 2.6914 | 1.0449 | -2.868 | -31.5012 | 0 | 0 | 0 | 0 | 0
92 | 2 | 0 | 0 |  | 0.074975 | 0.18936 | -4.0286 | 2.6914 | 2.0449 | -2.6063 | -27.4137 | 0 | 0 | 0 | 0 | 0
92 | 3 | 0 | 0 |  | 0.074975 | 0.18936 | -4.0286 | 2.6914 | 3.0449 | -2.3445 | -21.2767 | 0 | 0 | 0 | 0 | 0
92 | 4 | 0 | 0 |  | 0.074975 | 0.18936 | -4.0286 | 2.6914 | 4.0449 | -2.0827 | -13.6826 | 0 | 0 | 0 | 0 | 0
92 | 5 | 0 | 0 |  | 0.074975 | 0.18936 | -4.0286 | 2.6914 | 5.0449 | -1.8209 | -5.1656 | 0 | 0 | 0 | 0 | 0
92 | 6 | 0 | 2 |  | 0.074975 | 0.18936 | -4.0286 | 2.6914 | 6.0449 | -1.5591 | 3.8226 | 0 | 1.6667 | 1.6667 | 2.646 | 0
92 | 7 | 0 | 28 |  | 0.074975 | 0.18936 | -4.0286 | 2.6914 | 7.0449 | -1.2973 | 12.8787 | 0 | 23.3333 | 23.3333 | 37.044 | 1
92 | 8 | 0 | 80 |  | 0.074975 | 0.18936 | -4.0286 | 2.6914 | 8.0449 | -1.0355 | 21.591 | 0 | 66.6667 | 66.6667 | 105.84 | 1
92 | 9 | 0 | 134 |  | 0.074975 | 0.18936 | -4.0286 | 2.6914 | 9.0449 | -0.77365 | 29.4754 | 0 | 111.6667 | 111.6667 | 177.282 | 1
92 | 10 | 4 | 179 |  | 0.074975 | 0.18936 | -4.0286 | 2.6914 | 10.0449 | -0.51186 | 35.9196 | 3.3242 | 149.1667 | 152.4908 | 242.0945 | 1
92 | 11 | 10 | 208 |  | 0.074975 | 0.18936 | -4.0286 | 2.6914 | 11.0449 | -0.25006 | 40.1903 | 9.2035 | 173.3333 | 182.5368 | 289.7954 | 1
92 | 12 | 12 | 224 |  | 0.074975 | 0.18936 | -4.0286 | 2.6914 | 12.0449 | 0.011744 | 41.6125 | 11.3868 | 186.6667 | 198.0535 | 314.4297 | 1
92 | 13 | 12 | 222 |  | 0.074975 | 0.18936 | -4.0286 | 2.6914 | 13.0449 | 0.27354 | 39.9153 | 10.977 | 185 | 195.977 | 311.1332 | 1
92 | 14 | 10 | 206 |  | 0.074975 | 0.18936 | -4.0286 | 2.6914 | 14.0449 | 0.53534 | 35.4189 | 8.2024 | 171.6667 | 179.869 | 285.5601 | 1
92 | 15 | 4 | 175 |  | 0.074975 | 0.18936 | -4.0286 | 2.6914 | 15.0449 | 0.79714 | 28.8167 | 2.6872 | 145.8333 | 148.5205 | 235.7911 | 1
92 | 16 | 18 | 163 |  | 0.074975 | 0.18936 | -4.0286 | 2.6914 | 16.0449 | 1.0589 | 20.8352 | 8.6316 | 135.8333 | 144.4649 | 229.3525 | 1
92 | 17 | 17 | 114 |  | 0.074975 | 0.18936 | -4.0286 | 2.6914 | 17.0449 | 1.3207 | 12.0739 | 4.3616 | 95 | 99.3616 | 157.7464 | 0
92 | 18 | 0 | 38 |  | 0.074975 | 0.18936 | -4.0286 | 2.6914 | 18.0449 | 1.5825 | 3.0076 | 0 | 31.6667 | 31.6667 | 50.274 | 0
92 | 19 | 0 | 2 |  | 0.074975 | 0.18936 | -4.0286 | 2.6914 | 19.0449 | 1.8443 | -5.9552 | 0 | 1.6667 | 1.6667 | 2.646 | 0
92 | 20 | 0 | 0 |  | 0.074975 | 0.18936 | -4.0286 | 2.6914 | 20.0449 | 2.1061 | -14.4089 | 0 | 0 | 0 | 0 | 0
92 | 21 | 0 | 0 |  | 0.074975 | 0.18936 | -4.0286 | 2.6914 | 21.0449 | 2.3679 | -21.8953 | 0 | 0 | 0 | 0 | 0
92 | 22 | 0 | 0 |  | 0.074975 | 0.18936 | -4.0286 | 2.6914 | 22.0449 | 2.6297 | -27.8729 | 0 | 0 | 0 | 0 | 0
92 | 23 | 0 | 0 |  | 0.074975 | 0.18936 | -4.0286 | 2.6914 | 23.0449 | 2.8915 | -31.7485 | 0 | 0 | 0 | 0 | 0
92 | 24 | 0 | 0 |  | 0.074975 | 0.18936 | -4.0286 | 2.6914 | 24.0449 | 3.1533 | -33.0214 | 0 | 0 | 0 | 0 | 0
93 | 1 | 0 | 0 |  | 0.081712 | 0.20657 | -3.7149 | 3.0051 | 1.0501 | -2.8667 | -31.1074 | 0 | 0 | 0 | 0 | 0
93 | 2 | 0 | 0 |  | 0.081712 | 0.20657 | -3.7149 | 3.0051 | 2.0501 | -2.6049 | -27.0246 | 0 | 0 | 0 | 0 | 0
93 | 3 | 0 | 0 |  | 0.081712 | 0.20657 | -3.7149 | 3.0051 | 3.0501 | -2.3431 | -20.8986 | 0 | 0 | 0 | 0 | 0
93 | 4 | 0 | 0 |  | 0.081712 | 0.20657 | -3.7149 | 3.0051 | 4.0501 | -2.0813 | -13.3162 | 0 | 0 | 0 | 0 | 0
93 | 5 | 0 | 0 |  | 0.081712 | 0.20657 | -3.7149 | 3.0051 | 5.0501 | -1.8195 | -4.8078 | 0 | 0 | 0 | 0 | 0
93 | 6 | 0 | 5 |  | 0.081712 | 0.20657 | -3.7149 | 3.0051 | 6.0501 | -1.5577 | 4.1767 | 0 | 4.1667 | 4.1667 | 6.615 | 0
93 | 7 | 28 | 56 |  | 0.081712 | 0.20657 | -3.7149 | 3.0051 | 7.0501 | -1.2959 | 13.2346 | 7.871 | 46.6667 | 54.5377 | 86.584 | 1
93 | 8 | 15 | 126 |  | 0.081712 | 0.20657 | -3.7149 | 3.0051 | 8.0501 | -1.0341 | 21.9543 | 7.5251 | 105 | 112.5251 | 178.6448 | 1
93 | 9 | 53 | 195 |  | 0.081712 | 0.20657 | -3.7149 | 3.0051 | 9.0501 | -0.77229 | 29.8506 | 36.5802 | 162.5 | 199.0802 | 316.0598 | 1
93 | 10 | 5 | 181 |  | 0.081712 | 0.20657 | -3.7149 | 3.0051 | 10.0501 | -0.51049 | 36.3073 | 4.1691 | 150.8333 | 155.0025 | 246.0819 | 1
93 | 11 | 106 | 280 |  | 0.081712 | 0.20657 | -3.7149 | 3.0051 | 11.0501 | -0.24869 | 40.5842 | 97.8142 | 233.3333 | 331.1476 | 525.7299 | 1
93 | 12 | 482 | 326 |  | 0.081712 | 0.20657 | -3.7149 | 3.0051 | 12.0501 | 0.013112 | 41.9977 | 458.3757 | 271.6667 | 730.0424 | 1159.0152 | 1
93 | 13 | 107 | 305 |  | 0.081712 | 0.20657 | -3.7149 | 3.0051 | 13.0501 | 0.27491 | 40.2755 | 98.0692 | 254.1667 | 352.2359 | 559.2096 | 1
93 | 14 | 140 | 356 |  | 0.081712 | 0.20657 | -3.7149 | 3.0051 | 14.0501 | 0.53671 | 35.746 | 115.0473 | 296.6667 | 411.714 | 653.6371 | 1
93 | 15 | 198 | 264 |  | 0.081712 | 0.20657 | -3.7149 | 3.0051 | 15.0501 | 0.79851 | 29.1131 | 133.2819 | 220 | 353.2819 | 560.8704 | 1
93 | 16 | 55 | 188 |  | 0.081712 | 0.20657 | -3.7149 | 3.0051 | 16.0501 | 1.0603 | 21.1091 | 26.4433 | 156.6667 | 183.11 | 290.7054 | 1
93 | 17 | 14 | 120 |  | 0.081712 | 0.20657 | -3.7149 | 3.0051 | 17.0501 | 1.3221 | 12.3354 | 3.6094 | 100 | 103.6094 | 164.4903 | 0
93 | 18 | 115 | 55 |  | 0.081712 | 0.20657 | -3.7149 | 3.0051 | 18.0501 | 1.5839 | 3.2669 | 2.2326 | 45.8333 | 48.066 | 76.3095 | 0
93 | 19 | 0 | 4 |  | 0.081712 | 0.20657 | -3.7149 | 3.0051 | 19.0501 | 1.8457 | -5.6884 | 0 | 3.3333 | 3.3333 | 5.292 | 0
93 | 20 | 0 | 0 |  | 0.081712 | 0.20657 | -3.7149 | 3.0051 | 20.0501 | 2.1075 | -14.1255 | 0 | 0 | 0 | 0 | 0
93 | 21 | 0 | 0 |  | 0.081712 | 0.20657 | -3.7149 | 3.0051 | 21.0501 | 2.3693 | -21.5874 | 0 | 0 | 0 | 0 | 0
93 | 22 | 0 | 0 |  | 0.081712 | 0.20657 | -3.7149 | 3.0051 | 22.0501 | 2.6311 | -27.5354 | 0 | 0 | 0 | 0 | 0
93 | 23 | 0 | 0 |  | 0.081712 | 0.20657 | -3.7149 | 3.0051 | 23.0501 | 2.8929 | -31.3822 | 0 | 0 | 0 | 0 | 0
93 | 24 | 0 | 0 |  | 0.081712 | 0.20657 | -3.7149 | 3.0051 | 24.0501 | 3.1547 | -32.6347 | 0 | 0 | 0 | 0 | 0
94 | 1 | 0 | 0 |  | 0.088429 | 0.22378 | -3.4036 | 3.3164 | 1.0553 | -2.8653 | -30.7148 | 0 | 0 | 0 | 0 | 0
94 | 2 | 0 | 0 |  | 0.088429 | 0.22378 | -3.4036 | 3.3164 | 2.0553 | -2.6035 | -26.6369 | 0 | 0 | 0 | 0 | 0
94 | 3 | 0 | 0 |  | 0.088429 | 0.22378 | -3.4036 | 3.3164 | 3.0553 | -2.3417 | -20.5218 | 0 | 0 | 0 | 0 | 0
94 | 4 | 0 | 0 |  | 0.088429 | 0.22378 | -3.4036 | 3.3164 | 4.0553 | -2.0799 | -12.951 | 0 | 0 | 0 | 0 | 0
94 | 5 | 0 | 0 |  | 0.088429 | 0.22378 | -3.4036 | 3.3164 | 5.0553 | -1.8181 | -4.4513 | 0 | 0 | 0 | 0 | 0
94 | 6 | 0 | 7 |  | 0.088429 | 0.22378 | -3.4036 | 3.3164 | 6.0553 | -1.5563 | 4.5294 | 0 | 5.8333 | 5.8333 | 9.261 | 0
94 | 7 | 82 | 51 |  | 0.088429 | 0.22378 | -3.4036 | 3.3164 | 7.0553 | -1.2945 | 13.5891 | 23.3491 | 42.5 | 65.8491 | 104.542 | 1
94 | 8 | 8 | 134 |  | 0.088429 | 0.22378 | -3.4036 | 3.3164 | 8.0553 | -1.0327 | 22.3161 | 4.0404 | 111.6667 | 115.7071 | 183.6966 | 1
94 | 9 | 72 | 191 |  | 0.088429 | 0.22378 | -3.4036 | 3.3164 | 9.0553 | -0.77093 | 30.2243 | 49.9152 | 159.1667 | 209.0819 | 331.9384 | 1
94 | 10 | 182 | 283 |  | 0.088429 | 0.22378 | -3.4036 | 3.3164 | 10.0553 | -0.50913 | 36.6937 | 152.2529 | 235.8333 | 388.0862 | 616.1257 | 1
94 | 11 | 161 | 352 |  | 0.088429 | 0.22378 | -3.4036 | 3.3164 | 11.0553 | -0.24733 | 40.9768 | 148.9495 | 293.3333 | 442.2829 | 702.1683 | 1
94 | 12 | 591 | 258 |  | 0.088429 | 0.22378 | -3.4036 | 3.3164 | 12.0553 | 0.01447 | 42.3817 | 563.237 | 215 | 778.237 | 1235.529 | 1
94 | 13 | 789 | 147 |  | 0.088429 | 0.22378 | -3.4036 | 3.3164 | 13.0553 | 0.27627 | 40.6344 | 724.5138 | 122.5 | 847.0138 | 1344.7191 | 1
94 | 14 | 866 | 81 |  | 0.088429 | 0.22378 | -3.4036 | 3.3164 | 14.0553 | 0.53807 | 36.0718 | 712.9392 | 67.5 | 780.4392 | 1239.0252 | 1
94 | 15 | 121 | 226 |  | 0.088429 | 0.22378 | -3.4036 | 3.3164 | 15.0553 | 0.79987 | 29.4082 | 81.6096 | 188.3333 | 269.9429 | 428.5614 | 1
94 | 16 | 0 | 135 |  | 0.088429 | 0.22378 | -3.4036 | 3.3164 | 16.0553 | 1.0617 | 21.3818 | 0 | 112.5 | 112.5 | 178.605 | 1
94 | 17 | 0 | 79 |  | 0.088429 | 0.22378 | -3.4036 | 3.3164 | 17.0553 | 1.3235 | 12.596 | 0 | 65.8333 | 65.8333 | 104.517 | 1
94 | 18 | 0 | 26 |  | 0.088429 | 0.22378 | -3.4036 | 3.3164 | 18.0553 | 1.5853 | 3.5256 | 0 | 21.6667 | 21.6667 | 34.398 | 0
94 | 19 | 0 | 2 |  | 0.088429 | 0.22378 | -3.4036 | 3.3164 | 19.0553 | 1.8471 | -5.4221 | 0 | 1.6667 | 1.6667 | 2.646 | 0
94 | 20 | 0 | 0 |  | 0.088429 | 0.22378 | -3.4036 | 3.3164 | 20.0553 | 2.1089 | -13.8424 | 0 | 0 | 0 | 0 | 0
94 | 21 | 0 | 0 |  | 0.088429 | 0.22378 | -3.4036 | 3.3164 | 21.0553 | 2.3707 | -21.2797 | 0 | 0 | 0 | 0 | 0
94 | 22 | 0 | 0 |  | 0.088429 | 0.22378 | -3.4036 | 3.3164 | 22.0553 | 2.6325 | -27.1984 | 0 | 0 | 0 | 0 | 0
94 | 23 | 0 | 0 |  | 0.088429 | 0.22378 | -3.4036 | 3.3164 | 23.0553 | 2.8943 | -31.0167 | 0 | 0 | 0 | 0 | 0
94 | 24 | 0 | 0 |  | 0.088429 | 0.22378 | -3.4036 | 3.3164 | 24.0553 | 3.1561 | -32.2491 | 0 | 0 | 0 | 0 | 0
95 | 1 | 0 | 0 |  | 0.095123 | 0.241 | -3.0952 | 3.6248 | 1.0604 | -2.864 | -30.3236 | 0 | 0 | 0 | 0 | 0
95 | 2 | 0 | 0 |  | 0.095123 | 0.241 | -3.0952 | 3.6248 | 2.0604 | -2.6022 | -26.2505 | 0 | 0 | 0 | 0 | 0
95 | 3 | 0 | 0 |  | 0.095123 | 0.241 | -3.0952 | 3.6248 | 3.0604 | -2.3404 | -20.1464 | 0 | 0 | 0 | 0 | 0
95 | 4 | 0 | 0 |  | 0.095123 | 0.241 | -3.0952 | 3.6248 | 4.0604 | -2.0786 | -12.5872 | 0 | 0 | 0 | 0 | 0
95 | 5 | 0 | 0 |  | 0.095123 | 0.241 | -3.0952 | 3.6248 | 5.0604 | -1.8168 | -4.0962 | 0 | 0 | 0 | 0 | 0
95 | 6 | 0 | 3 |  | 0.095123 | 0.241 | -3.0952 | 3.6248 | 6.0604 | -1.555 | 4.8806 | 0 | 2.5 | 2.5 | 3.969 | 0
95 | 7 | 0 | 33 |  | 0.095123 | 0.241 | -3.0952 | 3.6248 | 7.0604 | -1.2932 | 13.9419 | 0 | 27.5 | 27.5 | 43.659 | 1
95 | 8 | 0 | 86 |  | 0.095123 | 0.241 | -3.0952 | 3.6248 | 8.0604 | -1.0314 | 22.6763 | 0 | 71.6667 | 71.6667 | 113.778 | 1
95 | 9 | 73 | 192 |  | 0.095123 | 0.241 | -3.0952 | 3.6248 | 9.0604 | -0.76958 | 30.5963 | 50.8293 | 160 | 210.8293 | 334.7126 | 1
95 | 10 | 5 | 185 |  | 0.095123 | 0.241 | -3.0952 | 3.6248 | 10.0604 | -0.50778 | 37.0785 | 4.1962 | 154.1667 | 158.3628 | 251.4168 | 1
95 | 11 | 105 | 285 |  | 0.095123 | 0.241 | -3.0952 | 3.6248 | 11.0604 | -0.24598 | 41.3679 | 97.385 | 237.5 | 334.885 | 531.6634 | 1
95 | 12 | 99 | 311 |  | 0.095123 | 0.241 | -3.0952 | 3.6248 | 12.0604 | 0.015816 | 42.7642 | 94.5459 | 259.1667 | 353.7126 | 561.5541 | 1
95 | 13 | 11 | 229 |  | 0.095123 | 0.241 | -3.0952 | 3.6248 | 13.0604 | 0.27762 | 40.9918 | 10.1195 | 190.8333 | 200.9529 | 319.0327 | 1
95 | 14 | 11 | 210 |  | 0.095123 | 0.241 | -3.0952 | 3.6248 | 14.0604 | 0.53942 | 36.3961 | 9.0718 | 175 | 184.0718 | 292.2323 | 1
95 | 15 | 4 | 180 |  | 0.095123 | 0.241 | -3.0952 | 3.6248 | 15.0604 | 0.80121 | 29.7019 | 2.703 | 150 | 152.703 | 242.4313 | 1
95 | 16 | 65 | 186 |  | 0.095123 | 0.241 | -3.0952 | 3.6248 | 16.0604 | 1.063 | 21.6535 | 31.4103 | 155 | 186.4103 | 295.945 | 1
95 | 17 | 111 | 129 |  | 0.095123 | 0.241 | -3.0952 | 3.6248 | 17.0604 | 1.3248 | 12.8558 | 28.8918 | 107.5 | 136.3918 | 216.5357 | 1
95 | 18 | 0 | 43 |  | 0.095123 | 0.241 | -3.0952 | 3.6248 | 18.0604 | 1.5866 | 3.7836 | 0 | 35.8333 | 35.8333 | 56.889 | 0
95 | 19 | 0 | 2 |  | 0.095123 | 0.241 | -3.0952 | 3.6248 | 19.0604 | 1.8484 | -5.1562 | 0 | 1.6667 | 1.6667 | 2.646 | 0
95 | 20 | 0 | 0 |  | 0.095123 | 0.241 | -3.0952 | 3.6248 | 20.0604 | 2.1102 | -13.5597 | 0 | 0 | 0 | 0 | 0
95 | 21 | 0 | 0 |  | 0.095123 | 0.241 | -3.0952 | 3.6248 | 21.0604 | 2.372 | -20.9725 | 0 | 0 | 0 | 0 | 0
95 | 22 | 0 | 0 |  | 0.095123 | 0.241 | -3.0952 | 3.6248 | 22.0604 | 2.6338 | -26.8619 | 0 | 0 | 0 | 0 | 0
95 | 23 | 0 | 0 |  | 0.095123 | 0.241 | -3.0952 | 3.6248 | 23.0604 | 2.8956 | -30.6521 | 0 | 0 | 0 | 0 | 0
95 | 24 | 0 | 0 |  | 0.095123 | 0.241 | -3.0952 | 3.6248 | 24.0604 | 3.1574 | -31.8648 | 0 | 0 | 0 | 0 | 0
96 | 1 | 0 | 0 |  | 0.10179 | 0.25821 | -2.7898 | 3.9302 | 1.0655 | -2.8626 | -29.934 | 0 | 0 | 0 | 0 | 0
96 | 2 | 0 | 0 |  | 0.10179 | 0.25821 | -2.7898 | 3.9302 | 2.0655 | -2.6008 | -25.8657 | 0 | 0 | 0 | 0 | 0
96 | 3 | 0 | 0 |  | 0.10179 | 0.25821 | -2.7898 | 3.9302 | 3.0655 | -2.339 | -19.7726 | 0 | 0 | 0 | 0 | 0
96 | 4 | 0 | 0 |  | 0.10179 | 0.25821 | -2.7898 | 3.9302 | 4.0655 | -2.0772 | -12.2249 | 0 | 0 | 0 | 0 | 0
96 | 5 | 0 | 0 |  | 0.10179 | 0.25821 | -2.7898 | 3.9302 | 5.0655 | -1.8154 | -3.7427 | 0 | 0 | 0 | 0 | 0
96 | 6 | 0 | 10 |  | 0.10179 | 0.25821 | -2.7898 | 3.9302 | 6.0655 | -1.5536 | 5.23 | 0 | 8.3333 | 8.3333 | 13.23 | 0
96 | 7 | 198 | 56 |  | 0.10179 | 0.25821 | -2.7898 | 3.9302 | 7.0655 | -1.2918 | 14.293 | 57.8001 | 46.6667 | 104.4668 | 165.8515 | 1
96 | 8 | 404 | 120 |  | 0.10179 | 0.25821 | -2.7898 | 3.9302 | 8.0655 | -1.03 | 23.0347 | 206.7244 | 100 | 306.7244 | 486.9556 | 1
96 | 9 | 616 | 114 |  | 0.10179 | 0.25821 | -2.7898 | 3.9302 | 9.0655 | -0.76825 | 30.9666 | 430.7487 | 95 | 525.7487 | 834.6786 | 1
96 | 10 | 676 | 156 |  | 0.10179 | 0.25821 | -2.7898 | 3.9302 | 10.0655 | -0.50645 | 37.4617 | 569.0953 | 130 | 699.0953 | 1109.8836 | 1
96 | 11 | 840 | 93 |  | 0.10179 | 0.25821 | -2.7898 | 3.9302 | 11.0655 | -0.24465 | 41.7576 | 780.9862 | 77.5 | 858.4862 | 1362.9327 | 1
96 | 12 | 876 | 91 |  | 0.10179 | 0.25821 | -2.7898 | 3.9302 | 12.0655 | 0.017149 | 43.1454 | 838.2827 | 75.8333 | 914.116 | 1451.2506 | 1
96 | 13 | 873 | 91 |  | 0.10179 | 0.25821 | -2.7898 | 3.9302 | 13.0655 | 0.27895 | 41.3477 | 804.555 | 75.8333 | 880.3883 | 1397.7045 | 1
96 | 14 | 856 | 86 |  | 0.10179 | 0.25821 | -2.7898 | 3.9302 | 14.0655 | 0.54075 | 36.7188 | 707.1562 | 71.6667 | 778.8228 | 1236.4591 | 1
96 | 15 | 782 | 96 |  | 0.10179 | 0.25821 | -2.7898 | 3.9302 | 15.0655 | 0.80255 | 29.9942 | 529.4201 | 80 | 609.4201 | 967.5153 | 1
96 | 16 | 670 | 95 |  | 0.10179 | 0.25821 | -2.7898 | 3.9302 | 16.0655 | 1.0643 | 21.9239 | 324.5693 | 79.1667 | 403.7359 | 640.9712 | 1
96 | 17 | 418 | 105 |  | 0.10179 | 0.25821 | -2.7898 | 3.9302 | 17.0655 | 1.3261 | 13.1147 | 109.3123 | 87.5 | 196.8123 | 312.4592 | 1
96 | 18 | 61 | 58 |  | 0.10179 | 0.25821 | -2.7898 | 3.9302 | 18.0655 | 1.5879 | 4.041 | 1.43 | 48.3333 | 49.7633 | 79.0042 | 0
96 | 19 | 0 | 5 |  | 0.10179 | 0.25821 | -2.7898 | 3.9302 | 19.0655 | 1.8497 | -4.8907 | 0 | 4.1667 | 4.1667 | 6.615 | 0
96 | 20 | 0 | 0 |  | 0.10179 | 0.25821 | -2.7898 | 3.9302 | 20.0655 | 2.1115 | -13.2773 | 0 | 0 | 0 | 0 | 0
96 | 21 | 0 | 0 |  | 0.10179 | 0.25821 | -2.7898 | 3.9302 | 21.0655 | 2.3733 | -20.6656 | 0 | 0 | 0 | 0 | 0
96 | 22 | 0 | 0 |  | 0.10179 | 0.25821 | -2.7898 | 3.9302 | 22.0655 | 2.6351 | -26.5261 | 0 | 0 | 0 | 0 | 0
96 | 23 | 0 | 0 |  | 0.10179 | 0.25821 | -2.7898 | 3.9302 | 23.0655 | 2.8969 | -30.2886 | 0 | 0 | 0 | 0 | 0
96 | 24 | 0 | 0 |  | 0.10179 | 0.25821 | -2.7898 | 3.9302 | 24.0655 | 3.1587 | -31.4817 | 0 | 0 | 0 | 0 | 0
97 | 1 | 0 | 0 |  | 0.10844 | 0.27543 | -2.488 | 4.232 | 1.0705 | -2.8613 | -29.5459 | 0 | 0 | 0 | 0 | 0
97 | 2 | 0 | 0 |  | 0.10844 | 0.27543 | -2.488 | 4.232 | 2.0705 | -2.5995 | -25.4826 | 0 | 0 | 0 | 0 | 0
97 | 3 | 0 | 0 |  | 0.10844 | 0.27543 | -2.488 | 4.232 | 3.0705 | -2.3377 | -19.4004 | 0 | 0 | 0 | 0 | 0
97 | 4 | 0 | 0 |  | 0.10844 | 0.27543 | -2.488 | 4.232 | 4.0705 | -2.0759 | -11.8644 | 0 | 0 | 0 | 0 | 0
97 | 5 | 0 | 0 |  | 0.10844 | 0.27543 | -2.488 | 4.232 | 5.0705 | -1.8141 | -3.3909 | 0 | 0 | 0 | 0 | 0
97 | 6 | 0 | 7 |  | 0.10844 | 0.27543 | -2.488 | 4.232 | 6.0705 | -1.5523 | 5.5777 | 0 | 5.8333 | 5.8333 | 9.261 | 0
97 | 7 | 0 | 36 |  | 0.10844 | 0.27543 | -2.488 | 4.232 | 7.0705 | -1.2905 | 14.6422 | 0 | 30 | 30 | 47.628 | 1
97 | 8 | 0 | 91 |  | 0.10844 | 0.27543 | -2.488 | 4.232 | 8.0705 | -1.0287 | 23.3912 | 0 | 75.8333 | 75.8333 | 120.393 | 1
97 | 9 | 0 | 146 |  | 0.10844 | 0.27543 | -2.488 | 4.232 | 9.0705 | -0.76693 | 31.335 | 0 | 121.6667 | 121.6667 | 193.158 | 1
97 | 10 | 8 | 188 |  | 0.10844 | 0.27543 | -2.488 | 4.232 | 10.0705 | -0.50513 | 37.8431 | 6.7554 | 156.6667 | 163.4221 | 259.4489 | 1
97 | 11 | 107 | 291 |  | 0.10844 | 0.27543 | -2.488 | 4.232 | 11.0705 | -0.24333 | 42.1456 | 99.7198 | 242.5 | 342.2198 | 543.3082 | 1
97 | 12 | 102 | 317 |  | 0.10844 | 0.27543 | -2.488 | 4.232 | 12.0705 | 0.018466 | 43.5249 | 97.8003 | 264.1667 | 361.967 | 574.6588 | 1
97 | 13 | 248 | 325 |  | 0.10844 | 0.27543 | -2.488 | 4.232 | 13.0705 | 0.28026 | 41.702 | 228.9521 | 270.8333 | 499.7855 | 793.4594 | 1
97 | 14 | 270 | 283 |  | 0.10844 | 0.27543 | -2.488 | 4.232 | 14.0705 | 0.54206 | 37.04 | 223.4225 | 235.8333 | 459.2559 | 729.1146 | 1
97 | 15 | 482 | 218 |  | 0.10844 | 0.27543 | -2.488 | 4.232 | 15.0705 | 0.80386 | 30.2851 | 326.9114 | 181.6667 | 508.5781 | 807.4186 | 1
97 | 16 | 650 | 101 |  | 0.10844 | 0.27543 | -2.488 | 4.232 | 16.0705 | 1.0657 | 22.1932 | 315.6471 | 84.1667 | 399.8138 | 634.7443 | 1
97 | 17 | 242 | 122 |  | 0.10844 | 0.27543 | -2.488 | 4.232 | 17.0705 | 1.3275 | 13.3726 | 63.5813 | 101.6667 | 165.248 | 262.3477 | 1
97 | 18 | 25 | 57 |  | 0.10844 | 0.27543 | -2.488 | 4.232 | 18.0705 | 1.5893 | 4.2977 | 0.61983 | 47.5 | 48.1198 | 76.395 | 0
97 | 19 | 0 | 5 |  | 0.10844 | 0.27543 | -2.488 | 4.232 | 19.0705 | 1.8511 | -4.6257 | 0 | 4.1667 | 4.1667 | 6.615 | 0
97 | 20 | 0 | 0 |  | 0.10844 | 0.27543 | -2.488 | 4.232 | 20.0705 | 2.1129 | -12.9953 | 0 | 0 | 0 | 0 | 0
97 | 21 | 0 | 0 |  | 0.10844 | 0.27543 | -2.488 | 4.232 | 21.0705 | 2.3747 | -20.3593 | 0 | 0 | 0 | 0 | 0
97 | 22 | 0 | 0 |  | 0.10844 | 0.27543 | -2.488 | 4.232 | 22.0705 | 2.6365 | -26.1911 | 0 | 0 | 0 | 0 | 0
97 | 23 | 0 | 0 |  | 0.10844 | 0.27543 | -2.488 | 4.232 | 23.0705 | 2.8983 | -29.9261 | 0 | 0 | 0 | 0 | 0
97 | 24 | 0 | 0 |  | 0.10844 | 0.27543 | -2.488 | 4.232 | 24.0705 | 3.1601 | -31.1001 | 0 | 0 | 0 | 0 | 0
98 | 1 | 0 | 0 |  | 0.11505 | 0.29264 | -2.1901 | 4.5299 | 1.0755 | -2.86 | -29.1597 | 0 | 0 | 0 | 0 | 0
98 | 2 | 0 | 0 |  | 0.11505 | 0.29264 | -2.1901 | 4.5299 | 2.0755 | -2.5982 | -25.1013 | 0 | 0 | 0 | 0 | 0
98 | 3 | 0 | 0 |  | 0.11505 | 0.29264 | -2.1901 | 4.5299 | 3.0755 | -2.3364 | -19.03 | 0 | 0 | 0 | 0 | 0
98 | 4 | 0 | 0 |  | 0.11505 | 0.29264 | -2.1901 | 4.5299 | 4.0755 | -2.0746 | -11.5056 | 0 | 0 | 0 | 0 | 0
98 | 5 | 0 | 0 |  | 0.11505 | 0.29264 | -2.1901 | 4.5299 | 5.0755 | -1.8128 | -3.041 | 0 | 0 | 0 | 0 | 0
98 | 6 | 0 | 13 |  | 0.11505 | 0.29264 | -2.1901 | 4.5299 | 6.0755 | -1.551 | 5.9235 | 0 | 10.8333 | 10.8333 | 17.199 | 0
98 | 7 | 48 | 69 |  | 0.11505 | 0.29264 | -2.1901 | 4.5299 | 7.0755 | -1.2892 | 14.9894 | 14.3493 | 57.5 | 71.8493 | 114.0679 | 1
98 | 8 | 24 | 140 |  | 0.11505 | 0.29264 | -2.1901 | 4.5299 | 8.0755 | -1.0274 | 23.7455 | 12.4356 | 116.6667 | 129.1023 | 204.9628 | 1
98 | 9 | 55 | 210 |  | 0.11505 | 0.29264 | -2.1901 | 4.5299 | 9.0755 | -0.76563 | 31.7013 | 38.7785 | 175 | 213.7785 | 339.3947 | 1
98 | 10 | 96 | 255 |  | 0.11505 | 0.29264 | -2.1901 | 4.5299 | 10.0755 | -0.50383 | 38.2225 | 81.3065 | 212.5 | 293.8065 | 466.4473 | 1
98 | 11 | 100 | 298 |  | 0.11505 | 0.29264 | -2.1901 | 4.5299 | 11.0755 | -0.24203 | 42.5319 | 93.4122 | 248.3333 | 341.7456 | 542.5552 | 1
98 | 12 | 60 | 350 |  | 0.11505 | 0.29264 | -2.1901 | 4.5299 | 12.0755 | 0.019766 | 43.9028 | 57.6395 | 291.6667 | 349.3062 | 554.5585 | 1
98 | 13 | 61 | 349 |  | 0.11505 | 0.29264 | -2.1901 | 4.5299 | 13.0755 | 0.28157 | 42.0546 | 56.4094 | 290.8333 | 347.2428 | 551.2826 | 1
98 | 14 | 60 | 321 |  | 0.11505 | 0.29264 | -2.1901 | 4.5299 | 14.0755 | 0.54336 | 37.3595 | 49.7297 | 267.5 | 317.2297 | 503.6338 | 1
98 | 15 | 75 | 261 |  | 0.11505 | 0.29264 | -2.1901 | 4.5299 | 15.0755 | 0.80516 | 30.5744 | 50.9583 | 217.5 | 268.4583 | 426.2044 | 1
98 | 16 | 65 | 197 |  | 0.11505 | 0.29264 | -2.1901 | 4.5299 | 16.0755 | 1.067 | 22.4613 | 31.6403 | 164.1667 | 195.807 | 310.8631 | 1
98 | 17 | 15 | 130 |  | 0.11505 | 0.29264 | -2.1901 | 4.5299 | 17.0755 | 1.3288 | 13.6296 | 3.9592 | 108.3333 | 112.2925 | 178.2756 | 1
98 | 18 | 0 | 49 |  | 0.11505 | 0.29264 | -2.1901 | 4.5299 | 18.0755 | 1.5906 | 4.5537 | 0 | 40.8333 | 40.8333 | 64.827 | 0
98 | 19 | 0 | 4 |  | 0.11505 | 0.29264 | -2.1901 | 4.5299 | 19.0755 | 1.8524 | -4.3613 | 0 | 3.3333 | 3.3333 | 5.292 | 0
98 | 20 | 0 | 0 |  | 0.11505 | 0.29264 | -2.1901 | 4.5299 | 20.0755 | 2.1142 | -12.7138 | 0 | 0 | 0 | 0 | 0
98 | 21 | 0 | 0 |  | 0.11505 | 0.29264 | -2.1901 | 4.5299 | 21.0755 | 2.376 | -20.0535 | 0 | 0 | 0 | 0 | 0
98 | 22 | 0 | 0 |  | 0.11505 | 0.29264 | -2.1901 | 4.5299 | 22.0755 | 2.6378 | -25.8568 | 0 | 0 | 0 | 0 | 0
98 | 23 | 0 | 0 |  | 0.11505 | 0.29264 | -2.1901 | 4.5299 | 23.0755 | 2.8996 | -29.5647 | 0 | 0 | 0 | 0 | 0
98 | 24 | 0 | 0 |  | 0.11505 | 0.29264 | -2.1901 | 4.5299 | 24.0755 | 3.1614 | -30.72 | 0 | 0 | 0 | 0 | 0
99 | 1 | 0 | 0 |  | 0.12164 | 0.30986 | -1.8963 | 4.8237 | 1.0804 | -2.8587 | -28.7752 | 0 | 0 | 0 | 0 | 0
99 | 2 | 0 | 0 |  | 0.12164 | 0.30986 | -1.8963 | 4.8237 | 2.0804 | -2.5969 | -24.7219 | 0 | 0 | 0 | 0 | 0
99 | 3 | 0 | 0 |  | 0.12164 | 0.30986 | -1.8963 | 4.8237 | 3.0804 | -2.3351 | -18.6616 | 0 | 0 | 0 | 0 | 0
99 | 4 | 0 | 0 |  | 0.12164 | 0.30986 | -1.8963 | 4.8237 | 4.0804 | -2.0733 | -11.1489 | 0 | 0 | 0 | 0 | 0
99 | 5 | 0 | 0 |  | 0.12164 | 0.30986 | -1.8963 | 4.8237 | 5.0804 | -1.8115 | -2.6931 | 0 | 0 | 0 | 0 | 0
99 | 6 | 0 | 8 |  | 0.12164 | 0.30986 | -1.8963 | 4.8237 | 6.0804 | -1.5497 | 6.2672 | 0 | 6.6667 | 6.6667 | 10.584 | 0
99 | 7 | 0 | 63 |  | 0.12164 | 0.30986 | -1.8963 | 4.8237 | 7.0804 | -1.2879 | 15.3344 | 0 | 52.5 | 52.5 | 83.349 | 1
99 | 8 | 10 | 147 |  | 0.12164 | 0.30986 | -1.8963 | 4.8237 | 8.0804 | -1.0262 | 24.0977 | 5.2131 | 122.5 | 127.7131 | 202.7573 | 1
99 | 9 | 55 | 213 |  | 0.12164 | 0.30986 | -1.8963 | 4.8237 | 9.0804 | -0.76435 | 32.0655 | 38.9335 | 177.5 | 216.4335 | 343.6098 | 1
99 | 10 | 95 | 258 |  | 0.12164 | 0.30986 | -1.8963 | 4.8237 | 10.0804 | -0.50255 | 38.5999 | 80.6933 | 215 | 295.6933 | 469.4427 | 1
99 | 11 | 100 | 300 |  | 0.12164 | 0.30986 | -1.8963 | 4.8237 | 11.0804 | -0.24075 | 42.9163 | 93.6228 | 250 | 343.6228 | 545.5356 | 1
99 | 12 | 61 | 353 |  | 0.12164 | 0.30986 | -1.8963 | 4.8237 | 12.0804 | 0.021047 | 44.2789 | 58.7088 | 294.1667 | 352.8755 | 560.2251 | 1
99 | 13 | 61 | 351 |  | 0.12164 | 0.30986 | -1.8963 | 4.8237 | 13.0804 | 0.28285 | 42.4055 | 56.5013 | 292.5 | 349.0013 | 554.0745 | 1
99 | 14 | 140 | 374 |  | 0.12164 | 0.30986 | -1.8963 | 4.8237 | 14.0804 | 0.54465 | 37.6773 | 116.218 | 311.6667 | 427.8846 | 679.3096 | 1
99 | 15 | 197 | 279 |  | 0.12164 | 0.30986 | -1.8963 | 4.8237 | 15.0804 | 0.80645 | 30.8623 | 134.0826 | 232.5 | 366.5826 | 581.9865 | 1
99 | 16 | 479 | 171 |  | 0.12164 | 0.30986 | -1.8963 | 4.8237 | 16.0804 | 1.0682 | 22.728 | 233.7143 | 142.5 | 376.2143 | 597.2778 | 1
99 | 17 | 463 | 94 |  | 0.12164 | 0.30986 | -1.8963 | 4.8237 | 17.0804 | 1.33 | 13.8857 | 122.7681 | 78.3333 | 201.1014 | 319.2686 | 1
99 | 18 | 201 | 58 |  | 0.12164 | 0.30986 | -1.8963 | 4.8237 | 18.0804 | 1.5918 | 4.809 | 5.5301 | 48.3333 | 53.8634 | 85.5136 | 0
99 | 19 | 0 | 9 |  | 0.12164 | 0.30986 | -1.8963 | 4.8237 | 19.0804 | 1.8536 | -4.0975 | 0 | 7.5 | 7.5 | 11.907 | 0
99 | 20 | 0 | 0 |  | 0.12164 | 0.30986 | -1.8963 | 4.8237 | 20.0804 | 2.1154 | -12.4329 | 0 | 0 | 0 | 0 | 0
99 | 21 | 0 | 0 |  | 0.12164 | 0.30986 | -1.8963 | 4.8237 | 21.0804 | 2.3772 | -19.7483 | 0 | 0 | 0 | 0 | 0
99 | 22 | 0 | 0 |  | 0.12164 | 0.30986 | -1.8963 | 4.8237 | 22.0804 | 2.639 | -25.5234 | 0 | 0 | 0 | 0 | 0
99 | 23 | 0 | 0 |  | 0.12164 | 0.30986 | -1.8963 | 4.8237 | 23.0804 | 2.9008 | -29.2047 | 0 | 0 | 0 | 0 | 0
99 | 24 | 0 | 0 |  | 0.12164 | 0.30986 | -1.8963 | 4.8237 | 24.0804 | 3.1626 | -30.3415 | 0 | 0 | 0 | 0 | 0
100 | 1 | 0 | 0 |  | 0.1282 | 0.32707 | -1.6071 | 5.1129 | 1.0852 | -2.8575 | -28.3927 | 0 | 0 | 0 | 0 | 0
100 | 2 | 0 | 0 |  | 0.1282 | 0.32707 | -1.6071 | 5.1129 | 2.0852 | -2.5957 | -24.3446 | 0 | 0 | 0 | 0 | 0
100 | 3 | 0 | 0 |  | 0.1282 | 0.32707 | -1.6071 | 5.1129 | 3.0852 | -2.3339 | -18.2952 | 0 | 0 | 0 | 0 | 0
100 | 4 | 0 | 0 |  | 0.1282 | 0.32707 | -1.6071 | 5.1129 | 4.0852 | -2.0721 | -10.7941 | 0 | 0 | 0 | 0 | 0
100 | 5 | 0 | 0 |  | 0.1282 | 0.32707 | -1.6071 | 5.1129 | 5.0852 | -1.8103 | -2.3473 | 0 | 0 | 0 | 0 | 0
100 | 6 | 0 | 12 |  | 0.1282 | 0.32707 | -1.6071 | 5.1129 | 6.0852 | -1.5485 | 6.6086 | 0 | 10 | 10 | 15.876 | 0
100 | 7 | 55 | 74 |  | 0.1282 | 0.32707 | -1.6071 | 5.1129 | 7.0852 | -1.2867 | 15.6771 | 16.8191 | 61.6667 | 78.4857 | 124.6039 | 1
100 | 8 | 379 | 134 |  | 0.1282 | 0.32707 | -1.6071 | 5.1129 | 8.0852 | -1.0249 | 24.4476 | 198.7521 | 111.6667 | 310.4188 | 492.8208 | 1
100 | 9 | 196 | 217 |  | 0.1282 | 0.32707 | -1.6071 | 5.1129 | 9.0852 | -0.76309 | 32.4273 | 139.2863 | 180.8333 | 320.1196 | 508.2219 | 1
100 | 10 | 384 | 245 |  | 0.1282 | 0.32707 | -1.6071 | 5.1129 | 10.0852 | -0.50129 | 38.9752 | 327.0938 | 204.1667 | 531.2605 | 843.4291 | 1
100 | 11 | 239 | 314 |  | 0.1282 | 0.32707 | -1.6071 | 5.1129 | 11.0852 | -0.23949 | 43.2988 | 224.2488 | 261.6667 | 485.9155 | 771.4394 | 1
100 | 12 | 91 | 331 |  | 0.1282 | 0.32707 | -1.6071 | 5.1129 | 12.0852 | 0.022309 | 44.6532 | 87.7394 | 275.8333 | 363.5728 | 577.2081 | 1
100 | 13 | 101 | 322 |  | 0.1282 | 0.32707 | -1.6071 | 5.1129 | 13.0852 | 0.28411 | 42.7546 | 93.699 | 268.3333 | 362.0323 | 574.7625 | 1
100 | 14 | 240 | 307 |  | 0.1282 | 0.32707 | -1.6071 | 5.1129 | 14.0852 | 0.54591 | 37.9934 | 199.5343 | 255.8333 | 455.3677 | 722.9417 | 1
100 | 15 | 85 | 257 |  | 0.1282 | 0.32707 | -1.6071 | 5.1129 | 15.0852 | 0.80771 | 31.1486 | 57.9509 | 214.1667 | 272.1175 | 432.0138 | 1
100 | 16 | 44 | 208 |  | 0.1282 | 0.32707 | -1.6071 | 5.1129 | 16.0852 | 1.0695 | 22.9936 | 21.5184 | 173.3333 | 194.8517 | 309.3466 | 1
100 | 17 | 209 | 139 |  | 0.1282 | 0.32707 | -1.6071 | 5.1129 | 17.0852 | 1.3313 | 14.1407 | 55.6703 | 115.8333 | 171.5036 | 272.2791 | 1
100 | 18 | 91 | 75 |  | 0.1282 | 0.32707 | -1.6071 | 5.1129 | 18.0852 | 1.5931 | 5.0635 | 2.6283 | 62.5 | 65.1283 | 103.3977 | 0
100 | 19 | 0 | 9 |  | 0.1282 | 0.32707 | -1.6071 | 5.1129 | 19.0852 | 1.8549 | -3.8342 | 0 | 7.5 | 7.5 | 11.907 | 0
100 | 20 | 0 | 0 |  | 0.1282 | 0.32707 | -1.6071 | 5.1129 | 20.0852 | 2.1167 | -12.1525 | 0 | 0 | 0 | 0 | 0
100 | 21 | 0 | 0 |  | 0.1282 | 0.32707 | -1.6071 | 5.1129 | 21.0852 | 2.3785 | -19.4438 | 0 | 0 | 0 | 0 | 0
100 | 22 | 0 | 0 |  | 0.1282 | 0.32707 | -1.6071 | 5.1129 | 22.0852 | 2.6403 | -25.191 | 0 | 0 | 0 | 0 | 0
100 | 23 | 0 | 0 |  | 0.1282 | 0.32707 | -1.6071 | 5.1129 | 23.0852 | 2.9021 | -28.8459 | 0 | 0 | 0 | 0 | 0
100 | 24 | 0 | 0 |  | 0.1282 | 0.32707 | -1.6071 | 5.1129 | 24.0852 | 3.1639 | -29.9648 | 0 | 0 | 0 | 0 | 0
101 | 1 | 0 | 0 |  | 0.13472 | 0.34428 | -1.3227 | 5.3973 | 1.09 | -2.8562 | -28.0124 | 0 | 0 | 0 | 0 | 0
101 | 2 | 0 | 0 |  | 0.13472 | 0.34428 | -1.3227 | 5.3973 | 2.09 | -2.5944 | -23.9694 | 0 | 0 | 0 | 0 | 0
101 | 3 | 0 | 0 |  | 0.13472 | 0.34428 | -1.3227 | 5.3973 | 3.09 | -2.3326 | -17.931 | 0 | 0 | 0 | 0 | 0
101 | 4 | 0 | 0 |  | 0.13472 | 0.34428 | -1.3227 | 5.3973 | 4.09 | -2.0708 | -10.4417 | 0 | 0 | 0 | 0 | 0
101 | 5 | 0 | 0 |  | 0.13472 | 0.34428 | -1.3227 | 5.3973 | 5.09 | -1.809 | -2.0038 | 0 | 0 | 0 | 0 | 0
101 | 6 | 0 | 10 |  | 0.13472 | 0.34428 | -1.3227 | 5.3973 | 6.09 | -1.5472 | 6.9477 | 0 | 8.3333 | 8.3333 | 13.23 | 0
101 | 7 | 0 | 68 |  | 0.13472 | 0.34428 | -1.3227 | 5.3973 | 7.09 | -1.2854 | 16.0175 | 0 | 56.6667 | 56.6667 | 89.964 | 1
101 | 8 | 160 | 145 |  | 0.13472 | 0.34428 | -1.3227 | 5.3973 | 8.09 | -1.0236 | 24.7949 | 84.3945 | 120.8333 | 205.2278 | 325.8196 | 1
101 | 9 | 70 | 211 |  | 0.13472 | 0.34428 | -1.3227 | 5.3973 | 9.09 | -0.76185 | 32.7867 | 49.9346 | 175.8333 | 225.7679 | 358.4292 | 1
101 | 10 | 94 | 263 |  | 0.13472 | 0.34428 | -1.3227 | 5.3973 | 10.09 | -0.50005 | 39.3481 | 80.2904 | 219.1667 | 299.4571 | 475.4181 | 1
101 | 11 | 98 | 305 |  | 0.13472 | 0.34428 | -1.3227 | 5.3973 | 11.09 | -0.23825 | 43.6791 | 92.147 | 254.1667 | 346.3137 | 549.8076 | 1
101 | 12 | 101 | 327 |  | 0.13472 | 0.34428 | -1.3227 | 5.3973 | 12.09 | 0.02355 | 45.0256 | 97.5507 | 272.5 | 370.0507 | 587.4925 | 1
101 | 13 | 141 | 412 |  | 0.13472 | 0.34428 | -1.3227 | 5.3973 | 13.09 | 0.28535 | 43.1018 | 131.0074 | 343.3333 | 474.3407 | 753.0634 | 1
101 | 14 | 158 | 367 |  | 0.13472 | 0.34428 | -1.3227 | 5.3973 | 14.09 | 0.54715 | 38.3076 | 131.5544 | 305.8333 | 437.3878 | 694.3968 | 1
101 | 15 | 333 | 269 |  | 0.13472 | 0.34428 | -1.3227 | 5.3973 | 15.09 | 0.80895 | 31.4333 | 227.4067 | 224.1667 | 451.5734 | 716.9179 | 1
101 | 16 | 412 | 188 |  | 0.13472 | 0.34428 | -1.3227 | 5.3973 | 16.09 | 1.0707 | 23.2578 | 201.9516 | 156.6667 | 358.6183 | 569.3424 | 1
101 | 17 | 338 | 133 |  | 0.13472 | 0.34428 | -1.3227 | 5.3973 | 17.09 | 1.3325 | 14.3947 | 90.4385 | 110.8333 | 201.2718 | 319.5391 | 1
101 | 18 | 85 | 71 |  | 0.13472 | 0.34428 | -1.3227 | 5.3973 | 18.09 | 1.5943 | 5.3172 | 2.5721 | 59.1667 | 61.7388 | 98.0165 | 0
101 | 19 | 0 | 8 |  | 0.13472 | 0.34428 | -1.3227 | 5.3973 | 19.09 | 1.8561 | -3.5716 | 0 | 6.6667 | 6.6667 | 10.584 | 0
101 | 20 | 0 | 0 |  | 0.13472 | 0.34428 | -1.3227 | 5.3973 | 20.09 | 2.1179 | -11.8727 | 0 | 0 | 0 | 0 | 0
101 | 21 | 0 | 0 |  | 0.13472 | 0.34428 | -1.3227 | 5.3973 | 21.09 | 2.3797 | -19.1401 | 0 | 0 | 0 | 0 | 0
101 | 22 | 0 | 0 |  | 0.13472 | 0.34428 | -1.3227 | 5.3973 | 22.09 | 2.6415 | -24.8596 | 0 | 0 | 0 | 0 | 0
101 | 23 | 0 | 0 |  | 0.13472 | 0.34428 | -1.3227 | 5.3973 | 23.09 | 2.9033 | -28.4887 | 0 | 0 | 0 | 0 | 0
101 | 24 | 0 | 0 |  | 0.13472 | 0.34428 | -1.3227 | 5.3973 | 24.09 | 3.1651 | -29.5899 | 0 | 0 | 0 | 0 | 0
102 | 1 | 0 | 0 |  | 0.14121 | 0.3615 | -1.0435 | 5.6765 | 1.0946 | -2.855 | -27.6342 | 0 | 0 | 0 | 0 | 0
102 | 2 | 0 | 0 |  | 0.14121 | 0.3615 | -1.0435 | 5.6765 | 2.0946 | -2.5932 | -23.5966 | 0 | 0 | 0 | 0 | 0
102 | 3 | 0 | 0 |  | 0.14121 | 0.3615 | -1.0435 | 5.6765 | 3.0946 | -2.3314 | -17.5692 | 0 | 0 | 0 | 0 | 0
102 | 4 | 0 | 0 |  | 0.14121 | 0.3615 | -1.0435 | 5.6765 | 4.0946 | -2.0696 | -10.0915 | 0 | 0 | 0 | 0 | 0
102 | 5 | 0 | 0 |  | 0.14121 | 0.3615 | -1.0435 | 5.6765 | 5.0946 | -1.8078 | -1.6627 | 0 | 0 | 0 | 0 | 0
102 | 6 | 0 | 11 |  | 0.14121 | 0.3615 | -1.0435 | 5.6765 | 6.0946 | -1.546 | 7.2844 | 0 | 9.1667 | 9.1667 | 14.553 | 0
102 | 7 | 11 | 70 |  | 0.14121 | 0.3615 | -1.0435 | 5.6765 | 7.0946 | -1.2842 | 16.3552 | 3.4372 | 58.3333 | 61.7706 | 98.067 | 1
102 | 8 | 152 | 152 |  | 0.14121 | 0.3615 | -1.0435 | 5.6765 | 8.0946 | -1.0224 | 25.1397 | 80.6307 | 126.6667 | 207.2974 | 329.1054 | 1
102 | 9 | 548 | 173 |  | 0.14121 | 0.3615 | -1.0435 | 5.6765 | 9.0946 | -0.76063 | 33.1435 | 392.369 | 144.1667 | 536.5356 | 851.804 | 1
102 | 10 | 336 | 282 |  | 0.14121 | 0.3615 | -1.0435 | 5.6765 | 10.0946 | -0.49883 | 39.7186 | 287.7646 | 235 | 522.7646 | 829.941 | 1
102 | 11 | 574 | 228 |  | 0.14121 | 0.3615 | -1.0435 | 5.6765 | 11.0946 | -0.23703 | 44.0573 | 540.8318 | 190 | 730.8318 | 1160.2686 | 1
102 | 12 | 686 | 224 |  | 0.14121 | 0.3615 | -1.0435 | 5.6765 | 12.0946 | 0.024768 | 45.3959 | 663.6893 | 186.6667 | 850.356 | 1350.0252 | 1
102 | 13 | 600 | 228 |  | 0.14121 | 0.3615 | -1.0435 | 5.6765 | 13.0946 | 0.28657 | 43.4469 | 558.303 | 190 | 748.303 | 1188.0058 | 1
102 | 14 | 645 | 174 |  | 0.14121 | 0.3615 | -1.0435 | 5.6765 | 14.0946 | 0.54837 | 38.62 | 537.8131 | 145 | 682.8131 | 1084.0341 | 1
102 | 15 | 659 | 154 |  | 0.14121 | 0.3615 | -1.0435 | 5.6765 | 15.0946 | 0.81017 | 31.7164 | 450.761 | 128.3333 | 579.0943 | 919.3701 | 1
102 | 16 | 606 | 119 |  | 0.14121 | 0.3615 | -1.0435 | 5.6765 | 16.0946 | 1.072 | 23.5206 | 297.7161 | 99.1667 | 396.8828 | 630.0911 | 1
102 | 17 | 482 | 95 |  | 0.14121 | 0.3615 | -1.0435 | 5.6765 | 17.0946 | 1.3338 | 14.6476 | 129.5482 | 79.1667 | 208.7149 | 331.3557 | 1
102 | 18 | 175 | 69 |  | 0.14121 | 0.3615 | -1.0435 | 5.6765 | 18.0946 | 1.5956 | 5.5701 | 5.538 | 57.5 | 63.038 | 100.0791 | 0
102 | 19 | 0 | 11 |  | 0.14121 | 0.3615 | -1.0435 | 5.6765 | 19.0946 | 1.8574 | -3.3097 | 0 | 9.1667 | 9.1667 | 14.553 | 0
102 | 20 | 0 | 0 |  | 0.14121 | 0.3615 | -1.0435 | 5.6765 | 20.0946 | 2.1192 | -11.5936 | 0 | 0 | 0 | 0 | 0
102 | 21 | 0 | 0 |  | 0.14121 | 0.3615 | -1.0435 | 5.6765 | 21.0946 | 2.381 | -18.8372 | 0 | 0 | 0 | 0 | 0
102 | 22 | 0 | 0 |  | 0.14121 | 0.3615 | -1.0435 | 5.6765 | 22.0946 | 2.6428 | -24.5294 | 0 | 0 | 0 | 0 | 0
102 | 23 | 0 | 0 |  | 0.14121 | 0.3615 | -1.0435 | 5.6765 | 23.0946 | 2.9046 | -28.133 | 0 | 0 | 0 | 0 | 0
102 | 24 | 0 | 0 |  | 0.14121 | 0.3615 | -1.0435 | 5.6765 | 24.0946 | 3.1664 | -29.217 | 0 | 0 | 0 | 0 | 0
103 | 1 | 0 | 0 |  | 0.14767 | 0.37871 | -0.76981 | 5.9502 | 1.0992 | -2.8538 | -27.2583 | 0 | 0 | 0 | 0 | 0
103 | 2 | 0 | 0 |  | 0.14767 | 0.37871 | -0.76981 | 5.9502 | 2.0992 | -2.592 | -23.2261 | 0 | 0 | 0 | 0 | 0
103 | 3 | 0 | 0 |  | 0.14767 | 0.37871 | -0.76981 | 5.9502 | 3.0992 | -2.3302 | -17.2098 | 0 | 0 | 0 | 0 | 0
103 | 4 | 0 | 0 |  | 0.14767 | 0.37871 | -0.76981 | 5.9502 | 4.0992 | -2.0684 | -9.7438 | 0 | 0 | 0 | 0 | 0
103 | 5 | 0 | 0 |  | 0.14767 | 0.37871 | -0.76981 | 5.9502 | 5.0992 | -1.8066 | -1.3241 | 0 | 0 | 0 | 0 | 0
103 | 6 | 0 | 17 |  | 0.14767 | 0.37871 | -0.76981 | 5.9502 | 6.0992 | -1.5448 | 7.6184 | 0 | 14.1667 | 14.1667 | 22.491 | 0
103 | 7 | 7 | 73 |  | 0.14767 | 0.37871 | -0.76981 | 5.9502 | 7.0992 | -1.283 | 16.6903 | 2.2102 | 60.8333 | 63.0435 | 100.0879 | 1
103 | 8 | 11 | 160 |  | 0.14767 | 0.37871 | -0.76981 | 5.9502 | 8.0992 | -1.0212 | 25.4817 | 5.8675 | 133.3333 | 139.2009 | 220.9953 | 1
103 | 9 | 57 | 225 |  | 0.14767 | 0.37871 | -0.76981 | 5.9502 | 9.0992 | -0.75944 | 33.4976 | 40.9599 | 187.5 | 228.4599 | 362.7029 | 1
103 | 10 | 96 | 269 |  | 0.14767 | 0.37871 | -0.76981 | 5.9502 | 10.0992 | -0.49764 | 40.0866 | 82.4326 | 224.1667 | 306.5993 | 486.757 | 1
103 | 11 | 100 | 311 |  | 0.14767 | 0.37871 | -0.76981 | 5.9502 | 11.0992 | -0.23584 | 44.4332 | 94.41 | 259.1667 | 353.5767 | 561.3384 | 1
103 | 12 | 101 | 332 |  | 0.14767 | 0.37871 | -0.76981 | 5.9502 | 12.0992 | 0.025963 | 45.7641 | 97.8746 | 276.6667 | 374.5412 | 594.6217 | 1
103 | 13 | 243 | 341 |  | 0.14767 | 0.37871 | -0.76981 | 5.9502 | 13.0992 | 0.28776 | 43.7901 | 226.4363 | 284.1667 | 510.603 | 810.6333 | 1
103 | 14 | 406 | 280 |  | 0.14767 | 0.37871 | -0.76981 | 5.9502 | 14.0992 | 0.54956 | 38.9305 | 339.0024 | 233.3333 | 572.3357 | 908.6401 | 1
103 | 15 | 229 | 267 |  | 0.14767 | 0.37871 | -0.76981 | 5.9502 | 15.0992 | 0.81136 | 31.9978 | 156.8854 | 222.5 | 379.3854 | 602.3123 | 1
103 | 16 | 148 | 232 |  | 0.14767 | 0.37871 | -0.76981 | 5.9502 | 16.0992 | 1.0732 | 23.7821 | 72.8716 | 193.3333 | 266.205 | 422.627 | 1
103 | 17 | 27 | 136 |  | 0.14767 | 0.37871 | -0.76981 | 5.9502 | 17.0992 | 1.335 | 14.8995 | 7.2893 | 113.3333 | 120.6226 | 191.5005 | 1
103 | 18 | 0 | 58 |  | 0.14767 | 0.37871 | -0.76981 | 5.9502 | 18.0992 | 1.5968 | 5.8221 | 0 | 48.3333 | 48.3333 | 76.734 | 0
103 | 19 | 0 | 4 |  | 0.14767 | 0.37871 | -0.76981 | 5.9502 | 19.0992 | 1.8586 | -3.0485 | 0 | 3.3333 | 3.3333 | 5.292 | 0
103 | 20 | 0 | 0 |  | 0.14767 | 0.37871 | -0.76981 | 5.9502 | 20.0992 | 2.1204 | -11.3152 | 0 | 0 | 0 | 0 | 0
103 | 21 | 0 | 0 |  | 0.14767 | 0.37871 | -0.76981 | 5.9502 | 21.0992 | 2.3822 | -18.5351 | 0 | 0 | 0 | 0 | 0
103 | 22 | 0 | 0 |  | 0.14767 | 0.37871 | -0.76981 | 5.9502 | 22.0992 | 2.644 | -24.2003 | 0 | 0 | 0 | 0 | 0
103 | 23 | 0 | 0 |  | 0.14767 | 0.37871 | -0.76981 | 5.9502 | 23.0992 | 2.9058 | -27.7789 | 0 | 0 | 0 | 0 | 0
103 | 24 | 0 | 0 |  | 0.14767 | 0.37871 | -0.76981 | 5.9502 | 24.0992 | 3.1676 | -28.8461 | 0 | 0 | 0 | 0 | 0
104 | 1 | 0 | 0 |  | 0.15408 | 0.39593 | -0.50192 | 6.2181 | 1.1036 | -2.8527 | -26.8848 | 0 | 0 | 0 | 0 | 0
104 | 2 | 0 | 0 |  | 0.15408 | 0.39593 | -0.50192 | 6.2181 | 2.1036 | -2.5909 | -22.8582 | 0 | 0 | 0 | 0 | 0
104 | 3 | 0 | 0 |  | 0.15408 | 0.39593 | -0.50192 | 6.2181 | 3.1036 | -2.3291 | -16.8529 | 0 | 0 | 0 | 0 | 0
104 | 4 | 0 | 0 |  | 0.15408 | 0.39593 | -0.50192 | 6.2181 | 4.1036 | -2.0673 | -9.3988 | 0 | 0 | 0 | 0 | 0
104 | 5 | 0 | 0 |  | 0.15408 | 0.39593 | -0.50192 | 6.2181 | 5.1036 | -1.8055 | -0.98821 | 0 | 0 | 0 | 0 | 0
104 | 6 | 0 | 12 |  | 0.15408 | 0.39593 | -0.50192 | 6.2181 | 6.1036 | -1.5437 | 7.9497 | 0 | 10 | 10 | 15.876 | 0
104 | 7 | 7 | 75 |  | 0.15408 | 0.39593 | -0.50192 | 6.2181 | 7.1036 | -1.2819 | 17.0225 | 2.2327 | 62.5 | 64.7327 | 102.7696 | 1
104 | 8 | 11 | 162 |  | 0.15408 | 0.39593 | -0.50192 | 6.2181 | 8.1036 | -1.0201 | 25.8208 | 5.8993 | 135 | 140.8993 | 223.6917 | 1
104 | 9 | 54 | 226 |  | 0.15408 | 0.39593 | -0.50192 | 6.2181 | 9.1036 | -0.75827 | 33.8489 | 38.9409 | 188.3333 | 227.2742 | 360.8206 | 1
104 | 10 | 3 | 203 |  | 0.15408 | 0.39593 | -0.50192 | 6.2181 | 10.1036 | -0.49647 | 40.4518 | 2.5825 | 169.1667 | 171.7492 | 272.669 | 1
104 | 11 | 13 | 229 |  | 0.15408 | 0.39593 | -0.50192 | 6.2181 | 11.1036 | -0.23467 | 44.8066 | 12.2971 | 190.8333 | 203.1304 | 322.4898 | 1
104 | 12 | 14 | 243 |  | 0.15408 | 0.39593 | -0.50192 | 6.2181 | 12.1036 | 0.027131 | 46.1301 | 13.5882 | 202.5 | 216.0882 | 343.0616 | 1
104 | 13 | 14 | 242 |  | 0.15408 | 0.39593 | -0.50192 | 6.2181 | 13.1036 | 0.28893 | 44.1311 | 13.0638 | 201.6667 | 214.7304 | 340.906 | 1
104 | 14 | 12 | 224 |  | 0.15408 | 0.39593 | -0.50192 | 6.2181 | 14.1036 | 0.55073 | 39.239 | 10.0333 | 186.6667 | 196.7 | 312.2809 | 1
104 | 15 | 8 | 192 |  | 0.15408 | 0.39593 | -0.50192 | 6.2181 | 15.1036 | 0.81253 | 32.2775 | 5.4892 | 160 | 165.4892 | 262.7306 | 1
104 | 16 | 205 | 206 |  | 0.15408 | 0.39593 | -0.50192 | 6.2181 | 16.1036 | 1.0743 | 24.0422 | 101.1593 | 171.6667 | 272.826 | 433.1385 | 1
104 | 17 | 27 | 138 |  | 0.15408 | 0.39593 | -0.50192 | 6.2181 | 17.1036 | 1.3361 | 15.1502 | 7.3217 | 115 | 122.3217 | 194.198 | 1
104 | 18 | 157 | 74 |  | 0.15408 | 0.39593 | -0.50192 | 6.2181 | 18.1036 | 1.5979 | 6.0733 | 5.4076 | 61.6667 | 67.0743 | 106.4871 | 0
104 | 19 | 0 | 7 |  | 0.15408 | 0.39593 | -0.50192 | 6.2181 | 19.1036 | 1.8597 | -2.7881 | 0 | 5.8333 | 5.8333 | 9.261 | 0
104 | 20 | 0 | 0 |  | 0.15408 | 0.39593 | -0.50192 | 6.2181 | 20.1036 | 2.1215 | -11.0376 | 0 | 0 | 0 | 0 | 0
104 | 21 | 0 | 0 |  | 0.15408 | 0.39593 | -0.50192 | 6.2181 | 21.1036 | 2.3833 | -18.2341 | 0 | 0 | 0 | 0 | 0
104 | 22 | 0 | 0 |  | 0.15408 | 0.39593 | -0.50192 | 6.2181 | 22.1036 | 2.6451 | -23.8726 | 0 | 0 | 0 | 0 | 0
104 | 23 | 0 | 0 |  | 0.15408 | 0.39593 | -0.50192 | 6.2181 | 23.1036 | 2.9069 | -27.4266 | 0 | 0 | 0 | 0 | 0
104 | 24 | 0 | 0 |  | 0.15408 | 0.39593 | -0.50192 | 6.2181 | 24.1036 | 3.1687 | -28.4773 | 0 | 0 | 0 | 0 | 0
105 | 1 | 0 | 0 |  | 0.16046 | 0.41314 | -0.24012 | 6.4799 | 1.108 | -2.8515 | -26.5139 | 0 | 0 | 0 | 0 | 0
105 | 2 | 0 | 0 |  | 0.16046 | 0.41314 | -0.24012 | 6.4799 | 2.108 | -2.5897 | -22.493 | 0 | 0 | 0 | 0 | 0
105 | 3 | 0 | 0 |  | 0.16046 | 0.41314 | -0.24012 | 6.4799 | 3.108 | -2.3279 | -16.4988 | 0 | 0 | 0 | 0 | 0
105 | 4 | 0 | 0 |  | 0.16046 | 0.41314 | -0.24012 | 6.4799 | 4.108 | -2.0661 | -9.0564 | 0 | 0 | 0 | 0 | 0
105 | 5 | 0 | 0 |  | 0.16046 | 0.41314 | -0.24012 | 6.4799 | 5.108 | -1.8043 | -0.65507 | 0 | 0 | 0 | 0 | 0
105 | 6 | 0 | 14 |  | 0.16046 | 0.41314 | -0.24012 | 6.4799 | 6.108 | -1.5425 | 8.2782 | 0 | 11.6667 | 11.6667 | 18.522 | 0
105 | 7 | 30 | 74 |  | 0.16046 | 0.41314 | -0.24012 | 6.4799 | 7.108 | -1.2807 | 17.3518 | 9.6636 | 61.6667 | 71.3303 | 113.2439 | 1
105 | 8 | 10 | 167 |  | 0.16046 | 0.41314 | -0.24012 | 6.4799 | 8.108 | -1.0189 | 26.157 | 5.3913 | 139.1667 | 144.558 | 229.5003 | 1
105 | 9 | 75 | 221 |  | 0.16046 | 0.41314 | -0.24012 | 6.4799 | 9.108 | -0.75712 | 34.1972 | 54.2702 | 184.1667 | 238.4368 | 378.5423 | 1
105 | 10 | 97 | 274 |  | 0.16046 | 0.41314 | -0.24012 | 6.4799 | 10.108 | -0.49532 | 40.8143 | 83.7069 | 228.3333 | 312.0402 | 495.3951 | 1
105 | 11 | 100 | 316 |  | 0.16046 | 0.41314 | -0.24012 | 6.4799 | 11.108 | -0.23353 | 45.1775 | 94.7703 | 263.3333 | 358.1036 | 568.5253 | 1
105 | 12 | 540 | 279 |  | 0.16046 | 0.41314 | -0.24012 | 6.4799 | 12.108 | 0.028274 | 46.4937 | 524.9132 | 232.5 | 757.4132 | 1202.4692 | 1
105 | 13 | 276 | 325 |  | 0.16046 | 0.41314 | -0.24012 | 6.4799 | 13.108 | 0.29007 | 44.47 | 257.8872 | 270.8333 | 528.7206 | 839.3968 | 1
105 | 14 | 268 | 301 |  | 0.16046 | 0.41314 | -0.24012 | 6.4799 | 14.108 | 0.55187 | 39.5455 | 224.372 | 250.8333 | 475.2053 | 754.436 | 1
105 | 15 | 150 | 321 |  | 0.16046 | 0.41314 | -0.24012 | 6.4799 | 15.108 | 0.81367 | 32.5554 | 103.0782 | 267.5 | 370.5782 | 588.3299 | 1
105 | 16 | 305 | 213 |  | 0.16046 | 0.41314 | -0.24012 | 6.4799 | 16.108 | 1.0755 | 24.3008 | 150.8329 | 177.5 | 328.3329 | 521.2614 | 1
105 | 17 | 294 | 145 |  | 0.16046 | 0.41314 | -0.24012 | 6.4799 | 17.108 | 1.3373 | 15.3998 | 80.0789 | 120.8333 | 200.9122 | 318.9683 | 1
105 | 18 | 41 | 72 |  | 0.16046 | 0.41314 | -0.24012 | 6.4799 | 18.108 | 1.5991 | 6.3235 | 1.4701 | 60 | 61.4701 | 97.59 | 0
105 | 19 | 0 | 10 |  | 0.16046 | 0.41314 | -0.24012 | 6.4799 | 19.108 | 1.8609 | -2.5286 | 0 | 8.3333 | 8.3333 | 13.23 | 0
105 | 20 | 0 | 0 |  | 0.16046 | 0.41314 | -0.24012 | 6.4799 | 20.108 | 2.1227 | -10.7609 | 0 | 0 | 0 | 0 | 0
105 | 21 | 0 | 0 |  | 0.16046 | 0.41314 | -0.24012 | 6.4799 | 21.108 | 2.3845 | -17.934 | 0 | 0 | 0 | 0 | 0
105 | 22 | 0 | 0 |  | 0.16046 | 0.41314 | -0.24012 | 6.4799 | 22.108 | 2.6463 | -23.5462 | 0 | 0 | 0 | 0 | 0
105 | 23 | 0 | 0 |  | 0.16046 | 0.41314 | -0.24012 | 6.4799 | 23.108 | 2.9081 | -27.0761 | 0 | 0 | 0 | 0 | 0
105 | 24 | 0 | 0 |  | 0.16046 | 0.41314 | -0.24012 | 6.4799 | 24.108 | 3.1699 | -28.1108 | 0 | 0 | 0 | 0 | 0
106 | 1 | 0 | 0 |  | 0.16679 | 0.43036 | 0.015291 | 6.7353 | 1.1123 | -2.8504 | -26.1456 | 0 | 0 | 0 | 0 | 0
106 | 2 | 0 | 0 |  | 0.16679 | 0.43036 | 0.015291 | 6.7353 | 2.1123 | -2.5886 | -22.1305 | 0 | 0 | 0 | 0 | 0
106 | 3 | 0 | 0 |  | 0.16679 | 0.43036 | 0.015291 | 6.7353 | 3.1123 | -2.3268 | -16.1475 | 0 | 0 | 0 | 0 | 0
106 | 4 | 0 | 0 |  | 0.16679 | 0.43036 | 0.015291 | 6.7353 | 4.1123 | -2.065 | -8.7169 | 0 | 0 | 0 | 0 | 0
106 | 5 | 0 | 0 |  | 0.16679 | 0.43036 | 0.015291 | 6.7353 | 5.1123 | -1.8032 | -0.32483 | 0 | 0 | 0 | 0 | 0
106 | 6 | 0 | 15 |  | 0.16679 | 0.43036 | 0.015291 | 6.7353 | 6.1123 | -1.5414 | 8.6036 | 0 | 12.5 | 12.5 | 19.845 | 0
106 | 7 | 15 | 79 |  | 0.16679 | 0.43036 | 0.015291 | 6.7353 | 7.1123 | -1.2796 | 17.6781 | 4.8784 | 65.8333 | 70.7118 | 112.262 | 1
106 | 8 | 12 | 169 |  | 0.16679 | 0.43036 | 0.015291 | 6.7353 | 8.1123 | -1.0178 | 26.49 | 6.5029 | 140.8333 | 147.3362 | 233.911 | 1
106 | 9 | 57 | 233 |  | 0.16679 | 0.43036 | 0.015291 | 6.7353 | 9.1123 | -0.75601 | 34.5424 | 41.3829 | 194.1667 | 235.5496 | 373.9585 | 1
106 | 10 | 96 | 276 |  | 0.16679 | 0.43036 | 0.015291 | 6.7353 | 10.1123 | -0.49421 | 41.1739 | 83.0411 | 230 | 313.0411 | 496.9841 | 1
106 | 11 | 99 | 318 |  | 0.16679 | 0.43036 | 0.015291 | 6.7353 | 11.1123 | -0.23241 | 45.5457 | 93.9926 | 265 | 358.9926 | 569.9367 | 1
106 | 12 | 244 | 351 |  | 0.16679 | 0.43036 | 0.015291 | 6.7353 | 12.1123 | 0.029388 | 46.855 | 237.5317 | 292.5 | 530.0317 | 841.4783 | 1
106 | 13 | 535 | 280 |  | 0.16679 | 0.43036 | 0.015291 | 6.7353 | 13.1123 | 0.29119 | 44.8066 | 500.5359 | 233.3333 | 733.8692 | 1165.0908 | 1
106 | 14 | 105 | 306 |  | 0.16679 | 0.43036 | 0.015291 | 6.7353 | 14.1123 | 0.55299 | 39.8499 | 88.019 | 255 | 343.019 | 544.5769 | 1
106 | 15 | 230 | 274 |  | 0.16679 | 0.43036 | 0.015291 | 6.7353 | 15.1123 | 0.81479 | 32.8316 | 158.2875 | 228.3333 | 386.6208 | 613.7992 | 1
106 | 16 | 485 | 182 |  | 0.16679 | 0.43036 | 0.015291 | 6.7353 | 16.1123 | 1.0766 | 24.558 | 240.3656 | 151.6667 | 392.0323 | 622.3904 | 1
106 | 17 | 260 | 136 |  | 0.16679 | 0.43036 | 0.015291 | 6.7353 | 17.1123 | 1.3384 | 15.6482 | 71.1308 | 113.3333 | 184.4642 | 292.8553 | 1
106 | 18 | 0 | 64 |  | 0.16679 | 0.43036 | 0.015291 | 6.7353 | 18.1123 | 1.6002 | 6.5727 | 0 | 53.3333 | 53.3333 | 84.672 | 0
106 | 19 | 0 | 9 |  | 0.16679 | 0.43036 | 0.015291 | 6.7353 | 19.1123 | 1.862 | -2.2699 | 0 | 7.5 | 7.5 | 11.907 | 0
106 | 20 | 0 | 0 |  | 0.16679 | 0.43036 | 0.015291 | 6.7353 | 20.1123 | 2.1238 | -10.4851 | 0 | 0 | 0 | 0 | 0
106 | 21 | 0 | 0 |  | 0.16679 | 0.43036 | 0.015291 | 6.7353 | 21.1123 | 2.3856 | -17.6351 | 0 | 0 | 0 | 0 | 0
106 | 22 | 0 | 0 |  | 0.16679 | 0.43036 | 0.015291 | 6.7353 | 22.1123 | 2.6474 | -23.2214 | 0 | 0 | 0 | 0 | 0
106 | 23 | 0 | 0 |  | 0.16679 | 0.43036 | 0.015291 | 6.7353 | 23.1123 | 2.9092 | -26.7275 | 0 | 0 | 0 | 0 | 0
106 | 24 | 0 | 0 |  | 0.16679 | 0.43036 | 0.015291 | 6.7353 | 24.1123 | 3.171 | -27.7467 | 0 | 0 | 0 | 0 | 0
107 | 1 | 0 | 0 |  | 0.17309 | 0.44757 | 0.26405 | 6.984 | 1.1164 | -2.8493 | -25.7801 | 0 | 0 | 0 | 0 | 0
107 | 2 | 0 | 0 |  | 0.17309 | 0.44757 | 0.26405 | 6.984 | 2.1164 | -2.5875 | -21.7709 | 0 | 0 | 0 | 0 | 0
107 | 3 | 0 | 0 |  | 0.17309 | 0.44757 | 0.26405 | 6.984 | 3.1164 | -2.3257 | -15.7991 | 0 | 0 | 0 | 0 | 0
107 | 4 | 0 | 0 |  | 0.17309 | 0.44757 | 0.26405 | 6.984 | 4.1164 | -2.0639 | -8.3804 | 0 | 0 | 0 | 0 | 0
107 | 5 | 0 | 0 |  | 0.17309 | 0.44757 | 0.26405 | 6.984 | 5.1164 | -1.8021 | 0.0023698 | 0 | 0 | 0 | 0 | 0
107 | 6 | 0 | 10 |  | 0.17309 | 0.44757 | 0.26405 | 6.984 | 6.1164 | -1.5403 | 8.926 | 0 | 8.3333 | 8.3333 | 13.23 | 0
107 | 7 | 0 | 53 |  | 0.17309 | 0.44757 | 0.26405 | 6.984 | 7.1164 | -1.2785 | 18.0011 | 0 | 44.1667 | 44.1667 | 70.119 | 1
107 | 8 | 86 | 142 |  | 0.17309 | 0.44757 | 0.26405 | 6.984 | 8.1164 | -1.0167 | 26.8198 | 46.8374 | 118.3333 | 165.1707 | 262.2251 | 1
107 | 9 | 56 | 235 |  | 0.17309 | 0.44757 | 0.26405 | 6.984 | 9.1164 | -0.75492 | 34.8844 | 40.7887 | 195.8333 | 236.622 | 375.6611 | 1
107 | 10 | 422 | 334 |  | 0.17309 | 0.44757 | 0.26405 | 6.984 | 10.1164 | -0.49313 | 41.5303 | 365.8764 | 278.3333 | 644.2098 | 1022.7474 | 1
107 | 11 | 587 | 227 |  | 0.17309 | 0.44757 | 0.26405 | 6.984 | 11.1164 | -0.23133 | 45.9111 | 558.2856 | 189.1667 | 747.4522 | 1186.6552 | 1
107 | 12 | 645 | 205 |  | 0.17309 | 0.44757 | 0.26405 | 6.984 | 12.1164 | 0.030474 | 47.2137 | 628.7915 | 170.8333 | 799.6248 | 1269.4843 | 1
107 | 13 | 765 | 170 |  | 0.17309 | 0.44757 | 0.26405 | 6.984 | 13.1164 | 0.29227 | 45.1408 | 716.6121 | 141.6667 | 858.2788 | 1362.6034 | 1
107 | 14 | 730 | 155 |  | 0.17309 | 0.44757 | 0.26405 | 6.984 | 14.1164 | 0.55407 | 40.1522 | 612.6984 | 129.1667 | 741.8651 | 1177.7851 | 1
107 | 15 | 776 | 103 |  | 0.17309 | 0.44757 | 0.26405 | 6.984 | 15.1164 | 0.81587 | 33.1059 | 534.8236 | 85.8333 | 620.6569 | 985.355 | 1
107 | 16 | 667 | 106 |  | 0.17309 | 0.44757 | 0.26405 | 6.984 | 16.1164 | 1.0777 | 24.8137 | 331.2693 | 88.3333 | 419.6027 | 666.1612 | 1
107 | 17 | 489 | 104 |  | 0.17309 | 0.44757 | 0.26405 | 6.984 | 17.1164 | 1.3395 | 15.8954 | 134.3698 | 86.6667 | 221.0365 | 350.9175 | 1
107 | 18 | 234 | 70 |  | 0.17309 | 0.44757 | 0.26405 | 6.984 | 18.1164 | 1.6013 | 6.8209 | 9.0589 | 58.3333 | 67.3923 | 106.992 | 0
107 | 19 | 0 | 14 |  | 0.17309 | 0.44757 | 0.26405 | 6.984 | 19.1164 | 1.8631 | -2.0121 | 0 | 11.6667 | 11.6667 | 18.522 | 0
107 | 20 | 0 | 0 |  | 0.17309 | 0.44757 | 0.26405 | 6.984 | 20.1164 | 2.1249 | -10.2103 | 0 | 0 | 0 | 0 | 0
107 | 21 | 0 | 0 |  | 0.17309 | 0.44757 | 0.26405 | 6.984 | 21.1164 | 2.3867 | -17.3374 | 0 | 0 | 0 | 0 | 0
107 | 22 | 0 | 0 |  | 0.17309 | 0.44757 | 0.26405 | 6.984 | 22.1164 | 2.6485 | -22.8981 | 0 | 0 | 0 | 0 | 0
107 | 23 | 0 | 0 |  | 0.17309 | 0.44757 | 0.26405 | 6.984 | 23.1164 | 2.9103 | -26.381 | 0 | 0 | 0 | 0 | 0
107 | 24 | 0 | 0 |  | 0.17309 | 0.44757 | 0.26405 | 6.984 | 24.1164 | 3.1721 | -27.385 | 0 | 0 | 0 | 0 | 0
108 | 1 | 0 | 0 |  | 0.17933 | 0.46478 | 0.50588 | 7.2259 | 1.1204 | -2.8483 | -25.4175 | 0 | 0 | 0 | 0 | 0
108 | 2 | 0 | 0 |  | 0.17933 | 0.46478 | 0.50588 | 7.2259 | 2.1204 | -2.5865 | -21.4143 | 0 | 0 | 0 | 0 | 0
108 | 3 | 0 | 0 |  | 0.17933 | 0.46478 | 0.50588 | 7.2259 | 3.1204 | -2.3247 | -15.4537 | 0 | 0 | 0 | 0 | 0
108 | 4 | 0 | 0 |  | 0.17933 | 0.46478 | 0.50588 | 7.2259 | 4.1204 | -2.0629 | -8.047 | 0 | 0 | 0 | 0 | 0
108 | 5 | 0 | 0 |  | 0.17933 | 0.46478 | 0.50588 | 7.2259 | 5.1204 | -1.8011 | 0.32642 | 0 | 0 | 0 | 0 | 0
108 | 6 | 0 | 10 |  | 0.17933 | 0.46478 | 0.50588 | 7.2259 | 6.1204 | -1.5393 | 9.2451 | 0 | 8.3333 | 8.3333 | 13.23 | 0
108 | 7 | 0 | 55 |  | 0.17933 | 0.46478 | 0.50588 | 7.2259 | 7.1204 | -1.2775 | 18.3208 | 0 | 45.8333 | 45.8333 | 72.765 | 1
108 | 8 | 0 | 112 |  | 0.17933 | 0.46478 | 0.50588 | 7.2259 | 8.1204 | -1.0157 | 27.1462 | 0 | 93.3333 | 93.3333 | 148.176 | 1
108 | 9 | 78 | 226 |  | 0.17933 | 0.46478 | 0.50588 | 7.2259 | 9.1204 | -0.75387 | 35.223 | 56.9915 | 188.3333 | 245.3249 | 389.4778 | 1
108 | 10 | 95 | 281 |  | 0.17933 | 0.46478 | 0.50588 | 7.2259 | 10.1204 | -0.49207 | 41.8837 | 82.5493 | 234.1667 | 316.716 | 502.8183 | 1
108 | 11 | 98 | 322 |  | 0.17933 | 0.46478 | 0.50588 | 7.2259 | 11.1204 | -0.23027 | 46.2737 | 93.3636 | 268.3333 | 361.6969 | 574.23 | 1
108 | 12 | 100 | 343 |  | 0.17933 | 0.46478 | 0.50588 | 7.2259 | 12.1204 | 0.031529 | 47.5698 | 97.6202 | 285.8333 | 383.4536 | 608.7709 | 1
108 | 13 | 100 | 340 |  | 0.17933 | 0.46478 | 0.50588 | 7.2259 | 13.1204 | 0.29333 | 45.4727 | 93.7875 | 283.3333 | 377.1208 | 598.7171 | 1
108 | 14 | 98 | 314 |  | 0.17933 | 0.46478 | 0.50588 | 7.2259 | 14.1204 | 0.55513 | 40.4523 | 82.3514 | 261.6667 | 344.0181 | 546.1631 | 1
108 | 15 | 93 | 268 |  | 0.17933 | 0.46478 | 0.50588 | 7.2259 | 15.1204 | 0.81693 | 33.3784 | 64.1874 | 223.3333 | 287.5207 | 456.4678 | 1
108 | 16 | 44 | 224 |  | 0.17933 | 0.46478 | 0.50588 | 7.2259 | 16.1204 | 1.0787 | 25.0678 | 21.899 | 186.6667 | 208.5657 | 331.1189 | 1
108 | 17 | 143 | 150 |  | 0.17933 | 0.46478 | 0.50588 | 7.2259 | 17.1204 | 1.3405 | 16.1414 | 39.4668 | 125 | 164.4668 | 261.1076 | 1
108 | 18 | 240 | 71 |  | 0.17933 | 0.46478 | 0.50588 | 7.2259 | 18.1204 | 1.6023 | 7.068 | 9.6379 | 59.1667 | 68.8046 | 109.2341 | 0
108 | 19 | 0 | 18 |  | 0.17933 | 0.46478 | 0.50588 | 7.2259 | 19.1204 | 1.8641 | -1.7554 | 0 | 15 | 15 | 23.814 | 0
108 | 20 | 0 | 0 |  | 0.17933 | 0.46478 | 0.50588 | 7.2259 | 20.1204 | 2.1259 | -9.9365 | 0 | 0 | 0 | 0 | 0
108 | 21 | 0 | 0 |  | 0.17933 | 0.46478 | 0.50588 | 7.2259 | 21.1204 | 2.3877 | -17.0409 | 0 | 0 | 0 | 0 | 0
108 | 22 | 0 | 0 |  | 0.17933 | 0.46478 | 0.50588 | 7.2259 | 22.1204 | 2.6495 | -22.5764 | 0 | 0 | 0 | 0 | 0
108 | 23 | 0 | 0 |  | 0.17933 | 0.46478 | 0.50588 | 7.2259 | 23.1204 | 2.9113 | -26.0366 | 0 | 0 | 0 | 0 | 0
108 | 24 | 0 | 0 |  | 0.17933 | 0.46478 | 0.50588 | 7.2259 | 24.1204 | 3.1731 | -27.026 | 0 | 0 | 0 | 0 | 0
109 | 1 | 0 | 0 |  | 0.18553 | 0.482 | 0.74054 | 7.4605 | 1.1243 | -2.8472 | -25.0578 | 0 | 0 | 0 | 0 | 0
109 | 2 | 0 | 0 |  | 0.18553 | 0.482 | 0.74054 | 7.4605 | 2.1243 | -2.5854 | -21.0609 | 0 | 0 | 0 | 0 | 0
109 | 3 | 0 | 0 |  | 0.18553 | 0.482 | 0.74054 | 7.4605 | 3.1243 | -2.3236 | -15.1116 | 0 | 0 | 0 | 0 | 0
109 | 4 | 0 | 0 |  | 0.18553 | 0.482 | 0.74054 | 7.4605 | 4.1243 | -2.0618 | -7.7168 | 0 | 0 | 0 | 0 | 0
109 | 5 | 0 | 0 |  | 0.18553 | 0.482 | 0.74054 | 7.4605 | 5.1243 | -1.8 | 0.64719 | 0 | 0 | 0 | 0 | 0
109 | 6 | 0 | 18 |  | 0.18553 | 0.482 | 0.74054 | 7.4605 | 6.1243 | -1.5382 | 9.5608 | 0 | 15 | 15 | 23.814 | 0
109 | 7 | 7 | 90 |  | 0.18553 | 0.482 | 0.74054 | 7.4605 | 7.1243 | -1.2764 | 18.6371 | 2.3395 | 75 | 77.3395 | 122.7843 | 1
109 | 8 | 165 | 171 |  | 0.18553 | 0.482 | 0.74054 | 7.4605 | 8.1243 | -1.0146 | 27.4691 | 90.7282 | 142.5 | 233.2282 | 370.2731 | 1
109 | 9 | 62 | 240 |  | 0.18553 | 0.482 | 0.74054 | 7.4605 | 9.1243 | -0.75285 | 35.5582 | 45.4392 | 200 | 245.4392 | 389.6593 | 1
109 | 10 | 57 | 310 |  | 0.18553 | 0.482 | 0.74054 | 7.4605 | 10.1243 | -0.49105 | 42.2337 | 49.6364 | 258.3333 | 307.9698 | 488.9328 | 1
109 | 11 | 59 | 355 |  | 0.18553 | 0.482 | 0.74054 | 7.4605 | 11.1243 | -0.22925 | 46.6333 | 56.3003 | 295.8333 | 352.1336 | 559.0473 | 1
109 | 12 | 102 | 346 |  | 0.18553 | 0.482 | 0.74054 | 7.4605 | 12.1243 | 0.032553 | 47.9232 | 99.7036 | 288.3333 | 388.0369 | 616.0474 | 1
109 | 13 | 487 | 324 |  | 0.18553 | 0.482 | 0.74054 | 7.4605 | 13.1243 | 0.29435 | 45.802 | 457.2753 | 270 | 727.2753 | 1154.6223 | 1
109 | 14 | 275 | 308 |  | 0.18553 | 0.482 | 0.74054 | 7.4605 | 14.1243 | 0.55615 | 40.7502 | 231.3574 | 256.6667 | 488.0241 | 774.787 | 1
109 | 15 | 595 | 221 |  | 0.18553 | 0.482 | 0.74054 | 7.4605 | 15.1243 | 0.81795 | 33.6489 | 411.2342 | 184.1667 | 595.4008 | 945.2584 | 1
109 | 16 | 198 | 225 |  | 0.18553 | 0.482 | 0.74054 | 7.4605 | 16.1243 | 1.0798 | 25.3204 | 98.7518 | 187.5 | 286.2518 | 454.4534 | 1
109 | 17 | 155 | 150 |  | 0.18553 | 0.482 | 0.74054 | 7.4605 | 17.1243 | 1.3415 | 16.386 | 42.9663 | 125 | 167.9663 | 266.6633 | 1
109 | 18 | 109 | 82 |  | 0.18553 | 0.482 | 0.74054 | 7.4605 | 18.1243 | 1.6033 | 7.314 | 4.5359 | 68.3333 | 72.8692 | 115.6872 | 0
109 | 19 | 0 | 13 |  | 0.18553 | 0.482 | 0.74054 | 7.4605 | 19.1243 | 1.8651 | -1.4996 | 0 | 10.8333 | 10.8333 | 17.199 | 0
109 | 20 | 0 | 0 |  | 0.18553 | 0.482 | 0.74054 | 7.4605 | 20.1243 | 2.1269 | -9.6638 | 0 | 0 | 0 | 0 | 0
109 | 21 | 0 | 0 |  | 0.18553 | 0.482 | 0.74054 | 7.4605 | 21.1243 | 2.3887 | -16.7458 | 0 | 0 | 0 | 0 | 0
109 | 22 | 0 | 0 |  | 0.18553 | 0.482 | 0.74054 | 7.4605 | 22.1243 | 2.6505 | -22.2565 | 0 | 0 | 0 | 0 | 0
109 | 23 | 0 | 0 |  | 0.18553 | 0.482 | 0.74054 | 7.4605 | 23.1243 | 2.9123 | -25.6944 | 0 | 0 | 0 | 0 | 0
109 | 24 | 0 | 0 |  | 0.18553 | 0.482 | 0.74054 | 7.4605 | 24.1243 | 3.1741 | -26.6696 | 0 | 0 | 0 | 0 | 0
110 | 1 | 0 | 0 |  | 0.19168 | 0.49921 | 0.96776 | 7.6878 | 1.1281 | -2.8462 | -24.7012 | 0 | 0 | 0 | 0 | 0
110 | 2 | 0 | 0 |  | 0.19168 | 0.49921 | 0.96776 | 7.6878 | 2.1281 | -2.5844 | -20.7107 | 0 | 0 | 0 | 0 | 0
110 | 3 | 0 | 0 |  | 0.19168 | 0.49921 | 0.96776 | 7.6878 | 3.1281 | -2.3227 | -14.7727 | 0 | 0 | 0 | 0 | 0
110 | 4 | 0 | 0 |  | 0.19168 | 0.49921 | 0.96776 | 7.6878 | 4.1281 | -2.0609 | -7.3899 | 0 | 0 | 0 | 0 | 0
110 | 5 | 0 | 0 |  | 0.19168 | 0.49921 | 0.96776 | 7.6878 | 5.1281 | -1.7991 | 0.96457 | 0 | 0 | 0 | 0 | 0
110 | 6 | 16 | 33 |  | 0.19168 | 0.49921 | 0.96776 | 7.6878 | 6.1281 | -1.5373 | 9.8731 | 1.6614 | 27.5 | 29.1614 | 46.2966 | 0
110 | 7 | 286 | 91 |  | 0.19168 | 0.49921 | 0.96776 | 7.6878 | 7.1281 | -1.2755 | 18.9498 | 96.4107 | 75.8333 | 172.2441 | 273.4547 | 1
110 | 8 | 428 | 151 |  | 0.19168 | 0.49921 | 0.96776 | 7.6878 | 8.1281 | -1.0137 | 27.7883 | 236.4265 | 125.8333 | 362.2598 | 575.1237 | 1
110 | 9 | 76 | 236 |  | 0.19168 | 0.49921 | 0.96776 | 7.6878 | 9.1281 | -0.75185 | 35.8897 | 55.8643 | 196.6667 | 252.531 | 400.9182 | 1
110 | 10 | 138 | 363 |  | 0.19168 | 0.49921 | 0.96776 | 7.6878 | 10.1281 | -0.49005 | 42.5803 | 120.4228 | 302.5 | 422.9228 | 671.4322 | 1
110 | 11 | 651 | 257 |  | 0.19168 | 0.49921 | 0.96776 | 7.6878 | 11.1281 | -0.22826 | 46.9898 | 622.186 | 214.1667 | 836.3526 | 1327.7934 | 1
110 | 12 | 893 | 98 |  | 0.19168 | 0.49921 | 0.96776 | 7.6878 | 12.1281 | 0.033544 | 48.2738 | 873.9993 | 81.6667 | 955.6659 | 1517.2152 | 1
110 | 13 | 870 | 105 |  | 0.19168 | 0.49921 | 0.96776 | 7.6878 | 13.1281 | 0.29534 | 46.1288 | 817.8123 | 87.5 | 905.3123 | 1437.2738 | 1
110 | 14 | 874 | 92 |  | 0.19168 | 0.49921 | 0.96776 | 7.6878 | 14.1281 | 0.55714 | 41.0458 | 736.1276 | 76.6667 | 812.7943 | 1290.3922 | 1
110 | 15 | 729 | 142 |  | 0.19168 | 0.49921 | 0.96776 | 7.6878 | 15.1281 | 0.81894 | 33.9175 | 504.5383 | 118.3333 | 622.8717 | 988.871 | 1
110 | 16 | 708 | 100 |  | 0.19168 | 0.49921 | 0.96776 | 7.6878 | 16.1281 | 1.0807 | 25.5713 | 353.846 | 83.3333 | 437.1793 | 694.0659 | 1
110 | 17 | 438 | 132 |  | 0.19168 | 0.49921 | 0.96776 | 7.6878 | 17.1281 | 1.3425 | 16.6293 | 121.9458 | 110 | 231.9458 | 368.2372 | 1
110 | 18 | 227 | 82 |  | 0.19168 | 0.49921 | 0.96776 | 7.6878 | 18.1281 | 1.6043 | 7.5589 | 9.7793 | 68.3333 | 78.1126 | 124.0115 | 0
110 | 19 | 0 | 20 |  | 0.19168 | 0.49921 | 0.96776 | 7.6878 | 19.1281 | 1.8661 | -1.2449 | 0 | 16.6667 | 16.6667 | 26.46 | 0
110 | 20 | 0 | 0 |  | 0.19168 | 0.49921 | 0.96776 | 7.6878 | 20.1281 | 2.1279 | -9.3923 | 0 | 0 | 0 | 0 | 0
110 | 21 | 0 | 0 |  | 0.19168 | 0.49921 | 0.96776 | 7.6878 | 21.1281 | 2.3897 | -16.4521 | 0 | 0 | 0 | 0 | 0
110 | 22 | 0 | 0 |  | 0.19168 | 0.49921 | 0.96776 | 7.6878 | 22.1281 | 2.6515 | -21.9384 | 0 | 0 | 0 | 0 | 0
110 | 23 | 0 | 0 |  | 0.19168 | 0.49921 | 0.96776 | 7.6878 | 23.1281 | 2.9133 | -25.3546 | 0 | 0 | 0 | 0 | 0
110 | 24 | 0 | 0 |  | 0.19168 | 0.49921 | 0.96776 | 7.6878 | 24.1281 | 3.1751 | -26.316 | 0 | 0 | 0 | 0 | 0
111 | 1 | 0 | 0 |  | 0.19778 | 0.51643 | 1.1873 | 7.9073 | 1.1318 | -2.8453 | -24.3479 | 0 | 0 | 0 | 0 | 0
111 | 2 | 0 | 0 |  | 0.19778 | 0.51643 | 1.1873 | 7.9073 | 2.1318 | -2.5835 | -20.3638 | 0 | 0 | 0 | 0 | 0
111 | 3 | 0 | 0 |  | 0.19778 | 0.51643 | 1.1873 | 7.9073 | 3.1318 | -2.3217 | -14.4373 | 0 | 0 | 0 | 0 | 0
111 | 4 | 0 | 0 |  | 0.19778 | 0.51643 | 1.1873 | 7.9073 | 4.1318 | -2.0599 | -7.0665 | 0 | 0 | 0 | 0 | 0
111 | 5 | 0 | 1 |  | 0.19778 | 0.51643 | 1.1873 | 7.9073 | 5.1318 | -1.7981 | 1.2784 | 0 | 0.83333 | 0.83333 | 1.323 | 0
111 | 6 | 29 | 36 |  | 0.19778 | 0.51643 | 1.1873 | 7.9073 | 6.1318 | -1.5363 | 10.1818 | 3.1022 | 30 | 33.1022 | 52.5531 | 0
111 | 7 | 322 | 91 |  | 0.19778 | 0.51643 | 1.1873 | 7.9073 | 7.1318 | -1.2745 | 19.2588 | 109.4544 | 75.8333 | 185.2878 | 294.1628 | 1
111 | 8 | 505 | 131 |  | 0.19778 | 0.51643 | 1.1873 | 7.9073 | 8.1318 | -1.0127 | 28.1039 | 280.2072 | 109.1667 | 389.3739 | 618.17 | 1
111 | 9 | 634 | 152 |  | 0.19778 | 0.51643 | 1.1873 | 7.9073 | 9.1318 | -0.7509 | 36.2176 | 467.3602 | 126.6667 | 594.0268 | 943.077 | 1
111 | 10 | 344 | 305 |  | 0.19778 | 0.51643 | 1.1873 | 7.9073 | 10.1318 | -0.4891 | 42.9233 | 300.7879 | 254.1667 | 554.9546 | 881.0459 | 1
111 | 11 | 742 | 182 |  | 0.19778 | 0.51643 | 1.1873 | 7.9073 | 11.1318 | -0.2273 | 47.343 | 710.2287 | 151.6667 | 861.8953 | 1368.345 | 1
111 | 12 | 861 | 112 |  | 0.19778 | 0.51643 | 1.1873 | 7.9073 | 12.1318 | 0.034502 | 48.6215 | 843.7046 | 93.3333 | 937.038 | 1487.6414 | 1
111 | 13 | 103 | 346 |  | 0.19778 | 0.51643 | 1.1873 | 7.9073 | 13.1318 | 0.2963 | 46.453 | 96.9258 | 288.3333 | 385.2591 | 611.6374 | 1
111 | 14 | 100 | 321 |  | 0.19778 | 0.51643 | 1.1873 | 7.9073 | 14.1318 | 0.5581 | 41.339 | 84.3176 | 267.5 | 351.8176 | 558.5456 | 1
111 | 15 | 56 | 299 |  | 0.19778 | 0.51643 | 1.1873 | 7.9073 | 15.1318 | 0.8199 | 34.1841 | 38.8095 | 249.1667 | 287.9762 | 457.191 | 1
111 | 16 | 45 | 231 |  | 0.19778 | 0.51643 | 1.1873 | 7.9073 | 16.1318 | 1.0817 | 25.8206 | 22.5366 | 192.5 | 215.0366 | 341.3921 | 1
111 | 17 | 19 | 156 |  | 0.19778 | 0.51643 | 1.1873 | 7.9073 | 17.1318 | 1.3435 | 16.8713 | 5.313 | 130 | 135.313 | 214.8229 | 1
111 | 18 | 1 | 74 |  | 0.19778 | 0.51643 | 1.1873 | 7.9073 | 18.1318 | 1.6053 | 7.8026 | 0.044559 | 61.6667 | 61.7112 | 97.9727 | 0
111 | 19 | 0 | 12 |  | 0.19778 | 0.51643 | 1.1873 | 7.9073 | 19.1318 | 1.8671 | -0.99142 | 0 | 10 | 10 | 15.876 | 0
111 | 20 | 0 | 0 |  | 0.19778 | 0.51643 | 1.1873 | 7.9073 | 20.1318 | 2.1289 | -9.122 | 0 | 0 | 0 | 0 | 0
111 | 21 | 0 | 0 |  | 0.19778 | 0.51643 | 1.1873 | 7.9073 | 21.1318 | 2.3907 | -16.16 | 0 | 0 | 0 | 0 | 0
111 | 22 | 0 | 0 |  | 0.19778 | 0.51643 | 1.1873 | 7.9073 | 22.1318 | 2.6525 | -21.6222 | 0 | 0 | 0 | 0 | 0
111 | 23 | 0 | 0 |  | 0.19778 | 0.51643 | 1.1873 | 7.9073 | 23.1318 | 2.9143 | -25.0172 | 0 | 0 | 0 | 0 | 0
111 | 24 | 0 | 0 |  | 0.19778 | 0.51643 | 1.1873 | 7.9073 | 24.1318 | 3.1761 | -25.9652 | 0 | 0 | 0 | 0 | 0
112 | 1 | 0 | 0 |  | 0.20383 | 0.53364 | 1.399 | 8.119 | 1.1353 | -2.8444 | -23.9978 | 0 | 0 | 0 | 0 | 0
112 | 2 | 0 | 0 |  | 0.20383 | 0.53364 | 1.399 | 8.119 | 2.1353 | -2.5826 | -20.0204 | 0 | 0 | 0 | 0 | 0
112 | 3 | 0 | 0 |  | 0.20383 | 0.53364 | 1.399 | 8.119 | 3.1353 | -2.3208 | -14.1054 | 0 | 0 | 0 | 0 | 0
112 | 4 | 0 | 0 |  | 0.20383 | 0.53364 | 1.399 | 8.119 | 4.1353 | -2.059 | -6.7466 | 0 | 0 | 0 | 0 | 0
112 | 5 | 0 | 1 |  | 0.20383 | 0.53364 | 1.399 | 8.119 | 5.1353 | -1.7972 | 1.5887 | 0 | 0.83333 | 0.83333 | 1.323 | 0
112 | 6 | 0 | 30 |  | 0.20383 | 0.53364 | 1.399 | 8.119 | 6.1353 | -1.5354 | 10.4868 | 0 | 25 | 25 | 39.69 | 0
112 | 7 | 80 | 107 |  | 0.20383 | 0.53364 | 1.399 | 8.119 | 7.1353 | -1.2736 | 19.5641 | 27.4143 | 89.1667 | 116.581 | 185.084 | 1
112 | 8 | 157 | 182 |  | 0.20383 | 0.53364 | 1.399 | 8.119 | 8.1353 | -1.0118 | 28.4156 | 87.4913 | 151.6667 | 239.158 | 379.6872 | 1
112 | 9 | 61 | 247 |  | 0.20383 | 0.53364 | 1.399 | 8.119 | 9.1353 | -0.74997 | 36.5416 | 45.0913 | 205.8333 | 250.9247 | 398.368 | 1
112 | 10 | 57 | 317 |  | 0.20383 | 0.53364 | 1.399 | 8.119 | 10.1353 | -0.48817 | 43.2627 | 49.9365 | 264.1667 | 314.1031 | 498.6701 | 1
112 | 11 | 139 | 420 |  | 0.20383 | 0.53364 | 1.399 | 8.119 | 11.1353 | -0.22637 | 47.6929 | 133.2412 | 350 | 483.2412 | 767.1938 | 1
112 | 12 | 159 | 431 |  | 0.20383 | 0.53364 | 1.399 | 8.119 | 12.1353 | 0.035426 | 48.9663 | 155.9879 | 359.1667 | 515.1546 | 817.8595 | 1
112 | 13 | 580 | 297 |  | 0.20383 | 0.53364 | 1.399 | 8.119 | 13.1353 | 0.29723 | 46.7744 | 546.3624 | 247.5 | 793.8624 | 1260.3359 | 1
112 | 14 | 772 | 134 |  | 0.20383 | 0.53364 | 1.399 | 8.119 | 14.1353 | 0.55902 | 41.6299 | 651.6259 | 111.6667 | 763.2926 | 1211.8033 | 1
112 | 15 | 470 | 258 |  | 0.20383 | 0.53364 | 1.399 | 8.119 | 15.1353 | 0.82082 | 34.4487 | 326.1531 | 215 | 541.1531 | 859.1347 | 1
112 | 16 | 312 | 226 |  | 0.20383 | 0.53364 | 1.399 | 8.119 | 16.1353 | 1.0826 | 26.0682 | 156.5736 | 188.3333 | 344.907 | 547.5743 | 1
112 | 17 | 242 | 158 |  | 0.20383 | 0.53364 | 1.399 | 8.119 | 17.1353 | 1.3444 | 17.1118 | 67.9667 | 131.6667 | 199.6333 | 316.9379 | 1
112 | 18 | 94 | 93 |  | 0.20383 | 0.53364 | 1.399 | 8.119 | 18.1353 | 1.6062 | 8.0451 | 4.3286 | 77.5 | 81.8286 | 129.9111 | 0
112 | 19 | 0 | 20 |  | 0.20383 | 0.53364 | 1.399 | 8.119 | 19.1353 | 1.868 | -0.7391 | 0 | 16.6667 | 16.6667 | 26.46 | 0
112 | 20 | 0 | 0 |  | 0.20383 | 0.53364 | 1.399 | 8.119 | 20.1353 | 2.1298 | -8.8531 | 0 | 0 | 0 | 0 | 0
112 | 21 | 0 | 0 |  | 0.20383 | 0.53364 | 1.399 | 8.119 | 21.1353 | 2.3916 | -15.8694 | 0 | 0 | 0 | 0 | 0
112 | 22 | 0 | 0 |  | 0.20383 | 0.53364 | 1.399 | 8.119 | 22.1353 | 2.6534 | -21.3081 | 0 | 0 | 0 | 0 | 0
112 | 23 | 0 | 0 |  | 0.20383 | 0.53364 | 1.399 | 8.119 | 23.1353 | 2.9152 | -24.6823 | 0 | 0 | 0 | 0 | 0
112 | 24 | 0 | 0 |  | 0.20383 | 0.53364 | 1.399 | 8.119 | 24.1353 | 3.177 | -25.6175 | 0 | 0 | 0 | 0 | 0
113 | 1 | 0 | 0 |  | 0.20983 | 0.55085 | 1.6026 | 8.3226 | 1.1387 | -2.8435 | -23.6512 | 0 | 0 | 0 | 0 | 0
113 | 2 | 0 | 0 |  | 0.20983 | 0.55085 | 1.6026 | 8.3226 | 2.1387 | -2.5817 | -19.6806 | 0 | 0 | 0 | 0 | 0
113 | 3 | 0 | 0 |  | 0.20983 | 0.55085 | 1.6026 | 8.3226 | 3.1387 | -2.3199 | -13.7771 | 0 | 0 | 0 | 0 | 0
113 | 4 | 0 | 0 |  | 0.20983 | 0.55085 | 1.6026 | 8.3226 | 4.1387 | -2.0581 | -6.4305 | 0 | 0 | 0 | 0 | 0
113 | 5 | 0 | 1 |  | 0.20983 | 0.55085 | 1.6026 | 8.3226 | 5.1387 | -1.7963 | 1.8952 | 0 | 0.83333 | 0.83333 | 1.323 | 0
113 | 6 | 0 | 26 |  | 0.20983 | 0.55085 | 1.6026 | 8.3226 | 6.1387 | -1.5345 | 10.788 | 0 | 21.6667 | 21.6667 | 34.398 | 0
113 | 7 | 12 | 99 |  | 0.20983 | 0.55085 | 1.6026 | 8.3226 | 7.1387 | -1.2727 | 19.8654 | 4.1445 | 82.5 | 86.6445 | 137.5568 | 1
113 | 8 | 13 | 189 |  | 0.20983 | 0.55085 | 1.6026 | 8.3226 | 8.1387 | -1.0109 | 28.7233 | 7.2749 | 157.5 | 164.7749 | 261.5967 | 1
113 | 9 | 4 | 175 |  | 0.20983 | 0.55085 | 1.6026 | 8.3226 | 9.1387 | -0.74908 | 36.8617 | 2.9647 | 145.8333 | 148.7981 | 236.2318 | 1
113 | 10 | 103 | 288 |  | 0.20983 | 0.55085 | 1.6026 | 8.3226 | 10.1387 | -0.48728 | 43.5983 | 90.4044 | 240 | 330.4044 | 524.5501 | 1
113 | 11 | 99 | 334 |  | 0.20983 | 0.55085 | 1.6026 | 8.3226 | 11.1387 | -0.22549 | 48.0394 | 95.0306 | 278.3333 | 373.3639 | 592.7526 | 1
113 | 12 | 100 | 354 |  | 0.20983 | 0.55085 | 1.6026 | 8.3226 | 12.1387 | 0.036314 | 49.3079 | 98.2155 | 295 | 393.2155 | 624.2689 | 1
113 | 13 | 244 | 364 |  | 0.20983 | 0.55085 | 1.6026 | 8.3226 | 13.1387 | 0.29811 | 47.0931 | 230.0786 | 303.3333 | 533.412 | 846.8449 | 1
113 | 14 | 89 | 331 |  | 0.20983 | 0.55085 | 1.6026 | 8.3226 | 14.1387 | 0.55991 | 41.9183 | 75.2005 | 275.8333 | 351.0338 | 557.3012 | 1
113 | 15 | 95 | 278 |  | 0.20983 | 0.55085 | 1.6026 | 8.3226 | 15.1387 | 0.82171 | 34.7112 | 66.0102 | 231.6667 | 297.6769 | 472.5918 | 1
113 | 16 | 46 | 235 |  | 0.20983 | 0.55085 | 1.6026 | 8.3226 | 16.1387 | 1.0835 | 26.3141 | 23.1316 | 195.8333 | 218.9649 | 347.6287 | 1
113 | 17 | 20 | 160 |  | 0.20983 | 0.55085 | 1.6026 | 8.3226 | 17.1387 | 1.3453 | 17.3509 | 5.6416 | 133.3333 | 138.9749 | 220.6366 | 1
113 | 18 | 2 | 77 |  | 0.20983 | 0.55085 | 1.6026 | 8.3226 | 18.1387 | 1.6071 | 8.2862 | 0.095101 | 64.1667 | 64.2618 | 102.022 | 0
113 | 19 | 0 | 17 |  | 0.20983 | 0.55085 | 1.6026 | 8.3226 | 19.1387 | 1.8689 | -0.48806 | 0 | 14.1667 | 14.1667 | 22.491 | 0
113 | 20 | 0 | 0 |  | 0.20983 | 0.55085 | 1.6026 | 8.3226 | 20.1387 | 2.1307 | -8.5855 | 0 | 0 | 0 | 0 | 0
113 | 21 | 0 | 0 |  | 0.20983 | 0.55085 | 1.6026 | 8.3226 | 21.1387 | 2.3925 | -15.5805 | 0 | 0 | 0 | 0 | 0
113 | 22 | 0 | 0 |  | 0.20983 | 0.55085 | 1.6026 | 8.3226 | 22.1387 | 2.6543 | -20.9961 | 0 | 0 | 0 | 0 | 0
113 | 23 | 0 | 0 |  | 0.20983 | 0.55085 | 1.6026 | 8.3226 | 23.1387 | 2.9161 | -24.3501 | 0 | 0 | 0 | 0 | 0
113 | 24 | 0 | 0 |  | 0.20983 | 0.55085 | 1.6026 | 8.3226 | 24.1387 | 3.1779 | -25.2729 | 0 | 0 | 0 | 0 | 0
114 | 1 | 0 | 0 |  | 0.21577 | 0.56807 | 1.7979 | 8.5179 | 1.142 | -2.8426 | -23.308 | 0 | 0 | 0 | 0 | 0
114 | 2 | 0 | 0 |  | 0.21577 | 0.56807 | 1.7979 | 8.5179 | 2.142 | -2.5808 | -19.3444 | 0 | 0 | 0 | 0 | 0
114 | 3 | 0 | 0 |  | 0.21577 | 0.56807 | 1.7979 | 8.5179 | 3.142 | -2.319 | -13.4526 | 0 | 0 | 0 | 0 | 0
114 | 4 | 0 | 0 |  | 0.21577 | 0.56807 | 1.7979 | 8.5179 | 4.142 | -2.0572 | -6.1181 | 0 | 0 | 0 | 0 | 0
114 | 5 | 0 | 1 |  | 0.21577 | 0.56807 | 1.7979 | 8.5179 | 5.142 | -1.7954 | 2.1979 | 0 | 0.83333 | 0.83333 | 1.323 | 0
114 | 6 | 0 | 27 |  | 0.21577 | 0.56807 | 1.7979 | 8.5179 | 6.142 | -1.5336 | 11.0853 | 0 | 22.5 | 22.5 | 35.721 | 0
114 | 7 | 13 | 101 |  | 0.21577 | 0.56807 | 1.7979 | 8.5179 | 7.142 | -1.2718 | 20.1628 | 4.5241 | 84.1667 | 88.6908 | 140.8055 | 1
114 | 8 | 13 | 191 |  | 0.21577 | 0.56807 | 1.7979 | 8.5179 | 8.142 | -1.01 | 29.0269 | 7.3045 | 159.1667 | 166.4711 | 264.2896 | 1
114 | 9 | 58 | 253 |  | 0.21577 | 0.56807 | 1.7979 | 8.5179 | 9.142 | -0.74823 | 37.1777 | 43.0994 | 210.8333 | 253.9327 | 403.1436 | 1
114 | 10 | 4 | 221 |  | 0.21577 | 0.56807 | 1.7979 | 8.5179 | 10.142 | -0.48643 | 43.9301 | 3.5172 | 184.1667 | 187.6838 | 297.9668 | 1
114 | 11 | 14 | 245 |  | 0.21577 | 0.56807 | 1.7979 | 8.5179 | 11.142 | -0.22463 | 48.3824 | 13.4566 | 204.1667 | 217.6233 | 345.4987 | 1
114 | 12 | 15 | 259 |  | 0.21577 | 0.56807 | 1.7979 | 8.5179 | 12.142 | 0.037166 | 49.6464 | 14.7481 | 215.8333 | 230.5815 | 366.0711 | 1
114 | 13 | 15 | 257 |  | 0.21577 | 0.56807 | 1.7979 | 8.5179 | 13.142 | 0.29897 | 47.409 | 14.1578 | 214.1667 | 228.3244 | 362.4879 | 1
114 | 14 | 14 | 238 |  | 0.21577 | 0.56807 | 1.7979 | 8.5179 | 14.142 | 0.56076 | 42.2042 | 11.8412 | 198.3333 | 210.1745 | 333.6731 | 1
114 | 15 | 10 | 206 |  | 0.21577 | 0.56807 | 1.7979 | 8.5179 | 15.142 | 0.82256 | 34.9715 | 6.9573 | 171.6667 | 178.624 | 283.5834 | 1
114 | 16 | 2 | 162 |  | 0.21577 | 0.56807 | 1.7979 | 8.5179 | 16.142 | 1.0844 | 26.5582 | 1.0078 | 135 | 136.0078 | 215.9259 | 1
114 | 17 | 39 | 155 |  | 0.21577 | 0.56807 | 1.7979 | 8.5179 | 17.142 | 1.3462 | 17.5885 | 11.0491 | 129.1667 | 140.2158 | 222.6066 | 1
114 | 18 | 3 | 79 |  | 0.21577 | 0.56807 | 1.7979 | 8.5179 | 18.142 | 1.608 | 8.5261 | 0.14719 | 65.8333 | 65.9805 | 104.7507 | 0
114 | 19 | 0 | 14 |  | 0.21577 | 0.56807 | 1.7979 | 8.5179 | 19.142 | 1.8698 | -0.23834 | 0 | 11.6667 | 11.6667 | 18.522 | 0
114 | 20 | 0 | 0 |  | 0.21577 | 0.56807 | 1.7979 | 8.5179 | 20.142 | 2.1316 | -8.3195 | 0 | 0 | 0 | 0 | 0
114 | 21 | 0 | 0 |  | 0.21577 | 0.56807 | 1.7979 | 8.5179 | 21.142 | 2.3934 | -15.2933 | 0 | 0 | 0 | 0 | 0
114 | 22 | 0 | 0 |  | 0.21577 | 0.56807 | 1.7979 | 8.5179 | 22.142 | 2.6552 | -20.6863 | 0 | 0 | 0 | 0 | 0
114 | 23 | 0 | 0 |  | 0.21577 | 0.56807 | 1.7979 | 8.5179 | 23.142 | 2.917 | -24.0206 | 0 | 0 | 0 | 0 | 0
114 | 24 | 0 | 0 |  | 0.21577 | 0.56807 | 1.7979 | 8.5179 | 24.142 | 3.1788 | -24.9315 | 0 | 0 | 0 | 0 | 0
115 | 1 | 0 | 0 |  | 0.22165 | 0.58528 | 1.9847 | 8.7047 | 1.1451 | -2.8418 | -22.9686 | 0 | 0 | 0 | 0 | 0
115 | 2 | 0 | 0 |  | 0.22165 | 0.58528 | 1.9847 | 8.7047 | 2.1451 | -2.58 | -19.0121 | 0 | 0 | 0 | 0 | 0
115 | 3 | 0 | 0 |  | 0.22165 | 0.58528 | 1.9847 | 8.7047 | 3.1451 | -2.3182 | -13.1319 | 0 | 0 | 0 | 0 | 0
115 | 4 | 0 | 0 |  | 0.22165 | 0.58528 | 1.9847 | 8.7047 | 4.1451 | -2.0564 | -5.8096 | 0 | 0 | 0 | 0 | 0
115 | 5 | 0 | 1 |  | 0.22165 | 0.58528 | 1.9847 | 8.7047 | 5.1451 | -1.7946 | 2.4966 | 0 | 0.83333 | 0.83333 | 1.323 | 0
115 | 6 | 0 | 18 |  | 0.22165 | 0.58528 | 1.9847 | 8.7047 | 6.1451 | -1.5328 | 11.3785 | 0 | 15 | 15 | 23.814 | 0
115 | 7 | 0 | 67 |  | 0.22165 | 0.58528 | 1.9847 | 8.7047 | 7.1451 | -1.271 | 20.456 | 0 | 55.8333 | 55.8333 | 88.641 | 1
115 | 8 | 0 | 124 |  | 0.22165 | 0.58528 | 1.9847 | 8.7047 | 8.1451 | -1.0092 | 29.3264 | 0 | 103.3333 | 103.3333 | 164.052 | 1
115 | 9 | 4 | 177 |  | 0.22165 | 0.58528 | 1.9847 | 8.7047 | 9.1451 | -0.74742 | 37.4896 | 2.9798 | 147.5 | 150.4798 | 238.9017 | 1
115 | 10 | 11 | 217 |  | 0.22165 | 0.58528 | 1.9847 | 8.7047 | 10.1451 | -0.48562 | 44.2578 | 9.6888 | 180.8333 | 190.5222 | 302.473 | 1
115 | 11 | 14 | 245 |  | 0.22165 | 0.58528 | 1.9847 | 8.7047 | 11.1451 | -0.22382 | 48.7216 | 13.4738 | 204.1667 | 217.6405 | 345.526 | 1
115 | 12 | 5 | 267 |  | 0.22165 | 0.58528 | 1.9847 | 8.7047 | 12.1451 | 0.037981 | 49.9817 | 4.9211 | 222.5 | 227.4211 | 361.0537 | 1
115 | 13 | 15 | 257 |  | 0.22165 | 0.58528 | 1.9847 | 8.7047 | 13.1451 | 0.29978 | 47.7219 | 14.1709 | 214.1667 | 228.3375 | 362.5087 | 1
115 | 14 | 13 | 239 |  | 0.22165 | 0.58528 | 1.9847 | 8.7047 | 14.1451 | 0.56158 | 42.4875 | 11.0061 | 199.1667 | 210.1728 | 333.6703 | 1
115 | 15 | 10 | 206 |  | 0.22165 | 0.58528 | 1.9847 | 8.7047 | 15.1451 | 0.82338 | 35.2297 | 6.9661 | 171.6667 | 178.6327 | 283.5973 | 1
115 | 16 | 2 | 163 |  | 0.22165 | 0.58528 | 1.9847 | 8.7047 | 16.1451 | 1.0852 | 26.8005 | 1.0098 | 135.8333 | 136.8431 | 217.2521 | 1
115 | 17 | 0 | 107 |  | 0.22165 | 0.58528 | 1.9847 | 8.7047 | 17.1451 | 1.347 | 17.8245 | 0 | 89.1667 | 89.1667 | 141.561 | 1
115 | 18 | 0 | 51 |  | 0.22165 | 0.58528 | 1.9847 | 8.7047 | 18.1451 | 1.6088 | 8.7645 | 0 | 42.5 | 42.5 | 67.473 | 0
115 | 19 | 0 | 9 |  | 0.22165 | 0.58528 | 1.9847 | 8.7047 | 19.1451 | 1.8706 | 0.0099852 | 0 | 7.5 | 7.5 | 11.907 | 0
115 | 20 | 0 | 0 |  | 0.22165 | 0.58528 | 1.9847 | 8.7047 | 20.1451 | 2.1324 | -8.0549 | 0 | 0 | 0 | 0 | 0
115 | 21 | 0 | 0 |  | 0.22165 | 0.58528 | 1.9847 | 8.7047 | 21.1451 | 2.3942 | -15.008 | 0 | 0 | 0 | 0 | 0
115 | 22 | 0 | 0 |  | 0.22165 | 0.58528 | 1.9847 | 8.7047 | 22.1451 | 2.656 | -20.3788 | 0 | 0 | 0 | 0 | 0
115 | 23 | 0 | 0 |  | 0.22165 | 0.58528 | 1.9847 | 8.7047 | 23.1451 | 2.9178 | -23.6939 | 0 | 0 | 0 | 0 | 0
115 | 24 | 0 | 0 |  | 0.22165 | 0.58528 | 1.9847 | 8.7047 | 24.1451 | 3.1796 | -24.5934 | 0 | 0 | 0 | 0 | 0
116 | 1 | 0 | 0 |  | 0.22747 | 0.6025 | 2.1628 | 8.8828 | 1.148 | -2.841 | -22.6328 | 0 | 0 | 0 | 0 | 0
116 | 2 | 0 | 0 |  | 0.22747 | 0.6025 | 2.1628 | 8.8828 | 2.148 | -2.5792 | -18.6836 | 0 | 0 | 0 | 0 | 0
116 | 3 | 0 | 0 |  | 0.22747 | 0.6025 | 2.1628 | 8.8828 | 3.148 | -2.3174 | -12.8153 | 0 | 0 | 0 | 0 | 0
116 | 4 | 0 | 0 |  | 0.22747 | 0.6025 | 2.1628 | 8.8828 | 4.148 | -2.0556 | -5.5052 | 0 | 0 | 0 | 0 | 0
116 | 5 | 0 | 1 |  | 0.22747 | 0.6025 | 2.1628 | 8.8828 | 5.148 | -1.7938 | 2.7912 | 0 | 0.83333 | 0.83333 | 1.323 | 0
116 | 6 | 0 | 19 |  | 0.22747 | 0.6025 | 2.1628 | 8.8828 | 6.148 | -1.532 | 11.6676 | 0 | 15.8333 | 15.8333 | 25.137 | 0
116 | 7 | 0 | 68 |  | 0.22747 | 0.6025 | 2.1628 | 8.8828 | 7.148 | -1.2702 | 20.745 | 0 | 56.6667 | 56.6667 | 89.964 | 1
116 | 8 | 0 | 126 |  | 0.22747 | 0.6025 | 2.1628 | 8.8828 | 8.148 | -1.0084 | 29.6215 | 0 | 105 | 105 | 166.698 | 1
116 | 9 | 4 | 178 |  | 0.22747 | 0.6025 | 2.1628 | 8.8828 | 9.148 | -0.74664 | 37.7971 | 2.9869 | 148.3333 | 151.3203 | 240.236 | 1
116 | 10 | 11 | 218 |  | 0.22747 | 0.6025 | 2.1628 | 8.8828 | 10.148 | -0.48484 | 44.5814 | 9.7049 | 181.6667 | 191.3715 | 303.8214 | 1
116 | 11 | 14 | 246 |  | 0.22747 | 0.6025 | 2.1628 | 8.8828 | 11.148 | -0.22304 | 49.0571 | 13.4903 | 205 | 218.4903 | 346.8752 | 1
116 | 12 | 5 | 268 |  | 0.22747 | 0.6025 | 2.1628 | 8.8828 | 12.148 | 0.038758 | 50.3135 | 4.9259 | 223.3333 | 228.2593 | 362.3844 | 1
116 | 13 | 15 | 257 |  | 0.22747 | 0.6025 | 2.1628 | 8.8828 | 13.148 | 0.30056 | 48.0318 | 14.1835 | 214.1667 | 228.3501 | 362.5286 | 1
116 | 14 | 13 | 239 |  | 0.22747 | 0.6025 | 2.1628 | 8.8828 | 14.148 | 0.56236 | 42.7682 | 11.0166 | 199.1667 | 210.1832 | 333.6869 | 1
116 | 15 | 10 | 207 |  | 0.22747 | 0.6025 | 2.1628 | 8.8828 | 15.148 | 0.82416 | 35.4857 | 6.9747 | 172.5 | 179.4747 | 284.934 | 1
116 | 16 | 2 | 163 |  | 0.22747 | 0.6025 | 2.1628 | 8.8828 | 16.148 | 1.086 | 27.041 | 1.0118 | 135.8333 | 136.8451 | 217.2554 | 1
116 | 17 | 0 | 108 |  | 0.22747 | 0.6025 | 2.1628 | 8.8828 | 17.148 | 1.3478 | 18.0589 | 0 | 90 | 90 | 142.884 | 1
116 | 18 | 0 | 52 |  | 0.22747 | 0.6025 | 2.1628 | 8.8828 | 18.148 | 1.6096 | 9.0014 | 0 | 43.3333 | 43.3333 | 68.796 | 0
116 | 19 | 0 | 9 |  | 0.22747 | 0.6025 | 2.1628 | 8.8828 | 19.148 | 1.8714 | 0.25685 | 0 | 7.5 | 7.5 | 11.907 | 0
116 | 20 | 0 | 0 |  | 0.22747 | 0.6025 | 2.1628 | 8.8828 | 20.148 | 2.1332 | -7.792 | 0 | 0 | 0 | 0 | 0
116 | 21 | 0 | 0 |  | 0.22747 | 0.6025 | 2.1628 | 8.8828 | 21.148 | 2.395 | -14.7247 | 0 | 0 | 0 | 0 | 0
116 | 22 | 0 | 0 |  | 0.22747 | 0.6025 | 2.1628 | 8.8828 | 22.148 | 2.6568 | -20.0738 | 0 | 0 | 0 | 0 | 0
116 | 23 | 0 | 0 |  | 0.22747 | 0.6025 | 2.1628 | 8.8828 | 23.148 | 2.9186 | -23.3702 | 0 | 0 | 0 | 0 | 0
116 | 24 | 0 | 0 |  | 0.22747 | 0.6025 | 2.1628 | 8.8828 | 24.148 | 3.1804 | -24.2588 | 0 | 0 | 0 | 0 | 0
117 | 1 | 0 | 0 |  | 0.23324 | 0.61971 | 2.3321 | 9.0521 | 1.1509 | -2.8403 | -22.3009 | 0 | 0 | 0 | 0 | 0
117 | 2 | 0 | 0 |  | 0.23324 | 0.61971 | 2.3321 | 9.0521 | 2.1509 | -2.5785 | -18.3592 | 0 | 0 | 0 | 0 | 0
117 | 3 | 0 | 0 |  | 0.23324 | 0.61971 | 2.3321 | 9.0521 | 3.1509 | -2.3167 | -12.5026 | 0 | 0 | 0 | 0 | 0
117 | 4 | 0 | 0 |  | 0.23324 | 0.61971 | 2.3321 | 9.0521 | 4.1509 | -2.0549 | -5.2048 | 0 | 0 | 0 | 0 | 0
117 | 5 | 0 | 1 |  | 0.23324 | 0.61971 | 2.3321 | 9.0521 | 5.1509 | -1.7931 | 3.0817 | 0 | 0.83333 | 0.83333 | 1.323 | 0
117 | 6 | 0 | 21 |  | 0.23324 | 0.61971 | 2.3321 | 9.0521 | 6.1509 | -1.5313 | 11.9524 | 0 | 17.5 | 17.5 | 27.783 | 0
117 | 7 | 0 | 70 |  | 0.23324 | 0.61971 | 2.3321 | 9.0521 | 7.1509 | -1.2695 | 21.0296 | 0 | 58.3333 | 58.3333 | 92.61 | 1
117 | 8 | 0 | 127 |  | 0.23324 | 0.61971 | 2.3321 | 9.0521 | 8.1509 | -1.0077 | 29.9123 | 0 | 105.8333 | 105.8333 | 168.021 | 1
117 | 9 | 4 | 179 |  | 0.23324 | 0.61971 | 2.3321 | 9.0521 | 9.1509 | -0.7459 | 38.1002 | 2.9938 | 149.1667 | 152.1605 | 241.57 | 1
117 | 10 | 11 | 219 |  | 0.23324 | 0.61971 | 2.3321 | 9.0521 | 10.1509 | -0.4841 | 44.9007 | 9.7202 | 182.5 | 192.2202 | 305.1689 | 1
117 | 11 | 14 | 247 |  | 0.23324 | 0.61971 | 2.3321 | 9.0521 | 11.1509 | -0.2223 | 49.3887 | 13.5061 | 205.8333 | 219.3394 | 348.2232 | 1
117 | 12 | 111 | 348 |  | 0.23324 | 0.61971 | 2.3321 | 9.0521 | 12.1509 | 0.039497 | 50.6419 | 109.4581 | 290 | 399.4581 | 634.1797 | 1
117 | 13 | 65 | 380 |  | 0.23324 | 0.61971 | 2.3321 | 9.0521 | 13.1509 | 0.3013 | 48.3387 | 61.5141 | 316.6667 | 378.1808 | 600.3998 | 1
117 | 14 | 95 | 330 |  | 0.23324 | 0.61971 | 2.3321 | 9.0521 | 14.1509 | 0.5631 | 43.0463 | 80.5801 | 275 | 355.5801 | 564.519 | 1
117 | 15 | 362 | 278 |  | 0.23324 | 0.61971 | 2.3321 | 9.0521 | 15.1509 | 0.8249 | 35.7395 | 252.7926 | 231.6667 | 484.4593 | 769.1276 | 1
117 | 16 | 74 | 226 |  | 0.23324 | 0.61971 | 2.3321 | 9.0521 | 16.1509 | 1.0867 | 27.2795 | 37.5118 | 188.3333 | 225.8451 | 358.5518 | 1
117 | 17 | 20 | 167 |  | 0.23324 | 0.61971 | 2.3321 | 9.0521 | 17.1509 | 1.3485 | 18.2917 | 5.7408 | 139.1667 | 144.9074 | 230.055 | 1
117 | 18 | 50 | 97 |  | 0.23324 | 0.61971 | 2.3321 | 9.0521 | 18.1509 | 1.6103 | 9.2369 | 2.6836 | 80.8333 | 83.517 | 132.5915 | 0
117 | 19 | 0 | 24 |  | 0.23324 | 0.61971 | 2.3321 | 9.0521 | 19.1509 | 1.8721 | 0.50219 | 0 | 20 | 20 | 31.752 | 0
117 | 20 | 0 | 0 |  | 0.23324 | 0.61971 | 2.3321 | 9.0521 | 20.1509 | 2.1339 | -7.5307 | 0 | 0 | 0 | 0 | 0
117 | 21 | 0 | 0 |  | 0.23324 | 0.61971 | 2.3321 | 9.0521 | 21.1509 | 2.3957 | -14.4434 | 0 | 0 | 0 | 0 | 0
117 | 22 | 0 | 0 |  | 0.23324 | 0.61971 | 2.3321 | 9.0521 | 22.1509 | 2.6575 | -19.7712 | 0 | 0 | 0 | 0 | 0
117 | 23 | 0 | 0 |  | 0.23324 | 0.61971 | 2.3321 | 9.0521 | 23.1509 | 2.9193 | -23.0496 | 0 | 0 | 0 | 0 | 0
117 | 24 | 0 | 0 |  | 0.23324 | 0.61971 | 2.3321 | 9.0521 | 24.1509 | 3.1811 | -23.9276 | 0 | 0 | 0 | 0 | 0
118 | 1 | 0 | 0 |  | 0.23894 | 0.63693 | 2.4924 | 9.2124 | 1.1535 | -2.8396 | -21.973 | 0 | 0 | 0 | 0 | 0
118 | 2 | 0 | 0 |  | 0.23894 | 0.63693 | 2.4924 | 9.2124 | 2.1535 | -2.5778 | -18.0389 | 0 | 0 | 0 | 0 | 0
118 | 3 | 0 | 0 |  | 0.23894 | 0.63693 | 2.4924 | 9.2124 | 3.1535 | -2.316 | -12.1942 | 0 | 0 | 0 | 0 | 0
118 | 4 | 0 | 0 |  | 0.23894 | 0.63693 | 2.4924 | 9.2124 | 4.1535 | -2.0542 | -4.9087 | 0 | 0 | 0 | 0 | 0
118 | 5 | 0 | 1 |  | 0.23894 | 0.63693 | 2.4924 | 9.2124 | 5.1535 | -1.7924 | 3.3679 | 0 | 0.83333 | 0.83333 | 1.323 | 0
118 | 6 | 0 | 35 |  | 0.23894 | 0.63693 | 2.4924 | 9.2124 | 6.1535 | -1.5306 | 12.2329 | 0 | 29.1667 | 29.1667 | 46.305 | 0
118 | 7 | 0 | 71 |  | 0.23894 | 0.63693 | 2.4924 | 9.2124 | 7.1535 | -1.2688 | 21.3099 | 0 | 59.1667 | 59.1667 | 93.933 | 1
118 | 8 | 43 | 186 |  | 0.23894 | 0.63693 | 2.4924 | 9.2124 | 8.1535 | -1.007 | 30.1985 | 24.5239 | 155 | 179.5239 | 285.0121 | 1
118 | 9 | 44 | 266 |  | 0.23894 | 0.63693 | 2.4924 | 9.2124 | 9.1535 | -0.7452 | 38.3989 | 33.0049 | 221.6667 | 254.6715 | 404.3165 | 1
118 | 10 | 218 | 320 |  | 0.23894 | 0.63693 | 2.4924 | 9.2124 | 10.1535 | -0.4834 | 45.2157 | 192.9297 | 266.6667 | 459.5963 | 729.6551 | 1
118 | 11 | 609 | 259 |  | 0.23894 | 0.63693 | 2.4924 | 9.2124 | 11.1535 | -0.2216 | 49.7164 | 588.1687 | 215.8333 | 804.0021 | 1276.4337 | 1
118 | 12 | 302 | 327 |  | 0.23894 | 0.63693 | 2.4924 | 9.2124 | 12.1535 | 0.040197 | 50.9668 | 298.0715 | 272.5 | 570.5715 | 905.8394 | 1
118 | 13 | 178 | 421 |  | 0.23894 | 0.63693 | 2.4924 | 9.2124 | 13.1535 | 0.302 | 48.6424 | 168.5921 | 350.8333 | 519.4254 | 824.6398 | 1
118 | 14 | 407 | 305 |  | 0.23894 | 0.63693 | 2.4924 | 9.2124 | 14.1535 | 0.5638 | 43.3216 | 345.5323 | 254.1667 | 599.6989 | 952.082 | 1
118 | 15 | 12 | 208 |  | 0.23894 | 0.63693 | 2.4924 | 9.2124 | 15.1535 | 0.82559 | 35.9909 | 8.39 | 173.3333 | 181.7233 | 288.5039 | 1
118 | 16 | 206 | 233 |  | 0.23894 | 0.63693 | 2.4924 | 9.2124 | 16.1535 | 1.0874 | 27.5161 | 104.6327 | 194.1667 | 298.7994 | 474.3739 | 1
118 | 17 | 38 | 161 |  | 0.23894 | 0.63693 | 2.4924 | 9.2124 | 17.1535 | 1.3492 | 18.5228 | 10.9551 | 134.1667 | 145.1218 | 230.3953 | 1
118 | 18 | 4 | 86 |  | 0.23894 | 0.63693 | 2.4924 | 9.2124 | 18.1535 | 1.611 | 9.4708 | 0.22093 | 71.6667 | 71.8876 | 114.1287 | 0
118 | 19 | 0 | 11 |  | 0.23894 | 0.63693 | 2.4924 | 9.2124 | 19.1535 | 1.8728 | 0.74593 | 0 | 9.1667 | 9.1667 | 14.553 | 0
118 | 20 | 0 | 0 |  | 0.23894 | 0.63693 | 2.4924 | 9.2124 | 20.1535 | 2.1346 | -7.2713 | 0 | 0 | 0 | 0 | 0
118 | 21 | 0 | 0 |  | 0.23894 | 0.63693 | 2.4924 | 9.2124 | 21.1535 | 2.3964 | -14.1642 | 0 | 0 | 0 | 0 | 0
118 | 22 | 0 | 0 |  | 0.23894 | 0.63693 | 2.4924 | 9.2124 | 22.1535 | 2.6582 | -19.4712 | 0 | 0 | 0 | 0 | 0
118 | 23 | 0 | 0 |  | 0.23894 | 0.63693 | 2.4924 | 9.2124 | 23.1535 | 2.92 | -22.7321 | 0 | 0 | 0 | 0 | 0
118 | 24 | 0 | 0 |  | 0.23894 | 0.63693 | 2.4924 | 9.2124 | 24.1535 | 3.1818 | -23.6001 | 0 | 0 | 0 | 0 | 0
119 | 1 | 0 | 0 |  | 0.24457 | 0.65414 | 2.6435 | 9.3635 | 1.1561 | -2.8389 | -21.6491 | 0 | 0 | 0 | 0 | 0
119 | 2 | 0 | 0 |  | 0.24457 | 0.65414 | 2.6435 | 9.3635 | 2.1561 | -2.5771 | -17.7228 | 0 | 0 | 0 | 0 | 0
119 | 3 | 0 | 0 |  | 0.24457 | 0.65414 | 2.6435 | 9.3635 | 3.1561 | -2.3153 | -11.8901 | 0 | 0 | 0 | 0 | 0
119 | 4 | 0 | 0 |  | 0.24457 | 0.65414 | 2.6435 | 9.3635 | 4.1561 | -2.0535 | -4.6169 | 0 | 0 | 0 | 0 | 0
119 | 5 | 0 | 3 |  | 0.24457 | 0.65414 | 2.6435 | 9.3635 | 5.1561 | -1.7917 | 3.6498 | 0 | 2.5 | 2.5 | 3.969 | 0
119 | 6 | 0 | 37 |  | 0.24457 | 0.65414 | 2.6435 | 9.3635 | 6.1561 | -1.5299 | 12.509 | 0 | 30.8333 | 30.8333 | 48.951 | 1
119 | 7 | 16 | 112 |  | 0.24457 | 0.65414 | 2.6435 | 9.3635 | 7.1561 | -1.2681 | 21.5856 | 5.763 | 93.3333 | 99.0964 | 157.3254 | 1
119 | 8 | 13 | 203 |  | 0.24457 | 0.65414 | 2.6435 | 9.3635 | 8.1561 | -1.0063 | 30.4802 | 7.4395 | 169.1667 | 176.6061 | 280.3799 | 1
119 | 9 | 5 | 183 |  | 0.24457 | 0.65414 | 2.6435 | 9.3635 | 9.1561 | -0.74454 | 38.6929 | 3.7585 | 152.5 | 156.2585 | 248.076 | 1
119 | 10 | 101 | 300 |  | 0.24457 | 0.65414 | 2.6435 | 9.3635 | 10.1561 | -0.48274 | 45.5262 | 89.5143 | 250 | 339.5143 | 539.0129 | 1
119 | 11 | 97 | 345 |  | 0.24457 | 0.65414 | 2.6435 | 9.3635 | 11.1561 | -0.22094 | 50.0399 | 93.7815 | 287.5 | 381.2815 | 605.3225 | 1
119 | 12 | 15 | 265 |  | 0.24457 | 0.65414 | 2.6435 | 9.3635 | 12.1561 | 0.040856 | 51.288 | 14.8175 | 220.8333 | 235.6508 | 374.1193 | 1
119 | 13 | 5 | 270 |  | 0.24457 | 0.65414 | 2.6435 | 9.3635 | 13.1561 | 0.30266 | 48.9429 | 4.7395 | 225 | 229.7395 | 364.7344 | 1
119 | 14 | 14 | 243 |  | 0.24457 | 0.65414 | 2.6435 | 9.3635 | 14.1561 | 0.56445 | 43.5941 | 11.896 | 202.5 | 214.396 | 340.3751 | 1
119 | 15 | 11 | 211 |  | 0.24457 | 0.65414 | 2.6435 | 9.3635 | 15.1561 | 0.82625 | 36.2399 | 7.6999 | 175.8333 | 183.5333 | 291.3774 | 1
119 | 16 | 22 | 210 |  | 0.24457 | 0.65414 | 2.6435 | 9.3635 | 16.1561 | 1.0881 | 27.7508 | 11.1965 | 175 | 186.1965 | 295.6056 | 1
119 | 17 | 11 | 174 |  | 0.24457 | 0.65414 | 2.6435 | 9.3635 | 17.1561 | 1.3499 | 18.7522 | 3.1851 | 145 | 148.1851 | 235.2586 | 1
119 | 18 | 5 | 87 |  | 0.24457 | 0.65414 | 2.6435 | 9.3635 | 18.1561 | 1.6117 | 9.703 | 0.28401 | 72.5 | 72.784 | 115.5519 | 0
119 | 19 | 0 | 18 |  | 0.24457 | 0.65414 | 2.6435 | 9.3635 | 19.1561 | 1.8735 | 0.988 | 0 | 15 | 15 | 23.814 | 0
119 | 20 | 0 | 0 |  | 0.24457 | 0.65414 | 2.6435 | 9.3635 | 20.1561 | 2.1353 | -7.0137 | 0 | 0 | 0 | 0 | 0
119 | 21 | 0 | 0 |  | 0.24457 | 0.65414 | 2.6435 | 9.3635 | 21.1561 | 2.3971 | -13.8873 | 0 | 0 | 0 | 0 | 0
119 | 22 | 0 | 0 |  | 0.24457 | 0.65414 | 2.6435 | 9.3635 | 22.1561 | 2.6589 | -19.174 | 0 | 0 | 0 | 0 | 0
119 | 23 | 0 | 0 |  | 0.24457 | 0.65414 | 2.6435 | 9.3635 | 23.1561 | 2.9206 | -22.4178 | 0 | 0 | 0 | 0 | 0
119 | 24 | 0 | 0 |  | 0.24457 | 0.65414 | 2.6435 | 9.3635 | 24.1561 | 3.1824 | -23.2764 | 0 | 0 | 0 | 0 | 0
120 | 1 | 0 | 0 |  | 0.25014 | 0.67135 | 2.7855 | 9.5055 | 1.1584 | -2.8383 | -21.3294 | 0 | 0 | 0 | 0 | 0
120 | 2 | 0 | 0 |  | 0.25014 | 0.67135 | 2.7855 | 9.5055 | 2.1584 | -2.5765 | -17.411 | 0 | 0 | 0 | 0 | 0
120 | 3 | 0 | 0 |  | 0.25014 | 0.67135 | 2.7855 | 9.5055 | 3.1584 | -2.3147 | -11.5903 | 0 | 0 | 0 | 0 | 0
120 | 4 | 0 | 0 |  | 0.25014 | 0.67135 | 2.7855 | 9.5055 | 4.1584 | -2.0529 | -4.3295 | 0 | 0 | 0 | 0 | 0
120 | 5 | 0 | 5 |  | 0.25014 | 0.67135 | 2.7855 | 9.5055 | 5.1584 | -1.7911 | 3.9272 | 0 | 4.1667 | 4.1667 | 6.615 | 0
120 | 6 | 91 | 55 |  | 0.25014 | 0.67135 | 2.7855 | 9.5055 | 6.1584 | -1.5293 | 12.7805 | 12.0589 | 45.8333 | 57.8922 | 91.9097 | 1
120 | 7 | 259 | 108 |  | 0.25014 | 0.67135 | 2.7855 | 9.5055 | 7.1584 | -1.2675 | 21.8567 | 93.8683 | 90 | 183.8683 | 291.9094 | 1
120 | 8 | 96 | 167 |  | 0.25014 | 0.67135 | 2.7855 | 9.5055 | 8.1584 | -1.0057 | 30.7571 | 55.1177 | 139.1667 | 194.2844 | 308.4459 | 1
120 | 9 | 86 | 248 |  | 0.25014 | 0.67135 | 2.7855 | 9.5055 | 9.1584 | -0.74392 | 38.9822 | 64.7784 | 206.6667 | 271.4451 | 430.9462 | 1
120 | 10 | 92 | 306 |  | 0.25014 | 0.67135 | 2.7855 | 9.5055 | 10.1584 | -0.48212 | 45.8322 | 81.6505 | 255 | 336.6505 | 534.4663 | 1
120 | 11 | 103 | 384 |  | 0.25014 | 0.67135 | 2.7855 | 9.5055 | 11.1584 | -0.22032 | 50.3592 | 99.6829 | 320 | 419.6829 | 666.2885 | 1
120 | 12 | 173 | 393 |  | 0.25014 | 0.67135 | 2.7855 | 9.5055 | 12.1584 | 0.041475 | 51.6055 | 171.034 | 327.5 | 498.534 | 791.4726 | 1
120 | 13 | 226 | 385 |  | 0.25014 | 0.67135 | 2.7855 | 9.5055 | 13.1584 | 0.30327 | 49.2401 | 214.3854 | 320.8333 | 535.2187 | 849.7132 | 1
120 | 14 | 86 | 342 |  | 0.25014 | 0.67135 | 2.7855 | 9.5055 | 14.1584 | 0.56507 | 43.8638 | 73.1377 | 285 | 358.1377 | 568.5794 | 1
120 | 15 | 91 | 289 |  | 0.25014 | 0.67135 | 2.7855 | 9.5055 | 15.1584 | 0.82687 | 36.4866 | 63.7744 | 240.8333 | 304.6077 | 483.5952 | 1
120 | 16 | 191 | 246 |  | 0.25014 | 0.67135 | 2.7855 | 9.5055 | 16.1584 | 1.0887 | 27.9833 | 97.3989 | 205 | 302.3989 | 480.0884 | 1
120 | 17 | 285 | 156 |  | 0.25014 | 0.67135 | 2.7855 | 9.5055 | 17.1584 | 1.3505 | 18.9798 | 82.8834 | 130 | 212.8834 | 337.9737 | 1
120 | 18 | 65 | 100 |  | 0.25014 | 0.67135 | 2.7855 | 9.5055 | 18.1584 | 1.6123 | 9.9335 | 3.7948 | 83.3333 | 87.1282 | 138.3247 | 0
120 | 19 | 0 | 20 |  | 0.25014 | 0.67135 | 2.7855 | 9.5055 | 19.1584 | 1.8741 | 1.2283 | 0 | 16.6667 | 16.6667 | 26.46 | 0
120 | 20 | 0 | 0 |  | 0.25014 | 0.67135 | 2.7855 | 9.5055 | 20.1584 | 2.1359 | -6.7581 | 0 | 0 | 0 | 0 | 0
120 | 21 | 0 | 0 |  | 0.25014 | 0.67135 | 2.7855 | 9.5055 | 21.1584 | 2.3977 | -13.6126 | 0 | 0 | 0 | 0 | 0
120 | 22 | 0 | 0 |  | 0.25014 | 0.67135 | 2.7855 | 9.5055 | 22.1584 | 2.6595 | -18.8796 | 0 | 0 | 0 | 0 | 0
120 | 23 | 0 | 0 |  | 0.25014 | 0.67135 | 2.7855 | 9.5055 | 23.1584 | 2.9213 | -22.1069 | 0 | 0 | 0 | 0 | 0
120 | 24 | 0 | 0 |  | 0.25014 | 0.67135 | 2.7855 | 9.5055 | 24.1584 | 3.1831 | -22.9564 | 0 | 0 | 0 | 0 | 0
121 | 1 | 0 | 0 |  | 0.25564 | 0.68857 | 2.918 | 9.638 | 1.1606 | -2.8377 | -21.0139 | 0 | 0 | 0 | 0 | 0
121 | 2 | 0 | 0 |  | 0.25564 | 0.68857 | 2.918 | 9.638 | 2.1606 | -2.5759 | -17.1037 | 0 | 0 | 0 | 0 | 0
121 | 3 | 0 | 0 |  | 0.25564 | 0.68857 | 2.918 | 9.638 | 3.1606 | -2.3141 | -11.295 | 0 | 0 | 0 | 0 | 0
121 | 4 | 0 | 0 |  | 0.25564 | 0.68857 | 2.918 | 9.638 | 4.1606 | -2.0523 | -4.0466 | 0 | 0 | 0 | 0 | 0
121 | 5 | 0 | 5 |  | 0.25564 | 0.68857 | 2.918 | 9.638 | 5.1606 | -1.7905 | 4.2 | 0 | 4.1667 | 4.1667 | 6.615 | 0
121 | 6 | 104 | 47 |  | 0.25564 | 0.68857 | 2.918 | 9.638 | 6.1606 | -1.5287 | 13.0474 | 14.0433 | 39.1667 | 53.21 | 84.4762 | 1
121 | 7 | 265 | 112 |  | 0.25564 | 0.68857 | 2.918 | 9.638 | 7.1606 | -1.2669 | 22.123 | 96.6172 | 93.3333 | 189.9505 | 301.5655 | 1
121 | 8 | 144 | 196 |  | 0.25564 | 0.68857 | 2.918 | 9.638 | 8.1606 | -1.0051 | 31.0292 | 82.9372 | 163.3333 | 246.2705 | 390.9791 | 1
121 | 9 | 6 | 178 |  | 0.25564 | 0.68857 | 2.918 | 9.638 | 9.1606 | -0.74334 | 39.2666 | 4.5282 | 148.3333 | 152.8616 | 242.683 | 1
121 | 10 | 469 | 301 |  | 0.25564 | 0.68857 | 2.918 | 9.638 | 10.1606 | -0.48155 | 46.1335 | 416.7875 | 250.8333 | 667.6208 | 1059.9149 | 1
121 | 11 | 373 | 333 |  | 0.25564 | 0.68857 | 2.918 | 9.638 | 11.1606 | -0.21975 | 50.6742 | 361.3334 | 277.5 | 638.8334 | 1014.2119 | 1
121 | 12 | 356 | 368 |  | 0.25564 | 0.68857 | 2.918 | 9.638 | 12.1606 | 0.042054 | 51.9192 | 352.2262 | 306.6667 | 658.8929 | 1046.0583 | 1
121 | 13 | 276 | 339 |  | 0.25564 | 0.68857 | 2.918 | 9.638 | 13.1606 | 0.30385 | 49.5339 | 262.0055 | 282.5 | 544.5055 | 864.457 | 1
121 | 14 | 239 | 338 |  | 0.25564 | 0.68857 | 2.918 | 9.638 | 14.1606 | 0.56565 | 44.1306 | 203.4232 | 281.6667 | 485.0898 | 770.1286 | 1
121 | 15 | 349 | 281 |  | 0.25564 | 0.68857 | 2.918 | 9.638 | 15.1606 | 0.82745 | 36.7308 | 244.8693 | 234.1667 | 479.036 | 760.5175 | 1
121 | 16 | 528 | 168 |  | 0.25564 | 0.68857 | 2.918 | 9.638 | 16.1606 | 1.0893 | 28.2138 | 269.7812 | 140 | 409.7812 | 650.5686 | 1
121 | 17 | 313 | 156 |  | 0.25564 | 0.68857 | 2.918 | 9.638 | 17.1606 | 1.3511 | 19.2055 | 91.4246 | 130 | 221.4246 | 351.5337 | 1
121 | 18 | 132 | 111 |  | 0.25564 | 0.68857 | 2.918 | 9.638 | 18.1606 | 1.6129 | 10.1623 | 7.9164 | 92.5 | 100.4164 | 159.4211 | 0
121 | 19 | 0 | 32 |  | 0.25564 | 0.68857 | 2.918 | 9.638 | 19.1606 | 1.8746 | 1.4668 | 0 | 26.6667 | 26.6667 | 42.336 | 0
121 | 20 | 0 | 1 |  | 0.25564 | 0.68857 | 2.918 | 9.638 | 20.1606 | 2.1364 | -6.5045 | 0 | 0.83333 | 0.83333 | 1.323 | 0
121 | 21 | 0 | 0 |  | 0.25564 | 0.68857 | 2.918 | 9.638 | 21.1606 | 2.3982 | -13.3404 | 0 | 0 | 0 | 0 | 0
121 | 22 | 0 | 0 |  | 0.25564 | 0.68857 | 2.918 | 9.638 | 22.1606 | 2.66 | -18.588 | 0 | 0 | 0 | 0 | 0
121 | 23 | 0 | 0 |  | 0.25564 | 0.68857 | 2.918 | 9.638 | 23.1606 | 2.9218 | -21.7995 | 0 | 0 | 0 | 0 | 0
121 | 24 | 0 | 0 |  | 0.25564 | 0.68857 | 2.918 | 9.638 | 24.1606 | 3.1836 | -22.6404 | 0 | 0 | 0 | 0 | 0
122 | 1 | 0 | 0 |  | 0.26108 | 0.70578 | 3.0411 | 9.7611 | 1.1627 | -2.8372 | -20.7029 | 0 | 0 | 0 | 0 | 0
122 | 2 | 0 | 0 |  | 0.26108 | 0.70578 | 3.0411 | 9.7611 | 2.1627 | -2.5754 | -16.8009 | 0 | 0 | 0 | 0 | 0
122 | 3 | 0 | 0 |  | 0.26108 | 0.70578 | 3.0411 | 9.7611 | 3.1627 | -2.3136 | -11.0043 | 0 | 0 | 0 | 0 | 0
122 | 4 | 0 | 0 |  | 0.26108 | 0.70578 | 3.0411 | 9.7611 | 4.1627 | -2.0518 | -3.7684 | 0 | 0 | 0 | 0 | 0
122 | 5 | 0 | 2 |  | 0.26108 | 0.70578 | 3.0411 | 9.7611 | 5.1627 | -1.79 | 4.4681 | 0 | 1.6667 | 1.6667 | 2.646 | 0
122 | 6 | 0 | 23 |  | 0.26108 | 0.70578 | 3.0411 | 9.7611 | 6.1627 | -1.5282 | 13.3096 | 0 | 19.1667 | 19.1667 | 30.429 | 1
122 | 7 | 0 | 72 |  | 0.26108 | 0.70578 | 3.0411 | 9.7611 | 7.1627 | -1.2664 | 22.3846 | 0 | 60 | 60 | 95.256 | 1
122 | 8 | 0 | 129 |  | 0.26108 | 0.70578 | 3.0411 | 9.7611 | 8.1627 | -1.0046 | 31.2965 | 0 | 107.5 | 107.5 | 170.667 | 1
122 | 9 | 6 | 181 |  | 0.26108 | 0.70578 | 3.0411 | 9.7611 | 9.1627 | -0.74281 | 39.5462 | 4.5367 | 150.8333 | 155.37 | 246.6654 | 1
122 | 10 | 11 | 222 |  | 0.26108 | 0.70578 | 3.0411 | 9.7611 | 10.1627 | -0.48101 | 46.43 | 9.7876 | 185 | 194.7876 | 309.2448 | 1
122 | 11 | 14 | 251 |  | 0.26108 | 0.70578 | 3.0411 | 9.7611 | 11.1627 | -0.21921 | 50.9848 | 13.5744 | 209.1667 | 222.7411 | 353.6238 | 1
122 | 12 | 5 | 273 |  | 0.26108 | 0.70578 | 3.0411 | 9.7611 | 12.1627 | 0.042591 | 52.2289 | 4.9506 | 227.5 | 232.4506 | 369.0386 | 1
122 | 13 | 5 | 270 |  | 0.26108 | 0.70578 | 3.0411 | 9.7611 | 13.1627 | 0.30439 | 49.8243 | 4.7498 | 225 | 229.7498 | 364.7507 | 1
122 | 14 | 96 | 333 |  | 0.26108 | 0.70578 | 3.0411 | 9.7611 | 14.1627 | 0.56619 | 44.3944 | 81.7757 | 277.5 | 359.2757 | 570.3861 | 1
122 | 15 | 8 | 211 |  | 0.26108 | 0.70578 | 3.0411 | 9.7611 | 15.1627 | 0.82799 | 36.9725 | 5.6195 | 175.8333 | 181.4528 | 288.0745 | 1
122 | 16 | 49 | 240 |  | 0.26108 | 0.70578 | 3.0411 | 9.7611 | 16.1627 | 1.0898 | 28.4422 | 25.0859 | 200 | 225.0859 | 357.3463 | 1
122 | 17 | 0 | 110 |  | 0.26108 | 0.70578 | 3.0411 | 9.7611 | 17.1627 | 1.3516 | 19.4293 | 0 | 91.6667 | 91.6667 | 145.53 | 1
122 | 18 | 0 | 86 |  | 0.26108 | 0.70578 | 3.0411 | 9.7611 | 18.1627 | 1.6134 | 10.3893 | 0 | 71.6667 | 71.6667 | 113.778 | 0
122 | 19 | 0 | 12 |  | 0.26108 | 0.70578 | 3.0411 | 9.7611 | 19.1627 | 1.8752 | 1.7035 | 0 | 10 | 10 | 15.876 | 0
122 | 20 | 0 | 0 |  | 0.26108 | 0.70578 | 3.0411 | 9.7611 | 20.1627 | 2.137 | -6.253 | 0 | 0 | 0 | 0 | 0
122 | 21 | 0 | 0 |  | 0.26108 | 0.70578 | 3.0411 | 9.7611 | 21.1627 | 2.3988 | -13.0706 | 0 | 0 | 0 | 0 | 0
122 | 22 | 0 | 0 |  | 0.26108 | 0.70578 | 3.0411 | 9.7611 | 22.1627 | 2.6606 | -18.2995 | 0 | 0 | 0 | 0 | 0
122 | 23 | 0 | 0 |  | 0.26108 | 0.70578 | 3.0411 | 9.7611 | 23.1627 | 2.9224 | -21.4957 | 0 | 0 | 0 | 0 | 0
122 | 24 | 0 | 0 |  | 0.26108 | 0.70578 | 3.0411 | 9.7611 | 24.1627 | 3.1842 | -22.3285 | 0 | 0 | 0 | 0 | 0
123 | 1 | 0 | 0 |  | 0.26644 | 0.723 | 3.1546 | 9.8746 | 1.1646 | -2.8367 | -20.3962 | 0 | 0 | 0 | 0 | 0
123 | 2 | 0 | 0 |  | 0.26644 | 0.723 | 3.1546 | 9.8746 | 2.1646 | -2.5749 | -16.5027 | 0 | 0 | 0 | 0 | 0
123 | 3 | 0 | 0 |  | 0.26644 | 0.723 | 3.1546 | 9.8746 | 3.1646 | -2.3131 | -10.7183 | 0 | 0 | 0 | 0 | 0
123 | 4 | 0 | 0 |  | 0.26644 | 0.723 | 3.1546 | 9.8746 | 4.1646 | -2.0513 | -3.4948 | 0 | 0 | 0 | 0 | 0
123 | 5 | 0 | 5 |  | 0.26644 | 0.723 | 3.1546 | 9.8746 | 5.1646 | -1.7895 | 4.7316 | 0 | 4.1667 | 4.1667 | 6.615 | 0
123 | 6 | 31 | 53 |  | 0.26644 | 0.723 | 3.1546 | 9.8746 | 6.1646 | -1.5277 | 13.567 | 4.3357 | 44.1667 | 48.5024 | 77.0024 | 1
123 | 7 | 226 | 131 |  | 0.26644 | 0.723 | 3.1546 | 9.8746 | 7.1646 | -1.2659 | 22.6412 | 83.3311 | 109.1667 | 192.4977 | 305.6094 | 1
123 | 8 | 384 | 168 |  | 0.26644 | 0.723 | 3.1546 | 9.8746 | 8.1646 | -1.0041 | 31.5587 | 222.4785 | 140 | 362.4785 | 575.4709 | 1
123 | 9 | 484 | 202 |  | 0.26644 | 0.723 | 3.1546 | 9.8746 | 9.1646 | -0.74231 | 39.8207 | 366.6088 | 168.3333 | 534.9422 | 849.2742 | 1
123 | 10 | 548 | 227 |  | 0.26644 | 0.723 | 3.1546 | 9.8746 | 10.1646 | -0.48051 | 46.7216 | 488.1807 | 189.1667 | 677.3473 | 1075.3566 | 1
123 | 11 | 602 | 228 |  | 0.26644 | 0.723 | 3.1546 | 9.8746 | 11.1646 | -0.21871 | 51.2908 | 584.2014 | 190 | 774.2014 | 1229.1222 | 1
123 | 12 | 574 | 270 |  | 0.26644 | 0.723 | 3.1546 | 9.8746 | 12.1646 | 0.043086 | 52.5346 | 568.7267 | 225 | 793.7267 | 1260.1205 | 1
123 | 13 | 676 | 225 |  | 0.26644 | 0.723 | 3.1546 | 9.8746 | 13.1646 | 0.30489 | 50.1112 | 642.5976 | 187.5 | 830.0976 | 1317.863 | 1
123 | 14 | 777 | 145 |  | 0.26644 | 0.723 | 3.1546 | 9.8746 | 14.1646 | 0.56668 | 44.6552 | 662.3932 | 120.8333 | 783.2265 | 1243.4505 | 1
123 | 15 | 710 | 149 |  | 0.26644 | 0.723 | 3.1546 | 9.8746 | 15.1646 | 0.82848 | 37.2116 | 499.2974 | 124.1667 | 623.464 | 989.8115 | 1
123 | 16 | 647 | 129 |  | 0.26644 | 0.723 | 3.1546 | 9.8746 | 16.1646 | 1.0903 | 28.6683 | 331.8883 | 107.5 | 439.3883 | 697.5728 | 1
123 | 17 | 454 | 133 |  | 0.26644 | 0.723 | 3.1546 | 9.8746 | 17.1646 | 1.3521 | 19.6511 | 133.7733 | 110.8333 | 244.6066 | 388.3375 | 1
123 | 18 | 240 | 95 |  | 0.26644 | 0.723 | 3.1546 | 9.8746 | 18.1646 | 1.6139 | 10.6144 | 15.164 | 79.1667 | 94.3306 | 149.7593 | 0
123 | 19 | 3 | 36 |  | 0.26644 | 0.723 | 3.1546 | 9.8746 | 19.1646 | 1.8757 | 1.9381 | 0 | 30 | 30 | 47.628 | 0
123 | 20 | 0 | 1 |  | 0.26644 | 0.723 | 3.1546 | 9.8746 | 20.1646 | 2.1375 | -6.0037 | 0 | 0.83333 | 0.83333 | 1.323 | 0
123 | 21 | 0 | 0 |  | 0.26644 | 0.723 | 3.1546 | 9.8746 | 21.1646 | 2.3993 | -12.8035 | 0 | 0 | 0 | 0 | 0
123 | 22 | 0 | 0 |  | 0.26644 | 0.723 | 3.1546 | 9.8746 | 22.1646 | 2.6611 | -18.0142 | 0 | 0 | 0 | 0 | 0
123 | 23 | 0 | 0 |  | 0.26644 | 0.723 | 3.1546 | 9.8746 | 23.1646 | 2.9229 | -21.1955 | 0 | 0 | 0 | 0 | 0
123 | 24 | 0 | 0 |  | 0.26644 | 0.723 | 3.1546 | 9.8746 | 24.1646 | 3.1847 | -22.0207 | 0 | 0 | 0 | 0 | 0
124 | 1 | 0 | 0 |  | 0.27173 | 0.74021 | 3.2585 | 9.9785 | 1.1663 | -2.8363 | -20.0942 | 0 | 0 | 0 | 0 | 0
124 | 2 | 0 | 0 |  | 0.27173 | 0.74021 | 3.2585 | 9.9785 | 2.1663 | -2.5745 | -16.2092 | 0 | 0 | 0 | 0 | 0
124 | 3 | 0 | 0 |  | 0.27173 | 0.74021 | 3.2585 | 9.9785 | 3.1663 | -2.3127 | -10.4371 | 0 | 0 | 0 | 0 | 0
124 | 4 | 0 | 0 |  | 0.27173 | 0.74021 | 3.2585 | 9.9785 | 4.1663 | -2.0509 | -3.2261 | 0 | 0 | 0 | 0 | 0
124 | 5 | 0 | 7 |  | 0.27173 | 0.74021 | 3.2585 | 9.9785 | 5.1663 | -1.7891 | 4.9901 | 0 | 5.8333 | 5.8333 | 9.261 | 0
124 | 6 | 137 | 50 |  | 0.27173 | 0.74021 | 3.2585 | 9.9785 | 6.1663 | -1.5273 | 13.8195 | 19.4779 | 41.6667 | 61.1446 | 97.0732 | 1
124 | 7 | 324 | 111 |  | 0.27173 | 0.74021 | 3.2585 | 9.9785 | 7.1663 | -1.2655 | 22.8929 | 120.1009 | 92.5 | 212.6009 | 337.5252 | 1
124 | 8 | 503 | 147 |  | 0.27173 | 0.74021 | 3.2585 | 9.9785 | 8.1663 | -1.0037 | 31.8159 | 292.233 | 122.5 | 414.733 | 658.4301 | 1
124 | 9 | 581 | 196 |  | 0.27173 | 0.74021 | 3.2585 | 9.9785 | 9.1663 | -0.74186 | 40.0902 | 440.8269 | 163.3333 | 604.1602 | 959.1648 | 1
124 | 10 | 754 | 138 |  | 0.27173 | 0.74021 | 3.2585 | 9.9785 | 10.1663 | -0.48006 | 47.0082 | 672.4489 | 115 | 787.4489 | 1250.1539 | 1
124 | 11 | 559 | 263 |  | 0.27173 | 0.74021 | 3.2585 | 9.9785 | 11.1663 | -0.21826 | 51.5923 | 542.9125 | 219.1667 | 762.0792 | 1209.8769 | 1
124 | 12 | 685 | 225 |  | 0.27173 | 0.74021 | 3.2585 | 9.9785 | 12.1663 | 0.043539 | 52.8362 | 679.1537 | 187.5 | 866.6537 | 1375.8994 | 1
124 | 13 | 778 | 166 |  | 0.27173 | 0.74021 | 3.2585 | 9.9785 | 13.1663 | 0.30534 | 50.3944 | 740.03 | 138.3333 | 878.3634 | 1394.4897 | 1
124 | 14 | 784 | 142 |  | 0.27173 | 0.74021 | 3.2585 | 9.9785 | 14.1663 | 0.56714 | 44.913 | 668.8741 | 118.3333 | 787.2075 | 1249.7706 | 1
124 | 15 | 658 | 170 |  | 0.27173 | 0.74021 | 3.2585 | 9.9785 | 15.1663 | 0.82894 | 37.4482 | 463.2501 | 141.6667 | 604.9168 | 960.3659 | 1
124 | 16 | 579 | 151 |  | 0.27173 | 0.74021 | 3.2585 | 9.9785 | 16.1663 | 1.0907 | 28.8922 | 297.5907 | 125.8333 | 423.424 | 672.228 | 1
124 | 17 | 476 | 126 |  | 0.27173 | 0.74021 | 3.2585 | 9.9785 | 17.1663 | 1.3525 | 19.8709 | 140.8701 | 105 | 245.8701 | 390.3434 | 1
124 | 18 | 243 | 96 |  | 0.27173 | 0.74021 | 3.2585 | 9.9785 | 18.1663 | 1.6143 | 10.8375 | 15.7469 | 80 | 95.7469 | 152.0078 | 0
124 | 19 | 12 | 37 |  | 0.27173 | 0.74021 | 3.2585 | 9.9785 | 19.1663 | 1.8761 | 2.1707 | 0 | 30.8333 | 30.8333 | 48.951 | 0
124 | 20 | 0 | 1 |  | 0.27173 | 0.74021 | 3.2585 | 9.9785 | 20.1663 | 2.1379 | -5.7567 | 0 | 0.83333 | 0.83333 | 1.323 | 0
124 | 21 | 0 | 0 |  | 0.27173 | 0.74021 | 3.2585 | 9.9785 | 21.1663 | 2.3997 | -12.5391 | 0 | 0 | 0 | 0 | 0
124 | 22 | 0 | 0 |  | 0.27173 | 0.74021 | 3.2585 | 9.9785 | 22.1663 | 2.6615 | -17.732 | 0 | 0 | 0 | 0 | 0
124 | 23 | 0 | 0 |  | 0.27173 | 0.74021 | 3.2585 | 9.9785 | 23.1663 | 2.9233 | -20.8991 | 0 | 0 | 0 | 0 | 0
124 | 24 | 0 | 0 |  | 0.27173 | 0.74021 | 3.2585 | 9.9785 | 24.1663 | 3.1851 | -21.7171 | 0 | 0 | 0 | 0 | 0
125 | 1 | 0 | 0 |  | 0.27694 | 0.75743 | 3.3526 | 10.0726 | 1.1679 | -2.8358 | -19.7968 | 0 | 0 | 0 | 0 | 0
125 | 2 | 0 | 0 |  | 0.27694 | 0.75743 | 3.3526 | 10.0726 | 2.1679 | -2.574 | -15.9205 | 0 | 0 | 0 | 0 | 0
125 | 3 | 0 | 0 |  | 0.27694 | 0.75743 | 3.3526 | 10.0726 | 3.1679 | -2.3122 | -10.1608 | 0 | 0 | 0 | 0 | 0
125 | 4 | 0 | 0 |  | 0.27694 | 0.75743 | 3.3526 | 10.0726 | 4.1679 | -2.0504 | -2.9623 | 0 | 0 | 0 | 0 | 0
125 | 5 | 0 | 7 |  | 0.27694 | 0.75743 | 3.3526 | 10.0726 | 5.1679 | -1.7886 | 5.2438 | 0 | 5.8333 | 5.8333 | 9.261 | 0
125 | 6 | 42 | 56 |  | 0.27694 | 0.75743 | 3.3526 | 10.0726 | 6.1679 | -1.5268 | 14.067 | 6.0655 | 46.6667 | 52.7322 | 83.7176 | 1
125 | 7 | 195 | 136 |  | 0.27694 | 0.75743 | 3.3526 | 10.0726 | 7.1679 | -1.265 | 23.1395 | 72.6517 | 113.3333 | 185.985 | 295.2698 | 1
125 | 8 | 441 | 164 |  | 0.27694 | 0.75743 | 3.3526 | 10.0726 | 8.1679 | -1.0032 | 32.0679 | 256.8924 | 136.6667 | 393.5591 | 624.8144 | 1
125 | 9 | 629 | 161 |  | 0.27694 | 0.75743 | 3.3526 | 10.0726 | 9.1679 | -0.74145 | 40.3544 | 478.0141 | 134.1667 | 612.1807 | 971.8981 | 1
125 | 10 | 689 | 166 |  | 0.27694 | 0.75743 | 3.3526 | 10.0726 | 10.1679 | -0.47965 | 47.2898 | 615.132 | 138.3333 | 753.4653 | 1196.2015 | 1
125 | 11 | 736 | 198 |  | 0.27694 | 0.75743 | 3.3526 | 10.0726 | 11.1679 | -0.21785 | 51.889 | 715.3644 | 165 | 880.3644 | 1397.6666 | 1
125 | 12 | 836 | 137 |  | 0.27694 | 0.75743 | 3.3526 | 10.0726 | 12.1679 | 0.04395 | 53.1336 | 829.3809 | 114.1667 | 943.5475 | 1497.9761 | 1
125 | 13 | 834 | 136 |  | 0.27694 | 0.75743 | 3.3526 | 10.0726 | 13.1679 | 0.30575 | 50.674 | 793.7827 | 113.3333 | 907.1161 | 1440.1374 | 1
125 | 14 | 809 | 132 |  | 0.27694 | 0.75743 | 3.3526 | 10.0726 | 14.1679 | 0.56755 | 45.1675 | 690.7207 | 110 | 800.7207 | 1271.2241 | 1
125 | 15 | 765 | 123 |  | 0.27694 | 0.75743 | 3.3526 | 10.0726 | 15.1679 | 0.82935 | 37.682 | 539.182 | 102.5 | 641.682 | 1018.7343 | 1
125 | 16 | 657 | 128 |  | 0.27694 | 0.75743 | 3.3526 | 10.0726 | 16.1679 | 1.0911 | 29.1138 | 338.3439 | 106.6667 | 445.0106 | 706.4988 | 1
125 | 17 | 463 | 134 |  | 0.27694 | 0.75743 | 3.3526 | 10.0726 | 17.1679 | 1.3529 | 20.0886 | 137.6232 | 111.6667 | 249.2898 | 395.7725 | 1
125 | 18 | 252 | 97 |  | 0.27694 | 0.75743 | 3.3526 | 10.0726 | 18.1679 | 1.6147 | 11.0585 | 16.7402 | 80.8333 | 97.5735 | 154.9077 | 0
125 | 19 | 19 | 38 |  | 0.27694 | 0.75743 | 3.3526 | 10.0726 | 19.1679 | 1.8765 | 2.4012 | 0 | 31.6667 | 31.6667 | 50.274 | 0
125 | 20 | 0 | 2 |  | 0.27694 | 0.75743 | 3.3526 | 10.0726 | 20.1679 | 2.1383 | -5.5121 | 0 | 1.6667 | 1.6667 | 2.646 | 0
125 | 21 | 0 | 0 |  | 0.27694 | 0.75743 | 3.3526 | 10.0726 | 21.1679 | 2.4001 | -12.2774 | 0 | 0 | 0 | 0 | 0
125 | 22 | 0 | 0 |  | 0.27694 | 0.75743 | 3.3526 | 10.0726 | 22.1679 | 2.6619 | -17.4531 | 0 | 0 | 0 | 0 | 0
125 | 23 | 0 | 0 |  | 0.27694 | 0.75743 | 3.3526 | 10.0726 | 23.1679 | 2.9237 | -20.6065 | 0 | 0 | 0 | 0 | 0
125 | 24 | 0 | 0 |  | 0.27694 | 0.75743 | 3.3526 | 10.0726 | 24.1679 | 3.1855 | -21.418 | 0 | 0 | 0 | 0 | 0
126 | 1 | 0 | 0 |  | 0.28207 | 0.77464 | 3.437 | 10.157 | 1.1693 | -2.8355 | -19.5042 | 0 | 0 | 0 | 0 | 0
126 | 2 | 0 | 0 |  | 0.28207 | 0.77464 | 3.437 | 10.157 | 2.1693 | -2.5737 | -15.6368 | 0 | 0 | 0 | 0 | 0
126 | 3 | 0 | 0 |  | 0.28207 | 0.77464 | 3.437 | 10.157 | 3.1693 | -2.3119 | -9.8894 | 0 | 0 | 0 | 0 | 0
126 | 4 | 0 | 0 |  | 0.28207 | 0.77464 | 3.437 | 10.157 | 4.1693 | -2.0501 | -2.7034 | 0 | 0 | 0 | 0 | 0
126 | 5 | 0 | 9 |  | 0.28207 | 0.77464 | 3.437 | 10.157 | 5.1693 | -1.7883 | 5.4925 | 0 | 7.5 | 7.5 | 11.907 | 0
126 | 6 | 154 | 52 |  | 0.28207 | 0.77464 | 3.437 | 10.157 | 6.1693 | -1.5265 | 14.3094 | 22.5747 | 43.3333 | 65.9081 | 104.6357 | 1
126 | 7 | 296 | 117 |  | 0.28207 | 0.77464 | 3.437 | 10.157 | 7.1693 | -1.2647 | 23.381 | 110.8206 | 97.5 | 208.3206 | 330.7298 | 1
126 | 8 | 486 | 155 |  | 0.28207 | 0.77464 | 3.437 | 10.157 | 8.1693 | -1.0029 | 32.3147 | 283.8232 | 129.1667 | 412.9899 | 655.6628 | 1
126 | 9 | 611 | 159 |  | 0.28207 | 0.77464 | 3.437 | 10.157 | 9.1693 | -0.74108 | 40.6133 | 465.0434 | 132.5 | 597.5434 | 948.6599 | 1
126 | 10 | 690 | 183 |  | 0.28207 | 0.77464 | 3.437 | 10.157 | 10.1693 | -0.47928 | 47.5661 | 616.6418 | 152.5 | 769.1418 | 1221.0895 | 1
126 | 11 | 791 | 145 |  | 0.28207 | 0.77464 | 3.437 | 10.157 | 11.1693 | -0.21748 | 52.1808 | 769.3741 | 120.8333 | 890.2075 | 1413.2934 | 1
126 | 12 | 803 | 151 |  | 0.28207 | 0.77464 | 3.437 | 10.157 | 12.1693 | 0.044318 | 53.4266 | 797.1103 | 125.8333 | 922.9437 | 1465.2653 | 1
126 | 13 | 705 | 204 |  | 0.28207 | 0.77464 | 3.437 | 10.157 | 13.1693 | 0.30612 | 50.9499 | 671.3971 | 170 | 841.3971 | 1335.8021 | 1
126 | 14 | 554 | 257 |  | 0.28207 | 0.77464 | 3.437 | 10.157 | 14.1693 | 0.56792 | 45.4189 | 473.3494 | 214.1667 | 687.516 | 1091.5005 | 1
126 | 15 | 650 | 175 |  | 0.28207 | 0.77464 | 3.437 | 10.157 | 15.1693 | 0.82972 | 37.9131 | 458.6354 | 145.8333 | 604.4687 | 959.6545 | 1
126 | 16 | 580 | 152 |  | 0.28207 | 0.77464 | 3.437 | 10.157 | 16.1693 | 1.0915 | 29.333 | 299.2764 | 126.6667 | 425.943 | 676.2271 | 1
126 | 17 | 468 | 130 |  | 0.28207 | 0.77464 | 3.437 | 10.157 | 17.1693 | 1.3533 | 20.3042 | 139.7188 | 108.3333 | 248.0522 | 393.8076 | 1
126 | 18 | 148 | 113 |  | 0.28207 | 0.77464 | 3.437 | 10.157 | 18.1693 | 1.6151 | 11.2775 | 10.0735 | 94.1667 | 104.2402 | 165.4917 | 0
126 | 19 | 0 | 36 |  | 0.28207 | 0.77464 | 3.437 | 10.157 | 19.1693 | 1.8769 | 2.6295 | 0 | 30 | 30 | 47.628 | 0
126 | 20 | 0 | 2 |  | 0.28207 | 0.77464 | 3.437 | 10.157 | 20.1693 | 2.1387 | -5.27 | 0 | 1.6667 | 1.6667 | 2.646 | 0
126 | 21 | 0 | 0 |  | 0.28207 | 0.77464 | 3.437 | 10.157 | 21.1693 | 2.4005 | -12.0187 | 0 | 0 | 0 | 0 | 0
126 | 22 | 0 | 0 |  | 0.28207 | 0.77464 | 3.437 | 10.157 | 22.1693 | 2.6623 | -17.1777 | 0 | 0 | 0 | 0 | 0
126 | 23 | 0 | 0 |  | 0.28207 | 0.77464 | 3.437 | 10.157 | 23.1693 | 2.9241 | -20.318 | 0 | 0 | 0 | 0 | 0
126 | 24 | 0 | 0 |  | 0.28207 | 0.77464 | 3.437 | 10.157 | 24.1693 | 3.1859 | -21.1232 | 0 | 0 | 0 | 0 | 0
127 | 1 | 0 | 0 |  | 0.28713 | 0.79185 | 3.5117 | 10.2317 | 1.1705 | -2.8351 | -19.2164 | 0 | 0 | 0 | 0 | 0
127 | 2 | 0 | 0 |  | 0.28713 | 0.79185 | 3.5117 | 10.2317 | 2.1705 | -2.5733 | -15.358 | 0 | 0 | 0 | 0 | 0
127 | 3 | 0 | 0 |  | 0.28713 | 0.79185 | 3.5117 | 10.2317 | 3.1705 | -2.3116 | -9.623 | 0 | 0 | 0 | 0 | 0
127 | 4 | 0 | 0 |  | 0.28713 | 0.79185 | 3.5117 | 10.2317 | 4.1705 | -2.0498 | -2.4496 | 0 | 0 | 0 | 0 | 0
127 | 5 | 0 | 9 |  | 0.28713 | 0.79185 | 3.5117 | 10.2317 | 5.1705 | -1.788 | 5.7361 | 0 | 7.5 | 7.5 | 11.907 | 0
127 | 6 | 84 | 66 |  | 0.28713 | 0.79185 | 3.5117 | 10.2317 | 6.1705 | -1.5262 | 14.5467 | 12.49 | 55 | 67.49 | 107.1472 | 1
127 | 7 | 338 | 114 |  | 0.28713 | 0.79185 | 3.5117 | 10.2317 | 7.1705 | -1.2644 | 23.6172 | 127.1372 | 95 | 222.1372 | 352.665 | 1
127 | 8 | 507 | 151 |  | 0.28713 | 0.79185 | 3.5117 | 10.2317 | 8.1705 | -1.0026 | 32.5562 | 296.802 | 125.8333 | 422.6353 | 670.9758 | 1
127 | 9 | 647 | 158 |  | 0.28713 | 0.79185 | 3.5117 | 10.2317 | 9.1705 | -0.74075 | 40.8669 | 493.1551 | 131.6667 | 624.8218 | 991.967 | 1
127 | 10 | 745 | 151 |  | 0.28713 | 0.79185 | 3.5117 | 10.2317 | 10.1705 | -0.47895 | 47.8372 | 666.4216 | 125.8333 | 792.255 | 1257.784 | 1
127 | 11 | 811 | 137 |  | 0.28713 | 0.79185 | 3.5117 | 10.2317 | 11.1705 | -0.21716 | 52.4677 | 789.3581 | 114.1667 | 903.5248 | 1434.4359 | 1
127 | 12 | 824 | 141 |  | 0.28713 | 0.79185 | 3.5117 | 10.2317 | 12.1705 | 0.044644 | 53.7153 | 818.4094 | 117.5 | 935.9094 | 1485.8498 | 1
127 | 13 | 821 | 141 |  | 0.28713 | 0.79185 | 3.5117 | 10.2317 | 13.1705 | 0.30644 | 51.2219 | 782.3078 | 117.5 | 899.8078 | 1428.5348 | 1
127 | 14 | 795 | 140 |  | 0.28713 | 0.79185 | 3.5117 | 10.2317 | 14.1705 | 0.56824 | 45.667 | 679.7515 | 116.6667 | 796.4182 | 1264.3935 | 1
127 | 15 | 727 | 147 |  | 0.28713 | 0.79185 | 3.5117 | 10.2317 | 15.1705 | 0.83004 | 38.1415 | 513.5292 | 122.5 | 636.0292 | 1009.7599 | 1
127 | 16 | 651 | 132 |  | 0.28713 | 0.79185 | 3.5117 | 10.2317 | 16.1705 | 1.0918 | 29.5498 | 336.5706 | 110 | 446.5706 | 708.9755 | 1
127 | 17 | 395 | 153 |  | 0.28713 | 0.79185 | 3.5117 | 10.2317 | 17.1705 | 1.3536 | 20.5176 | 118.4416 | 127.5 | 245.9416 | 390.4569 | 1
127 | 18 | 128 | 115 |  | 0.28713 | 0.79185 | 3.5117 | 10.2317 | 18.1705 | 1.6154 | 11.4943 | 8.9224 | 95.8333 | 104.7557 | 166.3102 | 0
127 | 19 | 0 | 32 |  | 0.28713 | 0.79185 | 3.5117 | 10.2317 | 19.1705 | 1.8772 | 2.8554 | 0 | 26.6667 | 26.6667 | 42.336 | 0
127 | 20 | 0 | 1 |  | 0.28713 | 0.79185 | 3.5117 | 10.2317 | 20.1705 | 2.139 | -5.0305 | 0 | 0.83333 | 0.83333 | 1.323 | 0
127 | 21 | 0 | 0 |  | 0.28713 | 0.79185 | 3.5117 | 10.2317 | 21.1705 | 2.4008 | -11.763 | 0 | 0 | 0 | 0 | 0
127 | 22 | 0 | 0 |  | 0.28713 | 0.79185 | 3.5117 | 10.2317 | 22.1705 | 2.6626 | -16.9058 | 0 | 0 | 0 | 0 | 0
127 | 23 | 0 | 0 |  | 0.28713 | 0.79185 | 3.5117 | 10.2317 | 23.1705 | 2.9244 | -20.0335 | 0 | 0 | 0 | 0 | 0
127 | 24 | 0 | 0 |  | 0.28713 | 0.79185 | 3.5117 | 10.2317 | 24.1705 | 3.1862 | -20.833 | 0 | 0 | 0 | 0 | 0
128 | 1 | 0 | 0 |  | 0.29211 | 0.80907 | 3.5765 | 10.2965 | 1.1716 | -2.8349 | -18.9336 | 0 | 0 | 0 | 0 | 0
128 | 2 | 0 | 0 |  | 0.29211 | 0.80907 | 3.5765 | 10.2965 | 2.1716 | -2.5731 | -15.0844 | 0 | 0 | 0 | 0 | 0
128 | 3 | 0 | 0 |  | 0.29211 | 0.80907 | 3.5765 | 10.2965 | 3.1716 | -2.3113 | -9.3618 | 0 | 0 | 0 | 0 | 0
128 | 4 | 0 | 0 |  | 0.29211 | 0.80907 | 3.5765 | 10.2965 | 4.1716 | -2.0495 | -2.2009 | 0 | 0 | 0 | 0 | 0
128 | 5 | 0 | 9 |  | 0.29211 | 0.80907 | 3.5765 | 10.2965 | 5.1716 | -1.7877 | 5.9745 | 0 | 7.5 | 7.5 | 11.907 | 0
128 | 6 | 3 | 60 |  | 0.29211 | 0.80907 | 3.5765 | 10.2965 | 6.1716 | -1.5259 | 14.7789 | 0.45216 | 50 | 50.4522 | 80.0979 | 1
128 | 7 | 177 | 132 |  | 0.29211 | 0.80907 | 3.5765 | 10.2965 | 7.1716 | -1.2641 | 23.8482 | 66.8755 | 110 | 176.8755 | 280.8075 | 1
128 | 8 | 444 | 168 |  | 0.29211 | 0.80907 | 3.5765 | 10.2965 | 8.1716 | -1.0023 | 32.7923 | 260.518 | 140 | 400.518 | 635.8624 | 1
128 | 9 | 587 | 175 |  | 0.29211 | 0.80907 | 3.5765 | 10.2965 | 9.1716 | -0.74047 | 41.115 | 448.0325 | 145.8333 | 593.8658 | 942.8214 | 1
128 | 10 | 93 | 314 |  | 0.29211 | 0.80907 | 3.5765 | 10.2965 | 10.1716 | -0.47867 | 48.1028 | 83.2644 | 261.6667 | 344.9311 | 547.6126 | 1
128 | 11 | 62 | 381 |  | 0.29211 | 0.80907 | 3.5765 | 10.2965 | 11.1716 | -0.21687 | 52.7496 | 60.3835 | 317.5 | 377.8835 | 599.9278 | 1
128 | 12 | 63 | 402 |  | 0.29211 | 0.80907 | 3.5765 | 10.2965 | 12.1716 | 0.044927 | 53.9995 | 62.6052 | 335 | 397.6052 | 631.238 | 1
128 | 13 | 62 | 397 |  | 0.29211 | 0.80907 | 3.5765 | 10.2965 | 13.1716 | 0.30673 | 51.4901 | 59.1099 | 330.8333 | 389.9432 | 619.0739 | 1
128 | 14 | 12 | 251 |  | 0.29211 | 0.80907 | 3.5765 | 10.2965 | 14.1716 | 0.56853 | 45.9118 | 10.2676 | 209.1667 | 219.4343 | 348.3738 | 1
128 | 15 | 91 | 296 |  | 0.29211 | 0.80907 | 3.5765 | 10.2965 | 15.1716 | 0.83032 | 38.367 | 64.3495 | 246.6667 | 311.0162 | 493.7693 | 1
128 | 16 | 48 | 251 |  | 0.29211 | 0.80907 | 3.5765 | 10.2965 | 16.1716 | 1.0921 | 29.7642 | 24.8649 | 209.1667 | 234.0316 | 371.5485 | 1
128 | 17 | 17 | 180 |  | 0.29211 | 0.80907 | 3.5765 | 10.2965 | 17.1716 | 1.3539 | 20.7286 | 5.1198 | 150 | 155.1198 | 246.2682 | 1
128 | 18 | 2 | 96 |  | 0.29211 | 0.80907 | 3.5765 | 10.2965 | 18.1716 | 1.6157 | 11.7089 | 0.14271 | 80 | 80.1427 | 127.2346 | 0
128 | 19 | 0 | 26 |  | 0.29211 | 0.80907 | 3.5765 | 10.2965 | 19.1716 | 1.8775 | 3.079 | 0 | 21.6667 | 21.6667 | 34.398 | 0
128 | 20 | 0 | 2 |  | 0.29211 | 0.80907 | 3.5765 | 10.2965 | 20.1716 | 2.1393 | -4.7936 | 0 | 1.6667 | 1.6667 | 2.646 | 0
128 | 21 | 0 | 0 |  | 0.29211 | 0.80907 | 3.5765 | 10.2965 | 21.1716 | 2.4011 | -11.5103 | 0 | 0 | 0 | 0 | 0
128 | 22 | 0 | 0 |  | 0.29211 | 0.80907 | 3.5765 | 10.2965 | 22.1716 | 2.6629 | -16.6375 | 0 | 0 | 0 | 0 | 0
128 | 23 | 0 | 0 |  | 0.29211 | 0.80907 | 3.5765 | 10.2965 | 23.1716 | 2.9247 | -19.7532 | 0 | 0 | 0 | 0 | 0
128 | 24 | 0 | 0 |  | 0.29211 | 0.80907 | 3.5765 | 10.2965 | 24.1716 | 3.1865 | -20.5475 | 0 | 0 | 0 | 0 | 0
129 | 1 | 0 | 0 |  | 0.29701 | 0.82628 | 3.6315 | 10.3515 | 1.1725 | -2.8346 | -18.6558 | 0 | 0 | 0 | 0 | 0
129 | 2 | 0 | 0 |  | 0.29701 | 0.82628 | 3.6315 | 10.3515 | 2.1725 | -2.5728 | -14.8159 | 0 | 0 | 0 | 0 | 0
129 | 3 | 0 | 0 |  | 0.29701 | 0.82628 | 3.6315 | 10.3515 | 3.1725 | -2.311 | -9.1058 | 0 | 0 | 0 | 0 | 0
129 | 4 | 0 | 0 |  | 0.29701 | 0.82628 | 3.6315 | 10.3515 | 4.1725 | -2.0492 | -1.9574 | 0 | 0 | 0 | 0 | 0
129 | 5 | 0 | 11 |  | 0.29701 | 0.82628 | 3.6315 | 10.3515 | 5.1725 | -1.7874 | 6.2077 | 0 | 9.1667 | 9.1667 | 14.553 | 0
129 | 6 | 80 | 69 |  | 0.29701 | 0.82628 | 3.6315 | 10.3515 | 6.1725 | -1.5256 | 15.0057 | 12.2144 | 57.5 | 69.7144 | 110.6786 | 1
129 | 7 | 120 | 153 |  | 0.29701 | 0.82628 | 3.6315 | 10.3515 | 7.1725 | -1.2638 | 24.0738 | 45.5328 | 127.5 | 173.0328 | 274.7068 | 1
129 | 8 | 116 | 229 |  | 0.29701 | 0.82628 | 3.6315 | 10.3515 | 8.1725 | -1.002 | 33.0229 | 68.2116 | 190.8333 | 259.0449 | 411.2598 | 1
129 | 9 | 449 | 232 |  | 0.29701 | 0.82628 | 3.6315 | 10.3515 | 9.1725 | -0.74023 | 41.3575 | 343.1435 | 193.3333 | 536.4768 | 851.7106 | 1
129 | 10 | 621 | 215 |  | 0.29701 | 0.82628 | 3.6315 | 10.3515 | 10.1725 | -0.47843 | 48.363 | 556.4508 | 179.1667 | 735.6175 | 1167.8663 | 1
129 | 11 | 753 | 173 |  | 0.29701 | 0.82628 | 3.6315 | 10.3515 | 11.1725 | -0.21663 | 53.0263 | 733.7971 | 144.1667 | 877.9638 | 1393.8553 | 1
129 | 12 | 695 | 215 |  | 0.29701 | 0.82628 | 3.6315 | 10.3515 | 12.1725 | 0.045167 | 54.2791 | 690.9829 | 179.1667 | 870.1496 | 1381.4495 | 1
129 | 13 | 787 | 166 |  | 0.29701 | 0.82628 | 3.6315 | 10.3515 | 13.1725 | 0.30697 | 51.7542 | 750.7016 | 138.3333 | 889.035 | 1411.4319 | 1
129 | 14 | 784 | 146 |  | 0.29701 | 0.82628 | 3.6315 | 10.3515 | 14.1725 | 0.56877 | 46.1532 | 671.2765 | 121.6667 | 792.9432 | 1258.8766 | 1
129 | 15 | 742 | 136 |  | 0.29701 | 0.82628 | 3.6315 | 10.3515 | 15.1725 | 0.83056 | 38.5897 | 525.2638 | 113.3333 | 638.5972 | 1013.8369 | 1
129 | 16 | 641 | 136 |  | 0.29701 | 0.82628 | 3.6315 | 10.3515 | 16.1725 | 1.0924 | 29.976 | 332.7003 | 113.3333 | 446.0336 | 708.123 | 1
129 | 17 | 461 | 139 |  | 0.29701 | 0.82628 | 3.6315 | 10.3515 | 17.1725 | 1.3542 | 20.9373 | 139.4444 | 115.8333 | 255.2778 | 405.279 | 1
129 | 18 | 184 | 117 |  | 0.29701 | 0.82628 | 3.6315 | 10.3515 | 18.1725 | 1.616 | 11.9211 | 13.4335 | 97.5 | 110.9335 | 176.1181 | 0
129 | 19 | 0 | 35 |  | 0.29701 | 0.82628 | 3.6315 | 10.3515 | 19.1725 | 1.8778 | 3.3001 | 0 | 29.1667 | 29.1667 | 46.305 | 0
129 | 20 | 0 | 2 |  | 0.29701 | 0.82628 | 3.6315 | 10.3515 | 20.1725 | 2.1396 | -4.5595 | 0 | 1.6667 | 1.6667 | 2.646 | 0
129 | 21 | 0 | 0 |  | 0.29701 | 0.82628 | 3.6315 | 10.3515 | 21.1725 | 2.4014 | -11.2609 | 0 | 0 | 0 | 0 | 0
129 | 22 | 0 | 0 |  | 0.29701 | 0.82628 | 3.6315 | 10.3515 | 22.1725 | 2.6632 | -16.373 | 0 | 0 | 0 | 0 | 0
129 | 23 | 0 | 0 |  | 0.29701 | 0.82628 | 3.6315 | 10.3515 | 23.1725 | 2.925 | -19.4772 | 0 | 0 | 0 | 0 | 0
129 | 24 | 0 | 0 |  | 0.29701 | 0.82628 | 3.6315 | 10.3515 | 24.1725 | 3.1868 | -20.2667 | 0 | 0 | 0 | 0 | 0
130 | 1 | 0 | 0 |  | 0.30182 | 0.8435 | 3.6766 | 10.3966 | 1.1733 | -2.8344 | -18.3832 | 0 | 0 | 0 | 0 | 0
130 | 2 | 0 | 0 |  | 0.30182 | 0.8435 | 3.6766 | 10.3966 | 2.1733 | -2.5726 | -14.5527 | 0 | 0 | 0 | 0 | 0
130 | 3 | 0 | 0 |  | 0.30182 | 0.8435 | 3.6766 | 10.3966 | 3.1733 | -2.3108 | -8.8552 | 0 | 0 | 0 | 0 | 0
130 | 4 | 0 | 0 |  | 0.30182 | 0.8435 | 3.6766 | 10.3966 | 4.1733 | -2.049 | -1.7193 | 0 | 0 | 0 | 0 | 0
130 | 5 | 0 | 12 |  | 0.30182 | 0.8435 | 3.6766 | 10.3966 | 5.1733 | -1.7872 | 6.4356 | 0 | 10 | 10 | 15.876 | 0
130 | 6 | 94 | 71 |  | 0.30182 | 0.8435 | 3.6766 | 10.3966 | 6.1733 | -1.5254 | 15.2272 | 14.5294 | 59.1667 | 73.696 | 116.9998 | 1
130 | 7 | 300 | 123 |  | 0.30182 | 0.8435 | 3.6766 | 10.3966 | 7.1733 | -1.2636 | 24.294 | 114.2948 | 102.5 | 216.7948 | 344.1834 | 1
130 | 8 | 501 | 156 |  | 0.30182 | 0.8435 | 3.6766 | 10.3966 | 8.1733 | -1.0018 | 33.2479 | 295.2118 | 130 | 425.2118 | 675.0662 | 1
130 | 9 | 482 | 211 |  | 0.30182 | 0.8435 | 3.6766 | 10.3966 | 9.1733 | -0.74003 | 41.5945 | 368.8083 | 175.8333 | 544.6417 | 864.6731 | 1
130 | 10 | 669 | 204 |  | 0.30182 | 0.8435 | 3.6766 | 10.3966 | 10.1733 | -0.47823 | 48.6177 | 599.9233 | 170 | 769.9233 | 1222.3302 | 1
130 | 11 | 432 | 304 |  | 0.30182 | 0.8435 | 3.6766 | 10.3966 | 11.1733 | -0.21644 | 53.2978 | 421.2127 | 253.3333 | 674.546 | 1070.9093 | 1
130 | 12 | 643 | 256 |  | 0.30182 | 0.8435 | 3.6766 | 10.3966 | 12.1733 | 0.045364 | 54.554 | 639.5772 | 213.3333 | 852.9105 | 1354.0808 | 1
130 | 13 | 755 | 183 |  | 0.30182 | 0.8435 | 3.6766 | 10.3966 | 13.1733 | 0.30716 | 52.0143 | 720.534 | 152.5 | 873.034 | 1386.0287 | 1
130 | 14 | 752 | 162 |  | 0.30182 | 0.8435 | 3.6766 | 10.3966 | 14.1733 | 0.56896 | 46.3911 | 644.3106 | 135 | 779.3106 | 1237.2336 | 1
130 | 15 | 730 | 141 |  | 0.30182 | 0.8435 | 3.6766 | 10.3966 | 15.1733 | 0.83076 | 38.8093 | 517.3249 | 117.5 | 634.8249 | 1007.848 | 1
130 | 16 | 640 | 138 |  | 0.30182 | 0.8435 | 3.6766 | 10.3966 | 16.1733 | 1.0926 | 30.1852 | 332.8314 | 115 | 447.8314 | 710.9772 | 1
130 | 17 | 461 | 141 |  | 0.30182 | 0.8435 | 3.6766 | 10.3966 | 17.1733 | 1.3544 | 21.1436 | 140.0539 | 117.5 | 257.5539 | 408.8925 | 1
130 | 18 | 265 | 103 |  | 0.30182 | 0.8435 | 3.6766 | 10.3966 | 18.1733 | 1.6162 | 12.1309 | 19.7868 | 85.8333 | 105.6201 | 167.6825 | 0
130 | 19 | 45 | 45 |  | 0.30182 | 0.8435 | 3.6766 | 10.3966 | 19.1733 | 1.878 | 3.5187 | 0 | 37.5 | 37.5 | 59.535 | 0
130 | 20 | 0 | 4 |  | 0.30182 | 0.8435 | 3.6766 | 10.3966 | 20.1733 | 2.1398 | -4.3282 | 0 | 3.3333 | 3.3333 | 5.292 | 0
130 | 21 | 0 | 0 |  | 0.30182 | 0.8435 | 3.6766 | 10.3966 | 21.1733 | 2.4016 | -11.0147 | 0 | 0 | 0 | 0 | 0
130 | 22 | 0 | 0 |  | 0.30182 | 0.8435 | 3.6766 | 10.3966 | 22.1733 | 2.6634 | -16.1123 | 0 | 0 | 0 | 0 | 0
130 | 23 | 0 | 0 |  | 0.30182 | 0.8435 | 3.6766 | 10.3966 | 23.1733 | 2.9252 | -19.2056 | 0 | 0 | 0 | 0 | 0
130 | 24 | 0 | 0 |  | 0.30182 | 0.8435 | 3.6766 | 10.3966 | 24.1733 | 3.187 | -19.9908 | 0 | 0 | 0 | 0 | 0
131 | 1 | 0 | 0 |  | 0.30655 | 0.86071 | 3.712 | 10.432 | 1.1739 | -2.8343 | -18.1158 | 0 | 0 | 0 | 0 | 0
131 | 2 | 0 | 0 |  | 0.30655 | 0.86071 | 3.712 | 10.432 | 2.1739 | -2.5725 | -14.2949 | 0 | 0 | 0 | 0 | 0
131 | 3 | 0 | 0 |  | 0.30655 | 0.86071 | 3.712 | 10.432 | 3.1739 | -2.3107 | -8.6099 | 0 | 0 | 0 | 0 | 0
131 | 4 | 0 | 0 |  | 0.30655 | 0.86071 | 3.712 | 10.432 | 4.1739 | -2.0489 | -1.4865 | 0 | 0 | 0 | 0 | 0
131 | 5 | 0 | 7 |  | 0.30655 | 0.86071 | 3.712 | 10.432 | 5.1739 | -1.7871 | 6.6581 | 0 | 5.8333 | 5.8333 | 9.261 | 0
131 | 6 | 88 | 72 |  | 0.30655 | 0.86071 | 3.712 | 10.432 | 6.1739 | -1.5253 | 15.4433 | 13.7617 | 60 | 73.7617 | 117.1041 | 1
131 | 7 | 17 | 127 |  | 0.30655 | 0.86071 | 3.712 | 10.432 | 7.1739 | -1.2635 | 24.5087 | 6.5018 | 105.8333 | 112.3351 | 178.3432 | 1
131 | 8 | 327 | 209 |  | 0.30655 | 0.86071 | 3.712 | 10.432 | 8.1739 | -1.0017 | 33.4674 | 193.059 | 174.1667 | 367.2257 | 583.0075 | 1
131 | 9 | 489 | 210 |  | 0.30655 | 0.86071 | 3.712 | 10.432 | 9.1739 | -0.73988 | 41.8257 | 374.5879 | 175 | 549.5879 | 872.5257 | 1
131 | 10 | 619 | 218 |  | 0.30655 | 0.86071 | 3.712 | 10.432 | 10.1739 | -0.47808 | 48.8667 | 555.4832 | 181.6667 | 737.1499 | 1170.2991 | 1
131 | 11 | 754 | 174 |  | 0.30655 | 0.86071 | 3.712 | 10.432 | 11.1739 | -0.21628 | 53.564 | 735.5434 | 145 | 880.5434 | 1397.9507 | 1
131 | 12 | 787 | 163 |  | 0.30655 | 0.86071 | 3.712 | 10.432 | 12.1739 | 0.045518 | 54.8242 | 783.1474 | 135.8333 | 918.9807 | 1458.9738 | 1
131 | 13 | 802 | 153 |  | 0.30655 | 0.86071 | 3.712 | 10.432 | 13.1739 | 0.30732 | 52.2703 | 765.7515 | 127.5 | 893.2515 | 1418.1261 | 1
131 | 14 | 784 | 148 |  | 0.30655 | 0.86071 | 3.712 | 10.432 | 14.1739 | 0.56912 | 46.6255 | 672.1714 | 123.3333 | 795.5047 | 1262.9432 | 1
131 | 15 | 745 | 136 |  | 0.30655 | 0.86071 | 3.712 | 10.432 | 15.1739 | 0.83092 | 39.026 | 528.5195 | 113.3333 | 641.8529 | 1019.0056 | 1
131 | 16 | 645 | 137 |  | 0.30655 | 0.86071 | 3.712 | 10.432 | 16.1739 | 1.0927 | 30.3917 | 336.0879 | 114.1667 | 450.2545 | 714.8241 | 1
131 | 17 | 467 | 141 |  | 0.30655 | 0.86071 | 3.712 | 10.432 | 17.1739 | 1.3545 | 21.3474 | 142.4959 | 117.5 | 259.9959 | 412.7695 | 1
131 | 18 | 270 | 104 |  | 0.30655 | 0.86071 | 3.712 | 10.432 | 18.1739 | 1.6163 | 12.3383 | 20.609 | 86.6667 | 107.2757 | 170.3109 | 0
131 | 19 | 31 | 49 |  | 0.30655 | 0.86071 | 3.712 | 10.432 | 19.1739 | 1.8781 | 3.7347 | 0 | 40.8333 | 40.8333 | 64.827 | 0
131 | 20 | 0 | 4 |  | 0.30655 | 0.86071 | 3.712 | 10.432 | 20.1739 | 2.1399 | -4.0999 | 0 | 3.3333 | 3.3333 | 5.292 | 0
131 | 21 | 0 | 0 |  | 0.30655 | 0.86071 | 3.712 | 10.432 | 21.1739 | 2.4017 | -10.7719 | 0 | 0 | 0 | 0 | 0
131 | 22 | 0 | 0 |  | 0.30655 | 0.86071 | 3.712 | 10.432 | 22.1739 | 2.6635 | -15.8556 | 0 | 0 | 0 | 0 | 0
131 | 23 | 0 | 0 |  | 0.30655 | 0.86071 | 3.712 | 10.432 | 23.1739 | 2.9253 | -18.9385 | 0 | 0 | 0 | 0 | 0
131 | 24 | 0 | 0 |  | 0.30655 | 0.86071 | 3.712 | 10.432 | 24.1739 | 3.1871 | -19.7198 | 0 | 0 | 0 | 0 | 0
132 | 1 | 0 | 0 |  | 0.31119 | 0.87792 | 3.7376 | 10.4576 | 1.1743 | -2.8342 | -17.8538 | 0 | 0 | 0 | 0 | 0
132 | 2 | 0 | 0 |  | 0.31119 | 0.87792 | 3.7376 | 10.4576 | 2.1743 | -2.5724 | -14.0425 | 0 | 0 | 0 | 0 | 0
132 | 3 | 0 | 0 |  | 0.31119 | 0.87792 | 3.7376 | 10.4576 | 3.1743 | -2.3106 | -8.37 | 0 | 0 | 0 | 0 | 0
132 | 4 | 0 | 0 |  | 0.31119 | 0.87792 | 3.7376 | 10.4576 | 4.1743 | -2.0488 | -1.2592 | 0 | 0 | 0 | 0 | 0
132 | 5 | 0 | 14 |  | 0.31119 | 0.87792 | 3.7376 | 10.4576 | 5.1743 | -1.787 | 6.8752 | 0 | 11.6667 | 11.6667 | 18.522 | 0
132 | 6 | 108 | 74 |  | 0.31119 | 0.87792 | 3.7376 | 10.4576 | 6.1743 | -1.5252 | 15.6539 | 17.0777 | 61.6667 | 78.7443 | 125.0145 | 1
132 | 7 | 335 | 125 |  | 0.31119 | 0.87792 | 3.7376 | 10.4576 | 7.1743 | -1.2634 | 24.7178 | 128.5932 | 104.1667 | 232.7599 | 369.5296 | 1
132 | 8 | 530 | 146 |  | 0.31119 | 0.87792 | 3.7376 | 10.4576 | 8.1743 | -1.0016 | 33.6812 | 313.4847 | 121.6667 | 435.1513 | 690.8462 | 1
132 | 9 | 640 | 166 |  | 0.31119 | 0.87792 | 3.7376 | 10.4576 | 9.1743 | -0.73977 | 42.0512 | 490.7762 | 138.3333 | 629.1096 | 998.7744 | 1
132 | 10 | 737 | 159 |  | 0.31119 | 0.87792 | 3.7376 | 10.4576 | 10.1743 | -0.47797 | 49.1099 | 661.8129 | 132.5 | 794.3129 | 1261.0511 | 1
132 | 11 | 775 | 158 |  | 0.31119 | 0.87792 | 3.7376 | 10.4576 | 11.1743 | -0.21617 | 53.8247 | 756.3815 | 131.6667 | 888.0482 | 1409.8653 | 1
132 | 12 | 784 | 165 |  | 0.31119 | 0.87792 | 3.7376 | 10.4576 | 12.1743 | 0.04563 | 55.0894 | 780.4757 | 137.5 | 917.9757 | 1457.3781 | 1
132 | 13 | 784 | 163 |  | 0.31119 | 0.87792 | 3.7376 | 10.4576 | 13.1743 | 0.30743 | 52.522 | 748.9057 | 135.8333 | 884.739 | 1404.6116 | 1
132 | 14 | 769 | 153 |  | 0.31119 | 0.87792 | 3.7376 | 10.4576 | 14.1743 | 0.56923 | 46.8563 | 659.738 | 127.5 | 787.238 | 1249.8191 | 1
132 | 15 | 529 | 230 |  | 0.31119 | 0.87792 | 3.7376 | 10.4576 | 15.1743 | 0.83103 | 39.2396 | 375.6836 | 191.6667 | 567.3502 | 900.7252 | 1
132 | 16 | 314 | 245 |  | 0.31119 | 0.87792 | 3.7376 | 10.4576 | 16.1743 | 1.0928 | 30.5955 | 163.9348 | 204.1667 | 368.1014 | 584.3978 | 1
132 | 17 | 220 | 194 |  | 0.31119 | 0.87792 | 3.7376 | 10.4576 | 17.1743 | 1.3546 | 21.5487 | 67.4212 | 161.6667 | 229.0879 | 363.6999 | 1
132 | 18 | 56 | 117 |  | 0.31119 | 0.87792 | 3.7376 | 10.4576 | 18.1743 | 1.6164 | 12.5431 | 4.3678 | 97.5 | 101.8678 | 161.7252 | 1
132 | 19 | 0 | 31 |  | 0.31119 | 0.87792 | 3.7376 | 10.4576 | 19.1743 | 1.8782 | 3.9479 | 0 | 25.8333 | 25.8333 | 41.013 | 0
132 | 20 | 0 | 3 |  | 0.31119 | 0.87792 | 3.7376 | 10.4576 | 20.1743 | 2.14 | -3.8746 | 0 | 2.5 | 2.5 | 3.969 | 0
132 | 21 | 0 | 0 |  | 0.31119 | 0.87792 | 3.7376 | 10.4576 | 21.1743 | 2.4018 | -10.5327 | 0 | 0 | 0 | 0 | 0
132 | 22 | 0 | 0 |  | 0.31119 | 0.87792 | 3.7376 | 10.4576 | 22.1743 | 2.6636 | -15.6029 | 0 | 0 | 0 | 0 | 0
132 | 23 | 0 | 0 |  | 0.31119 | 0.87792 | 3.7376 | 10.4576 | 23.1743 | 2.9254 | -18.676 | 0 | 0 | 0 | 0 | 0
132 | 24 | 0 | 0 |  | 0.31119 | 0.87792 | 3.7376 | 10.4576 | 24.1743 | 3.1872 | -19.4539 | 0 | 0 | 0 | 0 | 0
133 | 1 | 0 | 0 |  | 0.31574 | 0.89514 | 3.7534 | 10.4734 | 1.1746 | -2.8341 | -17.5971 | 0 | 0 | 0 | 0 | 0
133 | 2 | 0 | 0 |  | 0.31574 | 0.89514 | 3.7534 | 10.4734 | 2.1746 | -2.5723 | -13.7957 | 0 | 0 | 0 | 0 | 0
133 | 3 | 0 | 0 |  | 0.31574 | 0.89514 | 3.7534 | 10.4734 | 3.1746 | -2.3105 | -8.1358 | 0 | 0 | 0 | 0 | 0
133 | 4 | 0 | 0 |  | 0.31574 | 0.89514 | 3.7534 | 10.4734 | 4.1746 | -2.0487 | -1.0374 | 0 | 0 | 0 | 0 | 0
133 | 5 | 0 | 5 |  | 0.31574 | 0.89514 | 3.7534 | 10.4734 | 5.1746 | -1.7869 | 7.0867 | 0 | 4.1667 | 4.1667 | 6.615 | 0
133 | 6 | 0 | 34 |  | 0.31574 | 0.89514 | 3.7534 | 10.4734 | 6.1746 | -1.5251 | 15.8589 | 0 | 28.3333 | 28.3333 | 44.982 | 1
133 | 7 | 0 | 86 |  | 0.31574 | 0.89514 | 3.7534 | 10.4734 | 7.1746 | -1.2633 | 24.9213 | 0 | 71.6667 | 71.6667 | 113.778 | 1
133 | 8 | 0 | 144 |  | 0.31574 | 0.89514 | 3.7534 | 10.4734 | 8.1746 | -1.0015 | 33.8893 | 0 | 120 | 120 | 190.512 | 1
133 | 9 | 8 | 194 |  | 0.31574 | 0.89514 | 3.7534 | 10.4734 | 9.1746 | -0.7397 | 42.2709 | 6.1407 | 161.6667 | 167.8074 | 266.411 | 1
133 | 10 | 13 | 234 |  | 0.31574 | 0.89514 | 3.7534 | 10.4734 | 10.1746 | -0.4779 | 49.3474 | 11.6809 | 195 | 206.6809 | 328.1266 | 1
133 | 11 | 5 | 270 |  | 0.31574 | 0.89514 | 3.7534 | 10.4734 | 11.1746 | -0.2161 | 54.0799 | 4.882 | 225 | 229.882 | 364.9606 | 1
133 | 12 | 5 | 284 |  | 0.31574 | 0.89514 | 3.7534 | 10.4734 | 12.1746 | 0.045699 | 55.3498 | 4.9794 | 236.6667 | 241.6461 | 383.6373 | 1
133 | 13 | 5 | 281 |  | 0.31574 | 0.89514 | 3.7534 | 10.4734 | 13.1746 | 0.3075 | 52.7695 | 4.7783 | 234.1667 | 238.9449 | 379.349 | 1
133 | 14 | 4 | 261 |  | 0.31574 | 0.89514 | 3.7534 | 10.4734 | 14.1746 | 0.5693 | 47.0834 | 3.4339 | 217.5 | 220.9339 | 350.7546 | 1
133 | 15 | 11 | 221 |  | 0.31574 | 0.89514 | 3.7534 | 10.4734 | 15.1746 | 0.8311 | 39.45 | 7.8202 | 184.1667 | 191.9869 | 304.7984 | 1
133 | 16 | 5 | 177 |  | 0.31574 | 0.89514 | 3.7534 | 10.4734 | 16.1746 | 1.0929 | 30.7965 | 2.6155 | 147.5 | 150.1155 | 238.3234 | 1
133 | 17 | 35 | 182 |  | 0.31574 | 0.89514 | 3.7534 | 10.4734 | 17.1746 | 1.3547 | 21.7473 | 10.7727 | 151.6667 | 162.4394 | 257.8888 | 1
133 | 18 | 5 | 104 |  | 0.31574 | 0.89514 | 3.7534 | 10.4734 | 18.1746 | 1.6165 | 12.7452 | 0.39832 | 86.6667 | 87.065 | 138.2244 | 1
133 | 19 | 0 | 32 |  | 0.31574 | 0.89514 | 3.7534 | 10.4734 | 19.1746 | 1.8783 | 4.1583 | 0 | 26.6667 | 26.6667 | 42.336 | 0
133 | 20 | 0 | 2 |  | 0.31574 | 0.89514 | 3.7534 | 10.4734 | 20.1746 | 2.1401 | -3.6525 | 0 | 1.6667 | 1.6667 | 2.646 | 0
133 | 21 | 0 | 0 |  | 0.31574 | 0.89514 | 3.7534 | 10.4734 | 21.1746 | 2.4019 | -10.297 | 0 | 0 | 0 | 0 | 0
133 | 22 | 0 | 0 |  | 0.31574 | 0.89514 | 3.7534 | 10.4734 | 22.1746 | 2.6637 | -15.3543 | 0 | 0 | 0 | 0 | 0
133 | 23 | 0 | 0 |  | 0.31574 | 0.89514 | 3.7534 | 10.4734 | 23.1746 | 2.9255 | -18.4182 | 0 | 0 | 0 | 0 | 0
133 | 24 | 0 | 0 |  | 0.31574 | 0.89514 | 3.7534 | 10.4734 | 24.1746 | 3.1873 | -19.1931 | 0 | 0 | 0 | 0 | 0
134 | 1 | 0 | 0 |  | 0.3202 | 0.91235 | 3.7596 | 10.4796 | 1.1747 | -2.8341 | -17.346 | 0 | 0 | 0 | 0 | 0
134 | 2 | 0 | 0 |  | 0.3202 | 0.91235 | 3.7596 | 10.4796 | 2.1747 | -2.5723 | -13.5544 | 0 | 0 | 0 | 0 | 0
134 | 3 | 0 | 0 |  | 0.3202 | 0.91235 | 3.7596 | 10.4796 | 3.1747 | -2.3105 | -7.9071 | 0 | 0 | 0 | 0 | 0
134 | 4 | 0 | 0 |  | 0.3202 | 0.91235 | 3.7596 | 10.4796 | 4.1747 | -2.0487 | -0.82118 | 0 | 0 | 0 | 0 | 0
134 | 5 | 0 | 5 |  | 0.3202 | 0.91235 | 3.7596 | 10.4796 | 5.1747 | -1.7869 | 7.2927 | 0 | 4.1667 | 4.1667 | 6.615 | 0
134 | 6 | 0 | 35 |  | 0.3202 | 0.91235 | 3.7596 | 10.4796 | 6.1747 | -1.5251 | 16.0584 | 0 | 29.1667 | 29.1667 | 46.305 | 1
134 | 7 | 0 | 87 |  | 0.3202 | 0.91235 | 3.7596 | 10.4796 | 7.1747 | -1.2633 | 25.1192 | 0 | 72.5 | 72.5 | 115.101 | 1
134 | 8 | 0 | 145 |  | 0.3202 | 0.91235 | 3.7596 | 10.4796 | 8.1747 | -1.0015 | 34.0916 | 0 | 120.8333 | 120.8333 | 191.835 | 1
134 | 9 | 8 | 195 |  | 0.3202 | 0.91235 | 3.7596 | 10.4796 | 9.1747 | -0.73967 | 42.4847 | 6.1463 | 162.5 | 168.6463 | 267.7429 | 1
134 | 10 | 12 | 235 |  | 0.3202 | 0.91235 | 3.7596 | 10.4796 | 10.1747 | -0.47787 | 49.5789 | 10.7884 | 195.8333 | 206.6217 | 328.0326 | 1
134 | 11 | 5 | 270 |  | 0.3202 | 0.91235 | 3.7596 | 10.4796 | 11.1747 | -0.21607 | 54.3294 | 4.8839 | 225 | 229.8839 | 364.9636 | 1
134 | 12 | 105 | 373 |  | 0.3202 | 0.91235 | 3.7596 | 10.4796 | 12.1747 | 0.045726 | 55.605 | 104.6036 | 310.8333 | 415.437 | 659.5477 | 1
134 | 13 | 61 | 405 |  | 0.3202 | 0.91235 | 3.7596 | 10.4796 | 13.1747 | 0.30753 | 53.0126 | 58.3193 | 337.5 | 395.8193 | 628.4027 | 1
134 | 14 | 60 | 376 |  | 0.3202 | 0.91235 | 3.7596 | 10.4796 | 14.1747 | 0.56932 | 47.3069 | 51.54 | 313.3333 | 364.8733 | 579.2729 | 1
134 | 15 | 84 | 308 |  | 0.3202 | 0.91235 | 3.7596 | 10.4796 | 15.1747 | 0.83112 | 39.6573 | 59.7809 | 256.6667 | 316.4476 | 502.3922 | 1
134 | 16 | 73 | 245 |  | 0.3202 | 0.91235 | 3.7596 | 10.4796 | 16.1747 | 1.0929 | 30.9947 | 38.2612 | 204.1667 | 242.4279 | 384.8785 | 1
134 | 17 | 18 | 190 |  | 0.3202 | 0.91235 | 3.7596 | 10.4796 | 17.1747 | 1.3547 | 21.9432 | 5.5643 | 158.3333 | 163.8976 | 260.2039 | 1
134 | 18 | 5 | 105 |  | 0.3202 | 0.91235 | 3.7596 | 10.4796 | 18.1747 | 1.6165 | 12.9446 | 0.40667 | 87.5 | 87.9067 | 139.5606 | 1
134 | 19 | 0 | 34 |  | 0.3202 | 0.91235 | 3.7596 | 10.4796 | 19.1747 | 1.8783 | 4.3658 | 0 | 28.3333 | 28.3333 | 44.982 | 0
134 | 20 | 0 | 2 |  | 0.3202 | 0.91235 | 3.7596 | 10.4796 | 20.1747 | 2.1401 | -3.4336 | 0 | 1.6667 | 1.6667 | 2.646 | 0
134 | 21 | 0 | 0 |  | 0.3202 | 0.91235 | 3.7596 | 10.4796 | 21.1747 | 2.4019 | -10.0651 | 0 | 0 | 0 | 0 | 0
134 | 22 | 0 | 0 |  | 0.3202 | 0.91235 | 3.7596 | 10.4796 | 22.1747 | 2.6637 | -15.11 | 0 | 0 | 0 | 0 | 0
134 | 23 | 0 | 0 |  | 0.3202 | 0.91235 | 3.7596 | 10.4796 | 23.1747 | 2.9255 | -18.1651 | 0 | 0 | 0 | 0 | 0
134 | 24 | 0 | 0 |  | 0.3202 | 0.91235 | 3.7596 | 10.4796 | 24.1747 | 3.1873 | -18.9375 | 0 | 0 | 0 | 0 | 0
135 | 1 | 0 | 0 |  | 0.32457 | 0.92957 | 3.7562 | 10.4762 | 1.1746 | -2.8341 | -17.1004 | 0 | 0 | 0 | 0 | 0
135 | 2 | 0 | 0 |  | 0.32457 | 0.92957 | 3.7562 | 10.4762 | 2.1746 | -2.5723 | -13.3189 | 0 | 0 | 0 | 0 | 0
135 | 3 | 0 | 0 |  | 0.32457 | 0.92957 | 3.7562 | 10.4762 | 3.1746 | -2.3105 | -7.6841 | 0 | 0 | 0 | 0 | 0
135 | 4 | 0 | 0 |  | 0.32457 | 0.92957 | 3.7562 | 10.4762 | 4.1746 | -2.0487 | -0.61062 | 0 | 0 | 0 | 0 | 0
135 | 5 | 0 | 16 |  | 0.32457 | 0.92957 | 3.7562 | 10.4762 | 5.1746 | -1.7869 | 7.4931 | 0 | 13.3333 | 13.3333 | 21.168 | 0
135 | 6 | 123 | 78 |  | 0.32457 | 0.92957 | 3.7562 | 10.4762 | 6.1746 | -1.5251 | 16.2522 | 20.0396 | 65 | 85.0396 | 135.0088 | 1
135 | 7 | 354 | 126 |  | 0.32457 | 0.92957 | 3.7562 | 10.4762 | 7.1746 | -1.2633 | 25.3113 | 137.2324 | 105 | 242.2324 | 384.5681 | 1
135 | 8 | 557 | 142 |  | 0.32457 | 0.92957 | 3.7562 | 10.4762 | 8.1746 | -1.0015 | 34.2881 | 331.0596 | 118.3333 | 449.393 | 713.4563 | 1
135 | 9 | 648 | 151 |  | 0.32457 | 0.92957 | 3.7562 | 10.4762 | 9.1746 | -0.73969 | 42.6925 | 498.2711 | 125.8333 | 624.1045 | 990.8282 | 1
135 | 10 | 322 | 355 |  | 0.32457 | 0.92957 | 3.7562 | 10.4762 | 10.1746 | -0.47789 | 49.8045 | 289.6357 | 295.8333 | 585.469 | 929.4906 | 1
135 | 11 | 270 | 356 |  | 0.32457 | 0.92957 | 3.7562 | 10.4762 | 11.1746 | -0.21609 | 54.5733 | 263.8234 | 296.6667 | 560.49 | 889.834 | 1
135 | 12 | 101 | 383 |  | 0.32457 | 0.92957 | 3.7562 | 10.4762 | 12.1746 | 0.045711 | 55.8551 | 100.6513 | 319.1667 | 419.818 | 666.503 | 1
135 | 13 | 272 | 371 |  | 0.32457 | 0.92957 | 3.7562 | 10.4762 | 13.1746 | 0.30751 | 53.2512 | 260.1513 | 309.1667 | 569.318 | 903.8492 | 1
135 | 14 | 170 | 419 |  | 0.32457 | 0.92957 | 3.7562 | 10.4762 | 14.1746 | 0.56931 | 47.5265 | 146.12 | 349.1667 | 495.2867 | 786.3171 | 1
135 | 15 | 364 | 301 |  | 0.32457 | 0.92957 | 3.7562 | 10.4762 | 15.1746 | 0.83111 | 39.8612 | 259.3225 | 250.8333 | 510.1559 | 809.9234 | 1
135 | 16 | 572 | 169 |  | 0.32457 | 0.92957 | 3.7562 | 10.4762 | 16.1746 | 1.0929 | 31.1899 | 300.3851 | 140.8333 | 441.2184 | 700.4783 | 1
135 | 17 | 377 | 188 |  | 0.32457 | 0.92957 | 3.7562 | 10.4762 | 17.1746 | 1.3547 | 22.1364 | 117.0452 | 156.6667 | 273.7118 | 434.5449 | 1
135 | 18 | 76 | 118 |  | 0.32457 | 0.92957 | 3.7562 | 10.4762 | 18.1746 | 1.6165 | 13.1413 | 6.3082 | 98.3333 | 104.6415 | 166.1289 | 1
135 | 19 | 29 | 58 |  | 0.32457 | 0.92957 | 3.7562 | 10.4762 | 19.1746 | 1.8783 | 4.5703 | 0 | 48.3333 | 48.3333 | 76.734 | 0
135 | 20 | 0 | 6 |  | 0.32457 | 0.92957 | 3.7562 | 10.4762 | 20.1746 | 2.1401 | -3.218 | 0 | 5 | 5 | 7.938 | 0
135 | 21 | 0 | 0 |  | 0.32457 | 0.92957 | 3.7562 | 10.4762 | 21.1746 | 2.4019 | -9.8369 | 0 | 0 | 0 | 0 | 0
135 | 22 | 0 | 0 |  | 0.32457 | 0.92957 | 3.7562 | 10.4762 | 22.1746 | 2.6637 | -14.8701 | 0 | 0 | 0 | 0 | 0
135 | 23 | 0 | 0 |  | 0.32457 | 0.92957 | 3.7562 | 10.4762 | 23.1746 | 2.9255 | -17.917 | 0 | 0 | 0 | 0 | 0
135 | 24 | 0 | 0 |  | 0.32457 | 0.92957 | 3.7562 | 10.4762 | 24.1746 | 3.1873 | -18.6872 | 0 | 0 | 0 | 0 | 0
136 | 1 | 0 | 0 |  | 0.32885 | 0.94678 | 3.7433 | 10.4633 | 1.1744 | -2.8341 | -16.8605 | 0 | 0 | 0 | 0 | 0
136 | 2 | 0 | 0 |  | 0.32885 | 0.94678 | 3.7433 | 10.4633 | 2.1744 | -2.5723 | -13.0891 | 0 | 0 | 0 | 0 | 0
136 | 3 | 0 | 0 |  | 0.32885 | 0.94678 | 3.7433 | 10.4633 | 3.1744 | -2.3105 | -7.4669 | 0 | 0 | 0 | 0 | 0
136 | 4 | 0 | 0 |  | 0.32885 | 0.94678 | 3.7433 | 10.4633 | 4.1744 | -2.0487 | -0.40578 | 0 | 0 | 0 | 0 | 0
136 | 5 | 0 | 14 |  | 0.32885 | 0.94678 | 3.7433 | 10.4633 | 5.1744 | -1.7869 | 7.6878 | 0 | 11.6667 | 11.6667 | 18.522 | 0
136 | 6 | 84 | 79 |  | 0.32885 | 0.94678 | 3.7433 | 10.4633 | 6.1744 | -1.5251 | 16.4404 | 13.8077 | 65.8333 | 79.6411 | 126.4382 | 1
136 | 7 | 20 | 135 |  | 0.32885 | 0.94678 | 3.7433 | 10.4633 | 7.1744 | -1.2633 | 25.4977 | 7.7759 | 112.5 | 120.2759 | 190.95 | 1
136 | 8 | 12 | 229 |  | 0.32885 | 0.94678 | 3.7433 | 10.4633 | 8.1744 | -1.0015 | 34.4787 | 7.1424 | 190.8333 | 197.9757 | 314.3063 | 1
136 | 9 | 80 | 272 |  | 0.32885 | 0.94678 | 3.7433 | 10.4633 | 9.1744 | -0.73974 | 42.8943 | 61.5624 | 226.6667 | 288.2291 | 457.5925 | 1
136 | 10 | 89 | 330 |  | 0.32885 | 0.94678 | 3.7433 | 10.4633 | 10.1744 | -0.47794 | 50.024 | 80.0915 | 275 | 355.0915 | 563.7432 | 1
136 | 11 | 62 | 393 |  | 0.32885 | 0.94678 | 3.7433 | 10.4633 | 11.1744 | -0.21614 | 54.8114 | 60.6011 | 327.5 | 388.1011 | 616.1494 | 1
136 | 12 | 62 | 413 |  | 0.32885 | 0.94678 | 3.7433 | 10.4633 | 12.1744 | 0.045655 | 56.1 | 61.8045 | 344.1667 | 405.9712 | 644.5198 | 1
136 | 13 | 260 | 377 |  | 0.32885 | 0.94678 | 3.7433 | 10.4633 | 13.1744 | 0.30745 | 53.4853 | 248.7702 | 314.1667 | 562.9368 | 893.7185 | 1
136 | 14 | 93 | 354 |  | 0.32885 | 0.94678 | 3.7433 | 10.4633 | 14.1744 | 0.56925 | 47.7423 | 79.9848 | 295 | 374.9848 | 595.3258 | 1
136 | 15 | 85 | 310 |  | 0.32885 | 0.94678 | 3.7433 | 10.4633 | 15.1744 | 0.83105 | 40.0619 | 60.6194 | 258.3333 | 318.9527 | 506.3693 | 1
136 | 16 | 75 | 248 |  | 0.32885 | 0.94678 | 3.7433 | 10.4633 | 16.1744 | 1.0929 | 31.3821 | 39.4629 | 206.6667 | 246.1296 | 390.7553 | 1
136 | 17 | 19 | 193 |  | 0.32885 | 0.94678 | 3.7433 | 10.4633 | 17.1744 | 1.3547 | 22.3267 | 5.9243 | 160.8333 | 166.7576 | 264.7444 | 1
136 | 18 | 6 | 109 |  | 0.32885 | 0.94678 | 3.7433 | 10.4633 | 18.1744 | 1.6165 | 13.335 | 0.50803 | 90.8333 | 91.3414 | 145.0135 | 1
136 | 19 | 0 | 36 |  | 0.32885 | 0.94678 | 3.7433 | 10.4633 | 19.1744 | 1.8783 | 4.7717 | 0 | 30 | 30 | 47.628 | 0
136 | 20 | 0 | 2 |  | 0.32885 | 0.94678 | 3.7433 | 10.4633 | 20.1744 | 2.14 | -3.0059 | 0 | 1.6667 | 1.6667 | 2.646 | 0
136 | 21 | 0 | 0 |  | 0.32885 | 0.94678 | 3.7433 | 10.4633 | 21.1744 | 2.4018 | -9.6127 | 0 | 0 | 0 | 0 | 0
136 | 22 | 0 | 0 |  | 0.32885 | 0.94678 | 3.7433 | 10.4633 | 22.1744 | 2.6636 | -14.6345 | 0 | 0 | 0 | 0 | 0
136 | 23 | 0 | 0 |  | 0.32885 | 0.94678 | 3.7433 | 10.4633 | 23.1744 | 2.9254 | -17.6738 | 0 | 0 | 0 | 0 | 0
136 | 24 | 0 | 0 |  | 0.32885 | 0.94678 | 3.7433 | 10.4633 | 24.1744 | 3.1872 | -18.4424 | 0 | 0 | 0 | 0 | 0
137 | 1 | 0 | 0 |  | 0.33303 | 0.964 | 3.7209 | 10.4409 | 1.174 | -2.8342 | -16.6264 | 0 | 0 | 0 | 0 | 0
137 | 2 | 0 | 0 |  | 0.33303 | 0.964 | 3.7209 | 10.4409 | 2.174 | -2.5724 | -12.8652 | 0 | 0 | 0 | 0 | 0
137 | 3 | 0 | 0 |  | 0.33303 | 0.964 | 3.7209 | 10.4409 | 3.174 | -2.3106 | -7.2555 | 0 | 0 | 0 | 0 | 0
137 | 4 | 0 | 0 |  | 0.33303 | 0.964 | 3.7209 | 10.4409 | 4.174 | -2.0488 | -0.20672 | 0 | 0 | 0 | 0 | 0
137 | 5 | 0 | 17 |  | 0.33303 | 0.964 | 3.7209 | 10.4409 | 5.174 | -1.787 | 7.8767 | 0 | 14.1667 | 14.1667 | 22.491 | 0
137 | 6 | 0 | 60 |  | 0.33303 | 0.964 | 3.7209 | 10.4409 | 6.174 | -1.5252 | 16.6227 | 0 | 50 | 50 | 79.38 | 1
137 | 7 | 6 | 141 |  | 0.33303 | 0.964 | 3.7209 | 10.4409 | 7.174 | -1.2634 | 25.6783 | 2.3391 | 117.5 | 119.8391 | 190.2566 | 1
137 | 8 | 244 | 229 |  | 0.33303 | 0.964 | 3.7209 | 10.4409 | 8.174 | -1.0016 | 34.6633 | 145.4184 | 190.8333 | 336.2517 | 533.8332 | 1
137 | 9 | 350 | 261 |  | 0.33303 | 0.964 | 3.7209 | 10.4409 | 9.174 | -0.73984 | 43.09 | 269.525 | 217.5 | 487.025 | 773.2009 | 1
137 | 10 | 171 | 380 |  | 0.33303 | 0.964 | 3.7209 | 10.4409 | 10.174 | -0.47804 | 50.2374 | 153.9473 | 316.6667 | 470.614 | 747.1468 | 1
137 | 11 | 94 | 367 |  | 0.33303 | 0.964 | 3.7209 | 10.4409 | 11.174 | -0.21624 | 55.0435 | 91.9057 | 305.8333 | 397.739 | 631.4505 | 1
137 | 12 | 61 | 413 |  | 0.33303 | 0.964 | 3.7209 | 10.4409 | 12.174 | 0.045557 | 56.3396 | 60.8245 | 344.1667 | 404.9912 | 642.964 | 1
137 | 13 | 15 | 275 |  | 0.33303 | 0.964 | 3.7209 | 10.4409 | 13.174 | 0.30736 | 53.7148 | 14.3575 | 229.1667 | 243.5241 | 386.6189 | 1
137 | 14 | 104 | 347 |  | 0.33303 | 0.964 | 3.7209 | 10.4409 | 14.174 | 0.56916 | 47.9541 | 89.4989 | 289.1667 | 378.6655 | 601.1694 | 1
137 | 15 | 85 | 311 |  | 0.33303 | 0.964 | 3.7209 | 10.4409 | 15.174 | 0.83096 | 40.2591 | 60.6825 | 259.1667 | 319.8492 | 507.7925 | 1
137 | 16 | 187 | 267 |  | 0.33303 | 0.964 | 3.7209 | 10.4409 | 16.174 | 1.0928 | 31.5713 | 98.5856 | 222.5 | 321.0856 | 509.7555 | 1
137 | 17 | 411 | 163 |  | 0.33303 | 0.964 | 3.7209 | 10.4409 | 17.174 | 1.3546 | 22.514 | 128.7014 | 135.8333 | 264.5348 | 419.9754 | 1
137 | 18 | 76 | 120 |  | 0.33303 | 0.964 | 3.7209 | 10.4409 | 18.174 | 1.6164 | 13.5258 | 6.5617 | 100 | 106.5617 | 169.1774 | 1
137 | 19 | 0 | 37 |  | 0.33303 | 0.964 | 3.7209 | 10.4409 | 19.174 | 1.8782 | 4.97 | 0 | 30.8333 | 30.8333 | 48.951 | 0
137 | 20 | 0 | 4 |  | 0.33303 | 0.964 | 3.7209 | 10.4409 | 20.174 | 2.14 | -2.7973 | 0 | 3.3333 | 3.3333 | 5.292 | 0
137 | 21 | 0 | 0 |  | 0.33303 | 0.964 | 3.7209 | 10.4409 | 21.174 | 2.4018 | -9.3924 | 0 | 0 | 0 | 0 | 0
137 | 22 | 0 | 0 |  | 0.33303 | 0.964 | 3.7209 | 10.4409 | 22.174 | 2.6636 | -14.4036 | 0 | 0 | 0 | 0 | 0
137 | 23 | 0 | 0 |  | 0.33303 | 0.964 | 3.7209 | 10.4409 | 23.174 | 2.9254 | -17.4358 | 0 | 0 | 0 | 0 | 0
137 | 24 | 0 | 0 |  | 0.33303 | 0.964 | 3.7209 | 10.4409 | 24.174 | 3.1871 | -18.2031 | 0 | 0 | 0 | 0 | 0
138 | 1 | 0 | 0 |  | 0.33711 | 0.98121 | 3.6892 | 10.4092 | 1.1735 | -2.8344 | -16.3981 | 0 | 0 | 0 | 0 | 0
138 | 2 | 0 | 0 |  | 0.33711 | 0.98121 | 3.6892 | 10.4092 | 2.1735 | -2.5726 | -12.6472 | 0 | 0 | 0 | 0 | 0
138 | 3 | 0 | 0 |  | 0.33711 | 0.98121 | 3.6892 | 10.4092 | 3.1735 | -2.3108 | -7.05 | 0 | 0 | 0 | 0 | 0
138 | 4 | 0 | 0 |  | 0.33711 | 0.98121 | 3.6892 | 10.4092 | 4.1735 | -2.049 | -0.013505 | 0 | 0 | 0 | 0 | 0
138 | 5 | 0 | 10 |  | 0.33711 | 0.98121 | 3.6892 | 10.4092 | 5.1735 | -1.7872 | 8.0598 | 0 | 8.3333 | 8.3333 | 13.23 | 0
138 | 6 | 0 | 62 |  | 0.33711 | 0.98121 | 3.6892 | 10.4092 | 6.1735 | -1.5254 | 16.7993 | 0 | 51.6667 | 51.6667 | 82.026 | 1
138 | 7 | 6 | 143 |  | 0.33711 | 0.98121 | 3.6892 | 10.4092 | 7.1735 | -1.2636 | 25.853 | 2.3451 | 119.1667 | 121.5118 | 192.9121 | 1
138 | 8 | 153 | 228 |  | 0.33711 | 0.98121 | 3.6892 | 10.4092 | 8.1735 | -1.0018 | 34.842 | 91.2944 | 190 | 281.2944 | 446.5829 | 1
138 | 9 | 72 | 279 |  | 0.33711 | 0.98121 | 3.6892 | 10.4092 | 9.1735 | -0.73998 | 43.2797 | 55.4805 | 232.5 | 287.9805 | 457.1978 | 1
138 | 10 | 214 | 351 |  | 0.33711 | 0.98121 | 3.6892 | 10.4092 | 10.1735 | -0.47818 | 50.4447 | 192.7302 | 292.5 | 485.2302 | 770.3515 | 1
138 | 11 | 94 | 368 |  | 0.33711 | 0.98121 | 3.6892 | 10.4092 | 11.1735 | -0.21638 | 55.2697 | 91.9293 | 306.6667 | 398.596 | 632.8109 | 1
138 | 12 | 254 | 385 |  | 0.33711 | 0.98121 | 3.6892 | 10.4092 | 12.1735 | 0.045419 | 56.5737 | 253.334 | 320.8333 | 574.1674 | 911.5481 | 1
138 | 13 | 589 | 265 |  | 0.33711 | 0.98121 | 3.6892 | 10.4092 | 13.1735 | 0.30722 | 53.9396 | 563.9715 | 220.8333 | 784.8048 | 1245.9561 | 1
138 | 14 | 710 | 203 |  | 0.33711 | 0.98121 | 3.6892 | 10.4092 | 14.1735 | 0.56902 | 48.1619 | 611.3628 | 169.1667 | 780.5295 | 1239.1686 | 1
138 | 15 | 729 | 148 |  | 0.33711 | 0.98121 | 3.6892 | 10.4092 | 15.1735 | 0.83082 | 40.4529 | 520.9818 | 123.3333 | 644.3151 | 1022.9146 | 1
138 | 16 | 636 | 146 |  | 0.33711 | 0.98121 | 3.6892 | 10.4092 | 16.1735 | 1.0926 | 31.7573 | 335.9479 | 121.6667 | 457.6145 | 726.5088 | 1
138 | 17 | 467 | 149 |  | 0.33711 | 0.98121 | 3.6892 | 10.4092 | 17.1735 | 1.3544 | 22.6984 | 146.8628 | 124.1667 | 271.0295 | 430.2864 | 1
138 | 18 | 285 | 112 |  | 0.33711 | 0.98121 | 3.6892 | 10.4092 | 18.1735 | 1.6162 | 13.7135 | 25.0808 | 93.3333 | 118.4141 | 187.9943 | 1
138 | 19 | 49 | 60 |  | 0.33711 | 0.98121 | 3.6892 | 10.4092 | 19.1735 | 1.878 | 5.1649 | 0 | 50 | 50 | 79.38 | 0
138 | 20 | 0 | 8 |  | 0.33711 | 0.98121 | 3.6892 | 10.4092 | 20.1735 | 2.1398 | -2.5923 | 0 | 6.6667 | 6.6667 | 10.584 | 0
138 | 21 | 0 | 0 |  | 0.33711 | 0.98121 | 3.6892 | 10.4092 | 21.1735 | 2.4016 | -9.1763 | 0 | 0 | 0 | 0 | 0
138 | 22 | 0 | 0 |  | 0.33711 | 0.98121 | 3.6892 | 10.4092 | 22.1735 | 2.6634 | -14.1773 | 0 | 0 | 0 | 0 | 0
138 | 23 | 0 | 0 |  | 0.33711 | 0.98121 | 3.6892 | 10.4092 | 23.1735 | 2.9252 | -17.2029 | 0 | 0 | 0 | 0 | 0
138 | 24 | 0 | 0 |  | 0.33711 | 0.98121 | 3.6892 | 10.4092 | 24.1735 | 3.187 | -17.9694 | 0 | 0 | 0 | 0 | 0
139 | 1 | 0 | 0 |  | 0.3411 | 0.99842 | 3.6483 | 10.3683 | 1.1728 | -2.8346 | -16.1757 | 0 | 0 | 0 | 0 | 0
139 | 2 | 0 | 0 |  | 0.3411 | 0.99842 | 3.6483 | 10.3683 | 2.1728 | -2.5728 | -12.4351 | 0 | 0 | 0 | 0 | 0
139 | 3 | 0 | 0 |  | 0.3411 | 0.99842 | 3.6483 | 10.3683 | 3.1728 | -2.311 | -6.8505 | 0 | 0 | 0 | 0 | 0
139 | 4 | 0 | 0 |  | 0.3411 | 0.99842 | 3.6483 | 10.3683 | 4.1728 | -2.0492 | 0.17382 | 0 | 0 | 0 | 0 | 0
139 | 5 | 0 | 7 |  | 0.3411 | 0.99842 | 3.6483 | 10.3683 | 5.1728 | -1.7874 | 8.2371 | 0 | 5.8333 | 5.8333 | 9.261 | 0
139 | 6 | 0 | 39 |  | 0.3411 | 0.99842 | 3.6483 | 10.3683 | 6.1728 | -1.5256 | 16.9701 | 0 | 32.5 | 32.5 | 51.597 | 1
139 | 7 | 0 | 91 |  | 0.3411 | 0.99842 | 3.6483 | 10.3683 | 7.1728 | -1.2638 | 26.0218 | 0 | 75.8333 | 75.8333 | 120.393 | 1
139 | 8 | 0 | 149 |  | 0.3411 | 0.99842 | 3.6483 | 10.3683 | 8.1728 | -1.002 | 35.0147 | 0 | 124.1667 | 124.1667 | 197.127 | 1
139 | 9 | 8 | 198 |  | 0.3411 | 0.99842 | 3.6483 | 10.3683 | 9.1728 | -0.74016 | 43.4631 | 6.168 | 165 | 171.168 | 271.7464 | 1
139 | 10 | 70 | 342 |  | 0.3411 | 0.99842 | 3.6483 | 10.3683 | 10.1728 | -0.47836 | 50.6457 | 63.063 | 285 | 348.063 | 552.5849 | 1
139 | 11 | 87 | 372 |  | 0.3411 | 0.99842 | 3.6483 | 10.3683 | 11.1728 | -0.21656 | 55.4899 | 85.1027 | 310 | 395.1027 | 627.2651 | 1
139 | 12 | 89 | 391 |  | 0.3411 | 0.99842 | 3.6483 | 10.3683 | 12.1728 | 0.04524 | 56.8023 | 88.7875 | 325.8333 | 414.6208 | 658.252 | 1
139 | 13 | 252 | 383 |  | 0.3411 | 0.99842 | 3.6483 | 10.3683 | 13.1728 | 0.30704 | 54.1596 | 241.3749 | 319.1667 | 560.5416 | 889.9158 | 1
139 | 14 | 91 | 357 |  | 0.3411 | 0.99842 | 3.6483 | 10.3683 | 14.1728 | 0.56884 | 48.3657 | 78.4035 | 297.5 | 375.9035 | 596.7844 | 1
139 | 15 | 199 | 337 |  | 0.3411 | 0.99842 | 3.6483 | 10.3683 | 15.1728 | 0.83064 | 40.6432 | 142.363 | 280.8333 | 423.1963 | 671.8665 | 1
139 | 16 | 324 | 247 |  | 0.3411 | 0.99842 | 3.6483 | 10.3683 | 16.1728 | 1.0924 | 31.9401 | 171.4752 | 205.8333 | 377.3085 | 599.015 | 1
139 | 17 | 453 | 146 |  | 0.3411 | 0.99842 | 3.6483 | 10.3683 | 17.1728 | 1.3542 | 22.8797 | 143.0664 | 121.6667 | 264.7331 | 420.2902 | 1
139 | 18 | 248 | 119 |  | 0.3411 | 0.99842 | 3.6483 | 10.3683 | 18.1728 | 1.616 | 13.898 | 22.2364 | 99.1667 | 121.4031 | 192.7396 | 1
139 | 19 | 60 | 58 |  | 0.3411 | 0.99842 | 3.6483 | 10.3683 | 19.1728 | 1.8778 | 5.3566 | 0 | 48.3333 | 48.3333 | 76.734 | 0
139 | 20 | 0 | 7 |  | 0.3411 | 0.99842 | 3.6483 | 10.3683 | 20.1728 | 2.1396 | -2.3911 | 0 | 5.8333 | 5.8333 | 9.261 | 0
139 | 21 | 0 | 0 |  | 0.3411 | 0.99842 | 3.6483 | 10.3683 | 21.1728 | 2.4014 | -8.9644 | 0 | 0 | 0 | 0 | 0
139 | 22 | 0 | 0 |  | 0.3411 | 0.99842 | 3.6483 | 10.3683 | 22.1728 | 2.6632 | -13.9558 | 0 | 0 | 0 | 0 | 0
139 | 23 | 0 | 0 |  | 0.3411 | 0.99842 | 3.6483 | 10.3683 | 23.1728 | 2.925 | -16.9753 | 0 | 0 | 0 | 0 | 0
139 | 24 | 0 | 0 |  | 0.3411 | 0.99842 | 3.6483 | 10.3683 | 24.1728 | 3.1868 | -17.7413 | 0 | 0 | 0 | 0 | 0
140 | 1 | 0 | 0 |  | 0.34499 | 1.0156 | 3.5983 | 10.3183 | 1.172 | -2.8348 | -15.9593 | 0 | 0 | 0 | 0 | 0
140 | 2 | 0 | 0 |  | 0.34499 | 1.0156 | 3.5983 | 10.3183 | 2.172 | -2.573 | -12.2291 | 0 | 0 | 0 | 0 | 0
140 | 3 | 0 | 0 |  | 0.34499 | 1.0156 | 3.5983 | 10.3183 | 3.172 | -2.3112 | -6.657 | 0 | 0 | 0 | 0 | 0
140 | 4 | 0 | 0 |  | 0.34499 | 1.0156 | 3.5983 | 10.3183 | 4.172 | -2.0494 | 0.3552 | 0 | 0 | 0 | 0 | 0
140 | 5 | 0 | 11 |  | 0.34499 | 1.0156 | 3.5983 | 10.3183 | 5.172 | -1.7876 | 8.4085 | 0 | 9.1667 | 9.1667 | 14.553 | 0
140 | 6 | 0 | 40 |  | 0.34499 | 1.0156 | 3.5983 | 10.3183 | 6.172 | -1.5258 | 17.1349 | 0 | 33.3333 | 33.3333 | 52.92 | 1
140 | 7 | 0 | 92 |  | 0.34499 | 1.0156 | 3.5983 | 10.3183 | 7.172 | -1.264 | 26.1847 | 0 | 76.6667 | 76.6667 | 121.716 | 1
140 | 8 | 0 | 150 |  | 0.34499 | 1.0156 | 3.5983 | 10.3183 | 8.172 | -1.0022 | 35.1813 | 0 | 125 | 125 | 198.45 | 1
140 | 9 | 8 | 199 |  | 0.34499 | 1.0156 | 3.5983 | 10.3183 | 9.172 | -0.74038 | 43.6403 | 6.1712 | 165.8333 | 172.0045 | 273.0744 | 1
140 | 10 | 13 | 239 |  | 0.34499 | 1.0156 | 3.5983 | 10.3183 | 10.172 | -0.47858 | 50.8404 | 11.715 | 199.1667 | 210.8817 | 334.7957 | 1
140 | 11 | 5 | 275 |  | 0.34499 | 1.0156 | 3.5983 | 10.3183 | 11.172 | -0.21678 | 55.7039 | 4.8919 | 229.1667 | 234.0586 | 371.5914 | 1
140 | 12 | 5 | 288 |  | 0.34499 | 1.0156 | 3.5983 | 10.3183 | 12.172 | 0.045022 | 57.0253 | 4.9891 | 240 | 244.9891 | 388.9448 | 1
140 | 13 | 5 | 285 |  | 0.34499 | 1.0156 | 3.5983 | 10.3183 | 13.172 | 0.30682 | 54.3747 | 4.7908 | 237.5 | 242.2908 | 384.6608 | 1
140 | 14 | 4 | 266 |  | 0.34499 | 1.0156 | 3.5983 | 10.3183 | 14.172 | 0.56862 | 48.5653 | 3.4483 | 221.6667 | 225.115 | 357.3925 | 1
140 | 15 | 11 | 226 |  | 0.34499 | 1.0156 | 3.5983 | 10.3183 | 15.172 | 0.83042 | 40.8298 | 7.8774 | 188.3333 | 196.2108 | 311.5042 | 1
140 | 16 | 3 | 184 |  | 0.34499 | 1.0156 | 3.5983 | 10.3183 | 16.172 | 1.0922 | 32.1197 | 1.5908 | 153.3333 | 154.9241 | 245.9576 | 1
140 | 17 | 0 | 130 |  | 0.34499 | 1.0156 | 3.5983 | 10.3183 | 17.172 | 1.354 | 23.0578 | 0 | 108.3333 | 108.3333 | 171.99 | 1
140 | 18 | 0 | 96 |  | 0.34499 | 1.0156 | 3.5983 | 10.3183 | 18.172 | 1.6158 | 14.0794 | 0 | 80 | 80 | 127.008 | 1
140 | 19 | 0 | 41 |  | 0.34499 | 1.0156 | 3.5983 | 10.3183 | 19.172 | 1.8776 | 5.5447 | 0 | 34.1667 | 34.1667 | 54.243 | 0
140 | 20 | 0 | 5 |  | 0.34499 | 1.0156 | 3.5983 | 10.3183 | 20.172 | 2.1394 | -2.1937 | 0 | 4.1667 | 4.1667 | 6.615 | 0
140 | 21 | 0 | 0 |  | 0.34499 | 1.0156 | 3.5983 | 10.3183 | 21.172 | 2.4012 | -8.7568 | 0 | 0 | 0 | 0 | 0
140 | 22 | 0 | 0 |  | 0.34499 | 1.0156 | 3.5983 | 10.3183 | 22.172 | 2.663 | -13.7391 | 0 | 0 | 0 | 0 | 0
140 | 23 | 0 | 0 |  | 0.34499 | 1.0156 | 3.5983 | 10.3183 | 23.172 | 2.9248 | -16.753 | 0 | 0 | 0 | 0 | 0
140 | 24 | 0 | 0 |  | 0.34499 | 1.0156 | 3.5983 | 10.3183 | 24.172 | 3.1866 | -17.519 | 0 | 0 | 0 | 0 | 0
141 | 1 | 0 | 0 |  | 0.34877 | 1.0329 | 3.5394 | 10.2594 | 1.171 | -2.835 | -15.749 | 0 | 0 | 0 | 0 | 0
141 | 2 | 0 | 0 |  | 0.34877 | 1.0329 | 3.5394 | 10.2594 | 2.171 | -2.5732 | -12.0293 | 0 | 0 | 0 | 0 | 0
141 | 3 | 0 | 0 |  | 0.34877 | 1.0329 | 3.5394 | 10.2594 | 3.171 | -2.3114 | -6.4696 | 0 | 0 | 0 | 0 | 0
141 | 4 | 0 | 0 |  | 0.34877 | 1.0329 | 3.5394 | 10.2594 | 4.171 | -2.0496 | 0.53057 | 0 | 0 | 0 | 0 | 0
141 | 5 | 0 | 15 |  | 0.34877 | 1.0329 | 3.5394 | 10.2594 | 5.171 | -1.7878 | 8.574 | 0 | 12.5 | 12.5 | 19.845 | 0
141 | 6 | 0 | 65 |  | 0.34877 | 1.0329 | 3.5394 | 10.2594 | 6.171 | -1.526 | 17.2939 | 0 | 54.1667 | 54.1667 | 85.995 | 1
141 | 7 | 0 | 93 |  | 0.34877 | 1.0329 | 3.5394 | 10.2594 | 7.171 | -1.2642 | 26.3416 | 0 | 77.5 | 77.5 | 123.039 | 1
141 | 8 | 89 | 196 |  | 0.34877 | 1.0329 | 3.5394 | 10.2594 | 8.171 | -1.0024 | 35.3419 | 53.2667 | 163.3333 | 216.6001 | 343.8743 | 1
141 | 9 | 78 | 277 |  | 0.34877 | 1.0329 | 3.5394 | 10.2594 | 9.171 | -0.74063 | 43.8113 | 60.1959 | 230.8333 | 291.0293 | 462.0381 | 1
141 | 10 | 85 | 334 |  | 0.34877 | 1.0329 | 3.5394 | 10.2594 | 10.171 | -0.47883 | 51.0287 | 76.6164 | 278.3333 | 354.9498 | 563.5183 | 1
141 | 11 | 60 | 397 |  | 0.34877 | 1.0329 | 3.5394 | 10.2594 | 11.171 | -0.21703 | 55.9116 | 58.713 | 330.8333 | 389.5463 | 618.4438 | 1
141 | 12 | 61 | 418 |  | 0.34877 | 1.0329 | 3.5394 | 10.2594 | 12.171 | 0.044765 | 57.2427 | 60.8795 | 348.3333 | 409.2128 | 649.6662 | 1
141 | 13 | 15 | 278 |  | 0.34877 | 1.0329 | 3.5394 | 10.2594 | 13.171 | 0.30656 | 54.585 | 14.377 | 231.6667 | 246.0436 | 390.6189 | 1
141 | 14 | 5 | 267 |  | 0.34877 | 1.0329 | 3.5394 | 10.2594 | 14.171 | 0.56836 | 48.7608 | 4.3128 | 222.5 | 226.8128 | 360.088 | 1
141 | 15 | 90 | 312 |  | 0.34877 | 1.0329 | 3.5394 | 10.2594 | 15.171 | 0.83016 | 41.0128 | 64.5179 | 260 | 324.5179 | 515.2046 | 1
141 | 16 | 309 | 262 |  | 0.34877 | 1.0329 | 3.5394 | 10.2594 | 16.171 | 1.092 | 32.2959 | 164.1693 | 218.3333 | 382.5026 | 607.2612 | 1
141 | 17 | 78 | 174 |  | 0.34877 | 1.0329 | 3.5394 | 10.2594 | 17.171 | 1.3538 | 23.2327 | 24.8424 | 145 | 169.8424 | 269.6418 | 1
141 | 18 | 216 | 134 |  | 0.34877 | 1.0329 | 3.5394 | 10.2594 | 18.171 | 1.6156 | 14.2574 | 20.0809 | 111.6667 | 131.7476 | 209.1624 | 1
141 | 19 | 0 | 42 |  | 0.34877 | 1.0329 | 3.5394 | 10.2594 | 19.171 | 1.8774 | 5.7293 | 0 | 35 | 35 | 55.566 | 0
141 | 20 | 0 | 5 |  | 0.34877 | 1.0329 | 3.5394 | 10.2594 | 20.171 | 2.1392 | -2.0001 | 0 | 4.1667 | 4.1667 | 6.615 | 0
141 | 21 | 0 | 0 |  | 0.34877 | 1.0329 | 3.5394 | 10.2594 | 21.171 | 2.401 | -8.5536 | 0 | 0 | 0 | 0 | 0
141 | 22 | 0 | 0 |  | 0.34877 | 1.0329 | 3.5394 | 10.2594 | 22.171 | 2.6628 | -13.5273 | 0 | 0 | 0 | 0 | 0
141 | 23 | 0 | 0 |  | 0.34877 | 1.0329 | 3.5394 | 10.2594 | 23.171 | 2.9246 | -16.5363 | 0 | 0 | 0 | 0 | 0
141 | 24 | 0 | 0 |  | 0.34877 | 1.0329 | 3.5394 | 10.2594 | 24.171 | 3.1864 | -17.3026 | 0 | 0 | 0 | 0 | 0
142 | 1 | 0 | 0 |  | 0.35246 | 1.0501 | 3.4718 | 10.1918 | 1.1699 | -2.8353 | -15.5448 | 0 | 0 | 0 | 0 | 0
142 | 2 | 0 | 0 |  | 0.35246 | 1.0501 | 3.4718 | 10.1918 | 2.1699 | -2.5735 | -11.8356 | 0 | 0 | 0 | 0 | 0
142 | 3 | 0 | 0 |  | 0.35246 | 1.0501 | 3.4718 | 10.1918 | 3.1699 | -2.3117 | -6.2883 | 0 | 0 | 0 | 0 | 0
142 | 4 | 0 | 0 |  | 0.35246 | 1.0501 | 3.4718 | 10.1918 | 4.1699 | -2.0499 | 0.6999 | 0 | 0 | 0 | 0 | 0
142 | 5 | 0 | 21 |  | 0.35246 | 1.0501 | 3.4718 | 10.1918 | 5.1699 | -1.7881 | 8.7335 | 0 | 17.5 | 17.5 | 27.783 | 0
142 | 6 | 144 | 87 |  | 0.35246 | 1.0501 | 3.4718 | 10.1918 | 6.1699 | -1.5263 | 17.4469 | 24.7105 | 72.5 | 97.2105 | 154.3315 | 1
142 | 7 | 365 | 133 |  | 0.35246 | 1.0501 | 3.4718 | 10.1918 | 7.1699 | -1.2645 | 26.4926 | 143.8805 | 110.8333 | 254.7138 | 404.3837 | 1
142 | 8 | 563 | 145 |  | 0.35246 | 1.0501 | 3.4718 | 10.1918 | 8.1699 | -1.0027 | 35.4963 | 337.2328 | 120.8333 | 458.0661 | 727.2258 | 1
142 | 9 | 687 | 148 |  | 0.35246 | 1.0501 | 3.4718 | 10.1918 | 9.1699 | -0.74093 | 43.976 | 530.3932 | 123.3333 | 653.7265 | 1037.8562 | 1
142 | 10 | 745 | 162 |  | 0.35246 | 1.0501 | 3.4718 | 10.1918 | 10.1699 | -0.47913 | 51.2106 | 671.6546 | 135 | 806.6546 | 1280.6449 | 1
142 | 11 | 811 | 146 |  | 0.35246 | 1.0501 | 3.4718 | 10.1918 | 11.1699 | -0.21733 | 56.1131 | 793.7167 | 121.6667 | 915.3834 | 1453.2627 | 1
142 | 12 | 827 | 149 |  | 0.35246 | 1.0501 | 3.4718 | 10.1918 | 12.1699 | 0.04447 | 57.4542 | 825.5138 | 124.1667 | 949.6805 | 1507.7127 | 1
142 | 13 | 820 | 150 |  | 0.35246 | 1.0501 | 3.4718 | 10.1918 | 13.1699 | 0.30627 | 54.7902 | 786.1847 | 125 | 911.1847 | 1446.5968 | 1
142 | 14 | 801 | 144 |  | 0.35246 | 1.0501 | 3.4718 | 10.1918 | 14.1699 | 0.56807 | 48.9519 | 691.3059 | 120 | 811.3059 | 1288.0293 | 1
142 | 15 | 754 | 140 |  | 0.35246 | 1.0501 | 3.4718 | 10.1918 | 15.1699 | 0.82987 | 41.192 | 541.0708 | 116.6667 | 657.7375 | 1044.2241 | 1
142 | 16 | 664 | 140 |  | 0.35246 | 1.0501 | 3.4718 | 10.1918 | 16.1699 | 1.0917 | 32.4687 | 353.4572 | 116.6667 | 470.1239 | 746.3687 | 1
142 | 17 | 499 | 145 |  | 0.35246 | 1.0501 | 3.4718 | 10.1918 | 17.1699 | 1.3535 | 23.4042 | 159.5923 | 120.8333 | 280.4256 | 445.2037 | 1
142 | 18 | 313 | 114 |  | 0.35246 | 1.0501 | 3.4718 | 10.1918 | 18.1699 | 1.6153 | 14.4321 | 29.6125 | 95 | 124.6125 | 197.8348 | 1
142 | 19 | 68 | 66 |  | 0.35246 | 1.0501 | 3.4718 | 10.1918 | 19.1699 | 1.8771 | 5.9103 | 0 | 55 | 55 | 87.318 | 0
142 | 20 | 0 | 10 |  | 0.35246 | 1.0501 | 3.4718 | 10.1918 | 20.1699 | 2.1389 | -1.8107 | 0 | 8.3333 | 8.3333 | 13.23 | 0
142 | 21 | 0 | 0 |  | 0.35246 | 1.0501 | 3.4718 | 10.1918 | 21.1699 | 2.4007 | -8.3549 | 0 | 0 | 0 | 0 | 0
142 | 22 | 0 | 0 |  | 0.35246 | 1.0501 | 3.4718 | 10.1918 | 22.1699 | 2.6625 | -13.3206 | 0 | 0 | 0 | 0 | 0
142 | 23 | 0 | 0 |  | 0.35246 | 1.0501 | 3.4718 | 10.1918 | 23.1699 | 2.9243 | -16.325 | 0 | 0 | 0 | 0 | 0
142 | 24 | 0 | 0 |  | 0.35246 | 1.0501 | 3.4718 | 10.1918 | 24.1699 | 3.1861 | -17.0921 | 0 | 0 | 0 | 0 | 0
143 | 1 | 0 | 0 |  | 0.35603 | 1.0673 | 3.3955 | 10.1155 | 1.1686 | -2.8357 | -15.3469 | 0 | 0 | 0 | 0 | 0
143 | 2 | 0 | 0 |  | 0.35603 | 1.0673 | 3.3955 | 10.1155 | 2.1686 | -2.5739 | -11.6482 | 0 | 0 | 0 | 0 | 0
143 | 3 | 0 | 0 |  | 0.35603 | 1.0673 | 3.3955 | 10.1155 | 3.1686 | -2.3121 | -6.1132 | 0 | 0 | 0 | 0 | 0
143 | 4 | 0 | 0 |  | 0.35603 | 1.0673 | 3.3955 | 10.1155 | 4.1686 | -2.0503 | 0.86314 | 0 | 0 | 0 | 0 | 0
143 | 5 | 0 | 16 |  | 0.35603 | 1.0673 | 3.3955 | 10.1155 | 5.1686 | -1.7885 | 8.8869 | 0 | 13.3333 | 13.3333 | 21.168 | 0
143 | 6 | 65 | 87 |  | 0.35603 | 1.0673 | 3.3955 | 10.1155 | 6.1686 | -1.5267 | 17.5939 | 11.2162 | 72.5 | 83.7162 | 132.9078 | 1
143 | 7 | 282 | 155 |  | 0.35603 | 1.0673 | 3.3955 | 10.1155 | 7.1686 | -1.2649 | 26.6375 | 111.3527 | 129.1667 | 240.5194 | 381.8485 | 1
143 | 8 | 514 | 165 |  | 0.35603 | 1.0673 | 3.3955 | 10.1155 | 8.1686 | -1.0031 | 35.6446 | 308.106 | 137.5 | 445.606 | 707.4441 | 1
143 | 9 | 662 | 157 |  | 0.35603 | 1.0673 | 3.3955 | 10.1155 | 9.1686 | -0.74126 | 44.1344 | 511.2608 | 130.8333 | 642.0942 | 1019.3887 | 1
143 | 10 | 715 | 176 |  | 0.35603 | 1.0673 | 3.3955 | 10.1155 | 10.1686 | -0.47946 | 51.386 | 644.7119 | 146.6667 | 791.3785 | 1256.3926 | 1
143 | 11 | 770 | 167 |  | 0.35603 | 1.0673 | 3.3955 | 10.1155 | 11.1686 | -0.21766 | 56.3082 | 753.678 | 139.1667 | 892.8447 | 1417.4802 | 1
143 | 12 | 781 | 173 |  | 0.35603 | 1.0673 | 3.3955 | 10.1155 | 12.1686 | 0.044137 | 57.6599 | 779.7235 | 144.1667 | 923.8902 | 1466.7681 | 1
143 | 13 | 780 | 171 |  | 0.35603 | 1.0673 | 3.3955 | 10.1155 | 13.1686 | 0.30594 | 54.9903 | 748.0595 | 142.5 | 890.5595 | 1413.8523 | 1
143 | 14 | 766 | 162 |  | 0.35603 | 1.0673 | 3.3955 | 10.1155 | 14.1686 | 0.56774 | 49.1387 | 661.4695 | 135 | 796.4695 | 1264.4749 | 1
143 | 15 | 750 | 142 |  | 0.35603 | 1.0673 | 3.3955 | 10.1155 | 15.1686 | 0.82954 | 41.3675 | 538.7505 | 118.3333 | 657.0839 | 1043.1863 | 1
143 | 16 | 659 | 143 |  | 0.35603 | 1.0673 | 3.3955 | 10.1155 | 16.1686 | 1.0913 | 32.638 | 351.4689 | 119.1667 | 470.6356 | 747.181 | 1
143 | 17 | 474 | 153 |  | 0.35603 | 1.0673 | 3.3955 | 10.1155 | 17.1686 | 1.3531 | 23.5724 | 152.2263 | 127.5 | 279.7263 | 444.0935 | 1
143 | 18 | 274 | 119 |  | 0.35603 | 1.0673 | 3.3955 | 10.1155 | 18.1686 | 1.6149 | 14.6032 | 26.3701 | 99.1667 | 125.5368 | 199.3022 | 1
143 | 19 | 21 | 63 |  | 0.35603 | 1.0673 | 3.3955 | 10.1155 | 19.1686 | 1.8767 | 6.0876 | 0 | 52.5 | 52.5 | 83.349 | 0
143 | 20 | 0 | 10 |  | 0.35603 | 1.0673 | 3.3955 | 10.1155 | 20.1686 | 2.1385 | -1.6253 | 0 | 8.3333 | 8.3333 | 13.23 | 0
143 | 21 | 0 | 0 |  | 0.35603 | 1.0673 | 3.3955 | 10.1155 | 21.1686 | 2.4003 | -8.1608 | 0 | 0 | 0 | 0 | 0
143 | 22 | 0 | 0 |  | 0.35603 | 1.0673 | 3.3955 | 10.1155 | 22.1686 | 2.6621 | -13.1191 | 0 | 0 | 0 | 0 | 0
143 | 23 | 0 | 0 |  | 0.35603 | 1.0673 | 3.3955 | 10.1155 | 23.1686 | 2.9239 | -16.1195 | 0 | 0 | 0 | 0 | 0
143 | 24 | 0 | 0 |  | 0.35603 | 1.0673 | 3.3955 | 10.1155 | 24.1686 | 3.1857 | -16.8876 | 0 | 0 | 0 | 0 | 0
144 | 1 | 0 | 0 |  | 0.35951 | 1.0845 | 3.3108 | 10.0308 | 1.1672 | -2.836 | -15.1552 | 0 | 0 | 0 | 0 | 0
144 | 2 | 0 | 0 |  | 0.35951 | 1.0845 | 3.3108 | 10.0308 | 2.1672 | -2.5742 | -11.4672 | 0 | 0 | 0 | 0 | 0
144 | 3 | 0 | 0 |  | 0.35951 | 1.0845 | 3.3108 | 10.0308 | 3.1672 | -2.3124 | -5.9443 | 0 | 0 | 0 | 0 | 0
144 | 4 | 0 | 0 |  | 0.35951 | 1.0845 | 3.3108 | 10.0308 | 4.1672 | -2.0506 | 1.0202 | 0 | 0 | 0 | 0 | 0
144 | 5 | 0 | 19 |  | 0.35951 | 1.0845 | 3.3108 | 10.0308 | 5.1672 | -1.7888 | 9.0344 | 0 | 15.8333 | 15.8333 | 25.137 | 0
144 | 6 | 0 | 69 |  | 0.35951 | 1.0845 | 3.3108 | 10.0308 | 6.1672 | -1.527 | 17.735 | 0 | 57.5 | 57.5 | 91.287 | 1
144 | 7 | 15 | 147 |  | 0.35951 | 1.0845 | 3.3108 | 10.0308 | 7.1672 | -1.2652 | 26.7764 | 5.9322 | 122.5 | 128.4322 | 203.899 | 1
144 | 8 | 30 | 229 |  | 0.35951 | 1.0845 | 3.3108 | 10.0308 | 8.1672 | -1.0034 | 35.7867 | 17.9943 | 190.8333 | 208.8276 | 331.5347 | 1
144 | 9 | 65 | 288 |  | 0.35951 | 1.0845 | 3.3108 | 10.0308 | 9.1672 | -0.74163 | 44.2864 | 50.213 | 240 | 290.213 | 460.7422 | 1
144 | 10 | 71 | 347 |  | 0.35951 | 1.0845 | 3.3108 | 10.0308 | 10.1672 | -0.47983 | 51.5549 | 64.0283 | 289.1667 | 353.1949 | 560.7323 | 1
144 | 11 | 15 | 269 |  | 0.35951 | 1.0845 | 3.3108 | 10.0308 | 11.1672 | -0.21803 | 56.4969 | 14.6834 | 224.1667 | 238.8501 | 379.1983 | 1
144 | 12 | 124 | 366 |  | 0.35951 | 1.0845 | 3.3108 | 10.0308 | 12.1672 | 0.043768 | 57.8597 | 123.8156 | 305 | 428.8156 | 680.7877 | 1
144 | 13 | 88 | 392 |  | 0.35951 | 1.0845 | 3.3108 | 10.0308 | 13.1672 | 0.30557 | 55.1853 | 84.4211 | 326.6667 | 411.0878 | 652.643 | 1
144 | 14 | 59 | 387 |  | 0.35951 | 1.0845 | 3.3108 | 10.0308 | 14.1672 | 0.56737 | 49.321 | 50.977 | 322.5 | 373.477 | 592.9321 | 1
144 | 15 | 84 | 319 |  | 0.35951 | 1.0845 | 3.3108 | 10.0308 | 15.1672 | 0.82917 | 41.539 | 60.4016 | 265.8333 | 326.2349 | 517.9305 | 1
144 | 16 | 74 | 258 |  | 0.35951 | 1.0845 | 3.3108 | 10.0308 | 16.1672 | 1.091 | 32.8037 | 39.5424 | 215 | 254.5424 | 404.1115 | 1
144 | 17 | 19 | 204 |  | 0.35951 | 1.0845 | 3.3108 | 10.0308 | 17.1672 | 1.3528 | 23.7371 | 6.127 | 170 | 176.127 | 279.6193 | 1
144 | 18 | 8 | 120 |  | 0.35951 | 1.0845 | 3.3108 | 10.0308 | 18.1672 | 1.6146 | 14.7708 | 0.78291 | 100 | 100.7829 | 160.003 | 1
144 | 19 | 0 | 46 |  | 0.35951 | 1.0845 | 3.3108 | 10.0308 | 19.1672 | 1.8764 | 6.261 | 0 | 38.3333 | 38.3333 | 60.858 | 0
144 | 20 | 0 | 6 |  | 0.35951 | 1.0845 | 3.3108 | 10.0308 | 20.1672 | 2.1382 | -1.4441 | 0 | 5 | 5 | 7.938 | 0
144 | 21 | 0 | 0 |  | 0.35951 | 1.0845 | 3.3108 | 10.0308 | 21.1672 | 2.4 | -7.9714 | 0 | 0 | 0 | 0 | 0
144 | 22 | 0 | 0 |  | 0.35951 | 1.0845 | 3.3108 | 10.0308 | 22.1672 | 2.6618 | -12.9227 | 0 | 0 | 0 | 0 | 0
144 | 23 | 0 | 0 |  | 0.35951 | 1.0845 | 3.3108 | 10.0308 | 23.1672 | 2.9236 | -15.9196 | 0 | 0 | 0 | 0 | 0
144 | 24 | 0 | 0 |  | 0.35951 | 1.0845 | 3.3108 | 10.0308 | 24.1672 | 3.1854 | -16.6892 | 0 | 0 | 0 | 0 | 0
145 | 1 | 0 | 0 |  | 0.36287 | 1.1017 | 3.2179 | 9.9379 | 1.1656 | -2.8364 | -14.9699 | 0 | 0 | 0 | 0 | 0
145 | 2 | 0 | 0 |  | 0.36287 | 1.1017 | 3.2179 | 9.9379 | 2.1656 | -2.5746 | -11.2924 | 0 | 0 | 0 | 0 | 0
145 | 3 | 0 | 0 |  | 0.36287 | 1.1017 | 3.2179 | 9.9379 | 3.1656 | -2.3128 | -5.7818 | 0 | 0 | 0 | 0 | 0
145 | 4 | 0 | 0 |  | 0.36287 | 1.1017 | 3.2179 | 9.9379 | 4.1656 | -2.051 | 1.1712 | 0 | 0 | 0 | 0 | 0
145 | 5 | 0 | 8 |  | 0.36287 | 1.1017 | 3.2179 | 9.9379 | 5.1656 | -1.7892 | 9.1758 | 0 | 6.6667 | 6.6667 | 10.584 | 0
145 | 6 | 0 | 44 |  | 0.36287 | 1.1017 | 3.2179 | 9.9379 | 6.1656 | -1.5274 | 17.87 | 0 | 36.6667 | 36.6667 | 58.212 | 1
145 | 7 | 0 | 96 |  | 0.36287 | 1.1017 | 3.2179 | 9.9379 | 7.1656 | -1.2656 | 26.9092 | 0 | 80 | 80 | 127.008 | 1
145 | 8 | 0 | 154 |  | 0.36287 | 1.1017 | 3.2179 | 9.9379 | 8.1656 | -1.0038 | 35.9227 | 0 | 128.3333 | 128.3333 | 203.742 | 1
145 | 9 | 9 | 202 |  | 0.36287 | 1.1017 | 3.2179 | 9.9379 | 9.1656 | -0.74204 | 44.4321 | 6.9541 | 168.3333 | 175.2874 | 278.2863 | 1
145 | 10 | 13 | 242 |  | 0.36287 | 1.1017 | 3.2179 | 9.9379 | 10.1656 | -0.48024 | 51.7173 | 11.7245 | 201.6667 | 213.3912 | 338.7798 | 1
145 | 11 | 103 | 366 |  | 0.36287 | 1.1017 | 3.2179 | 9.9379 | 11.1656 | -0.21844 | 56.679 | 100.8328 | 305 | 405.8328 | 644.3002 | 1
145 | 12 | 61 | 421 |  | 0.36287 | 1.1017 | 3.2179 | 9.9379 | 12.1656 | 0.043362 | 58.0534 | 60.9174 | 350.8333 | 411.7507 | 653.6955 | 1
145 | 13 | 61 | 417 |  | 0.36287 | 1.1017 | 3.2179 | 9.9379 | 13.1656 | 0.30516 | 55.375 | 58.5358 | 347.5 | 406.0358 | 644.6225 | 1
145 | 14 | 60 | 389 |  | 0.36287 | 1.1017 | 3.2179 | 9.9379 | 14.1656 | 0.56696 | 49.4989 | 51.8696 | 324.1667 | 376.0363 | 596.9952 | 1
145 | 15 | 84 | 320 |  | 0.36287 | 1.1017 | 3.2179 | 9.9379 | 15.1656 | 0.82876 | 41.7066 | 60.4629 | 266.6667 | 327.1296 | 519.3509 | 1
145 | 16 | 75 | 259 |  | 0.36287 | 1.1017 | 3.2179 | 9.9379 | 16.1656 | 1.0906 | 32.9657 | 40.1531 | 215.8333 | 255.9864 | 406.404 | 1
145 | 17 | 19 | 206 |  | 0.36287 | 1.1017 | 3.2179 | 9.9379 | 17.1656 | 1.3524 | 23.8982 | 6.1521 | 171.6667 | 177.8188 | 282.3051 | 1
145 | 18 | 8 | 121 |  | 0.36287 | 1.1017 | 3.2179 | 9.9379 | 18.1656 | 1.6142 | 14.9348 | 0.79581 | 100.8333 | 101.6291 | 161.3464 | 1
145 | 19 | 0 | 47 |  | 0.36287 | 1.1017 | 3.2179 | 9.9379 | 19.1656 | 1.876 | 6.4306 | 0 | 39.1667 | 39.1667 | 62.181 | 0
145 | 20 | 0 | 7 |  | 0.36287 | 1.1017 | 3.2179 | 9.9379 | 20.1656 | 2.1378 | -1.2673 | 0 | 5.8333 | 5.8333 | 9.261 | 0
145 | 21 | 0 | 0 |  | 0.36287 | 1.1017 | 3.2179 | 9.9379 | 21.1656 | 2.3996 | -7.7868 | 0 | 0 | 0 | 0 | 0
145 | 22 | 0 | 0 |  | 0.36287 | 1.1017 | 3.2179 | 9.9379 | 22.1656 | 2.6614 | -12.7317 | 0 | 0 | 0 | 0 | 0
145 | 23 | 0 | 0 |  | 0.36287 | 1.1017 | 3.2179 | 9.9379 | 23.1656 | 2.9232 | -15.7255 | 0 | 0 | 0 | 0 | 0
145 | 24 | 0 | 0 |  | 0.36287 | 1.1017 | 3.2179 | 9.9379 | 24.1656 | 3.185 | -16.497 | 0 | 0 | 0 | 0 | 0
146 | 1 | 0 | 0 |  | 0.36613 | 1.1189 | 3.1169 | 9.8369 | 1.1639 | -2.8369 | -14.791 | 0 | 0 | 0 | 0 | 0
146 | 2 | 0 | 0 |  | 0.36613 | 1.1189 | 3.1169 | 9.8369 | 2.1639 | -2.5751 | -11.1242 | 0 | 0 | 0 | 0 | 0
146 | 3 | 0 | 0 |  | 0.36613 | 1.1189 | 3.1169 | 9.8369 | 3.1639 | -2.3133 | -5.6256 | 0 | 0 | 0 | 0 | 0
146 | 4 | 0 | 0 |  | 0.36613 | 1.1189 | 3.1169 | 9.8369 | 4.1639 | -2.0515 | 1.3159 | 0 | 0 | 0 | 0 | 0
146 | 5 | 0 | 9 |  | 0.36613 | 1.1189 | 3.1169 | 9.8369 | 5.1639 | -1.7897 | 9.311 | 0 | 7.5 | 7.5 | 11.907 | 0
146 | 6 | 0 | 44 |  | 0.36613 | 1.1189 | 3.1169 | 9.8369 | 6.1639 | -1.5279 | 17.9989 | 0 | 36.6667 | 36.6667 | 58.212 | 1
146 | 7 | 112 | 156 |  | 0.36613 | 1.1189 | 3.1169 | 9.8369 | 7.1639 | -1.2661 | 27.0359 | 44.4103 | 130 | 174.4103 | 276.8937 | 1
146 | 8 | 12 | 241 |  | 0.36613 | 1.1189 | 3.1169 | 9.8369 | 8.1639 | -1.0043 | 36.0524 | 7.205 | 200.8333 | 208.0383 | 330.2817 | 1
146 | 9 | 79 | 282 |  | 0.36613 | 1.1189 | 3.1169 | 9.8369 | 9.1639 | -0.74248 | 44.5713 | 61.0515 | 235 | 296.0515 | 470.0114 | 1
146 | 10 | 86 | 339 |  | 0.36613 | 1.1189 | 3.1169 | 9.8369 | 10.1639 | -0.48068 | 51.873 | 77.5663 | 282.5 | 360.0663 | 571.6412 | 1
146 | 11 | 251 | 375 |  | 0.36613 | 1.1189 | 3.1169 | 9.8369 | 11.1639 | -0.21888 | 56.8546 | 245.7301 | 312.5 | 558.2301 | 886.2461 | 1
146 | 12 | 93 | 394 |  | 0.36613 | 1.1189 | 3.1169 | 9.8369 | 12.1639 | 0.042922 | 58.241 | 92.8852 | 328.3333 | 421.2185 | 668.7265 | 1
146 | 13 | 15 | 281 |  | 0.36613 | 1.1189 | 3.1169 | 9.8369 | 13.1639 | 0.30472 | 55.5593 | 14.398 | 234.1667 | 248.5647 | 394.6213 | 1
146 | 14 | 5 | 270 |  | 0.36613 | 1.1189 | 3.1169 | 9.8369 | 14.1639 | 0.56652 | 49.6722 | 4.3248 | 225 | 229.3248 | 364.0761 | 1
146 | 15 | 12 | 230 |  | 0.36613 | 1.1189 | 3.1169 | 9.8369 | 15.1639 | 0.82832 | 41.8702 | 8.6463 | 191.6667 | 200.313 | 318.0169 | 1
146 | 16 | 6 | 187 |  | 0.36613 | 1.1189 | 3.1169 | 9.8369 | 16.1639 | 1.0901 | 33.1241 | 3.2183 | 155.8333 | 159.0517 | 252.5104 | 1
146 | 17 | 0 | 135 |  | 0.36613 | 1.1189 | 3.1169 | 9.8369 | 17.1639 | 1.3519 | 24.0557 | 0 | 112.5 | 112.5 | 178.605 | 1
146 | 18 | 0 | 78 |  | 0.36613 | 1.1189 | 3.1169 | 9.8369 | 18.1639 | 1.6137 | 15.095 | 0 | 65 | 65 | 103.194 | 1
146 | 19 | 0 | 30 |  | 0.36613 | 1.1189 | 3.1169 | 9.8369 | 19.1639 | 1.8755 | 6.5961 | 0 | 25 | 25 | 39.69 | 0
146 | 20 | 0 | 4 |  | 0.36613 | 1.1189 | 3.1169 | 9.8369 | 20.1639 | 2.1373 | -1.0948 | 0 | 3.3333 | 3.3333 | 5.292 | 0
146 | 21 | 0 | 0 |  | 0.36613 | 1.1189 | 3.1169 | 9.8369 | 21.1639 | 2.3991 | -7.607 | 0 | 0 | 0 | 0 | 0
146 | 22 | 0 | 0 |  | 0.36613 | 1.1189 | 3.1169 | 9.8369 | 22.1639 | 2.6609 | -12.5461 | 0 | 0 | 0 | 0 | 0
146 | 23 | 0 | 0 |  | 0.36613 | 1.1189 | 3.1169 | 9.8369 | 23.1639 | 2.9227 | -15.5374 | 0 | 0 | 0 | 0 | 0
146 | 24 | 0 | 0 |  | 0.36613 | 1.1189 | 3.1169 | 9.8369 | 24.1639 | 3.1845 | -16.311 | 0 | 0 | 0 | 0 | 0
147 | 1 | 0 | 0 |  | 0.36928 | 1.1361 | 3.0082 | 9.7282 | 1.1621 | -2.8373 | -14.6186 | 0 | 0 | 0 | 0 | 0
147 | 2 | 0 | 0 |  | 0.36928 | 1.1361 | 3.0082 | 9.7282 | 2.1621 | -2.5755 | -10.9624 | 0 | 0 | 0 | 0 | 0
147 | 3 | 0 | 0 |  | 0.36928 | 1.1361 | 3.0082 | 9.7282 | 3.1621 | -2.3137 | -5.4757 | 0 | 0 | 0 | 0 | 0
147 | 4 | 0 | 0 |  | 0.36928 | 1.1361 | 3.0082 | 9.7282 | 4.1621 | -2.0519 | 1.4543 | 0 | 0 | 0 | 0 | 0
147 | 5 | 0 | 9 |  | 0.36928 | 1.1361 | 3.0082 | 9.7282 | 5.1621 | -1.7901 | 9.4401 | 0 | 7.5 | 7.5 | 11.907 | 0
147 | 6 | 0 | 45 |  | 0.36928 | 1.1361 | 3.0082 | 9.7282 | 6.1621 | -1.5283 | 18.1218 | 0 | 37.5 | 37.5 | 59.535 | 1
147 | 7 | 0 | 98 |  | 0.36928 | 1.1361 | 3.0082 | 9.7282 | 7.1621 | -1.2665 | 27.1566 | 0 | 81.6667 | 81.6667 | 129.654 | 1
147 | 8 | 0 | 155 |  | 0.36928 | 1.1361 | 3.0082 | 9.7282 | 8.1621 | -1.0048 | 36.176 | 0 | 129.1667 | 129.1667 | 205.065 | 1
147 | 9 | 9 | 203 |  | 0.36928 | 1.1361 | 3.0082 | 9.7282 | 9.1621 | -0.74295 | 44.7041 | 6.956 | 169.1667 | 176.1227 | 279.6124 | 1
147 | 10 | 13 | 243 |  | 0.36928 | 1.1361 | 3.0082 | 9.7282 | 10.1621 | -0.48115 | 52.0221 | 11.7254 | 202.5 | 214.2254 | 340.1042 | 1
147 | 11 | 5 | 279 |  | 0.36928 | 1.1361 | 3.0082 | 9.7282 | 11.1621 | -0.21935 | 57.0235 | 4.8951 | 232.5 | 237.3951 | 376.8885 | 1
147 | 12 | 5 | 293 |  | 0.36928 | 1.1361 | 3.0082 | 9.7282 | 12.1621 | 0.042447 | 58.4225 | 4.9944 | 244.1667 | 249.161 | 395.568 | 1
147 | 13 | 5 | 290 |  | 0.36928 | 1.1361 | 3.0082 | 9.7282 | 13.1621 | 0.30425 | 55.7383 | 4.8006 | 241.6667 | 246.4673 | 391.2915 | 1
147 | 14 | 5 | 271 |  | 0.36928 | 1.1361 | 3.0082 | 9.7282 | 14.1621 | 0.56605 | 49.8408 | 4.3272 | 225.8333 | 230.1605 | 365.4028 | 1
147 | 15 | 12 | 231 |  | 0.36928 | 1.1361 | 3.0082 | 9.7282 | 15.1621 | 0.82785 | 42.0297 | 8.655 | 192.5 | 201.155 | 319.3537 | 1
147 | 16 | 7 | 188 |  | 0.36928 | 1.1361 | 3.0082 | 9.7282 | 16.1621 | 1.0896 | 33.2786 | 3.7618 | 156.6667 | 160.4285 | 254.6963 | 1
147 | 17 | 0 | 137 |  | 0.36928 | 1.1361 | 3.0082 | 9.7282 | 17.1621 | 1.3514 | 24.2095 | 0 | 114.1667 | 114.1667 | 181.251 | 1
147 | 18 | 0 | 79 |  | 0.36928 | 1.1361 | 3.0082 | 9.7282 | 18.1621 | 1.6132 | 15.2513 | 0 | 65.8333 | 65.8333 | 104.517 | 1
147 | 19 | 0 | 31 |  | 0.36928 | 1.1361 | 3.0082 | 9.7282 | 19.1621 | 1.875 | 6.7575 | 0 | 25.8333 | 25.8333 | 41.013 | 0
147 | 20 | 0 | 7 |  | 0.36928 | 1.1361 | 3.0082 | 9.7282 | 20.1621 | 2.1368 | -0.92683 | 0 | 5.8333 | 5.8333 | 9.261 | 0
147 | 21 | 0 | 0 |  | 0.36928 | 1.1361 | 3.0082 | 9.7282 | 21.1621 | 2.3986 | -7.4323 | 0 | 0 | 0 | 0 | 0
147 | 22 | 0 | 0 |  | 0.36928 | 1.1361 | 3.0082 | 9.7282 | 22.1621 | 2.6604 | -12.366 | 0 | 0 | 0 | 0 | 0
147 | 23 | 0 | 0 |  | 0.36928 | 1.1361 | 3.0082 | 9.7282 | 23.1621 | 2.9222 | -15.3552 | 0 | 0 | 0 | 0 | 0
147 | 24 | 0 | 0 |  | 0.36928 | 1.1361 | 3.0082 | 9.7282 | 24.1621 | 3.184 | -16.1314 | 0 | 0 | 0 | 0 | 0
148 | 1 | 0 | 0 |  | 0.37232 | 1.1534 | 2.8918 | 9.6118 | 1.1602 | -2.8379 | -14.4527 | 0 | 0 | 0 | 0 | 0
148 | 2 | 0 | 0 |  | 0.37232 | 1.1534 | 2.8918 | 9.6118 | 2.1602 | -2.5761 | -10.8071 | 0 | 0 | 0 | 0 | 0
148 | 3 | 0 | 0 |  | 0.37232 | 1.1534 | 2.8918 | 9.6118 | 3.1602 | -2.3143 | -5.3323 | 0 | 0 | 0 | 0 | 0
148 | 4 | 0 | 0 |  | 0.37232 | 1.1534 | 2.8918 | 9.6118 | 4.1602 | -2.0525 | 1.5865 | 0 | 0 | 0 | 0 | 0
148 | 5 | 0 | 9 |  | 0.37232 | 1.1534 | 2.8918 | 9.6118 | 5.1602 | -1.7907 | 9.5631 | 0 | 7.5 | 7.5 | 11.907 | 0
148 | 6 | 0 | 73 |  | 0.37232 | 1.1534 | 2.8918 | 9.6118 | 6.1602 | -1.5289 | 18.2386 | 0 | 60.8333 | 60.8333 | 96.579 | 1
148 | 7 | 7 | 155 |  | 0.37232 | 1.1534 | 2.8918 | 9.6118 | 7.1602 | -1.2671 | 27.2711 | 2.7812 | 129.1667 | 131.9479 | 209.4805 | 1
148 | 8 | 23 | 238 |  | 0.37232 | 1.1534 | 2.8918 | 9.6118 | 8.1602 | -1.0053 | 36.2933 | 13.8189 | 198.3333 | 212.1523 | 336.813 | 1
148 | 9 | 3 | 208 |  | 0.37232 | 1.1534 | 2.8918 | 9.6118 | 9.1602 | -0.74346 | 44.8305 | 2.3188 | 173.3333 | 175.6522 | 278.8654 | 1
148 | 10 | 13 | 244 |  | 0.37232 | 1.1534 | 2.8918 | 9.6118 | 10.1602 | -0.48166 | 52.1645 | 11.7252 | 203.3333 | 215.0586 | 341.427 | 1
148 | 11 | 5 | 281 |  | 0.37232 | 1.1534 | 2.8918 | 9.6118 | 11.1602 | -0.21986 | 57.1857 | 4.8952 | 234.1667 | 239.0618 | 379.5346 | 1
148 | 12 | 106 | 387 |  | 0.37232 | 1.1534 | 2.8918 | 9.6118 | 12.1602 | 0.041939 | 58.5976 | 105.8906 | 322.5 | 428.3906 | 680.1129 | 1
148 | 13 | 62 | 421 |  | 0.37232 | 1.1534 | 2.8918 | 9.6118 | 13.1602 | 0.30374 | 55.9117 | 59.5437 | 350.8333 | 410.377 | 651.5145 | 1
148 | 14 | 15 | 265 |  | 0.37232 | 1.1534 | 2.8918 | 9.6118 | 14.1602 | 0.56554 | 50.0047 | 12.9886 | 220.8333 | 233.8219 | 371.2157 | 1
148 | 15 | 12 | 233 |  | 0.37232 | 1.1534 | 2.8918 | 9.6118 | 15.1602 | 0.82734 | 42.185 | 8.6638 | 194.1667 | 202.8304 | 322.0136 | 1
148 | 16 | 7 | 189 |  | 0.37232 | 1.1534 | 2.8918 | 9.6118 | 16.1602 | 1.0891 | 33.4293 | 3.7689 | 157.5 | 161.2689 | 256.0305 | 1
148 | 17 | 0 | 138 |  | 0.37232 | 1.1534 | 2.8918 | 9.6118 | 17.1602 | 1.3509 | 24.3595 | 0 | 115 | 115 | 182.574 | 1
148 | 18 | 11 | 124 |  | 0.37232 | 1.1534 | 2.8918 | 9.6118 | 18.1602 | 1.6127 | 15.4038 | 1.1465 | 103.3333 | 104.4799 | 165.8723 | 1
148 | 19 | 0 | 50 |  | 0.37232 | 1.1534 | 2.8918 | 9.6118 | 19.1602 | 1.8745 | 6.9148 | 0 | 41.6667 | 41.6667 | 66.15 | 0
148 | 20 | 0 | 12 |  | 0.37232 | 1.1534 | 2.8918 | 9.6118 | 20.1602 | 2.1363 | -0.76344 | 0 | 10 | 10 | 15.876 | 0
148 | 21 | 0 | 0 |  | 0.37232 | 1.1534 | 2.8918 | 9.6118 | 21.1602 | 2.3981 | -7.2626 | 0 | 0 | 0 | 0 | 0
148 | 22 | 0 | 0 |  | 0.37232 | 1.1534 | 2.8918 | 9.6118 | 22.1602 | 2.6599 | -12.1916 | 0 | 0 | 0 | 0 | 0
148 | 23 | 0 | 0 |  | 0.37232 | 1.1534 | 2.8918 | 9.6118 | 23.1602 | 2.9217 | -15.1791 | 0 | 0 | 0 | 0 | 0
148 | 24 | 0 | 0 |  | 0.37232 | 1.1534 | 2.8918 | 9.6118 | 24.1602 | 3.1835 | -15.9581 | 0 | 0 | 0 | 0 | 0
149 | 1 | 0 | 0 |  | 0.37524 | 1.1706 | 2.7681 | 9.4881 | 1.1581 | -2.8384 | -14.2935 | 0 | 0 | 0 | 0 | 0
149 | 2 | 0 | 0 |  | 0.37524 | 1.1706 | 2.7681 | 9.4881 | 2.1581 | -2.5766 | -10.6585 | 0 | 0 | 0 | 0 | 0
149 | 3 | 0 | 0 |  | 0.37524 | 1.1706 | 2.7681 | 9.4881 | 3.1581 | -2.3148 | -5.1954 | 0 | 0 | 0 | 0 | 0
149 | 4 | 0 | 1 |  | 0.37524 | 1.1706 | 2.7681 | 9.4881 | 4.1581 | -2.053 | 1.7124 | 0 | 0.83333 | 0.83333 | 1.323 | 0
149 | 5 | 0 | 28 |  | 0.37524 | 1.1706 | 2.7681 | 9.4881 | 5.1581 | -1.7912 | 9.6799 | 0 | 23.3333 | 23.3333 | 37.044 | 0
149 | 6 | 179 | 89 |  | 0.37524 | 1.1706 | 2.7681 | 9.4881 | 6.1581 | -1.5294 | 18.3493 | 31.6555 | 74.1667 | 105.8222 | 168.0033 | 1
149 | 7 | 375 | 137 |  | 0.37524 | 1.1706 | 2.7681 | 9.4881 | 7.1581 | -1.2676 | 27.3796 | 149.1129 | 114.1667 | 263.2795 | 417.9826 | 1
149 | 8 | 562 | 150 |  | 0.37524 | 1.1706 | 2.7681 | 9.4881 | 8.1581 | -1.0058 | 36.4044 | 337.7364 | 125 | 462.7364 | 734.6403 | 1
149 | 9 | 633 | 165 |  | 0.37524 | 1.1706 | 2.7681 | 9.4881 | 9.1581 | -0.744 | 44.9504 | 489.2779 | 137.5 | 626.7779 | 995.0727 | 1
149 | 10 | 363 | 333 |  | 0.37524 | 1.1706 | 2.7681 | 9.4881 | 10.1581 | -0.4822 | 52.3002 | 327.3906 | 277.5 | 604.8906 | 960.3244 | 1
149 | 11 | 648 | 253 |  | 0.37524 | 1.1706 | 2.7681 | 9.4881 | 11.1581 | -0.2204 | 57.3412 | 634.406 | 210.8333 | 845.2393 | 1341.9019 | 1
149 | 12 | 720 | 210 |  | 0.37524 | 1.1706 | 2.7681 | 9.4881 | 12.1581 | 0.0414 | 58.7664 | 719.3177 | 175 | 894.3177 | 1419.8187 | 1
149 | 13 | 417 | 350 |  | 0.37524 | 1.1706 | 2.7681 | 9.4881 | 13.1581 | 0.3032 | 56.0796 | 400.5826 | 291.6667 | 692.2493 | 1099.015 | 1
149 | 14 | 528 | 297 |  | 0.37524 | 1.1706 | 2.7681 | 9.4881 | 14.1581 | 0.565 | 50.1639 | 457.4446 | 247.5 | 704.9446 | 1119.17 | 1
149 | 15 | 570 | 217 |  | 0.37524 | 1.1706 | 2.7681 | 9.4881 | 15.1581 | 0.8268 | 42.3361 | 411.941 | 180.8333 | 592.7744 | 941.0886 | 1
149 | 16 | 225 | 260 |  | 0.37524 | 1.1706 | 2.7681 | 9.4881 | 16.1581 | 1.0886 | 33.5761 | 121.3682 | 216.6667 | 338.0349 | 536.6641 | 1
149 | 17 | 39 | 202 |  | 0.37524 | 1.1706 | 2.7681 | 9.4881 | 17.1581 | 1.3504 | 24.5056 | 12.8308 | 168.3333 | 181.1641 | 287.6162 | 1
149 | 18 | 10 | 126 |  | 0.37524 | 1.1706 | 2.7681 | 9.4881 | 18.1581 | 1.6122 | 15.5522 | 1.0579 | 105 | 106.0579 | 168.3775 | 1
149 | 19 | 0 | 51 |  | 0.37524 | 1.1706 | 2.7681 | 9.4881 | 19.1581 | 1.874 | 7.0677 | 0 | 42.5 | 42.5 | 67.473 | 0
149 | 20 | 0 | 5 |  | 0.37524 | 1.1706 | 2.7681 | 9.4881 | 20.1581 | 2.1358 | -0.60473 | 0 | 4.1667 | 4.1667 | 6.615 | 0
149 | 21 | 0 | 0 |  | 0.37524 | 1.1706 | 2.7681 | 9.4881 | 21.1581 | 2.3976 | -7.0981 | 0 | 0 | 0 | 0 | 0
149 | 22 | 0 | 0 |  | 0.37524 | 1.1706 | 2.7681 | 9.4881 | 22.1581 | 2.6594 | -12.0228 | 0 | 0 | 0 | 0 | 0
149 | 23 | 0 | 0 |  | 0.37524 | 1.1706 | 2.7681 | 9.4881 | 23.1581 | 2.9212 | -15.0091 | 0 | 0 | 0 | 0 | 0
149 | 24 | 0 | 0 |  | 0.37524 | 1.1706 | 2.7681 | 9.4881 | 24.1581 | 3.183 | -15.7913 | 0 | 0 | 0 | 0 | 0
150 | 1 | 0 | 0 |  | 0.37806 | 1.1878 | 2.6373 | 9.3573 | 1.156 | -2.839 | -14.1409 | 0 | 0 | 0 | 0 | 0
150 | 2 | 0 | 0 |  | 0.37806 | 1.1878 | 2.6373 | 9.3573 | 2.156 | -2.5772 | -10.5164 | 0 | 0 | 0 | 0 | 0
150 | 3 | 0 | 0 |  | 0.37806 | 1.1878 | 2.6373 | 9.3573 | 3.156 | -2.3154 | -5.065 | 0 | 0 | 0 | 0 | 0
150 | 4 | 0 | 1 |  | 0.37806 | 1.1878 | 2.6373 | 9.3573 | 4.156 | -2.0536 | 1.8319 | 0 | 0.83333 | 0.83333 | 1.323 | 0
150 | 5 | 0 | 24 |  | 0.37806 | 1.1878 | 2.6373 | 9.3573 | 5.156 | -1.7918 | 9.7905 | 0 | 20 | 20 | 31.752 | 0
150 | 6 | 79 | 92 |  | 0.37806 | 1.1878 | 2.6373 | 9.3573 | 6.156 | -1.53 | 18.4539 | 14.0088 | 76.6667 | 90.6754 | 143.9563 | 1
150 | 7 | 71 | 176 |  | 0.37806 | 1.1878 | 2.6373 | 9.3573 | 7.156 | -1.2682 | 27.4819 | 28.2502 | 146.6667 | 174.9169 | 277.698 | 1
150 | 8 | 149 | 243 |  | 0.37806 | 1.1878 | 2.6373 | 9.3573 | 8.156 | -1.0064 | 36.5092 | 89.5547 | 202.5 | 292.0547 | 463.666 | 1
150 | 9 | 215 | 291 |  | 0.37806 | 1.1878 | 2.6373 | 9.3573 | 9.156 | -0.74457 | 45.0639 | 166.179 | 242.5 | 408.679 | 648.8187 | 1
150 | 10 | 235 | 346 |  | 0.37806 | 1.1878 | 2.6373 | 9.3573 | 10.156 | -0.48277 | 52.4292 | 211.932 | 288.3333 | 500.2653 | 794.2212 | 1
150 | 11 | 165 | 450 |  | 0.37806 | 1.1878 | 2.6373 | 9.3573 | 11.156 | -0.22097 | 57.4898 | 161.5336 | 375 | 536.5336 | 851.8007 | 1
150 | 12 | 95 | 398 |  | 0.37806 | 1.1878 | 2.6373 | 9.3573 | 12.156 | 0.040829 | 58.9288 | 94.9171 | 331.6667 | 426.5838 | 677.2444 | 1
150 | 13 | 255 | 392 |  | 0.37806 | 1.1878 | 2.6373 | 9.3573 | 13.156 | 0.30263 | 56.2419 | 245.0227 | 326.6667 | 571.6894 | 907.614 | 1
150 | 14 | 93 | 368 |  | 0.37806 | 1.1878 | 2.6373 | 9.3573 | 14.156 | 0.56443 | 50.3181 | 80.6158 | 306.6667 | 387.2825 | 614.8496 | 1
150 | 15 | 85 | 325 |  | 0.37806 | 1.1878 | 2.6373 | 9.3573 | 15.156 | 0.82623 | 42.4829 | 61.4912 | 270.8333 | 332.3245 | 527.5984 | 1
150 | 16 | 190 | 282 |  | 0.37806 | 1.1878 | 2.6373 | 9.3573 | 16.156 | 1.088 | 33.7188 | 102.6786 | 235 | 337.6786 | 536.0985 | 1
150 | 17 | 39 | 203 |  | 0.37806 | 1.1878 | 2.6373 | 9.3573 | 17.156 | 1.3498 | 24.6477 | 12.8806 | 169.1667 | 182.0473 | 289.0183 | 1
150 | 18 | 79 | 141 |  | 0.37806 | 1.1878 | 2.6373 | 9.3573 | 18.156 | 1.6116 | 15.6966 | 8.4785 | 117.5 | 125.9785 | 200.0035 | 1
150 | 19 | 40 | 70 |  | 0.37806 | 1.1878 | 2.6373 | 9.3573 | 19.156 | 1.8734 | 7.2163 | 0 | 58.3333 | 58.3333 | 92.61 | 0
150 | 20 | 0 | 11 |  | 0.37806 | 1.1878 | 2.6373 | 9.3573 | 20.156 | 2.1352 | -0.45078 | 0 | 9.1667 | 9.1667 | 14.553 | 0
150 | 21 | 0 | 0 |  | 0.37806 | 1.1878 | 2.6373 | 9.3573 | 21.156 | 2.397 | -6.9389 | 0 | 0 | 0 | 0 | 0
150 | 22 | 0 | 0 |  | 0.37806 | 1.1878 | 2.6373 | 9.3573 | 22.156 | 2.6588 | -11.8597 | 0 | 0 | 0 | 0 | 0
150 | 23 | 0 | 0 |  | 0.37806 | 1.1878 | 2.6373 | 9.3573 | 23.156 | 2.9206 | -14.8454 | 0 | 0 | 0 | 0 | 0
150 | 24 | 0 | 0 |  | 0.37806 | 1.1878 | 2.6373 | 9.3573 | 24.156 | 3.1824 | -15.6311 | 0 | 0 | 0 | 0 | 0
151 | 1 | 0 | 0 |  | 0.38075 | 1.205 | 2.4996 | 9.2196 | 1.1537 | -2.8396 | -13.995 | 0 | 0 | 0 | 0 | 0
151 | 2 | 0 | 0 |  | 0.38075 | 1.205 | 2.4996 | 9.2196 | 2.1537 | -2.5778 | -10.3811 | 0 | 0 | 0 | 0 | 0
151 | 3 | 0 | 0 |  | 0.38075 | 1.205 | 2.4996 | 9.2196 | 3.1537 | -2.316 | -4.9411 | 0 | 0 | 0 | 0 | 0
151 | 4 | 0 | 1 |  | 0.38075 | 1.205 | 2.4996 | 9.2196 | 4.1537 | -2.0542 | 1.9451 | 0 | 0.83333 | 0.83333 | 1.323 | 0
151 | 5 | 0 | 29 |  | 0.38075 | 1.205 | 2.4996 | 9.2196 | 5.1537 | -1.7924 | 9.8949 | 0 | 24.1667 | 24.1667 | 38.367 | 0
151 | 6 | 157 | 91 |  | 0.38075 | 1.205 | 2.4996 | 9.2196 | 6.1537 | -1.5306 | 18.5523 | 27.9052 | 75.8333 | 103.7385 | 164.6953 | 1
151 | 7 | 336 | 144 |  | 0.38075 | 1.205 | 2.4996 | 9.2196 | 7.1537 | -1.2688 | 27.5781 | 133.7583 | 120 | 253.7583 | 402.8667 | 1
151 | 8 | 497 | 171 |  | 0.38075 | 1.205 | 2.4996 | 9.2196 | 8.1537 | -1.007 | 36.6078 | 298.7349 | 142.5 | 441.2349 | 700.5045 | 1
151 | 9 | 549 | 194 |  | 0.38075 | 1.205 | 2.4996 | 9.2196 | 9.1537 | -0.74517 | 45.1709 | 424.3027 | 161.6667 | 585.9694 | 930.285 | 1
151 | 10 | 632 | 228 |  | 0.38075 | 1.205 | 2.4996 | 9.2196 | 10.1537 | -0.48337 | 52.5514 | 569.9053 | 190 | 759.9053 | 1206.4256 | 1
151 | 11 | 525 | 316 |  | 0.38075 | 1.205 | 2.4996 | 9.2196 | 11.1537 | -0.22157 | 57.6316 | 513.9463 | 263.3333 | 777.2796 | 1234.0091 | 1
151 | 12 | 668 | 256 |  | 0.38075 | 1.205 | 2.4996 | 9.2196 | 12.1537 | 0.040228 | 59.0847 | 667.461 | 213.3333 | 880.7944 | 1398.3491 | 1
151 | 13 | 728 | 203 |  | 0.38075 | 1.205 | 2.4996 | 9.2196 | 13.1537 | 0.30203 | 56.3984 | 699.6901 | 169.1667 | 868.8567 | 1379.3969 | 1
151 | 14 | 448 | 303 |  | 0.38075 | 1.205 | 2.4996 | 9.2196 | 14.1537 | 0.56383 | 50.4675 | 388.55 | 252.5 | 641.05 | 1017.7309 | 1
151 | 15 | 536 | 246 |  | 0.38075 | 1.205 | 2.4996 | 9.2196 | 15.1537 | 0.82563 | 42.6253 | 388.1419 | 205 | 593.1419 | 941.6721 | 1
151 | 16 | 228 | 262 |  | 0.38075 | 1.205 | 2.4996 | 9.2196 | 16.1537 | 1.0874 | 33.8574 | 123.4409 | 218.3333 | 341.7742 | 542.6008 | 1
151 | 17 | 40 | 205 |  | 0.38075 | 1.205 | 2.4996 | 9.2196 | 17.1537 | 1.3492 | 24.7858 | 13.2615 | 170.8333 | 184.0949 | 292.269 | 1
151 | 18 | 81 | 142 |  | 0.38075 | 1.205 | 2.4996 | 9.2196 | 18.1537 | 1.611 | 15.8368 | 8.8161 | 118.3333 | 127.1494 | 201.8624 | 1
151 | 19 | 4 | 67 |  | 0.38075 | 1.205 | 2.4996 | 9.2196 | 19.1537 | 1.8728 | 7.3605 | 0 | 55.8333 | 55.8333 | 88.641 | 0
151 | 20 | 0 | 14 |  | 0.38075 | 1.205 | 2.4996 | 9.2196 | 20.1537 | 2.1346 | -0.30168 | 0 | 11.6667 | 11.6667 | 18.522 | 0
151 | 21 | 0 | 0 |  | 0.38075 | 1.205 | 2.4996 | 9.2196 | 21.1537 | 2.3964 | -6.785 | 0 | 0 | 0 | 0 | 0
151 | 22 | 0 | 0 |  | 0.38075 | 1.205 | 2.4996 | 9.2196 | 22.1537 | 2.6582 | -11.7025 | 0 | 0 | 0 | 0 | 0
151 | 23 | 0 | 0 |  | 0.38075 | 1.205 | 2.4996 | 9.2196 | 23.1537 | 2.92 | -14.6879 | 0 | 0 | 0 | 0 | 0
151 | 24 | 0 | 0 |  | 0.38075 | 1.205 | 2.4996 | 9.2196 | 24.1537 | 3.1818 | -15.4774 | 0 | 0 | 0 | 0 | 0
152 | 1 | 0 | 0 |  | 0.38333 | 1.2222 | 2.3553 | 9.0753 | 1.1513 | -2.8402 | -13.8559 | 0 | 0 | 0 | 0 | 0
152 | 2 | 0 | 0 |  | 0.38333 | 1.2222 | 2.3553 | 9.0753 | 2.1513 | -2.5784 | -10.2524 | 0 | 0 | 0 | 0 | 0
152 | 3 | 0 | 0 |  | 0.38333 | 1.2222 | 2.3553 | 9.0753 | 3.1513 | -2.3166 | -4.8237 | 0 | 0 | 0 | 0 | 0
152 | 4 | 0 | 1 |  | 0.38333 | 1.2222 | 2.3553 | 9.0753 | 4.1513 | -2.0548 | 2.0519 | 0 | 0.83333 | 0.83333 | 1.323 | 0
152 | 5 | 10 | 34 |  | 0.38333 | 1.2222 | 2.3553 | 9.0753 | 5.1513 | -1.793 | 9.9931 | 0 | 28.3333 | 28.3333 | 44.982 | 0
152 | 6 | 204 | 98 |  | 0.38333 | 1.2222 | 2.3553 | 9.0753 | 6.1513 | -1.5312 | 18.6447 | 36.3303 | 81.6667 | 117.997 | 187.332 | 1
152 | 7 | 448 | 127 |  | 0.38333 | 1.2222 | 2.3553 | 9.0753 | 7.1513 | -1.2694 | 27.6682 | 178.4094 | 105.8333 | 284.2427 | 451.2638 | 1
152 | 8 | 621 | 137 |  | 0.38333 | 1.2222 | 2.3553 | 9.0753 | 8.1513 | -1.0076 | 36.7002 | 373.2643 | 114.1667 | 487.431 | 773.8454 | 1
152 | 9 | 743 | 131 |  | 0.38333 | 1.2222 | 2.3553 | 9.0753 | 9.1513 | -0.7458 | 45.2714 | 574.1683 | 109.1667 | 683.3349 | 1084.8625 | 1
152 | 10 | 787 | 148 |  | 0.38333 | 1.2222 | 2.3553 | 9.0753 | 10.1513 | -0.484 | 52.6669 | 709.5872 | 123.3333 | 832.9206 | 1322.3447 | 1
152 | 11 | 835 | 138 |  | 0.38333 | 1.2222 | 2.3553 | 9.0753 | 11.1513 | -0.2222 | 57.7665 | 817.3681 | 115 | 932.3681 | 1480.2277 | 1
152 | 12 | 846 | 143 |  | 0.38333 | 1.2222 | 2.3553 | 9.0753 | 12.1513 | 0.039598 | 59.234 | 845.3663 | 119.1667 | 964.533 | 1531.2926 | 1
152 | 13 | 842 | 143 |  | 0.38333 | 1.2222 | 2.3553 | 9.0753 | 13.1513 | 0.3014 | 56.5491 | 809.4555 | 119.1667 | 928.6222 | 1474.2806 | 1
152 | 14 | 827 | 136 |  | 0.38333 | 1.2222 | 2.3553 | 9.0753 | 14.1513 | 0.5632 | 50.6118 | 717.6374 | 113.3333 | 830.9708 | 1319.2492 | 1
152 | 15 | 793 | 128 |  | 0.38333 | 1.2222 | 2.3553 | 9.0753 | 15.1513 | 0.825 | 42.7632 | 574.8161 | 106.6667 | 681.4828 | 1081.922 | 1
152 | 16 | 715 | 129 |  | 0.38333 | 1.2222 | 2.3553 | 9.0753 | 16.1513 | 1.0868 | 33.9918 | 387.8126 | 107.5 | 495.3126 | 786.3583 | 1
152 | 17 | 611 | 117 |  | 0.38333 | 1.2222 | 2.3553 | 9.0753 | 17.1513 | 1.3486 | 24.9198 | 203.3361 | 97.5 | 300.8361 | 477.6075 | 1
152 | 18 | 403 | 112 |  | 0.38333 | 1.2222 | 2.3553 | 9.0753 | 18.1513 | 1.6104 | 15.9728 | 44.4663 | 93.3333 | 137.7996 | 218.7707 | 1
152 | 19 | 135 | 78 |  | 0.38333 | 1.2222 | 2.3553 | 9.0753 | 19.1513 | 1.8722 | 7.5001 | 0 | 65 | 65 | 103.194 | 0
152 | 20 | 0 | 18 |  | 0.38333 | 1.2222 | 2.3553 | 9.0753 | 20.1513 | 2.134 | -0.15753 | 0 | 15 | 15 | 23.814 | 0
152 | 21 | 0 | 0 |  | 0.38333 | 1.2222 | 2.3553 | 9.0753 | 21.1513 | 2.3958 | -6.6365 | 0 | 0 | 0 | 0 | 0
152 | 22 | 0 | 0 |  | 0.38333 | 1.2222 | 2.3553 | 9.0753 | 22.1513 | 2.6576 | -11.5512 | 0 | 0 | 0 | 0 | 0
152 | 23 | 0 | 0 |  | 0.38333 | 1.2222 | 2.3553 | 9.0753 | 23.1513 | 2.9194 | -14.5368 | 0 | 0 | 0 | 0 | 0
152 | 24 | 0 | 0 |  | 0.38333 | 1.2222 | 2.3553 | 9.0753 | 24.1513 | 3.1812 | -15.3304 | 0 | 0 | 0 | 0 | 0
153 | 1 | 0 | 0 |  | 0.3858 | 1.2394 | 2.2046 | 8.9246 | 1.1487 | -2.8409 | -13.7236 | 0 | 0 | 0 | 0 | 0
153 | 2 | 0 | 0 |  | 0.3858 | 1.2394 | 2.2046 | 8.9246 | 2.1487 | -2.5791 | -10.1305 | 0 | 0 | 0 | 0 | 0
153 | 3 | 0 | 0 |  | 0.3858 | 1.2394 | 2.2046 | 8.9246 | 3.1487 | -2.3173 | -4.713 | 0 | 0 | 0 | 0 | 0
153 | 4 | 0 | 2 |  | 0.3858 | 1.2394 | 2.2046 | 8.9246 | 4.1487 | -2.0555 | 2.1522 | 0 | 1.6667 | 1.6667 | 2.646 | 0
153 | 5 | 11 | 34 |  | 0.3858 | 1.2394 | 2.2046 | 8.9246 | 5.1487 | -1.7937 | 10.085 | 0 | 28.3333 | 28.3333 | 44.982 | 0
153 | 6 | 202 | 99 |  | 0.3858 | 1.2394 | 2.2046 | 8.9246 | 6.1487 | -1.5319 | 18.7309 | 36.0318 | 82.5 | 118.5318 | 188.1811 | 1
153 | 7 | 445 | 128 |  | 0.3858 | 1.2394 | 2.2046 | 8.9246 | 7.1487 | -1.2701 | 27.7522 | 177.2552 | 106.6667 | 283.9219 | 450.7544 | 1
153 | 8 | 614 | 139 |  | 0.3858 | 1.2394 | 2.2046 | 8.9246 | 8.1487 | -1.0083 | 36.7864 | 369.0263 | 115.8333 | 484.8596 | 769.7631 | 1
153 | 9 | 734 | 135 |  | 0.3858 | 1.2394 | 2.2046 | 8.9246 | 9.1487 | -0.74646 | 45.3655 | 567.12 | 112.5 | 679.62 | 1078.9647 | 1
153 | 10 | 779 | 152 |  | 0.3858 | 1.2394 | 2.2046 | 8.9246 | 10.1487 | -0.48466 | 52.7755 | 702.2683 | 126.6667 | 828.935 | 1316.0172 | 1
153 | 11 | 833 | 139 |  | 0.3858 | 1.2394 | 2.2046 | 8.9246 | 11.1487 | -0.22286 | 57.8943 | 815.3477 | 115.8333 | 931.181 | 1478.343 | 1
153 | 12 | 843 | 144 |  | 0.3858 | 1.2394 | 2.2046 | 8.9246 | 12.1487 | 0.038941 | 59.3767 | 842.4112 | 120 | 962.4112 | 1527.924 | 1
153 | 13 | 841 | 144 |  | 0.3858 | 1.2394 | 2.2046 | 8.9246 | 13.1487 | 0.30074 | 56.694 | 808.69 | 120 | 928.69 | 1474.3883 | 1
153 | 14 | 830 | 135 |  | 0.3858 | 1.2394 | 2.2046 | 8.9246 | 14.1487 | 0.56254 | 50.751 | 720.622 | 112.5 | 833.122 | 1322.6644 | 1
153 | 15 | 744 | 157 |  | 0.3858 | 1.2394 | 2.2046 | 8.9246 | 15.1487 | 0.82434 | 42.8966 | 539.8295 | 130.8333 | 670.6628 | 1064.7443 | 1
153 | 16 | 605 | 177 |  | 0.3858 | 1.2394 | 2.2046 | 8.9246 | 16.1487 | 1.0861 | 34.122 | 328.7427 | 147.5 | 476.2427 | 756.0829 | 1
153 | 17 | 592 | 122 |  | 0.3858 | 1.2394 | 2.2046 | 8.9246 | 17.1487 | 1.3479 | 25.0496 | 197.7477 | 101.6667 | 299.4143 | 475.3502 | 1
153 | 18 | 388 | 115 |  | 0.3858 | 1.2394 | 2.2046 | 8.9246 | 18.1487 | 1.6097 | 16.1044 | 43.3839 | 95.8333 | 139.2173 | 221.0213 | 1
153 | 19 | 136 | 79 |  | 0.3858 | 1.2394 | 2.2046 | 8.9246 | 19.1487 | 1.8715 | 7.6351 | 0 | 65.8333 | 65.8333 | 104.517 | 0
153 | 20 | 0 | 18 |  | 0.3858 | 1.2394 | 2.2046 | 8.9246 | 20.1487 | 2.1333 | -0.018412 | 0 | 15 | 15 | 23.814 | 0
153 | 21 | 0 | 0 |  | 0.3858 | 1.2394 | 2.2046 | 8.9246 | 21.1487 | 2.3951 | -6.4935 | 0 | 0 | 0 | 0 | 0
153 | 22 | 0 | 0 |  | 0.3858 | 1.2394 | 2.2046 | 8.9246 | 22.1487 | 2.6569 | -11.406 | 0 | 0 | 0 | 0 | 0
153 | 23 | 0 | 0 |  | 0.3858 | 1.2394 | 2.2046 | 8.9246 | 23.1487 | 2.9187 | -14.3922 | 0 | 0 | 0 | 0 | 0
153 | 24 | 0 | 0 |  | 0.3858 | 1.2394 | 2.2046 | 8.9246 | 24.1487 | 3.1805 | -15.1901 | 0 | 0 | 0 | 0 | 0
154 | 1 | 0 | 0 |  | 0.38814 | 1.2566 | 2.048 | 8.768 | 1.1461 | -2.8415 | -13.5981 | 0 | 0 | 0 | 0 | 0
154 | 2 | 0 | 0 |  | 0.38814 | 1.2566 | 2.048 | 8.768 | 2.1461 | -2.5797 | -10.0155 | 0 | 0 | 0 | 0 | 0
154 | 3 | 0 | 0 |  | 0.38814 | 1.2566 | 2.048 | 8.768 | 3.1461 | -2.3179 | -4.6089 | 0 | 0 | 0 | 0 | 0
154 | 4 | 0 | 2 |  | 0.38814 | 1.2566 | 2.048 | 8.768 | 4.1461 | -2.0561 | 2.2462 | 0 | 1.6667 | 1.6667 | 2.646 | 0
154 | 5 | 0 | 30 |  | 0.38814 | 1.2566 | 2.048 | 8.768 | 5.1461 | -1.7943 | 10.1707 | 0 | 25 | 25 | 39.69 | 0
154 | 6 | 1 | 84 |  | 0.38814 | 1.2566 | 2.048 | 8.768 | 6.1461 | -1.5325 | 18.811 | 0.1786 | 70 | 70.1786 | 111.4155 | 1
154 | 7 | 0 | 107 |  | 0.38814 | 1.2566 | 2.048 | 8.768 | 7.1461 | -1.2707 | 27.8301 | 0 | 89.1667 | 89.1667 | 141.561 | 1
154 | 8 | 1 | 163 |  | 0.38814 | 1.2566 | 2.048 | 8.768 | 8.1461 | -1.0089 | 36.8664 | 0.60093 | 135.8333 | 136.4343 | 216.603 | 1
154 | 9 | 10 | 210 |  | 0.38814 | 1.2566 | 2.048 | 8.768 | 9.1461 | -0.74714 | 45.4531 | 7.7248 | 175 | 182.7248 | 290.094 | 1
154 | 10 | 14 | 249 |  | 0.38814 | 1.2566 | 2.048 | 8.768 | 10.1461 | -0.48534 | 52.8774 | 12.6188 | 207.5 | 220.1188 | 349.4606 | 1
154 | 11 | 5 | 285 |  | 0.38814 | 1.2566 | 2.048 | 8.768 | 11.1461 | -0.22354 | 58.0152 | 4.8936 | 237.5 | 242.3936 | 384.8241 | 1
154 | 12 | 5 | 299 |  | 0.38814 | 1.2566 | 2.048 | 8.768 | 12.1461 | 0.038257 | 59.5126 | 4.9967 | 249.1667 | 254.1634 | 403.5098 | 1
154 | 13 | 5 | 297 |  | 0.38814 | 1.2566 | 2.048 | 8.768 | 13.1461 | 0.30006 | 56.8329 | 4.8091 | 247.5 | 252.3091 | 400.5659 | 1
154 | 14 | 5 | 278 |  | 0.38814 | 1.2566 | 2.048 | 8.768 | 14.1461 | 0.56186 | 50.8851 | 4.3434 | 231.6667 | 236.0101 | 374.6896 | 1
154 | 15 | 13 | 238 |  | 0.38814 | 1.2566 | 2.048 | 8.768 | 15.1461 | 0.82366 | 43.0254 | 9.4418 | 198.3333 | 207.7751 | 329.8637 | 1
154 | 16 | 8 | 197 |  | 0.38814 | 1.2566 | 2.048 | 8.768 | 16.1461 | 1.0855 | 34.2479 | 4.3548 | 164.1667 | 168.5215 | 267.5447 | 1
154 | 17 | 0 | 147 |  | 0.38814 | 1.2566 | 2.048 | 8.768 | 17.1461 | 1.3473 | 25.1751 | 0 | 122.5 | 122.5 | 194.481 | 1
154 | 18 | 0 | 90 |  | 0.38814 | 1.2566 | 2.048 | 8.768 | 18.1461 | 1.6091 | 16.2316 | 0 | 75 | 75 | 119.07 | 1
154 | 19 | 0 | 61 |  | 0.38814 | 1.2566 | 2.048 | 8.768 | 19.1461 | 1.8709 | 7.7654 | 0 | 50.8333 | 50.8333 | 80.703 | 0
154 | 20 | 0 | 11 |  | 0.38814 | 1.2566 | 2.048 | 8.768 | 20.1461 | 2.1327 | 0.1156 | 0 | 9.1667 | 9.1667 | 14.553 | 0
154 | 21 | 0 | 0 |  | 0.38814 | 1.2566 | 2.048 | 8.768 | 21.1461 | 2.3945 | -6.3561 | 0 | 0 | 0 | 0 | 0
154 | 22 | 0 | 0 |  | 0.38814 | 1.2566 | 2.048 | 8.768 | 22.1461 | 2.6563 | -11.2668 | 0 | 0 | 0 | 0 | 0
154 | 23 | 0 | 0 |  | 0.38814 | 1.2566 | 2.048 | 8.768 | 23.1461 | 2.9181 | -14.254 | 0 | 0 | 0 | 0 | 0
154 | 24 | 0 | 0 |  | 0.38814 | 1.2566 | 2.048 | 8.768 | 24.1461 | 3.1799 | -15.0566 | 0 | 0 | 0 | 0 | 0
155 | 1 | 0 | 0 |  | 0.39037 | 1.2739 | 1.8855 | 8.6055 | 1.1434 | -2.8422 | -13.4796 | 0 | 0 | 0 | 0 | 0
155 | 2 | 0 | 0 |  | 0.39037 | 1.2739 | 1.8855 | 8.6055 | 2.1434 | -2.5804 | -9.9072 | 0 | 0 | 0 | 0 | 0
155 | 3 | 0 | 0 |  | 0.39037 | 1.2739 | 1.8855 | 8.6055 | 3.1434 | -2.3186 | -4.5115 | 0 | 0 | 0 | 0 | 0
155 | 4 | 0 | 1 |  | 0.39037 | 1.2739 | 1.8855 | 8.6055 | 4.1434 | -2.0568 | 2.3337 | 0 | 0.83333 | 0.83333 | 1.323 | 0
155 | 5 | 0 | 21 |  | 0.39037 | 1.2739 | 1.8855 | 8.6055 | 5.1434 | -1.795 | 10.2502 | 0 | 17.5 | 17.5 | 27.783 | 0
155 | 6 | 1 | 84 |  | 0.39037 | 1.2739 | 1.8855 | 8.6055 | 6.1434 | -1.5332 | 18.885 | 0.17876 | 70 | 70.1788 | 111.4158 | 1
155 | 7 | 9 | 167 |  | 0.39037 | 1.2739 | 1.8855 | 8.6055 | 7.1434 | -1.2714 | 27.9019 | 3.5852 | 139.1667 | 142.7518 | 226.6328 | 1
155 | 8 | 49 | 236 |  | 0.39037 | 1.2739 | 1.8855 | 8.6055 | 8.1434 | -1.0096 | 36.9401 | 29.439 | 196.6667 | 226.1056 | 358.9653 | 1
155 | 9 | 87 | 290 |  | 0.39037 | 1.2739 | 1.8855 | 8.6055 | 9.1434 | -0.74785 | 45.5342 | 67.1897 | 241.6667 | 308.8564 | 490.3404 | 1
155 | 10 | 224 | 364 |  | 0.39037 | 1.2739 | 1.8855 | 8.6055 | 10.1434 | -0.48605 | 52.9724 | 201.8609 | 303.3333 | 505.1943 | 802.0464 | 1
155 | 11 | 172 | 454 |  | 0.39037 | 1.2739 | 1.8855 | 8.6055 | 11.1434 | -0.22425 | 58.1291 | 168.3227 | 378.3333 | 546.656 | 867.8711 | 1
155 | 12 | 173 | 476 |  | 0.39037 | 1.2739 | 1.8855 | 8.6055 | 12.1434 | 0.037549 | 59.6418 | 172.8934 | 396.6667 | 569.56 | 904.2335 | 1
155 | 13 | 511 | 352 |  | 0.39037 | 1.2739 | 1.8855 | 8.6055 | 13.1434 | 0.29935 | 56.9658 | 491.6023 | 293.3333 | 784.9357 | 1246.1639 | 1
155 | 14 | 711 | 201 |  | 0.39037 | 1.2739 | 1.8855 | 8.6055 | 14.1434 | 0.56115 | 51.0139 | 617.9541 | 167.5 | 785.4541 | 1246.9869 | 1
155 | 15 | 769 | 147 |  | 0.39037 | 1.2739 | 1.8855 | 8.6055 | 15.1434 | 0.82295 | 43.1495 | 559.0606 | 122.5 | 681.5606 | 1082.0456 | 1
155 | 16 | 693 | 138 |  | 0.39037 | 1.2739 | 1.8855 | 8.6055 | 16.1434 | 1.0847 | 34.3694 | 377.9037 | 115 | 492.9037 | 782.5339 | 1
155 | 17 | 610 | 119 |  | 0.39037 | 1.2739 | 1.8855 | 8.6055 | 17.1434 | 1.3465 | 25.2963 | 205.2474 | 99.1667 | 304.4141 | 483.2878 | 1
155 | 18 | 392 | 116 |  | 0.39037 | 1.2739 | 1.8855 | 8.6055 | 18.1434 | 1.6083 | 16.3543 | 44.9608 | 96.6667 | 141.6275 | 224.8478 | 1
155 | 19 | 139 | 81 |  | 0.39037 | 1.2739 | 1.8855 | 8.6055 | 19.1434 | 1.8701 | 7.8909 | 0 | 67.5 | 67.5 | 107.163 | 0
155 | 20 | 0 | 14 |  | 0.39037 | 1.2739 | 1.8855 | 8.6055 | 20.1434 | 2.1319 | 0.24441 | 0 | 11.6667 | 11.6667 | 18.522 | 0
155 | 21 | 0 | 0 |  | 0.39037 | 1.2739 | 1.8855 | 8.6055 | 21.1434 | 2.3937 | -6.2244 | 0 | 0 | 0 | 0 | 0
155 | 22 | 0 | 0 |  | 0.39037 | 1.2739 | 1.8855 | 8.6055 | 22.1434 | 2.6555 | -11.1338 | 0 | 0 | 0 | 0 | 0
155 | 23 | 0 | 0 |  | 0.39037 | 1.2739 | 1.8855 | 8.6055 | 23.1434 | 2.9173 | -14.1224 | 0 | 0 | 0 | 0 | 0
155 | 24 | 0 | 0 |  | 0.39037 | 1.2739 | 1.8855 | 8.6055 | 24.1434 | 3.1791 | -14.9299 | 0 | 0 | 0 | 0 | 0
156 | 1 | 0 | 0 |  | 0.39248 | 1.2911 | 1.7176 | 8.4376 | 1.1406 | -2.843 | -13.3681 | 0 | 0 | 0 | 0 | 0
156 | 2 | 0 | 0 |  | 0.39248 | 1.2911 | 1.7176 | 8.4376 | 2.1406 | -2.5812 | -9.8058 | 0 | 0 | 0 | 0 | 0
156 | 3 | 0 | 0 |  | 0.39248 | 1.2911 | 1.7176 | 8.4376 | 3.1406 | -2.3194 | -4.4207 | 0 | 0 | 0 | 0 | 0
156 | 4 | 0 | 2 |  | 0.39248 | 1.2911 | 1.7176 | 8.4376 | 4.1406 | -2.0576 | 2.4148 | 0 | 1.6667 | 1.6667 | 2.646 | 0
156 | 5 | 0 | 21 |  | 0.39248 | 1.2911 | 1.7176 | 8.4376 | 5.1406 | -1.7958 | 10.3234 | 0 | 17.5 | 17.5 | 27.783 | 0
156 | 6 | 1 | 84 |  | 0.39248 | 1.2911 | 1.7176 | 8.4376 | 6.1406 | -1.534 | 18.9529 | 0.17886 | 70 | 70.1789 | 111.416 | 1
156 | 7 | 22 | 162 |  | 0.39248 | 1.2911 | 1.7176 | 8.4376 | 7.1406 | -1.2722 | 27.9676 | 8.7623 | 135 | 143.7623 | 228.237 | 1
156 | 8 | 38 | 241 |  | 0.39248 | 1.2911 | 1.7176 | 8.4376 | 8.1406 | -1.0104 | 37.0077 | 22.8237 | 200.8333 | 223.657 | 355.0778 | 1
156 | 9 | 203 | 310 |  | 0.39248 | 1.2911 | 1.7176 | 8.4376 | 9.1406 | -0.74858 | 45.6089 | 156.7318 | 258.3333 | 415.0652 | 658.9575 | 1
156 | 10 | 551 | 294 |  | 0.39248 | 1.2911 | 1.7176 | 8.4376 | 10.1406 | -0.48678 | 53.0606 | 496.4334 | 245 | 741.4334 | 1177.0997 | 1
156 | 11 | 778 | 179 |  | 0.39248 | 1.2911 | 1.7176 | 8.4376 | 11.1406 | -0.22498 | 58.2359 | 761.2801 | 149.1667 | 910.4467 | 1445.4252 | 1
156 | 12 | 564 | 305 |  | 0.39248 | 1.2911 | 1.7176 | 8.4376 | 12.1406 | 0.036816 | 59.7642 | 563.671 | 254.1667 | 817.8377 | 1298.3991 | 1
156 | 13 | 128 | 371 |  | 0.39248 | 1.2911 | 1.7176 | 8.4376 | 13.1406 | 0.29862 | 57.0926 | 123.1701 | 309.1667 | 432.3367 | 686.3778 | 1
156 | 14 | 281 | 350 |  | 0.39248 | 1.2911 | 1.7176 | 8.4376 | 14.1406 | 0.56041 | 51.1375 | 244.3545 | 291.6667 | 536.0212 | 850.9872 | 1
156 | 15 | 78 | 339 |  | 0.39248 | 1.2911 | 1.7176 | 8.4376 | 15.1406 | 0.82221 | 43.2688 | 56.7607 | 282.5 | 339.2607 | 538.6103 | 1
156 | 16 | 69 | 280 |  | 0.39248 | 1.2911 | 1.7176 | 8.4376 | 16.1406 | 1.084 | 34.4864 | 37.6928 | 233.3333 | 271.0261 | 430.2811 | 1
156 | 17 | 33 | 219 |  | 0.39248 | 1.2911 | 1.7176 | 8.4376 | 17.1406 | 1.3458 | 25.413 | 11.143 | 182.5 | 193.643 | 307.4276 | 1
156 | 18 | 0 | 91 |  | 0.39248 | 1.2911 | 1.7176 | 8.4376 | 18.1406 | 1.6076 | 16.4724 | 0 | 75.8333 | 75.8333 | 120.393 | 1
156 | 19 | 0 | 63 |  | 0.39248 | 1.2911 | 1.7176 | 8.4376 | 19.1406 | 1.8694 | 8.0115 | 0 | 52.5 | 52.5 | 83.349 | 0
156 | 20 | 0 | 11 |  | 0.39248 | 1.2911 | 1.7176 | 8.4376 | 20.1406 | 2.1312 | 0.36794 | 0 | 9.1667 | 9.1667 | 14.553 | 0
156 | 21 | 0 | 0 |  | 0.39248 | 1.2911 | 1.7176 | 8.4376 | 21.1406 | 2.393 | -6.0985 | 0 | 0 | 0 | 0 | 0
156 | 22 | 0 | 0 |  | 0.39248 | 1.2911 | 1.7176 | 8.4376 | 22.1406 | 2.6548 | -11.0069 | 0 | 0 | 0 | 0 | 0
156 | 23 | 0 | 0 |  | 0.39248 | 1.2911 | 1.7176 | 8.4376 | 23.1406 | 2.9166 | -13.9974 | 0 | 0 | 0 | 0 | 0
156 | 24 | 0 | 0 |  | 0.39248 | 1.2911 | 1.7176 | 8.4376 | 24.1406 | 3.1784 | -14.8101 | 0 | 0 | 0 | 0 | 0
157 | 1 | 0 | 0 |  | 0.39447 | 1.3083 | 1.5445 | 8.2645 | 1.1377 | -2.8437 | -13.2635 | 0 | 0 | 0 | 0 | 0
157 | 2 | 0 | 0 |  | 0.39447 | 1.3083 | 1.5445 | 8.2645 | 2.1377 | -2.5819 | -9.7113 | 0 | 0 | 0 | 0 | 0
157 | 3 | 0 | 0 |  | 0.39447 | 1.3083 | 1.5445 | 8.2645 | 3.1377 | -2.3201 | -4.3366 | 0 | 0 | 0 | 0 | 0
157 | 4 | 0 | 1 |  | 0.39447 | 1.3083 | 1.5445 | 8.2645 | 4.1377 | -2.0583 | 2.4895 | 0 | 0.83333 | 0.83333 | 1.323 | 0
157 | 5 | 0 | 21 |  | 0.39447 | 1.3083 | 1.5445 | 8.2645 | 5.1377 | -1.7965 | 10.3904 | 0 | 17.5 | 17.5 | 27.783 | 0
157 | 6 | 1 | 84 |  | 0.39447 | 1.3083 | 1.5445 | 8.2645 | 6.1377 | -1.5347 | 19.0147 | 0.1789 | 70 | 70.1789 | 111.416 | 1
157 | 7 | 21 | 162 |  | 0.39447 | 1.3083 | 1.5445 | 8.2645 | 7.1377 | -1.2729 | 28.0272 | 8.3616 | 135 | 143.3616 | 227.6009 | 1
157 | 8 | 267 | 245 |  | 0.39447 | 1.3083 | 1.5445 | 8.2645 | 8.1377 | -1.0111 | 37.0691 | 160.3099 | 204.1667 | 364.4765 | 578.6429 | 1
157 | 9 | 644 | 181 |  | 0.39447 | 1.3083 | 1.5445 | 8.2645 | 9.1377 | -0.74934 | 45.6772 | 497.0602 | 150.8333 | 647.8936 | 1028.5958 | 1
157 | 10 | 376 | 328 |  | 0.39447 | 1.3083 | 1.5445 | 8.2645 | 10.1377 | -0.48754 | 53.142 | 338.6832 | 273.3333 | 612.0166 | 971.6375 | 1
157 | 11 | 124 | 356 |  | 0.39447 | 1.3083 | 1.5445 | 8.2645 | 11.1377 | -0.22574 | 58.3355 | 121.3201 | 296.6667 | 417.9867 | 663.5958 | 1
157 | 12 | 89 | 405 |  | 0.39447 | 1.3083 | 1.5445 | 8.2645 | 12.1377 | 0.036061 | 59.8796 | 88.9506 | 337.5 | 426.4506 | 677.033 | 1
157 | 13 | 482 | 410 |  | 0.39447 | 1.3083 | 1.5445 | 8.2645 | 13.1377 | 0.29786 | 57.2132 | 463.9206 | 341.6667 | 805.5873 | 1278.9503 | 1
157 | 14 | 336 | 302 |  | 0.39447 | 1.3083 | 1.5445 | 8.2645 | 14.1377 | 0.55966 | 51.2556 | 292.3344 | 251.6667 | 544.0011 | 863.6561 | 1
157 | 15 | 77 | 339 |  | 0.39447 | 1.3083 | 1.5445 | 8.2645 | 15.1377 | 0.82146 | 43.3834 | 56.0869 | 282.5 | 338.5869 | 537.5406 | 1
157 | 16 | 195 | 291 |  | 0.39447 | 1.3083 | 1.5445 | 8.2645 | 16.1377 | 1.0833 | 34.5988 | 106.7078 | 242.5 | 349.2078 | 554.4023 | 1
157 | 17 | 42 | 215 |  | 0.39447 | 1.3083 | 1.5445 | 8.2645 | 17.1377 | 1.3451 | 25.5252 | 14.2314 | 179.1667 | 193.3981 | 307.0388 | 1
157 | 18 | 17 | 139 |  | 0.39447 | 1.3083 | 1.5445 | 8.2645 | 18.1377 | 1.6069 | 16.5859 | 1.9971 | 115.8333 | 117.8304 | 187.0676 | 1
157 | 19 | 0 | 64 |  | 0.39447 | 1.3083 | 1.5445 | 8.2645 | 19.1377 | 1.8687 | 8.1272 | 0 | 53.3333 | 53.3333 | 84.672 | 0
157 | 20 | 0 | 7 |  | 0.39447 | 1.3083 | 1.5445 | 8.2645 | 20.1377 | 2.1305 | 0.48612 | 0 | 5.8333 | 5.8333 | 9.261 | 0
157 | 21 | 0 | 0 |  | 0.39447 | 1.3083 | 1.5445 | 8.2645 | 21.1377 | 2.3923 | -5.9783 | 0 | 0 | 0 | 0 | 0
157 | 22 | 0 | 0 |  | 0.39447 | 1.3083 | 1.5445 | 8.2645 | 22.1377 | 2.6541 | -10.8864 | 0 | 0 | 0 | 0 | 0
157 | 23 | 0 | 0 |  | 0.39447 | 1.3083 | 1.5445 | 8.2645 | 23.1377 | 2.9159 | -13.8792 | 0 | 0 | 0 | 0 | 0
157 | 24 | 0 | 0 |  | 0.39447 | 1.3083 | 1.5445 | 8.2645 | 24.1377 | 3.1777 | -14.6972 | 0 | 0 | 0 | 0 | 0
158 | 1 | 0 | 0 |  | 0.39633 | 1.3255 | 1.3666 | 8.0866 | 1.1348 | -2.8445 | -13.1659 | 0 | 0 | 0 | 0 | 0
158 | 2 | 0 | 0 |  | 0.39633 | 1.3255 | 1.3666 | 8.0866 | 2.1348 | -2.5827 | -9.6237 | 0 | 0 | 0 | 0 | 0
158 | 3 | 0 | 0 |  | 0.39633 | 1.3255 | 1.3666 | 8.0866 | 3.1348 | -2.3209 | -4.2591 | 0 | 0 | 0 | 0 | 0
158 | 4 | 0 | 1 |  | 0.39633 | 1.3255 | 1.3666 | 8.0866 | 4.1348 | -2.0591 | 2.5576 | 0 | 0.83333 | 0.83333 | 1.323 | 0
158 | 5 | 0 | 14 |  | 0.39633 | 1.3255 | 1.3666 | 8.0866 | 5.1348 | -1.7973 | 10.4511 | 0 | 11.6667 | 11.6667 | 18.522 | 0
158 | 6 | 0 | 53 |  | 0.39633 | 1.3255 | 1.3666 | 8.0866 | 6.1348 | -1.5355 | 19.0703 | 0 | 44.1667 | 44.1667 | 70.119 | 1
158 | 7 | 0 | 107 |  | 0.39633 | 1.3255 | 1.3666 | 8.0866 | 7.1348 | -1.2737 | 28.0808 | 0 | 89.1667 | 89.1667 | 141.561 | 1
158 | 8 | 46 | 235 |  | 0.39633 | 1.3255 | 1.3666 | 8.0866 | 8.1348 | -1.0119 | 37.1243 | 27.6075 | 195.8333 | 223.4408 | 354.7347 | 1
158 | 9 | 260 | 308 |  | 0.39633 | 1.3255 | 1.3666 | 8.0866 | 9.1348 | -0.75011 | 45.739 | 200.6058 | 256.6667 | 457.2724 | 725.9657 | 1
158 | 10 | 522 | 276 |  | 0.39633 | 1.3255 | 1.3666 | 8.0866 | 10.1348 | -0.48831 | 53.2166 | 470.0723 | 230 | 700.0723 | 1111.4347 | 1
158 | 11 | 428 | 329 |  | 0.39633 | 1.3255 | 1.3666 | 8.0866 | 11.1348 | -0.22651 | 58.4281 | 418.6941 | 274.1667 | 692.8608 | 1099.9857 | 1
158 | 12 | 108 | 388 |  | 0.39633 | 1.3255 | 1.3666 | 8.0866 | 12.1348 | 0.035284 | 59.9881 | 107.9428 | 323.3333 | 431.2761 | 684.6939 | 1
158 | 13 | 88 | 402 |  | 0.39633 | 1.3255 | 1.3666 | 8.0866 | 13.1348 | 0.29708 | 57.3276 | 84.7189 | 335 | 419.7189 | 666.3457 | 1
158 | 14 | 273 | 353 |  | 0.39633 | 1.3255 | 1.3666 | 8.0866 | 14.1348 | 0.55888 | 51.3684 | 237.6453 | 294.1667 | 531.8119 | 844.3046 | 1
158 | 15 | 597 | 263 |  | 0.39633 | 1.3255 | 1.3666 | 8.0866 | 15.1348 | 0.82068 | 43.493 | 435.2711 | 219.1667 | 654.4378 | 1038.9854 | 1
158 | 16 | 727 | 120 |  | 0.39633 | 1.3255 | 1.3666 | 8.0866 | 16.1348 | 1.0825 | 34.7066 | 398.5096 | 100 | 498.5096 | 791.4338 | 1
158 | 17 | 613 | 114 |  | 0.39633 | 1.3255 | 1.3666 | 8.0866 | 17.1348 | 1.3443 | 25.6328 | 208.4219 | 95 | 303.4219 | 481.7126 | 1
158 | 18 | 423 | 108 |  | 0.39633 | 1.3255 | 1.3666 | 8.0866 | 18.1348 | 1.6061 | 16.6946 | 50.2621 | 90 | 140.2621 | 222.6802 | 1
158 | 19 | 177 | 77 |  | 0.39633 | 1.3255 | 1.3666 | 8.0866 | 19.1348 | 1.8679 | 8.2378 | 0 | 64.1667 | 64.1667 | 101.871 | 0
158 | 20 | 0 | 21 |  | 0.39633 | 1.3255 | 1.3666 | 8.0866 | 20.1348 | 2.1297 | 0.59886 | 0 | 17.5 | 17.5 | 27.783 | 0
158 | 21 | 0 | 0 |  | 0.39633 | 1.3255 | 1.3666 | 8.0866 | 21.1348 | 2.3915 | -5.8641 | 0 | 0 | 0 | 0 | 0
158 | 22 | 0 | 0 |  | 0.39633 | 1.3255 | 1.3666 | 8.0866 | 22.1348 | 2.6533 | -10.7723 | 0 | 0 | 0 | 0 | 0
158 | 23 | 0 | 0 |  | 0.39633 | 1.3255 | 1.3666 | 8.0866 | 23.1348 | 2.9151 | -13.7676 | 0 | 0 | 0 | 0 | 0
158 | 24 | 0 | 0 |  | 0.39633 | 1.3255 | 1.3666 | 8.0866 | 24.1348 | 3.1769 | -14.5913 | 0 | 0 | 0 | 0 | 0
159 | 1 | 0 | 0 |  | 0.39807 | 1.3427 | 1.1841 | 7.9041 | 1.1317 | -2.8453 | -13.0754 | 0 | 0 | 0 | 0 | 0
159 | 2 | 0 | 0 |  | 0.39807 | 1.3427 | 1.1841 | 7.9041 | 2.1317 | -2.5835 | -9.5431 | 0 | 0 | 0 | 0 | 0
159 | 3 | 0 | 0 |  | 0.39807 | 1.3427 | 1.1841 | 7.9041 | 3.1317 | -2.3217 | -4.1884 | 0 | 0 | 0 | 0 | 0
159 | 4 | 0 | 1 |  | 0.39807 | 1.3427 | 1.1841 | 7.9041 | 4.1317 | -2.0599 | 2.6194 | 0 | 0.83333 | 0.83333 | 1.323 | 0
159 | 5 | 0 | 22 |  | 0.39807 | 1.3427 | 1.1841 | 7.9041 | 5.1317 | -1.7981 | 10.5056 | 0 | 18.3333 | 18.3333 | 29.106 | 0
159 | 6 | 1 | 85 |  | 0.39807 | 1.3427 | 1.1841 | 7.9041 | 6.1317 | -1.5363 | 19.12 | 0.1788 | 70.8333 | 71.0121 | 112.7389 | 1
159 | 7 | 22 | 163 |  | 0.39807 | 1.3427 | 1.1841 | 7.9041 | 7.1317 | -1.2745 | 28.1284 | 8.7516 | 135.8333 | 144.5849 | 229.543 | 1
159 | 8 | 178 | 241 |  | 0.39807 | 1.3427 | 1.1841 | 7.9041 | 8.1317 | -1.0127 | 37.1735 | 106.7784 | 200.8333 | 307.6117 | 488.3643 | 1
159 | 9 | 74 | 297 |  | 0.39807 | 1.3427 | 1.1841 | 7.9041 | 9.1317 | -0.75091 | 45.7945 | 57.0735 | 247.5 | 304.5735 | 483.5409 | 1
159 | 10 | 498 | 334 |  | 0.39807 | 1.3427 | 1.1841 | 7.9041 | 10.1317 | -0.48911 | 53.2844 | 448.3364 | 278.3333 | 726.6697 | 1153.6609 | 1
159 | 11 | 725 | 196 |  | 0.39807 | 1.3427 | 1.1841 | 7.9041 | 11.1317 | -0.22731 | 58.5134 | 709.1358 | 163.3333 | 872.4692 | 1385.132 | 1
159 | 12 | 746 | 192 |  | 0.39807 | 1.3427 | 1.1841 | 7.9041 | 12.1317 | 0.034488 | 60.0896 | 745.6208 | 160 | 905.6208 | 1437.7636 | 1
159 | 13 | 430 | 350 |  | 0.39807 | 1.3427 | 1.1841 | 7.9041 | 13.1317 | 0.29629 | 57.4357 | 414.0631 | 291.6667 | 705.7297 | 1120.4166 | 1
159 | 14 | 427 | 327 |  | 0.39807 | 1.3427 | 1.1841 | 7.9041 | 14.1317 | 0.55809 | 51.4756 | 371.8942 | 272.5 | 644.3942 | 1023.0402 | 1
159 | 15 | 208 | 356 |  | 0.39807 | 1.3427 | 1.1841 | 7.9041 | 15.1317 | 0.81989 | 43.5977 | 151.7959 | 296.6667 | 448.4626 | 711.9792 | 1
159 | 16 | 71 | 279 |  | 0.39807 | 1.3427 | 1.1841 | 7.9041 | 16.1317 | 1.0817 | 34.8097 | 38.9848 | 232.5 | 271.4848 | 431.0093 | 1
159 | 17 | 32 | 221 |  | 0.39807 | 1.3427 | 1.1841 | 7.9041 | 17.1317 | 1.3435 | 25.7358 | 10.9166 | 184.1667 | 195.0832 | 309.7141 | 1
159 | 18 | 205 | 144 |  | 0.39807 | 1.3427 | 1.1841 | 7.9041 | 18.1317 | 1.6053 | 16.7985 | 24.6289 | 120 | 144.6289 | 229.6129 | 1
159 | 19 | 81 | 95 |  | 0.39807 | 1.3427 | 1.1841 | 7.9041 | 19.1317 | 1.8671 | 8.3434 | 0 | 79.1667 | 79.1667 | 125.685 | 0
159 | 20 | 0 | 22 |  | 0.39807 | 1.3427 | 1.1841 | 7.9041 | 20.1317 | 2.1289 | 0.7061 | 0 | 18.3333 | 18.3333 | 29.106 | 0
159 | 21 | 0 | 0 |  | 0.39807 | 1.3427 | 1.1841 | 7.9041 | 21.1317 | 2.3907 | -5.7558 | 0 | 0 | 0 | 0 | 0
159 | 22 | 0 | 0 |  | 0.39807 | 1.3427 | 1.1841 | 7.9041 | 22.1317 | 2.6525 | -10.6646 | 0 | 0 | 0 | 0 | 0
159 | 23 | 0 | 0 |  | 0.39807 | 1.3427 | 1.1841 | 7.9041 | 23.1317 | 2.9143 | -13.6629 | 0 | 0 | 0 | 0 | 0
159 | 24 | 0 | 0 |  | 0.39807 | 1.3427 | 1.1841 | 7.9041 | 24.1317 | 3.1761 | -14.4925 | 0 | 0 | 0 | 0 | 0
160 | 1 | 0 | 0 |  | 0.39969 | 1.3599 | 0.99743 | 7.7174 | 1.1286 | -2.8461 | -12.9921 | 0 | 0 | 0 | 0 | 0
160 | 2 | 0 | 0 |  | 0.39969 | 1.3599 | 0.99743 | 7.7174 | 2.1286 | -2.5843 | -9.4694 | 0 | 0 | 0 | 0 | 0
160 | 3 | 0 | 0 |  | 0.39969 | 1.3599 | 0.99743 | 7.7174 | 3.1286 | -2.3225 | -4.1245 | 0 | 0 | 0 | 0 | 0
160 | 4 | 0 | 2 |  | 0.39969 | 1.3599 | 0.99743 | 7.7174 | 4.1286 | -2.0607 | 2.6746 | 0 | 1.6667 | 1.6667 | 2.646 | 0
160 | 5 | 19 | 38 |  | 0.39969 | 1.3599 | 0.99743 | 7.7174 | 5.1286 | -1.7989 | 10.5539 | 0 | 31.6667 | 31.6667 | 50.274 | 0
160 | 6 | 204 | 102 |  | 0.39969 | 1.3599 | 0.99743 | 7.7174 | 6.1286 | -1.5371 | 19.1635 | 36.4465 | 85 | 121.4465 | 192.8084 | 1
160 | 7 | 439 | 132 |  | 0.39969 | 1.3599 | 0.99743 | 7.7174 | 7.1286 | -1.2753 | 28.1699 | 174.5211 | 110 | 284.5211 | 451.7057 | 1
160 | 8 | 607 | 143 |  | 0.39969 | 1.3599 | 0.99743 | 7.7174 | 8.1286 | -1.0135 | 37.2165 | 363.9323 | 119.1667 | 483.0989 | 766.9679 | 1
160 | 9 | 735 | 136 |  | 0.39969 | 1.3599 | 0.99743 | 7.7174 | 9.1286 | -0.75172 | 45.8435 | 566.6422 | 113.3333 | 679.9755 | 1079.5292 | 1
160 | 10 | 780 | 152 |  | 0.39969 | 1.3599 | 0.99743 | 7.7174 | 10.1286 | -0.48993 | 53.3454 | 702.0089 | 126.6667 | 828.6756 | 1315.6054 | 1
160 | 11 | 805 | 154 |  | 0.39969 | 1.3599 | 0.99743 | 7.7174 | 11.1286 | -0.22813 | 58.5916 | 787.2675 | 128.3333 | 915.6009 | 1453.6079 | 1
160 | 12 | 714 | 223 |  | 0.39969 | 1.3599 | 0.99743 | 7.7174 | 12.1286 | 0.033674 | 60.1841 | 713.6507 | 185.8333 | 899.484 | 1428.0208 | 1
160 | 13 | 554 | 315 |  | 0.39969 | 1.3599 | 0.99743 | 7.7174 | 13.1286 | 0.29547 | 57.5374 | 533.5904 | 262.5 | 796.0904 | 1263.8732 | 1
160 | 14 | 486 | 340 |  | 0.39969 | 1.3599 | 0.99743 | 7.7174 | 14.1286 | 0.55727 | 51.5772 | 423.4985 | 283.3333 | 706.8318 | 1122.1661 | 1
160 | 15 | 386 | 310 |  | 0.39969 | 1.3599 | 0.99743 | 7.7174 | 15.1286 | 0.81907 | 43.6974 | 281.9627 | 258.3333 | 540.2961 | 857.774 | 1
160 | 16 | 375 | 249 |  | 0.39969 | 1.3599 | 0.99743 | 7.7174 | 16.1286 | 1.0809 | 34.9081 | 206.2483 | 207.5 | 413.7483 | 656.8668 | 1
160 | 17 | 164 | 225 |  | 0.39969 | 1.3599 | 0.99743 | 7.7174 | 17.1286 | 1.3427 | 25.834 | 56.1309 | 187.5 | 243.6309 | 386.7884 | 1
160 | 18 | 26 | 139 |  | 0.39969 | 1.3599 | 0.99743 | 7.7174 | 18.1286 | 1.6045 | 16.8975 | 3.1571 | 115.8333 | 118.9905 | 188.9093 | 1
160 | 19 | 128 | 80 |  | 0.39969 | 1.3599 | 0.99743 | 7.7174 | 19.1286 | 1.8663 | 8.4437 | 0 | 66.6667 | 66.6667 | 105.84 | 0
160 | 20 | 0 | 22 |  | 0.39969 | 1.3599 | 0.99743 | 7.7174 | 20.1286 | 2.1281 | 0.80774 | 0 | 18.3333 | 18.3333 | 29.106 | 0
160 | 21 | 0 | 0 |  | 0.39969 | 1.3599 | 0.99743 | 7.7174 | 21.1286 | 2.3899 | -5.6536 | 0 | 0 | 0 | 0 | 0
160 | 22 | 0 | 0 |  | 0.39969 | 1.3599 | 0.99743 | 7.7174 | 22.1286 | 2.6517 | -10.5634 | 0 | 0 | 0 | 0 | 0
160 | 23 | 0 | 0 |  | 0.39969 | 1.3599 | 0.99743 | 7.7174 | 23.1286 | 2.9135 | -13.565 | 0 | 0 | 0 | 0 | 0
160 | 24 | 0 | 0 |  | 0.39969 | 1.3599 | 0.99743 | 7.7174 | 24.1286 | 3.1753 | -14.4007 | 0 | 0 | 0 | 0 | 0
161 | 1 | 0 | 0 |  | 0.40119 | 1.3771 | 0.80686 | 7.5269 | 1.1254 | -2.847 | -12.9158 | 0 | 0 | 0 | 0 | 0
161 | 2 | 0 | 0 |  | 0.40119 | 1.3771 | 0.80686 | 7.5269 | 2.1254 | -2.5852 | -9.4026 | 0 | 0 | 0 | 0 | 0
161 | 3 | 0 | 0 |  | 0.40119 | 1.3771 | 0.80686 | 7.5269 | 3.1254 | -2.3234 | -4.0672 | 0 | 0 | 0 | 0 | 0
161 | 4 | 0 | 2 |  | 0.40119 | 1.3771 | 0.80686 | 7.5269 | 4.1254 | -2.0616 | 2.7235 | 0 | 1.6667 | 1.6667 | 2.646 | 0
161 | 5 | 22 | 38 |  | 0.40119 | 1.3771 | 0.80686 | 7.5269 | 5.1254 | -1.7998 | 10.596 | 0 | 31.6667 | 31.6667 | 50.274 | 0
161 | 6 | 231 | 93 |  | 0.40119 | 1.3771 | 0.80686 | 7.5269 | 6.1254 | -1.538 | 19.2011 | 41.2256 | 77.5 | 118.7256 | 188.4887 | 1
161 | 7 | 432 | 134 |  | 0.40119 | 1.3771 | 0.80686 | 7.5269 | 7.1254 | -1.2762 | 28.2055 | 171.608 | 111.6667 | 283.2746 | 449.7268 | 1
161 | 8 | 47 | 237 |  | 0.40119 | 1.3771 | 0.80686 | 7.5269 | 8.1254 | -1.0144 | 37.2535 | 28.1627 | 197.5 | 225.6627 | 358.262 | 1
161 | 9 | 472 | 283 |  | 0.40119 | 1.3771 | 0.80686 | 7.5269 | 9.1254 | -0.75256 | 45.8863 | 363.7219 | 235.8333 | 599.5552 | 951.8539 | 1
161 | 10 | 695 | 183 |  | 0.40119 | 1.3771 | 0.80686 | 7.5269 | 10.1254 | -0.49076 | 53.3996 | 625.316 | 152.5 | 777.816 | 1234.8606 | 1
161 | 11 | 423 | 338 |  | 0.40119 | 1.3771 | 0.80686 | 7.5269 | 11.1254 | -0.22896 | 58.6627 | 413.6175 | 281.6667 | 695.2842 | 1103.8331 | 1
161 | 12 | 281 | 380 |  | 0.40119 | 1.3771 | 0.80686 | 7.5269 | 12.1254 | 0.032842 | 60.2714 | 280.8673 | 316.6667 | 597.5339 | 948.6449 | 1
161 | 13 | 104 | 393 |  | 0.40119 | 1.3771 | 0.80686 | 7.5269 | 13.1254 | 0.29464 | 57.6327 | 100.1917 | 327.5 | 427.6917 | 679.0033 | 1
161 | 14 | 90 | 379 |  | 0.40119 | 1.3771 | 0.80686 | 7.5269 | 14.1254 | 0.55644 | 51.6732 | 78.4659 | 315.8333 | 394.2993 | 625.9895 | 1
161 | 15 | 74 | 345 |  | 0.40119 | 1.3771 | 0.80686 | 7.5269 | 15.1254 | 0.81824 | 43.7919 | 54.1053 | 287.5 | 341.6053 | 542.3326 | 1
161 | 16 | 69 | 283 |  | 0.40119 | 1.3771 | 0.80686 | 7.5269 | 16.1254 | 1.08 | 35.0016 | 38.0118 | 235.8333 | 273.8452 | 434.7566 | 1
161 | 17 | 33 | 223 |  | 0.40119 | 1.3771 | 0.80686 | 7.5269 | 17.1254 | 1.3418 | 25.9274 | 11.3308 | 185.8333 | 197.1642 | 313.0178 | 1
161 | 18 | 18 | 142 |  | 0.40119 | 1.3771 | 0.80686 | 7.5269 | 18.1254 | 1.6036 | 16.9915 | 2.2083 | 118.3333 | 120.5416 | 191.3719 | 1
161 | 19 | 0 | 67 |  | 0.40119 | 1.3771 | 0.80686 | 7.5269 | 19.1254 | 1.8654 | 8.5388 | 0 | 55.8333 | 55.8333 | 88.641 | 0
161 | 20 | 0 | 13 |  | 0.40119 | 1.3771 | 0.80686 | 7.5269 | 20.1254 | 2.1272 | 0.90373 | 0 | 10.8333 | 10.8333 | 17.199 | 0
161 | 21 | 0 | 0 |  | 0.40119 | 1.3771 | 0.80686 | 7.5269 | 21.1254 | 2.389 | -5.5575 | 0 | 0 | 0 | 0 | 0
161 | 22 | 0 | 0 |  | 0.40119 | 1.3771 | 0.80686 | 7.5269 | 22.1254 | 2.6508 | -10.4687 | 0 | 0 | 0 | 0 | 0
161 | 23 | 0 | 0 |  | 0.40119 | 1.3771 | 0.80686 | 7.5269 | 23.1254 | 2.9126 | -13.4741 | 0 | 0 | 0 | 0 | 0
161 | 24 | 0 | 0 |  | 0.40119 | 1.3771 | 0.80686 | 7.5269 | 24.1254 | 3.1744 | -14.316 | 0 | 0 | 0 | 0 | 0
162 | 1 | 0 | 0 |  | 0.40255 | 1.3944 | 0.61273 | 7.3327 | 1.1222 | -2.8478 | -12.8467 | 0 | 0 | 0 | 0 | 0
162 | 2 | 0 | 0 |  | 0.40255 | 1.3944 | 0.61273 | 7.3327 | 2.1222 | -2.586 | -9.3429 | 0 | 0 | 0 | 0 | 0
162 | 3 | 0 | 0 |  | 0.40255 | 1.3944 | 0.61273 | 7.3327 | 3.1222 | -2.3242 | -4.0167 | 0 | 0 | 0 | 0 | 0
162 | 4 | 0 | 1 |  | 0.40255 | 1.3944 | 0.61273 | 7.3327 | 4.1222 | -2.0624 | 2.7658 | 0 | 0.83333 | 0.83333 | 1.323 | 0
162 | 5 | 0 | 23 |  | 0.40255 | 1.3944 | 0.61273 | 7.3327 | 5.1222 | -1.8006 | 10.632 | 0 | 19.1667 | 19.1667 | 30.429 | 0
162 | 6 | 1 | 86 |  | 0.40255 | 1.3944 | 0.61273 | 7.3327 | 6.1222 | -1.5388 | 19.2326 | 0.17822 | 71.6667 | 71.8449 | 114.0609 | 1
162 | 7 | 21 | 163 |  | 0.40255 | 1.3944 | 0.61273 | 7.3327 | 7.1222 | -1.277 | 28.2352 | 8.3348 | 135.8333 | 144.1681 | 228.8813 | 1
162 | 8 | 35 | 244 |  | 0.40255 | 1.3944 | 0.61273 | 7.3327 | 8.1222 | -1.0152 | 37.2844 | 20.9587 | 203.3333 | 224.292 | 356.086 | 1
162 | 9 | 6 | 213 |  | 0.40255 | 1.3944 | 0.61273 | 7.3327 | 9.1222 | -0.7534 | 45.9227 | 4.6214 | 177.5 | 182.1214 | 289.1359 | 1
162 | 10 | 7 | 254 |  | 0.40255 | 1.3944 | 0.61273 | 7.3327 | 10.1222 | -0.4916 | 53.447 | 6.2961 | 211.6667 | 217.9628 | 346.0377 | 1
162 | 11 | 11 | 280 |  | 0.40255 | 1.3944 | 0.61273 | 7.3327 | 11.1222 | -0.2298 | 58.7265 | 10.7543 | 233.3333 | 244.0876 | 387.5135 | 1
162 | 12 | 12 | 293 |  | 0.40255 | 1.3944 | 0.61273 | 7.3327 | 12.1222 | 0.031995 | 60.3516 | 11.9945 | 244.1667 | 256.1612 | 406.6815 | 1
162 | 13 | 12 | 291 |  | 0.40255 | 1.3944 | 0.61273 | 7.3327 | 13.1222 | 0.29379 | 57.7215 | 11.5632 | 242.5 | 254.0632 | 403.3508 | 1
162 | 14 | 11 | 274 |  | 0.40255 | 1.3944 | 0.61273 | 7.3327 | 14.1222 | 0.55559 | 51.7634 | 9.5952 | 228.3333 | 237.9285 | 377.7353 | 1
162 | 15 | 7 | 245 |  | 0.40255 | 1.3944 | 0.61273 | 7.3327 | 15.1222 | 0.81739 | 43.8813 | 5.1228 | 204.1667 | 209.2894 | 332.2679 | 1
162 | 16 | 4 | 201 |  | 0.40255 | 1.3944 | 0.61273 | 7.3327 | 16.1222 | 1.0792 | 35.0902 | 2.2071 | 167.5 | 169.7071 | 269.427 | 1
162 | 17 | 42 | 218 |  | 0.40255 | 1.3944 | 0.61273 | 7.3327 | 17.1222 | 1.341 | 26.0159 | 14.4662 | 181.6667 | 196.1328 | 311.3805 | 1
162 | 18 | 17 | 142 |  | 0.40255 | 1.3944 | 0.61273 | 7.3327 | 18.1222 | 1.6028 | 17.0806 | 2.1064 | 118.3333 | 120.4397 | 191.2101 | 1
162 | 19 | 0 | 42 |  | 0.40255 | 1.3944 | 0.61273 | 7.3327 | 19.1222 | 1.8646 | 8.6285 | 0 | 35 | 35 | 55.566 | 0
162 | 20 | 0 | 13 |  | 0.40255 | 1.3944 | 0.61273 | 7.3327 | 20.1222 | 2.1264 | 0.994 | 0 | 10.8333 | 10.8333 | 17.199 | 0
162 | 21 | 0 | 0 |  | 0.40255 | 1.3944 | 0.61273 | 7.3327 | 21.1222 | 2.3882 | -5.4676 | 0 | 0 | 0 | 0 | 0
162 | 22 | 0 | 0 |  | 0.40255 | 1.3944 | 0.61273 | 7.3327 | 22.1222 | 2.65 | -10.3806 | 0 | 0 | 0 | 0 | 0
162 | 23 | 0 | 0 |  | 0.40255 | 1.3944 | 0.61273 | 7.3327 | 23.1222 | 2.9118 | -13.3901 | 0 | 0 | 0 | 0 | 0
162 | 24 | 0 | 0 |  | 0.40255 | 1.3944 | 0.61273 | 7.3327 | 24.1222 | 3.1736 | -14.2384 | 0 | 0 | 0 | 0 | 0
163 | 1 | 0 | 0 |  | 0.4038 | 1.4116 | 0.41539 | 7.1354 | 1.1189 | -2.8487 | -12.7847 | 0 | 0 | 0 | 0 | 0
163 | 2 | 0 | 0 |  | 0.4038 | 1.4116 | 0.41539 | 7.1354 | 2.1189 | -2.5869 | -9.2902 | 0 | 0 | 0 | 0 | 0
163 | 3 | 0 | 0 |  | 0.4038 | 1.4116 | 0.41539 | 7.1354 | 3.1189 | -2.3251 | -3.9729 | 0 | 0 | 0 | 0 | 0
163 | 4 | 0 | 2 |  | 0.4038 | 1.4116 | 0.41539 | 7.1354 | 4.1189 | -2.0633 | 2.8018 | 0 | 1.6667 | 1.6667 | 2.646 | 0
163 | 5 | 0 | 29 |  | 0.4038 | 1.4116 | 0.41539 | 7.1354 | 5.1189 | -1.8015 | 10.6617 | 0 | 24.1667 | 24.1667 | 38.367 | 0
163 | 6 | 57 | 96 |  | 0.4038 | 1.4116 | 0.41539 | 7.1354 | 6.1189 | -1.5397 | 19.2581 | 10.1411 | 80 | 90.1411 | 143.108 | 1
163 | 7 | 21 | 163 |  | 0.4038 | 1.4116 | 0.41539 | 7.1354 | 7.1189 | -1.2779 | 28.2589 | 8.3266 | 135.8333 | 144.16 | 228.8684 | 1
163 | 8 | 34 | 243 |  | 0.4038 | 1.4116 | 0.41539 | 7.1354 | 8.1189 | -1.0161 | 37.3093 | 20.3457 | 202.5 | 222.8457 | 353.7898 | 1
163 | 9 | 69 | 300 |  | 0.4038 | 1.4116 | 0.41539 | 7.1354 | 9.1189 | -0.75426 | 45.9528 | 53.1192 | 250 | 303.1192 | 481.232 | 1
163 | 10 | 73 | 358 |  | 0.4038 | 1.4116 | 0.41539 | 7.1354 | 10.1189 | -0.49246 | 53.4876 | 65.6376 | 298.3333 | 363.9709 | 577.8403 | 1
163 | 11 | 88 | 388 |  | 0.4038 | 1.4116 | 0.41539 | 7.1354 | 11.1189 | -0.23067 | 58.7831 | 86.0197 | 323.3333 | 409.353 | 649.8888 | 1
163 | 12 | 89 | 407 |  | 0.4038 | 1.4116 | 0.41539 | 7.1354 | 12.1189 | 0.031134 | 60.4246 | 88.9606 | 339.1667 | 428.1273 | 679.6948 | 1
163 | 13 | 28 | 277 |  | 0.4038 | 1.4116 | 0.41539 | 7.1354 | 13.1189 | 0.29293 | 57.8037 | 26.9871 | 230.8333 | 257.8204 | 409.3157 | 1
163 | 14 | 124 | 350 |  | 0.4038 | 1.4116 | 0.41539 | 7.1354 | 14.1189 | 0.55473 | 51.8479 | 108.2189 | 291.6667 | 399.8856 | 634.8584 | 1
163 | 15 | 72 | 345 |  | 0.4038 | 1.4116 | 0.41539 | 7.1354 | 15.1189 | 0.81653 | 43.9654 | 52.7394 | 287.5 | 340.2394 | 540.164 | 1
163 | 16 | 67 | 284 |  | 0.4038 | 1.4116 | 0.41539 | 7.1354 | 16.1189 | 1.0783 | 35.1738 | 37.0279 | 236.6667 | 273.6946 | 434.5176 | 1
163 | 17 | 32 | 224 |  | 0.4038 | 1.4116 | 0.41539 | 7.1354 | 17.1189 | 1.3401 | 26.0994 | 11.0554 | 186.6667 | 197.7221 | 313.9036 | 1
163 | 18 | 301 | 147 |  | 0.4038 | 1.4116 | 0.41539 | 7.1354 | 18.1189 | 1.6019 | 17.1644 | 37.652 | 122.5 | 160.152 | 254.2573 | 1
163 | 19 | 178 | 81 |  | 0.4038 | 1.4116 | 0.41539 | 7.1354 | 19.1189 | 1.8637 | 8.7129 | 0 | 67.5 | 67.5 | 107.163 | 0
163 | 20 | 0 | 23 |  | 0.4038 | 1.4116 | 0.41539 | 7.1354 | 20.1189 | 2.1255 | 1.0785 | 0 | 19.1667 | 19.1667 | 30.429 | 0
163 | 21 | 0 | 0 |  | 0.4038 | 1.4116 | 0.41539 | 7.1354 | 21.1189 | 2.3873 | -5.3839 | 0 | 0 | 0 | 0 | 0
163 | 22 | 0 | 0 |  | 0.4038 | 1.4116 | 0.41539 | 7.1354 | 22.1189 | 2.6491 | -10.2992 | 0 | 0 | 0 | 0 | 0
163 | 23 | 0 | 0 |  | 0.4038 | 1.4116 | 0.41539 | 7.1354 | 23.1189 | 2.9109 | -13.3131 | 0 | 0 | 0 | 0 | 0
163 | 24 | 0 | 0 |  | 0.4038 | 1.4116 | 0.41539 | 7.1354 | 24.1189 | 3.1727 | -14.1681 | 0 | 0 | 0 | 0 | 0
164 | 1 | 0 | 0 |  | 0.40492 | 1.4288 | 0.21518 | 6.9352 | 1.1156 | -2.8495 | -12.7299 | 0 | 0 | 0 | 0 | 0
164 | 2 | 0 | 0 |  | 0.40492 | 1.4288 | 0.21518 | 6.9352 | 2.1156 | -2.5877 | -9.2444 | 0 | 0 | 0 | 0 | 0
164 | 3 | 0 | 0 |  | 0.40492 | 1.4288 | 0.21518 | 6.9352 | 3.1156 | -2.3259 | -3.9358 | 0 | 0 | 0 | 0 | 0
164 | 4 | 0 | 2 |  | 0.40492 | 1.4288 | 0.21518 | 6.9352 | 4.1156 | -2.0641 | 2.8313 | 0 | 1.6667 | 1.6667 | 2.646 | 0
164 | 5 | 0 | 23 |  | 0.40492 | 1.4288 | 0.21518 | 6.9352 | 5.1156 | -1.8023 | 10.6853 | 0 | 19.1667 | 19.1667 | 30.429 | 0
164 | 6 | 146 | 91 |  | 0.40492 | 1.4288 | 0.21518 | 6.9352 | 6.1156 | -1.5405 | 19.2777 | 25.9233 | 75.8333 | 101.7566 | 161.5488 | 1
164 | 7 | 234 | 162 |  | 0.40492 | 1.4288 | 0.21518 | 6.9352 | 7.1156 | -1.2787 | 28.2768 | 92.6818 | 135 | 227.6818 | 361.4677 | 1
164 | 8 | 47 | 237 |  | 0.40492 | 1.4288 | 0.21518 | 6.9352 | 8.1156 | -1.0169 | 37.3283 | 28.1039 | 197.5 | 225.6039 | 358.1688 | 1
164 | 9 | 69 | 300 |  | 0.40492 | 1.4288 | 0.21518 | 6.9352 | 9.1156 | -0.75514 | 45.9767 | 53.0911 | 250 | 303.0911 | 481.1875 | 1
164 | 10 | 8 | 254 |  | 0.40492 | 1.4288 | 0.21518 | 6.9352 | 10.1156 | -0.49334 | 53.5216 | 7.1907 | 211.6667 | 218.8573 | 347.4579 | 1
164 | 11 | 11 | 280 |  | 0.40492 | 1.4288 | 0.21518 | 6.9352 | 11.1156 | -0.23154 | 58.8324 | 10.7506 | 233.3333 | 244.0839 | 387.5077 | 1
164 | 12 | 125 | 376 |  | 0.40492 | 1.4288 | 0.21518 | 6.9352 | 12.1156 | 0.03026 | 60.4903 | 124.9463 | 313.3333 | 438.2797 | 695.8128 | 1
164 | 13 | 28 | 277 |  | 0.40492 | 1.4288 | 0.21518 | 6.9352 | 13.1156 | 0.29206 | 57.8793 | 26.9933 | 230.8333 | 257.8266 | 409.3255 | 1
164 | 14 | 123 | 350 |  | 0.40492 | 1.4288 | 0.21518 | 6.9352 | 14.1156 | 0.55386 | 51.9265 | 107.4005 | 291.6667 | 399.0671 | 633.559 | 1
164 | 15 | 206 | 359 |  | 0.40492 | 1.4288 | 0.21518 | 6.9352 | 15.1156 | 0.81566 | 44.0443 | 151.0288 | 299.1667 | 450.1955 | 714.7303 | 1
164 | 16 | 71 | 281 |  | 0.40492 | 1.4288 | 0.21518 | 6.9352 | 16.1156 | 1.0775 | 35.2524 | 39.2994 | 234.1667 | 273.4661 | 434.1548 | 1
164 | 17 | 32 | 224 |  | 0.40492 | 1.4288 | 0.21518 | 6.9352 | 17.1156 | 1.3393 | 26.1779 | 11.0882 | 186.6667 | 197.7549 | 313.9557 | 1
164 | 18 | 252 | 152 |  | 0.40492 | 1.4288 | 0.21518 | 6.9352 | 18.1156 | 1.6011 | 17.2432 | 31.8122 | 126.6667 | 158.4789 | 251.6011 | 1
164 | 19 | 175 | 83 |  | 0.40492 | 1.4288 | 0.21518 | 6.9352 | 19.1156 | 1.8629 | 8.7918 | 0 | 69.1667 | 69.1667 | 109.809 | 0
164 | 20 | 0 | 24 |  | 0.40492 | 1.4288 | 0.21518 | 6.9352 | 20.1156 | 2.1247 | 1.1571 | 0 | 20 | 20 | 31.752 | 0
164 | 21 | 0 | 0 |  | 0.40492 | 1.4288 | 0.21518 | 6.9352 | 21.1156 | 2.3865 | -5.3064 | 0 | 0 | 0 | 0 | 0
164 | 22 | 0 | 0 |  | 0.40492 | 1.4288 | 0.21518 | 6.9352 | 22.1156 | 2.6483 | -10.2245 | 0 | 0 | 0 | 0 | 0
164 | 23 | 0 | 0 |  | 0.40492 | 1.4288 | 0.21518 | 6.9352 | 23.1156 | 2.9101 | -13.2431 | 0 | 0 | 0 | 0 | 0
164 | 24 | 0 | 0 |  | 0.40492 | 1.4288 | 0.21518 | 6.9352 | 24.1156 | 3.1719 | -14.1049 | 0 | 0 | 0 | 0 | 0
165 | 1 | 0 | 0 |  | 0.40591 | 1.446 | 0.012447 | 6.7324 | 1.1122 | -2.8504 | -12.6823 | 0 | 0 | 0 | 0 | 0
165 | 2 | 0 | 0 |  | 0.40591 | 1.446 | 0.012447 | 6.7324 | 2.1122 | -2.5886 | -9.2057 | 0 | 0 | 0 | 0 | 0
165 | 3 | 0 | 0 |  | 0.40591 | 1.446 | 0.012447 | 6.7324 | 3.1122 | -2.3268 | -3.9055 | 0 | 0 | 0 | 0 | 0
165 | 4 | 0 | 2 |  | 0.40591 | 1.446 | 0.012447 | 6.7324 | 4.1122 | -2.065 | 2.8544 | 0 | 1.6667 | 1.6667 | 2.646 | 0
165 | 5 | 0 | 14 |  | 0.40591 | 1.446 | 0.012447 | 6.7324 | 5.1122 | -1.8032 | 10.7027 | 0 | 11.6667 | 11.6667 | 18.522 | 0
165 | 6 | 2 | 86 |  | 0.40591 | 1.446 | 0.012447 | 6.7324 | 6.1122 | -1.5414 | 19.2914 | 0.3543 | 71.6667 | 72.021 | 114.3405 | 1
165 | 7 | 22 | 164 |  | 0.40591 | 1.446 | 0.012447 | 6.7324 | 7.1122 | -1.2796 | 28.2888 | 8.7033 | 136.6667 | 145.37 | 230.7894 | 1
165 | 8 | 48 | 238 |  | 0.40591 | 1.446 | 0.012447 | 6.7324 | 8.1122 | -1.0178 | 37.3413 | 28.679 | 198.3333 | 227.0123 | 360.4048 | 1
165 | 9 | 84 | 292 |  | 0.40591 | 1.446 | 0.012447 | 6.7324 | 9.1122 | -0.75602 | 45.9943 | 64.5969 | 243.3333 | 307.9302 | 488.8701 | 1
165 | 10 | 89 | 348 |  | 0.40591 | 1.446 | 0.012447 | 6.7324 | 10.1122 | -0.49422 | 53.5488 | 79.9675 | 290 | 369.9675 | 587.3604 | 1
165 | 11 | 259 | 381 |  | 0.40591 | 1.446 | 0.012447 | 6.7324 | 11.1122 | -0.23242 | 58.8746 | 253.0833 | 317.5 | 570.5833 | 905.858 | 1
165 | 12 | 96 | 405 |  | 0.40591 | 1.446 | 0.012447 | 6.7324 | 12.1122 | 0.029376 | 60.5488 | 95.96 | 337.5 | 433.46 | 688.1611 | 1
165 | 13 | 62 | 431 |  | 0.40591 | 1.446 | 0.012447 | 6.7324 | 13.1122 | 0.29118 | 57.9483 | 59.7846 | 359.1667 | 418.9512 | 665.127 | 1
165 | 14 | 90 | 381 |  | 0.40591 | 1.446 | 0.012447 | 6.7324 | 14.1122 | 0.55297 | 51.9993 | 78.6252 | 317.5 | 396.1252 | 628.8883 | 1
165 | 15 | 89 | 336 |  | 0.40591 | 1.446 | 0.012447 | 6.7324 | 15.1122 | 0.81477 | 44.1177 | 65.3081 | 280 | 345.3081 | 548.2112 | 1
165 | 16 | 83 | 277 |  | 0.40591 | 1.446 | 0.012447 | 6.7324 | 16.1122 | 1.0766 | 35.3258 | 46.0114 | 230.8333 | 276.8447 | 439.5186 | 1
165 | 17 | 24 | 231 |  | 0.40591 | 1.446 | 0.012447 | 6.7324 | 17.1122 | 1.3384 | 26.2514 | 8.3401 | 192.5 | 200.8401 | 318.8538 | 1
165 | 18 | 14 | 147 |  | 0.40591 | 1.446 | 0.012447 | 6.7324 | 18.1122 | 1.6002 | 17.3166 | 1.7829 | 122.5 | 124.2829 | 197.3116 | 1
165 | 19 | 0 | 70 |  | 0.40591 | 1.446 | 0.012447 | 6.7324 | 19.1122 | 1.862 | 8.8651 | 0 | 58.3333 | 58.3333 | 92.61 | 0
165 | 20 | 0 | 9 |  | 0.40591 | 1.446 | 0.012447 | 6.7324 | 20.1122 | 2.1238 | 1.2298 | 0 | 7.5 | 7.5 | 11.907 | 0
165 | 21 | 0 | 0 |  | 0.40591 | 1.446 | 0.012447 | 6.7324 | 21.1122 | 2.3856 | -5.2354 | 0 | 0 | 0 | 0 | 0
165 | 22 | 0 | 0 |  | 0.40591 | 1.446 | 0.012447 | 6.7324 | 22.1122 | 2.6474 | -10.1566 | 0 | 0 | 0 | 0 | 0
165 | 23 | 0 | 0 |  | 0.40591 | 1.446 | 0.012447 | 6.7324 | 23.1122 | 2.9092 | -13.1802 | 0 | 0 | 0 | 0 | 0
165 | 24 | 0 | 0 |  | 0.40591 | 1.446 | 0.012447 | 6.7324 | 24.1122 | 3.171 | -14.049 | 0 | 0 | 0 | 0 | 0
166 | 1 | 0 | 0 |  | 0.40677 | 1.4632 | -0.19246 | 6.5275 | 1.1088 | -2.8513 | -12.642 | 0 | 0 | 0 | 0 | 0
166 | 2 | 0 | 0 |  | 0.40677 | 1.4632 | -0.19246 | 6.5275 | 2.1088 | -2.5895 | -9.1739 | 0 | 0 | 0 | 0 | 0
166 | 3 | 0 | 0 |  | 0.40677 | 1.4632 | -0.19246 | 6.5275 | 3.1088 | -2.3277 | -3.8818 | 0 | 0 | 0 | 0 | 0
166 | 4 | 0 | 2 |  | 0.40677 | 1.4632 | -0.19246 | 6.5275 | 4.1088 | -2.0659 | 2.8712 | 0 | 1.6667 | 1.6667 | 2.646 | 0
166 | 5 | 0 | 23 |  | 0.40677 | 1.4632 | -0.19246 | 6.5275 | 5.1088 | -1.8041 | 10.7141 | 0 | 19.1667 | 19.1667 | 30.429 | 0
166 | 6 | 2 | 87 |  | 0.40677 | 1.4632 | -0.19246 | 6.5275 | 6.1088 | -1.5423 | 19.2991 | 0.35337 | 72.5 | 72.8534 | 115.662 | 1
166 | 7 | 9 | 170 |  | 0.40677 | 1.4632 | -0.19246 | 6.5275 | 7.1088 | -1.2805 | 28.295 | 3.5559 | 141.6667 | 145.2225 | 230.5553 | 1
166 | 8 | 49 | 239 |  | 0.40677 | 1.4632 | -0.19246 | 6.5275 | 8.1088 | -1.0187 | 37.3484 | 29.2518 | 199.1667 | 228.4184 | 362.6371 | 1
166 | 9 | 212 | 308 |  | 0.40677 | 1.4632 | -0.19246 | 6.5275 | 9.1088 | -0.75692 | 46.0058 | 162.9363 | 256.6667 | 419.603 | 666.1617 | 1
166 | 10 | 83 | 356 |  | 0.40677 | 1.4632 | -0.19246 | 6.5275 | 10.1088 | -0.49512 | 53.5693 | 74.549 | 296.6667 | 371.2156 | 589.342 | 1
166 | 11 | 63 | 414 |  | 0.40677 | 1.4632 | -0.19246 | 6.5275 | 11.1088 | -0.23332 | 58.9095 | 61.5497 | 345 | 406.5497 | 645.4384 | 1
166 | 12 | 265 | 400 |  | 0.40677 | 1.4632 | -0.19246 | 6.5275 | 12.1088 | 0.028482 | 60.6 | 264.8931 | 333.3333 | 598.2264 | 949.7443 | 1
166 | 13 | 465 | 325 |  | 0.40677 | 1.4632 | -0.19246 | 6.5275 | 13.1088 | 0.29028 | 58.0105 | 448.4872 | 270.8333 | 719.3205 | 1141.9933 | 1
166 | 14 | 263 | 373 |  | 0.40677 | 1.4632 | -0.19246 | 6.5275 | 14.1088 | 0.55208 | 52.066 | 229.8748 | 310.8333 | 540.7081 | 858.4282 | 1
166 | 15 | 82 | 344 |  | 0.40677 | 1.4632 | -0.19246 | 6.5275 | 15.1088 | 0.81388 | 44.1857 | 60.2241 | 286.6667 | 346.8908 | 550.7238 | 1
166 | 16 | 85 | 278 |  | 0.40677 | 1.4632 | -0.19246 | 6.5275 | 16.1088 | 1.0757 | 35.3941 | 47.1901 | 231.6667 | 278.8567 | 442.713 | 1
166 | 17 | 25 | 232 |  | 0.40677 | 1.4632 | -0.19246 | 6.5275 | 17.1088 | 1.3375 | 26.3196 | 8.7119 | 193.3333 | 202.0452 | 320.767 | 1
166 | 18 | 117 | 154 |  | 0.40677 | 1.4632 | -0.19246 | 6.5275 | 18.1088 | 1.5993 | 17.3848 | 15.0256 | 128.3333 | 143.3589 | 227.5966 | 1
166 | 19 | 0 | 70 |  | 0.40677 | 1.4632 | -0.19246 | 6.5275 | 19.1088 | 1.8611 | 8.9328 | 0 | 58.3333 | 58.3333 | 92.61 | 0
166 | 20 | 0 | 14 |  | 0.40677 | 1.4632 | -0.19246 | 6.5275 | 20.1088 | 2.1229 | 1.2965 | 0 | 11.6667 | 11.6667 | 18.522 | 0
166 | 21 | 0 | 0 |  | 0.40677 | 1.4632 | -0.19246 | 6.5275 | 21.1088 | 2.3847 | -5.1707 | 0 | 0 | 0 | 0 | 0
166 | 22 | 0 | 0 |  | 0.40677 | 1.4632 | -0.19246 | 6.5275 | 22.1088 | 2.6465 | -10.0955 | 0 | 0 | 0 | 0 | 0
166 | 23 | 0 | 0 |  | 0.40677 | 1.4632 | -0.19246 | 6.5275 | 23.1088 | 2.9083 | -13.1244 | 0 | 0 | 0 | 0 | 0
166 | 24 | 0 | 0 |  | 0.40677 | 1.4632 | -0.19246 | 6.5275 | 24.1088 | 3.1701 | -14.0003 | 0 | 0 | 0 | 0 | 0
167 | 1 | 0 | 0 |  | 0.40751 | 1.4804 | -0.39918 | 6.3208 | 1.1053 | -2.8522 | -12.6088 | 0 | 0 | 0 | 0 | 0
167 | 2 | 0 | 0 |  | 0.40751 | 1.4804 | -0.39918 | 6.3208 | 2.1053 | -2.5904 | -9.1492 | 0 | 0 | 0 | 0 | 0
167 | 3 | 0 | 0 |  | 0.40751 | 1.4804 | -0.39918 | 6.3208 | 3.1053 | -2.3286 | -3.8649 | 0 | 0 | 0 | 0 | 0
167 | 4 | 0 | 2 |  | 0.40751 | 1.4804 | -0.39918 | 6.3208 | 4.1053 | -2.0668 | 2.8815 | 0 | 1.6667 | 1.6667 | 2.646 | 0
167 | 5 | 0 | 23 |  | 0.40751 | 1.4804 | -0.39918 | 6.3208 | 5.1053 | -1.805 | 10.7194 | 0 | 19.1667 | 19.1667 | 30.429 | 0
167 | 6 | 61 | 96 |  | 0.40751 | 1.4804 | -0.39918 | 6.3208 | 6.1053 | -1.5432 | 19.301 | 10.7468 | 80 | 90.7468 | 144.0696 | 1
167 | 7 | 9 | 169 |  | 0.40751 | 1.4804 | -0.39918 | 6.3208 | 7.1053 | -1.2814 | 28.2954 | 3.5509 | 140.8333 | 144.3843 | 229.2244 | 1
167 | 8 | 49 | 238 |  | 0.40751 | 1.4804 | -0.39918 | 6.3208 | 8.1053 | -1.0196 | 37.3497 | 29.2257 | 198.3333 | 227.5591 | 361.2728 | 1
167 | 9 | 86 | 292 |  | 0.40751 | 1.4804 | -0.39918 | 6.3208 | 9.1053 | -0.75782 | 46.0112 | 66.0573 | 243.3333 | 309.3906 | 491.1885 | 1
167 | 10 | 90 | 348 |  | 0.40751 | 1.4804 | -0.39918 | 6.3208 | 10.1053 | -0.49602 | 53.5832 | 80.8057 | 290 | 370.8057 | 588.6911 | 1
167 | 11 | 62 | 413 |  | 0.40751 | 1.4804 | -0.39918 | 6.3208 | 11.1053 | -0.23422 | 58.9373 | 60.5617 | 344.1667 | 404.7284 | 642.5468 | 1
167 | 12 | 260 | 402 |  | 0.40751 | 1.4804 | -0.39918 | 6.3208 | 12.1053 | 0.02758 | 60.6439 | 259.8985 | 335 | 594.8985 | 944.4609 | 1
167 | 13 | 501 | 361 |  | 0.40751 | 1.4804 | -0.39918 | 6.3208 | 13.1053 | 0.28938 | 58.0659 | 483.3196 | 300.8333 | 784.153 | 1244.9213 | 1
167 | 14 | 735 | 204 |  | 0.40751 | 1.4804 | -0.39918 | 6.3208 | 14.1053 | 0.55118 | 52.1267 | 642.7434 | 170 | 812.7434 | 1290.3114 | 1
167 | 15 | 764 | 145 |  | 0.40751 | 1.4804 | -0.39918 | 6.3208 | 15.1053 | 0.81298 | 44.2482 | 561.5946 | 120.8333 | 682.428 | 1083.4226 | 1
167 | 16 | 498 | 223 |  | 0.40751 | 1.4804 | -0.39918 | 6.3208 | 16.1053 | 1.0748 | 35.4571 | 276.8793 | 185.8333 | 462.7126 | 734.6025 | 1
167 | 17 | 182 | 222 |  | 0.40751 | 1.4804 | -0.39918 | 6.3208 | 17.1053 | 1.3366 | 26.3827 | 63.5941 | 185 | 248.5941 | 394.6681 | 1
167 | 18 | 196 | 156 |  | 0.40751 | 1.4804 | -0.39918 | 6.3208 | 18.1053 | 1.5984 | 17.4475 | 25.3734 | 130 | 155.3734 | 246.6708 | 1
167 | 19 | 78 | 88 |  | 0.40751 | 1.4804 | -0.39918 | 6.3208 | 19.1053 | 1.8602 | 8.9949 | 0 | 73.3333 | 73.3333 | 116.424 | 0
167 | 20 | 0 | 18 |  | 0.40751 | 1.4804 | -0.39918 | 6.3208 | 20.1053 | 2.122 | 1.3572 | 0 | 15 | 15 | 23.814 | 0
167 | 21 | 0 | 0 |  | 0.40751 | 1.4804 | -0.39918 | 6.3208 | 21.1053 | 2.3838 | -5.1125 | 0 | 0 | 0 | 0 | 0
167 | 22 | 0 | 0 |  | 0.40751 | 1.4804 | -0.39918 | 6.3208 | 22.1053 | 2.6456 | -10.0412 | 0 | 0 | 0 | 0 | 0
167 | 23 | 0 | 0 |  | 0.40751 | 1.4804 | -0.39918 | 6.3208 | 23.1053 | 2.9074 | -13.0758 | 0 | 0 | 0 | 0 | 0
167 | 24 | 0 | 0 |  | 0.40751 | 1.4804 | -0.39918 | 6.3208 | 24.1053 | 3.1692 | -13.9589 | 0 | 0 | 0 | 0 | 0
168 | 1 | 0 | 0 |  | 0.40812 | 1.4976 | -0.60736 | 6.1126 | 1.1019 | -2.8531 | -12.5829 | 0 | 0 | 0 | 0 | 0
168 | 2 | 0 | 0 |  | 0.40812 | 1.4976 | -0.60736 | 6.1126 | 2.1019 | -2.5913 | -9.1315 | 0 | 0 | 0 | 0 | 0
168 | 3 | 0 | 0 |  | 0.40812 | 1.4976 | -0.60736 | 6.1126 | 3.1019 | -2.3295 | -3.8546 | 0 | 0 | 0 | 0 | 0
168 | 4 | 0 | 2 |  | 0.40812 | 1.4976 | -0.60736 | 6.1126 | 4.1019 | -2.0677 | 2.8856 | 0 | 1.6667 | 1.6667 | 2.646 | 0
168 | 5 | 0 | 23 |  | 0.40812 | 1.4976 | -0.60736 | 6.1126 | 5.1019 | -1.8059 | 10.7187 | 0 | 19.1667 | 19.1667 | 30.429 | 0
168 | 6 | 2 | 87 |  | 0.40812 | 1.4976 | -0.60736 | 6.1126 | 6.1019 | -1.5441 | 19.2971 | 0.35123 | 72.5 | 72.8512 | 115.6586 | 1
168 | 7 | 9 | 170 |  | 0.40812 | 1.4976 | -0.60736 | 6.1126 | 7.1019 | -1.2823 | 28.2901 | 3.5457 | 141.6667 | 145.2123 | 230.5391 | 1
168 | 8 | 49 | 238 |  | 0.40812 | 1.4976 | -0.60736 | 6.1126 | 8.1019 | -1.0205 | 37.3452 | 29.1985 | 198.3333 | 227.5318 | 361.2295 | 1
168 | 9 | 393 | 356 |  | 0.40812 | 1.4976 | -0.60736 | 6.1126 | 9.1019 | -0.75873 | 46.0104 | 301.6796 | 296.6667 | 598.3463 | 949.9346 | 1
168 | 10 | 444 | 284 |  | 0.40812 | 1.4976 | -0.60736 | 6.1126 | 10.1019 | -0.49693 | 53.5905 | 398.4875 | 236.6667 | 635.1541 | 1008.3707 | 1
168 | 11 | 553 | 300 |  | 0.40812 | 1.4976 | -0.60736 | 6.1126 | 11.1019 | -0.23513 | 58.9578 | 540.072 | 250 | 790.072 | 1254.3182 | 1
168 | 12 | 679 | 254 |  | 0.40812 | 1.4976 | -0.60736 | 6.1126 | 12.1019 | 0.026671 | 60.6804 | 678.7443 | 211.6667 | 890.411 | 1413.6164 | 1
168 | 13 | 733 | 205 |  | 0.40812 | 1.4976 | -0.60736 | 6.1126 | 13.1019 | 0.28847 | 58.1146 | 707.2945 | 170.8333 | 878.1278 | 1394.1157 | 1
168 | 14 | 724 | 192 |  | 0.40812 | 1.4976 | -0.60736 | 6.1126 | 14.1019 | 0.55027 | 52.1813 | 633.4342 | 160 | 793.4342 | 1259.6561 | 1
168 | 15 | 699 | 175 |  | 0.40812 | 1.4976 | -0.60736 | 6.1126 | 15.1019 | 0.81207 | 44.3051 | 514.249 | 145.8333 | 660.0824 | 1047.9467 | 1
168 | 16 | 637 | 163 |  | 0.40812 | 1.4976 | -0.60736 | 6.1126 | 16.1019 | 1.0739 | 35.5147 | 354.6615 | 135.8333 | 490.4948 | 778.7096 | 1
168 | 17 | 602 | 125 |  | 0.40812 | 1.4976 | -0.60736 | 6.1126 | 17.1019 | 1.3357 | 26.4404 | 210.899 | 104.1667 | 315.0656 | 500.1982 | 1
168 | 18 | 407 | 121 |  | 0.40812 | 1.4976 | -0.60736 | 6.1126 | 18.1019 | 1.5975 | 17.5049 | 53.0919 | 100.8333 | 153.9253 | 244.3717 | 1
168 | 19 | 206 | 81 |  | 0.40812 | 1.4976 | -0.60736 | 6.1126 | 19.1019 | 1.8593 | 9.0512 | 0 | 67.5 | 67.5 | 107.163 | 0
168 | 20 | 0 | 26 |  | 0.40812 | 1.4976 | -0.60736 | 6.1126 | 20.1019 | 2.1211 | 1.4118 | 0 | 21.6667 | 21.6667 | 34.398 | 0
168 | 21 | 0 | 1 |  | 0.40812 | 1.4976 | -0.60736 | 6.1126 | 21.1019 | 2.3829 | -5.0608 | 0 | 0.83333 | 0.83333 | 1.323 | 0
168 | 22 | 0 | 0 |  | 0.40812 | 1.4976 | -0.60736 | 6.1126 | 22.1019 | 2.6447 | -9.9938 | 0 | 0 | 0 | 0 | 0
168 | 23 | 0 | 0 |  | 0.40812 | 1.4976 | -0.60736 | 6.1126 | 23.1019 | 2.9065 | -13.0343 | 0 | 0 | 0 | 0 | 0
168 | 24 | 0 | 0 |  | 0.40812 | 1.4976 | -0.60736 | 6.1126 | 24.1019 | 3.1683 | -13.9248 | 0 | 0 | 0 | 0 | 0
169 | 1 | 0 | 0 |  | 0.4086 | 1.5149 | -0.81663 | 5.9034 | 1.0984 | -2.854 | -12.5642 | 0 | 0 | 0 | 0 | 0
169 | 2 | 0 | 0 |  | 0.4086 | 1.5149 | -0.81663 | 5.9034 | 2.0984 | -2.5922 | -9.1208 | 0 | 0 | 0 | 0 | 0
169 | 3 | 0 | 0 |  | 0.4086 | 1.5149 | -0.81663 | 5.9034 | 3.0984 | -2.3304 | -3.851 | 0 | 0 | 0 | 0 | 0
169 | 4 | 0 | 3 |  | 0.4086 | 1.5149 | -0.81663 | 5.9034 | 4.0984 | -2.0686 | 2.8833 | 0 | 2.5 | 2.5 | 3.969 | 0
169 | 5 | 0 | 35 |  | 0.4086 | 1.5149 | -0.81663 | 5.9034 | 5.0984 | -1.8068 | 10.7119 | 0 | 29.1667 | 29.1667 | 46.305 | 0
169 | 6 | 1 | 87 |  | 0.4086 | 1.5149 | -0.81663 | 5.9034 | 6.0984 | -1.545 | 19.2874 | 0.17501 | 72.5 | 72.675 | 115.3788 | 1
169 | 7 | 134 | 243 |  | 0.4086 | 1.5149 | -0.81663 | 5.9034 | 7.0984 | -1.2832 | 28.2791 | 52.7076 | 202.5 | 255.2076 | 405.1676 | 1
169 | 8 | 560 | 167 |  | 0.4086 | 1.5149 | -0.81663 | 5.9034 | 8.0984 | -1.0214 | 37.335 | 333.3714 | 139.1667 | 472.538 | 750.2014 | 1
169 | 9 | 90 | 288 |  | 0.4086 | 1.5149 | -0.81663 | 5.9034 | 9.0984 | -0.75964 | 46.0036 | 69.0429 | 240 | 309.0429 | 490.6364 | 1
169 | 10 | 61 | 370 |  | 0.4086 | 1.5149 | -0.81663 | 5.9034 | 10.0984 | -0.49784 | 53.5911 | 54.7256 | 308.3333 | 363.0589 | 576.3923 | 1
169 | 11 | 90 | 389 |  | 0.4086 | 1.5149 | -0.81663 | 5.9034 | 11.0984 | -0.23604 | 58.9712 | 87.8796 | 324.1667 | 412.0463 | 654.1647 | 1
169 | 12 | 418 | 364 |  | 0.4086 | 1.5149 | -0.81663 | 5.9034 | 12.0984 | 0.025758 | 60.7095 | 417.8486 | 303.3333 | 721.1819 | 1144.9484 | 1
169 | 13 | 127 | 375 |  | 0.4086 | 1.5149 | -0.81663 | 5.9034 | 13.0984 | 0.28756 | 58.1563 | 122.5743 | 312.5 | 435.0743 | 690.7239 | 1
169 | 14 | 89 | 382 |  | 0.4086 | 1.5149 | -0.81663 | 5.9034 | 14.0984 | 0.54936 | 52.2297 | 77.9046 | 318.3333 | 396.238 | 629.0674 | 1
169 | 15 | 17 | 239 |  | 0.4086 | 1.5149 | -0.81663 | 5.9034 | 15.0984 | 0.81116 | 44.3564 | 12.5171 | 199.1667 | 211.6838 | 336.0692 | 1
169 | 16 | 183 | 307 |  | 0.4086 | 1.5149 | -0.81663 | 5.9034 | 16.0984 | 1.073 | 35.567 | 102.0288 | 255.8333 | 357.8621 | 568.1419 | 1
169 | 17 | 46 | 221 |  | 0.4086 | 1.5149 | -0.81663 | 5.9034 | 17.0984 | 1.3348 | 26.4928 | 16.1557 | 184.1667 | 200.3224 | 318.0318 | 1
169 | 18 | 14 | 149 |  | 0.4086 | 1.5149 | -0.81663 | 5.9034 | 18.0984 | 1.5966 | 17.5567 | 1.8395 | 124.1667 | 126.0062 | 200.0474 | 1
169 | 19 | 0 | 72 |  | 0.4086 | 1.5149 | -0.81663 | 5.9034 | 19.0984 | 1.8584 | 9.1018 | 0 | 60 | 60 | 95.256 | 0
169 | 20 | 0 | 15 |  | 0.4086 | 1.5149 | -0.81663 | 5.9034 | 20.0984 | 2.1202 | 1.4602 | 0 | 12.5 | 12.5 | 19.845 | 0
169 | 21 | 0 | 0 |  | 0.4086 | 1.5149 | -0.81663 | 5.9034 | 21.0984 | 2.382 | -5.0156 | 0 | 0 | 0 | 0 | 0
169 | 22 | 0 | 0 |  | 0.4086 | 1.5149 | -0.81663 | 5.9034 | 22.0984 | 2.6438 | -9.9533 | 0 | 0 | 0 | 0 | 0
169 | 23 | 0 | 0 |  | 0.4086 | 1.5149 | -0.81663 | 5.9034 | 23.0984 | 2.9056 | -13 | 0 | 0 | 0 | 0 | 0
169 | 24 | 0 | 0 |  | 0.4086 | 1.5149 | -0.81663 | 5.9034 | 24.0984 | 3.1674 | -13.898 | 0 | 0 | 0 | 0 | 0
170 | 1 | 0 | 0 |  | 0.40895 | 1.5321 | -1.0266 | 5.6934 | 1.0949 | -2.855 | -12.5528 | 0 | 0 | 0 | 0 | 0
170 | 2 | 0 | 0 |  | 0.40895 | 1.5321 | -1.0266 | 5.6934 | 2.0949 | -2.5932 | -9.1171 | 0 | 0 | 0 | 0 | 0
170 | 3 | 0 | 0 |  | 0.40895 | 1.5321 | -1.0266 | 5.6934 | 3.0949 | -2.3314 | -3.8541 | 0 | 0 | 0 | 0 | 0
170 | 4 | 0 | 2 |  | 0.40895 | 1.5321 | -1.0266 | 5.6934 | 4.0949 | -2.0696 | 2.8747 | 0 | 1.6667 | 1.6667 | 2.646 | 0
170 | 5 | 0 | 23 |  | 0.40895 | 1.5321 | -1.0266 | 5.6934 | 5.0949 | -1.8078 | 10.6992 | 0 | 19.1667 | 19.1667 | 30.429 | 0
170 | 6 | 0 | 54 |  | 0.40895 | 1.5321 | -1.0266 | 5.6934 | 6.0949 | -1.546 | 19.272 | 0 | 45 | 45 | 71.442 | 1
170 | 7 | 0 | 108 |  | 0.40895 | 1.5321 | -1.0266 | 5.6934 | 7.0949 | -1.2842 | 28.2625 | 0 | 90 | 90 | 142.884 | 1
170 | 8 | 1 | 164 |  | 0.40895 | 1.5321 | -1.0266 | 5.6934 | 8.0949 | -1.0224 | 37.319 | 0.5947 | 136.6667 | 137.2614 | 217.9161 | 1
170 | 9 | 5 | 214 |  | 0.40895 | 1.5321 | -1.0266 | 5.6934 | 9.0949 | -0.76056 | 45.9908 | 3.8332 | 178.3333 | 182.1665 | 289.2076 | 1
170 | 10 | 7 | 255 |  | 0.40895 | 1.5321 | -1.0266 | 5.6934 | 10.0949 | -0.49876 | 53.5853 | 6.2775 | 212.5 | 218.7775 | 347.3311 | 1
170 | 11 | 11 | 280 |  | 0.40895 | 1.5321 | -1.0266 | 5.6934 | 11.0949 | -0.23696 | 58.9773 | 10.7388 | 233.3333 | 244.0722 | 387.489 | 1
170 | 12 | 12 | 294 |  | 0.40895 | 1.5321 | -1.0266 | 5.6934 | 12.0949 | 0.024842 | 60.7312 | 11.9958 | 245 | 256.9958 | 408.0066 | 1
170 | 13 | 4 | 365 |  | 0.40895 | 1.5321 | -1.0266 | 5.6934 | 13.0949 | 0.28664 | 58.1911 | 3.8615 | 304.1667 | 308.0282 | 489.0255 | 1
170 | 14 | 6 | 399 |  | 0.40895 | 1.5321 | -1.0266 | 5.6934 | 14.0949 | 0.54844 | 52.2719 | 5.2545 | 332.5 | 337.7545 | 536.2191 | 1
170 | 15 | 69 | 352 |  | 0.40895 | 1.5321 | -1.0266 | 5.6934 | 15.0949 | 0.81024 | 44.402 | 50.8461 | 293.3333 | 344.1795 | 546.4193 | 1
170 | 16 | 68 | 287 |  | 0.40895 | 1.5321 | -1.0266 | 5.6934 | 16.0949 | 1.072 | 35.6139 | 37.963 | 239.1667 | 277.1296 | 439.971 | 1
170 | 17 | 33 | 228 |  | 0.40895 | 1.5321 | -1.0266 | 5.6934 | 17.0949 | 1.3338 | 26.5398 | 11.618 | 190 | 201.618 | 320.0887 | 1
170 | 18 | 0 | 97 |  | 0.40895 | 1.5321 | -1.0266 | 5.6934 | 18.0949 | 1.5956 | 17.6029 | 0 | 80.8333 | 80.8333 | 128.331 | 1
170 | 19 | 0 | 45 |  | 0.40895 | 1.5321 | -1.0266 | 5.6934 | 19.0949 | 1.8574 | 9.1465 | 0 | 37.5 | 37.5 | 59.535 | 0
170 | 20 | 0 | 9 |  | 0.40895 | 1.5321 | -1.0266 | 5.6934 | 20.0949 | 2.1192 | 1.5025 | 0 | 7.5 | 7.5 | 11.907 | 0
170 | 21 | 0 | 0 |  | 0.40895 | 1.5321 | -1.0266 | 5.6934 | 21.0949 | 2.381 | -4.977 | 0 | 0 | 0 | 0 | 0
170 | 22 | 0 | 0 |  | 0.40895 | 1.5321 | -1.0266 | 5.6934 | 22.0949 | 2.6428 | -9.9198 | 0 | 0 | 0 | 0 | 0
170 | 23 | 0 | 0 |  | 0.40895 | 1.5321 | -1.0266 | 5.6934 | 23.0949 | 2.9046 | -12.973 | 0 | 0 | 0 | 0 | 0
170 | 24 | 0 | 0 |  | 0.40895 | 1.5321 | -1.0266 | 5.6934 | 24.0949 | 3.1664 | -13.8785 | 0 | 0 | 0 | 0 | 0
171 | 1 | 0 | 0 |  | 0.40918 | 1.5493 | -1.237 | 5.483 | 1.0914 | -2.8559 | -12.5486 | 0 | 0 | 0 | 0 | 0
171 | 2 | 0 | 0 |  | 0.40918 | 1.5493 | -1.237 | 5.483 | 2.0914 | -2.5941 | -9.1203 | 0 | 0 | 0 | 0 | 0
171 | 3 | 0 | 0 |  | 0.40918 | 1.5493 | -1.237 | 5.483 | 3.0914 | -2.3323 | -3.8637 | 0 | 0 | 0 | 0 | 0
171 | 4 | 0 | 2 |  | 0.40918 | 1.5493 | -1.237 | 5.483 | 4.0914 | -2.0705 | 2.8599 | 0 | 1.6667 | 1.6667 | 2.646 | 0
171 | 5 | 4 | 37 |  | 0.40918 | 1.5493 | -1.237 | 5.483 | 5.0914 | -1.8087 | 10.6806 | 0 | 30.8333 | 30.8333 | 48.951 | 0
171 | 6 | 193 | 103 |  | 0.40918 | 1.5493 | -1.237 | 5.483 | 6.0914 | -1.5469 | 19.2509 | 33.5158 | 85.8333 | 119.3491 | 189.4786 | 1
171 | 7 | 400 | 135 |  | 0.40918 | 1.5493 | -1.237 | 5.483 | 7.0914 | -1.2851 | 28.2403 | 156.7982 | 112.5 | 269.2982 | 427.5378 | 1
171 | 8 | 585 | 149 |  | 0.40918 | 1.5493 | -1.237 | 5.483 | 8.0914 | -1.0233 | 37.2974 | 347.5337 | 124.1667 | 471.7004 | 748.8716 | 1
171 | 9 | 536 | 213 |  | 0.40918 | 1.5493 | -1.237 | 5.483 | 9.0914 | -0.76147 | 45.9721 | 410.6421 | 177.5 | 588.1421 | 933.7343 | 1
171 | 10 | 406 | 312 |  | 0.40918 | 1.5493 | -1.237 | 5.483 | 10.0914 | -0.49967 | 53.5729 | 363.9449 | 260 | 623.9449 | 990.575 | 1
171 | 11 | 436 | 332 |  | 0.40918 | 1.5493 | -1.237 | 5.483 | 11.0914 | -0.23788 | 58.9764 | 425.5683 | 276.6667 | 702.235 | 1114.8683 | 1
171 | 12 | 110 | 396 |  | 0.40918 | 1.5493 | -1.237 | 5.483 | 12.0914 | 0.023924 | 60.7456 | 109.9636 | 330 | 439.9636 | 698.4862 | 1
171 | 13 | 16 | 291 |  | 0.40918 | 1.5493 | -1.237 | 5.483 | 13.0914 | 0.28572 | 58.219 | 15.4495 | 242.5 | 257.9495 | 409.5206 | 1
171 | 14 | 5 | 283 |  | 0.40918 | 1.5493 | -1.237 | 5.483 | 14.0914 | 0.54752 | 52.3079 | 4.3808 | 235.8333 | 240.2142 | 381.364 | 1
171 | 15 | 14 | 244 |  | 0.40918 | 1.5493 | -1.237 | 5.483 | 15.0914 | 0.80932 | 44.4418 | 10.3248 | 203.3333 | 213.6581 | 339.2037 | 1
171 | 16 | 9 | 203 |  | 0.40918 | 1.5493 | -1.237 | 5.483 | 16.0914 | 1.0711 | 35.6552 | 5.031 | 169.1667 | 174.1977 | 276.5562 | 1
171 | 17 | 1 | 154 |  | 0.40918 | 1.5493 | -1.237 | 5.483 | 17.0914 | 1.3329 | 26.5812 | 0.35288 | 128.3333 | 128.6862 | 204.3022 | 1
171 | 18 | 0 | 97 |  | 0.40918 | 1.5493 | -1.237 | 5.483 | 18.0914 | 1.5947 | 17.6436 | 0 | 80.8333 | 80.8333 | 128.331 | 1
171 | 19 | 0 | 45 |  | 0.40918 | 1.5493 | -1.237 | 5.483 | 19.0914 | 1.8565 | 9.1854 | 0 | 37.5 | 37.5 | 59.535 | 0
171 | 20 | 0 | 15 |  | 0.40918 | 1.5493 | -1.237 | 5.483 | 20.0914 | 2.1183 | 1.5385 | 0 | 12.5 | 12.5 | 19.845 | 0
171 | 21 | 0 | 0 |  | 0.40918 | 1.5493 | -1.237 | 5.483 | 21.0914 | 2.3801 | -4.9451 | 0 | 0 | 0 | 0 | 0
171 | 22 | 0 | 0 |  | 0.40918 | 1.5493 | -1.237 | 5.483 | 22.0914 | 2.6419 | -9.8933 | 0 | 0 | 0 | 0 | 0
171 | 23 | 0 | 0 |  | 0.40918 | 1.5493 | -1.237 | 5.483 | 23.0914 | 2.9037 | -12.9532 | 0 | 0 | 0 | 0 | 0
171 | 24 | 0 | 0 |  | 0.40918 | 1.5493 | -1.237 | 5.483 | 24.0914 | 3.1655 | -13.8664 | 0 | 0 | 0 | 0 | 0
172 | 1 | 0 | 0 |  | 0.40928 | 1.5665 | -1.4474 | 5.2726 | 1.0879 | -2.8568 | -12.5516 | 0 | 0 | 0 | 0 | 0
172 | 2 | 0 | 0 |  | 0.40928 | 1.5665 | -1.4474 | 5.2726 | 2.0879 | -2.595 | -9.1305 | 0 | 0 | 0 | 0 | 0
172 | 3 | 0 | 0 |  | 0.40928 | 1.5665 | -1.4474 | 5.2726 | 3.0879 | -2.3332 | -3.88 | 0 | 0 | 0 | 0 | 0
172 | 4 | 0 | 3 |  | 0.40928 | 1.5665 | -1.4474 | 5.2726 | 4.0879 | -2.0714 | 2.8389 | 0 | 2.5 | 2.5 | 3.969 | 0
172 | 5 | 0 | 29 |  | 0.40928 | 1.5665 | -1.4474 | 5.2726 | 5.0879 | -1.8096 | 10.6561 | 0 | 24.1667 | 24.1667 | 38.367 | 0
172 | 6 | 57 | 96 |  | 0.40928 | 1.5665 | -1.4474 | 5.2726 | 6.0879 | -1.5478 | 19.2242 | 9.8561 | 80 | 89.8561 | 142.6555 | 1
172 | 7 | 378 | 154 |  | 0.40928 | 1.5665 | -1.4474 | 5.2726 | 7.0879 | -1.286 | 28.2126 | 147.9016 | 128.3333 | 276.2349 | 438.5505 | 1
172 | 8 | 399 | 214 |  | 0.40928 | 1.5665 | -1.4474 | 5.2726 | 8.0879 | -1.0242 | 37.2702 | 236.7773 | 178.3333 | 415.1106 | 659.0296 | 1
172 | 9 | 643 | 188 |  | 0.40928 | 1.5665 | -1.4474 | 5.2726 | 9.0879 | -0.76239 | 45.9474 | 492.2778 | 156.6667 | 648.9444 | 1030.2642 | 1
172 | 10 | 260 | 337 |  | 0.40928 | 1.5665 | -1.4474 | 5.2726 | 10.0879 | -0.50059 | 53.5541 | 232.9721 | 280.8333 | 513.8054 | 815.7175 | 1
172 | 11 | 612 | 291 |  | 0.40928 | 1.5665 | -1.4474 | 5.2726 | 11.0879 | -0.23879 | 58.9683 | 597.2449 | 242.5 | 839.7449 | 1333.179 | 1
172 | 12 | 466 | 327 |  | 0.40928 | 1.5665 | -1.4474 | 5.2726 | 12.0879 | 0.023006 | 60.7525 | 465.8536 | 272.5 | 738.3536 | 1172.2101 | 1
172 | 13 | 440 | 348 |  | 0.40928 | 1.5665 | -1.4474 | 5.2726 | 13.0879 | 0.28481 | 58.2399 | 424.9568 | 290 | 714.9568 | 1135.0654 | 1
172 | 14 | 555 | 293 |  | 0.40928 | 1.5665 | -1.4474 | 5.2726 | 14.0879 | 0.5466 | 52.3375 | 486.4988 | 244.1667 | 730.6655 | 1160.0045 | 1
172 | 15 | 96 | 334 |  | 0.40928 | 1.5665 | -1.4474 | 5.2726 | 15.0879 | 0.8084 | 44.4758 | 70.8535 | 278.3333 | 349.1869 | 554.3691 | 1
172 | 16 | 83 | 279 |  | 0.40928 | 1.5665 | -1.4474 | 5.2726 | 16.0879 | 1.0702 | 35.691 | 46.4551 | 232.5 | 278.9551 | 442.8691 | 1
172 | 17 | 433 | 200 |  | 0.40928 | 1.5665 | -1.4474 | 5.2726 | 17.0879 | 1.332 | 26.6172 | 153.1334 | 166.6667 | 319.8001 | 507.7146 | 1
172 | 18 | 429 | 113 |  | 0.40928 | 1.5665 | -1.4474 | 5.2726 | 18.0879 | 1.5938 | 17.6785 | 57.4728 | 94.1667 | 151.6394 | 240.7428 | 1
172 | 19 | 160 | 91 |  | 0.40928 | 1.5665 | -1.4474 | 5.2726 | 19.0879 | 1.8556 | 9.2183 | 0 | 75.8333 | 75.8333 | 120.393 | 0
172 | 20 | 0 | 25 |  | 0.40928 | 1.5665 | -1.4474 | 5.2726 | 20.0879 | 2.1174 | 1.5682 | 0 | 20.8333 | 20.8333 | 33.075 | 0
172 | 21 | 0 | 1 |  | 0.40928 | 1.5665 | -1.4474 | 5.2726 | 21.0879 | 2.3792 | -4.9198 | 0 | 0.83333 | 0.83333 | 1.323 | 0
172 | 22 | 0 | 0 |  | 0.40928 | 1.5665 | -1.4474 | 5.2726 | 22.0879 | 2.641 | -9.8737 | 0 | 0 | 0 | 0 | 0
172 | 23 | 0 | 0 |  | 0.40928 | 1.5665 | -1.4474 | 5.2726 | 23.0879 | 2.9028 | -12.9406 | 0 | 0 | 0 | 0 | 0
172 | 24 | 0 | 0 |  | 0.40928 | 1.5665 | -1.4474 | 5.2726 | 24.0879 | 3.1646 | -13.8615 | 0 | 0 | 0 | 0 | 0
173 | 1 | 0 | 0 |  | 0.40924 | 1.5837 | -1.6575 | 5.0625 | 1.0844 | -2.8577 | -12.5618 | 0 | 0 | 0 | 0 | 0
173 | 2 | 0 | 0 |  | 0.40924 | 1.5837 | -1.6575 | 5.0625 | 2.0844 | -2.5959 | -9.1476 | 0 | 0 | 0 | 0 | 0
173 | 3 | 0 | 0 |  | 0.40924 | 1.5837 | -1.6575 | 5.0625 | 3.0844 | -2.3341 | -3.9028 | 0 | 0 | 0 | 0 | 0
173 | 4 | 0 | 2 |  | 0.40924 | 1.5837 | -1.6575 | 5.0625 | 4.0844 | -2.0723 | 2.8117 | 0 | 1.6667 | 1.6667 | 2.646 | 0
173 | 5 | 0 | 23 |  | 0.40924 | 1.5837 | -1.6575 | 5.0625 | 5.0844 | -1.8105 | 10.6257 | 0 | 19.1667 | 19.1667 | 30.429 | 0
173 | 6 | 1 | 85 |  | 0.40924 | 1.5837 | -1.6575 | 5.0625 | 6.0844 | -1.5487 | 19.1918 | 0.17213 | 70.8333 | 71.0055 | 112.7283 | 1
173 | 7 | 9 | 168 |  | 0.40924 | 1.5837 | -1.6575 | 5.0625 | 7.0844 | -1.2869 | 28.1794 | 3.5147 | 140 | 143.5147 | 227.8439 | 1
173 | 8 | 171 | 244 |  | 0.40924 | 1.5837 | -1.6575 | 5.0625 | 8.0844 | -1.0251 | 37.2374 | 101.3617 | 203.3333 | 304.695 | 483.7339 | 1
173 | 9 | 228 | 293 |  | 0.40924 | 1.5837 | -1.6575 | 5.0625 | 9.0844 | -0.76331 | 45.9169 | 174.4329 | 244.1667 | 418.5995 | 664.5686 | 1
173 | 10 | 81 | 354 |  | 0.40924 | 1.5837 | -1.6575 | 5.0625 | 10.0844 | -0.50151 | 53.5289 | 72.5495 | 295 | 367.5495 | 583.5216 | 1
173 | 11 | 259 | 381 |  | 0.40924 | 1.5837 | -1.6575 | 5.0625 | 11.0844 | -0.23971 | 58.9531 | 252.708 | 317.5 | 570.208 | 905.2623 | 1
173 | 12 | 104 | 397 |  | 0.40924 | 1.5837 | -1.6575 | 5.0625 | 12.0844 | 0.022089 | 60.752 | 103.9692 | 330.8333 | 434.8025 | 690.2925 | 1
173 | 13 | 63 | 432 |  | 0.40924 | 1.5837 | -1.6575 | 5.0625 | 13.0844 | 0.28389 | 58.2537 | 60.8598 | 360 | 420.8598 | 668.157 | 1
173 | 14 | 62 | 406 |  | 0.40924 | 1.5837 | -1.6575 | 5.0625 | 14.0844 | 0.54569 | 52.3608 | 54.3725 | 338.3333 | 392.7059 | 623.4598 | 1
173 | 15 | 217 | 358 |  | 0.40924 | 1.5837 | -1.6575 | 5.0625 | 15.0844 | 0.80749 | 44.5039 | 160.2795 | 298.3333 | 458.6128 | 728.0937 | 1
173 | 16 | 350 | 270 |  | 0.40924 | 1.5837 | -1.6575 | 5.0625 | 16.0844 | 1.0693 | 35.7211 | 196.1312 | 225 | 421.1312 | 668.5879 | 1
173 | 17 | 332 | 196 |  | 0.40924 | 1.5837 | -1.6575 | 5.0625 | 17.0844 | 1.3311 | 26.6475 | 117.6615 | 163.3333 | 280.9948 | 446.1073 | 1
173 | 18 | 394 | 119 |  | 0.40924 | 1.5837 | -1.6575 | 5.0625 | 18.0844 | 1.5929 | 17.7077 | 53.0849 | 99.1667 | 152.2515 | 241.7145 | 1
173 | 19 | 192 | 84 |  | 0.40924 | 1.5837 | -1.6575 | 5.0625 | 19.0844 | 1.8547 | 9.2452 | 0 | 70 | 70 | 111.132 | 0
173 | 20 | 0 | 27 |  | 0.40924 | 1.5837 | -1.6575 | 5.0625 | 20.0844 | 2.1165 | 1.5916 | 0 | 22.5 | 22.5 | 35.721 | 0
173 | 21 | 0 | 0 |  | 0.40924 | 1.5837 | -1.6575 | 5.0625 | 21.0844 | 2.3783 | -4.9012 | 0 | 0 | 0 | 0 | 0
173 | 22 | 0 | 0 |  | 0.40924 | 1.5837 | -1.6575 | 5.0625 | 22.0844 | 2.6401 | -9.8613 | 0 | 0 | 0 | 0 | 0
173 | 23 | 0 | 0 |  | 0.40924 | 1.5837 | -1.6575 | 5.0625 | 23.0844 | 2.9019 | -12.9353 | 0 | 0 | 0 | 0 | 0
173 | 24 | 0 | 0 |  | 0.40924 | 1.5837 | -1.6575 | 5.0625 | 24.0844 | 3.1637 | -13.8641 | 0 | 0 | 0 | 0 | 0
174 | 1 | 0 | 0 |  | 0.40908 | 1.6009 | -1.8668 | 4.8532 | 1.0809 | -2.8586 | -12.5792 | 0 | 0 | 0 | 0 | 0
174 | 2 | 0 | 0 |  | 0.40908 | 1.6009 | -1.8668 | 4.8532 | 2.0809 | -2.5968 | -9.1716 | 0 | 0 | 0 | 0 | 0
174 | 3 | 0 | 0 |  | 0.40908 | 1.6009 | -1.8668 | 4.8532 | 3.0809 | -2.335 | -3.9322 | 0 | 0 | 0 | 0 | 0
174 | 4 | 0 | 1 |  | 0.40908 | 1.6009 | -1.8668 | 4.8532 | 4.0809 | -2.0732 | 2.7783 | 0 | 0.83333 | 0.83333 | 1.323 | 0
174 | 5 | 0 | 22 |  | 0.40908 | 1.6009 | -1.8668 | 4.8532 | 5.0809 | -1.8114 | 10.5896 | 0 | 18.3333 | 18.3333 | 29.106 | 0
174 | 6 | 58 | 95 |  | 0.40908 | 1.6009 | -1.8668 | 4.8532 | 6.0809 | -1.5496 | 19.154 | 9.9353 | 79.1667 | 89.1019 | 141.4583 | 1
174 | 7 | 119 | 172 |  | 0.40908 | 1.6009 | -1.8668 | 4.8532 | 7.0809 | -1.2878 | 28.1408 | 46.3789 | 143.3333 | 189.7122 | 301.1871 | 1
174 | 8 | 61 | 229 |  | 0.40908 | 1.6009 | -1.8668 | 4.8532 | 8.0809 | -1.026 | 37.1992 | 36.1163 | 190.8333 | 226.9497 | 360.3053 | 1
174 | 9 | 85 | 290 |  | 0.40908 | 1.6009 | -1.8668 | 4.8532 | 9.0809 | -0.76422 | 45.8807 | 64.9831 | 241.6667 | 306.6498 | 486.8372 | 1
174 | 10 | 90 | 348 |  | 0.40908 | 1.6009 | -1.8668 | 4.8532 | 10.0809 | -0.50242 | 53.4973 | 80.5766 | 290 | 370.5766 | 588.3274 | 1
174 | 11 | 62 | 413 |  | 0.40908 | 1.6009 | -1.8668 | 4.8532 | 11.0809 | -0.24062 | 58.9308 | 60.4824 | 344.1667 | 404.6491 | 642.4209 | 1
174 | 12 | 16 | 293 |  | 0.40908 | 1.6009 | -1.8668 | 4.8532 | 12.0809 | 0.021176 | 60.7441 | 15.9956 | 244.1667 | 260.1622 | 413.0336 | 1
174 | 13 | 5 | 301 |  | 0.40908 | 1.6009 | -1.8668 | 4.8532 | 13.0809 | 0.28298 | 58.2604 | 4.8312 | 250.8333 | 255.6646 | 405.893 | 1
174 | 14 | 5 | 283 |  | 0.40908 | 1.6009 | -1.8668 | 4.8532 | 14.0809 | 0.54477 | 52.3776 | 4.3869 | 235.8333 | 240.2202 | 381.3736 | 1
174 | 15 | 96 | 334 |  | 0.40908 | 1.6009 | -1.8668 | 4.8532 | 15.0809 | 0.80657 | 44.5262 | 70.9591 | 278.3333 | 349.2925 | 554.5367 | 1
174 | 16 | 205 | 296 |  | 0.40908 | 1.6009 | -1.8668 | 4.8532 | 16.0809 | 1.0684 | 35.7456 | 115.01 | 246.6667 | 361.6766 | 574.1978 | 1
174 | 17 | 130 | 251 |  | 0.40908 | 1.6009 | -1.8668 | 4.8532 | 17.0809 | 1.3302 | 26.6723 | 46.1643 | 209.1667 | 255.331 | 405.3635 | 1
174 | 18 | 303 | 141 |  | 0.40908 | 1.6009 | -1.8668 | 4.8532 | 18.0809 | 1.592 | 17.7312 | 41.0408 | 117.5 | 158.5408 | 251.6993 | 1
174 | 19 | 119 | 92 |  | 0.40908 | 1.6009 | -1.8668 | 4.8532 | 19.0809 | 1.8538 | 9.2661 | 0 | 76.6667 | 76.6667 | 121.716 | 0
174 | 20 | 0 | 28 |  | 0.40908 | 1.6009 | -1.8668 | 4.8532 | 20.0809 | 2.1156 | 1.6086 | 0 | 23.3333 | 23.3333 | 37.044 | 0
174 | 21 | 0 | 1 |  | 0.40908 | 1.6009 | -1.8668 | 4.8532 | 21.0809 | 2.3774 | -4.8894 | 0 | 0.83333 | 0.83333 | 1.323 | 0
174 | 22 | 0 | 0 |  | 0.40908 | 1.6009 | -1.8668 | 4.8532 | 22.0809 | 2.6392 | -9.8558 | 0 | 0 | 0 | 0 | 0
174 | 23 | 0 | 0 |  | 0.40908 | 1.6009 | -1.8668 | 4.8532 | 23.0809 | 2.901 | -12.9373 | 0 | 0 | 0 | 0 | 0
174 | 24 | 0 | 0 |  | 0.40908 | 1.6009 | -1.8668 | 4.8532 | 24.0809 | 3.1628 | -13.8739 | 0 | 0 | 0 | 0 | 0
175 | 1 | 0 | 0 |  | 0.40879 | 1.6181 | -2.0751 | 4.6449 | 1.0774 | -2.8595 | -12.6038 | 0 | 0 | 0 | 0 | 0
175 | 2 | 0 | 0 |  | 0.40879 | 1.6181 | -2.0751 | 4.6449 | 2.0774 | -2.5977 | -9.2025 | 0 | 0 | 0 | 0 | 0
175 | 3 | 0 | 0 |  | 0.40879 | 1.6181 | -2.0751 | 4.6449 | 3.0774 | -2.3359 | -3.968 | 0 | 0 | 0 | 0 | 0
175 | 4 | 0 | 1 |  | 0.40879 | 1.6181 | -2.0751 | 4.6449 | 4.0774 | -2.0741 | 2.7389 | 0 | 0.83333 | 0.83333 | 1.323 | 0
175 | 5 | 0 | 22 |  | 0.40879 | 1.6181 | -2.0751 | 4.6449 | 5.0774 | -1.8123 | 10.5477 | 0 | 18.3333 | 18.3333 | 29.106 | 0
175 | 6 | 58 | 95 |  | 0.40879 | 1.6181 | -2.0751 | 4.6449 | 6.0774 | -1.5505 | 19.1106 | 9.8849 | 79.1667 | 89.0515 | 141.3782 | 1
175 | 7 | 382 | 153 |  | 0.40879 | 1.6181 | -2.0751 | 4.6449 | 7.0774 | -1.2887 | 28.0968 | 148.5702 | 127.5 | 276.0702 | 438.289 | 1
175 | 8 | 68 | 227 |  | 0.40879 | 1.6181 | -2.0751 | 4.6449 | 8.0774 | -1.0269 | 37.1555 | 40.2129 | 189.1667 | 229.3795 | 364.163 | 1
175 | 9 | 86 | 291 |  | 0.40879 | 1.6181 | -2.0751 | 4.6449 | 9.0774 | -0.76513 | 45.8387 | 65.6996 | 242.5 | 308.1996 | 489.2977 | 1
175 | 10 | 380 | 428 |  | 0.40879 | 1.6181 | -2.0751 | 4.6449 | 10.0774 | -0.50333 | 53.4595 | 340.0679 | 356.6667 | 696.7346 | 1106.1358 | 1
175 | 11 | 293 | 354 |  | 0.40879 | 1.6181 | -2.0751 | 4.6449 | 11.0774 | -0.24153 | 58.9015 | 285.7747 | 295 | 580.7747 | 922.0379 | 1
175 | 12 | 172 | 480 |  | 0.40879 | 1.6181 | -2.0751 | 4.6449 | 12.0774 | 0.020267 | 60.7288 | 171.9557 | 400 | 571.9557 | 908.0368 | 1
175 | 13 | 171 | 478 |  | 0.40879 | 1.6181 | -2.0751 | 4.6449 | 13.0774 | 0.28207 | 58.2601 | 165.2644 | 398.3333 | 563.5977 | 894.7678 | 1
175 | 14 | 464 | 304 |  | 0.40879 | 1.6181 | -2.0751 | 4.6449 | 14.0774 | 0.54387 | 52.388 | 407.2795 | 253.3333 | 660.6128 | 1048.7889 | 1
175 | 15 | 437 | 280 |  | 0.40879 | 1.6181 | -2.0751 | 4.6449 | 15.0774 | 0.80567 | 44.5424 | 323.2419 | 233.3333 | 556.5752 | 883.6188 | 1
175 | 16 | 208 | 296 |  | 0.40879 | 1.6181 | -2.0751 | 4.6449 | 16.0774 | 1.0675 | 35.7644 | 116.8226 | 246.6667 | 363.4893 | 577.0756 | 1
175 | 17 | 48 | 224 |  | 0.40879 | 1.6181 | -2.0751 | 4.6449 | 17.0774 | 1.3293 | 26.6913 | 17.0775 | 186.6667 | 203.7441 | 323.4642 | 1
175 | 18 | 15 | 151 |  | 0.40879 | 1.6181 | -2.0751 | 4.6449 | 18.0774 | 1.5911 | 17.7488 | 2.0417 | 125.8333 | 127.875 | 203.0144 | 1
175 | 19 | 0 | 73 |  | 0.40879 | 1.6181 | -2.0751 | 4.6449 | 19.0774 | 1.8529 | 9.2809 | 0 | 60.8333 | 60.8333 | 96.579 | 0
175 | 20 | 0 | 15 |  | 0.40879 | 1.6181 | -2.0751 | 4.6449 | 20.0774 | 2.1147 | 1.6192 | 0 | 12.5 | 12.5 | 19.845 | 0
175 | 21 | 0 | 1 |  | 0.40879 | 1.6181 | -2.0751 | 4.6449 | 21.0774 | 2.3765 | -4.8843 | 0 | 0.83333 | 0.83333 | 1.323 | 0
175 | 22 | 0 | 0 |  | 0.40879 | 1.6181 | -2.0751 | 4.6449 | 22.0774 | 2.6383 | -9.8575 | 0 | 0 | 0 | 0 | 0
175 | 23 | 0 | 0 |  | 0.40879 | 1.6181 | -2.0751 | 4.6449 | 23.0774 | 2.9001 | -12.9466 | 0 | 0 | 0 | 0 | 0
175 | 24 | 0 | 0 |  | 0.40879 | 1.6181 | -2.0751 | 4.6449 | 24.0774 | 3.1619 | -13.8911 | 0 | 0 | 0 | 0 | 0
176 | 1 | 0 | 0 |  | 0.40838 | 1.6353 | -2.2819 | 4.4381 | 1.074 | -2.8604 | -12.6355 | 0 | 0 | 0 | 0 | 0
176 | 2 | 0 | 0 |  | 0.40838 | 1.6353 | -2.2819 | 4.4381 | 2.074 | -2.5986 | -9.2402 | 0 | 0 | 0 | 0 | 0
176 | 3 | 0 | 0 |  | 0.40838 | 1.6353 | -2.2819 | 4.4381 | 3.074 | -2.3368 | -4.0103 | 0 | 0 | 0 | 0 | 0
176 | 4 | 0 | 1 |  | 0.40838 | 1.6353 | -2.2819 | 4.4381 | 4.074 | -2.075 | 2.6934 | 0 | 0.83333 | 0.83333 | 1.323 | 0
176 | 5 | 0 | 14 |  | 0.40838 | 1.6353 | -2.2819 | 4.4381 | 5.074 | -1.8132 | 10.5002 | 0 | 11.6667 | 11.6667 | 18.522 | 0
176 | 6 | 0 | 53 |  | 0.40838 | 1.6353 | -2.2819 | 4.4381 | 6.074 | -1.5514 | 19.0618 | 0 | 44.1667 | 44.1667 | 70.119 | 1
176 | 7 | 0 | 106 |  | 0.40838 | 1.6353 | -2.2819 | 4.4381 | 7.074 | -1.2896 | 28.0475 | 0 | 88.3333 | 88.3333 | 140.238 | 1
176 | 8 | 1 | 163 |  | 0.40838 | 1.6353 | -2.2819 | 4.4381 | 8.074 | -1.0278 | 37.1065 | 0.59064 | 135.8333 | 136.424 | 216.5867 | 1
176 | 9 | 10 | 210 |  | 0.40838 | 1.6353 | -2.2819 | 4.4381 | 9.074 | -0.76603 | 45.791 | 7.6338 | 175 | 182.6338 | 289.9495 | 1
176 | 10 | 14 | 249 |  | 0.40838 | 1.6353 | -2.2819 | 4.4381 | 10.074 | -0.50423 | 53.4153 | 12.5235 | 207.5 | 220.0235 | 349.3092 | 1
176 | 11 | 5 | 286 |  | 0.40838 | 1.6353 | -2.2819 | 4.4381 | 11.074 | -0.24243 | 58.8652 | 4.8758 | 238.3333 | 243.2091 | 386.1188 | 1
176 | 12 | 12 | 295 |  | 0.40838 | 1.6353 | -2.2819 | 4.4381 | 12.074 | 0.019365 | 60.706 | 11.9972 | 245.8333 | 257.8305 | 409.3317 | 1
176 | 13 | 12 | 293 |  | 0.40838 | 1.6353 | -2.2819 | 4.4381 | 13.074 | 0.28116 | 58.2526 | 11.6 | 244.1667 | 255.7667 | 406.0552 | 1
176 | 14 | 11 | 277 |  | 0.40838 | 1.6353 | -2.2819 | 4.4381 | 14.074 | 0.54296 | 52.3918 | 9.6595 | 230.8333 | 240.4928 | 381.8064 | 1
176 | 15 | 7 | 248 |  | 0.40838 | 1.6353 | -2.2819 | 4.4381 | 15.074 | 0.80476 | 44.5526 | 5.1814 | 206.6667 | 211.848 | 336.3299 | 1
176 | 16 | 5 | 205 |  | 0.40838 | 1.6353 | -2.2819 | 4.4381 | 16.074 | 1.0666 | 35.7773 | 2.8112 | 170.8333 | 173.6445 | 275.6781 | 1
176 | 17 | 0 | 155 |  | 0.40838 | 1.6353 | -2.2819 | 4.4381 | 17.074 | 1.3284 | 26.7045 | 0 | 129.1667 | 129.1667 | 205.065 | 1
176 | 18 | 0 | 98 |  | 0.40838 | 1.6353 | -2.2819 | 4.4381 | 18.074 | 1.5902 | 17.7606 | 0 | 81.6667 | 81.6667 | 129.654 | 1
176 | 19 | 0 | 46 |  | 0.40838 | 1.6353 | -2.2819 | 4.4381 | 19.074 | 1.852 | 9.2896 | 0 | 38.3333 | 38.3333 | 60.858 | 0
176 | 20 | 0 | 10 |  | 0.40838 | 1.6353 | -2.2819 | 4.4381 | 20.074 | 2.1138 | 1.6234 | 0 | 8.3333 | 8.3333 | 13.23 | 0
176 | 21 | 0 | 0 |  | 0.40838 | 1.6353 | -2.2819 | 4.4381 | 21.074 | 2.3756 | -4.8859 | 0 | 0 | 0 | 0 | 0
176 | 22 | 0 | 0 |  | 0.40838 | 1.6353 | -2.2819 | 4.4381 | 22.074 | 2.6374 | -9.8662 | 0 | 0 | 0 | 0 | 0
176 | 23 | 0 | 0 |  | 0.40838 | 1.6353 | -2.2819 | 4.4381 | 23.074 | 2.8992 | -12.9632 | 0 | 0 | 0 | 0 | 0
176 | 24 | 0 | 0 |  | 0.40838 | 1.6353 | -2.2819 | 4.4381 | 24.074 | 3.161 | -13.9156 | 0 | 0 | 0 | 0 | 0
177 | 1 | 0 | 0 |  | 0.40783 | 1.6526 | -2.4869 | 4.2331 | 1.0706 | -2.8613 | -12.6744 | 0 | 0 | 0 | 0 | 0
177 | 2 | 0 | 0 |  | 0.40783 | 1.6526 | -2.4869 | 4.2331 | 2.0706 | -2.5995 | -9.2848 | 0 | 0 | 0 | 0 | 0
177 | 3 | 0 | 0 |  | 0.40783 | 1.6526 | -2.4869 | 4.2331 | 3.0706 | -2.3377 | -4.059 | 0 | 0 | 0 | 0 | 0
177 | 4 | 0 | 1 |  | 0.40783 | 1.6526 | -2.4869 | 4.2331 | 4.0706 | -2.0759 | 2.6419 | 0 | 0.83333 | 0.83333 | 1.323 | 0
177 | 5 | 0 | 22 |  | 0.40783 | 1.6526 | -2.4869 | 4.2331 | 5.0706 | -1.8141 | 10.447 | 0 | 18.3333 | 18.3333 | 29.106 | 0
177 | 6 | 0 | 52 |  | 0.40783 | 1.6526 | -2.4869 | 4.2331 | 6.0706 | -1.5523 | 19.0077 | 0 | 43.3333 | 43.3333 | 68.796 | 1
177 | 7 | 29 | 157 |  | 0.40783 | 1.6526 | -2.4869 | 4.2331 | 7.0706 | -1.2905 | 27.993 | 11.2294 | 130.8333 | 142.0628 | 225.5389 | 1
177 | 8 | 34 | 241 |  | 0.40783 | 1.6526 | -2.4869 | 4.2331 | 8.0706 | -1.0287 | 37.0521 | 20.0568 | 200.8333 | 220.8901 | 350.6851 | 1
177 | 9 | 6 | 211 |  | 0.40783 | 1.6526 | -2.4869 | 4.2331 | 9.0706 | -0.76693 | 45.7377 | 4.5768 | 175.8333 | 180.4102 | 286.4192 | 1
177 | 10 | 7 | 253 |  | 0.40783 | 1.6526 | -2.4869 | 4.2331 | 10.0706 | -0.50513 | 53.365 | 6.259 | 210.8333 | 217.0924 | 344.6559 | 1
177 | 11 | 125 | 357 |  | 0.40783 | 1.6526 | -2.4869 | 4.2331 | 11.0706 | -0.24333 | 58.822 | 121.8721 | 297.5 | 419.3721 | 665.7951 | 1
177 | 12 | 28 | 280 |  | 0.40783 | 1.6526 | -2.4869 | 4.2331 | 12.0706 | 0.018471 | 60.6759 | 27.9939 | 233.3333 | 261.3273 | 414.8832 | 1
177 | 13 | 12 | 293 |  | 0.40783 | 1.6526 | -2.4869 | 4.2331 | 13.0706 | 0.28027 | 58.238 | 11.6025 | 244.1667 | 255.7692 | 406.0592 | 1
177 | 14 | 11 | 276 |  | 0.40783 | 1.6526 | -2.4869 | 4.2331 | 14.0706 | 0.54207 | 52.3891 | 9.6636 | 230 | 239.6636 | 380.4899 | 1
177 | 15 | 72 | 350 |  | 0.40783 | 1.6526 | -2.4869 | 4.2331 | 15.0706 | 0.80387 | 44.5567 | 53.3293 | 291.6667 | 344.9959 | 547.7155 | 1
177 | 16 | 12 | 201 |  | 0.40783 | 1.6526 | -2.4869 | 4.2331 | 16.0706 | 1.0657 | 35.7845 | 6.7537 | 167.5 | 174.2537 | 276.6452 | 1
177 | 17 | 0 | 154 |  | 0.40783 | 1.6526 | -2.4869 | 4.2331 | 17.0706 | 1.3275 | 26.712 | 0 | 128.3333 | 128.3333 | 203.742 | 1
177 | 18 | 0 | 98 |  | 0.40783 | 1.6526 | -2.4869 | 4.2331 | 18.0706 | 1.5893 | 17.7664 | 0 | 81.6667 | 81.6667 | 129.654 | 1
177 | 19 | 0 | 46 |  | 0.40783 | 1.6526 | -2.4869 | 4.2331 | 19.0706 | 1.8511 | 9.2921 | 0 | 38.3333 | 38.3333 | 60.858 | 0
177 | 20 | 0 | 10 |  | 0.40783 | 1.6526 | -2.4869 | 4.2331 | 20.0706 | 2.1129 | 1.6211 | 0 | 8.3333 | 8.3333 | 13.23 | 0
177 | 21 | 0 | 0 |  | 0.40783 | 1.6526 | -2.4869 | 4.2331 | 21.0706 | 2.3747 | -4.8944 | 0 | 0 | 0 | 0 | 0
177 | 22 | 0 | 0 |  | 0.40783 | 1.6526 | -2.4869 | 4.2331 | 22.0706 | 2.6365 | -9.8821 | 0 | 0 | 0 | 0 | 0
177 | 23 | 0 | 0 |  | 0.40783 | 1.6526 | -2.4869 | 4.2331 | 23.0706 | 2.8983 | -12.9871 | 0 | 0 | 0 | 0 | 0
177 | 24 | 0 | 0 |  | 0.40783 | 1.6526 | -2.4869 | 4.2331 | 24.0706 | 3.1601 | -13.9474 | 0 | 0 | 0 | 0 | 0
178 | 1 | 0 | 0 |  | 0.40716 | 1.6698 | -2.6897 | 4.0303 | 1.0672 | -2.8622 | -12.7204 | 0 | 0 | 0 | 0 | 0
178 | 2 | 0 | 0 |  | 0.40716 | 1.6698 | -2.6897 | 4.0303 | 2.0672 | -2.6004 | -9.3361 | 0 | 0 | 0 | 0 | 0
178 | 3 | 0 | 0 |  | 0.40716 | 1.6698 | -2.6897 | 4.0303 | 3.0672 | -2.3386 | -4.114 | 0 | 0 | 0 | 0 | 0
178 | 4 | 0 | 1 |  | 0.40716 | 1.6698 | -2.6897 | 4.0303 | 4.0672 | -2.0768 | 2.5845 | 0 | 0.83333 | 0.83333 | 1.323 | 0
178 | 5 | 0 | 13 |  | 0.40716 | 1.6698 | -2.6897 | 4.0303 | 5.0672 | -1.815 | 10.3882 | 0 | 10.8333 | 10.8333 | 17.199 | 0
178 | 6 | 0 | 52 |  | 0.40716 | 1.6698 | -2.6897 | 4.0303 | 6.0672 | -1.5532 | 18.9482 | 0 | 43.3333 | 43.3333 | 68.796 | 1
178 | 7 | 0 | 105 |  | 0.40716 | 1.6698 | -2.6897 | 4.0303 | 7.0672 | -1.2914 | 27.9333 | 0 | 87.5 | 87.5 | 138.915 | 1
178 | 8 | 1 | 162 |  | 0.40716 | 1.6698 | -2.6897 | 4.0303 | 8.0672 | -1.0296 | 36.9925 | 0.58915 | 135 | 135.5892 | 215.2613 | 1
178 | 9 | 5 | 212 |  | 0.40716 | 1.6698 | -2.6897 | 4.0303 | 9.0672 | -0.76781 | 45.6788 | 3.8111 | 176.6667 | 180.4778 | 286.5265 | 1
178 | 10 | 7 | 253 |  | 0.40716 | 1.6698 | -2.6897 | 4.0303 | 10.0672 | -0.50601 | 53.3085 | 6.2563 | 210.8333 | 217.0897 | 344.6516 | 1
178 | 11 | 11 | 279 |  | 0.40716 | 1.6698 | -2.6897 | 4.0303 | 11.0672 | -0.24421 | 58.7718 | 10.7228 | 232.5 | 243.2228 | 386.1405 | 1
178 | 12 | 12 | 294 |  | 0.40716 | 1.6698 | -2.6897 | 4.0303 | 12.0672 | 0.017585 | 60.6383 | 11.9977 | 245 | 256.9977 | 408.0095 | 1
178 | 13 | 12 | 293 |  | 0.40716 | 1.6698 | -2.6897 | 4.0303 | 13.0672 | 0.27938 | 58.2163 | 11.605 | 244.1667 | 255.7717 | 406.0631 | 1
178 | 14 | 11 | 276 |  | 0.40716 | 1.6698 | -2.6897 | 4.0303 | 14.0672 | 0.54118 | 52.3798 | 9.6675 | 230 | 239.6675 | 380.4961 | 1
178 | 15 | 7 | 248 |  | 0.40716 | 1.6698 | -2.6897 | 4.0303 | 15.0672 | 0.80298 | 44.5547 | 5.1881 | 206.6667 | 211.8548 | 336.3406 | 1
178 | 16 | 5 | 205 |  | 0.40716 | 1.6698 | -2.6897 | 4.0303 | 16.0672 | 1.0648 | 35.7857 | 2.8167 | 170.8333 | 173.6501 | 275.6868 | 1
178 | 17 | 0 | 154 |  | 0.40716 | 1.6698 | -2.6897 | 4.0303 | 17.0672 | 1.3266 | 26.7136 | 0 | 128.3333 | 128.3333 | 203.742 | 1
178 | 18 | 0 | 98 |  | 0.40716 | 1.6698 | -2.6897 | 4.0303 | 18.0672 | 1.5884 | 17.7663 | 0 | 81.6667 | 81.6667 | 129.654 | 1
178 | 19 | 0 | 46 |  | 0.40716 | 1.6698 | -2.6897 | 4.0303 | 19.0672 | 1.8502 | 9.2885 | 0 | 38.3333 | 38.3333 | 60.858 | 0
178 | 20 | 0 | 10 |  | 0.40716 | 1.6698 | -2.6897 | 4.0303 | 20.0672 | 2.112 | 1.6124 | 0 | 8.3333 | 8.3333 | 13.23 | 0
178 | 21 | 0 | 0 |  | 0.40716 | 1.6698 | -2.6897 | 4.0303 | 21.0672 | 2.3738 | -4.9097 | 0 | 0 | 0 | 0 | 0
178 | 22 | 0 | 0 |  | 0.40716 | 1.6698 | -2.6897 | 4.0303 | 22.0672 | 2.6356 | -9.905 | 0 | 0 | 0 | 0 | 0
178 | 23 | 0 | 0 |  | 0.40716 | 1.6698 | -2.6897 | 4.0303 | 23.0672 | 2.8974 | -13.0182 | 0 | 0 | 0 | 0 | 0
178 | 24 | 0 | 0 |  | 0.40716 | 1.6698 | -2.6897 | 4.0303 | 24.0672 | 3.1592 | -13.9865 | 0 | 0 | 0 | 0 | 0
179 | 1 | 0 | 0 |  | 0.40636 | 1.687 | -2.89 | 3.83 | 1.0638 | -2.8631 | -12.7735 | 0 | 0 | 0 | 0 | 0
179 | 2 | 0 | 0 |  | 0.40636 | 1.687 | -2.89 | 3.83 | 2.0638 | -2.6013 | -9.3942 | 0 | 0 | 0 | 0 | 0
179 | 3 | 0 | 0 |  | 0.40636 | 1.687 | -2.89 | 3.83 | 3.0638 | -2.3395 | -4.1754 | 0 | 0 | 0 | 0 | 0
179 | 4 | 0 | 1 |  | 0.40636 | 1.687 | -2.89 | 3.83 | 4.0638 | -2.0777 | 2.5212 | 0 | 0.83333 | 0.83333 | 1.323 | 0
179 | 5 | 0 | 34 |  | 0.40636 | 1.687 | -2.89 | 3.83 | 5.0638 | -1.8159 | 10.3239 | 0 | 28.3333 | 28.3333 | 44.982 | 0
179 | 6 | 211 | 94 |  | 0.40636 | 1.687 | -2.89 | 3.83 | 6.0638 | -1.5541 | 18.8835 | 35.1465 | 78.3333 | 113.4798 | 180.1605 | 1
179 | 7 | 414 | 124 |  | 0.40636 | 1.687 | -2.89 | 3.83 | 7.0638 | -1.2923 | 27.8685 | 159.5623 | 103.3333 | 262.8957 | 417.3732 | 1
179 | 8 | 595 | 137 |  | 0.40636 | 1.687 | -2.89 | 3.83 | 8.0638 | -1.0305 | 36.9278 | 350.0876 | 114.1667 | 464.2543 | 737.0501 | 1
179 | 9 | 185 | 318 |  | 0.40636 | 1.687 | -2.89 | 3.83 | 9.0638 | -0.76869 | 45.6145 | 140.903 | 265 | 405.903 | 644.4116 | 1
179 | 10 | 198 | 378 |  | 0.40636 | 1.687 | -2.89 | 3.83 | 10.0638 | -0.50689 | 53.2459 | 176.8883 | 315 | 491.8883 | 780.9219 | 1
179 | 11 | 664 | 262 |  | 0.40636 | 1.687 | -2.89 | 3.83 | 11.0638 | -0.24509 | 58.7148 | 647.1456 | 218.3333 | 865.479 | 1374.0344 | 1
179 | 12 | 812 | 154 |  | 0.40636 | 1.687 | -2.89 | 3.83 | 12.0638 | 0.016711 | 60.5934 | 811.859 | 128.3333 | 940.1923 | 1492.6494 | 1
179 | 13 | 841 | 137 |  | 0.40636 | 1.687 | -2.89 | 3.83 | 13.0638 | 0.27851 | 58.1873 | 813.4872 | 114.1667 | 927.6539 | 1472.7433 | 1
179 | 14 | 570 | 275 |  | 0.40636 | 1.687 | -2.89 | 3.83 | 14.0638 | 0.54031 | 52.3639 | 501.151 | 229.1667 | 730.3177 | 1159.4524 | 1
179 | 15 | 386 | 314 |  | 0.40636 | 1.687 | -2.89 | 3.83 | 15.0638 | 0.80211 | 44.5466 | 286.2609 | 261.6667 | 547.9276 | 869.8898 | 1
179 | 16 | 196 | 300 |  | 0.40636 | 1.687 | -2.89 | 3.83 | 16.0638 | 1.0639 | 35.781 | 110.5149 | 250 | 360.5149 | 572.3535 | 1
179 | 17 | 43 | 224 |  | 0.40636 | 1.687 | -2.89 | 3.83 | 17.0638 | 1.3257 | 26.7094 | 15.3964 | 186.6667 | 202.0631 | 320.7953 | 1
179 | 18 | 19 | 149 |  | 0.40636 | 1.687 | -2.89 | 3.83 | 18.0638 | 1.5875 | 17.7602 | 2.6267 | 124.1667 | 126.7933 | 201.2971 | 1
179 | 19 | 94 | 87 |  | 0.40636 | 1.687 | -2.89 | 3.83 | 19.0638 | 1.8493 | 9.2786 | 0 | 72.5 | 72.5 | 115.101 | 0
179 | 20 | 0 | 20 |  | 0.40636 | 1.687 | -2.89 | 3.83 | 20.0638 | 2.1111 | 1.5971 | 0 | 16.6667 | 16.6667 | 26.46 | 0
179 | 21 | 0 | 1 |  | 0.40636 | 1.687 | -2.89 | 3.83 | 21.0638 | 2.3729 | -4.9319 | 0 | 0.83333 | 0.83333 | 1.323 | 0
179 | 22 | 0 | 0 |  | 0.40636 | 1.687 | -2.89 | 3.83 | 22.0638 | 2.6347 | -9.9351 | 0 | 0 | 0 | 0 | 0
179 | 23 | 0 | 0 |  | 0.40636 | 1.687 | -2.89 | 3.83 | 23.0638 | 2.8965 | -13.0567 | 0 | 0 | 0 | 0 | 0
179 | 24 | 0 | 0 |  | 0.40636 | 1.687 | -2.89 | 3.83 | 24.0638 | 3.1583 | -14.0329 | 0 | 0 | 0 | 0 | 0
180 | 1 | 0 | 0 |  | 0.40543 | 1.7042 | -3.0874 | 3.6326 | 1.0605 | -2.8639 | -12.8336 | 0 | 0 | 0 | 0 | 0
180 | 2 | 0 | 0 |  | 0.40543 | 1.7042 | -3.0874 | 3.6326 | 2.0605 | -2.6021 | -9.459 | 0 | 0 | 0 | 0 | 0
180 | 3 | 0 | 0 |  | 0.40543 | 1.7042 | -3.0874 | 3.6326 | 3.0605 | -2.3403 | -4.2431 | 0 | 0 | 0 | 0 | 0
180 | 4 | 0 | 2 |  | 0.40543 | 1.7042 | -3.0874 | 3.6326 | 4.0605 | -2.0785 | 2.4521 | 0 | 1.6667 | 1.6667 | 2.646 | 0
180 | 5 | 5 | 35 |  | 0.40543 | 1.7042 | -3.0874 | 3.6326 | 5.0605 | -1.8167 | 10.2542 | 0 | 29.1667 | 29.1667 | 46.305 | 0
180 | 6 | 237 | 82 |  | 0.40543 | 1.7042 | -3.0874 | 3.6326 | 6.0605 | -1.5549 | 18.8136 | 39.2276 | 68.3333 | 107.561 | 170.7638 | 1
180 | 7 | 344 | 136 |  | 0.40543 | 1.7042 | -3.0874 | 3.6326 | 7.0605 | -1.2931 | 27.7986 | 132.2605 | 113.3333 | 245.5938 | 389.9047 | 1
180 | 8 | 46 | 233 |  | 0.40543 | 1.7042 | -3.0874 | 3.6326 | 8.0605 | -1.0313 | 36.8579 | 27.0297 | 194.1667 | 221.1963 | 351.1713 | 1
180 | 9 | 6 | 210 |  | 0.40543 | 1.7042 | -3.0874 | 3.6326 | 9.0605 | -0.76955 | 45.5447 | 4.5663 | 175 | 179.5663 | 285.0794 | 1
180 | 10 | 7 | 252 |  | 0.40543 | 1.7042 | -3.0874 | 3.6326 | 10.0605 | -0.50775 | 53.1773 | 6.2509 | 210 | 216.2509 | 343.3199 | 1
180 | 11 | 11 | 279 |  | 0.40543 | 1.7042 | -3.0874 | 3.6326 | 11.0605 | -0.24595 | 58.651 | 10.7188 | 232.5 | 243.2188 | 386.1342 | 1
180 | 12 | 12 | 293 |  | 0.40543 | 1.7042 | -3.0874 | 3.6326 | 12.0605 | 0.01585 | 60.5412 | 11.9982 | 244.1667 | 256.1648 | 406.6873 | 1
180 | 13 | 12 | 292 |  | 0.40543 | 1.7042 | -3.0874 | 3.6326 | 13.0605 | 0.27765 | 58.1511 | 11.6098 | 243.3333 | 254.9431 | 404.7477 | 1
180 | 14 | 11 | 276 |  | 0.40543 | 1.7042 | -3.0874 | 3.6326 | 14.0605 | 0.53945 | 52.3413 | 9.675 | 230 | 239.675 | 380.5081 | 1
180 | 15 | 7 | 248 |  | 0.40543 | 1.7042 | -3.0874 | 3.6326 | 15.0605 | 0.80125 | 44.5322 | 5.1943 | 206.6667 | 211.8609 | 336.3504 | 1
180 | 16 | 5 | 205 |  | 0.40543 | 1.7042 | -3.0874 | 3.6326 | 16.0605 | 1.063 | 35.7704 | 2.8216 | 170.8333 | 173.655 | 275.6946 | 1
180 | 17 | 0 | 154 |  | 0.40543 | 1.7042 | -3.0874 | 3.6326 | 17.0605 | 1.3248 | 26.6992 | 0 | 128.3333 | 128.3333 | 203.742 | 1
180 | 18 | 0 | 98 |  | 0.40543 | 1.7042 | -3.0874 | 3.6326 | 18.0605 | 1.5866 | 17.748 | 0 | 81.6667 | 81.6667 | 129.654 | 1
180 | 19 | 0 | 46 |  | 0.40543 | 1.7042 | -3.0874 | 3.6326 | 19.0605 | 1.8484 | 9.2625 | 0 | 38.3333 | 38.3333 | 60.858 | 0
180 | 20 | 0 | 10 |  | 0.40543 | 1.7042 | -3.0874 | 3.6326 | 20.0605 | 2.1102 | 1.5753 | 0 | 8.3333 | 8.3333 | 13.23 | 0
180 | 21 | 0 | 0 |  | 0.40543 | 1.7042 | -3.0874 | 3.6326 | 21.0605 | 2.372 | -4.9609 | 0 | 0 | 0 | 0 | 0
180 | 22 | 0 | 0 |  | 0.40543 | 1.7042 | -3.0874 | 3.6326 | 22.0605 | 2.6338 | -9.9723 | 0 | 0 | 0 | 0 | 0
180 | 23 | 0 | 0 |  | 0.40543 | 1.7042 | -3.0874 | 3.6326 | 23.0605 | 2.8956 | -13.1024 | 0 | 0 | 0 | 0 | 0
180 | 24 | 0 | 0 |  | 0.40543 | 1.7042 | -3.0874 | 3.6326 | 24.0605 | 3.1574 | -14.0865 | 0 | 0 | 0 | 0 | 0
181 | 1 | 0 | 0 |  | 0.40437 | 1.7214 | -3.2817 | 3.4383 | 1.0573 | -2.8648 | -12.9008 | 0 | 0 | 0 | 0 | 0
181 | 2 | 0 | 0 |  | 0.40437 | 1.7214 | -3.2817 | 3.4383 | 2.0573 | -2.603 | -9.5304 | 0 | 0 | 0 | 0 | 0
181 | 3 | 0 | 0 |  | 0.40437 | 1.7214 | -3.2817 | 3.4383 | 3.0573 | -2.3412 | -4.3169 | 0 | 0 | 0 | 0 | 0
181 | 4 | 0 | 1 |  | 0.40437 | 1.7214 | -3.2817 | 3.4383 | 4.0573 | -2.0794 | 2.3772 | 0 | 0.83333 | 0.83333 | 1.323 | 0
181 | 5 | 0 | 13 |  | 0.40437 | 1.7214 | -3.2817 | 3.4383 | 5.0573 | -1.8176 | 10.1791 | 0 | 10.8333 | 10.8333 | 17.199 | 0
181 | 6 | 0 | 51 |  | 0.40437 | 1.7214 | -3.2817 | 3.4383 | 6.0573 | -1.5558 | 18.7386 | 0 | 42.5 | 42.5 | 67.473 | 1
181 | 7 | 0 | 104 |  | 0.40437 | 1.7214 | -3.2817 | 3.4383 | 7.0573 | -1.294 | 27.7237 | 0 | 86.6667 | 86.6667 | 137.592 | 1
181 | 8 | 1 | 160 |  | 0.40437 | 1.7214 | -3.2817 | 3.4383 | 8.0573 | -1.0322 | 36.7829 | 0.58681 | 133.3333 | 133.9201 | 212.6116 | 1
181 | 9 | 5 | 211 |  | 0.40437 | 1.7214 | -3.2817 | 3.4383 | 9.0573 | -0.7704 | 45.4696 | 3.8022 | 175.8333 | 179.6356 | 285.1894 | 1
181 | 10 | 7 | 252 |  | 0.40437 | 1.7214 | -3.2817 | 3.4383 | 10.0573 | -0.5086 | 53.1027 | 6.2482 | 210 | 216.2482 | 343.3156 | 1
181 | 11 | 11 | 279 |  | 0.40437 | 1.7214 | -3.2817 | 3.4383 | 11.0573 | -0.2468 | 58.5803 | 10.7169 | 232.5 | 243.2169 | 386.1311 | 1
181 | 12 | 12 | 293 |  | 0.40437 | 1.7214 | -3.2817 | 3.4383 | 12.0573 | 0.015003 | 60.4816 | 11.9984 | 244.1667 | 256.1651 | 406.6877 | 1
181 | 13 | 12 | 292 |  | 0.40437 | 1.7214 | -3.2817 | 3.4383 | 13.0573 | 0.2768 | 58.1078 | 11.6121 | 243.3333 | 254.9454 | 404.7514 | 1
181 | 14 | 11 | 276 |  | 0.40437 | 1.7214 | -3.2817 | 3.4383 | 14.0573 | 0.5386 | 52.312 | 9.6786 | 230 | 239.6786 | 380.5138 | 1
181 | 15 | 13 | 243 |  | 0.40437 | 1.7214 | -3.2817 | 3.4383 | 15.0573 | 0.8004 | 44.5116 | 9.6518 | 202.5 | 212.1518 | 336.8122 | 1
181 | 16 | 9 | 203 |  | 0.40437 | 1.7214 | -3.2817 | 3.4383 | 16.0573 | 1.0622 | 35.7537 | 5.0829 | 169.1667 | 174.2496 | 276.6386 | 1
181 | 17 | 1 | 155 |  | 0.40437 | 1.7214 | -3.2817 | 3.4383 | 17.0573 | 1.324 | 26.6831 | 0.35893 | 129.1667 | 129.5256 | 205.6348 | 1
181 | 18 | 0 | 98 |  | 0.40437 | 1.7214 | -3.2817 | 3.4383 | 18.0573 | 1.5858 | 17.7298 | 0 | 81.6667 | 81.6667 | 129.654 | 1
181 | 19 | 0 | 46 |  | 0.40437 | 1.7214 | -3.2817 | 3.4383 | 19.0573 | 1.8476 | 9.2401 | 0 | 38.3333 | 38.3333 | 60.858 | 0
181 | 20 | 0 | 15 |  | 0.40437 | 1.7214 | -3.2817 | 3.4383 | 20.0573 | 2.1094 | 1.5469 | 0 | 12.5 | 12.5 | 19.845 | 0
181 | 21 | 0 | 0 |  | 0.40437 | 1.7214 | -3.2817 | 3.4383 | 21.0573 | 2.3712 | -4.9967 | 0 | 0 | 0 | 0 | 0
181 | 22 | 0 | 0 |  | 0.40437 | 1.7214 | -3.2817 | 3.4383 | 22.0573 | 2.633 | -10.0166 | 0 | 0 | 0 | 0 | 0
181 | 23 | 0 | 0 |  | 0.40437 | 1.7214 | -3.2817 | 3.4383 | 23.0573 | 2.8948 | -13.1553 | 0 | 0 | 0 | 0 | 0
181 | 24 | 0 | 0 |  | 0.40437 | 1.7214 | -3.2817 | 3.4383 | 24.0573 | 3.1566 | -14.1474 | 0 | 0 | 0 | 0 | 0
182 | 1 | 0 | 0 |  | 0.40319 | 1.7386 | -3.4723 | 3.2477 | 1.0541 | -2.8656 | -12.9749 | 0 | 0 | 0 | 0 | 0
182 | 2 | 0 | 0 |  | 0.40319 | 1.7386 | -3.4723 | 3.2477 | 2.0541 | -2.6038 | -9.6085 | 0 | 0 | 0 | 0 | 0
182 | 3 | 0 | 0 |  | 0.40319 | 1.7386 | -3.4723 | 3.2477 | 3.0541 | -2.342 | -4.3969 | 0 | 0 | 0 | 0 | 0
182 | 4 | 0 | 1 |  | 0.40319 | 1.7386 | -3.4723 | 3.2477 | 4.0541 | -2.0802 | 2.2966 | 0 | 0.83333 | 0.83333 | 1.323 | 0
182 | 5 | 0 | 25 |  | 0.40319 | 1.7386 | -3.4723 | 3.2477 | 5.0541 | -1.8184 | 10.0986 | 0 | 20.8333 | 20.8333 | 33.075 | 0
182 | 6 | 0 | 79 |  | 0.40319 | 1.7386 | -3.4723 | 3.2477 | 6.0541 | -1.5566 | 18.6586 | 0 | 65.8333 | 65.8333 | 104.517 | 1
182 | 7 | 19 | 156 |  | 0.40319 | 1.7386 | -3.4723 | 3.2477 | 7.0541 | -1.2948 | 27.6439 | 7.2682 | 130 | 137.2682 | 217.927 | 1
182 | 8 | 1 | 158 |  | 0.40319 | 1.7386 | -3.4723 | 3.2477 | 8.0541 | -1.033 | 36.703 | 0.586 | 131.6667 | 132.2527 | 209.9643 | 1
182 | 9 | 66 | 295 |  | 0.40319 | 1.7386 | -3.4723 | 3.2477 | 9.0541 | -0.77123 | 45.3892 | 50.1496 | 245.8333 | 295.9829 | 469.9025 | 1
182 | 10 | 207 | 368 |  | 0.40319 | 1.7386 | -3.4723 | 3.2477 | 10.0541 | -0.50943 | 53.0223 | 184.6874 | 306.6667 | 491.3541 | 780.0738 | 1
182 | 11 | 101 | 374 |  | 0.40319 | 1.7386 | -3.4723 | 3.2477 | 11.0541 | -0.24763 | 58.503 | 98.3826 | 311.6667 | 410.0492 | 650.9942 | 1
182 | 12 | 274 | 381 |  | 0.40319 | 1.7386 | -3.4723 | 3.2477 | 12.0541 | 0.014171 | 60.4147 | 273.9692 | 317.5 | 591.4692 | 939.0166 | 1
182 | 13 | 416 | 357 |  | 0.40319 | 1.7386 | -3.4723 | 3.2477 | 13.0541 | 0.27597 | 58.0572 | 402.6297 | 297.5 | 700.1297 | 1111.5259 | 1
182 | 14 | 272 | 358 |  | 0.40319 | 1.7386 | -3.4723 | 3.2477 | 14.0541 | 0.53777 | 52.276 | 239.41 | 298.3333 | 537.7433 | 853.7212 | 1
182 | 15 | 76 | 345 |  | 0.40319 | 1.7386 | -3.4723 | 3.2477 | 15.0541 | 0.79957 | 44.4847 | 56.4554 | 287.5 | 343.9554 | 546.0636 | 1
182 | 16 | 66 | 287 |  | 0.40319 | 1.7386 | -3.4723 | 3.2477 | 16.0541 | 1.0614 | 35.731 | 37.3014 | 239.1667 | 276.468 | 438.9206 | 1
182 | 17 | 31 | 228 |  | 0.40319 | 1.7386 | -3.4723 | 3.2477 | 17.0541 | 1.3232 | 26.6609 | 11.1384 | 190 | 201.1384 | 319.3274 | 1
182 | 18 | 18 | 147 |  | 0.40319 | 1.7386 | -3.4723 | 3.2477 | 18.0541 | 1.585 | 17.7055 | 2.5067 | 122.5 | 125.0067 | 198.4606 | 1
182 | 19 | 0 | 71 |  | 0.40319 | 1.7386 | -3.4723 | 3.2477 | 19.0541 | 1.8468 | 9.2114 | 0 | 59.1667 | 59.1667 | 93.933 | 0
182 | 20 | 0 | 15 |  | 0.40319 | 1.7386 | -3.4723 | 3.2477 | 20.0541 | 2.1086 | 1.5119 | 0 | 12.5 | 12.5 | 19.845 | 0
182 | 21 | 0 | 0 |  | 0.40319 | 1.7386 | -3.4723 | 3.2477 | 21.0541 | 2.3704 | -5.0394 | 0 | 0 | 0 | 0 | 0
182 | 22 | 0 | 0 |  | 0.40319 | 1.7386 | -3.4723 | 3.2477 | 22.0541 | 2.6322 | -10.068 | 0 | 0 | 0 | 0 | 0
182 | 23 | 0 | 0 |  | 0.40319 | 1.7386 | -3.4723 | 3.2477 | 23.0541 | 2.894 | -13.2155 | 0 | 0 | 0 | 0 | 0
182 | 24 | 0 | 0 |  | 0.40319 | 1.7386 | -3.4723 | 3.2477 | 24.0541 | 3.1558 | -14.2155 | 0 | 0 | 0 | 0 | 0
183 | 1 | 0 | 0 |  | 0.40189 | 1.7558 | -3.659 | 3.061 | 1.051 | -2.8664 | -13.056 | 0 | 0 | 0 | 0 | 0
183 | 2 | 0 | 0 |  | 0.40189 | 1.7558 | -3.659 | 3.061 | 2.051 | -2.6046 | -9.6931 | 0 | 0 | 0 | 0 | 0
183 | 3 | 0 | 0 |  | 0.40189 | 1.7558 | -3.659 | 3.061 | 3.051 | -2.3428 | -4.483 | 0 | 0 | 0 | 0 | 0
183 | 4 | 0 | 1 |  | 0.40189 | 1.7558 | -3.659 | 3.061 | 4.051 | -2.081 | 2.2103 | 0 | 0.83333 | 0.83333 | 1.323 | 0
183 | 5 | 0 | 31 |  | 0.40189 | 1.7558 | -3.659 | 3.061 | 5.051 | -1.8192 | 10.0129 | 0 | 25.8333 | 25.8333 | 41.013 | 0
183 | 6 | 216 | 82 |  | 0.40189 | 1.7558 | -3.659 | 3.061 | 6.051 | -1.5574 | 18.5736 | 35.0274 | 68.3333 | 103.3608 | 164.0955 | 1
183 | 7 | 330 | 137 |  | 0.40189 | 1.7558 | -3.659 | 3.061 | 7.051 | -1.2956 | 27.5593 | 125.907 | 114.1667 | 240.0737 | 381.141 | 1
183 | 8 | 499 | 173 |  | 0.40189 | 1.7558 | -3.659 | 3.061 | 8.051 | -1.0338 | 36.6182 | 292.0079 | 144.1667 | 436.1745 | 692.4707 | 1
183 | 9 | 626 | 173 |  | 0.40189 | 1.7558 | -3.659 | 3.061 | 9.051 | -0.77204 | 45.3035 | 475.2809 | 144.1667 | 619.4476 | 983.435 | 1
183 | 10 | 661 | 204 |  | 0.40189 | 1.7558 | -3.659 | 3.061 | 10.051 | -0.51024 | 52.9359 | 589.4937 | 170 | 759.4937 | 1205.7722 | 1
183 | 11 | 709 | 202 |  | 0.40189 | 1.7558 | -3.659 | 3.061 | 11.051 | -0.24844 | 58.419 | 690.5018 | 168.3333 | 858.8352 | 1363.4867 | 1
183 | 12 | 785 | 174 |  | 0.40189 | 1.7558 | -3.659 | 3.061 | 12.051 | 0.013356 | 60.3406 | 784.9262 | 145 | 929.9262 | 1476.3508 | 1
183 | 13 | 711 | 215 |  | 0.40189 | 1.7558 | -3.659 | 3.061 | 13.051 | 0.27516 | 57.9995 | 688.2756 | 179.1667 | 867.4423 | 1377.1514 | 1
183 | 14 | 720 | 188 |  | 0.40189 | 1.7558 | -3.659 | 3.061 | 14.051 | 0.53695 | 52.2332 | 633.9455 | 156.6667 | 790.6122 | 1255.1759 | 1
183 | 15 | 192 | 372 |  | 0.40189 | 1.7558 | -3.659 | 3.061 | 15.051 | 0.79875 | 44.4514 | 142.6936 | 310 | 452.6936 | 718.6964 | 1
183 | 16 | 289 | 275 |  | 0.40189 | 1.7558 | -3.659 | 3.061 | 16.051 | 1.0606 | 35.7022 | 163.4418 | 229.1667 | 392.6085 | 623.3053 | 1
183 | 17 | 311 | 204 |  | 0.40189 | 1.7558 | -3.659 | 3.061 | 17.051 | 1.3224 | 26.6328 | 111.844 | 170 | 281.844 | 447.4555 | 1
183 | 18 | 24 | 145 |  | 0.40189 | 1.7558 | -3.659 | 3.061 | 18.051 | 1.5842 | 17.675 | 3.3476 | 120.8333 | 124.1809 | 197.1496 | 1
183 | 19 | 85 | 86 |  | 0.40189 | 1.7558 | -3.659 | 3.061 | 19.051 | 1.846 | 9.1764 | 0 | 71.6667 | 71.6667 | 113.778 | 0
183 | 20 | 0 | 26 |  | 0.40189 | 1.7558 | -3.659 | 3.061 | 20.051 | 2.1078 | 1.4704 | 0 | 21.6667 | 21.6667 | 34.398 | 0
183 | 21 | 0 | 1 |  | 0.40189 | 1.7558 | -3.659 | 3.061 | 21.051 | 2.3696 | -5.089 | 0 | 0.83333 | 0.83333 | 1.323 | 0
183 | 22 | 0 | 0 |  | 0.40189 | 1.7558 | -3.659 | 3.061 | 22.051 | 2.6314 | -10.1265 | 0 | 0 | 0 | 0 | 0
183 | 23 | 0 | 0 |  | 0.40189 | 1.7558 | -3.659 | 3.061 | 23.051 | 2.8931 | -13.283 | 0 | 0 | 0 | 0 | 0
183 | 24 | 0 | 0 |  | 0.40189 | 1.7558 | -3.659 | 3.061 | 24.051 | 3.1549 | -14.2907 | 0 | 0 | 0 | 0 | 0
184 | 1 | 0 | 0 |  | 0.40045 | 1.7731 | -3.8415 | 2.8785 | 1.048 | -2.8672 | -13.1439 | 0 | 0 | 0 | 0 | 0
184 | 2 | 0 | 0 |  | 0.40045 | 1.7731 | -3.8415 | 2.8785 | 2.048 | -2.6054 | -9.7842 | 0 | 0 | 0 | 0 | 0
184 | 3 | 0 | 0 |  | 0.40045 | 1.7731 | -3.8415 | 2.8785 | 3.048 | -2.3436 | -4.5752 | 0 | 0 | 0 | 0 | 0
184 | 4 | 0 | 1 |  | 0.40045 | 1.7731 | -3.8415 | 2.8785 | 4.048 | -2.0818 | 2.1185 | 0 | 0.83333 | 0.83333 | 1.323 | 0
184 | 5 | 0 | 33 |  | 0.40045 | 1.7731 | -3.8415 | 2.8785 | 5.048 | -1.82 | 9.922 | 0 | 27.5 | 27.5 | 43.659 | 0
184 | 6 | 247 | 79 |  | 0.40045 | 1.7731 | -3.8415 | 2.8785 | 6.048 | -1.5582 | 18.4836 | 39.7636 | 65.8333 | 105.5969 | 167.6457 | 1
184 | 7 | 394 | 135 |  | 0.40045 | 1.7731 | -3.8415 | 2.8785 | 7.048 | -1.2964 | 27.4699 | 149.9238 | 112.5 | 262.4238 | 416.624 | 1
184 | 8 | 596 | 130 |  | 0.40045 | 1.7731 | -3.8415 | 2.8785 | 8.048 | -1.0346 | 36.5285 | 348.2788 | 108.3333 | 456.6121 | 724.9174 | 1
184 | 9 | 66 | 294 |  | 0.40045 | 1.7731 | -3.8415 | 2.8785 | 9.048 | -0.77284 | 45.2127 | 50.0692 | 245 | 295.0692 | 468.4518 | 1
184 | 10 | 8 | 249 |  | 0.40045 | 1.7731 | -3.8415 | 2.8785 | 10.048 | -0.51104 | 52.8438 | 7.1315 | 207.5 | 214.6315 | 340.7489 | 1
184 | 11 | 11 | 277 |  | 0.40045 | 1.7731 | -3.8415 | 2.8785 | 11.048 | -0.24924 | 58.3284 | 10.7111 | 230.8333 | 241.5444 | 383.4759 | 1
184 | 12 | 124 | 374 |  | 0.40045 | 1.7731 | -3.8415 | 2.8785 | 12.048 | 0.01256 | 60.2592 | 123.9904 | 311.6667 | 435.657 | 691.6491 | 1
184 | 13 | 548 | 386 |  | 0.40045 | 1.7731 | -3.8415 | 2.8785 | 13.048 | 0.27436 | 57.9345 | 530.5794 | 321.6667 | 852.2461 | 1353.0259 | 1
184 | 14 | 819 | 135 |  | 0.40045 | 1.7731 | -3.8415 | 2.8785 | 14.048 | 0.53616 | 52.1837 | 721.343 | 112.5 | 833.843 | 1323.8091 | 1
184 | 15 | 766 | 143 |  | 0.40045 | 1.7731 | -3.8415 | 2.8785 | 15.048 | 0.79796 | 44.4118 | 569.5455 | 119.1667 | 688.7121 | 1093.3994 | 1
184 | 16 | 707 | 133 |  | 0.40045 | 1.7731 | -3.8415 | 2.8785 | 16.048 | 1.0598 | 35.6673 | 400.0747 | 110.8333 | 510.908 | 811.1175 | 1
184 | 17 | 615 | 118 |  | 0.40045 | 1.7731 | -3.8415 | 2.8785 | 17.048 | 1.3216 | 26.5985 | 221.3392 | 98.3333 | 319.6725 | 507.5121 | 1
184 | 18 | 424 | 114 |  | 0.40045 | 1.7731 | -3.8415 | 2.8785 | 18.048 | 1.5834 | 17.6385 | 59.2086 | 95 | 154.2086 | 244.8215 | 1
184 | 19 | 183 | 84 |  | 0.40045 | 1.7731 | -3.8415 | 2.8785 | 19.048 | 1.8452 | 9.135 | 0 | 70 | 70 | 111.132 | 0
184 | 20 | 0 | 26 |  | 0.40045 | 1.7731 | -3.8415 | 2.8785 | 20.048 | 2.107 | 1.4223 | 0 | 21.6667 | 21.6667 | 34.398 | 0
184 | 21 | 0 | 1 |  | 0.40045 | 1.7731 | -3.8415 | 2.8785 | 21.048 | 2.3688 | -5.1454 | 0 | 0.83333 | 0.83333 | 1.323 | 0
184 | 22 | 0 | 0 |  | 0.40045 | 1.7731 | -3.8415 | 2.8785 | 22.048 | 2.6306 | -10.1921 | 0 | 0 | 0 | 0 | 0
184 | 23 | 0 | 0 |  | 0.40045 | 1.7731 | -3.8415 | 2.8785 | 23.048 | 2.8924 | -13.3576 | 0 | 0 | 0 | 0 | 0
184 | 24 | 0 | 0 |  | 0.40045 | 1.7731 | -3.8415 | 2.8785 | 24.048 | 3.1542 | -14.3731 | 0 | 0 | 0 | 0 | 0
185 | 1 | 0 | 0 |  | 0.3989 | 1.7903 | -4.0193 | 2.7007 | 1.045 | -2.868 | -13.2387 | 0 | 0 | 0 | 0 | 0
185 | 2 | 0 | 0 |  | 0.3989 | 1.7903 | -4.0193 | 2.7007 | 2.045 | -2.6062 | -9.8817 | 0 | 0 | 0 | 0 | 0
185 | 3 | 0 | 0 |  | 0.3989 | 1.7903 | -4.0193 | 2.7007 | 3.045 | -2.3444 | -4.6733 | 0 | 0 | 0 | 0 | 0
185 | 4 | 0 | 1 |  | 0.3989 | 1.7903 | -4.0193 | 2.7007 | 4.045 | -2.0826 | 2.0211 | 0 | 0.83333 | 0.83333 | 1.323 | 0
185 | 5 | 0 | 32 |  | 0.3989 | 1.7903 | -4.0193 | 2.7007 | 5.045 | -1.8208 | 9.826 | 0 | 26.6667 | 26.6667 | 42.336 | 0
185 | 6 | 243 | 79 |  | 0.3989 | 1.7903 | -4.0193 | 2.7007 | 6.045 | -1.559 | 18.3889 | 38.8267 | 65.8333 | 104.66 | 166.1582 | 1
185 | 7 | 394 | 134 |  | 0.3989 | 1.7903 | -4.0193 | 2.7007 | 7.045 | -1.2972 | 27.3758 | 149.5153 | 111.6667 | 261.182 | 414.6525 | 1
185 | 8 | 594 | 135 |  | 0.3989 | 1.7903 | -4.0193 | 2.7007 | 8.045 | -1.0354 | 36.4341 | 346.6142 | 112.5 | 459.1142 | 728.8897 | 1
185 | 9 | 713 | 135 |  | 0.3989 | 1.7903 | -4.0193 | 2.7007 | 9.045 | -0.77361 | 45.1168 | 540.4614 | 112.5 | 652.9614 | 1036.6415 | 1
185 | 10 | 762 | 150 |  | 0.3989 | 1.7903 | -4.0193 | 2.7007 | 10.045 | -0.51181 | 52.746 | 678.9755 | 125 | 803.9755 | 1276.3915 | 1
185 | 11 | 819 | 137 |  | 0.3989 | 1.7903 | -4.0193 | 2.7007 | 11.045 | -0.25002 | 58.2312 | 797.346 | 114.1667 | 911.5126 | 1447.1174 | 1
185 | 12 | 831 | 142 |  | 0.3989 | 1.7903 | -4.0193 | 2.7007 | 12.045 | 0.011784 | 60.1706 | 830.9471 | 118.3333 | 949.2804 | 1507.0776 | 1
185 | 13 | 828 | 143 |  | 0.3989 | 1.7903 | -4.0193 | 2.7007 | 13.045 | 0.27358 | 57.8623 | 801.8139 | 119.1667 | 920.9805 | 1462.1487 | 1
185 | 14 | 696 | 205 |  | 0.3989 | 1.7903 | -4.0193 | 2.7007 | 14.045 | 0.53538 | 52.1273 | 613.1934 | 170.8333 | 784.0268 | 1244.7209 | 1
185 | 15 | 525 | 261 |  | 0.3989 | 1.7903 | -4.0193 | 2.7007 | 15.045 | 0.79718 | 44.3658 | 390.5168 | 217.5 | 608.0168 | 965.2874 | 1
185 | 16 | 521 | 202 |  | 0.3989 | 1.7903 | -4.0193 | 2.7007 | 16.045 | 1.059 | 35.6262 | 294.9758 | 168.3333 | 463.3091 | 735.5496 | 1
185 | 17 | 158 | 231 |  | 0.3989 | 1.7903 | -4.0193 | 2.7007 | 17.045 | 1.3208 | 26.5582 | 56.8998 | 192.5 | 249.3998 | 395.9472 | 1
185 | 18 | 104 | 157 |  | 0.3989 | 1.7903 | -4.0193 | 2.7007 | 18.045 | 1.5826 | 17.5957 | 14.5332 | 130.8333 | 145.3666 | 230.784 | 1
185 | 19 | 44 | 95 |  | 0.3989 | 1.7903 | -4.0193 | 2.7007 | 19.045 | 1.8444 | 9.0873 | 0 | 79.1667 | 79.1667 | 125.685 | 0
185 | 20 | 0 | 14 |  | 0.3989 | 1.7903 | -4.0193 | 2.7007 | 20.045 | 2.1062 | 1.3675 | 0 | 11.6667 | 11.6667 | 18.522 | 0
185 | 21 | 0 | 1 |  | 0.3989 | 1.7903 | -4.0193 | 2.7007 | 21.045 | 2.368 | -5.2087 | 0 | 0.83333 | 0.83333 | 1.323 | 0
185 | 22 | 0 | 0 |  | 0.3989 | 1.7903 | -4.0193 | 2.7007 | 22.045 | 2.6298 | -10.2648 | 0 | 0 | 0 | 0 | 0
185 | 23 | 0 | 0 |  | 0.3989 | 1.7903 | -4.0193 | 2.7007 | 23.045 | 2.8916 | -13.4394 | 0 | 0 | 0 | 0 | 0
185 | 24 | 0 | 0 |  | 0.3989 | 1.7903 | -4.0193 | 2.7007 | 24.045 | 3.1534 | -14.4626 | 0 | 0 | 0 | 0 | 0
186 | 1 | 0 | 0 |  | 0.39722 | 1.8075 | -4.1923 | 2.5277 | 1.0421 | -2.8688 | -13.3404 | 0 | 0 | 0 | 0 | 0
186 | 2 | 0 | 0 |  | 0.39722 | 1.8075 | -4.1923 | 2.5277 | 2.0421 | -2.607 | -9.9856 | 0 | 0 | 0 | 0 | 0
186 | 3 | 0 | 0 |  | 0.39722 | 1.8075 | -4.1923 | 2.5277 | 3.0421 | -2.3452 | -4.7773 | 0 | 0 | 0 | 0 | 0
186 | 4 | 0 | 1 |  | 0.39722 | 1.8075 | -4.1923 | 2.5277 | 4.0421 | -2.0834 | 1.9183 | 0 | 0.83333 | 0.83333 | 1.323 | 0
186 | 5 | 0 | 30 |  | 0.39722 | 1.8075 | -4.1923 | 2.5277 | 5.0421 | -1.8216 | 9.7249 | 0 | 25 | 25 | 39.69 | 0
186 | 6 | 237 | 79 |  | 0.39722 | 1.8075 | -4.1923 | 2.5277 | 6.0421 | -1.5598 | 18.2893 | 37.576 | 65.8333 | 103.4093 | 164.1726 | 1
186 | 7 | 387 | 135 |  | 0.39722 | 1.8075 | -4.1923 | 2.5277 | 7.0421 | -1.298 | 27.277 | 146.4514 | 112.5 | 258.9514 | 411.1113 | 1
186 | 8 | 529 | 150 |  | 0.39722 | 1.8075 | -4.1923 | 2.5277 | 8.0421 | -1.0362 | 36.3349 | 308.2391 | 125 | 433.2391 | 687.8104 | 1
186 | 9 | 343 | 274 |  | 0.39722 | 1.8075 | -4.1923 | 2.5277 | 9.0421 | -0.77437 | 45.0159 | 259.7862 | 228.3333 | 488.1196 | 774.9386 | 1
186 | 10 | 84 | 339 |  | 0.39722 | 1.8075 | -4.1923 | 2.5277 | 10.0421 | -0.51257 | 52.6426 | 74.8151 | 282.5 | 357.3151 | 567.2735 | 1
186 | 11 | 58 | 404 |  | 0.39722 | 1.8075 | -4.1923 | 2.5277 | 11.0421 | -0.25077 | 58.1276 | 56.4564 | 336.6667 | 393.1231 | 624.1222 | 1
186 | 12 | 259 | 389 |  | 0.39722 | 1.8075 | -4.1923 | 2.5277 | 12.0421 | 0.011029 | 60.0749 | 258.9864 | 324.1667 | 583.153 | 925.8137 | 1
186 | 13 | 95 | 393 |  | 0.39722 | 1.8075 | -4.1923 | 2.5277 | 13.0421 | 0.27283 | 57.7829 | 92.0102 | 327.5 | 419.5102 | 666.0145 | 1
186 | 14 | 57 | 400 |  | 0.39722 | 1.8075 | -4.1923 | 2.5277 | 14.0421 | 0.53463 | 52.0642 | 50.2325 | 333.3333 | 383.5658 | 608.9491 | 1
186 | 15 | 359 | 323 |  | 0.39722 | 1.8075 | -4.1923 | 2.5277 | 15.0421 | 0.79643 | 44.3134 | 267.1403 | 269.1667 | 536.3069 | 851.4409 | 1
186 | 16 | 201 | 290 |  | 0.39722 | 1.8075 | -4.1923 | 2.5277 | 16.0421 | 1.0582 | 35.5789 | 113.8522 | 241.6667 | 355.5189 | 564.4218 | 1
186 | 17 | 73 | 204 |  | 0.39722 | 1.8075 | -4.1923 | 2.5277 | 17.0421 | 1.32 | 26.5117 | 26.3018 | 170 | 196.3018 | 311.6488 | 1
186 | 18 | 17 | 146 |  | 0.39722 | 1.8075 | -4.1923 | 2.5277 | 18.0421 | 1.5818 | 17.5467 | 2.3763 | 121.6667 | 124.0429 | 196.9306 | 1
186 | 19 | 0 | 70 |  | 0.39722 | 1.8075 | -4.1923 | 2.5277 | 19.0421 | 1.8436 | 9.0332 | 0 | 58.3333 | 58.3333 | 92.61 | 0
186 | 20 | 0 | 14 |  | 0.39722 | 1.8075 | -4.1923 | 2.5277 | 20.0421 | 2.1054 | 1.3062 | 0 | 11.6667 | 11.6667 | 18.522 | 0
186 | 21 | 0 | 0 |  | 0.39722 | 1.8075 | -4.1923 | 2.5277 | 21.0421 | 2.3672 | -5.2789 | 0 | 0 | 0 | 0 | 0
186 | 22 | 0 | 0 |  | 0.39722 | 1.8075 | -4.1923 | 2.5277 | 22.0421 | 2.629 | -10.3445 | 0 | 0 | 0 | 0 | 0
186 | 23 | 0 | 0 |  | 0.39722 | 1.8075 | -4.1923 | 2.5277 | 23.0421 | 2.8908 | -13.5284 | 0 | 0 | 0 | 0 | 0
186 | 24 | 0 | 0 |  | 0.39722 | 1.8075 | -4.1923 | 2.5277 | 24.0421 | 3.1526 | -14.5592 | 0 | 0 | 0 | 0 | 0
187 | 1 | 0 | 0 |  | 0.39541 | 1.8247 | -4.36 | 2.36 | 1.0393 | -2.8695 | -13.4487 | 0 | 0 | 0 | 0 | 0
187 | 2 | 0 | 0 |  | 0.39541 | 1.8247 | -4.36 | 2.36 | 2.0393 | -2.6077 | -10.0958 | 0 | 0 | 0 | 0 | 0
187 | 3 | 0 | 0 |  | 0.39541 | 1.8247 | -4.36 | 2.36 | 3.0393 | -2.3459 | -4.8872 | 0 | 0 | 0 | 0 | 0
187 | 4 | 0 | 1 |  | 0.39541 | 1.8247 | -4.36 | 2.36 | 4.0393 | -2.0841 | 1.8102 | 0 | 0.83333 | 0.83333 | 1.323 | 0
187 | 5 | 0 | 29 |  | 0.39541 | 1.8247 | -4.36 | 2.36 | 5.0393 | -1.8223 | 9.6189 | 0 | 24.1667 | 24.1667 | 38.367 | 0
187 | 6 | 0 | 75 |  | 0.39541 | 1.8247 | -4.36 | 2.36 | 6.0393 | -1.5605 | 18.1851 | 0 | 62.5 | 62.5 | 99.225 | 1
187 | 7 | 218 | 200 |  | 0.39541 | 1.8247 | -4.36 | 2.36 | 7.0393 | -1.2987 | 27.1737 | 82.2643 | 166.6667 | 248.9309 | 395.2027 | 1
187 | 8 | 594 | 129 |  | 0.39541 | 1.8247 | -4.36 | 2.36 | 8.0393 | -1.0369 | 36.2311 | 345.6083 | 107.5 | 453.1083 | 719.3548 | 1
187 | 9 | 528 | 203 |  | 0.39541 | 1.8247 | -4.36 | 2.36 | 9.0393 | -0.7751 | 44.91 | 399.5778 | 169.1667 | 568.7444 | 902.9387 | 1
187 | 10 | 542 | 256 |  | 0.39541 | 1.8247 | -4.36 | 2.36 | 10.0393 | -0.5133 | 52.5336 | 482.5256 | 213.3333 | 695.8589 | 1104.7456 | 1
187 | 11 | 654 | 246 |  | 0.39541 | 1.8247 | -4.36 | 2.36 | 11.0393 | -0.2515 | 58.0175 | 636.4808 | 205 | 841.4808 | 1335.9349 | 1
187 | 12 | 457 | 326 |  | 0.39541 | 1.8247 | -4.36 | 2.36 | 12.0393 | 0.010298 | 59.9721 | 456.9793 | 271.6667 | 728.646 | 1156.7984 | 1
187 | 13 | 651 | 268 |  | 0.39541 | 1.8247 | -4.36 | 2.36 | 13.0393 | 0.2721 | 57.6964 | 630.6065 | 223.3333 | 853.9398 | 1355.7149 | 1
187 | 14 | 450 | 308 |  | 0.39541 | 1.8247 | -4.36 | 2.36 | 14.0393 | 0.5339 | 51.9942 | 396.6752 | 256.6667 | 653.3419 | 1037.2456 | 1
187 | 15 | 215 | 357 |  | 0.39541 | 1.8247 | -4.36 | 2.36 | 15.0393 | 0.7957 | 44.2546 | 160.0409 | 297.5 | 457.5409 | 726.3919 | 1
187 | 16 | 221 | 282 |  | 0.39541 | 1.8247 | -4.36 | 2.36 | 16.0393 | 1.0575 | 35.5255 | 125.2287 | 235 | 360.2287 | 571.899 | 1
187 | 17 | 45 | 221 |  | 0.39541 | 1.8247 | -4.36 | 2.36 | 17.0393 | 1.3193 | 26.4591 | 16.2189 | 184.1667 | 200.3856 | 318.1322 | 1
187 | 18 | 18 | 146 |  | 0.39541 | 1.8247 | -4.36 | 2.36 | 18.0393 | 1.5811 | 17.4916 | 2.5156 | 121.6667 | 124.1823 | 197.1517 | 1
187 | 19 | 0 | 70 |  | 0.39541 | 1.8247 | -4.36 | 2.36 | 19.0393 | 1.8429 | 8.9727 | 0 | 58.3333 | 58.3333 | 92.61 | 0
187 | 20 | 0 | 21 |  | 0.39541 | 1.8247 | -4.36 | 2.36 | 20.0393 | 2.1047 | 1.2382 | 0 | 17.5 | 17.5 | 27.783 | 0
187 | 21 | 0 | 0 |  | 0.39541 | 1.8247 | -4.36 | 2.36 | 21.0393 | 2.3665 | -5.3559 | 0 | 0 | 0 | 0 | 0
187 | 22 | 0 | 0 |  | 0.39541 | 1.8247 | -4.36 | 2.36 | 22.0393 | 2.6283 | -10.4313 | 0 | 0 | 0 | 0 | 0
187 | 23 | 0 | 0 |  | 0.39541 | 1.8247 | -4.36 | 2.36 | 23.0393 | 2.8901 | -13.6245 | 0 | 0 | 0 | 0 | 0
187 | 24 | 0 | 0 |  | 0.39541 | 1.8247 | -4.36 | 2.36 | 24.0393 | 3.1519 | -14.6627 | 0 | 0 | 0 | 0 | 0
188 | 1 | 0 | 0 |  | 0.39349 | 1.8419 | -4.5221 | 2.1979 | 1.0366 | -2.8702 | -13.5637 | 0 | 0 | 0 | 0 | 0
188 | 2 | 0 | 0 |  | 0.39349 | 1.8419 | -4.5221 | 2.1979 | 2.0366 | -2.6084 | -10.2123 | 0 | 0 | 0 | 0 | 0
188 | 3 | 0 | 0 |  | 0.39349 | 1.8419 | -4.5221 | 2.1979 | 3.0366 | -2.3466 | -5.0028 | 0 | 0 | 0 | 0 | 0
188 | 4 | 0 | 1 |  | 0.39349 | 1.8419 | -4.5221 | 2.1979 | 4.0366 | -2.0848 | 1.6967 | 0 | 0.83333 | 0.83333 | 1.323 | 0
188 | 5 | 0 | 29 |  | 0.39349 | 1.8419 | -4.5221 | 2.1979 | 5.0366 | -1.823 | 9.508 | 0 | 24.1667 | 24.1667 | 38.367 | 0
188 | 6 | 200 | 86 |  | 0.39349 | 1.8419 | -4.5221 | 2.1979 | 6.0366 | -1.5612 | 18.0763 | 31.2019 | 71.6667 | 102.8686 | 163.3142 | 1
188 | 7 | 390 | 133 |  | 0.39349 | 1.8419 | -4.5221 | 2.1979 | 7.0366 | -1.2994 | 27.0659 | 146.7477 | 110.8333 | 257.5811 | 408.9357 | 1
188 | 8 | 568 | 147 |  | 0.39349 | 1.8419 | -4.5221 | 2.1979 | 8.0366 | -1.0376 | 36.1227 | 329.9939 | 122.5 | 452.4939 | 718.3792 | 1
188 | 9 | 677 | 152 |  | 0.39349 | 1.8419 | -4.5221 | 2.1979 | 9.0366 | -0.77581 | 44.7992 | 511.9178 | 126.6667 | 638.5845 | 1013.8168 | 1
188 | 10 | 683 | 183 |  | 0.39349 | 1.8419 | -4.5221 | 2.1979 | 10.0366 | -0.51401 | 52.419 | 607.7892 | 152.5 | 760.2892 | 1207.0351 | 1
188 | 11 | 756 | 182 |  | 0.39349 | 1.8419 | -4.5221 | 2.1979 | 11.0366 | -0.25221 | 57.9011 | 735.6166 | 151.6667 | 887.2833 | 1408.651 | 1
188 | 12 | 821 | 155 |  | 0.39349 | 1.8419 | -4.5221 | 2.1979 | 12.0366 | 0.0095901 | 59.8622 | 820.9656 | 129.1667 | 950.1322 | 1508.4299 | 1
188 | 13 | 796 | 167 |  | 0.39349 | 1.8419 | -4.5221 | 2.1979 | 13.0366 | 0.27139 | 57.6026 | 771.1709 | 139.1667 | 910.3375 | 1445.2519 | 1
188 | 14 | 694 | 213 |  | 0.39349 | 1.8419 | -4.5221 | 2.1979 | 14.0366 | 0.53319 | 51.9174 | 611.9063 | 177.5 | 789.4063 | 1253.2615 | 1
188 | 15 | 753 | 150 |  | 0.39349 | 1.8419 | -4.5221 | 2.1979 | 15.0366 | 0.79499 | 44.1892 | 560.6831 | 125 | 685.6831 | 1088.5905 | 1
188 | 16 | 676 | 149 |  | 0.39349 | 1.8419 | -4.5221 | 2.1979 | 16.0366 | 1.0568 | 35.4658 | 383.1706 | 124.1667 | 507.3373 | 805.4486 | 1
188 | 17 | 605 | 125 |  | 0.39349 | 1.8419 | -4.5221 | 2.1979 | 17.0366 | 1.3186 | 26.4004 | 218.0957 | 104.1667 | 322.2624 | 511.6237 | 1
188 | 18 | 398 | 123 |  | 0.39349 | 1.8419 | -4.5221 | 2.1979 | 18.0366 | 1.5804 | 17.4302 | 55.5868 | 102.5 | 158.0868 | 250.9785 | 1
188 | 19 | 148 | 90 |  | 0.39349 | 1.8419 | -4.5221 | 2.1979 | 19.0366 | 1.8422 | 8.9058 | 0 | 75 | 75 | 119.07 | 0
188 | 20 | 0 | 24 |  | 0.39349 | 1.8419 | -4.5221 | 2.1979 | 20.0366 | 2.104 | 1.1637 | 0 | 20 | 20 | 31.752 | 0
188 | 21 | 0 | 1 |  | 0.39349 | 1.8419 | -4.5221 | 2.1979 | 21.0366 | 2.3658 | -5.4397 | 0 | 0.83333 | 0.83333 | 1.323 | 0
188 | 22 | 0 | 0 |  | 0.39349 | 1.8419 | -4.5221 | 2.1979 | 22.0366 | 2.6276 | -10.5251 | 0 | 0 | 0 | 0 | 0
188 | 23 | 0 | 0 |  | 0.39349 | 1.8419 | -4.5221 | 2.1979 | 23.0366 | 2.8894 | -13.7276 | 0 | 0 | 0 | 0 | 0
188 | 24 | 0 | 0 |  | 0.39349 | 1.8419 | -4.5221 | 2.1979 | 24.0366 | 3.1512 | -14.7733 | 0 | 0 | 0 | 0 | 0
189 | 1 | 0 | 0 |  | 0.39144 | 1.8591 | -4.6784 | 2.0416 | 1.034 | -2.8709 | -13.6854 | 0 | 0 | 0 | 0 | 0
189 | 2 | 0 | 0 |  | 0.39144 | 1.8591 | -4.6784 | 2.0416 | 2.034 | -2.6091 | -10.335 | 0 | 0 | 0 | 0 | 0
189 | 3 | 0 | 0 |  | 0.39144 | 1.8591 | -4.6784 | 2.0416 | 3.034 | -2.3473 | -5.1241 | 0 | 0 | 0 | 0 | 0
189 | 4 | 0 | 0 |  | 0.39144 | 1.8591 | -4.6784 | 2.0416 | 4.034 | -2.0855 | 1.5781 | 0 | 0 | 0 | 0 | 0
189 | 5 | 0 | 10 |  | 0.39144 | 1.8591 | -4.6784 | 2.0416 | 5.034 | -1.8237 | 9.3922 | 0 | 8.3333 | 8.3333 | 13.23 | 0
189 | 6 | 0 | 46 |  | 0.39144 | 1.8591 | -4.6784 | 2.0416 | 6.034 | -1.5619 | 17.9629 | 0 | 38.3333 | 38.3333 | 60.858 | 1
189 | 7 | 55 | 137 |  | 0.39144 | 1.8591 | -4.6784 | 2.0416 | 7.034 | -1.3001 | 26.9536 | 20.6349 | 114.1667 | 134.8016 | 214.011 | 1
189 | 8 | 1 | 156 |  | 0.39144 | 1.8591 | -4.6784 | 2.0416 | 8.034 | -1.0383 | 36.0099 | 0.58011 | 130 | 130.5801 | 207.309 | 1
189 | 9 | 9 | 203 |  | 0.39144 | 1.8591 | -4.6784 | 2.0416 | 9.034 | -0.77649 | 44.6836 | 6.7998 | 169.1667 | 175.9665 | 279.3644 | 1
189 | 10 | 13 | 244 |  | 0.39144 | 1.8591 | -4.6784 | 2.0416 | 10.034 | -0.51469 | 52.299 | 11.5634 | 203.3333 | 214.8968 | 341.1701 | 1
189 | 11 | 11 | 275 |  | 0.39144 | 1.8591 | -4.6784 | 2.0416 | 11.034 | -0.25289 | 57.7784 | 10.7015 | 229.1667 | 239.8682 | 380.8147 | 1
189 | 12 | 125 | 372 |  | 0.39144 | 1.8591 | -4.6784 | 2.0416 | 12.034 | 0.0089083 | 59.7454 | 124.9946 | 310 | 434.9946 | 690.5974 | 1
189 | 13 | 277 | 377 |  | 0.39144 | 1.8591 | -4.6784 | 2.0416 | 13.034 | 0.27071 | 57.5018 | 268.3936 | 314.1667 | 582.5603 | 924.8727 | 1
189 | 14 | 543 | 291 |  | 0.39144 | 1.8591 | -4.6784 | 2.0416 | 14.034 | 0.53251 | 51.8338 | 478.8704 | 242.5 | 721.3704 | 1145.2477 | 1
189 | 15 | 191 | 370 |  | 0.39144 | 1.8591 | -4.6784 | 2.0416 | 15.034 | 0.79431 | 44.1174 | 142.255 | 308.3333 | 450.5884 | 715.3541 | 1
189 | 16 | 70 | 283 |  | 0.39144 | 1.8591 | -4.6784 | 2.0416 | 16.034 | 1.0561 | 35.3998 | 39.6867 | 235.8333 | 275.52 | 437.4156 | 1
189 | 17 | 31 | 226 |  | 0.39144 | 1.8591 | -4.6784 | 2.0416 | 17.034 | 1.3179 | 26.3354 | 11.1756 | 188.3333 | 199.5089 | 316.7404 | 1
189 | 18 | 17 | 145 |  | 0.39144 | 1.8591 | -4.6784 | 2.0416 | 18.034 | 1.5797 | 17.3625 | 2.3717 | 120.8333 | 123.205 | 195.6003 | 1
189 | 19 | 0 | 69 |  | 0.39144 | 1.8591 | -4.6784 | 2.0416 | 19.034 | 1.8415 | 8.8326 | 0 | 57.5 | 57.5 | 91.287 | 0
189 | 20 | 0 | 13 |  | 0.39144 | 1.8591 | -4.6784 | 2.0416 | 20.034 | 2.1033 | 1.0825 | 0 | 10.8333 | 10.8333 | 17.199 | 0
189 | 21 | 0 | 0 |  | 0.39144 | 1.8591 | -4.6784 | 2.0416 | 21.034 | 2.3651 | -5.5304 | 0 | 0 | 0 | 0 | 0
189 | 22 | 0 | 0 |  | 0.39144 | 1.8591 | -4.6784 | 2.0416 | 22.034 | 2.6269 | -10.6259 | 0 | 0 | 0 | 0 | 0
189 | 23 | 0 | 0 |  | 0.39144 | 1.8591 | -4.6784 | 2.0416 | 23.034 | 2.8887 | -13.8378 | 0 | 0 | 0 | 0 | 0
189 | 24 | 0 | 0 |  | 0.39144 | 1.8591 | -4.6784 | 2.0416 | 24.034 | 3.1505 | -14.8908 | 0 | 0 | 0 | 0 | 0
190 | 1 | 0 | 0 |  | 0.38927 | 1.8763 | -4.8285 | 1.8915 | 1.0315 | -2.8715 | -13.8136 | 0 | 0 | 0 | 0 | 0
190 | 2 | 0 | 0 |  | 0.38927 | 1.8763 | -4.8285 | 1.8915 | 2.0315 | -2.6097 | -10.4638 | 0 | 0 | 0 | 0 | 0
190 | 3 | 0 | 0 |  | 0.38927 | 1.8763 | -4.8285 | 1.8915 | 3.0315 | -2.3479 | -5.2511 | 0 | 0 | 0 | 0 | 0
190 | 4 | 0 | 1 |  | 0.38927 | 1.8763 | -4.8285 | 1.8915 | 4.0315 | -2.0861 | 1.4543 | 0 | 0.83333 | 0.83333 | 1.323 | 0
190 | 5 | 0 | 25 |  | 0.38927 | 1.8763 | -4.8285 | 1.8915 | 5.0315 | -1.8243 | 9.2718 | 0 | 20.8333 | 20.8333 | 33.075 | 0
190 | 6 | 87 | 88 |  | 0.38927 | 1.8763 | -4.8285 | 1.8915 | 6.0315 | -1.5625 | 17.8451 | 13.3441 | 73.3333 | 86.6774 | 137.6091 | 1
190 | 7 | 75 | 171 |  | 0.38927 | 1.8763 | -4.8285 | 1.8915 | 7.0315 | -1.3007 | 26.8371 | 28.0554 | 142.5 | 170.5554 | 270.7738 | 1
190 | 8 | 344 | 223 |  | 0.38927 | 1.8763 | -4.8285 | 1.8915 | 8.0315 | -1.0389 | 35.8926 | 199.2598 | 185.8333 | 385.0932 | 611.3739 | 1
190 | 9 | 65 | 289 |  | 0.38927 | 1.8763 | -4.8285 | 1.8915 | 9.0315 | -0.77714 | 44.5633 | 49.0694 | 240.8333 | 289.9027 | 460.2495 | 1
190 | 10 | 8 | 247 |  | 0.38927 | 1.8763 | -4.8285 | 1.8915 | 10.0315 | -0.51535 | 52.1737 | 7.1129 | 205.8333 | 212.9462 | 338.0734 | 1
190 | 11 | 124 | 351 |  | 0.38927 | 1.8763 | -4.8285 | 1.8915 | 11.0315 | -0.25355 | 57.6495 | 120.6131 | 292.5 | 413.1131 | 655.8584 | 1
190 | 12 | 89 | 402 |  | 0.38927 | 1.8763 | -4.8285 | 1.8915 | 12.0315 | 0.0082533 | 59.6215 | 88.9955 | 335 | 423.9955 | 673.1352 | 1
190 | 13 | 434 | 452 |  | 0.38927 | 1.8763 | -4.8285 | 1.8915 | 13.0315 | 0.27005 | 57.3938 | 420.5632 | 376.6667 | 797.2299 | 1265.6822 | 1
190 | 14 | 563 | 275 |  | 0.38927 | 1.8763 | -4.8285 | 1.8915 | 14.0315 | 0.53185 | 51.7433 | 496.6021 | 229.1667 | 725.7688 | 1152.2305 | 1
190 | 15 | 724 | 167 |  | 0.38927 | 1.8763 | -4.8285 | 1.8915 | 15.0315 | 0.79365 | 44.0392 | 539.3437 | 139.1667 | 678.5103 | 1077.203 | 1
190 | 16 | 686 | 140 |  | 0.38927 | 1.8763 | -4.8285 | 1.8915 | 16.0315 | 1.0555 | 35.3276 | 388.9901 | 116.6667 | 505.6567 | 802.7806 | 1
190 | 17 | 602 | 122 |  | 0.38927 | 1.8763 | -4.8285 | 1.8915 | 17.0315 | 1.3173 | 26.2643 | 216.9979 | 101.6667 | 318.6646 | 505.9119 | 1
190 | 18 | 404 | 116 |  | 0.38927 | 1.8763 | -4.8285 | 1.8915 | 18.0315 | 1.579 | 17.2886 | 56.2732 | 96.6667 | 152.9398 | 242.8073 | 1
190 | 19 | 174 | 83 |  | 0.38927 | 1.8763 | -4.8285 | 1.8915 | 19.0315 | 1.8408 | 8.753 | 0 | 69.1667 | 69.1667 | 109.809 | 0
190 | 20 | 0 | 23 |  | 0.38927 | 1.8763 | -4.8285 | 1.8915 | 20.0315 | 2.1026 | 0.99476 | 0 | 19.1667 | 19.1667 | 30.429 | 0
190 | 21 | 0 | 0 |  | 0.38927 | 1.8763 | -4.8285 | 1.8915 | 21.0315 | 2.3644 | -5.6279 | 0 | 0 | 0 | 0 | 0
190 | 22 | 0 | 0 |  | 0.38927 | 1.8763 | -4.8285 | 1.8915 | 22.0315 | 2.6262 | -10.7337 | 0 | 0 | 0 | 0 | 0
190 | 23 | 0 | 0 |  | 0.38927 | 1.8763 | -4.8285 | 1.8915 | 23.0315 | 2.888 | -13.9551 | 0 | 0 | 0 | 0 | 0
190 | 24 | 0 | 0 |  | 0.38927 | 1.8763 | -4.8285 | 1.8915 | 24.0315 | 3.1498 | -15.0152 | 0 | 0 | 0 | 0 | 0
191 | 1 | 0 | 0 |  | 0.38699 | 1.8936 | -4.9721 | 1.7479 | 1.0291 | -2.8722 | -13.9484 | 0 | 0 | 0 | 0 | 0
191 | 2 | 0 | 0 |  | 0.38699 | 1.8936 | -4.9721 | 1.7479 | 2.0291 | -2.6104 | -10.5987 | 0 | 0 | 0 | 0 | 0
191 | 3 | 0 | 0 |  | 0.38699 | 1.8936 | -4.9721 | 1.7479 | 3.0291 | -2.3486 | -5.3836 | 0 | 0 | 0 | 0 | 0
191 | 4 | 0 | 0 |  | 0.38699 | 1.8936 | -4.9721 | 1.7479 | 4.0291 | -2.0868 | 1.3254 | 0 | 0 | 0 | 0 | 0
191 | 5 | 0 | 15 |  | 0.38699 | 1.8936 | -4.9721 | 1.7479 | 5.0291 | -1.825 | 9.1466 | 0 | 12.5 | 12.5 | 19.845 | 0
191 | 6 | 103 | 83 |  | 0.38699 | 1.8936 | -4.9721 | 1.7479 | 6.0291 | -1.5632 | 17.7228 | 15.6597 | 69.1667 | 84.8263 | 134.6703 | 1
191 | 7 | 75 | 170 |  | 0.38699 | 1.8936 | -4.9721 | 1.7479 | 7.0291 | -1.3014 | 26.7163 | 27.9715 | 141.6667 | 169.6381 | 269.3175 | 1
191 | 8 | 0 | 154 |  | 0.38699 | 1.8936 | -4.9721 | 1.7479 | 8.0291 | -1.0396 | 35.771 | 0 | 128.3333 | 128.3333 | 203.742 | 1
191 | 9 | 65 | 288 |  | 0.38699 | 1.8936 | -4.9721 | 1.7479 | 9.0291 | -0.77777 | 44.4383 | 49.0289 | 240 | 289.0289 | 458.8623 | 1
191 | 10 | 71 | 348 |  | 0.38699 | 1.8936 | -4.9721 | 1.7479 | 10.0291 | -0.51597 | 52.0431 | 63.0994 | 290 | 353.0994 | 560.5806 | 1
191 | 11 | 88 | 380 |  | 0.38699 | 1.8936 | -4.9721 | 1.7479 | 11.0291 | -0.25417 | 57.5144 | 85.5808 | 316.6667 | 402.2475 | 638.6081 | 1
191 | 12 | 88 | 401 |  | 0.38699 | 1.8936 | -4.9721 | 1.7479 | 12.0291 | 0.0076266 | 59.4908 | 87.9944 | 334.1667 | 422.161 | 670.2229 | 1
191 | 13 | 88 | 401 |  | 0.38699 | 1.8936 | -4.9721 | 1.7479 | 13.0291 | 0.26943 | 57.2787 | 85.284 | 334.1667 | 419.4506 | 665.9198 | 1
191 | 14 | 87 | 378 |  | 0.38699 | 1.8936 | -4.9721 | 1.7479 | 14.0291 | 0.53123 | 51.646 | 76.7521 | 315 | 391.7521 | 621.9456 | 1
191 | 15 | 72 | 345 |  | 0.38699 | 1.8936 | -4.9721 | 1.7479 | 15.0291 | 0.79302 | 43.9544 | 53.6454 | 287.5 | 341.1454 | 541.6025 | 1
191 | 16 | 66 | 284 |  | 0.38699 | 1.8936 | -4.9721 | 1.7479 | 16.0291 | 1.0548 | 35.249 | 37.4276 | 236.6667 | 274.0942 | 435.152 | 1
191 | 17 | 162 | 226 |  | 0.38699 | 1.8936 | -4.9721 | 1.7479 | 17.0291 | 1.3166 | 26.1869 | 58.379 | 188.3333 | 246.7123 | 391.6805 | 1
191 | 18 | 66 | 148 |  | 0.38699 | 1.8936 | -4.9721 | 1.7479 | 18.0291 | 1.5784 | 17.2085 | 9.1742 | 123.3333 | 132.5075 | 210.3689 | 1
191 | 19 | 0 | 67 |  | 0.38699 | 1.8936 | -4.9721 | 1.7479 | 19.0291 | 1.8402 | 8.6669 | 0 | 55.8333 | 55.8333 | 88.641 | 0
191 | 20 | 0 | 13 |  | 0.38699 | 1.8936 | -4.9721 | 1.7479 | 20.0291 | 2.102 | 0.90042 | 0 | 10.8333 | 10.8333 | 17.199 | 0
191 | 21 | 0 | 0 |  | 0.38699 | 1.8936 | -4.9721 | 1.7479 | 21.0291 | 2.3638 | -5.7321 | 0 | 0 | 0 | 0 | 0
191 | 22 | 0 | 0 |  | 0.38699 | 1.8936 | -4.9721 | 1.7479 | 22.0291 | 2.6256 | -10.8484 | 0 | 0 | 0 | 0 | 0
191 | 23 | 0 | 0 |  | 0.38699 | 1.8936 | -4.9721 | 1.7479 | 23.0291 | 2.8874 | -14.0793 | 0 | 0 | 0 | 0 | 0
191 | 24 | 0 | 0 |  | 0.38699 | 1.8936 | -4.9721 | 1.7479 | 24.0291 | 3.1492 | -15.1464 | 0 | 0 | 0 | 0 | 0
192 | 1 | 0 | 0 |  | 0.38458 | 1.9108 | -5.109 | 1.611 | 1.0268 | -2.8728 | -14.0896 | 0 | 0 | 0 | 0 | 0
192 | 2 | 0 | 0 |  | 0.38458 | 1.9108 | -5.109 | 1.611 | 2.0268 | -2.611 | -10.7395 | 0 | 0 | 0 | 0 | 0
192 | 3 | 0 | 0 |  | 0.38458 | 1.9108 | -5.109 | 1.611 | 3.0268 | -2.3492 | -5.5215 | 0 | 0 | 0 | 0 | 0
192 | 4 | 0 | 0 |  | 0.38458 | 1.9108 | -5.109 | 1.611 | 4.0268 | -2.0874 | 1.1916 | 0 | 0 | 0 | 0 | 0
192 | 5 | 0 | 14 |  | 0.38458 | 1.9108 | -5.109 | 1.611 | 5.0268 | -1.8256 | 9.0169 | 0 | 11.6667 | 11.6667 | 18.522 | 0
192 | 6 | 0 | 70 |  | 0.38458 | 1.9108 | -5.109 | 1.611 | 6.0268 | -1.5638 | 17.5963 | 0 | 58.3333 | 58.3333 | 92.61 | 1
192 | 7 | 16 | 147 |  | 0.38458 | 1.9108 | -5.109 | 1.611 | 7.0268 | -1.302 | 26.5912 | 5.9492 | 122.5 | 128.4492 | 203.9259 | 1
192 | 8 | 31 | 228 |  | 0.38458 | 1.9108 | -5.109 | 1.611 | 8.0268 | -1.0402 | 35.6452 | 17.9023 | 190 | 207.9023 | 330.0657 | 1
192 | 9 | 66 | 287 |  | 0.38458 | 1.9108 | -5.109 | 1.611 | 9.0268 | -0.77837 | 44.3087 | 49.7421 | 239.1667 | 288.9088 | 458.6715 | 1
192 | 10 | 71 | 347 |  | 0.38458 | 1.9108 | -5.109 | 1.611 | 10.0268 | -0.51657 | 51.9072 | 63.0721 | 289.1667 | 352.2387 | 559.2142 | 1
192 | 11 | 87 | 379 |  | 0.38458 | 1.9108 | -5.109 | 1.611 | 11.0268 | -0.25477 | 57.3732 | 84.5927 | 315.8333 | 400.426 | 635.7163 | 1
192 | 12 | 89 | 401 |  | 0.38458 | 1.9108 | -5.109 | 1.611 | 12.0268 | 0.0070293 | 59.3533 | 88.9925 | 334.1667 | 423.1591 | 671.8075 | 1
192 | 13 | 88 | 400 |  | 0.38458 | 1.9108 | -5.109 | 1.611 | 13.0268 | 0.26883 | 57.1566 | 85.2911 | 333.3333 | 418.6245 | 664.6082 | 1
192 | 14 | 26 | 260 |  | 0.38458 | 1.9108 | -5.109 | 1.611 | 14.0268 | 0.53063 | 51.5418 | 22.9405 | 216.6667 | 239.6072 | 380.4003 | 1
192 | 15 | 70 | 345 |  | 0.38458 | 1.9108 | -5.109 | 1.611 | 15.0268 | 0.79243 | 43.863 | 52.1616 | 287.5 | 339.6616 | 539.2468 | 1
192 | 16 | 66 | 284 |  | 0.38458 | 1.9108 | -5.109 | 1.611 | 16.0268 | 1.0542 | 35.1642 | 37.4274 | 236.6667 | 274.094 | 435.1517 | 1
192 | 17 | 31 | 224 |  | 0.38458 | 1.9108 | -5.109 | 1.611 | 17.0268 | 1.316 | 26.1033 | 11.1665 | 186.6667 | 197.8332 | 314.0799 | 1
192 | 18 | 0 | 93 |  | 0.38458 | 1.9108 | -5.109 | 1.611 | 18.0268 | 1.5778 | 17.1221 | 0 | 77.5 | 77.5 | 123.039 | 1
192 | 19 | 0 | 67 |  | 0.38458 | 1.9108 | -5.109 | 1.611 | 19.0268 | 1.8396 | 8.5745 | 0 | 55.8333 | 55.8333 | 88.641 | 0
192 | 20 | 0 | 13 |  | 0.38458 | 1.9108 | -5.109 | 1.611 | 20.0268 | 2.1014 | 0.79952 | 0 | 10.8333 | 10.8333 | 17.199 | 0
192 | 21 | 0 | 0 |  | 0.38458 | 1.9108 | -5.109 | 1.611 | 21.0268 | 2.3632 | -5.8432 | 0 | 0 | 0 | 0 | 0
192 | 22 | 0 | 0 |  | 0.38458 | 1.9108 | -5.109 | 1.611 | 22.0268 | 2.625 | -10.97 | 0 | 0 | 0 | 0 | 0
192 | 23 | 0 | 0 |  | 0.38458 | 1.9108 | -5.109 | 1.611 | 23.0268 | 2.8868 | -14.2104 | 0 | 0 | 0 | 0 | 0
192 | 24 | 0 | 0 |  | 0.38458 | 1.9108 | -5.109 | 1.611 | 24.0268 | 3.1486 | -15.2843 | 0 | 0 | 0 | 0 | 0
193 | 1 | 0 | 0 |  | 0.38206 | 1.928 | -5.2389 | 1.4811 | 1.0247 | -2.8733 | -14.2371 | 0 | 0 | 0 | 0 | 0
193 | 2 | 0 | 0 |  | 0.38206 | 1.928 | -5.2389 | 1.4811 | 2.0247 | -2.6115 | -10.8863 | 0 | 0 | 0 | 0 | 0
193 | 3 | 0 | 0 |  | 0.38206 | 1.928 | -5.2389 | 1.4811 | 3.0247 | -2.3497 | -5.6648 | 0 | 0 | 0 | 0 | 0
193 | 4 | 0 | 0 |  | 0.38206 | 1.928 | -5.2389 | 1.4811 | 4.0247 | -2.0879 | 1.0529 | 0 | 0 | 0 | 0 | 0
193 | 5 | 0 | 13 |  | 0.38206 | 1.928 | -5.2389 | 1.4811 | 5.0247 | -1.8261 | 8.8828 | 0 | 10.8333 | 10.8333 | 17.199 | 0
193 | 6 | 0 | 69 |  | 0.38206 | 1.928 | -5.2389 | 1.4811 | 6.0247 | -1.5643 | 17.4656 | 0 | 57.5 | 57.5 | 91.287 | 1
193 | 7 | 16 | 146 |  | 0.38206 | 1.928 | -5.2389 | 1.4811 | 7.0247 | -1.3025 | 26.4621 | 5.931 | 121.6667 | 127.5976 | 202.574 | 1
193 | 8 | 0 | 152 |  | 0.38206 | 1.928 | -5.2389 | 1.4811 | 8.0247 | -1.0407 | 35.5151 | 0 | 126.6667 | 126.6667 | 201.096 | 1
193 | 9 | 64 | 286 |  | 0.38206 | 1.928 | -5.2389 | 1.4811 | 9.0247 | -0.77894 | 44.1745 | 48.1949 | 238.3333 | 286.5282 | 454.8922 | 1
193 | 10 | 70 | 346 |  | 0.38206 | 1.928 | -5.2389 | 1.4811 | 10.0247 | -0.51714 | 51.7662 | 62.1568 | 288.3333 | 350.4901 | 556.4381 | 1
193 | 11 | 86 | 378 |  | 0.38206 | 1.928 | -5.2389 | 1.4811 | 11.0247 | -0.25534 | 57.2261 | 83.6047 | 315 | 398.6047 | 632.8248 | 1
193 | 12 | 87 | 399 |  | 0.38206 | 1.928 | -5.2389 | 1.4811 | 12.0247 | 0.0064626 | 59.209 | 86.9902 | 332.5 | 419.4902 | 665.9826 | 1
193 | 13 | 86 | 399 |  | 0.38206 | 1.928 | -5.2389 | 1.4811 | 13.0247 | 0.26826 | 57.0274 | 83.3584 | 332.5 | 415.8584 | 660.2167 | 1
193 | 14 | 86 | 376 |  | 0.38206 | 1.928 | -5.2389 | 1.4811 | 14.0247 | 0.53006 | 51.4308 | 75.8882 | 313.3333 | 389.2215 | 617.9281 | 1
193 | 15 | 44 | 361 |  | 0.38206 | 1.928 | -5.2389 | 1.4811 | 15.0247 | 0.79186 | 43.7652 | 32.7897 | 300.8333 | 333.623 | 529.6599 | 1
193 | 16 | 65 | 283 |  | 0.38206 | 1.928 | -5.2389 | 1.4811 | 16.0247 | 1.0537 | 35.0731 | 36.857 | 235.8333 | 272.6903 | 432.9232 | 1
193 | 17 | 31 | 223 |  | 0.38206 | 1.928 | -5.2389 | 1.4811 | 17.0247 | 1.3155 | 26.0135 | 11.1599 | 185.8333 | 196.9932 | 312.7464 | 1
193 | 18 | 0 | 93 |  | 0.38206 | 1.928 | -5.2389 | 1.4811 | 18.0247 | 1.5773 | 17.0294 | 0 | 77.5 | 77.5 | 123.039 | 1
193 | 19 | 0 | 41 |  | 0.38206 | 1.928 | -5.2389 | 1.4811 | 19.0247 | 1.8391 | 8.4757 | 0 | 34.1667 | 34.1667 | 54.243 | 0
193 | 20 | 0 | 12 |  | 0.38206 | 1.928 | -5.2389 | 1.4811 | 20.0247 | 2.1009 | 0.69206 | 0 | 10 | 10 | 15.876 | 0
193 | 21 | 0 | 0 |  | 0.38206 | 1.928 | -5.2389 | 1.4811 | 21.0247 | 2.3627 | -5.9609 | 0 | 0 | 0 | 0 | 0
193 | 22 | 0 | 0 |  | 0.38206 | 1.928 | -5.2389 | 1.4811 | 22.0247 | 2.6245 | -11.0985 | 0 | 0 | 0 | 0 | 0
193 | 23 | 0 | 0 |  | 0.38206 | 1.928 | -5.2389 | 1.4811 | 23.0247 | 2.8863 | -14.3484 | 0 | 0 | 0 | 0 | 0
193 | 24 | 0 | 0 |  | 0.38206 | 1.928 | -5.2389 | 1.4811 | 24.0247 | 3.1481 | -15.429 | 0 | 0 | 0 | 0 | 0
194 | 1 | 0 | 0 |  | 0.37942 | 1.9452 | -5.3614 | 1.3586 | 1.0226 | -2.8739 | -14.3909 | 0 | 0 | 0 | 0 | 0
194 | 2 | 0 | 0 |  | 0.37942 | 1.9452 | -5.3614 | 1.3586 | 2.0226 | -2.6121 | -11.0388 | 0 | 0 | 0 | 0 | 0
194 | 3 | 0 | 0 |  | 0.37942 | 1.9452 | -5.3614 | 1.3586 | 3.0226 | -2.3503 | -5.8134 | 0 | 0 | 0 | 0 | 0
194 | 4 | 0 | 0 |  | 0.37942 | 1.9452 | -5.3614 | 1.3586 | 4.0226 | -2.0885 | 0.90938 | 0 | 0 | 0 | 0 | 0
194 | 5 | 0 | 17 |  | 0.37942 | 1.9452 | -5.3614 | 1.3586 | 5.0226 | -1.8267 | 8.7442 | 0 | 14.1667 | 14.1667 | 22.491 | 0
194 | 6 | 136 | 81 |  | 0.37942 | 1.9452 | -5.3614 | 1.3586 | 6.0226 | -1.5649 | 17.3308 | 20.1135 | 67.5 | 87.6135 | 139.0952 | 1
194 | 7 | 356 | 133 |  | 0.37942 | 1.9452 | -5.3614 | 1.3586 | 7.0226 | -1.3031 | 26.329 | 131.5554 | 110.8333 | 242.3887 | 384.8164 | 1
194 | 8 | 588 | 127 |  | 0.37942 | 1.9452 | -5.3614 | 1.3586 | 8.0226 | -1.0413 | 35.3809 | 338.53 | 105.8333 | 444.3633 | 705.4712 | 1
194 | 9 | 694 | 137 |  | 0.37942 | 1.9452 | -5.3614 | 1.3586 | 9.0226 | -0.77947 | 44.0359 | 522.1809 | 114.1667 | 636.3476 | 1010.2655 | 1
194 | 10 | 745 | 154 |  | 0.37942 | 1.9452 | -5.3614 | 1.3586 | 10.0226 | -0.51767 | 51.6201 | 661.239 | 128.3333 | 789.5723 | 1253.525 | 1
194 | 11 | 804 | 141 |  | 0.37942 | 1.9452 | -5.3614 | 1.3586 | 11.0226 | -0.25587 | 57.073 | 781.4576 | 117.5 | 898.9576 | 1427.1851 | 1
194 | 12 | 817 | 147 |  | 0.37942 | 1.9452 | -5.3614 | 1.3586 | 12.0226 | 0.0059279 | 59.058 | 816.8775 | 122.5 | 939.3775 | 1491.3558 | 1
194 | 13 | 816 | 147 |  | 0.37942 | 1.9452 | -5.3614 | 1.3586 | 13.0226 | 0.26773 | 56.8913 | 790.9752 | 122.5 | 913.4752 | 1450.2332 | 1
194 | 14 | 806 | 139 |  | 0.37942 | 1.9452 | -5.3614 | 1.3586 | 14.0226 | 0.52953 | 51.313 | 711.2858 | 115.8333 | 827.1192 | 1313.1344 | 1
194 | 15 | 755 | 145 |  | 0.37942 | 1.9452 | -5.3614 | 1.3586 | 15.0226 | 0.79133 | 43.6608 | 562.6541 | 120.8333 | 683.4874 | 1085.1047 | 1
194 | 16 | 697 | 134 |  | 0.37942 | 1.9452 | -5.3614 | 1.3586 | 16.0226 | 1.0531 | 34.9756 | 395.1513 | 111.6667 | 506.818 | 804.6242 | 1
194 | 17 | 514 | 149 |  | 0.37942 | 1.9452 | -5.3614 | 1.3586 | 17.0226 | 1.3149 | 25.9175 | 184.8976 | 124.1667 | 309.0643 | 490.6704 | 1
194 | 18 | 104 | 151 |  | 0.37942 | 1.9452 | -5.3614 | 1.3586 | 18.0226 | 1.5767 | 16.9305 | 14.3242 | 125.8333 | 140.1575 | 222.514 | 1
194 | 19 | 0 | 65 |  | 0.37942 | 1.9452 | -5.3614 | 1.3586 | 19.0226 | 1.8385 | 8.3705 | 0 | 54.1667 | 54.1667 | 85.995 | 0
194 | 20 | 0 | 12 |  | 0.37942 | 1.9452 | -5.3614 | 1.3586 | 20.0226 | 2.1003 | 0.57807 | 0 | 10 | 10 | 15.876 | 0
194 | 21 | 0 | 0 |  | 0.37942 | 1.9452 | -5.3614 | 1.3586 | 21.0226 | 2.3621 | -6.0854 | 0 | 0 | 0 | 0 | 0
194 | 22 | 0 | 0 |  | 0.37942 | 1.9452 | -5.3614 | 1.3586 | 22.0226 | 2.6239 | -11.2337 | 0 | 0 | 0 | 0 | 0
194 | 23 | 0 | 0 |  | 0.37942 | 1.9452 | -5.3614 | 1.3586 | 23.0226 | 2.8857 | -14.4932 | 0 | 0 | 0 | 0 | 0
194 | 24 | 0 | 0 |  | 0.37942 | 1.9452 | -5.3614 | 1.3586 | 24.0226 | 3.1475 | -15.5803 | 0 | 0 | 0 | 0 | 0
195 | 1 | 0 | 0 |  | 0.37666 | 1.9624 | -5.4764 | 1.2436 | 1.0207 | -2.8744 | -14.551 | 0 | 0 | 0 | 0 | 0
195 | 2 | 0 | 0 |  | 0.37666 | 1.9624 | -5.4764 | 1.2436 | 2.0207 | -2.6126 | -11.1971 | 0 | 0 | 0 | 0 | 0
195 | 3 | 0 | 0 |  | 0.37666 | 1.9624 | -5.4764 | 1.2436 | 3.0207 | -2.3508 | -5.9672 | 0 | 0 | 0 | 0 | 0
195 | 4 | 0 | 0 |  | 0.37666 | 1.9624 | -5.4764 | 1.2436 | 4.0207 | -2.089 | 0.76116 | 0 | 0 | 0 | 0 | 0
195 | 5 | 0 | 8 |  | 0.37666 | 1.9624 | -5.4764 | 1.2436 | 5.0207 | -1.8272 | 8.6013 | 0 | 6.6667 | 6.6667 | 10.584 | 0
195 | 6 | 0 | 42 |  | 0.37666 | 1.9624 | -5.4764 | 1.2436 | 6.0207 | -1.5654 | 17.1919 | 0 | 35 | 35 | 55.566 | 1
195 | 7 | 21 | 141 |  | 0.37666 | 1.9624 | -5.4764 | 1.2436 | 7.0207 | -1.3036 | 26.1919 | 7.7361 | 117.5 | 125.2361 | 198.8248 | 1
195 | 8 | 372 | 199 |  | 0.37666 | 1.9624 | -5.4764 | 1.2436 | 8.0207 | -1.0418 | 35.2427 | 213.8428 | 165.8333 | 379.6762 | 602.7739 | 1
195 | 9 | 356 | 257 |  | 0.37666 | 1.9624 | -5.4764 | 1.2436 | 9.0207 | -0.77997 | 43.8929 | 267.6406 | 214.1667 | 481.8073 | 764.9173 | 1
195 | 10 | 681 | 200 |  | 0.37666 | 1.9624 | -5.4764 | 1.2436 | 10.0207 | -0.51817 | 51.4689 | 604.1723 | 166.6667 | 770.839 | 1223.784 | 1
195 | 11 | 857 | 97 |  | 0.37666 | 1.9624 | -5.4764 | 1.2436 | 11.0207 | -0.25637 | 56.914 | 832.8099 | 80.8333 | 913.6433 | 1450.5 | 1
195 | 12 | 723 | 193 |  | 0.37666 | 1.9624 | -5.4764 | 1.2436 | 12.0207 | 0.0054261 | 58.9003 | 722.8579 | 160.8333 | 883.6913 | 1402.9482 | 1
195 | 13 | 747 | 171 |  | 0.37666 | 1.9624 | -5.4764 | 1.2436 | 13.0207 | 0.26723 | 56.7482 | 724.1147 | 142.5 | 866.6147 | 1375.8374 | 1
195 | 14 | 418 | 321 |  | 0.37666 | 1.9624 | -5.4764 | 1.2436 | 14.0207 | 0.52902 | 51.1884 | 368.8969 | 267.5 | 636.3969 | 1010.3437 | 1
195 | 15 | 83 | 331 |  | 0.37666 | 1.9624 | -5.4764 | 1.2436 | 15.0207 | 0.79082 | 43.5499 | 61.8529 | 275.8333 | 337.6862 | 536.1107 | 1
195 | 16 | 310 | 282 |  | 0.37666 | 1.9624 | -5.4764 | 1.2436 | 16.0207 | 1.0526 | 34.8718 | 175.7026 | 235 | 410.7026 | 652.0315 | 1
195 | 17 | 158 | 223 |  | 0.37666 | 1.9624 | -5.4764 | 1.2436 | 17.0207 | 1.3144 | 25.8152 | 56.7836 | 185.8333 | 242.6169 | 385.1786 | 1
195 | 18 | 0 | 91 |  | 0.37666 | 1.9624 | -5.4764 | 1.2436 | 18.0207 | 1.5762 | 16.8253 | 0 | 75.8333 | 75.8333 | 120.393 | 1
195 | 19 | 0 | 64 |  | 0.37666 | 1.9624 | -5.4764 | 1.2436 | 19.0207 | 1.838 | 8.259 | 0 | 53.3333 | 53.3333 | 84.672 | 0
195 | 20 | 0 | 7 |  | 0.37666 | 1.9624 | -5.4764 | 1.2436 | 20.0207 | 2.0998 | 0.45756 | 0 | 5.8333 | 5.8333 | 9.261 | 0
195 | 21 | 0 | 0 |  | 0.37666 | 1.9624 | -5.4764 | 1.2436 | 21.0207 | 2.3616 | -6.2165 | 0 | 0 | 0 | 0 | 0
195 | 22 | 0 | 0 |  | 0.37666 | 1.9624 | -5.4764 | 1.2436 | 22.0207 | 2.6234 | -11.3758 | 0 | 0 | 0 | 0 | 0
195 | 23 | 0 | 0 |  | 0.37666 | 1.9624 | -5.4764 | 1.2436 | 23.0207 | 2.8852 | -14.6448 | 0 | 0 | 0 | 0 | 0
195 | 24 | 0 | 0 |  | 0.37666 | 1.9624 | -5.4764 | 1.2436 | 24.0207 | 3.147 | -15.7383 | 0 | 0 | 0 | 0 | 0
196 | 1 | 0 | 0 |  | 0.3738 | 1.9796 | -5.5836 | 1.1364 | 1.0189 | -2.8748 | -14.7172 | 0 | 0 | 0 | 0 | 0
196 | 2 | 0 | 0 |  | 0.3738 | 1.9796 | -5.5836 | 1.1364 | 2.0189 | -2.613 | -11.361 | 0 | 0 | 0 | 0 | 0
196 | 3 | 0 | 0 |  | 0.3738 | 1.9796 | -5.5836 | 1.1364 | 3.0189 | -2.3512 | -6.1262 | 0 | 0 | 0 | 0 | 0
196 | 4 | 0 | 0 |  | 0.3738 | 1.9796 | -5.5836 | 1.1364 | 4.0189 | -2.0894 | 0.6083 | 0 | 0 | 0 | 0 | 0
196 | 5 | 0 | 16 |  | 0.3738 | 1.9796 | -5.5836 | 1.1364 | 5.0189 | -1.8276 | 8.4541 | 0 | 13.3333 | 13.3333 | 21.168 | 0
196 | 6 | 132 | 85 |  | 0.3738 | 1.9796 | -5.5836 | 1.1364 | 6.0189 | -1.5658 | 17.049 | 19.1473 | 70.8333 | 89.9807 | 142.8533 | 1
196 | 7 | 359 | 130 |  | 0.3738 | 1.9796 | -5.5836 | 1.1364 | 7.0189 | -1.304 | 26.051 | 131.8331 | 108.3333 | 240.1664 | 381.2882 | 1
196 | 8 | 368 | 204 |  | 0.3738 | 1.9796 | -5.5836 | 1.1364 | 8.0189 | -1.0422 | 35.1005 | 211.2172 | 170 | 381.2172 | 605.2205 | 1
196 | 9 | 198 | 293 |  | 0.3738 | 1.9796 | -5.5836 | 1.1364 | 9.0189 | -0.78044 | 43.7456 | 148.7331 | 244.1667 | 392.8998 | 623.7677 | 1
196 | 10 | 367 | 323 |  | 0.3738 | 1.9796 | -5.5836 | 1.1364 | 10.0189 | -0.51864 | 51.3129 | 325.4551 | 269.1667 | 594.6217 | 944.0214 | 1
196 | 11 | 255 | 370 |  | 0.3738 | 1.9796 | -5.5836 | 1.1364 | 11.0189 | -0.25684 | 56.7493 | 247.7531 | 308.3333 | 556.0864 | 882.8428 | 1
196 | 12 | 95 | 395 |  | 0.3738 | 1.9796 | -5.5836 | 1.1364 | 12.0189 | 0.0049584 | 58.7361 | 94.9759 | 329.1667 | 424.1426 | 673.3688 | 1
196 | 13 | 62 | 423 |  | 0.3738 | 1.9796 | -5.5836 | 1.1364 | 13.0189 | 0.26676 | 56.5982 | 60.1013 | 352.5 | 412.6013 | 655.0459 | 1
196 | 14 | 61 | 399 |  | 0.3738 | 1.9796 | -5.5836 | 1.1364 | 14.0189 | 0.52856 | 51.0571 | 53.8349 | 332.5 | 386.3349 | 613.3453 | 1
196 | 15 | 87 | 332 |  | 0.3738 | 1.9796 | -5.5836 | 1.1364 | 15.0189 | 0.79036 | 43.4325 | 64.8284 | 276.6667 | 341.4951 | 542.1576 | 1
196 | 16 | 7 | 198 |  | 0.3738 | 1.9796 | -5.5836 | 1.1364 | 16.0189 | 1.0522 | 34.7617 | 3.9661 | 165 | 168.9661 | 268.2505 | 1
196 | 17 | 0 | 149 |  | 0.3738 | 1.9796 | -5.5836 | 1.1364 | 17.0189 | 1.314 | 25.7067 | 0 | 124.1667 | 124.1667 | 197.127 | 1
196 | 18 | 23 | 138 |  | 0.3738 | 1.9796 | -5.5836 | 1.1364 | 18.0189 | 1.5758 | 16.7139 | 3.1404 | 115 | 118.1404 | 187.5596 | 1
196 | 19 | 0 | 40 |  | 0.3738 | 1.9796 | -5.5836 | 1.1364 | 19.0189 | 1.8376 | 8.1411 | 0 | 33.3333 | 33.3333 | 52.92 | 0
196 | 20 | 0 | 7 |  | 0.3738 | 1.9796 | -5.5836 | 1.1364 | 20.0189 | 2.0994 | 0.33057 | 0 | 5.8333 | 5.8333 | 9.261 | 0
196 | 21 | 0 | 0 |  | 0.3738 | 1.9796 | -5.5836 | 1.1364 | 21.0189 | 2.3612 | -6.3543 | 0 | 0 | 0 | 0 | 0
196 | 22 | 0 | 0 |  | 0.3738 | 1.9796 | -5.5836 | 1.1364 | 22.0189 | 2.623 | -11.5246 | 0 | 0 | 0 | 0 | 0
196 | 23 | 0 | 0 |  | 0.3738 | 1.9796 | -5.5836 | 1.1364 | 23.0189 | 2.8848 | -14.8031 | 0 | 0 | 0 | 0 | 0
196 | 24 | 0 | 0 |  | 0.3738 | 1.9796 | -5.5836 | 1.1364 | 24.0189 | 3.1466 | -15.9027 | 0 | 0 | 0 | 0 | 0
197 | 1 | 0 | 0 |  | 0.37081 | 1.9968 | -5.6827 | 1.0373 | 1.0173 | -2.8753 | -14.8895 | 0 | 0 | 0 | 0 | 0
197 | 2 | 0 | 0 |  | 0.37081 | 1.9968 | -5.6827 | 1.0373 | 2.0173 | -2.6135 | -11.5305 | 0 | 0 | 0 | 0 | 0
197 | 3 | 0 | 0 |  | 0.37081 | 1.9968 | -5.6827 | 1.0373 | 3.0173 | -2.3517 | -6.2901 | 0 | 0 | 0 | 0 | 0
197 | 4 | 0 | 0 |  | 0.37081 | 1.9968 | -5.6827 | 1.0373 | 4.0173 | -2.0899 | 0.45092 | 0 | 0 | 0 | 0 | 0
197 | 5 | 0 | 7 |  | 0.37081 | 1.9968 | -5.6827 | 1.0373 | 5.0173 | -1.8281 | 8.3029 | 0 | 5.8333 | 5.8333 | 9.261 | 0
197 | 6 | 0 | 41 |  | 0.37081 | 1.9968 | -5.6827 | 1.0373 | 6.0173 | -1.5663 | 16.9022 | 0 | 34.1667 | 34.1667 | 54.243 | 1
197 | 7 | 0 | 92 |  | 0.37081 | 1.9968 | -5.6827 | 1.0373 | 7.0173 | -1.3045 | 25.9062 | 0 | 76.6667 | 76.6667 | 121.716 | 1
197 | 8 | 42 | 217 |  | 0.37081 | 1.9968 | -5.6827 | 1.0373 | 8.0173 | -1.0427 | 34.9544 | 24.069 | 180.8333 | 204.9024 | 325.303 | 1
197 | 9 | 5 | 200 |  | 0.37081 | 1.9968 | -5.6827 | 1.0373 | 9.0173 | -0.78087 | 43.594 | 3.7528 | 166.6667 | 170.4194 | 270.5579 | 1
197 | 10 | 7 | 243 |  | 0.37081 | 1.9968 | -5.6827 | 1.0373 | 10.0173 | -0.51907 | 51.1519 | 6.2049 | 202.5 | 208.7049 | 331.3399 | 1
197 | 11 | 11 | 271 |  | 0.37081 | 1.9968 | -5.6827 | 1.0373 | 11.0173 | -0.25727 | 56.5788 | 10.6852 | 225.8333 | 236.5185 | 375.4968 | 1
197 | 12 | 12 | 285 |  | 0.37081 | 1.9968 | -5.6827 | 1.0373 | 12.0173 | 0.0045259 | 58.5654 | 11.9961 | 237.5 | 249.4961 | 396.1001 | 1
197 | 13 | 12 | 285 |  | 0.37081 | 1.9968 | -5.6827 | 1.0373 | 13.0173 | 0.26633 | 56.4414 | 11.6324 | 237.5 | 249.1324 | 395.5226 | 1
197 | 14 | 121 | 345 |  | 0.37081 | 1.9968 | -5.6827 | 1.0373 | 14.0173 | 0.52812 | 50.9189 | 106.7849 | 287.5 | 394.2849 | 625.9668 | 1
197 | 15 | 70 | 341 |  | 0.37081 | 1.9968 | -5.6827 | 1.0373 | 15.0173 | 0.78992 | 43.3086 | 52.1536 | 284.1667 | 336.3203 | 533.9421 | 1
197 | 16 | 187 | 293 |  | 0.37081 | 1.9968 | -5.6827 | 1.0373 | 16.0173 | 1.0517 | 34.6453 | 105.9039 | 244.1667 | 350.0706 | 555.7721 | 1
197 | 17 | 466 | 172 |  | 0.37081 | 1.9968 | -5.6827 | 1.0373 | 17.0173 | 1.3135 | 25.5919 | 167.0788 | 143.3333 | 310.4121 | 492.8103 | 1
197 | 18 | 186 | 149 |  | 0.37081 | 1.9968 | -5.6827 | 1.0373 | 18.0173 | 1.5753 | 16.5962 | 25.265 | 124.1667 | 149.4317 | 237.2378 | 1
197 | 19 | 11 | 79 |  | 0.37081 | 1.9968 | -5.6827 | 1.0373 | 19.0173 | 1.8371 | 8.0169 | 0 | 65.8333 | 65.8333 | 104.517 | 0
197 | 20 | 0 | 14 |  | 0.37081 | 1.9968 | -5.6827 | 1.0373 | 20.0173 | 2.0989 | 0.19712 | 0 | 11.6667 | 11.6667 | 18.522 | 0
197 | 21 | 0 | 0 |  | 0.37081 | 1.9968 | -5.6827 | 1.0373 | 21.0173 | 2.3607 | -6.4986 | 0 | 0 | 0 | 0 | 0
197 | 22 | 0 | 0 |  | 0.37081 | 1.9968 | -5.6827 | 1.0373 | 22.0173 | 2.6225 | -11.6801 | 0 | 0 | 0 | 0 | 0
197 | 23 | 0 | 0 |  | 0.37081 | 1.9968 | -5.6827 | 1.0373 | 23.0173 | 2.8843 | -14.968 | 0 | 0 | 0 | 0 | 0
197 | 24 | 0 | 0 |  | 0.37081 | 1.9968 | -5.6827 | 1.0373 | 24.0173 | 3.1461 | -16.0736 | 0 | 0 | 0 | 0 | 0
198 | 1 | 0 | 0 |  | 0.36772 | 2.0141 | -5.7736 | 0.94642 | 1.0158 | -2.8757 | -15.0678 | 0 | 0 | 0 | 0 | 0
198 | 2 | 0 | 0 |  | 0.36772 | 2.0141 | -5.7736 | 0.94642 | 2.0158 | -2.6139 | -11.7055 | 0 | 0 | 0 | 0 | 0
198 | 3 | 0 | 0 |  | 0.36772 | 2.0141 | -5.7736 | 0.94642 | 3.0158 | -2.3521 | -6.459 | 0 | 0 | 0 | 0 | 0
198 | 4 | 0 | 0 |  | 0.36772 | 2.0141 | -5.7736 | 0.94642 | 4.0158 | -2.0903 | 0.28908 | 0 | 0 | 0 | 0 | 0
198 | 5 | 0 | 20 |  | 0.36772 | 2.0141 | -5.7736 | 0.94642 | 5.0158 | -1.8285 | 8.1475 | 0 | 16.6667 | 16.6667 | 26.46 | 0
198 | 6 | 146 | 82 |  | 0.36772 | 2.0141 | -5.7736 | 0.94642 | 6.0158 | -1.5667 | 16.7517 | 20.7566 | 68.3333 | 89.09 | 141.4392 | 1
198 | 7 | 321 | 134 |  | 0.36772 | 2.0141 | -5.7736 | 0.94642 | 7.0158 | -1.3049 | 25.7577 | 117.1286 | 111.6667 | 228.7953 | 363.2354 | 1
198 | 8 | 511 | 160 |  | 0.36772 | 2.0141 | -5.7736 | 0.94642 | 8.0158 | -1.0431 | 34.8044 | 292.3862 | 133.3333 | 425.7196 | 675.8724 | 1
198 | 9 | 338 | 268 |  | 0.36772 | 2.0141 | -5.7736 | 0.94642 | 9.0158 | -0.78127 | 43.4383 | 253.478 | 223.3333 | 476.8114 | 756.9857 | 1
198 | 10 | 205 | 356 |  | 0.36772 | 2.0141 | -5.7736 | 0.94642 | 10.0158 | -0.51947 | 50.9862 | 181.6351 | 296.6667 | 478.3018 | 759.3519 | 1
198 | 11 | 238 | 379 |  | 0.36772 | 2.0141 | -5.7736 | 0.94642 | 11.0158 | -0.25767 | 56.4027 | 231.1409 | 315.8333 | 546.9742 | 868.3763 | 1
198 | 12 | 419 | 348 |  | 0.36772 | 2.0141 | -5.7736 | 0.94642 | 12.0158 | 0.0041295 | 58.3883 | 418.8313 | 290 | 708.8313 | 1125.3405 | 1
198 | 13 | 368 | 391 |  | 0.36772 | 2.0141 | -5.7736 | 0.94642 | 13.0158 | 0.26593 | 56.2777 | 356.717 | 325.8333 | 682.5504 | 1083.617 | 1
198 | 14 | 273 | 350 |  | 0.36772 | 2.0141 | -5.7736 | 0.94642 | 14.0158 | 0.52773 | 50.774 | 240.9142 | 291.6667 | 532.5809 | 845.5254 | 1
198 | 15 | 194 | 362 |  | 0.36772 | 2.0141 | -5.7736 | 0.94642 | 15.0158 | 0.78953 | 43.1781 | 144.5119 | 301.6667 | 446.1786 | 708.3531 | 1
198 | 16 | 538 | 228 |  | 0.36772 | 2.0141 | -5.7736 | 0.94642 | 16.0158 | 1.0513 | 34.5226 | 304.5221 | 190 | 494.5221 | 785.1033 | 1
198 | 17 | 278 | 210 |  | 0.36772 | 2.0141 | -5.7736 | 0.94642 | 17.0158 | 1.3131 | 25.471 | 99.529 | 175 | 274.529 | 435.8423 | 1
198 | 18 | 354 | 119 |  | 0.36772 | 2.0141 | -5.7736 | 0.94642 | 18.0158 | 1.5749 | 16.4723 | 47.8105 | 99.1667 | 146.9771 | 233.3409 | 1
198 | 19 | 104 | 79 |  | 0.36772 | 2.0141 | -5.7736 | 0.94642 | 19.0158 | 1.8367 | 7.8864 | 0 | 65.8333 | 65.8333 | 104.517 | 0
198 | 20 | 0 | 16 |  | 0.36772 | 2.0141 | -5.7736 | 0.94642 | 20.0158 | 2.0985 | 0.057233 | 0 | 13.3333 | 13.3333 | 21.168 | 0
198 | 21 | 0 | 0 |  | 0.36772 | 2.0141 | -5.7736 | 0.94642 | 21.0158 | 2.3603 | -6.6496 | 0 | 0 | 0 | 0 | 0
198 | 22 | 0 | 0 |  | 0.36772 | 2.0141 | -5.7736 | 0.94642 | 22.0158 | 2.6221 | -11.8423 | 0 | 0 | 0 | 0 | 0
198 | 23 | 0 | 0 |  | 0.36772 | 2.0141 | -5.7736 | 0.94642 | 23.0158 | 2.8839 | -15.1396 | 0 | 0 | 0 | 0 | 0
198 | 24 | 0 | 0 |  | 0.36772 | 2.0141 | -5.7736 | 0.94642 | 24.0158 | 3.1457 | -16.2509 | 0 | 0 | 0 | 0 | 0
199 | 1 | 0 | 0 |  | 0.36452 | 2.0313 | -5.8559 | 0.86408 | 1.0144 | -2.876 | -15.252 | 0 | 0 | 0 | 0 | 0
199 | 2 | 0 | 0 |  | 0.36452 | 2.0313 | -5.8559 | 0.86408 | 2.0144 | -2.6142 | -11.8859 | 0 | 0 | 0 | 0 | 0
199 | 3 | 0 | 0 |  | 0.36452 | 2.0313 | -5.8559 | 0.86408 | 3.0144 | -2.3524 | -6.6328 | 0 | 0 | 0 | 0 | 0
199 | 4 | 0 | 0 |  | 0.36452 | 2.0313 | -5.8559 | 0.86408 | 4.0144 | -2.0906 | 0.12289 | 0 | 0 | 0 | 0 | 0
199 | 5 | 0 | 7 |  | 0.36452 | 2.0313 | -5.8559 | 0.86408 | 5.0144 | -1.8288 | 7.9882 | 0 | 5.8333 | 5.8333 | 9.261 | 0
199 | 6 | 0 | 39 |  | 0.36452 | 2.0313 | -5.8559 | 0.86408 | 6.0144 | -1.567 | 16.5974 | 0 | 32.5 | 32.5 | 51.597 | 1
199 | 7 | 0 | 90 |  | 0.36452 | 2.0313 | -5.8559 | 0.86408 | 7.0144 | -1.3052 | 25.6056 | 0 | 75 | 75 | 119.07 | 1
199 | 8 | 41 | 214 |  | 0.36452 | 2.0313 | -5.8559 | 0.86408 | 8.0144 | -1.0434 | 34.6508 | 23.4232 | 178.3333 | 201.7565 | 320.3086 | 1
199 | 9 | 65 | 280 |  | 0.36452 | 2.0313 | -5.8559 | 0.86408 | 9.0144 | -0.78163 | 43.2784 | 48.7055 | 233.3333 | 282.0388 | 447.7648 | 1
199 | 10 | 205 | 355 |  | 0.36452 | 2.0313 | -5.8559 | 0.86408 | 10.0144 | -0.51983 | 50.8157 | 181.5555 | 295.8333 | 477.3888 | 757.9025 | 1
199 | 11 | 93 | 370 |  | 0.36452 | 2.0313 | -5.8559 | 0.86408 | 11.0144 | -0.25803 | 56.2211 | 90.3003 | 308.3333 | 398.6336 | 632.8708 | 1
199 | 12 | 61 | 420 |  | 0.36452 | 2.0313 | -5.8559 | 0.86408 | 12.0144 | 0.0037703 | 58.2048 | 60.9697 | 350 | 410.9697 | 652.4555 | 1
199 | 13 | 255 | 390 |  | 0.36452 | 2.0313 | -5.8559 | 0.86408 | 13.0144 | 0.26557 | 56.1074 | 247.1686 | 325 | 572.1686 | 908.3749 | 1
199 | 14 | 93 | 369 |  | 0.36452 | 2.0313 | -5.8559 | 0.86408 | 14.0144 | 0.52737 | 50.6225 | 82.0619 | 307.5 | 389.5619 | 618.4685 | 1
199 | 15 | 87 | 330 |  | 0.36452 | 2.0313 | -5.8559 | 0.86408 | 15.0144 | 0.78917 | 43.0412 | 64.7905 | 275 | 339.7905 | 539.4514 | 1
199 | 16 | 79 | 271 |  | 0.36452 | 2.0313 | -5.8559 | 0.86408 | 16.0144 | 1.051 | 34.3935 | 44.6877 | 225.8333 | 270.521 | 429.4792 | 1
199 | 17 | 0 | 147 |  | 0.36452 | 2.0313 | -5.8559 | 0.86408 | 17.0144 | 1.3128 | 25.3438 | 0 | 122.5 | 122.5 | 194.481 | 1
199 | 18 | 21 | 135 |  | 0.36452 | 2.0313 | -5.8559 | 0.86408 | 18.0144 | 1.5746 | 16.3422 | 2.8184 | 112.5 | 115.3184 | 183.0795 | 1
199 | 19 | 0 | 61 |  | 0.36452 | 2.0313 | -5.8559 | 0.86408 | 19.0144 | 1.8364 | 7.7496 | 0 | 50.8333 | 50.8333 | 80.703 | 0
199 | 20 | 0 | 11 |  | 0.36452 | 2.0313 | -5.8559 | 0.86408 | 20.0144 | 2.0982 | -0.089047 | 0 | 9.1667 | 9.1667 | 14.553 | 0
199 | 21 | 0 | 0 |  | 0.36452 | 2.0313 | -5.8559 | 0.86408 | 21.0144 | 2.36 | -6.807 | 0 | 0 | 0 | 0 | 0
199 | 22 | 0 | 0 |  | 0.36452 | 2.0313 | -5.8559 | 0.86408 | 22.0144 | 2.6218 | -12.011 | 0 | 0 | 0 | 0 | 0
199 | 23 | 0 | 0 |  | 0.36452 | 2.0313 | -5.8559 | 0.86408 | 23.0144 | 2.8836 | -15.3177 | 0 | 0 | 0 | 0 | 0
199 | 24 | 0 | 0 |  | 0.36452 | 2.0313 | -5.8559 | 0.86408 | 24.0144 | 3.1454 | -16.4345 | 0 | 0 | 0 | 0 | 0
200 | 1 | 0 | 0 |  | 0.3612 | 2.0485 | -5.9295 | 0.79047 | 1.0132 | -2.8763 | -15.4421 | 0 | 0 | 0 | 0 | 0
200 | 2 | 0 | 0 |  | 0.3612 | 2.0485 | -5.9295 | 0.79047 | 2.0132 | -2.6145 | -12.0716 | 0 | 0 | 0 | 0 | 0
200 | 3 | 0 | 0 |  | 0.3612 | 2.0485 | -5.9295 | 0.79047 | 3.0132 | -2.3527 | -6.8113 | 0 | 0 | 0 | 0 | 0
200 | 4 | 0 | 0 |  | 0.3612 | 2.0485 | -5.9295 | 0.79047 | 4.0132 | -2.0909 | -0.047565 | 0 | 0 | 0 | 0 | 0
200 | 5 | 0 | 19 |  | 0.3612 | 2.0485 | -5.9295 | 0.79047 | 5.0132 | -1.8291 | 7.8251 | 0 | 15.8333 | 15.8333 | 25.137 | 0
200 | 6 | 139 | 80 |  | 0.3612 | 2.0485 | -5.9295 | 0.79047 | 6.0132 | -1.5673 | 16.4395 | 19.3548 | 66.6667 | 86.0214 | 136.5676 | 1
200 | 7 | 350 | 127 |  | 0.3612 | 2.0485 | -5.9295 | 0.79047 | 7.0132 | -1.3055 | 25.45 | 126.8875 | 105.8333 | 232.7208 | 369.4676 | 1
200 | 8 | 155 | 223 |  | 0.3612 | 2.0485 | -5.9295 | 0.79047 | 8.0132 | -1.0437 | 34.4934 | 88.4133 | 185.8333 | 274.2467 | 435.394 | 1
200 | 9 | 72 | 276 |  | 0.3612 | 2.0485 | -5.9295 | 0.79047 | 9.0132 | -0.78195 | 43.1146 | 53.9061 | 230 | 283.9061 | 450.7293 | 1
200 | 10 | 5 | 242 |  | 0.3612 | 2.0485 | -5.9295 | 0.79047 | 10.0132 | -0.52015 | 50.6406 | 4.4262 | 201.6667 | 206.0929 | 327.1931 | 1
200 | 11 | 5 | 274 |  | 0.3612 | 2.0485 | -5.9295 | 0.79047 | 11.0132 | -0.25835 | 56.034 | 4.8538 | 228.3333 | 233.1871 | 370.2079 | 1
200 | 12 | 12 | 284 |  | 0.3612 | 2.0485 | -5.9295 | 0.79047 | 12.0132 | 0.0034491 | 58.0151 | 11.9927 | 236.6667 | 248.6594 | 394.7717 | 1
200 | 13 | 12 | 284 |  | 0.3612 | 2.0485 | -5.9295 | 0.79047 | 13.0132 | 0.26525 | 55.9303 | 11.6306 | 236.6667 | 248.2972 | 394.1967 | 1
200 | 14 | 11 | 268 |  | 0.3612 | 2.0485 | -5.9295 | 0.79047 | 14.0132 | 0.52705 | 50.4642 | 9.705 | 223.3333 | 233.0383 | 369.9716 | 1
200 | 15 | 6 | 239 |  | 0.3612 | 2.0485 | -5.9295 | 0.79047 | 15.0132 | 0.78885 | 42.8978 | 4.4669 | 199.1667 | 203.6336 | 323.2887 | 1
200 | 16 | 4 | 197 |  | 0.3612 | 2.0485 | -5.9295 | 0.79047 | 16.0132 | 1.0506 | 34.2582 | 2.261 | 164.1667 | 166.4277 | 264.2206 | 1
200 | 17 | 39 | 212 |  | 0.3612 | 2.0485 | -5.9295 | 0.79047 | 17.0132 | 1.3124 | 25.2104 | 13.9146 | 176.6667 | 190.5813 | 302.5668 | 1
200 | 18 | 94 | 147 |  | 0.3612 | 2.0485 | -5.9295 | 0.79047 | 18.0132 | 1.5742 | 16.2059 | 12.5292 | 122.5 | 135.0292 | 214.3723 | 1
200 | 19 | 0 | 60 |  | 0.3612 | 2.0485 | -5.9295 | 0.79047 | 19.0132 | 1.836 | 7.6066 | 0 | 50 | 50 | 79.38 | 0
200 | 20 | 0 | 10 |  | 0.3612 | 2.0485 | -5.9295 | 0.79047 | 20.0132 | 2.0978 | -0.24169 | 0 | 8.3333 | 8.3333 | 13.23 | 0
200 | 21 | 0 | 0 |  | 0.3612 | 2.0485 | -5.9295 | 0.79047 | 21.0132 | 2.3596 | -6.971 | 0 | 0 | 0 | 0 | 0
200 | 22 | 0 | 0 |  | 0.3612 | 2.0485 | -5.9295 | 0.79047 | 22.0132 | 2.6214 | -12.1863 | 0 | 0 | 0 | 0 | 0
200 | 23 | 0 | 0 |  | 0.3612 | 2.0485 | -5.9295 | 0.79047 | 23.0132 | 2.8832 | -15.5023 | 0 | 0 | 0 | 0 | 0
200 | 24 | 0 | 0 |  | 0.3612 | 2.0485 | -5.9295 | 0.79047 | 24.0132 | 3.145 | -16.6243 | 0 | 0 | 0 | 0 | 0
201 | 1 | 0 | 0 |  | 0.35778 | 2.0657 | -5.9942 | 0.72578 | 1.0121 | -2.8766 | -15.6378 | 0 | 0 | 0 | 0 | 0
201 | 2 | 0 | 0 |  | 0.35778 | 2.0657 | -5.9942 | 0.72578 | 2.0121 | -2.6148 | -12.2625 | 0 | 0 | 0 | 0 | 0
201 | 3 | 0 | 0 |  | 0.35778 | 2.0657 | -5.9942 | 0.72578 | 3.0121 | -2.353 | -6.9945 | 0 | 0 | 0 | 0 | 0
201 | 4 | 0 | 0 |  | 0.35778 | 2.0657 | -5.9942 | 0.72578 | 4.0121 | -2.0912 | -0.22219 | 0 | 0 | 0 | 0 | 0
201 | 5 | 0 | 13 |  | 0.35778 | 2.0657 | -5.9942 | 0.72578 | 5.0121 | -1.8294 | 7.6581 | 0 | 10.8333 | 10.8333 | 17.199 | 0
201 | 6 | 0 | 60 |  | 0.35778 | 2.0657 | -5.9942 | 0.72578 | 6.0121 | -1.5676 | 16.278 | 0 | 50 | 50 | 79.38 | 1
201 | 7 | 108 | 143 |  | 0.35778 | 2.0657 | -5.9942 | 0.72578 | 7.0121 | -1.3058 | 25.2908 | 39.0265 | 119.1667 | 158.1932 | 251.1475 | 1
201 | 8 | 145 | 227 |  | 0.35778 | 2.0657 | -5.9942 | 0.72578 | 8.0121 | -1.044 | 34.3324 | 82.5806 | 189.1667 | 271.7473 | 431.426 | 1
201 | 9 | 71 | 275 |  | 0.35778 | 2.0657 | -5.9942 | 0.72578 | 9.0121 | -0.78223 | 42.9467 | 53.1135 | 229.1667 | 282.2801 | 448.1479 | 1
201 | 10 | 87 | 329 |  | 0.35778 | 2.0657 | -5.9942 | 0.72578 | 10.0121 | -0.52043 | 50.4609 | 76.9823 | 274.1667 | 351.1489 | 557.4841 | 1
201 | 11 | 254 | 366 |  | 0.35778 | 2.0657 | -5.9942 | 0.72578 | 11.0121 | -0.25863 | 55.8415 | 246.5151 | 305 | 551.5151 | 875.5853 | 1
201 | 12 | 601 | 300 |  | 0.35778 | 2.0657 | -5.9942 | 0.72578 | 12.0121 | 0.0031668 | 57.8192 | 600.5622 | 250 | 850.5622 | 1350.3526 | 1
201 | 13 | 542 | 311 |  | 0.35778 | 2.0657 | -5.9942 | 0.72578 | 13.0121 | 0.26497 | 55.7466 | 525.2603 | 259.1667 | 784.427 | 1245.3563 | 1
201 | 14 | 285 | 341 |  | 0.35778 | 2.0657 | -5.9942 | 0.72578 | 14.0121 | 0.52677 | 50.2994 | 251.4033 | 284.1667 | 535.57 | 850.2709 | 1
201 | 15 | 79 | 334 |  | 0.35778 | 2.0657 | -5.9942 | 0.72578 | 15.0121 | 0.78856 | 42.748 | 58.7923 | 278.3333 | 337.1256 | 535.2206 | 1
201 | 16 | 79 | 269 |  | 0.35778 | 2.0657 | -5.9942 | 0.72578 | 16.0121 | 1.0504 | 34.1166 | 44.6177 | 224.1667 | 268.7844 | 426.7221 | 1
201 | 17 | 246 | 223 |  | 0.35778 | 2.0657 | -5.9942 | 0.72578 | 17.0121 | 1.3122 | 25.0709 | 87.5931 | 185.8333 | 273.4264 | 434.0918 | 1
201 | 18 | 171 | 149 |  | 0.35778 | 2.0657 | -5.9942 | 0.72578 | 18.0121 | 1.574 | 16.0635 | 22.6224 | 124.1667 | 146.789 | 233.0423 | 1
201 | 19 | 128 | 76 |  | 0.35778 | 2.0657 | -5.9942 | 0.72578 | 19.0121 | 1.8358 | 7.4573 | 0 | 63.3333 | 63.3333 | 100.548 | 0
201 | 20 | 0 | 13 |  | 0.35778 | 2.0657 | -5.9942 | 0.72578 | 20.0121 | 2.0976 | -0.40065 | 0 | 10.8333 | 10.8333 | 17.199 | 0
201 | 21 | 0 | 0 |  | 0.35778 | 2.0657 | -5.9942 | 0.72578 | 21.0121 | 2.3594 | -7.1413 | 0 | 0 | 0 | 0 | 0
201 | 22 | 0 | 0 |  | 0.35778 | 2.0657 | -5.9942 | 0.72578 | 22.0121 | 2.6212 | -12.368 | 0 | 0 | 0 | 0 | 0
201 | 23 | 0 | 0 |  | 0.35778 | 2.0657 | -5.9942 | 0.72578 | 23.0121 | 2.883 | -15.6932 | 0 | 0 | 0 | 0 | 0
201 | 24 | 0 | 0 |  | 0.35778 | 2.0657 | -5.9942 | 0.72578 | 24.0121 | 3.1448 | -16.8203 | 0 | 0 | 0 | 0 | 0
202 | 1 | 0 | 0 |  | 0.35426 | 2.0829 | -6.0498 | 0.6702 | 1.0112 | -2.8769 | -15.8393 | 0 | 0 | 0 | 0 | 0
202 | 2 | 0 | 0 |  | 0.35426 | 2.0829 | -6.0498 | 0.6702 | 2.0112 | -2.6151 | -12.4586 | 0 | 0 | 0 | 0 | 0
202 | 3 | 0 | 0 |  | 0.35426 | 2.0829 | -6.0498 | 0.6702 | 3.0112 | -2.3533 | -7.1822 | 0 | 0 | 0 | 0 | 0
202 | 4 | 0 | 0 |  | 0.35426 | 2.0829 | -6.0498 | 0.6702 | 4.0112 | -2.0915 | -0.40088 | 0 | 0 | 0 | 0 | 0
202 | 5 | 0 | 18 |  | 0.35426 | 2.0829 | -6.0498 | 0.6702 | 5.0112 | -1.8297 | 7.4875 | 0 | 15 | 15 | 23.814 | 0
202 | 6 | 134 | 78 |  | 0.35426 | 2.0829 | -6.0498 | 0.6702 | 6.0112 | -1.5679 | 16.1131 | 18.2625 | 65 | 83.2625 | 132.1876 | 1
202 | 7 | 356 | 124 |  | 0.35426 | 2.0829 | -6.0498 | 0.6702 | 7.0112 | -1.3061 | 25.1283 | 128.2229 | 103.3333 | 231.5563 | 367.6187 | 1
202 | 8 | 548 | 141 |  | 0.35426 | 2.0829 | -6.0498 | 0.6702 | 8.0112 | -1.0443 | 34.1679 | 311.6125 | 117.5 | 429.1125 | 681.259 | 1
202 | 9 | 651 | 162 |  | 0.35426 | 2.0829 | -6.0498 | 0.6702 | 9.0112 | -0.78247 | 42.775 | 486.5957 | 135 | 621.5957 | 986.8453 | 1
202 | 10 | 681 | 177 |  | 0.35426 | 2.0829 | -6.0498 | 0.6702 | 10.0112 | -0.52067 | 50.2767 | 602.3165 | 147.5 | 749.8165 | 1190.4087 | 1
202 | 11 | 105 | 359 |  | 0.35426 | 2.0829 | -6.0498 | 0.6702 | 11.0112 | -0.25888 | 55.6437 | 101.8815 | 299.1667 | 401.0482 | 636.7041 | 1
202 | 12 | 431 | 338 |  | 0.35426 | 2.0829 | -6.0498 | 0.6702 | 12.0112 | 0.0029243 | 57.6172 | 430.6258 | 281.6667 | 712.2925 | 1130.8356 | 1
202 | 13 | 428 | 340 |  | 0.35426 | 2.0829 | -6.0498 | 0.6702 | 13.0112 | 0.26472 | 55.5564 | 414.7277 | 283.3333 | 698.061 | 1108.2417 | 1
202 | 14 | 106 | 358 |  | 0.35426 | 2.0829 | -6.0498 | 0.6702 | 14.0112 | 0.52652 | 50.1279 | 93.4844 | 298.3333 | 391.8177 | 622.0498 | 1
202 | 15 | 352 | 327 |  | 0.35426 | 2.0829 | -6.0498 | 0.6702 | 15.0112 | 0.78832 | 42.5917 | 261.8458 | 272.5 | 534.3458 | 848.3273 | 1
202 | 16 | 85 | 265 |  | 0.35426 | 2.0829 | -6.0498 | 0.6702 | 16.0112 | 1.0501 | 33.9687 | 47.9615 | 220.8333 | 268.7948 | 426.7387 | 1
202 | 17 | 22 | 220 |  | 0.35426 | 2.0829 | -6.0498 | 0.6702 | 17.0112 | 1.3119 | 24.9252 | 7.8163 | 183.3333 | 191.1497 | 303.4692 | 1
202 | 18 | 274 | 143 |  | 0.35426 | 2.0829 | -6.0498 | 0.6702 | 18.0112 | 1.5737 | 15.9149 | 35.956 | 119.1667 | 155.1227 | 246.2728 | 1
202 | 19 | 61 | 74 |  | 0.35426 | 2.0829 | -6.0498 | 0.6702 | 19.0112 | 1.8355 | 7.3019 | 0 | 61.6667 | 61.6667 | 97.902 | 0
202 | 20 | 0 | 10 |  | 0.35426 | 2.0829 | -6.0498 | 0.6702 | 20.0112 | 2.0973 | -0.5659 | 0 | 8.3333 | 8.3333 | 13.23 | 0
202 | 21 | 0 | 0 |  | 0.35426 | 2.0829 | -6.0498 | 0.6702 | 21.0112 | 2.3591 | -7.318 | 0 | 0 | 0 | 0 | 0
202 | 22 | 0 | 0 |  | 0.35426 | 2.0829 | -6.0498 | 0.6702 | 22.0112 | 2.6209 | -12.5562 | 0 | 0 | 0 | 0 | 0
202 | 23 | 0 | 0 |  | 0.35426 | 2.0829 | -6.0498 | 0.6702 | 23.0112 | 2.8827 | -15.8905 | 0 | 0 | 0 | 0 | 0
202 | 24 | 0 | 0 |  | 0.35426 | 2.0829 | -6.0498 | 0.6702 | 24.0112 | 3.1445 | -17.0224 | 0 | 0 | 0 | 0 | 0
203 | 1 | 0 | 0 |  | 0.35063 | 2.1001 | -6.0961 | 0.6239 | 1.0104 | -2.8771 | -16.0463 | 0 | 0 | 0 | 0 | 0
203 | 2 | 0 | 0 |  | 0.35063 | 2.1001 | -6.0961 | 0.6239 | 2.0104 | -2.6153 | -12.6596 | 0 | 0 | 0 | 0 | 0
203 | 3 | 0 | 0 |  | 0.35063 | 2.1001 | -6.0961 | 0.6239 | 3.0104 | -2.3535 | -7.3744 | 0 | 0 | 0 | 0 | 0
203 | 4 | 0 | 0 |  | 0.35063 | 2.1001 | -6.0961 | 0.6239 | 4.0104 | -2.0917 | -0.58356 | 0 | 0 | 0 | 0 | 0
203 | 5 | 0 | 6 |  | 0.35063 | 2.1001 | -6.0961 | 0.6239 | 5.0104 | -1.8299 | 7.3132 | 0 | 5 | 5 | 7.938 | 0
203 | 6 | 0 | 36 |  | 0.35063 | 2.1001 | -6.0961 | 0.6239 | 6.0104 | -1.5681 | 15.9448 | 0 | 30 | 30 | 47.628 | 1
203 | 7 | 0 | 86 |  | 0.35063 | 2.1001 | -6.0961 | 0.6239 | 7.0104 | -1.3063 | 24.9625 | 0 | 71.6667 | 71.6667 | 113.778 | 1
203 | 8 | 0 | 143 |  | 0.35063 | 2.1001 | -6.0961 | 0.6239 | 8.0104 | -1.0445 | 34 | 0 | 119.1667 | 119.1667 | 189.189 | 1
203 | 9 | 4 | 195 |  | 0.35063 | 2.1001 | -6.0961 | 0.6239 | 9.0104 | -0.78268 | 42.5994 | 2.9874 | 162.5 | 165.4874 | 262.7277 | 1
203 | 10 | 68 | 336 |  | 0.35063 | 2.1001 | -6.0961 | 0.6239 | 10.0104 | -0.52088 | 50.0881 | 60.1161 | 280 | 340.1161 | 539.9684 | 1
203 | 11 | 25 | 254 |  | 0.35063 | 2.1001 | -6.0961 | 0.6239 | 11.0104 | -0.25908 | 55.4406 | 24.2515 | 211.6667 | 235.9181 | 374.5436 | 1
203 | 12 | 18 | 275 |  | 0.35063 | 2.1001 | -6.0961 | 0.6239 | 12.0104 | 0.0027223 | 57.4092 | 17.9815 | 229.1667 | 247.1482 | 392.3725 | 1
203 | 13 | 11 | 281 |  | 0.35063 | 2.1001 | -6.0961 | 0.6239 | 13.0104 | 0.26452 | 55.3597 | 10.6572 | 234.1667 | 244.8239 | 388.6824 | 1
203 | 14 | 120 | 340 |  | 0.35063 | 2.1001 | -6.0961 | 0.6239 | 14.0104 | 0.52632 | 49.9499 | 105.8042 | 283.3333 | 389.1376 | 617.7948 | 1
203 | 15 | 70 | 335 |  | 0.35063 | 2.1001 | -6.0961 | 0.6239 | 15.0104 | 0.78812 | 42.429 | 52.0454 | 279.1667 | 331.212 | 525.8322 | 1
203 | 16 | 64 | 274 |  | 0.35063 | 2.1001 | -6.0961 | 0.6239 | 16.0104 | 1.0499 | 33.8146 | 36.0746 | 228.3333 | 264.4079 | 419.7741 | 1
203 | 17 | 29 | 213 |  | 0.35063 | 2.1001 | -6.0961 | 0.6239 | 17.0104 | 1.3117 | 24.7734 | 10.2787 | 177.5 | 187.7787 | 298.1175 | 1
203 | 18 | 14 | 132 |  | 0.35063 | 2.1001 | -6.0961 | 0.6239 | 18.0104 | 1.5735 | 15.7602 | 1.8212 | 110 | 111.8212 | 177.5273 | 1
203 | 19 | 0 | 57 |  | 0.35063 | 2.1001 | -6.0961 | 0.6239 | 19.0104 | 1.8353 | 7.1403 | 0 | 47.5 | 47.5 | 75.411 | 0
203 | 20 | 0 | 9 |  | 0.35063 | 2.1001 | -6.0961 | 0.6239 | 20.0104 | 2.0971 | -0.73739 | 0 | 7.5 | 7.5 | 11.907 | 0
203 | 21 | 0 | 0 |  | 0.35063 | 2.1001 | -6.0961 | 0.6239 | 21.0104 | 2.3589 | -7.5011 | 0 | 0 | 0 | 0 | 0
203 | 22 | 0 | 0 |  | 0.35063 | 2.1001 | -6.0961 | 0.6239 | 22.0104 | 2.6207 | -12.7507 | 0 | 0 | 0 | 0 | 0
203 | 23 | 0 | 0 |  | 0.35063 | 2.1001 | -6.0961 | 0.6239 | 23.0104 | 2.8825 | -16.0941 | 0 | 0 | 0 | 0 | 0
203 | 24 | 0 | 0 |  | 0.35063 | 2.1001 | -6.0961 | 0.6239 | 24.0104 | 3.1443 | -17.2305 | 0 | 0 | 0 | 0 | 0
204 | 1 | 0 | 0 |  | 0.34689 | 2.1173 | -6.1329 | 0.58706 | 1.0098 | -2.8772 | -16.2588 | 0 | 0 | 0 | 0 | 0
204 | 2 | 0 | 0 |  | 0.34689 | 2.1173 | -6.1329 | 0.58706 | 2.0098 | -2.6154 | -12.8656 | 0 | 0 | 0 | 0 | 0
204 | 3 | 0 | 0 |  | 0.34689 | 2.1173 | -6.1329 | 0.58706 | 3.0098 | -2.3536 | -7.571 | 0 | 0 | 0 | 0 | 0
204 | 4 | 0 | 0 |  | 0.34689 | 2.1173 | -6.1329 | 0.58706 | 4.0098 | -2.0918 | -0.77011 | 0 | 0 | 0 | 0 | 0
204 | 5 | 0 | 16 |  | 0.34689 | 2.1173 | -6.1329 | 0.58706 | 5.0098 | -1.83 | 7.1354 | 0 | 13.3333 | 13.3333 | 21.168 | 0
204 | 6 | 132 | 71 |  | 0.34689 | 2.1173 | -6.1329 | 0.58706 | 6.0098 | -1.5682 | 15.7732 | 17.5972 | 59.1667 | 76.7639 | 121.8703 | 1
204 | 7 | 345 | 124 |  | 0.34689 | 2.1173 | -6.1329 | 0.58706 | 7.0098 | -1.3064 | 24.7934 | 123.4466 | 103.3333 | 226.7799 | 360.0358 | 1
204 | 8 | 576 | 124 |  | 0.34689 | 2.1173 | -6.1329 | 0.58706 | 8.0098 | -1.0446 | 33.8286 | 326.5167 | 103.3333 | 429.8501 | 682.4299 | 1
204 | 9 | 627 | 153 |  | 0.34689 | 2.1173 | -6.1329 | 0.58706 | 9.0098 | -0.78284 | 42.4201 | 467.8829 | 127.5 | 595.3829 | 945.2299 | 1
204 | 10 | 676 | 195 |  | 0.34689 | 2.1173 | -6.1329 | 0.58706 | 10.0098 | -0.52104 | 49.8951 | 597.3539 | 162.5 | 759.8539 | 1206.3441 | 1
204 | 11 | 787 | 145 |  | 0.34689 | 2.1173 | -6.1329 | 0.58706 | 11.0098 | -0.25924 | 55.2324 | 763.239 | 120.8333 | 884.0724 | 1403.5533 | 1
204 | 12 | 822 | 140 |  | 0.34689 | 2.1173 | -6.1329 | 0.58706 | 12.0098 | 0.0025615 | 57.1952 | 821.0131 | 116.6667 | 937.6798 | 1488.6604 | 1
204 | 13 | 796 | 153 |  | 0.34689 | 2.1173 | -6.1329 | 0.58706 | 13.0098 | 0.26436 | 55.1565 | 771.0515 | 127.5 | 898.5515 | 1426.5403 | 1
204 | 14 | 779 | 149 |  | 0.34689 | 2.1173 | -6.1329 | 0.58706 | 14.0098 | 0.52616 | 49.7653 | 686.6394 | 124.1667 | 810.8061 | 1287.2357 | 1
204 | 15 | 749 | 143 |  | 0.34689 | 2.1173 | -6.1329 | 0.58706 | 15.0098 | 0.78796 | 42.26 | 556.5679 | 119.1667 | 675.7346 | 1072.7963 | 1
204 | 16 | 684 | 134 |  | 0.34689 | 2.1173 | -6.1329 | 0.58706 | 16.0098 | 1.0498 | 33.6543 | 385.1053 | 111.6667 | 496.772 | 788.6753 | 1
204 | 17 | 561 | 128 |  | 0.34689 | 2.1173 | -6.1329 | 0.58706 | 17.0098 | 1.3116 | 24.6154 | 198.326 | 106.6667 | 304.9927 | 484.2064 | 1
204 | 18 | 379 | 110 |  | 0.34689 | 2.1173 | -6.1329 | 0.58706 | 18.0098 | 1.5734 | 15.5994 | 48.8405 | 91.6667 | 140.5072 | 223.0692 | 1
204 | 19 | 132 | 73 |  | 0.34689 | 2.1173 | -6.1329 | 0.58706 | 19.0098 | 1.8352 | 6.9725 | 0 | 60.8333 | 60.8333 | 96.579 | 0
204 | 20 | 0 | 16 |  | 0.34689 | 2.1173 | -6.1329 | 0.58706 | 20.0098 | 2.097 | -0.91507 | 0 | 13.3333 | 13.3333 | 21.168 | 0
204 | 21 | 0 | 0 |  | 0.34689 | 2.1173 | -6.1329 | 0.58706 | 21.0098 | 2.3588 | -7.6904 | 0 | 0 | 0 | 0 | 0
204 | 22 | 0 | 0 |  | 0.34689 | 2.1173 | -6.1329 | 0.58706 | 22.0098 | 2.6206 | -12.9515 | 0 | 0 | 0 | 0 | 0
204 | 23 | 0 | 0 |  | 0.34689 | 2.1173 | -6.1329 | 0.58706 | 23.0098 | 2.8824 | -16.3039 | 0 | 0 | 0 | 0 | 0
204 | 24 | 0 | 0 |  | 0.34689 | 2.1173 | -6.1329 | 0.58706 | 24.0098 | 3.1442 | -17.4445 | 0 | 0 | 0 | 0 | 0
205 | 1 | 0 | 0 |  | 0.34306 | 2.1346 | -6.1602 | 0.55983 | 1.0093 | -2.8774 | -16.4766 | 0 | 0 | 0 | 0 | 0
205 | 2 | 0 | 0 |  | 0.34306 | 2.1346 | -6.1602 | 0.55983 | 2.0093 | -2.6156 | -13.0764 | 0 | 0 | 0 | 0 | 0
205 | 3 | 0 | 0 |  | 0.34306 | 2.1346 | -6.1602 | 0.55983 | 3.0093 | -2.3538 | -7.7719 | 0 | 0 | 0 | 0 | 0
205 | 4 | 0 | 0 |  | 0.34306 | 2.1346 | -6.1602 | 0.55983 | 4.0093 | -2.092 | -0.96046 | 0 | 0 | 0 | 0 | 0
205 | 5 | 0 | 15 |  | 0.34306 | 2.1346 | -6.1602 | 0.55983 | 5.0093 | -1.8302 | 6.9542 | 0 | 12.5 | 12.5 | 19.845 | 0
205 | 6 | 148 | 69 |  | 0.34306 | 2.1346 | -6.1602 | 0.55983 | 6.0093 | -1.5684 | 15.5984 | 19.5093 | 57.5 | 77.0093 | 122.26 | 1
205 | 7 | 340 | 124 |  | 0.34306 | 2.1346 | -6.1602 | 0.55983 | 7.0093 | -1.3066 | 24.6211 | 121.2566 | 103.3333 | 224.59 | 356.559 | 1
205 | 8 | 564 | 127 |  | 0.34306 | 2.1346 | -6.1602 | 0.55983 | 8.0093 | -1.0448 | 33.654 | 319.2178 | 105.8333 | 425.0512 | 674.8112 | 1
205 | 9 | 680 | 135 |  | 0.34306 | 2.1346 | -6.1602 | 0.55983 | 9.0093 | -0.78296 | 42.237 | 507.0137 | 112.5 | 619.5137 | 983.5399 | 1
205 | 10 | 720 | 156 |  | 0.34306 | 2.1346 | -6.1602 | 0.55983 | 10.0093 | -0.52116 | 49.6978 | 635.9431 | 130 | 765.9431 | 1216.0113 | 1
205 | 11 | 698 | 190 |  | 0.34306 | 2.1346 | -6.1602 | 0.55983 | 11.0093 | -0.25936 | 55.0191 | 676.7435 | 158.3333 | 835.0769 | 1325.768 | 1
205 | 12 | 704 | 203 |  | 0.34306 | 2.1346 | -6.1602 | 0.55983 | 12.0093 | 0.0024427 | 56.9754 | 703.0176 | 169.1667 | 872.1843 | 1384.6798 | 1
205 | 13 | 329 | 317 |  | 0.34306 | 2.1346 | -6.1602 | 0.55983 | 13.0093 | 0.26424 | 54.9471 | 318.6194 | 264.1667 | 582.786 | 925.2311 | 1
205 | 14 | 536 | 281 |  | 0.34306 | 2.1346 | -6.1602 | 0.55983 | 14.0093 | 0.52604 | 49.5744 | 472.2867 | 234.1667 | 706.4533 | 1121.5653 | 1
205 | 15 | 361 | 310 |  | 0.34306 | 2.1346 | -6.1602 | 0.55983 | 15.0093 | 0.78784 | 42.0846 | 268.081 | 258.3333 | 526.4143 | 835.7354 | 1
205 | 16 | 604 | 176 |  | 0.34306 | 2.1346 | -6.1602 | 0.55983 | 16.0093 | 1.0496 | 33.4878 | 339.6369 | 146.6667 | 486.3036 | 772.0556 | 1
205 | 17 | 535 | 135 |  | 0.34306 | 2.1346 | -6.1602 | 0.55983 | 17.0093 | 1.3114 | 24.4514 | 188.6072 | 112.5 | 301.1072 | 478.0378 | 1
205 | 18 | 296 | 128 |  | 0.34306 | 2.1346 | -6.1602 | 0.55983 | 18.0093 | 1.5732 | 15.4326 | 37.7621 | 106.6667 | 144.4288 | 229.2951 | 1
205 | 19 | 85 | 72 |  | 0.34306 | 2.1346 | -6.1602 | 0.55983 | 19.0093 | 1.835 | 6.7987 | 0 | 60 | 60 | 95.256 | 0
205 | 20 | 0 | 11 |  | 0.34306 | 2.1346 | -6.1602 | 0.55983 | 20.0093 | 2.0968 | -1.0989 | 0 | 9.1667 | 9.1667 | 14.553 | 0
205 | 21 | 0 | 0 |  | 0.34306 | 2.1346 | -6.1602 | 0.55983 | 21.0093 | 2.3586 | -7.8859 | 0 | 0 | 0 | 0 | 0
205 | 22 | 0 | 0 |  | 0.34306 | 2.1346 | -6.1602 | 0.55983 | 22.0093 | 2.6204 | -13.1585 | 0 | 0 | 0 | 0 | 0
205 | 23 | 0 | 0 |  | 0.34306 | 2.1346 | -6.1602 | 0.55983 | 23.0093 | 2.8822 | -16.5198 | 0 | 0 | 0 | 0 | 0
205 | 24 | 0 | 0 |  | 0.34306 | 2.1346 | -6.1602 | 0.55983 | 24.0093 | 3.144 | -17.6643 | 0 | 0 | 0 | 0 | 0
206 | 1 | 0 | 0 |  | 0.33912 | 2.1518 | -6.1777 | 0.54235 | 1.009 | -2.8774 | -16.6998 | 0 | 0 | 0 | 0 | 0
206 | 2 | 0 | 0 |  | 0.33912 | 2.1518 | -6.1777 | 0.54235 | 2.009 | -2.6156 | -13.292 | 0 | 0 | 0 | 0 | 0
206 | 3 | 0 | 0 |  | 0.33912 | 2.1518 | -6.1777 | 0.54235 | 3.009 | -2.3538 | -7.9769 | 0 | 0 | 0 | 0 | 0
206 | 4 | 0 | 0 |  | 0.33912 | 2.1518 | -6.1777 | 0.54235 | 4.009 | -2.092 | -1.1545 | 0 | 0 | 0 | 0 | 0
206 | 5 | 0 | 12 |  | 0.33912 | 2.1518 | -6.1777 | 0.54235 | 5.009 | -1.8302 | 6.7697 | 0 | 10 | 10 | 15.876 | 0
206 | 6 | 57 | 69 |  | 0.33912 | 2.1518 | -6.1777 | 0.54235 | 6.009 | -1.5684 | 15.4205 | 7.4286 | 57.5 | 64.9286 | 103.0806 | 1
206 | 7 | 259 | 140 |  | 0.33912 | 2.1518 | -6.1777 | 0.54235 | 7.009 | -1.3066 | 24.4457 | 92.0641 | 116.6667 | 208.7308 | 331.381 | 1
206 | 8 | 153 | 213 |  | 0.33912 | 2.1518 | -6.1777 | 0.54235 | 8.009 | -1.0448 | 33.476 | 86.462 | 177.5 | 263.962 | 419.0661 | 1
206 | 9 | 435 | 238 |  | 0.33912 | 2.1518 | -6.1777 | 0.54235 | 9.009 | -0.78303 | 42.0504 | 324.0716 | 198.3333 | 522.405 | 829.3701 | 1
206 | 10 | 360 | 309 |  | 0.33912 | 2.1518 | -6.1777 | 0.54235 | 10.009 | -0.52123 | 49.4962 | 317.824 | 257.5 | 575.324 | 913.3844 | 1
206 | 11 | 119 | 338 |  | 0.33912 | 2.1518 | -6.1777 | 0.54235 | 11.009 | -0.25943 | 54.8009 | 115.3435 | 281.6667 | 397.0102 | 630.2934 | 1
206 | 12 | 269 | 366 |  | 0.33912 | 2.1518 | -6.1777 | 0.54235 | 12.009 | 0.0023664 | 56.7499 | 268.5667 | 305 | 573.5667 | 910.5945 | 1
206 | 13 | 99 | 377 |  | 0.33912 | 2.1518 | -6.1777 | 0.54235 | 13.009 | 0.26417 | 54.7313 | 95.8526 | 314.1667 | 410.0192 | 650.9465 | 1
206 | 14 | 85 | 365 |  | 0.33912 | 2.1518 | -6.1777 | 0.54235 | 14.009 | 0.52597 | 49.377 | 74.8668 | 304.1667 | 379.0334 | 601.7535 | 1
206 | 15 | 69 | 331 |  | 0.33912 | 2.1518 | -6.1777 | 0.54235 | 15.009 | 0.78776 | 41.9029 | 51.2035 | 275.8333 | 327.0369 | 519.2037 | 1
206 | 16 | 9 | 188 |  | 0.33912 | 2.1518 | -6.1777 | 0.54235 | 16.009 | 1.0496 | 33.3152 | 5.0539 | 156.6667 | 161.7206 | 256.7476 | 1
206 | 17 | 38 | 205 |  | 0.33912 | 2.1518 | -6.1777 | 0.54235 | 17.009 | 1.3114 | 24.2813 | 13.3563 | 170.8333 | 184.1896 | 292.4195 | 1
206 | 18 | 282 | 138 |  | 0.33912 | 2.1518 | -6.1777 | 0.54235 | 18.009 | 1.5732 | 15.2597 | 35.5905 | 115 | 150.5905 | 239.0775 | 1
206 | 19 | 60 | 68 |  | 0.33912 | 2.1518 | -6.1777 | 0.54235 | 19.009 | 1.835 | 6.6189 | 0 | 56.6667 | 56.6667 | 89.964 | 0
206 | 20 | 0 | 14 |  | 0.33912 | 2.1518 | -6.1777 | 0.54235 | 20.009 | 2.0968 | -1.2888 | 0 | 11.6667 | 11.6667 | 18.522 | 0
206 | 21 | 0 | 0 |  | 0.33912 | 2.1518 | -6.1777 | 0.54235 | 21.009 | 2.3586 | -8.0876 | 0 | 0 | 0 | 0 | 0
206 | 22 | 0 | 0 |  | 0.33912 | 2.1518 | -6.1777 | 0.54235 | 22.009 | 2.6204 | -13.3717 | 0 | 0 | 0 | 0 | 0
206 | 23 | 0 | 0 |  | 0.33912 | 2.1518 | -6.1777 | 0.54235 | 23.009 | 2.8822 | -16.7417 | 0 | 0 | 0 | 0 | 0
206 | 24 | 0 | 0 |  | 0.33912 | 2.1518 | -6.1777 | 0.54235 | 24.009 | 3.144 | -17.8899 | 0 | 0 | 0 | 0 | 0
207 | 1 | 0 | 0 |  | 0.33508 | 2.169 | -6.1853 | 0.53475 | 1.0089 | -2.8775 | -16.9281 | 0 | 0 | 0 | 0 | 0
207 | 2 | 0 | 0 |  | 0.33508 | 2.169 | -6.1853 | 0.53475 | 2.0089 | -2.6157 | -13.5122 | 0 | 0 | 0 | 0 | 0
207 | 3 | 0 | 0 |  | 0.33508 | 2.169 | -6.1853 | 0.53475 | 3.0089 | -2.3539 | -8.186 | 0 | 0 | 0 | 0 | 0
207 | 4 | 0 | 0 |  | 0.33508 | 2.169 | -6.1853 | 0.53475 | 4.0089 | -2.0921 | -1.3521 | 0 | 0 | 0 | 0 | 0
207 | 5 | 0 | 10 |  | 0.33508 | 2.169 | -6.1853 | 0.53475 | 5.0089 | -1.8303 | 6.5819 | 0 | 8.3333 | 8.3333 | 13.23 | 0
207 | 6 | 0 | 52 |  | 0.33508 | 2.169 | -6.1853 | 0.53475 | 6.0089 | -1.5685 | 15.2395 | 0 | 43.3333 | 43.3333 | 68.796 | 1
207 | 7 | 14 | 127 |  | 0.33508 | 2.169 | -6.1853 | 0.53475 | 7.0089 | -1.3067 | 24.2674 | 4.96 | 105.8333 | 110.7933 | 175.8955 | 1
207 | 8 | 27 | 209 |  | 0.33508 | 2.169 | -6.1853 | 0.53475 | 8.0089 | -1.0449 | 33.2949 | 15.2344 | 174.1667 | 189.401 | 300.6931 | 1
207 | 9 | 48 | 278 |  | 0.33508 | 2.169 | -6.1853 | 0.53475 | 9.0089 | -0.78306 | 41.8602 | 35.7301 | 231.6667 | 267.3967 | 424.519 | 1
207 | 10 | 69 | 330 |  | 0.33508 | 2.169 | -6.1853 | 0.53475 | 10.0089 | -0.52127 | 49.2905 | 60.8876 | 275 | 335.8876 | 533.2552 | 1
207 | 11 | 24 | 251 |  | 0.33508 | 2.169 | -6.1853 | 0.53475 | 11.0089 | -0.25947 | 54.5777 | 23.2557 | 209.1667 | 232.4224 | 368.9938 | 1
207 | 12 | 11 | 278 |  | 0.33508 | 2.169 | -6.1853 | 0.53475 | 12.0089 | 0.0023333 | 56.5186 | 10.9797 | 231.6667 | 242.6463 | 385.2253 | 1
207 | 13 | 11 | 278 |  | 0.33508 | 2.169 | -6.1853 | 0.53475 | 13.0089 | 0.26413 | 54.5094 | 10.6473 | 231.6667 | 242.314 | 384.6976 | 1
207 | 14 | 10 | 262 |  | 0.33508 | 2.169 | -6.1853 | 0.53475 | 14.0089 | 0.52593 | 49.1733 | 8.804 | 218.3333 | 227.1373 | 360.6032 | 1
207 | 15 | 68 | 331 |  | 0.33508 | 2.169 | -6.1853 | 0.53475 | 15.0089 | 0.78773 | 41.715 | 50.4221 | 275.8333 | 326.2554 | 517.9631 | 1
207 | 16 | 63 | 269 |  | 0.33508 | 2.169 | -6.1853 | 0.53475 | 16.0089 | 1.0495 | 33.1365 | 35.325 | 224.1667 | 259.4917 | 411.969 | 1
207 | 17 | 0 | 139 |  | 0.33508 | 2.169 | -6.1853 | 0.53475 | 17.0089 | 1.3113 | 24.1053 | 0 | 115.8333 | 115.8333 | 183.897 | 1
207 | 18 | 0 | 82 |  | 0.33508 | 2.169 | -6.1853 | 0.53475 | 18.0089 | 1.5731 | 15.0809 | 0 | 68.3333 | 68.3333 | 108.486 | 1
207 | 19 | 0 | 52 |  | 0.33508 | 2.169 | -6.1853 | 0.53475 | 19.0089 | 1.8349 | 6.4331 | 0 | 43.3333 | 43.3333 | 68.796 | 0
207 | 20 | 0 | 13 |  | 0.33508 | 2.169 | -6.1853 | 0.53475 | 20.0089 | 2.0967 | -1.4847 | 0 | 10.8333 | 10.8333 | 17.199 | 0
207 | 21 | 0 | 0 |  | 0.33508 | 2.169 | -6.1853 | 0.53475 | 21.0089 | 2.3585 | -8.2954 | 0 | 0 | 0 | 0 | 0
207 | 22 | 0 | 0 |  | 0.33508 | 2.169 | -6.1853 | 0.53475 | 22.0089 | 2.6203 | -13.5909 | 0 | 0 | 0 | 0 | 0
207 | 23 | 0 | 0 |  | 0.33508 | 2.169 | -6.1853 | 0.53475 | 23.0089 | 2.8821 | -16.9696 | 0 | 0 | 0 | 0 | 0
207 | 24 | 0 | 0 |  | 0.33508 | 2.169 | -6.1853 | 0.53475 | 24.0089 | 3.1439 | -18.1211 | 0 | 0 | 0 | 0 | 0
208 | 1 | 0 | 0 |  | 0.33095 | 2.1862 | -6.1829 | 0.53715 | 1.009 | -2.8774 | -17.1616 | 0 | 0 | 0 | 0 | 0
208 | 2 | 0 | 0 |  | 0.33095 | 2.1862 | -6.1829 | 0.53715 | 2.009 | -2.6157 | -13.7369 | 0 | 0 | 0 | 0 | 0
208 | 3 | 0 | 0 |  | 0.33095 | 2.1862 | -6.1829 | 0.53715 | 3.009 | -2.3539 | -8.3991 | 0 | 0 | 0 | 0 | 0
208 | 4 | 0 | 0 |  | 0.33095 | 2.1862 | -6.1829 | 0.53715 | 4.009 | -2.0921 | -1.5533 | 0 | 0 | 0 | 0 | 0
208 | 5 | 0 | 5 |  | 0.33095 | 2.1862 | -6.1829 | 0.53715 | 5.009 | -1.8303 | 6.391 | 0 | 4.1667 | 4.1667 | 6.615 | 0
208 | 6 | 0 | 32 |  | 0.33095 | 2.1862 | -6.1829 | 0.53715 | 6.009 | -1.5685 | 15.0556 | 0 | 26.6667 | 26.6667 | 42.336 | 1
208 | 7 | 0 | 82 |  | 0.33095 | 2.1862 | -6.1829 | 0.53715 | 7.009 | -1.3067 | 24.0861 | 0 | 68.3333 | 68.3333 | 108.486 | 1
208 | 8 | 0 | 139 |  | 0.33095 | 2.1862 | -6.1829 | 0.53715 | 8.009 | -1.0449 | 33.1107 | 0 | 115.8333 | 115.8333 | 183.897 | 1
208 | 9 | 63 | 269 |  | 0.33095 | 2.1862 | -6.1829 | 0.53715 | 9.009 | -0.78305 | 41.6665 | 46.8569 | 224.1667 | 271.0235 | 430.277 | 1
208 | 10 | 70 | 330 |  | 0.33095 | 2.1862 | -6.1829 | 0.53715 | 10.009 | -0.52126 | 49.0807 | 61.7406 | 275 | 336.7406 | 534.6094 | 1
208 | 11 | 271 | 341 |  | 0.33095 | 2.1862 | -6.1829 | 0.53715 | 11.009 | -0.25946 | 54.3496 | 262.5147 | 284.1667 | 546.6814 | 867.9114 | 1
208 | 12 | 240 | 392 |  | 0.33095 | 2.1862 | -6.1829 | 0.53715 | 12.009 | 0.0023437 | 56.2818 | 239.4943 | 326.6667 | 566.1609 | 898.8371 | 1
208 | 13 | 448 | 315 |  | 0.33095 | 2.1862 | -6.1829 | 0.53715 | 13.009 | 0.26414 | 54.2813 | 433.4984 | 262.5 | 695.9984 | 1104.9671 | 1
208 | 14 | 632 | 246 |  | 0.33095 | 2.1862 | -6.1829 | 0.53715 | 14.009 | 0.52594 | 48.9633 | 556.1372 | 205 | 761.1372 | 1208.3814 | 1
208 | 15 | 362 | 309 |  | 0.33095 | 2.1862 | -6.1829 | 0.53715 | 15.009 | 0.78774 | 41.5209 | 268.1941 | 257.5 | 525.6941 | 834.592 | 1
208 | 16 | 64 | 270 |  | 0.33095 | 2.1862 | -6.1829 | 0.53715 | 16.009 | 1.0495 | 32.9517 | 35.8286 | 225 | 260.8286 | 414.0914 | 1
208 | 17 | 150 | 213 |  | 0.33095 | 2.1862 | -6.1829 | 0.53715 | 17.009 | 1.3113 | 23.9232 | 52.3743 | 177.5 | 229.8743 | 364.9485 | 1
208 | 18 | 311 | 120 |  | 0.33095 | 2.1862 | -6.1829 | 0.53715 | 18.009 | 1.5731 | 14.8962 | 38.3297 | 100 | 138.3297 | 219.6122 | 1
208 | 19 | 0 | 51 |  | 0.33095 | 2.1862 | -6.1829 | 0.53715 | 19.009 | 1.8349 | 6.2413 | 0 | 42.5 | 42.5 | 67.473 | 0
208 | 20 | 0 | 7 |  | 0.33095 | 2.1862 | -6.1829 | 0.53715 | 20.009 | 2.0967 | -1.6867 | 0 | 5.8333 | 5.8333 | 9.261 | 0
208 | 21 | 0 | 0 |  | 0.33095 | 2.1862 | -6.1829 | 0.53715 | 21.009 | 2.3585 | -8.5092 | 0 | 0 | 0 | 0 | 0
208 | 22 | 0 | 0 |  | 0.33095 | 2.1862 | -6.1829 | 0.53715 | 22.009 | 2.6203 | -13.8162 | 0 | 0 | 0 | 0 | 0
208 | 23 | 0 | 0 |  | 0.33095 | 2.1862 | -6.1829 | 0.53715 | 23.009 | 2.8821 | -17.2033 | 0 | 0 | 0 | 0 | 0
208 | 24 | 0 | 0 |  | 0.33095 | 2.1862 | -6.1829 | 0.53715 | 24.009 | 3.1439 | -18.358 | 0 | 0 | 0 | 0 | 0
209 | 1 | 0 | 0 |  | 0.32672 | 2.2034 | -6.1704 | 0.54965 | 1.0092 | -2.8774 | -17.4001 | 0 | 0 | 0 | 0 | 0
209 | 2 | 0 | 0 |  | 0.32672 | 2.2034 | -6.1704 | 0.54965 | 2.0092 | -2.6156 | -13.9661 | 0 | 0 | 0 | 0 | 0
209 | 3 | 0 | 0 |  | 0.32672 | 2.2034 | -6.1704 | 0.54965 | 3.0092 | -2.3538 | -8.6161 | 0 | 0 | 0 | 0 | 0
209 | 4 | 0 | 0 |  | 0.32672 | 2.2034 | -6.1704 | 0.54965 | 4.0092 | -2.092 | -1.7578 | 0 | 0 | 0 | 0 | 0
209 | 5 | 0 | 4 |  | 0.32672 | 2.2034 | -6.1704 | 0.54965 | 5.0092 | -1.8302 | 6.197 | 0 | 3.3333 | 3.3333 | 5.292 | 0
209 | 6 | 0 | 31 |  | 0.32672 | 2.2034 | -6.1704 | 0.54965 | 6.0092 | -1.5684 | 14.8688 | 0 | 25.8333 | 25.8333 | 41.013 | 1
209 | 7 | 0 | 80 |  | 0.32672 | 2.2034 | -6.1704 | 0.54965 | 7.0092 | -1.3066 | 23.9019 | 0 | 66.6667 | 66.6667 | 105.84 | 1
209 | 8 | 0 | 137 |  | 0.32672 | 2.2034 | -6.1704 | 0.54965 | 8.0092 | -1.0448 | 32.9235 | 0 | 114.1667 | 114.1667 | 181.251 | 1
209 | 9 | 61 | 267 |  | 0.32672 | 2.2034 | -6.1704 | 0.54965 | 9.0092 | -0.783 | 41.4693 | 45.3318 | 222.5 | 267.8318 | 425.2097 | 1
209 | 10 | 7 | 232 |  | 0.32672 | 2.2034 | -6.1704 | 0.54965 | 10.0092 | -0.5212 | 48.8669 | 6.1711 | 193.3333 | 199.5044 | 316.7332 | 1
209 | 11 | 10 | 260 |  | 0.32672 | 2.2034 | -6.1704 | 0.54965 | 11.0092 | -0.2594 | 54.1168 | 9.6838 | 216.6667 | 226.3504 | 359.3539 | 1
209 | 12 | 11 | 277 |  | 0.32672 | 2.2034 | -6.1704 | 0.54965 | 12.0092 | 0.0023983 | 56.0395 | 10.9737 | 230.8333 | 241.807 | 383.8929 | 1
209 | 13 | 11 | 277 |  | 0.32672 | 2.2034 | -6.1704 | 0.54965 | 13.0092 | 0.2642 | 54.0472 | 10.6402 | 230.8333 | 241.4735 | 383.3634 | 1
209 | 14 | 10 | 261 |  | 0.32672 | 2.2034 | -6.1704 | 0.54965 | 14.0092 | 0.526 | 48.7471 | 8.7949 | 217.5 | 226.2949 | 359.2657 | 1
209 | 15 | 6 | 232 |  | 0.32672 | 2.2034 | -6.1704 | 0.54965 | 15.0092 | 0.7878 | 41.3206 | 4.4411 | 193.3333 | 197.7744 | 313.9867 | 1
209 | 16 | 3 | 189 |  | 0.32672 | 2.2034 | -6.1704 | 0.54965 | 16.0092 | 1.0496 | 32.7608 | 1.6766 | 157.5 | 159.1766 | 252.7088 | 1
209 | 17 | 37 | 201 |  | 0.32672 | 2.2034 | -6.1704 | 0.54965 | 17.0092 | 1.3114 | 23.7353 | 12.8721 | 167.5 | 180.3721 | 286.3588 | 1
209 | 18 | 0 | 80 |  | 0.32672 | 2.2034 | -6.1704 | 0.54965 | 18.0092 | 1.5732 | 14.7056 | 0 | 66.6667 | 66.6667 | 105.84 | 1
209 | 19 | 3 | 63 |  | 0.32672 | 2.2034 | -6.1704 | 0.54965 | 19.0092 | 1.835 | 6.0437 | 0 | 52.5 | 52.5 | 83.349 | 0
209 | 20 | 0 | 12 |  | 0.32672 | 2.2034 | -6.1704 | 0.54965 | 20.0092 | 2.0968 | -1.8945 | 0 | 10 | 10 | 15.876 | 0
209 | 21 | 0 | 0 |  | 0.32672 | 2.2034 | -6.1704 | 0.54965 | 21.0092 | 2.3586 | -8.7289 | 0 | 0 | 0 | 0 | 0
209 | 22 | 0 | 0 |  | 0.32672 | 2.2034 | -6.1704 | 0.54965 | 22.0092 | 2.6204 | -14.0474 | 0 | 0 | 0 | 0 | 0
209 | 23 | 0 | 0 |  | 0.32672 | 2.2034 | -6.1704 | 0.54965 | 23.0092 | 2.8822 | -17.4429 | 0 | 0 | 0 | 0 | 0
209 | 24 | 0 | 0 |  | 0.32672 | 2.2034 | -6.1704 | 0.54965 | 24.0092 | 3.144 | -18.6003 | 0 | 0 | 0 | 0 | 0
210 | 1 | 0 | 0 |  | 0.3224 | 2.2206 | -6.1477 | 0.57234 | 1.0095 | -2.8773 | -17.6435 | 0 | 0 | 0 | 0 | 0
210 | 2 | 0 | 0 |  | 0.3224 | 2.2206 | -6.1477 | 0.57234 | 2.0095 | -2.6155 | -14.1996 | 0 | 0 | 0 | 0 | 0
210 | 3 | 0 | 0 |  | 0.3224 | 2.2206 | -6.1477 | 0.57234 | 3.0095 | -2.3537 | -8.8368 | 0 | 0 | 0 | 0 | 0
210 | 4 | 0 | 0 |  | 0.3224 | 2.2206 | -6.1477 | 0.57234 | 4.0095 | -2.0919 | -1.9656 | 0 | 0 | 0 | 0 | 0
210 | 5 | 0 | 4 |  | 0.3224 | 2.2206 | -6.1477 | 0.57234 | 5.0095 | -1.8301 | 6.0001 | 0 | 3.3333 | 3.3333 | 5.292 | 0
210 | 6 | 0 | 30 |  | 0.3224 | 2.2206 | -6.1477 | 0.57234 | 6.0095 | -1.5683 | 14.6792 | 0 | 25 | 25 | 39.69 | 1
210 | 7 | 0 | 80 |  | 0.3224 | 2.2206 | -6.1477 | 0.57234 | 7.0095 | -1.3065 | 23.7149 | 0 | 66.6667 | 66.6667 | 105.84 | 1
210 | 8 | 38 | 200 |  | 0.3224 | 2.2206 | -6.1477 | 0.57234 | 8.0095 | -1.0447 | 32.7333 | 21.3418 | 166.6667 | 188.0085 | 298.4823 | 1
210 | 9 | 63 | 266 |  | 0.3224 | 2.2206 | -6.1477 | 0.57234 | 9.0095 | -0.7829 | 41.2688 | 46.7792 | 221.6667 | 268.4458 | 426.1846 | 1
210 | 10 | 201 | 341 |  | 0.3224 | 2.2206 | -6.1477 | 0.57234 | 10.0095 | -0.5211 | 48.6492 | 177.1109 | 284.1667 | 461.2775 | 732.3242 | 1
210 | 11 | 100 | 351 |  | 0.3224 | 2.2206 | -6.1477 | 0.57234 | 11.0095 | -0.2593 | 53.8794 | 96.8048 | 292.5 | 389.3048 | 618.0602 | 1
210 | 12 | 479 | 391 |  | 0.3224 | 2.2206 | -6.1477 | 0.57234 | 12.0095 | 0.0024973 | 55.7917 | 477.7074 | 325.8333 | 803.5407 | 1275.7012 | 1
210 | 13 | 415 | 339 |  | 0.3224 | 2.2206 | -6.1477 | 0.57234 | 13.0095 | 0.2643 | 53.8072 | 401.2703 | 282.5 | 683.7703 | 1085.5537 | 1
210 | 14 | 122 | 333 |  | 0.3224 | 2.2206 | -6.1477 | 0.57234 | 14.0095 | 0.5261 | 48.5248 | 107.2335 | 277.5 | 384.7335 | 610.8029 | 1
210 | 15 | 202 | 341 |  | 0.3224 | 2.2206 | -6.1477 | 0.57234 | 15.0095 | 0.7879 | 41.1142 | 149.366 | 284.1667 | 433.5326 | 688.2764 | 1
210 | 16 | 67 | 264 |  | 0.3224 | 2.2206 | -6.1477 | 0.57234 | 16.0095 | 1.0497 | 32.564 | 37.3754 | 220 | 257.3754 | 408.6092 | 1
210 | 17 | 28 | 204 |  | 0.3224 | 2.2206 | -6.1477 | 0.57234 | 17.0095 | 1.3115 | 23.5414 | 9.7036 | 170 | 179.7036 | 285.2975 | 1
210 | 18 | 13 | 123 |  | 0.3224 | 2.2206 | -6.1477 | 0.57234 | 18.0095 | 1.5733 | 14.5092 | 1.5598 | 102.5 | 104.0598 | 165.2053 | 1
210 | 19 | 0 | 30 |  | 0.3224 | 2.2206 | -6.1477 | 0.57234 | 19.0095 | 1.8351 | 5.8402 | 0 | 25 | 25 | 39.69 | 0
210 | 20 | 0 | 4 |  | 0.3224 | 2.2206 | -6.1477 | 0.57234 | 20.0095 | 2.0969 | -2.1082 | 0 | 3.3333 | 3.3333 | 5.292 | 0
210 | 21 | 0 | 0 |  | 0.3224 | 2.2206 | -6.1477 | 0.57234 | 21.0095 | 2.3587 | -8.9546 | 0 | 0 | 0 | 0 | 0
210 | 22 | 0 | 0 |  | 0.3224 | 2.2206 | -6.1477 | 0.57234 | 22.0095 | 2.6205 | -14.2845 | 0 | 0 | 0 | 0 | 0
210 | 23 | 0 | 0 |  | 0.3224 | 2.2206 | -6.1477 | 0.57234 | 23.0095 | 2.8823 | -17.6882 | 0 | 0 | 0 | 0 | 0
210 | 24 | 0 | 0 |  | 0.3224 | 2.2206 | -6.1477 | 0.57234 | 24.0095 | 3.1441 | -18.848 | 0 | 0 | 0 | 0 | 0
211 | 1 | 0 | 0 |  | 0.31798 | 2.2378 | -6.1147 | 0.60531 | 1.0101 | -2.8772 | -17.8917 | 0 | 0 | 0 | 0 | 0
211 | 2 | 0 | 0 |  | 0.31798 | 2.2378 | -6.1147 | 0.60531 | 2.0101 | -2.6154 | -14.4374 | 0 | 0 | 0 | 0 | 0
211 | 3 | 0 | 0 |  | 0.31798 | 2.2378 | -6.1147 | 0.60531 | 3.0101 | -2.3536 | -9.0612 | 0 | 0 | 0 | 0 | 0
211 | 4 | 0 | 0 |  | 0.31798 | 2.2378 | -6.1147 | 0.60531 | 4.0101 | -2.0918 | -2.1767 | 0 | 0 | 0 | 0 | 0
211 | 5 | 0 | 4 |  | 0.31798 | 2.2378 | -6.1147 | 0.60531 | 5.0101 | -1.83 | 5.8002 | 0 | 3.3333 | 3.3333 | 5.292 | 0
211 | 6 | 0 | 29 |  | 0.31798 | 2.2378 | -6.1147 | 0.60531 | 6.0101 | -1.5682 | 14.4869 | 0 | 24.1667 | 24.1667 | 38.367 | 1
211 | 7 | 0 | 79 |  | 0.31798 | 2.2378 | -6.1147 | 0.60531 | 7.0101 | -1.3064 | 23.5252 | 0 | 65.8333 | 65.8333 | 104.517 | 1
211 | 8 | 38 | 198 |  | 0.31798 | 2.2378 | -6.1147 | 0.60531 | 8.0101 | -1.0446 | 32.5401 | 21.309 | 165 | 186.309 | 295.7842 | 1
211 | 9 | 4 | 187 |  | 0.31798 | 2.2378 | -6.1147 | 0.60531 | 9.0101 | -0.78276 | 41.065 | 2.9676 | 155.8333 | 158.801 | 252.1124 | 1
211 | 10 | 69 | 327 |  | 0.31798 | 2.2378 | -6.1147 | 0.60531 | 10.0101 | -0.52096 | 48.4275 | 60.7688 | 272.5 | 333.2688 | 529.0976 | 1
211 | 11 | 86 | 360 |  | 0.31798 | 2.2378 | -6.1147 | 0.60531 | 11.0101 | -0.25916 | 53.6373 | 83.2225 | 300 | 383.2225 | 608.404 | 1
211 | 12 | 87 | 382 |  | 0.31798 | 2.2378 | -6.1147 | 0.60531 | 12.0101 | 0.0026412 | 55.5387 | 86.7362 | 318.3333 | 405.0695 | 643.0883 | 1
211 | 13 | 87 | 382 |  | 0.31798 | 2.2378 | -6.1147 | 0.60531 | 13.0101 | 0.26444 | 53.5613 | 84.0859 | 318.3333 | 402.4193 | 638.8808 | 1
211 | 14 | 86 | 359 |  | 0.31798 | 2.2378 | -6.1147 | 0.60531 | 14.0101 | 0.52624 | 48.2964 | 75.5418 | 299.1667 | 374.7084 | 594.8871 | 1
211 | 15 | 70 | 326 |  | 0.31798 | 2.2378 | -6.1147 | 0.60531 | 15.0101 | 0.78804 | 40.9018 | 51.7044 | 271.6667 | 323.3711 | 513.3839 | 1
211 | 16 | 63 | 264 |  | 0.31798 | 2.2378 | -6.1147 | 0.60531 | 16.0101 | 1.0498 | 32.3613 | 35.0756 | 220 | 255.0756 | 404.958 | 1
211 | 17 | 317 | 202 |  | 0.31798 | 2.2378 | -6.1147 | 0.60531 | 17.0101 | 1.3116 | 23.3417 | 109.4123 | 168.3333 | 277.7456 | 440.949 | 1
211 | 18 | 19 | 119 |  | 0.31798 | 2.2378 | -6.1147 | 0.60531 | 18.0101 | 1.5734 | 14.3069 | 2.2465 | 99.1667 | 101.4132 | 161.0036 | 1
211 | 19 | 0 | 47 |  | 0.31798 | 2.2378 | -6.1147 | 0.60531 | 19.0101 | 1.8352 | 5.631 | 0 | 39.1667 | 39.1667 | 62.181 | 0
211 | 20 | 0 | 11 |  | 0.31798 | 2.2378 | -6.1147 | 0.60531 | 20.0101 | 2.097 | -2.3277 | 0 | 9.1667 | 9.1667 | 14.553 | 0
211 | 21 | 0 | 0 |  | 0.31798 | 2.2378 | -6.1147 | 0.60531 | 21.0101 | 2.3588 | -9.186 | 0 | 0 | 0 | 0 | 0
211 | 22 | 0 | 0 |  | 0.31798 | 2.2378 | -6.1147 | 0.60531 | 22.0101 | 2.6206 | -14.5274 | 0 | 0 | 0 | 0 | 0
211 | 23 | 0 | 0 |  | 0.31798 | 2.2378 | -6.1147 | 0.60531 | 23.0101 | 2.8824 | -17.9391 | 0 | 0 | 0 | 0 | 0
211 | 24 | 0 | 0 |  | 0.31798 | 2.2378 | -6.1147 | 0.60531 | 24.0101 | 3.1442 | -19.101 | 0 | 0 | 0 | 0 | 0
212 | 1 | 0 | 0 |  | 0.31347 | 2.2551 | -6.0714 | 0.64863 | 1.0108 | -2.877 | -18.1446 | 0 | 0 | 0 | 0 | 0
212 | 2 | 0 | 0 |  | 0.31347 | 2.2551 | -6.0714 | 0.64863 | 2.0108 | -2.6152 | -14.6792 | 0 | 0 | 0 | 0 | 0
212 | 3 | 0 | 0 |  | 0.31347 | 2.2551 | -6.0714 | 0.64863 | 3.0108 | -2.3534 | -9.2892 | 0 | 0 | 0 | 0 | 0
212 | 4 | 0 | 0 |  | 0.31347 | 2.2551 | -6.0714 | 0.64863 | 4.0108 | -2.0916 | -2.3908 | 0 | 0 | 0 | 0 | 0
212 | 5 | 0 | 5 |  | 0.31347 | 2.2551 | -6.0714 | 0.64863 | 5.0108 | -1.8298 | 5.5976 | 0 | 4.1667 | 4.1667 | 6.615 | 0
212 | 6 | 0 | 46 |  | 0.31347 | 2.2551 | -6.0714 | 0.64863 | 6.0108 | -1.568 | 14.2919 | 0 | 38.3333 | 38.3333 | 60.858 | 1
212 | 7 | 12 | 120 |  | 0.31347 | 2.2551 | -6.0714 | 0.64863 | 7.0108 | -1.3062 | 23.3329 | 4.1816 | 100 | 104.1816 | 165.3987 | 1
212 | 8 | 150 | 205 |  | 0.31347 | 2.2551 | -6.0714 | 0.64863 | 8.0108 | -1.0444 | 32.3441 | 83.9857 | 170.8333 | 254.819 | 404.5506 | 1
212 | 9 | 67 | 261 |  | 0.31347 | 2.2551 | -6.0714 | 0.64863 | 9.0108 | -0.78257 | 40.858 | 49.6663 | 217.5 | 267.1663 | 424.1533 | 1
212 | 10 | 202 | 339 |  | 0.31347 | 2.2551 | -6.0714 | 0.64863 | 10.0108 | -0.52077 | 48.2021 | 177.8121 | 282.5 | 460.3121 | 730.7915 | 1
212 | 11 | 99 | 348 |  | 0.31347 | 2.2551 | -6.0714 | 0.64863 | 11.0108 | -0.25897 | 53.3907 | 95.7669 | 290 | 385.7669 | 612.4435 | 1
212 | 12 | 271 | 358 |  | 0.31347 | 2.2551 | -6.0714 | 0.64863 | 12.0108 | 0.0028302 | 55.2804 | 270.0803 | 298.3333 | 568.4136 | 902.4134 | 1
212 | 13 | 237 | 387 |  | 0.31347 | 2.2551 | -6.0714 | 0.64863 | 13.0108 | 0.26463 | 53.3096 | 228.9553 | 322.5 | 551.4553 | 875.4904 | 1
212 | 14 | 99 | 348 |  | 0.31347 | 2.2551 | -6.0714 | 0.64863 | 14.0108 | 0.52643 | 48.0619 | 86.8996 | 290 | 376.8996 | 598.3658 | 1
212 | 15 | 70 | 324 |  | 0.31347 | 2.2551 | -6.0714 | 0.64863 | 15.0108 | 0.78823 | 40.6834 | 51.6443 | 270 | 321.6443 | 510.6425 | 1
212 | 16 | 184 | 276 |  | 0.31347 | 2.2551 | -6.0714 | 0.64863 | 16.0108 | 1.05 | 32.1526 | 102.2308 | 230 | 332.2308 | 527.4496 | 1
212 | 17 | 361 | 180 |  | 0.31347 | 2.2551 | -6.0714 | 0.64863 | 17.0108 | 1.3118 | 23.1363 | 124.0641 | 150 | 274.0641 | 435.1041 | 1
212 | 18 | 109 | 123 |  | 0.31347 | 2.2551 | -6.0714 | 0.64863 | 18.0108 | 1.5736 | 14.099 | 12.6894 | 102.5 | 115.1894 | 182.8746 | 1
212 | 19 | 1 | 58 |  | 0.31347 | 2.2551 | -6.0714 | 0.64863 | 19.0108 | 1.8354 | 5.4161 | 0 | 48.3333 | 48.3333 | 76.734 | 0
212 | 20 | 0 | 6 |  | 0.31347 | 2.2551 | -6.0714 | 0.64863 | 20.0108 | 2.0972 | -2.553 | 0 | 5 | 5 | 7.938 | 0
212 | 21 | 0 | 0 |  | 0.31347 | 2.2551 | -6.0714 | 0.64863 | 21.0108 | 2.359 | -9.4232 | 0 | 0 | 0 | 0 | 0
212 | 22 | 0 | 0 |  | 0.31347 | 2.2551 | -6.0714 | 0.64863 | 22.0108 | 2.6208 | -14.7759 | 0 | 0 | 0 | 0 | 0
212 | 23 | 0 | 0 |  | 0.31347 | 2.2551 | -6.0714 | 0.64863 | 23.0108 | 2.8826 | -18.1955 | 0 | 0 | 0 | 0 | 0
212 | 24 | 0 | 0 |  | 0.31347 | 2.2551 | -6.0714 | 0.64863 | 24.0108 | 3.1444 | -19.3592 | 0 | 0 | 0 | 0 | 0
213 | 1 | 0 | 0 |  | 0.30888 | 2.2723 | -6.0177 | 0.70233 | 1.0117 | -2.8767 | -18.4021 | 0 | 0 | 0 | 0 | 0
213 | 2 | 0 | 0 |  | 0.30888 | 2.2723 | -6.0177 | 0.70233 | 2.0117 | -2.6149 | -14.9251 | 0 | 0 | 0 | 0 | 0
213 | 3 | 0 | 0 |  | 0.30888 | 2.2723 | -6.0177 | 0.70233 | 3.0117 | -2.3531 | -9.5207 | 0 | 0 | 0 | 0 | 0
213 | 4 | 0 | 0 |  | 0.30888 | 2.2723 | -6.0177 | 0.70233 | 4.0117 | -2.0913 | -2.608 | 0 | 0 | 0 | 0 | 0
213 | 5 | 0 | 8 |  | 0.30888 | 2.2723 | -6.0177 | 0.70233 | 5.0117 | -1.8295 | 5.3922 | 0 | 6.6667 | 6.6667 | 10.584 | 0
213 | 6 | 63 | 61 |  | 0.30888 | 2.2723 | -6.0177 | 0.70233 | 6.0117 | -1.5677 | 14.0944 | 7.5541 | 50.8333 | 58.3875 | 92.6959 | 1
213 | 7 | 240 | 119 |  | 0.30888 | 2.2723 | -6.0177 | 0.70233 | 7.0117 | -1.3059 | 23.138 | 83.3563 | 99.1667 | 182.523 | 289.7735 | 1
213 | 8 | 61 | 182 |  | 0.30888 | 2.2723 | -6.0177 | 0.70233 | 8.0117 | -1.0441 | 32.1454 | 34.1019 | 151.6667 | 185.7686 | 294.9262 | 1
213 | 9 | 5 | 183 |  | 0.30888 | 2.2723 | -6.0177 | 0.70233 | 9.0117 | -0.78233 | 40.6478 | 3.7033 | 152.5 | 156.2033 | 247.9884 | 1
213 | 10 | 6 | 227 |  | 0.30888 | 2.2723 | -6.0177 | 0.70233 | 10.0117 | -0.52053 | 47.9728 | 5.2788 | 189.1667 | 194.4455 | 308.7016 | 1
213 | 11 | 16 | 252 |  | 0.30888 | 2.2723 | -6.0177 | 0.70233 | 11.0117 | -0.25873 | 53.1397 | 15.4714 | 210 | 225.4714 | 357.9584 | 1
213 | 12 | 17 | 267 |  | 0.30888 | 2.2723 | -6.0177 | 0.70233 | 12.0117 | 0.0030645 | 55.017 | 16.9357 | 222.5 | 239.4357 | 380.1281 | 1
213 | 13 | 104 | 363 |  | 0.30888 | 2.2723 | -6.0177 | 0.70233 | 13.0117 | 0.26486 | 53.0523 | 100.4191 | 302.5 | 402.9191 | 639.6744 | 1
213 | 14 | 550 | 257 |  | 0.30888 | 2.2723 | -6.0177 | 0.70233 | 14.0117 | 0.52666 | 47.8216 | 482.4082 | 214.1667 | 696.5749 | 1105.8823 | 1
213 | 15 | 390 | 275 |  | 0.30888 | 2.2723 | -6.0177 | 0.70233 | 15.0117 | 0.78846 | 40.459 | 287.3746 | 229.1667 | 516.5412 | 820.0609 | 1
213 | 16 | 365 | 223 |  | 0.30888 | 2.2723 | -6.0177 | 0.70233 | 16.0117 | 1.0503 | 31.9382 | 202.3495 | 185.8333 | 388.1828 | 616.279 | 1
213 | 17 | 431 | 141 |  | 0.30888 | 2.2723 | -6.0177 | 0.70233 | 17.0117 | 1.3121 | 22.9251 | 147.4512 | 117.5 | 264.9512 | 420.6365 | 1
213 | 18 | 160 | 128 |  | 0.30888 | 2.2723 | -6.0177 | 0.70233 | 18.0117 | 1.5739 | 13.8854 | 18.3231 | 106.6667 | 124.9898 | 198.4338 | 1
213 | 19 | 50 | 66 |  | 0.30888 | 2.2723 | -6.0177 | 0.70233 | 19.0117 | 1.8357 | 5.1955 | 0 | 55 | 55 | 87.318 | 0
213 | 20 | 0 | 9 |  | 0.30888 | 2.2723 | -6.0177 | 0.70233 | 20.0117 | 2.0975 | -2.7839 | 0 | 7.5 | 7.5 | 11.907 | 0
213 | 21 | 0 | 0 |  | 0.30888 | 2.2723 | -6.0177 | 0.70233 | 21.0117 | 2.3593 | -9.6661 | 0 | 0 | 0 | 0 | 0
213 | 22 | 0 | 0 |  | 0.30888 | 2.2723 | -6.0177 | 0.70233 | 22.0117 | 2.6211 | -15.0301 | 0 | 0 | 0 | 0 | 0
213 | 23 | 0 | 0 |  | 0.30888 | 2.2723 | -6.0177 | 0.70233 | 23.0117 | 2.8829 | -18.4574 | 0 | 0 | 0 | 0 | 0
213 | 24 | 0 | 0 |  | 0.30888 | 2.2723 | -6.0177 | 0.70233 | 24.0117 | 3.1447 | -19.6225 | 0 | 0 | 0 | 0 | 0
214 | 1 | 0 | 0 |  | 0.30419 | 2.2895 | -5.9535 | 0.76647 | 1.0128 | -2.8764 | -18.6641 | 0 | 0 | 0 | 0 | 0
214 | 2 | 0 | 0 |  | 0.30419 | 2.2895 | -5.9535 | 0.76647 | 2.0128 | -2.6146 | -15.175 | 0 | 0 | 0 | 0 | 0
214 | 3 | 0 | 0 |  | 0.30419 | 2.2895 | -5.9535 | 0.76647 | 3.0128 | -2.3529 | -9.7555 | 0 | 0 | 0 | 0 | 0
214 | 4 | 0 | 0 |  | 0.30419 | 2.2895 | -5.9535 | 0.76647 | 4.0128 | -2.0911 | -2.8281 | 0 | 0 | 0 | 0 | 0
214 | 5 | 0 | 9 |  | 0.30419 | 2.2895 | -5.9535 | 0.76647 | 5.0128 | -1.8293 | 5.1843 | 0 | 7.5 | 7.5 | 11.907 | 0
214 | 6 | 94 | 60 |  | 0.30419 | 2.2895 | -5.9535 | 0.76647 | 6.0128 | -1.5675 | 13.8944 | 11.1329 | 50 | 61.1329 | 97.0546 | 1
214 | 7 | 302 | 116 |  | 0.30419 | 2.2895 | -5.9535 | 0.76647 | 7.0128 | -1.3057 | 22.9406 | 104.5449 | 96.6667 | 201.2116 | 319.4435 | 1
214 | 8 | 471 | 155 |  | 0.30419 | 2.2895 | -5.9535 | 0.76647 | 8.0128 | -1.0439 | 31.9439 | 262.9096 | 129.1667 | 392.0762 | 622.4602 | 1
214 | 9 | 488 | 196 |  | 0.30419 | 2.2895 | -5.9535 | 0.76647 | 9.0128 | -0.78205 | 40.4345 | 361.1415 | 163.3333 | 524.4748 | 832.6563 | 1
214 | 10 | 201 | 336 |  | 0.30419 | 2.2895 | -5.9535 | 0.76647 | 10.0128 | -0.52025 | 47.7399 | 176.7456 | 280 | 456.7456 | 725.1294 | 1
214 | 11 | 234 | 361 |  | 0.30419 | 2.2895 | -5.9535 | 0.76647 | 11.0128 | -0.25846 | 52.8843 | 226.1761 | 300.8333 | 527.0094 | 836.6802 | 1
214 | 12 | 237 | 384 |  | 0.30419 | 2.2895 | -5.9535 | 0.76647 | 12.0128 | 0.0033443 | 54.7486 | 236.0042 | 320 | 556.0042 | 882.7123 | 1
214 | 13 | 233 | 385 |  | 0.30419 | 2.2895 | -5.9535 | 0.76647 | 13.0128 | 0.26514 | 52.7893 | 224.8545 | 320.8333 | 545.6878 | 866.3339 | 1
214 | 14 | 232 | 361 |  | 0.30419 | 2.2895 | -5.9535 | 0.76647 | 14.0128 | 0.52694 | 47.5754 | 203.3219 | 300.8333 | 504.1552 | 800.3968 | 1
214 | 15 | 185 | 343 |  | 0.30419 | 2.2895 | -5.9535 | 0.76647 | 15.0128 | 0.78874 | 40.2288 | 136.1379 | 285.8333 | 421.9712 | 669.9215 | 1
214 | 16 | 65 | 257 |  | 0.30419 | 2.2895 | -5.9535 | 0.76647 | 16.0128 | 1.0505 | 31.7179 | 35.9512 | 214.1667 | 250.1178 | 397.0871 | 1
214 | 17 | 144 | 201 |  | 0.30419 | 2.2895 | -5.9535 | 0.76647 | 17.0128 | 1.3123 | 22.7082 | 49.0302 | 167.5 | 216.5302 | 343.7634 | 1
214 | 18 | 77 | 127 |  | 0.30419 | 2.2895 | -5.9535 | 0.76647 | 18.0128 | 1.5741 | 13.6662 | 8.6661 | 105.8333 | 114.4995 | 181.7793 | 1
214 | 19 | 15 | 60 |  | 0.30419 | 2.2895 | -5.9535 | 0.76647 | 19.0128 | 1.8359 | 4.9693 | 0 | 50 | 50 | 79.38 | 0
214 | 20 | 0 | 5 |  | 0.30419 | 2.2895 | -5.9535 | 0.76647 | 20.0128 | 2.0977 | -3.0203 | 0 | 4.1667 | 4.1667 | 6.615 | 0
214 | 21 | 0 | 0 |  | 0.30419 | 2.2895 | -5.9535 | 0.76647 | 21.0128 | 2.3595 | -9.9146 | 0 | 0 | 0 | 0 | 0
214 | 22 | 0 | 0 |  | 0.30419 | 2.2895 | -5.9535 | 0.76647 | 22.0128 | 2.6213 | -15.2898 | 0 | 0 | 0 | 0 | 0
214 | 23 | 0 | 0 |  | 0.30419 | 2.2895 | -5.9535 | 0.76647 | 23.0128 | 2.8831 | -18.7247 | 0 | 0 | 0 | 0 | 0
214 | 24 | 0 | 0 |  | 0.30419 | 2.2895 | -5.9535 | 0.76647 | 24.0128 | 3.1449 | -19.8909 | 0 | 0 | 0 | 0 | 0
215 | 1 | 0 | 0 |  | 0.29942 | 2.3067 | -5.8789 | 0.84107 | 1.014 | -2.8761 | -18.9305 | 0 | 0 | 0 | 0 | 0
215 | 2 | 0 | 0 |  | 0.29942 | 2.3067 | -5.8789 | 0.84107 | 2.014 | -2.6143 | -15.4286 | 0 | 0 | 0 | 0 | 0
215 | 3 | 0 | 0 |  | 0.29942 | 2.3067 | -5.8789 | 0.84107 | 3.014 | -2.3525 | -9.9936 | 0 | 0 | 0 | 0 | 0
215 | 4 | 0 | 0 |  | 0.29942 | 2.3067 | -5.8789 | 0.84107 | 4.014 | -2.0907 | -3.051 | 0 | 0 | 0 | 0 | 0
215 | 5 | 0 | 5 |  | 0.29942 | 2.3067 | -5.8789 | 0.84107 | 5.014 | -1.8289 | 4.9738 | 0 | 4.1667 | 4.1667 | 6.615 | 0
215 | 6 | 0 | 41 |  | 0.29942 | 2.3067 | -5.8789 | 0.84107 | 6.014 | -1.5671 | 13.692 | 0 | 34.1667 | 34.1667 | 54.243 | 1
215 | 7 | 16 | 112 |  | 0.29942 | 2.3067 | -5.8789 | 0.84107 | 7.014 | -1.3053 | 22.7407 | 5.5206 | 93.3333 | 98.854 | 156.9405 | 1
215 | 8 | 174 | 275 |  | 0.29942 | 2.3067 | -5.8789 | 0.84107 | 8.014 | -1.0435 | 31.7398 | 96.9779 | 229.1667 | 326.1446 | 517.7871 | 1
215 | 9 | 606 | 145 |  | 0.29942 | 2.3067 | -5.8789 | 0.84107 | 9.014 | -0.78173 | 40.2181 | 448.0875 | 120.8333 | 568.9208 | 903.2187 | 1
215 | 10 | 363 | 290 |  | 0.29942 | 2.3067 | -5.8789 | 0.84107 | 10.014 | -0.51993 | 47.5034 | 319.0237 | 241.6667 | 560.6904 | 890.152 | 1
215 | 11 | 251 | 341 |  | 0.29942 | 2.3067 | -5.8789 | 0.84107 | 11.014 | -0.25813 | 52.6247 | 242.5028 | 284.1667 | 526.6694 | 836.1404 | 1
215 | 12 | 157 | 443 |  | 0.29942 | 2.3067 | -5.8789 | 0.84107 | 12.014 | 0.0036698 | 54.4753 | 156.2699 | 369.1667 | 525.4365 | 834.183 | 1
215 | 13 | 156 | 443 |  | 0.29942 | 2.3067 | -5.8789 | 0.84107 | 13.014 | 0.26547 | 52.5209 | 150.4576 | 369.1667 | 519.6243 | 824.9555 | 1
215 | 14 | 695 | 200 |  | 0.29942 | 2.3067 | -5.8789 | 0.84107 | 14.014 | 0.52727 | 47.3234 | 608.5544 | 166.6667 | 775.221 | 1230.7409 | 1
215 | 15 | 741 | 128 |  | 0.29942 | 2.3067 | -5.8789 | 0.84107 | 15.014 | 0.78907 | 39.9928 | 544.5185 | 106.6667 | 651.1852 | 1033.8216 | 1
215 | 16 | 606 | 145 |  | 0.29942 | 2.3067 | -5.8789 | 0.84107 | 16.014 | 1.0509 | 31.492 | 334.3546 | 120.8333 | 455.188 | 722.6564 | 1
215 | 17 | 489 | 129 |  | 0.29942 | 2.3067 | -5.8789 | 0.84107 | 17.014 | 1.3127 | 22.4858 | 165.6676 | 107.5 | 273.1676 | 433.6808 | 1
215 | 18 | 323 | 103 |  | 0.29942 | 2.3067 | -5.8789 | 0.84107 | 18.014 | 1.5745 | 13.4414 | 35.6914 | 85.8333 | 121.5247 | 192.9326 | 1
215 | 19 | 20 | 57 |  | 0.29942 | 2.3067 | -5.8789 | 0.84107 | 19.014 | 1.8363 | 4.7376 | 0 | 47.5 | 47.5 | 75.411 | 0
215 | 20 | 0 | 8 |  | 0.29942 | 2.3067 | -5.8789 | 0.84107 | 20.014 | 2.0981 | -3.2623 | 0 | 6.6667 | 6.6667 | 10.584 | 0
215 | 21 | 0 | 0 |  | 0.29942 | 2.3067 | -5.8789 | 0.84107 | 21.014 | 2.3599 | -10.1685 | 0 | 0 | 0 | 0 | 0
215 | 22 | 0 | 0 |  | 0.29942 | 2.3067 | -5.8789 | 0.84107 | 22.014 | 2.6217 | -15.555 | 0 | 0 | 0 | 0 | 0
215 | 23 | 0 | 0 |  | 0.29942 | 2.3067 | -5.8789 | 0.84107 | 23.014 | 2.8835 | -18.9972 | 0 | 0 | 0 | 0 | 0
215 | 24 | 0 | 0 |  | 0.29942 | 2.3067 | -5.8789 | 0.84107 | 24.014 | 3.1453 | -20.1641 | 0 | 0 | 0 | 0 | 0
216 | 1 | 0 | 0 |  | 0.29457 | 2.3239 | -5.7939 | 0.92613 | 1.0154 | -2.8758 | -19.2013 | 0 | 0 | 0 | 0 | 0
216 | 2 | 0 | 0 |  | 0.29457 | 2.3239 | -5.7939 | 0.92613 | 2.0154 | -2.614 | -15.686 | 0 | 0 | 0 | 0 | 0
216 | 3 | 0 | 0 |  | 0.29457 | 2.3239 | -5.7939 | 0.92613 | 3.0154 | -2.3522 | -10.2348 | 0 | 0 | 0 | 0 | 0
216 | 4 | 0 | 0 |  | 0.29457 | 2.3239 | -5.7939 | 0.92613 | 4.0154 | -2.0904 | -3.2767 | 0 | 0 | 0 | 0 | 0
216 | 5 | 0 | 4 |  | 0.29457 | 2.3239 | -5.7939 | 0.92613 | 5.0154 | -1.8286 | 4.7608 | 0 | 3.3333 | 3.3333 | 5.292 | 0
216 | 6 | 0 | 40 |  | 0.29457 | 2.3239 | -5.7939 | 0.92613 | 6.0154 | -1.5668 | 13.4873 | 0 | 33.3333 | 33.3333 | 52.92 | 1
216 | 7 | 16 | 110 |  | 0.29457 | 2.3239 | -5.7939 | 0.92613 | 7.0154 | -1.305 | 22.5385 | 5.5025 | 91.6667 | 97.1692 | 154.2658 | 1
216 | 8 | 55 | 180 |  | 0.29457 | 2.3239 | -5.7939 | 0.92613 | 8.0154 | -1.0432 | 31.533 | 30.6073 | 150 | 180.6073 | 286.7322 | 1
216 | 9 | 39 | 269 |  | 0.29457 | 2.3239 | -5.7939 | 0.92613 | 9.0154 | -0.78136 | 39.9987 | 28.8128 | 224.1667 | 252.9795 | 401.6302 | 1
216 | 10 | 42 | 334 |  | 0.29457 | 2.3239 | -5.7939 | 0.92613 | 10.0154 | -0.51956 | 47.2634 | 36.8913 | 278.3333 | 315.2246 | 500.4506 | 1
216 | 11 | 56 | 371 |  | 0.29457 | 2.3239 | -5.7939 | 0.92613 | 11.0154 | -0.25776 | 52.3608 | 54.0796 | 309.1667 | 363.2463 | 576.6898 | 1
216 | 12 | 23 | 259 |  | 0.29457 | 2.3239 | -5.7939 | 0.92613 | 12.0154 | 0.004041 | 54.197 | 22.882 | 215.8333 | 238.7153 | 378.9844 | 1
216 | 13 | 17 | 264 |  | 0.29457 | 2.3239 | -5.7939 | 0.92613 | 13.0154 | 0.26584 | 52.2471 | 16.3856 | 220 | 236.3856 | 375.2858 | 1
216 | 14 | 102 | 336 |  | 0.29457 | 2.3239 | -5.7939 | 0.92613 | 14.0154 | 0.52764 | 47.0658 | 89.2292 | 280 | 369.2292 | 586.1882 | 1
216 | 15 | 17 | 215 |  | 0.29457 | 2.3239 | -5.7939 | 0.92613 | 15.0154 | 0.78944 | 39.7511 | 12.4736 | 179.1667 | 191.6403 | 304.2482 | 1
216 | 16 | 3 | 180 |  | 0.29457 | 2.3239 | -5.7939 | 0.92613 | 16.0154 | 1.0512 | 31.2605 | 1.651 | 150 | 151.651 | 240.7611 | 1
216 | 17 | 0 | 128 |  | 0.29457 | 2.3239 | -5.7939 | 0.92613 | 17.0154 | 1.313 | 22.2578 | 0 | 106.6667 | 106.6667 | 169.344 | 1
216 | 18 | 0 | 94 |  | 0.29457 | 2.3239 | -5.7939 | 0.92613 | 18.0154 | 1.5748 | 13.2112 | 0 | 78.3333 | 78.3333 | 124.362 | 1
216 | 19 | 0 | 39 |  | 0.29457 | 2.3239 | -5.7939 | 0.92613 | 19.0154 | 1.8366 | 4.5005 | 0 | 32.5 | 32.5 | 51.597 | 0
216 | 20 | 0 | 4 |  | 0.29457 | 2.3239 | -5.7939 | 0.92613 | 20.0154 | 2.0984 | -3.5098 | 0 | 3.3333 | 3.3333 | 5.292 | 0
216 | 21 | 0 | 0 |  | 0.29457 | 2.3239 | -5.7939 | 0.92613 | 21.0154 | 2.3602 | -10.4279 | 0 | 0 | 0 | 0 | 0
216 | 22 | 0 | 0 |  | 0.29457 | 2.3239 | -5.7939 | 0.92613 | 22.0154 | 2.622 | -15.8256 | 0 | 0 | 0 | 0 | 0
216 | 23 | 0 | 0 |  | 0.29457 | 2.3239 | -5.7939 | 0.92613 | 23.0154 | 2.8838 | -19.2749 | 0 | 0 | 0 | 0 | 0
216 | 24 | 0 | 0 |  | 0.29457 | 2.3239 | -5.7939 | 0.92613 | 24.0154 | 3.1456 | -20.4422 | 0 | 0 | 0 | 0 | 0
217 | 1 | 0 | 0 |  | 0.28963 | 2.3411 | -5.6983 | 1.0217 | 1.017 | -2.8753 | -19.4762 | 0 | 0 | 0 | 0 | 0
217 | 2 | 0 | 0 |  | 0.28963 | 2.3411 | -5.6983 | 1.0217 | 2.017 | -2.6135 | -15.947 | 0 | 0 | 0 | 0 | 0
217 | 3 | 0 | 0 |  | 0.28963 | 2.3411 | -5.6983 | 1.0217 | 3.017 | -2.3517 | -10.4792 | 0 | 0 | 0 | 0 | 0
217 | 4 | 0 | 0 |  | 0.28963 | 2.3411 | -5.6983 | 1.0217 | 4.017 | -2.0899 | -3.505 | 0 | 0 | 0 | 0 | 0
217 | 5 | 0 | 4 |  | 0.28963 | 2.3411 | -5.6983 | 1.0217 | 5.017 | -1.8281 | 4.5455 | 0 | 3.3333 | 3.3333 | 5.292 | 0
217 | 6 | 0 | 49 |  | 0.28963 | 2.3411 | -5.6983 | 1.0217 | 6.017 | -1.5663 | 13.2803 | 0 | 40.8333 | 40.8333 | 64.827 | 1
217 | 7 | 4 | 112 |  | 0.28963 | 2.3411 | -5.6983 | 1.0217 | 7.017 | -1.3045 | 22.3339 | 1.3711 | 93.3333 | 94.7045 | 150.3528 | 1
217 | 8 | 171 | 271 |  | 0.28963 | 2.3411 | -5.6983 | 1.0217 | 8.017 | -1.0427 | 31.3237 | 95.0167 | 225.8333 | 320.85 | 509.3815 | 1
217 | 9 | 484 | 188 |  | 0.28963 | 2.3411 | -5.6983 | 1.0217 | 9.017 | -0.78094 | 39.7763 | 357.2682 | 156.6667 | 513.9349 | 815.923 | 1
217 | 10 | 80 | 307 |  | 0.28963 | 2.3411 | -5.6983 | 1.0217 | 10.017 | -0.51914 | 47.0198 | 70.229 | 255.8333 | 326.0623 | 517.6565 | 1
217 | 11 | 57 | 370 |  | 0.28963 | 2.3411 | -5.6983 | 1.0217 | 11.017 | -0.25734 | 52.0929 | 55.0191 | 308.3333 | 363.3524 | 576.8583 | 1
217 | 12 | 58 | 395 |  | 0.28963 | 2.3411 | -5.6983 | 1.0217 | 12.017 | 0.0044579 | 53.9141 | 57.6727 | 329.1667 | 386.8393 | 614.1461 | 1
217 | 13 | 509 | 349 |  | 0.28963 | 2.3411 | -5.6983 | 1.0217 | 13.017 | 0.26626 | 51.968 | 490.2721 | 290.8333 | 781.1054 | 1240.083 | 1
217 | 14 | 155 | 297 |  | 0.28963 | 2.3411 | -5.6983 | 1.0217 | 14.017 | 0.52806 | 46.8025 | 135.4577 | 247.5 | 382.9577 | 607.9836 | 1
217 | 15 | 195 | 331 |  | 0.28963 | 2.3411 | -5.6983 | 1.0217 | 15.017 | 0.78986 | 39.5038 | 142.8536 | 275.8333 | 418.687 | 664.7074 | 1
217 | 16 | 522 | 211 |  | 0.28963 | 2.3411 | -5.6983 | 1.0217 | 16.017 | 1.0517 | 31.0233 | 286.4869 | 175.8333 | 462.3202 | 733.9796 | 1
217 | 17 | 508 | 130 |  | 0.28963 | 2.3411 | -5.6983 | 1.0217 | 17.017 | 1.3135 | 22.0243 | 170.267 | 108.3333 | 278.6004 | 442.3059 | 1
217 | 18 | 285 | 113 |  | 0.28963 | 2.3411 | -5.6983 | 1.0217 | 18.017 | 1.5753 | 12.9756 | 30.2614 | 94.1667 | 124.4281 | 197.542 | 1
217 | 19 | 73 | 55 |  | 0.28963 | 2.3411 | -5.6983 | 1.0217 | 19.017 | 1.8371 | 4.258 | 0 | 45.8333 | 45.8333 | 72.765 | 0
217 | 20 | 0 | 7 |  | 0.28963 | 2.3411 | -5.6983 | 1.0217 | 20.017 | 2.0989 | -3.7626 | 0 | 5.8333 | 5.8333 | 9.261 | 0
217 | 21 | 0 | 0 |  | 0.28963 | 2.3411 | -5.6983 | 1.0217 | 21.017 | 2.3607 | -10.6927 | 0 | 0 | 0 | 0 | 0
217 | 22 | 0 | 0 |  | 0.28963 | 2.3411 | -5.6983 | 1.0217 | 22.017 | 2.6225 | -16.1014 | 0 | 0 | 0 | 0 | 0
217 | 23 | 0 | 0 |  | 0.28963 | 2.3411 | -5.6983 | 1.0217 | 23.017 | 2.8843 | -19.5577 | 0 | 0 | 0 | 0 | 0
217 | 24 | 0 | 0 |  | 0.28963 | 2.3411 | -5.6983 | 1.0217 | 24.017 | 3.1461 | -20.725 | 0 | 0 | 0 | 0 | 0
218 | 1 | 0 | 0 |  | 0.28461 | 2.3583 | -5.5923 | 1.1277 | 1.0188 | -2.8749 | -19.7553 | 0 | 0 | 0 | 0 | 0
218 | 2 | 0 | 0 |  | 0.28461 | 2.3583 | -5.5923 | 1.1277 | 2.0188 | -2.6131 | -16.2115 | 0 | 0 | 0 | 0 | 0
218 | 3 | 0 | 0 |  | 0.28461 | 2.3583 | -5.5923 | 1.1277 | 3.0188 | -2.3513 | -10.7265 | 0 | 0 | 0 | 0 | 0
218 | 4 | 0 | 0 |  | 0.28461 | 2.3583 | -5.5923 | 1.1277 | 4.0188 | -2.0895 | -3.7358 | 0 | 0 | 0 | 0 | 0
218 | 5 | 0 | 4 |  | 0.28461 | 2.3583 | -5.5923 | 1.1277 | 5.0188 | -1.8277 | 4.3279 | 0 | 3.3333 | 3.3333 | 5.292 | 0
218 | 6 | 0 | 37 |  | 0.28461 | 2.3583 | -5.5923 | 1.1277 | 6.0188 | -1.5659 | 13.0712 | 0 | 30.8333 | 30.8333 | 48.951 | 1
218 | 7 | 6 | 110 |  | 0.28461 | 2.3583 | -5.5923 | 1.1277 | 7.0188 | -1.3041 | 22.1271 | 2.05 | 91.6667 | 93.7167 | 148.7846 | 1
218 | 8 | 24 | 191 |  | 0.28461 | 2.3583 | -5.5923 | 1.1277 | 8.0188 | -1.0423 | 31.112 | 13.3155 | 159.1667 | 172.4821 | 273.8327 | 1
218 | 9 | 190 | 259 |  | 0.28461 | 2.3583 | -5.5923 | 1.1277 | 9.0188 | -0.78048 | 39.5511 | 140.129 | 215.8333 | 355.9624 | 565.1259 | 1
218 | 10 | 77 | 308 |  | 0.28461 | 2.3583 | -5.5923 | 1.1277 | 10.0188 | -0.51868 | 46.7728 | 67.5558 | 256.6667 | 324.2225 | 514.7356 | 1
218 | 11 | 57 | 369 |  | 0.28461 | 2.3583 | -5.5923 | 1.1277 | 11.0188 | -0.25688 | 51.8209 | 54.9915 | 307.5 | 362.4915 | 575.4915 | 1
218 | 12 | 58 | 393 |  | 0.28461 | 2.3583 | -5.5923 | 1.1277 | 12.0188 | 0.0049204 | 53.6264 | 57.641 | 327.5 | 385.141 | 611.4498 | 1
218 | 13 | 256 | 358 |  | 0.28461 | 2.3583 | -5.5923 | 1.1277 | 13.0188 | 0.26672 | 51.6837 | 246.402 | 298.3333 | 544.7354 | 864.8219 | 1
218 | 14 | 155 | 411 |  | 0.28461 | 2.3583 | -5.5923 | 1.1277 | 14.0188 | 0.52852 | 46.5338 | 135.3136 | 342.5 | 477.8136 | 758.5769 | 1
218 | 15 | 117 | 382 |  | 0.28461 | 2.3583 | -5.5923 | 1.1277 | 15.0188 | 0.79032 | 39.2509 | 85.569 | 318.3333 | 403.9024 | 641.2354 | 1
218 | 16 | 127 | 295 |  | 0.28461 | 2.3583 | -5.5923 | 1.1277 | 16.0188 | 1.0521 | 30.7807 | 69.5026 | 245.8333 | 315.336 | 500.6274 | 1
218 | 17 | 337 | 175 |  | 0.28461 | 2.3583 | -5.5923 | 1.1277 | 17.0188 | 1.3139 | 21.7854 | 112.3063 | 145.8333 | 258.1397 | 409.8226 | 1
218 | 18 | 11 | 107 |  | 0.28461 | 2.3583 | -5.5923 | 1.1277 | 18.0188 | 1.5757 | 12.7346 | 1.143 | 89.1667 | 90.3097 | 143.3756 | 1
218 | 19 | 8 | 52 |  | 0.28461 | 2.3583 | -5.5923 | 1.1277 | 19.0188 | 1.8375 | 4.0102 | 0 | 43.3333 | 43.3333 | 68.796 | 0
218 | 20 | 0 | 5 |  | 0.28461 | 2.3583 | -5.5923 | 1.1277 | 20.0188 | 2.0993 | -4.0206 | 0 | 4.1667 | 4.1667 | 6.615 | 0
218 | 21 | 0 | 0 |  | 0.28461 | 2.3583 | -5.5923 | 1.1277 | 21.0188 | 2.3611 | -10.9627 | 0 | 0 | 0 | 0 | 0
218 | 22 | 0 | 0 |  | 0.28461 | 2.3583 | -5.5923 | 1.1277 | 22.0188 | 2.6229 | -16.3824 | 0 | 0 | 0 | 0 | 0
218 | 23 | 0 | 0 |  | 0.28461 | 2.3583 | -5.5923 | 1.1277 | 23.0188 | 2.8847 | -19.8455 | 0 | 0 | 0 | 0 | 0
218 | 24 | 0 | 0 |  | 0.28461 | 2.3583 | -5.5923 | 1.1277 | 24.0188 | 3.1465 | -21.0124 | 0 | 0 | 0 | 0 | 0
219 | 1 | 0 | 0 |  | 0.27952 | 2.3756 | -5.4759 | 1.2441 | 1.0207 | -2.8744 | -20.0383 | 0 | 0 | 0 | 0 | 0
219 | 2 | 0 | 0 |  | 0.27952 | 2.3756 | -5.4759 | 1.2441 | 2.0207 | -2.6126 | -16.4794 | 0 | 0 | 0 | 0 | 0
219 | 3 | 0 | 0 |  | 0.27952 | 2.3756 | -5.4759 | 1.2441 | 3.0207 | -2.3508 | -10.9766 | 0 | 0 | 0 | 0 | 0
219 | 4 | 0 | 0 |  | 0.27952 | 2.3756 | -5.4759 | 1.2441 | 4.0207 | -2.089 | -3.9691 | 0 | 0 | 0 | 0 | 0
219 | 5 | 0 | 4 |  | 0.27952 | 2.3756 | -5.4759 | 1.2441 | 5.0207 | -1.8272 | 4.1082 | 0 | 3.3333 | 3.3333 | 5.292 | 0
219 | 6 | 0 | 36 |  | 0.27952 | 2.3756 | -5.4759 | 1.2441 | 6.0207 | -1.5654 | 12.8599 | 0 | 30 | 30 | 47.628 | 1
219 | 7 | 6 | 109 |  | 0.27952 | 2.3756 | -5.4759 | 1.2441 | 7.0207 | -1.3036 | 21.9181 | 2.0434 | 90.8333 | 92.8767 | 147.4511 | 1
219 | 8 | 24 | 190 |  | 0.27952 | 2.3756 | -5.4759 | 1.2441 | 8.0207 | -1.0418 | 30.8978 | 13.2954 | 158.3333 | 171.6287 | 272.4777 | 1
219 | 9 | 61 | 253 |  | 0.27952 | 2.3756 | -5.4759 | 1.2441 | 9.0207 | -0.77997 | 39.3231 | 44.9497 | 210.8333 | 255.7831 | 406.0812 | 1
219 | 10 | 69 | 314 |  | 0.27952 | 2.3756 | -5.4759 | 1.2441 | 10.0207 | -0.51817 | 46.5224 | 60.5006 | 261.6667 | 322.1673 | 511.4728 | 1
219 | 11 | 206 | 374 |  | 0.27952 | 2.3756 | -5.4759 | 1.2441 | 11.0207 | -0.25637 | 51.5449 | 198.6368 | 311.6667 | 510.3034 | 810.1577 | 1
219 | 12 | 406 | 332 |  | 0.27952 | 2.3756 | -5.4759 | 1.2441 | 12.0207 | 0.0054284 | 53.3343 | 403.2509 | 276.6667 | 679.9176 | 1079.4371 | 1
219 | 13 | 559 | 270 |  | 0.27952 | 2.3756 | -5.4759 | 1.2441 | 13.0207 | 0.26723 | 51.3943 | 537.6261 | 225 | 762.6261 | 1210.7453 | 1
219 | 14 | 721 | 179 |  | 0.27952 | 2.3756 | -5.4759 | 1.2441 | 14.0207 | 0.52903 | 46.2596 | 628.7166 | 149.1667 | 777.8832 | 1234.9674 | 1
219 | 15 | 511 | 236 |  | 0.27952 | 2.3756 | -5.4759 | 1.2441 | 15.0207 | 0.79083 | 38.9925 | 373.0669 | 196.6667 | 569.7336 | 904.5091 | 1
219 | 16 | 636 | 137 |  | 0.27952 | 2.3756 | -5.4759 | 1.2441 | 16.0207 | 1.0526 | 30.5327 | 347.0236 | 114.1667 | 461.1903 | 732.1857 | 1
219 | 17 | 338 | 173 |  | 0.27952 | 2.3756 | -5.4759 | 1.2441 | 17.0207 | 1.3144 | 21.5412 | 111.9667 | 144.1667 | 256.1333 | 406.6373 | 1
219 | 18 | 280 | 103 |  | 0.27952 | 2.3756 | -5.4759 | 1.2441 | 18.0207 | 1.5762 | 12.4884 | 28.4381 | 85.8333 | 114.2714 | 181.4173 | 0
219 | 19 | 50 | 52 |  | 0.27952 | 2.3756 | -5.4759 | 1.2441 | 19.0207 | 1.838 | 3.7572 | 0 | 43.3333 | 43.3333 | 68.796 | 0
219 | 20 | 0 | 5 |  | 0.27952 | 2.3756 | -5.4759 | 1.2441 | 20.0207 | 2.0998 | -4.2839 | 0 | 4.1667 | 4.1667 | 6.615 | 0
219 | 21 | 0 | 0 |  | 0.27952 | 2.3756 | -5.4759 | 1.2441 | 21.0207 | 2.3616 | -11.2379 | 0 | 0 | 0 | 0 | 0
219 | 22 | 0 | 0 |  | 0.27952 | 2.3756 | -5.4759 | 1.2441 | 22.0207 | 2.6234 | -16.6685 | 0 | 0 | 0 | 0 | 0
219 | 23 | 0 | 0 |  | 0.27952 | 2.3756 | -5.4759 | 1.2441 | 23.0207 | 2.8852 | -20.1382 | 0 | 0 | 0 | 0 | 0
219 | 24 | 0 | 0 |  | 0.27952 | 2.3756 | -5.4759 | 1.2441 | 24.0207 | 3.147 | -21.3044 | 0 | 0 | 0 | 0 | 0
220 | 1 | 0 | 0 |  | 0.27434 | 2.3928 | -5.3491 | 1.3709 | 1.0228 | -2.8738 | -20.3252 | 0 | 0 | 0 | 0 | 0
220 | 2 | 0 | 0 |  | 0.27434 | 2.3928 | -5.3491 | 1.3709 | 2.0228 | -2.612 | -16.7506 | 0 | 0 | 0 | 0 | 0
220 | 3 | 0 | 0 |  | 0.27434 | 2.3928 | -5.3491 | 1.3709 | 3.0228 | -2.3502 | -11.2296 | 0 | 0 | 0 | 0 | 0
220 | 4 | 0 | 0 |  | 0.27434 | 2.3928 | -5.3491 | 1.3709 | 4.0228 | -2.0884 | -4.2048 | 0 | 0 | 0 | 0 | 0
220 | 5 | 0 | 3 |  | 0.27434 | 2.3928 | -5.3491 | 1.3709 | 5.0228 | -1.8266 | 3.8863 | 0 | 2.5 | 2.5 | 3.969 | 0
220 | 6 | 0 | 34 |  | 0.27434 | 2.3928 | -5.3491 | 1.3709 | 6.0228 | -1.5648 | 12.6466 | 0 | 28.3333 | 28.3333 | 44.982 | 1
220 | 7 | 5 | 107 |  | 0.27434 | 2.3928 | -5.3491 | 1.3709 | 7.0228 | -1.303 | 21.7071 | 1.6973 | 89.1667 | 90.864 | 144.2557 | 1
220 | 8 | 24 | 188 |  | 0.27434 | 2.3928 | -5.3491 | 1.3709 | 8.0228 | -1.0412 | 30.6813 | 13.2753 | 156.6667 | 169.942 | 269.7998 | 1
220 | 9 | 61 | 251 |  | 0.27434 | 2.3928 | -5.3491 | 1.3709 | 9.0228 | -0.77942 | 39.0923 | 44.9103 | 209.1667 | 254.077 | 403.3726 | 1
220 | 10 | 69 | 313 |  | 0.27434 | 2.3928 | -5.3491 | 1.3709 | 10.0228 | -0.51762 | 46.2688 | 60.4632 | 260.8333 | 321.2966 | 510.0904 | 1
220 | 11 | 214 | 368 |  | 0.27434 | 2.3928 | -5.3491 | 1.3709 | 11.0228 | -0.25582 | 51.265 | 206.237 | 306.6667 | 512.9036 | 814.2858 | 1
220 | 12 | 236 | 376 |  | 0.27434 | 2.3928 | -5.3491 | 1.3709 | 12.0228 | 0.0059818 | 53.0376 | 234.2565 | 313.3333 | 547.5898 | 869.3536 | 1
220 | 13 | 237 | 375 |  | 0.27434 | 2.3928 | -5.3491 | 1.3709 | 13.0228 | 0.26778 | 51.0999 | 227.7508 | 312.5 | 540.2508 | 857.7022 | 1
220 | 14 | 194 | 380 |  | 0.27434 | 2.3928 | -5.3491 | 1.3709 | 14.0228 | 0.52958 | 45.9802 | 168.9674 | 316.6667 | 485.634 | 770.9926 | 1
220 | 15 | 514 | 265 |  | 0.27434 | 2.3928 | -5.3491 | 1.3709 | 15.0228 | 0.79138 | 38.7287 | 374.5629 | 220.8333 | 595.3962 | 945.251 | 1
220 | 16 | 670 | 123 |  | 0.27434 | 2.3928 | -5.3491 | 1.3709 | 16.0228 | 1.0532 | 30.2793 | 364.4364 | 102.5 | 466.9364 | 741.3082 | 1
220 | 17 | 503 | 127 |  | 0.27434 | 2.3928 | -5.3491 | 1.3709 | 17.0228 | 1.315 | 21.2918 | 165.5869 | 105.8333 | 271.4203 | 430.9068 | 1
220 | 18 | 171 | 108 |  | 0.27434 | 2.3928 | -5.3491 | 1.3709 | 18.0228 | 1.5768 | 12.237 | 16.9541 | 90 | 106.9541 | 169.8004 | 0
220 | 19 | 3 | 49 |  | 0.27434 | 2.3928 | -5.3491 | 1.3709 | 19.0228 | 1.8386 | 3.4991 | 0 | 40.8333 | 40.8333 | 64.827 | 0
220 | 20 | 0 | 4 |  | 0.27434 | 2.3928 | -5.3491 | 1.3709 | 20.0228 | 2.1004 | -4.5523 | 0 | 3.3333 | 3.3333 | 5.292 | 0
220 | 21 | 0 | 0 |  | 0.27434 | 2.3928 | -5.3491 | 1.3709 | 21.0228 | 2.3622 | -11.5181 | 0 | 0 | 0 | 0 | 0
220 | 22 | 0 | 0 |  | 0.27434 | 2.3928 | -5.3491 | 1.3709 | 22.0228 | 2.624 | -16.9596 | 0 | 0 | 0 | 0 | 0
220 | 23 | 0 | 0 |  | 0.27434 | 2.3928 | -5.3491 | 1.3709 | 23.0228 | 2.8858 | -20.4357 | 0 | 0 | 0 | 0 | 0
220 | 24 | 0 | 0 |  | 0.27434 | 2.3928 | -5.3491 | 1.3709 | 24.0228 | 3.1476 | -21.6008 | 0 | 0 | 0 | 0 | 0
221 | 1 | 0 | 0 |  | 0.26909 | 2.41 | -5.2119 | 1.5081 | 1.0251 | -2.8732 | -20.6159 | 0 | 0 | 0 | 0 | 0
221 | 2 | 0 | 0 |  | 0.26909 | 2.41 | -5.2119 | 1.5081 | 2.0251 | -2.6114 | -17.025 | 0 | 0 | 0 | 0 | 0
221 | 3 | 0 | 0 |  | 0.26909 | 2.41 | -5.2119 | 1.5081 | 3.0251 | -2.3496 | -11.4852 | 0 | 0 | 0 | 0 | 0
221 | 4 | 0 | 0 |  | 0.26909 | 2.41 | -5.2119 | 1.5081 | 4.0251 | -2.0878 | -4.4427 | 0 | 0 | 0 | 0 | 0
221 | 5 | 0 | 5 |  | 0.26909 | 2.41 | -5.2119 | 1.5081 | 5.0251 | -1.826 | 3.6623 | 0 | 4.1667 | 4.1667 | 6.615 | 0
221 | 6 | 36 | 50 |  | 0.26909 | 2.41 | -5.2119 | 1.5081 | 6.0251 | -1.5642 | 12.4314 | 3.901 | 41.6667 | 45.5677 | 72.3433 | 0
221 | 7 | 136 | 119 |  | 0.26909 | 2.41 | -5.2119 | 1.5081 | 7.0251 | -1.3024 | 21.4939 | 46.0182 | 99.1667 | 145.1849 | 230.4955 | 1
221 | 8 | 92 | 212 |  | 0.26909 | 2.41 | -5.2119 | 1.5081 | 8.0251 | -1.0406 | 30.4624 | 50.8119 | 176.6667 | 227.4785 | 361.1449 | 1
221 | 9 | 168 | 268 |  | 0.26909 | 2.41 | -5.2119 | 1.5081 | 9.0251 | -0.77882 | 38.8587 | 123.5781 | 223.3333 | 346.9114 | 550.7565 | 1
221 | 10 | 475 | 260 |  | 0.26909 | 2.41 | -5.2119 | 1.5081 | 10.0251 | -0.51702 | 46.0119 | 415.9677 | 216.6667 | 632.6344 | 1004.3704 | 1
221 | 11 | 536 | 263 |  | 0.26909 | 2.41 | -5.2119 | 1.5081 | 11.0251 | -0.25522 | 50.9814 | 516.2571 | 219.1667 | 735.4238 | 1167.5588 | 1
221 | 12 | 657 | 228 |  | 0.26909 | 2.41 | -5.2119 | 1.5081 | 12.0251 | 0.0065802 | 52.7366 | 651.7169 | 190 | 841.7169 | 1336.3097 | 1
221 | 13 | 762 | 164 |  | 0.26909 | 2.41 | -5.2119 | 1.5081 | 13.0251 | 0.26838 | 50.8006 | 731.6241 | 136.6667 | 868.2908 | 1378.4985 | 1
221 | 14 | 743 | 160 |  | 0.26909 | 2.41 | -5.2119 | 1.5081 | 14.0251 | 0.53018 | 45.6955 | 646.3124 | 133.3333 | 779.6458 | 1237.7656 | 1
221 | 15 | 643 | 174 |  | 0.26909 | 2.41 | -5.2119 | 1.5081 | 15.0251 | 0.79198 | 38.4597 | 467.6581 | 145 | 612.6581 | 972.6559 | 1
221 | 16 | 306 | 245 |  | 0.26909 | 2.41 | -5.2119 | 1.5081 | 16.0251 | 1.0538 | 30.0206 | 165.9026 | 204.1667 | 370.0693 | 587.522 | 1
221 | 17 | 226 | 190 |  | 0.26909 | 2.41 | -5.2119 | 1.5081 | 17.0251 | 1.3156 | 21.0371 | 73.9161 | 158.3333 | 232.2494 | 368.7192 | 1
221 | 18 | 208 | 109 |  | 0.26909 | 2.41 | -5.2119 | 1.5081 | 18.0251 | 1.5774 | 11.9805 | 20.1046 | 90.8333 | 110.9379 | 176.125 | 0
221 | 19 | 3 | 46 |  | 0.26909 | 2.41 | -5.2119 | 1.5081 | 19.0251 | 1.8392 | 3.2359 | 0 | 38.3333 | 38.3333 | 60.858 | 0
221 | 20 | 0 | 4 |  | 0.26909 | 2.41 | -5.2119 | 1.5081 | 20.0251 | 2.101 | -4.8257 | 0 | 3.3333 | 3.3333 | 5.292 | 0
221 | 21 | 0 | 0 |  | 0.26909 | 2.41 | -5.2119 | 1.5081 | 21.0251 | 2.3628 | -11.8034 | 0 | 0 | 0 | 0 | 0
221 | 22 | 0 | 0 |  | 0.26909 | 2.41 | -5.2119 | 1.5081 | 22.0251 | 2.6246 | -17.2556 | 0 | 0 | 0 | 0 | 0
221 | 23 | 0 | 0 |  | 0.26909 | 2.41 | -5.2119 | 1.5081 | 23.0251 | 2.8864 | -20.7378 | 0 | 0 | 0 | 0 | 0
221 | 24 | 0 | 0 |  | 0.26909 | 2.41 | -5.2119 | 1.5081 | 24.0251 | 3.1482 | -21.9014 | 0 | 0 | 0 | 0 | 0
222 | 1 | 0 | 0 |  | 0.26377 | 2.4272 | -5.0645 | 1.6555 | 1.0276 | -2.8726 | -20.9103 | 0 | 0 | 0 | 0 | 0
222 | 2 | 0 | 0 |  | 0.26377 | 2.4272 | -5.0645 | 1.6555 | 2.0276 | -2.6108 | -17.3025 | 0 | 0 | 0 | 0 | 0
222 | 3 | 0 | 0 |  | 0.26377 | 2.4272 | -5.0645 | 1.6555 | 3.0276 | -2.349 | -11.7434 | 0 | 0 | 0 | 0 | 0
222 | 4 | 0 | 0 |  | 0.26377 | 2.4272 | -5.0645 | 1.6555 | 4.0276 | -2.0872 | -4.6829 | 0 | 0 | 0 | 0 | 0
222 | 5 | 0 | 2 |  | 0.26377 | 2.4272 | -5.0645 | 1.6555 | 5.0276 | -1.8254 | 3.4364 | 0 | 1.6667 | 1.6667 | 2.646 | 0
222 | 6 | 0 | 20 |  | 0.26377 | 2.4272 | -5.0645 | 1.6555 | 6.0276 | -1.5636 | 12.2142 | 0 | 16.6667 | 16.6667 | 26.46 | 0
222 | 7 | 0 | 66 |  | 0.26377 | 2.4272 | -5.0645 | 1.6555 | 7.0276 | -1.3018 | 21.2788 | 0 | 55 | 55 | 87.318 | 1
222 | 8 | 0 | 122 |  | 0.26377 | 2.4272 | -5.0645 | 1.6555 | 8.0276 | -1.04 | 30.2413 | 0 | 101.6667 | 101.6667 | 161.406 | 1
222 | 9 | 2 | 176 |  | 0.26377 | 2.4272 | -5.0645 | 1.6555 | 9.0276 | -0.77817 | 38.6225 | 1.4699 | 146.6667 | 148.1365 | 235.1815 | 1
222 | 10 | 5 | 219 |  | 0.26377 | 2.4272 | -5.0645 | 1.6555 | 10.0276 | -0.51638 | 45.7518 | 4.3757 | 182.5 | 186.8757 | 296.6839 | 1
222 | 11 | 71 | 355 |  | 0.26377 | 2.4272 | -5.0645 | 1.6555 | 11.0276 | -0.25458 | 50.694 | 68.3433 | 295.8333 | 364.1766 | 578.1668 | 1
222 | 12 | 86 | 366 |  | 0.26377 | 2.4272 | -5.0645 | 1.6555 | 12.0276 | 0.0072235 | 52.4313 | 85.249 | 305 | 390.249 | 619.5593 | 1
222 | 13 | 86 | 366 |  | 0.26377 | 2.4272 | -5.0645 | 1.6555 | 13.0276 | 0.26902 | 50.4965 | 82.4956 | 305 | 387.4956 | 615.188 | 1
222 | 14 | 71 | 353 |  | 0.26377 | 2.4272 | -5.0645 | 1.6555 | 14.0276 | 0.53082 | 45.4057 | 61.6787 | 294.1667 | 355.8454 | 564.9401 | 1
222 | 15 | 68 | 307 |  | 0.26377 | 2.4272 | -5.0645 | 1.6555 | 15.0276 | 0.79262 | 38.1854 | 49.3562 | 255.8333 | 305.1895 | 484.5189 | 1
222 | 16 | 17 | 269 |  | 0.26377 | 2.4272 | -5.0645 | 1.6555 | 16.0276 | 1.0544 | 29.7568 | 9.1855 | 224.1667 | 233.3522 | 370.47 | 1
222 | 17 | 24 | 181 |  | 0.26377 | 2.4272 | -5.0645 | 1.6555 | 17.0276 | 1.3162 | 20.7774 | 7.7965 | 150.8333 | 158.6298 | 251.8407 | 1
222 | 18 | 0 | 64 |  | 0.26377 | 2.4272 | -5.0645 | 1.6555 | 18.0276 | 1.578 | 11.719 | 0 | 53.3333 | 53.3333 | 84.672 | 0
222 | 19 | 0 | 19 |  | 0.26377 | 2.4272 | -5.0645 | 1.6555 | 19.0276 | 1.8398 | 2.9677 | 0 | 15.8333 | 15.8333 | 25.137 | 0
222 | 20 | 0 | 1 |  | 0.26377 | 2.4272 | -5.0645 | 1.6555 | 20.0276 | 2.1016 | -5.104 | 0 | 0.83333 | 0.83333 | 1.323 | 0
222 | 21 | 0 | 0 |  | 0.26377 | 2.4272 | -5.0645 | 1.6555 | 21.0276 | 2.3634 | -12.0935 | 0 | 0 | 0 | 0 | 0
222 | 22 | 0 | 0 |  | 0.26377 | 2.4272 | -5.0645 | 1.6555 | 22.0276 | 2.6252 | -17.5564 | 0 | 0 | 0 | 0 | 0
222 | 23 | 0 | 0 |  | 0.26377 | 2.4272 | -5.0645 | 1.6555 | 23.0276 | 2.887 | -21.0446 | 0 | 0 | 0 | 0 | 0
222 | 24 | 0 | 0 |  | 0.26377 | 2.4272 | -5.0645 | 1.6555 | 24.0276 | 3.1488 | -22.2064 | 0 | 0 | 0 | 0 | 0
223 | 1 | 0 | 0 |  | 0.25837 | 2.4444 | -4.9069 | 1.8131 | 1.0302 | -2.8719 | -21.2083 | 0 | 0 | 0 | 0 | 0
223 | 2 | 0 | 0 |  | 0.25837 | 2.4444 | -4.9069 | 1.8131 | 2.0302 | -2.6101 | -17.583 | 0 | 0 | 0 | 0 | 0
223 | 3 | 0 | 0 |  | 0.25837 | 2.4444 | -4.9069 | 1.8131 | 3.0302 | -2.3483 | -12.004 | 0 | 0 | 0 | 0 | 0
223 | 4 | 0 | 0 |  | 0.25837 | 2.4444 | -4.9069 | 1.8131 | 4.0302 | -2.0865 | -4.9251 | 0 | 0 | 0 | 0 | 0
223 | 5 | 0 | 1 |  | 0.25837 | 2.4444 | -4.9069 | 1.8131 | 5.0302 | -1.8247 | 3.2086 | 0 | 0.83333 | 0.83333 | 1.323 | 0
223 | 6 | 0 | 19 |  | 0.25837 | 2.4444 | -4.9069 | 1.8131 | 6.0302 | -1.5629 | 11.9952 | 0 | 15.8333 | 15.8333 | 25.137 | 0
223 | 7 | 0 | 64 |  | 0.25837 | 2.4444 | -4.9069 | 1.8131 | 7.0302 | -1.3011 | 21.0617 | 0 | 53.3333 | 53.3333 | 84.672 | 1
223 | 8 | 0 | 120 |  | 0.25837 | 2.4444 | -4.9069 | 1.8131 | 8.0302 | -1.0393 | 30.0179 | 0 | 100 | 100 | 158.76 | 1
223 | 9 | 2 | 174 |  | 0.25837 | 2.4444 | -4.9069 | 1.8131 | 9.0302 | -0.77749 | 38.3837 | 1.4685 | 145 | 146.4685 | 232.5334 | 1
223 | 10 | 5 | 217 |  | 0.25837 | 2.4444 | -4.9069 | 1.8131 | 10.0302 | -0.51569 | 45.4885 | 4.3728 | 180.8333 | 185.2061 | 294.0332 | 1
223 | 11 | 7 | 248 |  | 0.25837 | 2.4444 | -4.9069 | 1.8131 | 11.0302 | -0.25389 | 50.4029 | 6.7338 | 206.6667 | 213.4005 | 338.7946 | 1
223 | 12 | 10 | 262 |  | 0.25837 | 2.4444 | -4.9069 | 1.8131 | 12.0302 | 0.0079112 | 52.1218 | 9.9054 | 218.3333 | 228.2387 | 362.3518 | 1
223 | 13 | 119 | 336 |  | 0.25837 | 2.4444 | -4.9069 | 1.8131 | 13.0302 | 0.26971 | 50.1877 | 114.0397 | 280 | 394.0397 | 625.5774 | 1
223 | 14 | 17 | 240 |  | 0.25837 | 2.4444 | -4.9069 | 1.8131 | 14.0302 | 0.53151 | 45.1108 | 14.7475 | 200 | 214.7475 | 340.9332 | 1
223 | 15 | 5 | 216 |  | 0.25837 | 2.4444 | -4.9069 | 1.8131 | 15.0302 | 0.79331 | 37.9059 | 3.6214 | 180 | 183.6214 | 291.5173 | 1
223 | 16 | 1 | 172 |  | 0.25837 | 2.4444 | -4.9069 | 1.8131 | 16.0302 | 1.0551 | 29.4879 | 0.53842 | 143.3333 | 143.8717 | 228.4108 | 1
223 | 17 | 0 | 118 |  | 0.25837 | 2.4444 | -4.9069 | 1.8131 | 17.0302 | 1.3169 | 20.5127 | 0 | 98.3333 | 98.3333 | 156.114 | 1
223 | 18 | 3 | 99 |  | 0.25837 | 2.4444 | -4.9069 | 1.8131 | 18.0302 | 1.5787 | 11.4525 | 0.27438 | 82.5 | 82.7744 | 131.4126 | 0
223 | 19 | 0 | 28 |  | 0.25837 | 2.4444 | -4.9069 | 1.8131 | 19.0302 | 1.8405 | 2.6947 | 0 | 23.3333 | 23.3333 | 37.044 | 0
223 | 20 | 0 | 2 |  | 0.25837 | 2.4444 | -4.9069 | 1.8131 | 20.0302 | 2.1023 | -5.3871 | 0 | 1.6667 | 1.6667 | 2.646 | 0
223 | 21 | 0 | 0 |  | 0.25837 | 2.4444 | -4.9069 | 1.8131 | 21.0302 | 2.3641 | -12.3884 | 0 | 0 | 0 | 0 | 0
223 | 22 | 0 | 0 |  | 0.25837 | 2.4444 | -4.9069 | 1.8131 | 22.0302 | 2.6259 | -17.8619 | 0 | 0 | 0 | 0 | 0
223 | 23 | 0 | 0 |  | 0.25837 | 2.4444 | -4.9069 | 1.8131 | 23.0302 | 2.8877 | -21.3559 | 0 | 0 | 0 | 0 | 0
223 | 24 | 0 | 0 |  | 0.25837 | 2.4444 | -4.9069 | 1.8131 | 24.0302 | 3.1495 | -22.5154 | 0 | 0 | 0 | 0 | 0
224 | 1 | 0 | 0 |  | 0.2529 | 2.4616 | -4.7392 | 1.9808 | 1.033 | -2.8712 | -21.5097 | 0 | 0 | 0 | 0 | 0
224 | 2 | 0 | 0 |  | 0.2529 | 2.4616 | -4.7392 | 1.9808 | 2.033 | -2.6094 | -17.8664 | 0 | 0 | 0 | 0 | 0
224 | 3 | 0 | 0 |  | 0.2529 | 2.4616 | -4.7392 | 1.9808 | 3.033 | -2.3476 | -12.2671 | 0 | 0 | 0 | 0 | 0
224 | 4 | 0 | 0 |  | 0.2529 | 2.4616 | -4.7392 | 1.9808 | 4.033 | -2.0858 | -5.1693 | 0 | 0 | 0 | 0 | 0
224 | 5 | 0 | 1 |  | 0.2529 | 2.4616 | -4.7392 | 1.9808 | 5.033 | -1.824 | 2.9791 | 0 | 0.83333 | 0.83333 | 1.323 | 0
224 | 6 | 0 | 18 |  | 0.2529 | 2.4616 | -4.7392 | 1.9808 | 6.033 | -1.5622 | 11.7745 | 0 | 15 | 15 | 23.814 | 0
224 | 7 | 0 | 64 |  | 0.2529 | 2.4616 | -4.7392 | 1.9808 | 7.033 | -1.3004 | 20.8427 | 0 | 53.3333 | 53.3333 | 84.672 | 1
224 | 8 | 0 | 120 |  | 0.2529 | 2.4616 | -4.7392 | 1.9808 | 8.033 | -1.0386 | 29.7925 | 0 | 100 | 100 | 158.76 | 1
224 | 9 | 2 | 173 |  | 0.2529 | 2.4616 | -4.7392 | 1.9808 | 9.033 | -0.77676 | 38.1423 | 1.4672 | 144.1667 | 145.6338 | 231.2083 | 1
224 | 10 | 5 | 217 |  | 0.2529 | 2.4616 | -4.7392 | 1.9808 | 10.033 | -0.51496 | 45.2223 | 4.3698 | 180.8333 | 185.2031 | 294.0284 | 1
224 | 11 | 7 | 249 |  | 0.2529 | 2.4616 | -4.7392 | 1.9808 | 11.033 | -0.25316 | 50.1083 | 6.7293 | 207.5 | 214.2293 | 340.1104 | 1
224 | 12 | 10 | 262 |  | 0.2529 | 2.4616 | -4.7392 | 1.9808 | 12.033 | 0.0086429 | 51.8082 | 9.8977 | 218.3333 | 228.231 | 362.3396 | 1
224 | 13 | 10 | 262 |  | 0.2529 | 2.4616 | -4.7392 | 1.9808 | 13.033 | 0.27044 | 49.8743 | 9.5733 | 218.3333 | 227.9067 | 361.8246 | 1
224 | 14 | 7 | 248 |  | 0.2529 | 2.4616 | -4.7392 | 1.9808 | 14.033 | 0.53224 | 44.8111 | 6.0636 | 206.6667 | 212.7303 | 337.7306 | 1
224 | 15 | 5 | 216 |  | 0.2529 | 2.4616 | -4.7392 | 1.9808 | 15.033 | 0.79404 | 37.6215 | 3.6134 | 180 | 183.6134 | 291.5046 | 1
224 | 16 | 46 | 250 |  | 0.2529 | 2.4616 | -4.7392 | 1.9808 | 16.033 | 1.0558 | 29.214 | 24.6761 | 208.3333 | 233.0094 | 369.9258 | 1
224 | 17 | 24 | 177 |  | 0.2529 | 2.4616 | -4.7392 | 1.9808 | 17.033 | 1.3176 | 20.243 | 7.6853 | 147.5 | 155.1853 | 246.3722 | 1
224 | 18 | 4 | 97 |  | 0.2529 | 2.4616 | -4.7392 | 1.9808 | 18.033 | 1.5794 | 11.1813 | 0.35503 | 80.8333 | 81.1884 | 128.8947 | 0
224 | 19 | 0 | 27 |  | 0.2529 | 2.4616 | -4.7392 | 1.9808 | 19.033 | 1.8412 | 2.4169 | 0 | 22.5 | 22.5 | 35.721 | 0
224 | 20 | 0 | 2 |  | 0.2529 | 2.4616 | -4.7392 | 1.9808 | 20.033 | 2.103 | -5.675 | 0 | 1.6667 | 1.6667 | 2.646 | 0
224 | 21 | 0 | 0 |  | 0.2529 | 2.4616 | -4.7392 | 1.9808 | 21.033 | 2.3648 | -12.6881 | 0 | 0 | 0 | 0 | 0
224 | 22 | 0 | 0 |  | 0.2529 | 2.4616 | -4.7392 | 1.9808 | 22.033 | 2.6266 | -18.172 | 0 | 0 | 0 | 0 | 0
224 | 23 | 0 | 0 |  | 0.2529 | 2.4616 | -4.7392 | 1.9808 | 23.033 | 2.8884 | -21.6715 | 0 | 0 | 0 | 0 | 0
224 | 24 | 0 | 0 |  | 0.2529 | 2.4616 | -4.7392 | 1.9808 | 24.033 | 3.1502 | -22.8284 | 0 | 0 | 0 | 0 | 0
225 | 1 | 0 | 0 |  | 0.24737 | 2.4788 | -4.5615 | 2.1585 | 1.036 | -2.8704 | -21.8145 | 0 | 0 | 0 | 0 | 0
225 | 2 | 0 | 0 |  | 0.24737 | 2.4788 | -4.5615 | 2.1585 | 2.036 | -2.6086 | -18.1525 | 0 | 0 | 0 | 0 | 0
225 | 3 | 0 | 0 |  | 0.24737 | 2.4788 | -4.5615 | 2.1585 | 3.036 | -2.3468 | -12.5324 | 0 | 0 | 0 | 0 | 0
225 | 4 | 0 | 0 |  | 0.24737 | 2.4788 | -4.5615 | 2.1585 | 4.036 | -2.085 | -5.4155 | 0 | 0 | 0 | 0 | 0
225 | 5 | 0 | 3 |  | 0.24737 | 2.4788 | -4.5615 | 2.1585 | 5.036 | -1.8232 | 2.7477 | 0 | 2.5 | 2.5 | 3.969 | 0
225 | 6 | 23 | 45 |  | 0.24737 | 2.4788 | -4.5615 | 2.1585 | 6.036 | -1.5614 | 11.552 | 2.3652 | 37.5 | 39.8652 | 63.29 | 0
225 | 7 | 160 | 118 |  | 0.24737 | 2.4788 | -4.5615 | 2.1585 | 7.036 | -1.2996 | 20.6219 | 53.452 | 98.3333 | 151.7853 | 240.9744 | 1
225 | 8 | 182 | 204 |  | 0.24737 | 2.4788 | -4.5615 | 2.1585 | 8.036 | -1.0378 | 29.5648 | 99.9146 | 170 | 269.9146 | 428.5163 | 1
225 | 9 | 428 | 213 |  | 0.24737 | 2.4788 | -4.5615 | 2.1585 | 9.036 | -0.77598 | 37.8984 | 313.685 | 177.5 | 491.185 | 779.8054 | 1
225 | 10 | 605 | 200 |  | 0.24737 | 2.4788 | -4.5615 | 2.1585 | 10.036 | -0.51418 | 44.953 | 528.3612 | 166.6667 | 695.0279 | 1103.4262 | 1
225 | 11 | 687 | 184 |  | 0.24737 | 2.4788 | -4.5615 | 2.1585 | 11.036 | -0.25238 | 49.8102 | 659.972 | 153.3333 | 813.3053 | 1291.2036 | 1
225 | 12 | 706 | 189 |  | 0.24737 | 2.4788 | -4.5615 | 2.1585 | 12.036 | 0.0094181 | 51.4907 | 698.2046 | 157.5 | 855.7046 | 1358.5166 | 1
225 | 13 | 755 | 171 |  | 0.24737 | 2.4788 | -4.5615 | 2.1585 | 13.036 | 0.27122 | 49.5565 | 722.004 | 142.5 | 864.504 | 1372.4866 | 1
225 | 14 | 757 | 151 |  | 0.24737 | 2.4788 | -4.5615 | 2.1585 | 14.036 | 0.53302 | 44.5065 | 654.7286 | 125.8333 | 780.5619 | 1239.2201 | 1
225 | 15 | 740 | 131 |  | 0.24737 | 2.4788 | -4.5615 | 2.1585 | 15.036 | 0.79482 | 37.3321 | 533.5355 | 109.1667 | 642.7021 | 1020.3539 | 1
225 | 16 | 644 | 131 |  | 0.24737 | 2.4788 | -4.5615 | 2.1585 | 16.036 | 1.0566 | 28.9352 | 344.146 | 109.1667 | 453.3126 | 719.6791 | 1
225 | 17 | 464 | 135 |  | 0.24737 | 2.4788 | -4.5615 | 2.1585 | 17.036 | 1.3184 | 19.9685 | 147.4586 | 112.5 | 259.9586 | 412.7102 | 1
225 | 18 | 255 | 99 |  | 0.24737 | 2.4788 | -4.5615 | 2.1585 | 18.036 | 1.5802 | 10.9052 | 21.9263 | 82.5 | 104.4263 | 165.7873 | 0
225 | 19 | 0 | 37 |  | 0.24737 | 2.4788 | -4.5615 | 2.1585 | 19.036 | 1.842 | 2.1344 | 0 | 30.8333 | 30.8333 | 48.951 | 0
225 | 20 | 0 | 1 |  | 0.24737 | 2.4788 | -4.5615 | 2.1585 | 20.036 | 2.1038 | -5.9676 | 0 | 0.83333 | 0.83333 | 1.323 | 0
225 | 21 | 0 | 0 |  | 0.24737 | 2.4788 | -4.5615 | 2.1585 | 21.036 | 2.3656 | -12.9923 | 0 | 0 | 0 | 0 | 0
225 | 22 | 0 | 0 |  | 0.24737 | 2.4788 | -4.5615 | 2.1585 | 22.036 | 2.6274 | -18.4867 | 0 | 0 | 0 | 0 | 0
225 | 23 | 0 | 0 |  | 0.24737 | 2.4788 | -4.5615 | 2.1585 | 23.036 | 2.8892 | -21.9915 | 0 | 0 | 0 | 0 | 0
225 | 24 | 0 | 0 |  | 0.24737 | 2.4788 | -4.5615 | 2.1585 | 24.036 | 3.151 | -23.1453 | 0 | 0 | 0 | 0 | 0
226 | 1 | 0 | 0 |  | 0.24176 | 2.4961 | -4.374 | 2.346 | 1.0391 | -2.8696 | -22.1226 | 0 | 0 | 0 | 0 | 0
226 | 2 | 0 | 0 |  | 0.24176 | 2.4961 | -4.374 | 2.346 | 2.0391 | -2.6078 | -18.4414 | 0 | 0 | 0 | 0 | 0
226 | 3 | 0 | 0 |  | 0.24176 | 2.4961 | -4.374 | 2.346 | 3.0391 | -2.346 | -12.7999 | 0 | 0 | 0 | 0 | 0
226 | 4 | 0 | 0 |  | 0.24176 | 2.4961 | -4.374 | 2.346 | 4.0391 | -2.0842 | -5.6635 | 0 | 0 | 0 | 0 | 0
226 | 5 | 0 | 1 |  | 0.24176 | 2.4961 | -4.374 | 2.346 | 5.0391 | -1.8224 | 2.5147 | 0 | 0.83333 | 0.83333 | 1.323 | 0
226 | 6 | 0 | 40 |  | 0.24176 | 2.4961 | -4.374 | 2.346 | 6.0391 | -1.5606 | 11.3279 | 0 | 33.3333 | 33.3333 | 52.92 | 0
226 | 7 | 211 | 115 |  | 0.24176 | 2.4961 | -4.374 | 2.346 | 7.0391 | -1.2988 | 20.3993 | 70.2673 | 95.8333 | 166.1006 | 263.7014 | 1
226 | 8 | 450 | 143 |  | 0.24176 | 2.4961 | -4.374 | 2.346 | 8.0391 | -1.037 | 29.3352 | 246.6685 | 119.1667 | 365.8352 | 580.7999 | 1
226 | 9 | 606 | 153 |  | 0.24176 | 2.4961 | -4.374 | 2.346 | 9.0391 | -0.77516 | 37.652 | 443.725 | 127.5 | 571.225 | 906.8768 | 1
226 | 10 | 657 | 164 |  | 0.24176 | 2.4961 | -4.374 | 2.346 | 10.0391 | -0.51336 | 44.6808 | 573.3497 | 136.6667 | 710.0163 | 1127.2219 | 1
226 | 11 | 255 | 328 |  | 0.24176 | 2.4961 | -4.374 | 2.346 | 11.0391 | -0.25156 | 49.5087 | 244.789 | 273.3333 | 518.1223 | 822.5709 | 1
226 | 12 | 403 | 324 |  | 0.24176 | 2.4961 | -4.374 | 2.346 | 12.0391 | 0.010236 | 51.1692 | 398.207 | 270 | 668.207 | 1060.8454 | 1
226 | 13 | 355 | 361 |  | 0.24176 | 2.4961 | -4.374 | 2.346 | 13.0391 | 0.27204 | 49.2343 | 339.0995 | 300.8333 | 639.9329 | 1015.9574 | 1
226 | 14 | 660 | 219 |  | 0.24176 | 2.4961 | -4.374 | 2.346 | 14.0391 | 0.53384 | 44.1973 | 569.9155 | 182.5 | 752.4155 | 1194.5348 | 1
226 | 15 | 735 | 132 |  | 0.24176 | 2.4961 | -4.374 | 2.346 | 15.0391 | 0.79563 | 37.0379 | 528.6496 | 110 | 638.6496 | 1013.92 | 1
226 | 16 | 643 | 130 |  | 0.24176 | 2.4961 | -4.374 | 2.346 | 16.0391 | 1.0574 | 28.6515 | 342.2491 | 108.3333 | 450.5824 | 715.3447 | 1
226 | 17 | 461 | 134 |  | 0.24176 | 2.4961 | -4.374 | 2.346 | 17.0391 | 1.3192 | 19.6893 | 145.3557 | 111.6667 | 257.0224 | 408.0487 | 1
226 | 18 | 259 | 97 |  | 0.24176 | 2.4961 | -4.374 | 2.346 | 18.0391 | 1.581 | 10.6246 | 21.5345 | 80.8333 | 102.3678 | 162.5191 | 0
226 | 19 | 26 | 39 |  | 0.24176 | 2.4961 | -4.374 | 2.346 | 19.0391 | 1.8428 | 1.8473 | 0 | 32.5 | 32.5 | 51.597 | 0
226 | 20 | 0 | 2 |  | 0.24176 | 2.4961 | -4.374 | 2.346 | 20.0391 | 2.1046 | -6.2647 | 0 | 1.6667 | 1.6667 | 2.646 | 0
226 | 21 | 0 | 0 |  | 0.24176 | 2.4961 | -4.374 | 2.346 | 21.0391 | 2.3664 | -13.3011 | 0 | 0 | 0 | 0 | 0
226 | 22 | 0 | 0 |  | 0.24176 | 2.4961 | -4.374 | 2.346 | 22.0391 | 2.6282 | -18.8057 | 0 | 0 | 0 | 0 | 0
226 | 23 | 0 | 0 |  | 0.24176 | 2.4961 | -4.374 | 2.346 | 23.0391 | 2.89 | -22.3156 | 0 | 0 | 0 | 0 | 0
226 | 24 | 0 | 0 |  | 0.24176 | 2.4961 | -4.374 | 2.346 | 24.0391 | 3.1518 | -23.466 | 0 | 0 | 0 | 0 | 0
227 | 1 | 0 | 0 |  | 0.2361 | 2.5133 | -4.1767 | 2.5433 | 1.0424 | -2.8687 | -22.4338 | 0 | 0 | 0 | 0 | 0
227 | 2 | 0 | 0 |  | 0.2361 | 2.5133 | -4.1767 | 2.5433 | 2.0424 | -2.6069 | -18.7329 | 0 | 0 | 0 | 0 | 0
227 | 3 | 0 | 0 |  | 0.2361 | 2.5133 | -4.1767 | 2.5433 | 3.0424 | -2.3451 | -13.0695 | 0 | 0 | 0 | 0 | 0
227 | 4 | 0 | 0 |  | 0.2361 | 2.5133 | -4.1767 | 2.5433 | 4.0424 | -2.0833 | -5.9132 | 0 | 0 | 0 | 0 | 0
227 | 5 | 0 | 2 |  | 0.2361 | 2.5133 | -4.1767 | 2.5433 | 5.0424 | -1.8215 | 2.2802 | 0 | 1.6667 | 1.6667 | 2.646 | 0
227 | 6 | 0 | 32 |  | 0.2361 | 2.5133 | -4.1767 | 2.5433 | 6.0424 | -1.5597 | 11.1022 | 0 | 26.6667 | 26.6667 | 42.336 | 0
227 | 7 | 2 | 96 |  | 0.2361 | 2.5133 | -4.1767 | 2.5433 | 7.0424 | -1.2979 | 20.1749 | 0.66395 | 80 | 80.6639 | 128.0621 | 1
227 | 8 | 130 | 183 |  | 0.2361 | 2.5133 | -4.1767 | 2.5433 | 8.0424 | -1.0361 | 29.1035 | 71.152 | 152.5 | 223.652 | 355.0699 | 1
227 | 9 | 49 | 247 |  | 0.2361 | 2.5133 | -4.1767 | 2.5433 | 9.0424 | -0.7743 | 37.4032 | 35.8445 | 205.8333 | 241.6778 | 383.6877 | 1
227 | 10 | 205 | 311 |  | 0.2361 | 2.5133 | -4.1767 | 2.5433 | 10.0424 | -0.5125 | 44.4057 | 178.7625 | 259.1667 | 437.9291 | 695.2563 | 1
227 | 11 | 573 | 267 |  | 0.2361 | 2.5133 | -4.1767 | 2.5433 | 11.0424 | -0.2507 | 49.2038 | 549.6353 | 222.5 | 772.1353 | 1225.842 | 1
227 | 12 | 435 | 299 |  | 0.2361 | 2.5133 | -4.1767 | 2.5433 | 12.0424 | 0.011097 | 50.844 | 429.4375 | 249.1667 | 678.6042 | 1077.352 | 1
227 | 13 | 535 | 281 |  | 0.2361 | 2.5133 | -4.1767 | 2.5433 | 13.0424 | 0.2729 | 48.9078 | 510.4279 | 234.1667 | 744.5946 | 1182.1184 | 1
227 | 14 | 661 | 198 |  | 0.2361 | 2.5133 | -4.1767 | 2.5433 | 14.0424 | 0.5347 | 43.8834 | 569.8198 | 165 | 734.8198 | 1166.5999 | 1
227 | 15 | 710 | 140 |  | 0.2361 | 2.5133 | -4.1767 | 2.5433 | 15.0424 | 0.7965 | 36.7389 | 509.3838 | 116.6667 | 626.0505 | 993.9178 | 1
227 | 16 | 627 | 134 |  | 0.2361 | 2.5133 | -4.1767 | 2.5433 | 16.0424 | 1.0583 | 28.3632 | 332.3607 | 111.6667 | 444.0273 | 704.9378 | 1
227 | 17 | 452 | 134 |  | 0.2361 | 2.5133 | -4.1767 | 2.5433 | 17.0424 | 1.3201 | 19.4055 | 141.3593 | 111.6667 | 253.026 | 401.7041 | 1
227 | 18 | 236 | 99 |  | 0.2361 | 2.5133 | -4.1767 | 2.5433 | 18.0424 | 1.5819 | 10.3393 | 18.9358 | 82.5 | 101.4358 | 161.0395 | 0
227 | 19 | 13 | 38 |  | 0.2361 | 2.5133 | -4.1767 | 2.5433 | 19.0424 | 1.8437 | 1.5557 | 0 | 31.6667 | 31.6667 | 50.274 | 0
227 | 20 | 0 | 1 |  | 0.2361 | 2.5133 | -4.1767 | 2.5433 | 20.0424 | 2.1055 | -6.5662 | 0 | 0.83333 | 0.83333 | 1.323 | 0
227 | 21 | 0 | 0 |  | 0.2361 | 2.5133 | -4.1767 | 2.5433 | 21.0424 | 2.3673 | -13.6142 | 0 | 0 | 0 | 0 | 0
227 | 22 | 0 | 0 |  | 0.2361 | 2.5133 | -4.1767 | 2.5433 | 22.0424 | 2.6291 | -19.1291 | 0 | 0 | 0 | 0 | 0
227 | 23 | 0 | 0 |  | 0.2361 | 2.5133 | -4.1767 | 2.5433 | 23.0424 | 2.8909 | -22.6439 | 0 | 0 | 0 | 0 | 0
227 | 24 | 0 | 0 |  | 0.2361 | 2.5133 | -4.1767 | 2.5433 | 24.0424 | 3.1527 | -23.7904 | 0 | 0 | 0 | 0 | 0
228 | 1 | 0 | 0 |  | 0.23036 | 2.5305 | -3.9699 | 2.7501 | 1.0458 | -2.8678 | -22.7481 | 0 | 0 | 0 | 0 | 0
228 | 2 | 0 | 0 |  | 0.23036 | 2.5305 | -3.9699 | 2.7501 | 2.0458 | -2.606 | -19.0268 | 0 | 0 | 0 | 0 | 0
228 | 3 | 0 | 0 |  | 0.23036 | 2.5305 | -3.9699 | 2.7501 | 3.0458 | -2.3442 | -13.3411 | 0 | 0 | 0 | 0 | 0
228 | 4 | 0 | 0 |  | 0.23036 | 2.5305 | -3.9699 | 2.7501 | 4.0458 | -2.0824 | -6.1647 | 0 | 0 | 0 | 0 | 0
228 | 5 | 0 | 2 |  | 0.23036 | 2.5305 | -3.9699 | 2.7501 | 5.0458 | -1.8206 | 2.0441 | 0 | 1.6667 | 1.6667 | 2.646 | 0
228 | 6 | 0 | 36 |  | 0.23036 | 2.5305 | -3.9699 | 2.7501 | 6.0458 | -1.5588 | 10.875 | 0 | 30 | 30 | 47.628 | 0
228 | 7 | 260 | 90 |  | 0.23036 | 2.5305 | -3.9699 | 2.7501 | 7.0458 | -1.297 | 19.9489 | 86.0426 | 75 | 161.0426 | 255.6712 | 1
228 | 8 | 384 | 153 |  | 0.23036 | 2.5305 | -3.9699 | 2.7501 | 8.0458 | -1.0352 | 28.8698 | 209.8534 | 127.5 | 337.3534 | 535.5822 | 1
228 | 9 | 337 | 216 |  | 0.23036 | 2.5305 | -3.9699 | 2.7501 | 9.0458 | -0.7734 | 37.152 | 246.2832 | 180 | 426.2832 | 676.7671 | 1
228 | 10 | 66 | 300 |  | 0.23036 | 2.5305 | -3.9699 | 2.7501 | 10.0458 | -0.5116 | 44.1277 | 57.5074 | 250 | 307.5074 | 488.1988 | 1
228 | 11 | 525 | 313 |  | 0.23036 | 2.5305 | -3.9699 | 2.7501 | 11.0458 | -0.2498 | 48.8957 | 503.1907 | 260.8333 | 764.0241 | 1212.9646 | 1
228 | 12 | 157 | 301 |  | 0.23036 | 2.5305 | -3.9699 | 2.7501 | 12.0458 | 0.012 | 50.5151 | 154.8452 | 250.8333 | 405.6786 | 644.0553 | 1
228 | 13 | 86 | 355 |  | 0.23036 | 2.5305 | -3.9699 | 2.7501 | 13.0458 | 0.2738 | 48.5772 | 81.9476 | 295.8333 | 377.7809 | 599.765 | 1
228 | 14 | 16 | 234 |  | 0.23036 | 2.5305 | -3.9699 | 2.7501 | 14.0458 | 0.5356 | 43.565 | 13.7687 | 195 | 208.7687 | 331.4412 | 1
228 | 15 | 71 | 293 |  | 0.23036 | 2.5305 | -3.9699 | 2.7501 | 15.0458 | 0.7974 | 36.4354 | 50.8052 | 244.1667 | 294.9719 | 468.2974 | 1
228 | 16 | 17 | 255 |  | 0.23036 | 2.5305 | -3.9699 | 2.7501 | 16.0458 | 1.0592 | 28.0703 | 8.973 | 212.5 | 221.473 | 351.6105 | 1
228 | 17 | 22 | 168 |  | 0.23036 | 2.5305 | -3.9699 | 2.7501 | 17.0458 | 1.321 | 19.1171 | 6.8224 | 140 | 146.8224 | 233.0953 | 1
228 | 18 | 0 | 88 |  | 0.23036 | 2.5305 | -3.9699 | 2.7501 | 18.0458 | 1.5828 | 10.0496 | 0 | 73.3333 | 73.3333 | 116.424 | 0
228 | 19 | 0 | 20 |  | 0.23036 | 2.5305 | -3.9699 | 2.7501 | 19.0458 | 1.8446 | 1.2598 | 0 | 16.6667 | 16.6667 | 26.46 | 0
228 | 20 | 0 | 1 |  | 0.23036 | 2.5305 | -3.9699 | 2.7501 | 20.0458 | 2.1064 | -6.8721 | 0 | 0.83333 | 0.83333 | 1.323 | 0
228 | 21 | 0 | 0 |  | 0.23036 | 2.5305 | -3.9699 | 2.7501 | 21.0458 | 2.3682 | -13.9317 | 0 | 0 | 0 | 0 | 0
228 | 22 | 0 | 0 |  | 0.23036 | 2.5305 | -3.9699 | 2.7501 | 22.0458 | 2.63 | -19.4566 | 0 | 0 | 0 | 0 | 0
228 | 23 | 0 | 0 |  | 0.23036 | 2.5305 | -3.9699 | 2.7501 | 23.0458 | 2.8918 | -22.9761 | 0 | 0 | 0 | 0 | 0
228 | 24 | 0 | 0 |  | 0.23036 | 2.5305 | -3.9699 | 2.7501 | 24.0458 | 3.1536 | -24.1184 | 0 | 0 | 0 | 0 | 0
229 | 1 | 0 | 0 |  | 0.22457 | 2.5477 | -3.7536 | 2.9664 | 1.0494 | -2.8668 | -23.0653 | 0 | 0 | 0 | 0 | 0
229 | 2 | 0 | 0 |  | 0.22457 | 2.5477 | -3.7536 | 2.9664 | 2.0494 | -2.6051 | -19.3231 | 0 | 0 | 0 | 0 | 0
229 | 3 | 0 | 0 |  | 0.22457 | 2.5477 | -3.7536 | 2.9664 | 3.0494 | -2.3433 | -13.6147 | 0 | 0 | 0 | 0 | 0
229 | 4 | 0 | 0 |  | 0.22457 | 2.5477 | -3.7536 | 2.9664 | 4.0494 | -2.0815 | -6.4177 | 0 | 0 | 0 | 0 | 0
229 | 5 | 0 | 1 |  | 0.22457 | 2.5477 | -3.7536 | 2.9664 | 5.0494 | -1.8197 | 1.8065 | 0 | 0.83333 | 0.83333 | 1.323 | 0
229 | 6 | 0 | 37 |  | 0.22457 | 2.5477 | -3.7536 | 2.9664 | 6.0494 | -1.5579 | 10.6463 | 0 | 30.8333 | 30.8333 | 48.951 | 0
229 | 7 | 2 | 92 |  | 0.22457 | 2.5477 | -3.7536 | 2.9664 | 7.0494 | -1.2961 | 19.7213 | 0.6598 | 76.6667 | 77.3265 | 122.7635 | 1
229 | 8 | 9 | 178 |  | 0.22457 | 2.5477 | -3.7536 | 2.9664 | 8.0494 | -1.0343 | 28.6343 | 4.911 | 148.3333 | 153.2443 | 243.2906 | 1
229 | 9 | 34 | 250 |  | 0.22457 | 2.5477 | -3.7536 | 2.9664 | 9.0494 | -0.77245 | 36.8985 | 24.823 | 208.3333 | 233.1564 | 370.1591 | 1
229 | 10 | 68 | 298 |  | 0.22457 | 2.5477 | -3.7536 | 2.9664 | 10.0494 | -0.51066 | 43.847 | 59.2018 | 248.3333 | 307.5351 | 488.2427 | 1
229 | 11 | 206 | 356 |  | 0.22457 | 2.5477 | -3.7536 | 2.9664 | 11.0494 | -0.24886 | 48.5844 | 197.2779 | 296.6667 | 493.9446 | 784.1864 | 1
229 | 12 | 93 | 352 |  | 0.22457 | 2.5477 | -3.7536 | 2.9664 | 12.0494 | 0.012943 | 50.1825 | 91.6323 | 293.3333 | 384.9657 | 611.1715 | 1
229 | 13 | 272 | 331 |  | 0.22457 | 2.5477 | -3.7536 | 2.9664 | 13.0494 | 0.27474 | 48.2425 | 258.8442 | 275.8333 | 534.6776 | 848.8541 | 1
229 | 14 | 78 | 336 |  | 0.22457 | 2.5477 | -3.7536 | 2.9664 | 14.0494 | 0.53654 | 43.2423 | 66.9998 | 280 | 346.9998 | 550.8969 | 1
229 | 15 | 327 | 291 |  | 0.22457 | 2.5477 | -3.7536 | 2.9664 | 15.0494 | 0.79834 | 36.1273 | 233.3553 | 242.5 | 475.8553 | 755.4679 | 1
229 | 16 | 169 | 247 |  | 0.22457 | 2.5477 | -3.7536 | 2.9664 | 16.0494 | 1.0601 | 27.7728 | 88.8089 | 205.8333 | 294.6423 | 467.7741 | 1
229 | 17 | 78 | 170 |  | 0.22457 | 2.5477 | -3.7536 | 2.9664 | 17.0494 | 1.3219 | 18.8242 | 23.9779 | 141.6667 | 165.6445 | 262.9773 | 1
229 | 18 | 0 | 86 |  | 0.22457 | 2.5477 | -3.7536 | 2.9664 | 18.0494 | 1.5837 | 9.7556 | 0 | 71.6667 | 71.6667 | 113.778 | 0
229 | 19 | 0 | 19 |  | 0.22457 | 2.5477 | -3.7536 | 2.9664 | 19.0494 | 1.8455 | 0.9595 | 0 | 15.8333 | 15.8333 | 25.137 | 0
229 | 20 | 0 | 0 |  | 0.22457 | 2.5477 | -3.7536 | 2.9664 | 20.0494 | 2.1073 | -7.1823 | 0 | 0 | 0 | 0 | 0
229 | 21 | 0 | 0 |  | 0.22457 | 2.5477 | -3.7536 | 2.9664 | 21.0494 | 2.3691 | -14.2533 | 0 | 0 | 0 | 0 | 0
229 | 22 | 0 | 0 |  | 0.22457 | 2.5477 | -3.7536 | 2.9664 | 22.0494 | 2.6309 | -19.7882 | 0 | 0 | 0 | 0 | 0
229 | 23 | 0 | 0 |  | 0.22457 | 2.5477 | -3.7536 | 2.9664 | 23.0494 | 2.8927 | -23.3122 | 0 | 0 | 0 | 0 | 0
229 | 24 | 0 | 0 |  | 0.22457 | 2.5477 | -3.7536 | 2.9664 | 24.0494 | 3.1545 | -24.4499 | 0 | 0 | 0 | 0 | 0
230 | 1 | 0 | 0 |  | 0.21872 | 2.5649 | -3.5281 | 3.1919 | 1.0532 | -2.8659 | -23.3854 | 0 | 0 | 0 | 0 | 0
230 | 2 | 0 | 0 |  | 0.21872 | 2.5649 | -3.5281 | 3.1919 | 2.0532 | -2.6041 | -19.6217 | 0 | 0 | 0 | 0 | 0
230 | 3 | 0 | 0 |  | 0.21872 | 2.5649 | -3.5281 | 3.1919 | 3.0532 | -2.3423 | -13.89 | 0 | 0 | 0 | 0 | 0
230 | 4 | 0 | 0 |  | 0.21872 | 2.5649 | -3.5281 | 3.1919 | 4.0532 | -2.0805 | -6.6723 | 0 | 0 | 0 | 0 | 0
230 | 5 | 0 | 1 |  | 0.21872 | 2.5649 | -3.5281 | 3.1919 | 5.0532 | -1.8187 | 1.5675 | 0 | 0.83333 | 0.83333 | 1.323 | 0
230 | 6 | 0 | 27 |  | 0.21872 | 2.5649 | -3.5281 | 3.1919 | 6.0532 | -1.5569 | 10.4162 | 0 | 22.5 | 22.5 | 35.721 | 0
230 | 7 | 193 | 109 |  | 0.21872 | 2.5649 | -3.5281 | 3.1919 | 7.0532 | -1.2951 | 19.492 | 63.4725 | 90.8333 | 154.3059 | 244.976 | 1
230 | 8 | 0 | 112 |  | 0.21872 | 2.5649 | -3.5281 | 3.1919 | 8.0532 | -1.0333 | 28.3968 | 0 | 93.3333 | 93.3333 | 148.176 | 1
230 | 9 | 101 | 212 |  | 0.21872 | 2.5649 | -3.5281 | 3.1919 | 9.0532 | -0.77147 | 36.6427 | 73.665 | 176.6667 | 250.3317 | 397.4265 | 1
230 | 10 | 472 | 248 |  | 0.21872 | 2.5649 | -3.5281 | 3.1919 | 10.0532 | -0.50967 | 43.5636 | 410.5839 | 206.6667 | 617.2506 | 979.947 | 1
230 | 11 | 583 | 218 |  | 0.21872 | 2.5649 | -3.5281 | 3.1919 | 11.0532 | -0.24787 | 48.2699 | 557.8299 | 181.6667 | 739.4965 | 1174.0247 | 1
230 | 12 | 554 | 261 |  | 0.21872 | 2.5649 | -3.5281 | 3.1919 | 12.0532 | 0.013927 | 49.8465 | 545.2841 | 217.5 | 762.7841 | 1210.996 | 1
230 | 13 | 643 | 228 |  | 0.21872 | 2.5649 | -3.5281 | 3.1919 | 13.0532 | 0.27573 | 47.904 | 611.0643 | 190 | 801.0643 | 1271.7697 | 1
230 | 14 | 717 | 163 |  | 0.21872 | 2.5649 | -3.5281 | 3.1919 | 14.0532 | 0.53753 | 42.9153 | 614.7108 | 135.8333 | 750.5441 | 1191.5638 | 1
230 | 15 | 706 | 138 |  | 0.21872 | 2.5649 | -3.5281 | 3.1919 | 15.0532 | 0.79933 | 35.8148 | 502.4013 | 115 | 617.4013 | 980.1862 | 1
230 | 16 | 482 | 180 |  | 0.21872 | 2.5649 | -3.5281 | 3.1919 | 16.0532 | 1.0611 | 27.4709 | 252.1351 | 150 | 402.1351 | 638.4296 | 1
230 | 17 | 218 | 169 |  | 0.21872 | 2.5649 | -3.5281 | 3.1919 | 17.0532 | 1.3229 | 18.5271 | 66.4115 | 140.8333 | 207.2449 | 329.022 | 1
230 | 18 | 0 | 84 |  | 0.21872 | 2.5649 | -3.5281 | 3.1919 | 18.0532 | 1.5847 | 9.4573 | 0 | 70 | 70 | 111.132 | 0
230 | 19 | 0 | 17 |  | 0.21872 | 2.5649 | -3.5281 | 3.1919 | 19.0532 | 1.8465 | 0.65505 | 0 | 14.1667 | 14.1667 | 22.491 | 0
230 | 20 | 0 | 0 |  | 0.21872 | 2.5649 | -3.5281 | 3.1919 | 20.0532 | 2.1083 | -7.4966 | 0 | 0 | 0 | 0 | 0
230 | 21 | 0 | 0 |  | 0.21872 | 2.5649 | -3.5281 | 3.1919 | 21.0532 | 2.3701 | -14.579 | 0 | 0 | 0 | 0 | 0
230 | 22 | 0 | 0 |  | 0.21872 | 2.5649 | -3.5281 | 3.1919 | 22.0532 | 2.6319 | -20.1239 | 0 | 0 | 0 | 0 | 0
230 | 23 | 0 | 0 |  | 0.21872 | 2.5649 | -3.5281 | 3.1919 | 23.0532 | 2.8937 | -23.652 | 0 | 0 | 0 | 0 | 0
230 | 24 | 0 | 0 |  | 0.21872 | 2.5649 | -3.5281 | 3.1919 | 24.0532 | 3.1555 | -24.7848 | 0 | 0 | 0 | 0 | 0
231 | 1 | 0 | 0 |  | 0.21281 | 2.5821 | -3.2935 | 3.4265 | 1.0571 | -2.8648 | -23.7082 | 0 | 0 | 0 | 0 | 0
231 | 2 | 0 | 0 |  | 0.21281 | 2.5821 | -3.2935 | 3.4265 | 2.0571 | -2.603 | -19.9225 | 0 | 0 | 0 | 0 | 0
231 | 3 | 0 | 0 |  | 0.21281 | 2.5821 | -3.2935 | 3.4265 | 3.0571 | -2.3412 | -14.1671 | 0 | 0 | 0 | 0 | 0
231 | 4 | 0 | 0 |  | 0.21281 | 2.5821 | -3.2935 | 3.4265 | 4.0571 | -2.0794 | -6.9283 | 0 | 0 | 0 | 0 | 0
231 | 5 | 0 | 1 |  | 0.21281 | 2.5821 | -3.2935 | 3.4265 | 5.0571 | -1.8176 | 1.3273 | 0 | 0.83333 | 0.83333 | 1.323 | 0
231 | 6 | 0 | 20 |  | 0.21281 | 2.5821 | -3.2935 | 3.4265 | 6.0571 | -1.5558 | 10.1847 | 0 | 16.6667 | 16.6667 | 26.46 | 0
231 | 7 | 204 | 91 |  | 0.21281 | 2.5821 | -3.2935 | 3.4265 | 7.0571 | -1.294 | 19.2612 | 66.8819 | 75.8333 | 142.7153 | 226.5748 | 1
231 | 8 | 30 | 165 |  | 0.21281 | 2.5821 | -3.2935 | 3.4265 | 8.0571 | -1.0322 | 28.1575 | 16.3198 | 137.5 | 153.8198 | 244.2043 | 1
231 | 9 | 172 | 245 |  | 0.21281 | 2.5821 | -3.2935 | 3.4265 | 9.0571 | -0.77045 | 36.3847 | 125.321 | 204.1667 | 329.4876 | 523.0946 | 1
231 | 10 | 71 | 292 |  | 0.21281 | 2.5821 | -3.2935 | 3.4265 | 10.0571 | -0.50865 | 43.2775 | 61.7078 | 243.3333 | 305.0411 | 484.2833 | 1
231 | 11 | 71 | 338 |  | 0.21281 | 2.5821 | -3.2935 | 3.4265 | 11.0571 | -0.24685 | 47.9524 | 67.873 | 281.6667 | 349.5397 | 554.9292 | 1
231 | 12 | 209 | 376 |  | 0.21281 | 2.5821 | -3.2935 | 3.4265 | 12.0571 | 0.014951 | 49.507 | 205.4878 | 313.3333 | 518.8211 | 823.6804 | 1
231 | 13 | 379 | 332 |  | 0.21281 | 2.5821 | -3.2935 | 3.4265 | 13.0571 | 0.27675 | 47.5616 | 359.6629 | 276.6667 | 636.3296 | 1010.2368 | 1
231 | 14 | 93 | 321 |  | 0.21281 | 2.5821 | -3.2935 | 3.4265 | 14.0571 | 0.53855 | 42.5842 | 79.5746 | 267.5 | 347.0746 | 551.0156 | 1
231 | 15 | 68 | 290 |  | 0.21281 | 2.5821 | -3.2935 | 3.4265 | 15.0571 | 0.80035 | 35.498 | 48.2489 | 241.6667 | 289.9155 | 460.2699 | 1
231 | 16 | 168 | 243 |  | 0.21281 | 2.5821 | -3.2935 | 3.4265 | 16.0571 | 1.0621 | 27.1648 | 87.4674 | 202.5 | 289.9674 | 460.3522 | 1
231 | 17 | 314 | 152 |  | 0.21281 | 2.5821 | -3.2935 | 3.4265 | 17.0571 | 1.3239 | 18.2257 | 94.7668 | 126.6667 | 221.4335 | 351.5477 | 1
231 | 18 | 121 | 107 |  | 0.21281 | 2.5821 | -3.2935 | 3.4265 | 18.0571 | 1.5857 | 9.1548 | 8.2224 | 89.1667 | 97.389 | 154.6148 | 0
231 | 19 | 0 | 28 |  | 0.21281 | 2.5821 | -3.2935 | 3.4265 | 19.0571 | 1.8475 | 0.34652 | 0 | 23.3333 | 23.3333 | 37.044 | 0
231 | 20 | 0 | 0 |  | 0.21281 | 2.5821 | -3.2935 | 3.4265 | 20.0571 | 2.1093 | -7.8149 | 0 | 0 | 0 | 0 | 0
231 | 21 | 0 | 0 |  | 0.21281 | 2.5821 | -3.2935 | 3.4265 | 21.0571 | 2.3711 | -14.9087 | 0 | 0 | 0 | 0 | 0
231 | 22 | 0 | 0 |  | 0.21281 | 2.5821 | -3.2935 | 3.4265 | 22.0571 | 2.6329 | -20.4634 | 0 | 0 | 0 | 0 | 0
231 | 23 | 0 | 0 |  | 0.21281 | 2.5821 | -3.2935 | 3.4265 | 23.0571 | 2.8947 | -23.9955 | 0 | 0 | 0 | 0 | 0
231 | 24 | 0 | 0 |  | 0.21281 | 2.5821 | -3.2935 | 3.4265 | 24.0571 | 3.1565 | -25.1229 | 0 | 0 | 0 | 0 | 0
232 | 1 | 0 | 0 |  | 0.20684 | 2.5993 | -3.05 | 3.67 | 1.0612 | -2.8638 | -24.0337 | 0 | 0 | 0 | 0 | 0
232 | 2 | 0 | 0 |  | 0.20684 | 2.5993 | -3.05 | 3.67 | 2.0612 | -2.602 | -20.2254 | 0 | 0 | 0 | 0 | 0
232 | 3 | 0 | 0 |  | 0.20684 | 2.5993 | -3.05 | 3.67 | 3.0612 | -2.3402 | -14.4459 | 0 | 0 | 0 | 0 | 0
232 | 4 | 0 | 0 |  | 0.20684 | 2.5993 | -3.05 | 3.67 | 4.0612 | -2.0784 | -7.1857 | 0 | 0 | 0 | 0 | 0
232 | 5 | 0 | 1 |  | 0.20684 | 2.5993 | -3.05 | 3.67 | 5.0612 | -1.8166 | 1.0857 | 0 | 0.83333 | 0.83333 | 1.323 | 0
232 | 6 | 0 | 24 |  | 0.20684 | 2.5993 | -3.05 | 3.67 | 6.0612 | -1.5548 | 9.9519 | 0 | 20 | 20 | 31.752 | 0
232 | 7 | 0 | 87 |  | 0.20684 | 2.5993 | -3.05 | 3.67 | 7.0612 | -1.293 | 19.029 | 0 | 72.5 | 72.5 | 115.101 | 1
232 | 8 | 9 | 172 |  | 0.20684 | 2.5993 | -3.05 | 3.67 | 8.0612 | -1.0312 | 27.9163 | 4.8884 | 143.3333 | 148.2217 | 235.3168 | 1
232 | 9 | 34 | 245 |  | 0.20684 | 2.5993 | -3.05 | 3.67 | 9.0612 | -0.76938 | 36.1245 | 24.7469 | 204.1667 | 228.9136 | 363.4232 | 1
232 | 10 | 68 | 293 |  | 0.20684 | 2.5993 | -3.05 | 3.67 | 10.0612 | -0.50759 | 42.9888 | 59.0472 | 244.1667 | 303.2139 | 481.3824 | 1
232 | 11 | 87 | 327 |  | 0.20684 | 2.5993 | -3.05 | 3.67 | 11.0612 | -0.24579 | 47.632 | 83.0897 | 272.5 | 355.5897 | 564.5341 | 1
232 | 12 | 73 | 360 |  | 0.20684 | 2.5993 | -3.05 | 3.67 | 12.0612 | 0.016013 | 49.1643 | 71.6916 | 300 | 371.6916 | 590.0975 | 1
232 | 13 | 218 | 368 |  | 0.20684 | 2.5993 | -3.05 | 3.67 | 13.0612 | 0.27781 | 47.2155 | 206.57 | 306.6667 | 513.2366 | 814.8145 | 1
232 | 14 | 79 | 330 |  | 0.20684 | 2.5993 | -3.05 | 3.67 | 14.0612 | 0.53961 | 42.249 | 67.4567 | 275 | 342.4567 | 543.6842 | 1
232 | 15 | 67 | 287 |  | 0.20684 | 2.5993 | -3.05 | 3.67 | 15.0612 | 0.80141 | 35.1771 | 47.3959 | 239.1667 | 286.5626 | 454.9467 | 1
232 | 16 | 33 | 237 |  | 0.20684 | 2.5993 | -3.05 | 3.67 | 16.0612 | 1.0632 | 26.8545 | 17.0976 | 197.5 | 214.5976 | 340.6951 | 1
232 | 17 | 21 | 159 |  | 0.20684 | 2.5993 | -3.05 | 3.67 | 17.0612 | 1.325 | 17.9202 | 6.277 | 132.5 | 138.777 | 220.3224 | 1
232 | 18 | 0 | 79 |  | 0.20684 | 2.5993 | -3.05 | 3.67 | 18.0612 | 1.5868 | 8.8483 | 0 | 65.8333 | 65.8333 | 104.517 | 0
232 | 19 | 0 | 15 |  | 0.20684 | 2.5993 | -3.05 | 3.67 | 19.0612 | 1.8486 | 0.034023 | 0 | 12.5 | 12.5 | 19.845 | 0
232 | 20 | 0 | 0 |  | 0.20684 | 2.5993 | -3.05 | 3.67 | 20.0612 | 2.1104 | -8.1371 | 0 | 0 | 0 | 0 | 0
232 | 21 | 0 | 0 |  | 0.20684 | 2.5993 | -3.05 | 3.67 | 21.0612 | 2.3722 | -15.2423 | 0 | 0 | 0 | 0 | 0
232 | 22 | 0 | 0 |  | 0.20684 | 2.5993 | -3.05 | 3.67 | 22.0612 | 2.634 | -20.8066 | 0 | 0 | 0 | 0 | 0
232 | 23 | 0 | 0 |  | 0.20684 | 2.5993 | -3.05 | 3.67 | 23.0612 | 2.8958 | -24.3426 | 0 | 0 | 0 | 0 | 0
232 | 24 | 0 | 0 |  | 0.20684 | 2.5993 | -3.05 | 3.67 | 24.0612 | 3.1576 | -25.4642 | 0 | 0 | 0 | 0 | 0
233 | 1 | 0 | 0 |  | 0.20082 | 2.6166 | -2.7979 | 3.9221 | 1.0654 | -2.8627 | -24.3617 | 0 | 0 | 0 | 0 | 0
233 | 2 | 0 | 0 |  | 0.20082 | 2.6166 | -2.7979 | 3.9221 | 2.0654 | -2.6009 | -20.5303 | 0 | 0 | 0 | 0 | 0
233 | 3 | 0 | 0 |  | 0.20082 | 2.6166 | -2.7979 | 3.9221 | 3.0654 | -2.3391 | -14.7262 | 0 | 0 | 0 | 0 | 0
233 | 4 | 0 | 0 |  | 0.20082 | 2.6166 | -2.7979 | 3.9221 | 4.0654 | -2.0773 | -7.4444 | 0 | 0 | 0 | 0 | 0
233 | 5 | 0 | 0 |  | 0.20082 | 2.6166 | -2.7979 | 3.9221 | 5.0654 | -1.8155 | 0.84298 | 0 | 0 | 0 | 0 | 0
233 | 6 | 0 | 11 |  | 0.20082 | 2.6166 | -2.7979 | 3.9221 | 6.0654 | -1.5537 | 9.7178 | 0 | 9.1667 | 9.1667 | 14.553 | 0
233 | 7 | 0 | 85 |  | 0.20082 | 2.6166 | -2.7979 | 3.9221 | 7.0654 | -1.2919 | 18.7952 | 0 | 70.8333 | 70.8333 | 112.455 | 1
233 | 8 | 9 | 170 |  | 0.20082 | 2.6166 | -2.7979 | 3.9221 | 8.0654 | -1.0301 | 27.6735 | 4.8808 | 141.6667 | 146.5475 | 232.6587 | 1
233 | 9 | 364 | 231 |  | 0.20082 | 2.6166 | -2.7979 | 3.9221 | 9.0654 | -0.76828 | 35.8621 | 264.6556 | 192.5 | 457.1556 | 725.7802 | 1
233 | 10 | 600 | 192 |  | 0.20082 | 2.6166 | -2.7979 | 3.9221 | 10.0654 | -0.50649 | 42.6975 | 520.5201 | 160 | 680.5201 | 1080.3938 | 1
233 | 11 | 678 | 177 |  | 0.20082 | 2.6166 | -2.7979 | 3.9221 | 11.0654 | -0.24469 | 47.3086 | 646.8878 | 147.5 | 794.3878 | 1261.1701 | 1
233 | 12 | 374 | 334 |  | 0.20082 | 2.6166 | -2.7979 | 3.9221 | 12.0654 | 0.017113 | 48.8183 | 366.8605 | 278.3333 | 645.1938 | 1024.3097 | 1
233 | 13 | 544 | 263 |  | 0.20082 | 2.6166 | -2.7979 | 3.9221 | 13.0654 | 0.27891 | 46.8658 | 514.68 | 219.1667 | 733.8467 | 1165.055 | 1
233 | 14 | 658 | 191 |  | 0.20082 | 2.6166 | -2.7979 | 3.9221 | 14.0654 | 0.54071 | 41.91 | 560.6565 | 159.1667 | 719.8232 | 1142.7913 | 1
233 | 15 | 501 | 217 |  | 0.20082 | 2.6166 | -2.7979 | 3.9221 | 15.0654 | 0.80251 | 34.8521 | 353.3027 | 180.8333 | 534.136 | 847.9943 | 1
233 | 16 | 450 | 176 |  | 0.20082 | 2.6166 | -2.7979 | 3.9221 | 16.0654 | 1.0643 | 26.54 | 231.9804 | 146.6667 | 378.6471 | 601.1401 | 1
233 | 17 | 336 | 137 |  | 0.20082 | 2.6166 | -2.7979 | 3.9221 | 17.0654 | 1.3261 | 17.6107 | 99.4355 | 114.1667 | 213.6022 | 339.1148 | 1
233 | 18 | 97 | 91 |  | 0.20082 | 2.6166 | -2.7979 | 3.9221 | 18.0654 | 1.5879 | 8.5379 | 5.9597 | 75.8333 | 81.793 | 129.8546 | 0
233 | 19 | 0 | 20 |  | 0.20082 | 2.6166 | -2.7979 | 3.9221 | 19.0654 | 1.8497 | -0.28233 | 0 | 16.6667 | 16.6667 | 26.46 | 0
233 | 20 | 0 | 0 |  | 0.20082 | 2.6166 | -2.7979 | 3.9221 | 20.0654 | 2.1115 | -8.4631 | 0 | 0 | 0 | 0 | 0
233 | 21 | 0 | 0 |  | 0.20082 | 2.6166 | -2.7979 | 3.9221 | 21.0654 | 2.3733 | -15.5796 | 0 | 0 | 0 | 0 | 0
233 | 22 | 0 | 0 |  | 0.20082 | 2.6166 | -2.7979 | 3.9221 | 22.0654 | 2.6351 | -21.1536 | 0 | 0 | 0 | 0 | 0
233 | 23 | 0 | 0 |  | 0.20082 | 2.6166 | -2.7979 | 3.9221 | 23.0654 | 2.8969 | -24.6931 | 0 | 0 | 0 | 0 | 0
233 | 24 | 0 | 0 |  | 0.20082 | 2.6166 | -2.7979 | 3.9221 | 24.0654 | 3.1587 | -25.8086 | 0 | 0 | 0 | 0 | 0
234 | 1 | 0 | 0 |  | 0.19474 | 2.6338 | -2.5373 | 4.1827 | 1.0697 | -2.8615 | -24.6921 | 0 | 0 | 0 | 0 | 0
234 | 2 | 0 | 0 |  | 0.19474 | 2.6338 | -2.5373 | 4.1827 | 2.0697 | -2.5997 | -20.8371 | 0 | 0 | 0 | 0 | 0
234 | 3 | 0 | 0 |  | 0.19474 | 2.6338 | -2.5373 | 4.1827 | 3.0697 | -2.3379 | -15.008 | 0 | 0 | 0 | 0 | 0
234 | 4 | 0 | 0 |  | 0.19474 | 2.6338 | -2.5373 | 4.1827 | 4.0697 | -2.0761 | -7.7043 | 0 | 0 | 0 | 0 | 0
234 | 5 | 0 | 0 |  | 0.19474 | 2.6338 | -2.5373 | 4.1827 | 5.0697 | -1.8143 | 0.59908 | 0 | 0 | 0 | 0 | 0
234 | 6 | 0 | 17 |  | 0.19474 | 2.6338 | -2.5373 | 4.1827 | 6.0697 | -1.5525 | 9.4825 | 0 | 14.1667 | 14.1667 | 22.491 | 0
234 | 7 | 0 | 83 |  | 0.19474 | 2.6338 | -2.5373 | 4.1827 | 7.0697 | -1.2907 | 18.5601 | 0 | 69.1667 | 69.1667 | 109.809 | 1
234 | 8 | 20 | 162 |  | 0.19474 | 2.6338 | -2.5373 | 4.1827 | 8.0697 | -1.0289 | 27.4288 | 10.8292 | 135 | 145.8292 | 231.5185 | 1
234 | 9 | 33 | 240 |  | 0.19474 | 2.6338 | -2.5373 | 4.1827 | 9.0697 | -0.76715 | 35.5976 | 23.9674 | 200 | 223.9674 | 355.5707 | 1
234 | 10 | 191 | 302 |  | 0.19474 | 2.6338 | -2.5373 | 4.1827 | 10.0697 | -0.50535 | 42.4038 | 165.5394 | 251.6667 | 417.2061 | 662.3564 | 1
234 | 11 | 524 | 283 |  | 0.19474 | 2.6338 | -2.5373 | 4.1827 | 11.0697 | -0.24355 | 46.9825 | 499.4413 | 235.8333 | 735.2747 | 1167.3221 | 1
234 | 12 | 760 | 156 |  | 0.19474 | 2.6338 | -2.5373 | 4.1827 | 12.0697 | 0.01825 | 48.4692 | 744.5694 | 130 | 874.5694 | 1388.4664 | 1
234 | 13 | 669 | 197 |  | 0.19474 | 2.6338 | -2.5373 | 4.1827 | 13.0697 | 0.28005 | 46.5126 | 631.9247 | 164.1667 | 796.0914 | 1263.8747 | 1
234 | 14 | 188 | 352 |  | 0.19474 | 2.6338 | -2.5373 | 4.1827 | 14.0697 | 0.54185 | 41.5671 | 159.8336 | 293.3333 | 453.1669 | 719.4478 | 1
234 | 15 | 69 | 279 |  | 0.19474 | 2.6338 | -2.5373 | 4.1827 | 15.0697 | 0.80365 | 34.5231 | 48.5017 | 232.5 | 281.0017 | 446.1183 | 1
234 | 16 | 0 | 155 |  | 0.19474 | 2.6338 | -2.5373 | 4.1827 | 16.0697 | 1.0654 | 26.2217 | 0 | 129.1667 | 129.1667 | 205.065 | 1
234 | 17 | 25 | 151 |  | 0.19474 | 2.6338 | -2.5373 | 4.1827 | 17.0697 | 1.3272 | 17.2972 | 7.3228 | 125.8333 | 133.1561 | 211.3986 | 1
234 | 18 | 203 | 79 |  | 0.19474 | 2.6338 | -2.5373 | 4.1827 | 18.0697 | 1.589 | 8.2237 | 11.7933 | 65.8333 | 77.6266 | 123.2401 | 0
234 | 19 | 0 | 22 |  | 0.19474 | 2.6338 | -2.5373 | 4.1827 | 19.0697 | 1.8508 | -0.60243 | 0 | 18.3333 | 18.3333 | 29.106 | 0
234 | 20 | 0 | 0 |  | 0.19474 | 2.6338 | -2.5373 | 4.1827 | 20.0697 | 2.1126 | -8.7928 | 0 | 0 | 0 | 0 | 0
234 | 21 | 0 | 0 |  | 0.19474 | 2.6338 | -2.5373 | 4.1827 | 21.0697 | 2.3744 | -15.9206 | 0 | 0 | 0 | 0 | 0
234 | 22 | 0 | 0 |  | 0.19474 | 2.6338 | -2.5373 | 4.1827 | 22.0697 | 2.6362 | -21.504 | 0 | 0 | 0 | 0 | 0
234 | 23 | 0 | 0 |  | 0.19474 | 2.6338 | -2.5373 | 4.1827 | 23.0697 | 2.898 | -25.0469 | 0 | 0 | 0 | 0 | 0
234 | 24 | 0 | 0 |  | 0.19474 | 2.6338 | -2.5373 | 4.1827 | 24.0697 | 3.1598 | -26.1559 | 0 | 0 | 0 | 0 | 0
235 | 1 | 0 | 0 |  | 0.18861 | 2.651 | -2.2686 | 4.4514 | 1.0742 | -2.8604 | -25.0248 | 0 | 0 | 0 | 0 | 0
235 | 2 | 0 | 0 |  | 0.18861 | 2.651 | -2.2686 | 4.4514 | 2.0742 | -2.5986 | -21.1457 | 0 | 0 | 0 | 0 | 0
235 | 3 | 0 | 0 |  | 0.18861 | 2.651 | -2.2686 | 4.4514 | 3.0742 | -2.3368 | -15.2912 | 0 | 0 | 0 | 0 | 0
235 | 4 | 0 | 0 |  | 0.18861 | 2.651 | -2.2686 | 4.4514 | 4.0742 | -2.075 | -7.9654 | 0 | 0 | 0 | 0 | 0
235 | 5 | 0 | 0 |  | 0.18861 | 2.651 | -2.2686 | 4.4514 | 5.0742 | -1.8132 | 0.35409 | 0 | 0 | 0 | 0 | 0
235 | 6 | 0 | 20 |  | 0.18861 | 2.651 | -2.2686 | 4.4514 | 6.0742 | -1.5514 | 9.2461 | 0 | 16.6667 | 16.6667 | 26.46 | 0
235 | 7 | 0 | 81 |  | 0.18861 | 2.651 | -2.2686 | 4.4514 | 7.0742 | -1.2896 | 18.3235 | 0 | 67.5 | 67.5 | 107.163 | 1
235 | 8 | 43 | 151 |  | 0.18861 | 2.651 | -2.2686 | 4.4514 | 8.0742 | -1.0278 | 27.1825 | 23.2462 | 125.8333 | 149.0795 | 236.6786 | 1
235 | 9 | 26 | 241 |  | 0.18861 | 2.651 | -2.2686 | 4.4514 | 9.0742 | -0.76598 | 35.3311 | 18.8625 | 200.8333 | 219.6958 | 348.789 | 1
235 | 10 | 342 | 270 |  | 0.18861 | 2.651 | -2.2686 | 4.4514 | 10.0742 | -0.50418 | 42.1076 | 296.1158 | 225 | 521.1158 | 827.3235 | 1
235 | 11 | 687 | 180 |  | 0.18861 | 2.651 | -2.2686 | 4.4514 | 11.0742 | -0.24238 | 46.6536 | 654.1024 | 150 | 804.1024 | 1276.593 | 1
235 | 12 | 736 | 153 |  | 0.18861 | 2.651 | -2.2686 | 4.4514 | 12.0742 | 0.019423 | 48.1171 | 720.1276 | 127.5 | 847.6276 | 1345.6936 | 1
235 | 13 | 634 | 211 |  | 0.18861 | 2.651 | -2.2686 | 4.4514 | 13.0742 | 0.28122 | 46.1561 | 597.8636 | 175.8333 | 773.697 | 1228.3213 | 1
235 | 14 | 547 | 226 |  | 0.18861 | 2.651 | -2.2686 | 4.4514 | 14.0742 | 0.54302 | 41.2206 | 463.9838 | 188.3333 | 652.3171 | 1035.6187 | 1
235 | 15 | 65 | 280 |  | 0.18861 | 2.651 | -2.2686 | 4.4514 | 15.0742 | 0.80482 | 34.1903 | 45.5381 | 233.3333 | 278.8714 | 442.7363 | 1
235 | 16 | 32 | 229 |  | 0.18861 | 2.651 | -2.2686 | 4.4514 | 16.0742 | 1.0666 | 25.8995 | 16.3239 | 190.8333 | 207.1572 | 328.8828 | 1
235 | 17 | 210 | 155 |  | 0.18861 | 2.651 | -2.2686 | 4.4514 | 17.0742 | 1.3284 | 16.9801 | 60.8621 | 129.1667 | 190.0287 | 301.6896 | 1
235 | 18 | 0 | 71 |  | 0.18861 | 2.651 | -2.2686 | 4.4514 | 18.0742 | 1.5902 | 7.9057 | 0 | 59.1667 | 59.1667 | 93.933 | 0
235 | 19 | 0 | 12 |  | 0.18861 | 2.651 | -2.2686 | 4.4514 | 19.0742 | 1.852 | -0.92615 | 0 | 10 | 10 | 15.876 | 0
235 | 20 | 0 | 0 |  | 0.18861 | 2.651 | -2.2686 | 4.4514 | 20.0742 | 2.1138 | -9.1261 | 0 | 0 | 0 | 0 | 0
235 | 21 | 0 | 0 |  | 0.18861 | 2.651 | -2.2686 | 4.4514 | 21.0742 | 2.3756 | -16.2651 | 0 | 0 | 0 | 0 | 0
235 | 22 | 0 | 0 |  | 0.18861 | 2.651 | -2.2686 | 4.4514 | 22.0742 | 2.6374 | -21.8579 | 0 | 0 | 0 | 0 | 0
235 | 23 | 0 | 0 |  | 0.18861 | 2.651 | -2.2686 | 4.4514 | 23.0742 | 2.8992 | -25.404 | 0 | 0 | 0 | 0 | 0
235 | 24 | 0 | 0 |  | 0.18861 | 2.651 | -2.2686 | 4.4514 | 24.0742 | 3.161 | -26.506 | 0 | 0 | 0 | 0 | 0
236 | 1 | 0 | 0 |  | 0.18244 | 2.6682 | -1.9918 | 4.7282 | 1.0788 | -2.8592 | -25.3598 | 0 | 0 | 0 | 0 | 0
236 | 2 | 0 | 0 |  | 0.18244 | 2.6682 | -1.9918 | 4.7282 | 2.0788 | -2.5974 | -21.456 | 0 | 0 | 0 | 0 | 0
236 | 3 | 0 | 0 |  | 0.18244 | 2.6682 | -1.9918 | 4.7282 | 3.0788 | -2.3356 | -15.5757 | 0 | 0 | 0 | 0 | 0
236 | 4 | 0 | 0 |  | 0.18244 | 2.6682 | -1.9918 | 4.7282 | 4.0788 | -2.0738 | -8.2276 | 0 | 0 | 0 | 0 | 0
236 | 5 | 0 | 0 |  | 0.18244 | 2.6682 | -1.9918 | 4.7282 | 5.0788 | -1.812 | 0.10806 | 0 | 0 | 0 | 0 | 0
236 | 6 | 0 | 25 |  | 0.18244 | 2.6682 | -1.9918 | 4.7282 | 6.0788 | -1.5502 | 9.0085 | 0 | 20.8333 | 20.8333 | 33.075 | 0
236 | 7 | 227 | 82 |  | 0.18244 | 2.6682 | -1.9918 | 4.7282 | 7.0788 | -1.2884 | 18.0857 | 73.2819 | 68.3333 | 141.6153 | 224.8284 | 1
236 | 8 | 368 | 143 |  | 0.18244 | 2.6682 | -1.9918 | 4.7282 | 8.0788 | -1.0266 | 26.9346 | 198.6278 | 119.1667 | 317.7944 | 504.5305 | 1
236 | 9 | 173 | 236 |  | 0.18244 | 2.6682 | -1.9918 | 4.7282 | 9.0788 | -0.76477 | 35.0625 | 125.3654 | 196.6667 | 322.032 | 511.258 | 1
236 | 10 | 341 | 274 |  | 0.18244 | 2.6682 | -1.9918 | 4.7282 | 10.0788 | -0.50297 | 41.8091 | 294.946 | 228.3333 | 523.2794 | 830.7583 | 1
236 | 11 | 93 | 315 |  | 0.18244 | 2.6682 | -1.9918 | 4.7282 | 11.0788 | -0.24117 | 46.322 | 88.4482 | 262.5 | 350.9482 | 557.1654 | 1
236 | 12 | 89 | 341 |  | 0.18244 | 2.6682 | -1.9918 | 4.7282 | 12.0788 | 0.02063 | 47.7621 | 86.9639 | 284.1667 | 371.1306 | 589.2069 | 1
236 | 13 | 89 | 340 |  | 0.18244 | 2.6682 | -1.9918 | 4.7282 | 13.0788 | 0.28243 | 45.7963 | 83.7817 | 283.3333 | 367.115 | 582.8318 | 1
236 | 14 | 87 | 315 |  | 0.18244 | 2.6682 | -1.9918 | 4.7282 | 14.0788 | 0.54423 | 40.8705 | 73.6217 | 262.5 | 336.1217 | 533.6268 | 1
236 | 15 | 200 | 287 |  | 0.18244 | 2.6682 | -1.9918 | 4.7282 | 15.0788 | 0.80603 | 33.8538 | 139.6368 | 239.1667 | 378.8035 | 601.3884 | 1
236 | 16 | 431 | 201 |  | 0.18244 | 2.6682 | -1.9918 | 4.7282 | 16.0788 | 1.0678 | 25.5736 | 218.6588 | 167.5 | 386.1588 | 613.0657 | 1
236 | 17 | 124 | 154 |  | 0.18244 | 2.6682 | -1.9918 | 4.7282 | 17.0788 | 1.3296 | 16.6592 | 35.5468 | 128.3333 | 163.8801 | 260.1761 | 1
236 | 18 | 15 | 86 |  | 0.18244 | 2.6682 | -1.9918 | 4.7282 | 18.0788 | 1.5914 | 7.5842 | 0.76856 | 71.6667 | 72.4352 | 114.9982 | 0
236 | 19 | 0 | 11 |  | 0.18244 | 2.6682 | -1.9918 | 4.7282 | 19.0788 | 1.8532 | -1.2534 | 0 | 9.1667 | 9.1667 | 14.553 | 0
236 | 20 | 0 | 0 |  | 0.18244 | 2.6682 | -1.9918 | 4.7282 | 20.0788 | 2.115 | -9.4628 | 0 | 0 | 0 | 0 | 0
236 | 21 | 0 | 0 |  | 0.18244 | 2.6682 | -1.9918 | 4.7282 | 21.0788 | 2.3768 | -16.613 | 0 | 0 | 0 | 0 | 0
236 | 22 | 0 | 0 |  | 0.18244 | 2.6682 | -1.9918 | 4.7282 | 22.0788 | 2.6386 | -22.2152 | 0 | 0 | 0 | 0 | 0
236 | 23 | 0 | 0 |  | 0.18244 | 2.6682 | -1.9918 | 4.7282 | 23.0788 | 2.9004 | -25.7642 | 0 | 0 | 0 | 0 | 0
236 | 24 | 0 | 0 |  | 0.18244 | 2.6682 | -1.9918 | 4.7282 | 24.0788 | 3.1622 | -26.8589 | 0 | 0 | 0 | 0 | 0
237 | 1 | 0 | 0 |  | 0.17621 | 2.6854 | -1.7074 | 5.0126 | 1.0835 | -2.8579 | -25.6969 | 0 | 0 | 0 | 0 | 0
237 | 2 | 0 | 0 |  | 0.17621 | 2.6854 | -1.7074 | 5.0126 | 2.0835 | -2.5961 | -21.7679 | 0 | 0 | 0 | 0 | 0
237 | 3 | 0 | 0 |  | 0.17621 | 2.6854 | -1.7074 | 5.0126 | 3.0835 | -2.3343 | -15.8615 | 0 | 0 | 0 | 0 | 0
237 | 4 | 0 | 0 |  | 0.17621 | 2.6854 | -1.7074 | 5.0126 | 4.0835 | -2.0725 | -8.4908 | 0 | 0 | 0 | 0 | 0
237 | 5 | 0 | 0 |  | 0.17621 | 2.6854 | -1.7074 | 5.0126 | 5.0835 | -1.8107 | -0.13895 | 0 | 0 | 0 | 0 | 0
237 | 6 | 0 | 23 |  | 0.17621 | 2.6854 | -1.7074 | 5.0126 | 6.0835 | -1.5489 | 8.7699 | 0 | 19.1667 | 19.1667 | 30.429 | 0
237 | 7 | 207 | 84 |  | 0.17621 | 2.6854 | -1.7074 | 5.0126 | 7.0835 | -1.2871 | 17.8465 | 66.6198 | 70 | 136.6198 | 216.8976 | 1
237 | 8 | 396 | 137 |  | 0.17621 | 2.6854 | -1.7074 | 5.0126 | 8.0835 | -1.0253 | 26.685 | 213.3975 | 114.1667 | 327.5642 | 520.0409 | 1
237 | 9 | 330 | 203 |  | 0.17621 | 2.6854 | -1.7074 | 5.0126 | 9.0835 | -0.76353 | 34.7919 | 238.8583 | 169.1667 | 408.025 | 647.7805 | 1
237 | 10 | 66 | 283 |  | 0.17621 | 2.6854 | -1.7074 | 5.0126 | 10.0835 | -0.50173 | 41.5082 | 57.0255 | 235.8333 | 292.8589 | 464.9428 | 1
237 | 11 | 71 | 327 |  | 0.17621 | 2.6854 | -1.7074 | 5.0126 | 11.0835 | -0.23993 | 45.9879 | 67.447 | 272.5 | 339.947 | 539.6999 | 1
237 | 12 | 73 | 349 |  | 0.17621 | 2.6854 | -1.7074 | 5.0126 | 12.0835 | 0.021872 | 47.4043 | 71.2306 | 290.8333 | 362.0639 | 574.8127 | 1
237 | 13 | 72 | 347 |  | 0.17621 | 2.6854 | -1.7074 | 5.0126 | 13.0835 | 0.28367 | 45.4334 | 67.6566 | 289.1667 | 356.8233 | 566.4926 | 1
237 | 14 | 70 | 322 |  | 0.17621 | 2.6854 | -1.7074 | 5.0126 | 14.0835 | 0.54547 | 40.517 | 59.091 | 268.3333 | 327.4243 | 519.8189 | 1
237 | 15 | 66 | 275 |  | 0.17621 | 2.6854 | -1.7074 | 5.0126 | 15.0835 | 0.80727 | 33.5138 | 45.9174 | 229.1667 | 275.0841 | 436.7235 | 1
237 | 16 | 165 | 225 |  | 0.17621 | 2.6854 | -1.7074 | 5.0126 | 16.0835 | 1.0691 | 25.2441 | 83.2381 | 187.5 | 270.7381 | 429.8238 | 1
237 | 17 | 106 | 156 |  | 0.17621 | 2.6854 | -1.7074 | 5.0126 | 17.0835 | 1.3309 | 16.3348 | 30.0463 | 130 | 160.0463 | 254.0896 | 1
237 | 18 | 0 | 66 |  | 0.17621 | 2.6854 | -1.7074 | 5.0126 | 18.0835 | 1.5927 | 7.2592 | 0 | 55 | 55 | 87.318 | 0
237 | 19 | 0 | 15 |  | 0.17621 | 2.6854 | -1.7074 | 5.0126 | 19.0835 | 1.8545 | -1.584 | 0 | 12.5 | 12.5 | 19.845 | 0
237 | 20 | 0 | 0 |  | 0.17621 | 2.6854 | -1.7074 | 5.0126 | 20.0835 | 2.1163 | -9.8029 | 0 | 0 | 0 | 0 | 0
237 | 21 | 0 | 0 |  | 0.17621 | 2.6854 | -1.7074 | 5.0126 | 21.0835 | 2.3781 | -16.9641 | 0 | 0 | 0 | 0 | 0
237 | 22 | 0 | 0 |  | 0.17621 | 2.6854 | -1.7074 | 5.0126 | 22.0835 | 2.6399 | -22.5756 | 0 | 0 | 0 | 0 | 0
237 | 23 | 0 | 0 |  | 0.17621 | 2.6854 | -1.7074 | 5.0126 | 23.0835 | 2.9017 | -26.1273 | 0 | 0 | 0 | 0 | 0
237 | 24 | 0 | 0 |  | 0.17621 | 2.6854 | -1.7074 | 5.0126 | 24.0835 | 3.1635 | -27.2145 | 0 | 0 | 0 | 0 | 0
238 | 1 | 0 | 0 |  | 0.16995 | 2.7026 | -1.4155 | 5.3045 | 1.0884 | -2.8566 | -26.0361 | 0 | 0 | 0 | 0 | 0
238 | 2 | 0 | 0 |  | 0.16995 | 2.7026 | -1.4155 | 5.3045 | 2.0884 | -2.5948 | -22.0814 | 0 | 0 | 0 | 0 | 0
238 | 3 | 0 | 0 |  | 0.16995 | 2.7026 | -1.4155 | 5.3045 | 3.0884 | -2.333 | -16.1484 | 0 | 0 | 0 | 0 | 0
238 | 4 | 0 | 0 |  | 0.16995 | 2.7026 | -1.4155 | 5.3045 | 4.0884 | -2.0712 | -8.7549 | 0 | 0 | 0 | 0 | 0
238 | 5 | 0 | 0 |  | 0.16995 | 2.7026 | -1.4155 | 5.3045 | 5.0884 | -1.8095 | -0.38689 | 0 | 0 | 0 | 0 | 0
238 | 6 | 0 | 13 |  | 0.16995 | 2.7026 | -1.4155 | 5.3045 | 6.0884 | -1.5477 | 8.5302 | 0 | 10.8333 | 10.8333 | 17.199 | 0
238 | 7 | 0 | 76 |  | 0.16995 | 2.7026 | -1.4155 | 5.3045 | 7.0884 | -1.2859 | 17.606 | 0 | 63.3333 | 63.3333 | 100.548 | 1
238 | 8 | 19 | 155 |  | 0.16995 | 2.7026 | -1.4155 | 5.3045 | 8.0884 | -1.0241 | 26.4338 | 10.2222 | 129.1667 | 139.3888 | 221.2937 | 1
238 | 9 | 33 | 232 |  | 0.16995 | 2.7026 | -1.4155 | 5.3045 | 9.0884 | -0.76225 | 34.5194 | 23.8574 | 193.3333 | 217.1907 | 344.812 | 1
238 | 10 | 5 | 199 |  | 0.16995 | 2.7026 | -1.4155 | 5.3045 | 10.0884 | -0.50045 | 41.205 | 4.3154 | 165.8333 | 170.1487 | 270.1281 | 1
238 | 11 | 6 | 230 |  | 0.16995 | 2.7026 | -1.4155 | 5.3045 | 11.0884 | -0.23865 | 45.6512 | 5.6929 | 191.6667 | 197.3596 | 313.3281 | 1
238 | 12 | 71 | 347 |  | 0.16995 | 2.7026 | -1.4155 | 5.3045 | 12.0884 | 0.023145 | 47.0437 | 69.1789 | 289.1667 | 358.3455 | 568.9094 | 1
238 | 13 | 72 | 345 |  | 0.16995 | 2.7026 | -1.4155 | 5.3045 | 13.0884 | 0.28494 | 45.0675 | 67.5306 | 287.5 | 355.0306 | 563.6466 | 1
238 | 14 | 339 | 315 |  | 0.16995 | 2.7026 | -1.4155 | 5.3045 | 14.0884 | 0.54674 | 40.1602 | 285.4469 | 262.5 | 547.9469 | 869.9204 | 1
238 | 15 | 574 | 187 |  | 0.16995 | 2.7026 | -1.4155 | 5.3045 | 15.0884 | 0.80854 | 33.1703 | 397.8902 | 155.8333 | 553.7236 | 879.0915 | 1
238 | 16 | 566 | 136 |  | 0.16995 | 2.7026 | -1.4155 | 5.3045 | 16.0884 | 1.0703 | 24.9111 | 283.8804 | 113.3333 | 397.2137 | 630.6165 | 1
238 | 17 | 335 | 134 |  | 0.16995 | 2.7026 | -1.4155 | 5.3045 | 17.0884 | 1.3321 | 16.007 | 93.8625 | 111.6667 | 205.5291 | 326.298 | 1
238 | 18 | 0 | 64 |  | 0.16995 | 2.7026 | -1.4155 | 5.3045 | 18.0884 | 1.5939 | 6.9309 | 0 | 53.3333 | 53.3333 | 84.672 | 0
238 | 19 | 0 | 16 |  | 0.16995 | 2.7026 | -1.4155 | 5.3045 | 19.0884 | 1.8557 | -1.9179 | 0 | 13.3333 | 13.3333 | 21.168 | 0
238 | 20 | 0 | 0 |  | 0.16995 | 2.7026 | -1.4155 | 5.3045 | 20.0884 | 2.1175 | -10.1462 | 0 | 0 | 0 | 0 | 0
238 | 21 | 0 | 0 |  | 0.16995 | 2.7026 | -1.4155 | 5.3045 | 21.0884 | 2.3793 | -17.3185 | 0 | 0 | 0 | 0 | 0
238 | 22 | 0 | 0 |  | 0.16995 | 2.7026 | -1.4155 | 5.3045 | 22.0884 | 2.6411 | -22.9391 | 0 | 0 | 0 | 0 | 0
238 | 23 | 0 | 0 |  | 0.16995 | 2.7026 | -1.4155 | 5.3045 | 23.0884 | 2.9029 | -26.4934 | 0 | 0 | 0 | 0 | 0
238 | 24 | 0 | 0 |  | 0.16995 | 2.7026 | -1.4155 | 5.3045 | 24.0884 | 3.1647 | -27.5725 | 0 | 0 | 0 | 0 | 0
239 | 1 | 0 | 0 |  | 0.16363 | 2.7198 | -1.1165 | 5.6035 | 1.0934 | -2.8553 | -26.3771 | 0 | 0 | 0 | 0 | 0
239 | 2 | 0 | 0 |  | 0.16363 | 2.7198 | -1.1165 | 5.6035 | 2.0934 | -2.5935 | -22.3963 | 0 | 0 | 0 | 0 | 0
239 | 3 | 0 | 0 |  | 0.16363 | 2.7198 | -1.1165 | 5.6035 | 3.0934 | -2.3317 | -16.4364 | 0 | 0 | 0 | 0 | 0
239 | 4 | 0 | 0 |  | 0.16363 | 2.7198 | -1.1165 | 5.6035 | 4.0934 | -2.0699 | -9.02 | 0 | 0 | 0 | 0 | 0
239 | 5 | 0 | 0 |  | 0.16363 | 2.7198 | -1.1165 | 5.6035 | 5.0934 | -1.8081 | -0.63572 | 0 | 0 | 0 | 0 | 0
239 | 6 | 0 | 8 |  | 0.16363 | 2.7198 | -1.1165 | 5.6035 | 6.0934 | -1.5463 | 8.2895 | 0 | 6.6667 | 6.6667 | 10.584 | 0
239 | 7 | 0 | 74 |  | 0.16363 | 2.7198 | -1.1165 | 5.6035 | 7.0934 | -1.2845 | 17.3643 | 0 | 61.6667 | 61.6667 | 97.902 | 1
239 | 8 | 18 | 153 |  | 0.16363 | 2.7198 | -1.1165 | 5.6035 | 8.0934 | -1.0227 | 26.1811 | 9.6682 | 127.5 | 137.1682 | 217.7683 | 1
239 | 9 | 32 | 230 |  | 0.16363 | 2.7198 | -1.1165 | 5.6035 | 9.0934 | -0.76095 | 34.245 | 23.1063 | 191.6667 | 214.7729 | 340.9735 | 1
239 | 10 | 67 | 279 |  | 0.16363 | 2.7198 | -1.1165 | 5.6035 | 10.0934 | -0.49915 | 40.8996 | 57.76 | 232.5 | 290.26 | 460.8167 | 1
239 | 11 | 349 | 314 |  | 0.16363 | 2.7198 | -1.1165 | 5.6035 | 11.0934 | -0.23735 | 45.3121 | 330.7258 | 261.6667 | 592.3925 | 940.4824 | 1
239 | 12 | 546 | 252 |  | 0.16363 | 2.7198 | -1.1165 | 5.6035 | 12.0934 | 0.02445 | 46.6805 | 531.1971 | 210 | 741.1971 | 1176.7244 | 1
239 | 13 | 641 | 218 |  | 0.16363 | 2.7198 | -1.1165 | 5.6035 | 13.0934 | 0.28625 | 44.6987 | 600.0517 | 181.6667 | 781.7183 | 1241.0561 | 1
239 | 14 | 734 | 150 |  | 0.16363 | 2.7198 | -1.1165 | 5.6035 | 14.0934 | 0.54805 | 39.8002 | 616.4377 | 125 | 741.4377 | 1177.1066 | 1
239 | 15 | 684 | 139 |  | 0.16363 | 2.7198 | -1.1165 | 5.6035 | 15.0934 | 0.80985 | 32.8234 | 472.3678 | 115.8333 | 588.2011 | 933.828 | 1
239 | 16 | 589 | 128 |  | 0.16363 | 2.7198 | -1.1165 | 5.6035 | 16.0934 | 1.0716 | 24.5748 | 293.6615 | 106.6667 | 400.3282 | 635.561 | 1
239 | 17 | 393 | 120 |  | 0.16363 | 2.7198 | -1.1165 | 5.6035 | 17.0934 | 1.3334 | 15.6759 | 108.806 | 100 | 208.806 | 331.5004 | 1
239 | 18 | 131 | 82 |  | 0.16363 | 2.7198 | -1.1165 | 5.6035 | 18.0934 | 1.5952 | 6.5994 | 5.3129 | 68.3333 | 73.6463 | 116.9208 | 0
239 | 19 | 0 | 15 |  | 0.16363 | 2.7198 | -1.1165 | 5.6035 | 19.0934 | 1.857 | -2.2549 | 0 | 12.5 | 12.5 | 19.845 | 0
239 | 20 | 0 | 0 |  | 0.16363 | 2.7198 | -1.1165 | 5.6035 | 20.0934 | 2.1188 | -10.4926 | 0 | 0 | 0 | 0 | 0
239 | 21 | 0 | 0 |  | 0.16363 | 2.7198 | -1.1165 | 5.6035 | 21.0934 | 2.3806 | -17.6759 | 0 | 0 | 0 | 0 | 0
239 | 22 | 0 | 0 |  | 0.16363 | 2.7198 | -1.1165 | 5.6035 | 22.0934 | 2.6424 | -23.3056 | 0 | 0 | 0 | 0 | 0
239 | 23 | 0 | 0 |  | 0.16363 | 2.7198 | -1.1165 | 5.6035 | 23.0934 | 2.9042 | -26.8623 | 0 | 0 | 0 | 0 | 0
239 | 24 | 0 | 0 |  | 0.16363 | 2.7198 | -1.1165 | 5.6035 | 24.0934 | 3.166 | -27.933 | 0 | 0 | 0 | 0 | 0
240 | 1 | 0 | 0 |  | 0.15728 | 2.7371 | -0.81053 | 5.9095 | 1.0985 | -2.854 | -26.72 | 0 | 0 | 0 | 0 | 0
240 | 2 | 0 | 0 |  | 0.15728 | 2.7371 | -0.81053 | 5.9095 | 2.0985 | -2.5922 | -22.7126 | 0 | 0 | 0 | 0 | 0
240 | 3 | 0 | 0 |  | 0.15728 | 2.7371 | -0.81053 | 5.9095 | 3.0985 | -2.3304 | -16.7254 | 0 | 0 | 0 | 0 | 0
240 | 4 | 0 | 0 |  | 0.15728 | 2.7371 | -0.81053 | 5.9095 | 4.0985 | -2.0686 | -9.2859 | 0 | 0 | 0 | 0 | 0
240 | 5 | 0 | 0 |  | 0.15728 | 2.7371 | -0.81053 | 5.9095 | 5.0985 | -1.8068 | -0.88539 | 0 | 0 | 0 | 0 | 0
240 | 6 | 0 | 21 |  | 0.15728 | 2.7371 | -0.81053 | 5.9095 | 6.0985 | -1.545 | 8.0478 | 0 | 17.5 | 17.5 | 27.783 | 0
240 | 7 | 183 | 88 |  | 0.15728 | 2.7371 | -0.81053 | 5.9095 | 7.0985 | -1.2832 | 17.1214 | 58.3527 | 73.3333 | 131.686 | 209.0647 | 1
240 | 8 | 413 | 129 |  | 0.15728 | 2.7371 | -0.81053 | 5.9095 | 8.0985 | -1.0214 | 25.9268 | 221.4636 | 107.5 | 328.9636 | 522.2626 | 1
240 | 9 | 572 | 144 |  | 0.15728 | 2.7371 | -0.81053 | 5.9095 | 9.0985 | -0.75961 | 33.9687 | 412.5082 | 120 | 532.5082 | 845.4101 | 1
240 | 10 | 689 | 142 |  | 0.15728 | 2.7371 | -0.81053 | 5.9095 | 10.0985 | -0.49781 | 40.5921 | 593.2802 | 118.3333 | 711.6135 | 1129.7576 | 1
240 | 11 | 691 | 164 |  | 0.15728 | 2.7371 | -0.81053 | 5.9095 | 11.0985 | -0.23601 | 44.9706 | 653.9729 | 136.6667 | 790.6396 | 1255.2194 | 1
240 | 12 | 705 | 173 |  | 0.15728 | 2.7371 | -0.81053 | 5.9095 | 12.0985 | 0.025785 | 46.3148 | 684.8196 | 144.1667 | 828.9863 | 1316.0986 | 1
240 | 13 | 561 | 243 |  | 0.15728 | 2.7371 | -0.81053 | 5.9095 | 13.0985 | 0.28758 | 44.3271 | 524.1162 | 202.5 | 726.6162 | 1153.5759 | 1
240 | 14 | 387 | 284 |  | 0.15728 | 2.7371 | -0.81053 | 5.9095 | 14.0985 | 0.54938 | 39.4371 | 324.1433 | 236.6667 | 560.8099 | 890.3418 | 1
240 | 15 | 204 | 276 |  | 0.15728 | 2.7371 | -0.81053 | 5.9095 | 15.0985 | 0.81118 | 32.4734 | 140.3401 | 230 | 370.3401 | 587.9519 | 1
240 | 16 | 309 | 197 |  | 0.15728 | 2.7371 | -0.81053 | 5.9095 | 16.0985 | 1.073 | 24.2352 | 153.121 | 164.1667 | 317.2877 | 503.7259 | 1
240 | 17 | 392 | 118 |  | 0.15728 | 2.7371 | -0.81053 | 5.9095 | 17.0985 | 1.3348 | 15.3416 | 107.2037 | 98.3333 | 205.537 | 326.3105 | 1
240 | 18 | 128 | 80 |  | 0.15728 | 2.7371 | -0.81053 | 5.9095 | 18.0985 | 1.5966 | 6.2648 | 4.723 | 66.6667 | 71.3897 | 113.3383 | 0
240 | 19 | 0 | 14 |  | 0.15728 | 2.7371 | -0.81053 | 5.9095 | 19.0985 | 1.8584 | -2.595 | 0 | 11.6667 | 11.6667 | 18.522 | 0
240 | 20 | 0 | 0 |  | 0.15728 | 2.7371 | -0.81053 | 5.9095 | 20.0985 | 2.1202 | -10.842 | 0 | 0 | 0 | 0 | 0
240 | 21 | 0 | 0 |  | 0.15728 | 2.7371 | -0.81053 | 5.9095 | 21.0985 | 2.382 | -18.0362 | 0 | 0 | 0 | 0 | 0
240 | 22 | 0 | 0 |  | 0.15728 | 2.7371 | -0.81053 | 5.9095 | 22.0985 | 2.6438 | -23.6749 | 0 | 0 | 0 | 0 | 0
240 | 23 | 0 | 0 |  | 0.15728 | 2.7371 | -0.81053 | 5.9095 | 23.0985 | 2.9056 | -27.2338 | 0 | 0 | 0 | 0 | 0
240 | 24 | 0 | 0 |  | 0.15728 | 2.7371 | -0.81053 | 5.9095 | 24.0985 | 3.1674 | -28.2958 | 0 | 0 | 0 | 0 | 0
241 | 1 | 0 | 0 |  | 0.15088 | 2.7543 | -0.498 | 6.222 | 1.1037 | -2.8526 | -27.0647 | 0 | 0 | 0 | 0 | 0
241 | 2 | 0 | 0 |  | 0.15088 | 2.7543 | -0.498 | 6.222 | 2.1037 | -2.5908 | -23.0302 | 0 | 0 | 0 | 0 | 0
241 | 3 | 0 | 0 |  | 0.15088 | 2.7543 | -0.498 | 6.222 | 3.1037 | -2.329 | -17.0154 | 0 | 0 | 0 | 0 | 0
241 | 4 | 0 | 0 |  | 0.15088 | 2.7543 | -0.498 | 6.222 | 4.1037 | -2.0672 | -9.5526 | 0 | 0 | 0 | 0 | 0
241 | 5 | 0 | 0 |  | 0.15088 | 2.7543 | -0.498 | 6.222 | 5.1037 | -1.8054 | -1.1358 | 0 | 0 | 0 | 0 | 0
241 | 6 | 0 | 20 |  | 0.15088 | 2.7543 | -0.498 | 6.222 | 6.1037 | -1.5436 | 7.8052 | 0 | 16.6667 | 16.6667 | 26.46 | 0
241 | 7 | 155 | 87 |  | 0.15088 | 2.7543 | -0.498 | 6.222 | 7.1037 | -1.2818 | 16.8773 | 49.2713 | 72.5 | 121.7713 | 193.3242 | 1
241 | 8 | 314 | 139 |  | 0.15088 | 2.7543 | -0.498 | 6.222 | 8.1037 | -1.02 | 25.671 | 168.0929 | 115.8333 | 283.9263 | 450.7614 | 1
241 | 9 | 165 | 230 |  | 0.15088 | 2.7543 | -0.498 | 6.222 | 9.1037 | -0.75825 | 33.6906 | 118.8403 | 191.6667 | 310.5069 | 492.9608 | 1
241 | 10 | 224 | 270 |  | 0.15088 | 2.7543 | -0.498 | 6.222 | 10.1037 | -0.49645 | 40.2824 | 192.6459 | 225 | 417.6459 | 663.0546 | 1
241 | 11 | 363 | 302 |  | 0.15088 | 2.7543 | -0.498 | 6.222 | 11.1037 | -0.23465 | 44.6269 | 343.089 | 251.6667 | 594.7557 | 944.2342 | 1
241 | 12 | 219 | 349 |  | 0.15088 | 2.7543 | -0.498 | 6.222 | 12.1037 | 0.027149 | 45.9466 | 212.3886 | 290.8333 | 503.2219 | 798.9151 | 1
241 | 13 | 580 | 259 |  | 0.15088 | 2.7543 | -0.498 | 6.222 | 13.1037 | 0.28895 | 43.9528 | 540.7522 | 215.8333 | 756.5855 | 1201.1551 | 1
241 | 14 | 538 | 226 |  | 0.15088 | 2.7543 | -0.498 | 6.222 | 14.1037 | 0.55075 | 39.0712 | 449.3724 | 188.3333 | 637.7057 | 1012.4216 | 1
241 | 15 | 236 | 252 |  | 0.15088 | 2.7543 | -0.498 | 6.222 | 15.1037 | 0.81255 | 32.1203 | 161.7133 | 210 | 371.7133 | 590.132 | 1
241 | 16 | 44 | 208 |  | 0.15088 | 2.7543 | -0.498 | 6.222 | 16.1037 | 1.0743 | 23.8926 | 21.6673 | 173.3333 | 195.0007 | 309.5831 | 1
241 | 17 | 100 | 147 |  | 0.15088 | 2.7543 | -0.498 | 6.222 | 17.1037 | 1.3361 | 15.0043 | 27.0044 | 122.5 | 149.5044 | 237.3532 | 1
241 | 18 | 0 | 57 |  | 0.15088 | 2.7543 | -0.498 | 6.222 | 18.1037 | 1.5979 | 5.9272 | 0 | 47.5 | 47.5 | 75.411 | 0
241 | 19 | 0 | 11 |  | 0.15088 | 2.7543 | -0.498 | 6.222 | 19.1037 | 1.8597 | -2.938 | 0 | 9.1667 | 9.1667 | 14.553 | 0
241 | 20 | 0 | 0 |  | 0.15088 | 2.7543 | -0.498 | 6.222 | 20.1037 | 2.1215 | -11.1942 | 0 | 0 | 0 | 0 | 0
241 | 21 | 0 | 0 |  | 0.15088 | 2.7543 | -0.498 | 6.222 | 21.1037 | 2.3833 | -18.3994 | 0 | 0 | 0 | 0 | 0
241 | 22 | 0 | 0 |  | 0.15088 | 2.7543 | -0.498 | 6.222 | 22.1037 | 2.6451 | -24.047 | 0 | 0 | 0 | 0 | 0
241 | 23 | 0 | 0 |  | 0.15088 | 2.7543 | -0.498 | 6.222 | 23.1037 | 2.9069 | -27.6079 | 0 | 0 | 0 | 0 | 0
241 | 24 | 0 | 0 |  | 0.15088 | 2.7543 | -0.498 | 6.222 | 24.1037 | 3.1687 | -28.6608 | 0 | 0 | 0 | 0 | 0
242 | 1 | 0 | 0 |  | 0.14445 | 2.7715 | -0.17919 | 6.5408 | 1.109 | -2.8513 | -27.411 | 0 | 0 | 0 | 0 | 0
242 | 2 | 0 | 0 |  | 0.14445 | 2.7715 | -0.17919 | 6.5408 | 2.109 | -2.5895 | -23.3489 | 0 | 0 | 0 | 0 | 0
242 | 3 | 0 | 0 |  | 0.14445 | 2.7715 | -0.17919 | 6.5408 | 3.109 | -2.3277 | -17.3063 | 0 | 0 | 0 | 0 | 0
242 | 4 | 0 | 0 |  | 0.14445 | 2.7715 | -0.17919 | 6.5408 | 4.109 | -2.0659 | -9.8201 | 0 | 0 | 0 | 0 | 0
242 | 5 | 0 | 0 |  | 0.14445 | 2.7715 | -0.17919 | 6.5408 | 5.109 | -1.8041 | -1.3871 | 0 | 0 | 0 | 0 | 0
242 | 6 | 0 | 11 |  | 0.14445 | 2.7715 | -0.17919 | 6.5408 | 6.109 | -1.5423 | 7.5616 | 0 | 9.1667 | 9.1667 | 14.553 | 0
242 | 7 | 59 | 75 |  | 0.14445 | 2.7715 | -0.17919 | 6.5408 | 7.109 | -1.2805 | 16.6321 | 18.6966 | 62.5 | 81.1966 | 128.9077 | 1
242 | 8 | 19 | 147 |  | 0.14445 | 2.7715 | -0.17919 | 6.5408 | 8.109 | -1.0187 | 25.4138 | 10.1538 | 122.5 | 132.6538 | 210.6012 | 1
242 | 9 | 169 | 224 |  | 0.14445 | 2.7715 | -0.17919 | 6.5408 | 9.109 | -0.75686 | 33.4107 | 121.5612 | 186.6667 | 308.2278 | 489.3425 | 1
242 | 10 | 70 | 271 |  | 0.14445 | 2.7715 | -0.17919 | 6.5408 | 10.109 | -0.49506 | 39.9707 | 60.1261 | 225.8333 | 285.9594 | 453.9892 | 1
242 | 11 | 71 | 317 |  | 0.14445 | 2.7715 | -0.17919 | 6.5408 | 11.109 | -0.23326 | 44.2809 | 67.0125 | 264.1667 | 331.1792 | 525.7801 | 1
242 | 12 | 16 | 233 |  | 0.14445 | 2.7715 | -0.17919 | 6.5408 | 12.109 | 0.02854 | 45.5761 | 15.4911 | 194.1667 | 209.6578 | 332.8527 | 1
242 | 13 | 6 | 239 |  | 0.14445 | 2.7715 | -0.17919 | 6.5408 | 13.109 | 0.29034 | 43.5759 | 5.5821 | 199.1667 | 204.7488 | 325.0592 | 1
242 | 14 | 5 | 220 |  | 0.14445 | 2.7715 | -0.17919 | 6.5408 | 14.109 | 0.55214 | 38.7024 | 4.1644 | 183.3333 | 187.4978 | 297.6715 | 1
242 | 15 | 3 | 187 |  | 0.14445 | 2.7715 | -0.17919 | 6.5408 | 15.109 | 0.81394 | 31.7642 | 2.0473 | 155.8333 | 157.8807 | 250.6514 | 1
242 | 16 | 40 | 206 |  | 0.14445 | 2.7715 | -0.17919 | 6.5408 | 16.109 | 1.0757 | 23.5469 | 19.5714 | 171.6667 | 191.238 | 303.6095 | 1
242 | 17 | 15 | 132 |  | 0.14445 | 2.7715 | -0.17919 | 6.5408 | 17.109 | 1.3375 | 14.6641 | 3.9984 | 110 | 113.9984 | 180.9838 | 1
242 | 18 | 0 | 54 |  | 0.14445 | 2.7715 | -0.17919 | 6.5408 | 18.109 | 1.5993 | 5.5867 | 0 | 45 | 45 | 71.442 | 0
242 | 19 | 0 | 7 |  | 0.14445 | 2.7715 | -0.17919 | 6.5408 | 19.109 | 1.8611 | -3.2837 | 0 | 5.8333 | 5.8333 | 9.261 | 0
242 | 20 | 0 | 0 |  | 0.14445 | 2.7715 | -0.17919 | 6.5408 | 20.109 | 2.1229 | -11.5491 | 0 | 0 | 0 | 0 | 0
242 | 21 | 0 | 0 |  | 0.14445 | 2.7715 | -0.17919 | 6.5408 | 21.109 | 2.3847 | -18.7652 | 0 | 0 | 0 | 0 | 0
242 | 22 | 0 | 0 |  | 0.14445 | 2.7715 | -0.17919 | 6.5408 | 22.109 | 2.6465 | -24.4217 | 0 | 0 | 0 | 0 | 0
242 | 23 | 0 | 0 |  | 0.14445 | 2.7715 | -0.17919 | 6.5408 | 23.109 | 2.9083 | -27.9844 | 0 | 0 | 0 | 0 | 0
242 | 24 | 0 | 0 |  | 0.14445 | 2.7715 | -0.17919 | 6.5408 | 24.109 | 3.1701 | -29.0279 | 0 | 0 | 0 | 0 | 0
243 | 1 | 0 | 0 |  | 0.13797 | 2.7887 | 0.14559 | 6.8656 | 1.1144 | -2.8498 | -27.7588 | 0 | 0 | 0 | 0 | 0
243 | 2 | 0 | 0 |  | 0.13797 | 2.7887 | 0.14559 | 6.8656 | 2.1144 | -2.588 | -23.6688 | 0 | 0 | 0 | 0 | 0
243 | 3 | 0 | 0 |  | 0.13797 | 2.7887 | 0.14559 | 6.8656 | 3.1144 | -2.3262 | -17.5979 | 0 | 0 | 0 | 0 | 0
243 | 4 | 0 | 0 |  | 0.13797 | 2.7887 | 0.14559 | 6.8656 | 4.1144 | -2.0644 | -10.0882 | 0 | 0 | 0 | 0 | 0
243 | 5 | 0 | 0 |  | 0.13797 | 2.7887 | 0.14559 | 6.8656 | 5.1144 | -1.8026 | -1.639 | 0 | 0 | 0 | 0 | 0
243 | 6 | 0 | 6 |  | 0.13797 | 2.7887 | 0.14559 | 6.8656 | 6.1144 | -1.5408 | 7.3173 | 0 | 5 | 5 | 7.938 | 0
243 | 7 | 0 | 42 |  | 0.13797 | 2.7887 | 0.14559 | 6.8656 | 7.1144 | -1.279 | 16.3858 | 0 | 35 | 35 | 55.566 | 1
243 | 8 | 0 | 95 |  | 0.13797 | 2.7887 | 0.14559 | 6.8656 | 8.1144 | -1.0172 | 25.1552 | 0 | 79.1667 | 79.1667 | 125.685 | 1
243 | 9 | 0 | 149 |  | 0.13797 | 2.7887 | 0.14559 | 6.8656 | 9.1144 | -0.75544 | 33.129 | 0 | 124.1667 | 124.1667 | 197.127 | 1
243 | 10 | 4 | 192 |  | 0.13797 | 2.7887 | 0.14559 | 6.8656 | 10.1144 | -0.49364 | 39.6569 | 3.4313 | 160 | 163.4313 | 259.4635 | 1
243 | 11 | 70 | 315 |  | 0.13797 | 2.7887 | 0.14559 | 6.8656 | 11.1144 | -0.23184 | 43.9329 | 65.9739 | 262.5 | 328.4739 | 521.4852 | 1
243 | 12 | 72 | 336 |  | 0.13797 | 2.7887 | 0.14559 | 6.8656 | 12.1144 | 0.029957 | 45.2034 | 69.5899 | 280 | 349.5899 | 555.0089 | 1
243 | 13 | 16 | 230 |  | 0.13797 | 2.7887 | 0.14559 | 6.8656 | 13.1144 | 0.29176 | 43.1966 | 14.853 | 191.6667 | 206.5197 | 327.8707 | 1
243 | 14 | 5 | 218 |  | 0.13797 | 2.7887 | 0.14559 | 6.8656 | 14.1144 | 0.55356 | 38.3309 | 4.1523 | 181.6667 | 185.8189 | 295.0061 | 1
243 | 15 | 3 | 185 |  | 0.13797 | 2.7887 | 0.14559 | 6.8656 | 15.1144 | 0.81535 | 31.4053 | 2.0388 | 154.1667 | 156.2055 | 247.9919 | 1
243 | 16 | 39 | 203 |  | 0.13797 | 2.7887 | 0.14559 | 6.8656 | 16.1144 | 1.0772 | 23.1985 | 18.9568 | 169.1667 | 188.1235 | 298.6649 | 1
243 | 17 | 11 | 130 |  | 0.13797 | 2.7887 | 0.14559 | 6.8656 | 17.1144 | 1.339 | 14.3211 | 2.8932 | 108.3333 | 111.2266 | 176.5833 | 1
243 | 18 | 0 | 32 |  | 0.13797 | 2.7887 | 0.14559 | 6.8656 | 18.1144 | 1.6008 | 5.2436 | 0 | 26.6667 | 26.6667 | 42.336 | 0
243 | 19 | 0 | 4 |  | 0.13797 | 2.7887 | 0.14559 | 6.8656 | 19.1144 | 1.8626 | -3.6321 | 0 | 3.3333 | 3.3333 | 5.292 | 0
243 | 20 | 0 | 0 |  | 0.13797 | 2.7887 | 0.14559 | 6.8656 | 20.1144 | 2.1244 | -11.9066 | 0 | 0 | 0 | 0 | 0
243 | 21 | 0 | 0 |  | 0.13797 | 2.7887 | 0.14559 | 6.8656 | 21.1144 | 2.3862 | -19.1336 | 0 | 0 | 0 | 0 | 0
243 | 22 | 0 | 0 |  | 0.13797 | 2.7887 | 0.14559 | 6.8656 | 22.1144 | 2.648 | -24.7989 | 0 | 0 | 0 | 0 | 0
243 | 23 | 0 | 0 |  | 0.13797 | 2.7887 | 0.14559 | 6.8656 | 23.1144 | 2.9098 | -28.3633 | 0 | 0 | 0 | 0 | 0
243 | 24 | 0 | 0 |  | 0.13797 | 2.7887 | 0.14559 | 6.8656 | 24.1144 | 3.1715 | -29.397 | 0 | 0 | 0 | 0 | 0
244 | 1 | 0 | 0 |  | 0.13147 | 2.8059 | 0.47602 | 7.196 | 1.1199 | -2.8484 | -28.1081 | 0 | 0 | 0 | 0 | 0
244 | 2 | 0 | 0 |  | 0.13147 | 2.8059 | 0.47602 | 7.196 | 2.1199 | -2.5866 | -23.9896 | 0 | 0 | 0 | 0 | 0
244 | 3 | 0 | 0 |  | 0.13147 | 2.8059 | 0.47602 | 7.196 | 3.1199 | -2.3248 | -17.8903 | 0 | 0 | 0 | 0 | 0
244 | 4 | 0 | 0 |  | 0.13147 | 2.8059 | 0.47602 | 7.196 | 4.1199 | -2.063 | -10.3569 | 0 | 0 | 0 | 0 | 0
244 | 5 | 0 | 0 |  | 0.13147 | 2.8059 | 0.47602 | 7.196 | 5.1199 | -1.8012 | -1.8916 | 0 | 0 | 0 | 0 | 0
244 | 6 | 0 | 17 |  | 0.13147 | 2.8059 | 0.47602 | 7.196 | 6.1199 | -1.5394 | 7.0721 | 0 | 14.1667 | 14.1667 | 22.491 | 0
244 | 7 | 0 | 66 |  | 0.13147 | 2.8059 | 0.47602 | 7.196 | 7.1199 | -1.2776 | 16.1383 | 0 | 55 | 55 | 87.318 | 1
244 | 8 | 18 | 144 |  | 0.13147 | 2.8059 | 0.47602 | 7.196 | 8.1199 | -1.0158 | 24.8951 | 9.5858 | 120 | 129.5858 | 205.7304 | 1
244 | 9 | 32 | 221 |  | 0.13147 | 2.8059 | 0.47602 | 7.196 | 9.1199 | -0.754 | 32.8456 | 22.9546 | 184.1667 | 207.1212 | 328.8257 | 1
244 | 10 | 66 | 269 |  | 0.13147 | 2.8059 | 0.47602 | 7.196 | 10.1199 | -0.4922 | 39.3412 | 56.5406 | 224.1667 | 280.7073 | 445.6508 | 1
244 | 11 | 71 | 312 |  | 0.13147 | 2.8059 | 0.47602 | 7.196 | 11.1199 | -0.2304 | 43.5827 | 66.817 | 260 | 326.817 | 518.8547 | 1
244 | 12 | 73 | 334 |  | 0.13147 | 2.8059 | 0.47602 | 7.196 | 12.1199 | 0.031399 | 44.8285 | 70.4308 | 278.3333 | 348.7641 | 553.6979 | 1
244 | 13 | 73 | 331 |  | 0.13147 | 2.8059 | 0.47602 | 7.196 | 13.1199 | 0.2932 | 42.8151 | 67.6141 | 275.8333 | 343.4474 | 545.2571 | 1
244 | 14 | 71 | 305 |  | 0.13147 | 2.8059 | 0.47602 | 7.196 | 14.1199 | 0.555 | 37.957 | 58.7851 | 254.1667 | 312.9518 | 496.8423 | 1
244 | 15 | 66 | 258 |  | 0.13147 | 2.8059 | 0.47602 | 7.196 | 15.1199 | 0.8168 | 31.0438 | 44.6635 | 215 | 259.6635 | 412.2418 | 1
244 | 16 | 31 | 205 |  | 0.13147 | 2.8059 | 0.47602 | 7.196 | 16.1199 | 1.0786 | 22.8474 | 14.967 | 170.8333 | 185.8003 | 294.9766 | 1
244 | 17 | 12 | 129 |  | 0.13147 | 2.8059 | 0.47602 | 7.196 | 17.1199 | 1.3404 | 13.9754 | 3.1132 | 107.5 | 110.6132 | 175.6096 | 1
244 | 18 | 0 | 50 |  | 0.13147 | 2.8059 | 0.47602 | 7.196 | 18.1199 | 1.6022 | 4.8979 | 0 | 41.6667 | 41.6667 | 66.15 | 0
244 | 19 | 0 | 5 |  | 0.13147 | 2.8059 | 0.47602 | 7.196 | 19.1199 | 1.864 | -3.9829 | 0 | 4.1667 | 4.1667 | 6.615 | 0
244 | 20 | 0 | 0 |  | 0.13147 | 2.8059 | 0.47602 | 7.196 | 20.1199 | 2.1258 | -12.2666 | 0 | 0 | 0 | 0 | 0
244 | 21 | 0 | 0 |  | 0.13147 | 2.8059 | 0.47602 | 7.196 | 21.1199 | 2.3876 | -19.5044 | 0 | 0 | 0 | 0 | 0
244 | 22 | 0 | 0 |  | 0.13147 | 2.8059 | 0.47602 | 7.196 | 22.1199 | 2.6494 | -25.1785 | 0 | 0 | 0 | 0 | 0
244 | 23 | 0 | 0 |  | 0.13147 | 2.8059 | 0.47602 | 7.196 | 23.1199 | 2.9112 | -28.7444 | 0 | 0 | 0 | 0 | 0
244 | 24 | 0 | 0 |  | 0.13147 | 2.8059 | 0.47602 | 7.196 | 24.1199 | 3.173 | -29.768 | 0 | 0 | 0 | 0 | 0
245 | 1 | 0 | 0 |  | 0.12493 | 2.8231 | 0.81176 | 7.5318 | 1.1255 | -2.8469 | -28.4587 | 0 | 0 | 0 | 0 | 0
245 | 2 | 0 | 0 |  | 0.12493 | 2.8231 | 0.81176 | 7.5318 | 2.1255 | -2.5851 | -24.3114 | 0 | 0 | 0 | 0 | 0
245 | 3 | 0 | 0 |  | 0.12493 | 2.8231 | 0.81176 | 7.5318 | 3.1255 | -2.3233 | -18.1833 | 0 | 0 | 0 | 0 | 0
245 | 4 | 0 | 0 |  | 0.12493 | 2.8231 | 0.81176 | 7.5318 | 4.1255 | -2.0615 | -10.6262 | 0 | 0 | 0 | 0 | 0
245 | 5 | 0 | 0 |  | 0.12493 | 2.8231 | 0.81176 | 7.5318 | 5.1255 | -1.7997 | -2.1448 | 0 | 0 | 0 | 0 | 0
245 | 6 | 0 | 6 |  | 0.12493 | 2.8231 | 0.81176 | 7.5318 | 6.1255 | -1.5379 | 6.826 | 0 | 5 | 5 | 7.938 | 0
245 | 7 | 0 | 40 |  | 0.12493 | 2.8231 | 0.81176 | 7.5318 | 7.1255 | -1.2761 | 15.8898 | 0 | 33.3333 | 33.3333 | 52.92 | 1
245 | 8 | 0 | 93 |  | 0.12493 | 2.8231 | 0.81176 | 7.5318 | 8.1255 | -1.0143 | 24.6337 | 0 | 77.5 | 77.5 | 123.039 | 1
245 | 9 | 0 | 147 |  | 0.12493 | 2.8231 | 0.81176 | 7.5318 | 9.1255 | -0.75253 | 32.5605 | 0 | 122.5 | 122.5 | 194.481 | 1
245 | 10 | 3 | 191 |  | 0.12493 | 2.8231 | 0.81176 | 7.5318 | 10.1255 | -0.49074 | 39.0237 | 2.5665 | 159.1667 | 161.7331 | 256.7675 | 1
245 | 11 | 5 | 221 |  | 0.12493 | 2.8231 | 0.81176 | 7.5318 | 11.1255 | -0.22894 | 43.2306 | 4.6982 | 184.1667 | 188.8649 | 299.8419 | 1
245 | 12 | 6 | 236 |  | 0.12493 | 2.8231 | 0.81176 | 7.5318 | 12.1255 | 0.032864 | 44.4516 | 5.7782 | 196.6667 | 202.4449 | 321.4015 | 1
245 | 13 | 6 | 234 |  | 0.12493 | 2.8231 | 0.81176 | 7.5318 | 13.1255 | 0.29466 | 42.4313 | 5.5444 | 195 | 200.5444 | 318.3843 | 1
245 | 14 | 5 | 215 |  | 0.12493 | 2.8231 | 0.81176 | 7.5318 | 14.1255 | 0.55646 | 37.5806 | 4.127 | 179.1667 | 183.2937 | 290.9971 | 1
245 | 15 | 3 | 182 |  | 0.12493 | 2.8231 | 0.81176 | 7.5318 | 15.1255 | 0.81826 | 30.6797 | 2.0213 | 151.6667 | 153.688 | 243.995 | 1
245 | 16 | 5 | 162 |  | 0.12493 | 2.8231 | 0.81176 | 7.5318 | 16.1255 | 1.0801 | 22.4937 | 2.3974 | 135 | 137.3974 | 218.1322 | 1
245 | 17 | 3 | 114 |  | 0.12493 | 2.8231 | 0.81176 | 7.5318 | 17.1255 | 1.3419 | 13.6273 | 0.76741 | 95 | 95.7674 | 152.0403 | 1
245 | 18 | 0 | 48 |  | 0.12493 | 2.8231 | 0.81176 | 7.5318 | 18.1255 | 1.6037 | 4.5498 | 0 | 40 | 40 | 63.504 | 0
245 | 19 | 0 | 4 |  | 0.12493 | 2.8231 | 0.81176 | 7.5318 | 19.1255 | 1.8655 | -4.3362 | 0 | 3.3333 | 3.3333 | 5.292 | 0
245 | 20 | 0 | 0 |  | 0.12493 | 2.8231 | 0.81176 | 7.5318 | 20.1255 | 2.1273 | -12.6289 | 0 | 0 | 0 | 0 | 0
245 | 21 | 0 | 0 |  | 0.12493 | 2.8231 | 0.81176 | 7.5318 | 21.1255 | 2.3891 | -19.8775 | 0 | 0 | 0 | 0 | 0
245 | 22 | 0 | 0 |  | 0.12493 | 2.8231 | 0.81176 | 7.5318 | 22.1255 | 2.6509 | -25.5603 | 0 | 0 | 0 | 0 | 0
245 | 23 | 0 | 0 |  | 0.12493 | 2.8231 | 0.81176 | 7.5318 | 23.1255 | 2.9127 | -29.1276 | 0 | 0 | 0 | 0 | 0
245 | 24 | 0 | 0 |  | 0.12493 | 2.8231 | 0.81176 | 7.5318 | 24.1255 | 3.1745 | -30.1408 | 0 | 0 | 0 | 0 | 0
246 | 1 | 0 | 0 |  | 0.11835 | 2.8403 | 1.1525 | 7.8725 | 1.1312 | -2.8454 | -28.8106 | 0 | 0 | 0 | 0 | 0
246 | 2 | 0 | 0 |  | 0.11835 | 2.8403 | 1.1525 | 7.8725 | 2.1312 | -2.5836 | -24.6341 | 0 | 0 | 0 | 0 | 0
246 | 3 | 0 | 0 |  | 0.11835 | 2.8403 | 1.1525 | 7.8725 | 3.1312 | -2.3218 | -18.477 | 0 | 0 | 0 | 0 | 0
246 | 4 | 0 | 0 |  | 0.11835 | 2.8403 | 1.1525 | 7.8725 | 4.1312 | -2.06 | -10.896 | 0 | 0 | 0 | 0 | 0
246 | 5 | 0 | 0 |  | 0.11835 | 2.8403 | 1.1525 | 7.8725 | 5.1312 | -1.7982 | -2.3986 | 0 | 0 | 0 | 0 | 0
246 | 6 | 0 | 15 |  | 0.11835 | 2.8403 | 1.1525 | 7.8725 | 6.1312 | -1.5364 | 6.5792 | 0 | 12.5 | 12.5 | 19.845 | 0
246 | 7 | 144 | 78 |  | 0.11835 | 2.8403 | 1.1525 | 7.8725 | 7.1312 | -1.2746 | 15.6403 | 45.0601 | 65 | 110.0601 | 174.7314 | 1
246 | 8 | 389 | 123 |  | 0.11835 | 2.8403 | 1.1525 | 7.8725 | 8.1312 | -1.0128 | 24.3709 | 206.4103 | 102.5 | 308.9103 | 490.426 | 1
246 | 9 | 575 | 137 |  | 0.11835 | 2.8403 | 1.1525 | 7.8725 | 9.1312 | -0.75105 | 32.2738 | 411.2746 | 114.1667 | 525.4413 | 834.1906 | 1
246 | 10 | 508 | 198 |  | 0.11835 | 2.8403 | 1.1525 | 7.8725 | 10.1312 | -0.48925 | 38.7043 | 433.9649 | 165 | 598.9649 | 950.9167 | 1
246 | 11 | 589 | 191 |  | 0.11835 | 2.8403 | 1.1525 | 7.8725 | 11.1312 | -0.22745 | 42.8766 | 552.5699 | 159.1667 | 711.7365 | 1129.9529 | 1
246 | 12 | 221 | 337 |  | 0.11835 | 2.8403 | 1.1525 | 7.8725 | 12.1312 | 0.03435 | 44.0728 | 212.4265 | 280.8333 | 493.2599 | 783.0994 | 1
246 | 13 | 81 | 323 |  | 0.11835 | 2.8403 | 1.1525 | 7.8725 | 13.1312 | 0.29615 | 42.0454 | 74.6708 | 269.1667 | 343.8374 | 545.8763 | 1
246 | 14 | 212 | 307 |  | 0.11835 | 2.8403 | 1.1525 | 7.8725 | 14.1312 | 0.55795 | 37.2019 | 174.4326 | 255.8333 | 430.266 | 683.0903 | 1
246 | 15 | 466 | 208 |  | 0.11835 | 2.8403 | 1.1525 | 7.8725 | 15.1312 | 0.81975 | 30.3132 | 312.5744 | 173.3333 | 485.9077 | 771.4271 | 1
246 | 16 | 90 | 173 |  | 0.11835 | 2.8403 | 1.1525 | 7.8725 | 16.1312 | 1.0815 | 22.1375 | 42.8505 | 144.1667 | 187.0172 | 296.9085 | 1
246 | 17 | 222 | 136 |  | 0.11835 | 2.8403 | 1.1525 | 7.8725 | 17.1312 | 1.3433 | 13.2767 | 55.9727 | 113.3333 | 169.306 | 268.7903 | 1
246 | 18 | 62 | 64 |  | 0.11835 | 2.8403 | 1.1525 | 7.8725 | 18.1312 | 1.6051 | 4.1993 | 0.87186 | 53.3333 | 54.2052 | 86.0562 | 0
246 | 19 | 0 | 8 |  | 0.11835 | 2.8403 | 1.1525 | 7.8725 | 19.1312 | 1.8669 | -4.6916 | 0 | 6.6667 | 6.6667 | 10.584 | 0
246 | 20 | 0 | 0 |  | 0.11835 | 2.8403 | 1.1525 | 7.8725 | 20.1312 | 2.1287 | -12.9934 | 0 | 0 | 0 | 0 | 0
246 | 21 | 0 | 0 |  | 0.11835 | 2.8403 | 1.1525 | 7.8725 | 21.1312 | 2.3905 | -20.2528 | 0 | 0 | 0 | 0 | 0
246 | 22 | 0 | 0 |  | 0.11835 | 2.8403 | 1.1525 | 7.8725 | 22.1312 | 2.6523 | -25.9443 | 0 | 0 | 0 | 0 | 0
246 | 23 | 0 | 0 |  | 0.11835 | 2.8403 | 1.1525 | 7.8725 | 23.1312 | 2.9141 | -29.5128 | 0 | 0 | 0 | 0 | 0
246 | 24 | 0 | 0 |  | 0.11835 | 2.8403 | 1.1525 | 7.8725 | 24.1312 | 3.1759 | -30.5153 | 0 | 0 | 0 | 0 | 0
247 | 1 | 0 | 0 |  | 0.11175 | 2.8576 | 1.4978 | 8.2178 | 1.137 | -2.8439 | -29.1636 | 0 | 0 | 0 | 0 | 0
247 | 2 | 0 | 0 |  | 0.11175 | 2.8576 | 1.4978 | 8.2178 | 2.137 | -2.5821 | -24.9575 | 0 | 0 | 0 | 0 | 0
247 | 3 | 0 | 0 |  | 0.11175 | 2.8576 | 1.4978 | 8.2178 | 3.137 | -2.3203 | -18.7711 | 0 | 0 | 0 | 0 | 0
247 | 4 | 0 | 0 |  | 0.11175 | 2.8576 | 1.4978 | 8.2178 | 4.137 | -2.0585 | -11.1663 | 0 | 0 | 0 | 0 | 0
247 | 5 | 0 | 0 |  | 0.11175 | 2.8576 | 1.4978 | 8.2178 | 5.137 | -1.7967 | -2.6529 | 0 | 0 | 0 | 0 | 0
247 | 6 | 0 | 14 |  | 0.11175 | 2.8576 | 1.4978 | 8.2178 | 6.137 | -1.5349 | 6.3317 | 0 | 11.6667 | 11.6667 | 18.522 | 0
247 | 7 | 188 | 69 |  | 0.11175 | 2.8576 | 1.4978 | 8.2178 | 7.137 | -1.2731 | 15.3897 | 58.6397 | 57.5 | 116.1397 | 184.3834 | 1
247 | 8 | 378 | 123 |  | 0.11175 | 2.8576 | 1.4978 | 8.2178 | 8.137 | -1.0113 | 24.1068 | 200.2003 | 102.5 | 302.7003 | 480.567 | 1
247 | 9 | 170 | 214 |  | 0.11175 | 2.8576 | 1.4978 | 8.2178 | 9.137 | -0.74954 | 31.9855 | 121.4114 | 178.3333 | 299.7447 | 475.8747 | 1
247 | 10 | 71 | 261 |  | 0.11175 | 2.8576 | 1.4978 | 8.2178 | 10.137 | -0.48774 | 38.3831 | 60.5629 | 217.5 | 278.0629 | 441.4526 | 1
247 | 11 | 214 | 313 |  | 0.11175 | 2.8576 | 1.4978 | 8.2178 | 11.137 | -0.22594 | 42.5207 | 200.435 | 260.8333 | 461.2683 | 732.3096 | 1
247 | 12 | 576 | 250 |  | 0.11175 | 2.8576 | 1.4978 | 8.2178 | 12.137 | 0.035857 | 43.6921 | 552.5726 | 208.3333 | 760.906 | 1208.0143 | 1
247 | 13 | 738 | 153 |  | 0.11175 | 2.8576 | 1.4978 | 8.2178 | 13.137 | 0.29766 | 41.6575 | 678.6624 | 127.5 | 806.1624 | 1279.8634 | 1
247 | 14 | 254 | 279 |  | 0.11175 | 2.8576 | 1.4978 | 8.2178 | 14.137 | 0.55946 | 36.821 | 208.3123 | 232.5 | 440.8123 | 699.8337 | 1
247 | 15 | 524 | 211 |  | 0.11175 | 2.8576 | 1.4978 | 8.2178 | 15.137 | 0.82126 | 29.9444 | 349.8737 | 175.8333 | 525.707 | 834.6125 | 1
247 | 16 | 563 | 121 |  | 0.11175 | 2.8576 | 1.4978 | 8.2178 | 16.137 | 1.0831 | 21.7791 | 266.128 | 100.8333 | 366.9614 | 582.5879 | 1
247 | 17 | 378 | 101 |  | 0.11175 | 2.8576 | 1.4978 | 8.2178 | 17.137 | 1.3449 | 12.9239 | 93.8996 | 84.1667 | 178.0663 | 282.698 | 1
247 | 18 | 87 | 62 |  | 0.11175 | 2.8576 | 1.4978 | 8.2178 | 18.137 | 1.6067 | 3.8467 | 0.88117 | 51.6667 | 52.5478 | 83.4249 | 0
247 | 19 | 0 | 7 |  | 0.11175 | 2.8576 | 1.4978 | 8.2178 | 19.137 | 1.8685 | -5.0492 | 0 | 5.8333 | 5.8333 | 9.261 | 0
247 | 20 | 0 | 0 |  | 0.11175 | 2.8576 | 1.4978 | 8.2178 | 20.137 | 2.1303 | -13.36 | 0 | 0 | 0 | 0 | 0
247 | 21 | 0 | 0 |  | 0.11175 | 2.8576 | 1.4978 | 8.2178 | 21.137 | 2.3921 | -20.6301 | 0 | 0 | 0 | 0 | 0
247 | 22 | 0 | 0 |  | 0.11175 | 2.8576 | 1.4978 | 8.2178 | 22.137 | 2.6539 | -26.3303 | 0 | 0 | 0 | 0 | 0
247 | 23 | 0 | 0 |  | 0.11175 | 2.8576 | 1.4978 | 8.2178 | 23.137 | 2.9157 | -29.8999 | 0 | 0 | 0 | 0 | 0
247 | 24 | 0 | 0 |  | 0.11175 | 2.8576 | 1.4978 | 8.2178 | 24.137 | 3.1774 | -30.8913 | 0 | 0 | 0 | 0 | 0
248 | 1 | 0 | 0 |  | 0.10512 | 2.8748 | 1.8475 | 8.5675 | 1.1428 | -2.8424 | -29.5178 | 0 | 0 | 0 | 0 | 0
248 | 2 | 0 | 0 |  | 0.10512 | 2.8748 | 1.8475 | 8.5675 | 2.1428 | -2.5806 | -25.2817 | 0 | 0 | 0 | 0 | 0
248 | 3 | 0 | 0 |  | 0.10512 | 2.8748 | 1.8475 | 8.5675 | 3.1428 | -2.3188 | -19.0658 | 0 | 0 | 0 | 0 | 0
248 | 4 | 0 | 0 |  | 0.10512 | 2.8748 | 1.8475 | 8.5675 | 4.1428 | -2.057 | -11.4371 | 0 | 0 | 0 | 0 | 0
248 | 5 | 0 | 0 |  | 0.10512 | 2.8748 | 1.8475 | 8.5675 | 5.1428 | -1.7952 | -2.9078 | 0 | 0 | 0 | 0 | 0
248 | 6 | 0 | 8 |  | 0.10512 | 2.8748 | 1.8475 | 8.5675 | 6.1428 | -1.5334 | 6.0834 | 0 | 6.6667 | 6.6667 | 10.584 | 0
248 | 7 | 0 | 59 |  | 0.10512 | 2.8748 | 1.8475 | 8.5675 | 7.1428 | -1.2716 | 15.1381 | 0 | 49.1667 | 49.1667 | 78.057 | 1
248 | 8 | 17 | 137 |  | 0.10512 | 2.8748 | 1.8475 | 8.5675 | 8.1428 | -1.0098 | 23.8414 | 8.9866 | 114.1667 | 123.1533 | 195.5182 | 1
248 | 9 | 268 | 265 |  | 0.10512 | 2.8748 | 1.8475 | 8.5675 | 9.1428 | -0.74802 | 31.6957 | 191.1055 | 220.8333 | 411.9388 | 653.9941 | 1
248 | 10 | 66 | 262 |  | 0.10512 | 2.8748 | 1.8475 | 8.5675 | 10.1428 | -0.48622 | 38.0602 | 56.212 | 218.3333 | 274.5453 | 435.8681 | 1
248 | 11 | 349 | 294 |  | 0.10512 | 2.8748 | 1.8475 | 8.5675 | 11.1428 | -0.22442 | 42.1631 | 326.3248 | 245 | 571.3248 | 907.0352 | 1
248 | 12 | 418 | 271 |  | 0.10512 | 2.8748 | 1.8475 | 8.5675 | 12.1428 | 0.037383 | 43.3097 | 400.1916 | 225.8333 | 626.0249 | 993.8772 | 1
248 | 13 | 615 | 218 |  | 0.10512 | 2.8748 | 1.8475 | 8.5675 | 13.1428 | 0.29918 | 41.2678 | 564.125 | 181.6667 | 745.7916 | 1184.0188 | 1
248 | 14 | 676 | 152 |  | 0.10512 | 2.8748 | 1.8475 | 8.5675 | 14.1428 | 0.56098 | 36.4382 | 552.5644 | 126.6667 | 679.231 | 1078.3472 | 1
248 | 15 | 66 | 247 |  | 0.10512 | 2.8748 | 1.8475 | 8.5675 | 15.1428 | 0.82278 | 29.5735 | 43.8624 | 205.8333 | 249.6957 | 396.4169 | 1
248 | 16 | 22 | 198 |  | 0.10512 | 2.8748 | 1.8475 | 8.5675 | 16.1428 | 1.0846 | 21.4185 | 10.323 | 165 | 175.323 | 278.3428 | 1
248 | 17 | 11 | 117 |  | 0.10512 | 2.8748 | 1.8475 | 8.5675 | 17.1428 | 1.3464 | 12.569 | 2.6912 | 97.5 | 100.1912 | 159.0635 | 1
248 | 18 | 0 | 40 |  | 0.10512 | 2.8748 | 1.8475 | 8.5675 | 18.1428 | 1.6082 | 3.492 | 0 | 33.3333 | 33.3333 | 52.92 | 0
248 | 19 | 0 | 5 |  | 0.10512 | 2.8748 | 1.8475 | 8.5675 | 19.1428 | 1.87 | -5.4088 | 0 | 4.1667 | 4.1667 | 6.615 | 0
248 | 20 | 0 | 0 |  | 0.10512 | 2.8748 | 1.8475 | 8.5675 | 20.1428 | 2.1318 | -13.7285 | 0 | 0 | 0 | 0 | 0
248 | 21 | 0 | 0 |  | 0.10512 | 2.8748 | 1.8475 | 8.5675 | 21.1428 | 2.3936 | -21.0094 | 0 | 0 | 0 | 0 | 0
248 | 22 | 0 | 0 |  | 0.10512 | 2.8748 | 1.8475 | 8.5675 | 22.1428 | 2.6554 | -26.7182 | 0 | 0 | 0 | 0 | 0
248 | 23 | 0 | 0 |  | 0.10512 | 2.8748 | 1.8475 | 8.5675 | 23.1428 | 2.9172 | -30.2887 | 0 | 0 | 0 | 0 | 0
248 | 24 | 0 | 0 |  | 0.10512 | 2.8748 | 1.8475 | 8.5675 | 24.1428 | 3.179 | -31.2689 | 0 | 0 | 0 | 0 | 0
249 | 1 | 0 | 0 |  | 0.098461 | 2.892 | 2.201 | 8.921 | 1.1487 | -2.8409 | -29.8729 | 0 | 0 | 0 | 0 | 0
249 | 2 | 0 | 0 |  | 0.098461 | 2.892 | 2.201 | 8.921 | 2.1487 | -2.5791 | -25.6065 | 0 | 0 | 0 | 0 | 0
249 | 3 | 0 | 0 |  | 0.098461 | 2.892 | 2.201 | 8.921 | 3.1487 | -2.3173 | -19.3609 | 0 | 0 | 0 | 0 | 0
249 | 4 | 0 | 0 |  | 0.098461 | 2.892 | 2.201 | 8.921 | 4.1487 | -2.0555 | -11.7082 | 0 | 0 | 0 | 0 | 0
249 | 5 | 0 | 0 |  | 0.098461 | 2.892 | 2.201 | 8.921 | 5.1487 | -1.7937 | -3.1632 | 0 | 0 | 0 | 0 | 0
249 | 6 | 0 | 7 |  | 0.098461 | 2.892 | 2.201 | 8.921 | 6.1487 | -1.5319 | 5.8345 | 0 | 5.8333 | 5.8333 | 9.261 | 0
249 | 7 | 0 | 57 |  | 0.098461 | 2.892 | 2.201 | 8.921 | 7.1487 | -1.2701 | 14.8856 | 0 | 47.5 | 47.5 | 75.411 | 1
249 | 8 | 7 | 138 |  | 0.098461 | 2.892 | 2.201 | 8.921 | 8.1487 | -1.0083 | 23.5748 | 3.6932 | 115 | 118.6932 | 188.4374 | 1
249 | 9 | 0 | 142 |  | 0.098461 | 2.892 | 2.201 | 8.921 | 9.1487 | -0.74647 | 31.4043 | 0 | 118.3333 | 118.3333 | 187.866 | 1
249 | 10 | 6 | 183 |  | 0.098461 | 2.892 | 2.201 | 8.921 | 10.1487 | -0.48467 | 37.7356 | 5.1021 | 152.5 | 157.6021 | 250.2091 | 1
249 | 11 | 10 | 212 |  | 0.098461 | 2.892 | 2.201 | 8.921 | 11.1487 | -0.22287 | 41.8039 | 9.334 | 176.6667 | 186.0006 | 295.2946 | 1
249 | 12 | 21 | 293 |  | 0.098461 | 2.892 | 2.201 | 8.921 | 12.1487 | 0.038925 | 42.9256 | 20.0637 | 244.1667 | 264.2303 | 419.4921 | 1
249 | 13 | 78 | 316 |  | 0.098461 | 2.892 | 2.201 | 8.921 | 13.1487 | 0.30072 | 40.8764 | 71.3622 | 263.3333 | 334.6956 | 531.3627 | 1
249 | 14 | 71 | 292 |  | 0.098461 | 2.892 | 2.201 | 8.921 | 14.1487 | 0.56252 | 36.0534 | 57.8382 | 243.3333 | 301.1716 | 478.14 | 1
249 | 15 | 185 | 255 |  | 0.098461 | 2.892 | 2.201 | 8.921 | 15.1487 | 0.82432 | 29.2006 | 122.3615 | 212.5 | 334.8615 | 531.6261 | 1
249 | 16 | 37 | 186 |  | 0.098461 | 2.892 | 2.201 | 8.921 | 16.1487 | 1.0861 | 21.0559 | 17.2314 | 155 | 172.2314 | 273.4345 | 1
249 | 17 | 67 | 130 |  | 0.098461 | 2.892 | 2.201 | 8.921 | 17.1487 | 1.3479 | 12.2122 | 16.1375 | 108.3333 | 124.4708 | 197.6098 | 0
249 | 18 | 0 | 38 |  | 0.098461 | 2.892 | 2.201 | 8.921 | 18.1487 | 1.6097 | 3.1355 | 0 | 31.6667 | 31.6667 | 50.274 | 0
249 | 19 | 0 | 4 |  | 0.098461 | 2.892 | 2.201 | 8.921 | 19.1487 | 1.8715 | -5.7701 | 0 | 3.3333 | 3.3333 | 5.292 | 0
249 | 20 | 0 | 0 |  | 0.098461 | 2.892 | 2.201 | 8.921 | 20.1487 | 2.1333 | -14.0987 | 0 | 0 | 0 | 0 | 0
249 | 21 | 0 | 0 |  | 0.098461 | 2.892 | 2.201 | 8.921 | 21.1487 | 2.3951 | -21.3904 | 0 | 0 | 0 | 0 | 0
249 | 22 | 0 | 0 |  | 0.098461 | 2.892 | 2.201 | 8.921 | 22.1487 | 2.6569 | -27.1078 | 0 | 0 | 0 | 0 | 0
249 | 23 | 0 | 0 |  | 0.098461 | 2.892 | 2.201 | 8.921 | 23.1487 | 2.9187 | -30.6792 | 0 | 0 | 0 | 0 | 0
249 | 24 | 0 | 0 |  | 0.098461 | 2.892 | 2.201 | 8.921 | 24.1487 | 3.1805 | -31.6478 | 0 | 0 | 0 | 0 | 0
250 | 1 | 0 | 0 |  | 0.091779 | 2.9092 | 2.5581 | 9.2781 | 1.1546 | -2.8393 | -30.2289 | 0 | 0 | 0 | 0 | 0
250 | 2 | 0 | 0 |  | 0.091779 | 2.9092 | 2.5581 | 9.2781 | 2.1546 | -2.5775 | -25.9318 | 0 | 0 | 0 | 0 | 0
250 | 3 | 0 | 0 |  | 0.091779 | 2.9092 | 2.5581 | 9.2781 | 3.1546 | -2.3157 | -19.6564 | 0 | 0 | 0 | 0 | 0
250 | 4 | 0 | 0 |  | 0.091779 | 2.9092 | 2.5581 | 9.2781 | 4.1546 | -2.0539 | -11.9796 | 0 | 0 | 0 | 0 | 0
250 | 5 | 0 | 0 |  | 0.091779 | 2.9092 | 2.5581 | 9.2781 | 5.1546 | -1.7921 | -3.419 | 0 | 0 | 0 | 0 | 0
250 | 6 | 0 | 4 |  | 0.091779 | 2.9092 | 2.5581 | 9.2781 | 6.1546 | -1.5303 | 5.5848 | 0 | 3.3333 | 3.3333 | 5.292 | 0
250 | 7 | 0 | 34 |  | 0.091779 | 2.9092 | 2.5581 | 9.2781 | 7.1546 | -1.2685 | 14.6321 | 0 | 28.3333 | 28.3333 | 44.982 | 1
250 | 8 | 27 | 128 |  | 0.091779 | 2.9092 | 2.5581 | 9.2781 | 8.1546 | -1.0067 | 23.3069 | 14.2171 | 106.6667 | 120.8838 | 191.9151 | 1
250 | 9 | 31 | 207 |  | 0.091779 | 2.9092 | 2.5581 | 9.2781 | 9.1546 | -0.74491 | 31.1114 | 22.0343 | 172.5 | 194.5343 | 308.8426 | 1
250 | 10 | 3 | 182 |  | 0.091779 | 2.9092 | 2.5581 | 9.2781 | 10.1546 | -0.48312 | 37.4094 | 2.5469 | 151.6667 | 154.2136 | 244.8295 | 1
250 | 11 | 5 | 213 |  | 0.091779 | 2.9092 | 2.5581 | 9.2781 | 11.1546 | -0.22132 | 41.443 | 4.6586 | 177.5 | 182.1586 | 289.195 | 1
250 | 12 | 192 | 341 |  | 0.091779 | 2.9092 | 2.5581 | 9.2781 | 12.1546 | 0.040483 | 42.5401 | 183.0481 | 284.1667 | 467.2147 | 741.7501 | 1
250 | 13 | 76 | 313 |  | 0.091779 | 2.9092 | 2.5581 | 9.2781 | 13.1546 | 0.30228 | 40.4834 | 69.3477 | 260.8333 | 330.181 | 524.1954 | 1
250 | 14 | 70 | 289 |  | 0.091779 | 2.9092 | 2.5581 | 9.2781 | 14.1546 | 0.56408 | 35.6669 | 56.8252 | 240.8333 | 297.6586 | 472.5627 | 1
250 | 15 | 44 | 252 |  | 0.091779 | 2.9092 | 2.5581 | 9.2781 | 15.1546 | 0.82588 | 28.8259 | 28.9606 | 210 | 238.9606 | 379.3738 | 1
250 | 16 | 28 | 187 |  | 0.091779 | 2.9092 | 2.5581 | 9.2781 | 16.1546 | 1.0877 | 20.6915 | 12.9403 | 155.8333 | 168.7736 | 267.945 | 1
250 | 17 | 11 | 110 |  | 0.091779 | 2.9092 | 2.5581 | 9.2781 | 17.1546 | 1.3495 | 11.8535 | 2.6073 | 91.6667 | 94.2739 | 149.6693 | 0
250 | 18 | 0 | 35 |  | 0.091779 | 2.9092 | 2.5581 | 9.2781 | 18.1546 | 1.6113 | 2.7772 | 0 | 29.1667 | 29.1667 | 46.305 | 0
250 | 19 | 0 | 2 |  | 0.091779 | 2.9092 | 2.5581 | 9.2781 | 19.1546 | 1.8731 | -6.1332 | 0 | 1.6667 | 1.6667 | 2.646 | 0
250 | 20 | 0 | 0 |  | 0.091779 | 2.9092 | 2.5581 | 9.2781 | 20.1546 | 2.1349 | -14.4707 | 0 | 0 | 0 | 0 | 0
250 | 21 | 0 | 0 |  | 0.091779 | 2.9092 | 2.5581 | 9.2781 | 21.1546 | 2.3967 | -21.7731 | 0 | 0 | 0 | 0 | 0
250 | 22 | 0 | 0 |  | 0.091779 | 2.9092 | 2.5581 | 9.2781 | 22.1546 | 2.6585 | -27.4991 | 0 | 0 | 0 | 0 | 0
250 | 23 | 0 | 0 |  | 0.091779 | 2.9092 | 2.5581 | 9.2781 | 23.1546 | 2.9203 | -31.0713 | 0 | 0 | 0 | 0 | 0
250 | 24 | 0 | 0 |  | 0.091779 | 2.9092 | 2.5581 | 9.2781 | 24.1546 | 3.1821 | -32.028 | 0 | 0 | 0 | 0 | 0
251 | 1 | 0 | 0 |  | 0.085073 | 2.9264 | 2.9184 | 9.6384 | 1.1606 | -2.8377 | -30.5857 | 0 | 0 | 0 | 0 | 0
251 | 2 | 0 | 0 |  | 0.085073 | 2.9264 | 2.9184 | 9.6384 | 2.1606 | -2.5759 | -26.2576 | 0 | 0 | 0 | 0 | 0
251 | 3 | 0 | 0 |  | 0.085073 | 2.9264 | 2.9184 | 9.6384 | 3.1606 | -2.3141 | -19.9521 | 0 | 0 | 0 | 0 | 0
251 | 4 | 0 | 0 |  | 0.085073 | 2.9264 | 2.9184 | 9.6384 | 4.1606 | -2.0523 | -12.2514 | 0 | 0 | 0 | 0 | 0
251 | 5 | 0 | 0 |  | 0.085073 | 2.9264 | 2.9184 | 9.6384 | 5.1606 | -1.7905 | -3.6753 | 0 | 0 | 0 | 0 | 0
251 | 6 | 0 | 4 |  | 0.085073 | 2.9264 | 2.9184 | 9.6384 | 6.1606 | -1.5287 | 5.3345 | 0 | 3.3333 | 3.3333 | 5.292 | 0
251 | 7 | 0 | 33 |  | 0.085073 | 2.9264 | 2.9184 | 9.6384 | 7.1606 | -1.2669 | 14.3777 | 0 | 27.5 | 27.5 | 43.659 | 1
251 | 8 | 0 | 85 |  | 0.085073 | 2.9264 | 2.9184 | 9.6384 | 8.1606 | -1.0051 | 23.0378 | 0 | 70.8333 | 70.8333 | 112.455 | 1
251 | 9 | 0 | 138 |  | 0.085073 | 2.9264 | 2.9184 | 9.6384 | 9.1606 | -0.74334 | 30.8171 | 0 | 115 | 115 | 182.574 | 1
251 | 10 | 3 | 181 |  | 0.085073 | 2.9264 | 2.9184 | 9.6384 | 10.1606 | -0.48154 | 37.0817 | 2.5427 | 150.8333 | 153.376 | 243.4997 | 1
251 | 11 | 5 | 211 |  | 0.085073 | 2.9264 | 2.9184 | 9.6384 | 11.1606 | -0.21974 | 41.0807 | 4.65 | 175.8333 | 180.4833 | 286.5353 | 1
251 | 12 | 21 | 287 |  | 0.085073 | 2.9264 | 2.9184 | 9.6384 | 12.1606 | 0.042055 | 42.153 | 19.977 | 239.1667 | 259.1437 | 411.4165 | 1
251 | 13 | 75 | 310 |  | 0.085073 | 2.9264 | 2.9184 | 9.6384 | 13.1606 | 0.30385 | 40.0888 | 68.2488 | 258.3333 | 326.5822 | 518.4819 | 1
251 | 14 | 69 | 286 |  | 0.085073 | 2.9264 | 2.9184 | 9.6384 | 14.1606 | 0.56565 | 35.2788 | 55.8142 | 238.3333 | 294.1475 | 466.9887 | 1
251 | 15 | 43 | 248 |  | 0.085073 | 2.9264 | 2.9184 | 9.6384 | 15.1606 | 0.82745 | 28.4494 | 28.1618 | 206.6667 | 234.8285 | 372.8137 | 1
251 | 16 | 27 | 184 |  | 0.085073 | 2.9264 | 2.9184 | 9.6384 | 16.1606 | 1.0893 | 20.3252 | 12.3809 | 153.3333 | 165.7142 | 263.0879 | 1
251 | 17 | 10 | 107 |  | 0.085073 | 2.9264 | 2.9184 | 9.6384 | 17.1606 | 1.3511 | 11.4931 | 2.3316 | 89.1667 | 91.4983 | 145.2626 | 0
251 | 18 | 0 | 33 |  | 0.085073 | 2.9264 | 2.9184 | 9.6384 | 18.1606 | 1.6129 | 2.4173 | 0 | 27.5 | 27.5 | 43.659 | 0
251 | 19 | 0 | 2 |  | 0.085073 | 2.9264 | 2.9184 | 9.6384 | 19.1606 | 1.8747 | -6.4978 | 0 | 1.6667 | 1.6667 | 2.646 | 0
251 | 20 | 0 | 0 |  | 0.085073 | 2.9264 | 2.9184 | 9.6384 | 20.1606 | 2.1365 | -14.8441 | 0 | 0 | 0 | 0 | 0
251 | 21 | 0 | 0 |  | 0.085073 | 2.9264 | 2.9184 | 9.6384 | 21.1606 | 2.3982 | -22.1573 | 0 | 0 | 0 | 0 | 0
251 | 22 | 0 | 0 |  | 0.085073 | 2.9264 | 2.9184 | 9.6384 | 22.1606 | 2.66 | -27.8919 | 0 | 0 | 0 | 0 | 0
251 | 23 | 0 | 0 |  | 0.085073 | 2.9264 | 2.9184 | 9.6384 | 23.1606 | 2.9218 | -31.4647 | 0 | 0 | 0 | 0 | 0
251 | 24 | 0 | 0 |  | 0.085073 | 2.9264 | 2.9184 | 9.6384 | 24.1606 | 3.1836 | -32.4094 | 0 | 0 | 0 | 0 | 0
252 | 1 | 0 | 0 |  | 0.078346 | 2.9436 | 3.2814 | 10.0014 | 1.1667 | -2.8362 | -30.9433 | 0 | 0 | 0 | 0 | 0
252 | 2 | 0 | 0 |  | 0.078346 | 2.9436 | 3.2814 | 10.0014 | 2.1667 | -2.5744 | -26.5839 | 0 | 0 | 0 | 0 | 0
252 | 3 | 0 | 0 |  | 0.078346 | 2.9436 | 3.2814 | 10.0014 | 3.1667 | -2.3126 | -20.2481 | 0 | 0 | 0 | 0 | 0
252 | 4 | 0 | 0 |  | 0.078346 | 2.9436 | 3.2814 | 10.0014 | 4.1667 | -2.0508 | -12.5234 | 0 | 0 | 0 | 0 | 0
252 | 5 | 0 | 0 |  | 0.078346 | 2.9436 | 3.2814 | 10.0014 | 5.1667 | -1.789 | -3.932 | 0 | 0 | 0 | 0 | 0
252 | 6 | 0 | 4 |  | 0.078346 | 2.9436 | 3.2814 | 10.0014 | 6.1667 | -1.5272 | 5.0836 | 0 | 3.3333 | 3.3333 | 5.292 | 0
252 | 7 | 0 | 51 |  | 0.078346 | 2.9436 | 3.2814 | 10.0014 | 7.1667 | -1.2654 | 14.1224 | 0 | 42.5 | 42.5 | 67.473 | 1
252 | 8 | 17 | 127 |  | 0.078346 | 2.9436 | 3.2814 | 10.0014 | 8.1667 | -1.0036 | 22.7675 | 8.915 | 105.8333 | 114.7484 | 182.1745 | 1
252 | 9 | 255 | 255 |  | 0.078346 | 2.9436 | 3.2814 | 10.0014 | 9.1667 | -0.74176 | 30.5213 | 180.632 | 212.5 | 393.132 | 624.1364 | 1
252 | 10 | 521 | 173 |  | 0.078346 | 2.9436 | 3.2814 | 10.0014 | 10.1667 | -0.47996 | 36.7524 | 440.8134 | 144.1667 | 584.98 | 928.7143 | 1
252 | 11 | 657 | 158 |  | 0.078346 | 2.9436 | 3.2814 | 10.0014 | 11.1667 | -0.21816 | 40.7169 | 609.8391 | 131.6667 | 741.5057 | 1177.2145 | 1
252 | 12 | 552 | 222 |  | 0.078346 | 2.9436 | 3.2814 | 10.0014 | 12.1667 | 0.043639 | 41.7647 | 523.9279 | 185 | 708.9279 | 1125.4939 | 1
252 | 13 | 211 | 322 |  | 0.078346 | 2.9436 | 3.2814 | 10.0014 | 13.1667 | 0.30544 | 39.693 | 191.471 | 268.3333 | 459.8044 | 729.9854 | 1
252 | 14 | 355 | 268 |  | 0.078346 | 2.9436 | 3.2814 | 10.0014 | 14.1667 | 0.56724 | 34.8892 | 286.1166 | 223.3333 | 509.4499 | 808.8027 | 1
252 | 15 | 555 | 167 |  | 0.078346 | 2.9436 | 3.2814 | 10.0014 | 15.1667 | 0.82904 | 28.0713 | 361.6437 | 139.1667 | 500.8104 | 795.0866 | 1
252 | 16 | 387 | 153 |  | 0.078346 | 2.9436 | 3.2814 | 10.0014 | 16.1667 | 1.0908 | 19.9574 | 176.0498 | 127.5 | 303.5498 | 481.9156 | 1
252 | 17 | 298 | 100 |  | 0.078346 | 2.9436 | 3.2814 | 10.0014 | 17.1667 | 1.3526 | 11.1312 | 68.3203 | 83.3333 | 151.6536 | 240.7653 | 0
252 | 18 | 0 | 40 |  | 0.078346 | 2.9436 | 3.2814 | 10.0014 | 18.1667 | 1.6144 | 2.0559 | 0 | 33.3333 | 33.3333 | 52.92 | 0
252 | 19 | 0 | 3 |  | 0.078346 | 2.9436 | 3.2814 | 10.0014 | 19.1667 | 1.8762 | -6.8638 | 0 | 2.5 | 2.5 | 3.969 | 0
252 | 20 | 0 | 0 |  | 0.078346 | 2.9436 | 3.2814 | 10.0014 | 20.1667 | 2.138 | -15.219 | 0 | 0 | 0 | 0 | 0
252 | 21 | 0 | 0 |  | 0.078346 | 2.9436 | 3.2814 | 10.0014 | 21.1667 | 2.3998 | -22.543 | 0 | 0 | 0 | 0 | 0
252 | 22 | 0 | 0 |  | 0.078346 | 2.9436 | 3.2814 | 10.0014 | 22.1667 | 2.6616 | -28.2861 | 0 | 0 | 0 | 0 | 0
252 | 23 | 0 | 0 |  | 0.078346 | 2.9436 | 3.2814 | 10.0014 | 23.1667 | 2.9234 | -31.8595 | 0 | 0 | 0 | 0 | 0
252 | 24 | 0 | 0 |  | 0.078346 | 2.9436 | 3.2814 | 10.0014 | 24.1667 | 3.1852 | -32.7919 | 0 | 0 | 0 | 0 | 0
253 | 1 | 0 | 0 |  | 0.071599 | 2.9608 | 3.6469 | 10.3669 | 1.1728 | -2.8346 | -31.3015 | 0 | 0 | 0 | 0 | 0
253 | 2 | 0 | 0 |  | 0.071599 | 2.9608 | 3.6469 | 10.3669 | 2.1728 | -2.5728 | -26.9105 | 0 | 0 | 0 | 0 | 0
253 | 3 | 0 | 0 |  | 0.071599 | 2.9608 | 3.6469 | 10.3669 | 3.1728 | -2.311 | -20.5444 | 0 | 0 | 0 | 0 | 0
253 | 4 | 0 | 0 |  | 0.071599 | 2.9608 | 3.6469 | 10.3669 | 4.1728 | -2.0492 | -12.7957 | 0 | 0 | 0 | 0 | 0
253 | 5 | 0 | 0 |  | 0.071599 | 2.9608 | 3.6469 | 10.3669 | 5.1728 | -1.7874 | -4.189 | 0 | 0 | 0 | 0 | 0
253 | 6 | 0 | 9 |  | 0.071599 | 2.9608 | 3.6469 | 10.3669 | 6.1728 | -1.5256 | 4.8321 | 0 | 7.5 | 7.5 | 11.907 | 0
253 | 7 | 128 | 66 |  | 0.071599 | 2.9608 | 3.6469 | 10.3669 | 7.1728 | -1.2638 | 13.8662 | 39.1335 | 55 | 94.1335 | 149.4464 | 1
253 | 8 | 371 | 113 |  | 0.071599 | 2.9608 | 3.6469 | 10.3669 | 8.1728 | -1.002 | 22.496 | 194.147 | 94.1667 | 288.3137 | 457.7268 | 1
253 | 9 | 593 | 113 |  | 0.071599 | 2.9608 | 3.6469 | 10.3669 | 9.1728 | -0.74016 | 30.2243 | 419.311 | 94.1667 | 513.4776 | 815.1971 | 1
253 | 10 | 712 | 110 |  | 0.071599 | 2.9608 | 3.6469 | 10.3669 | 10.1728 | -0.47836 | 36.4218 | 601.3459 | 91.6667 | 693.0126 | 1100.2268 | 1
253 | 11 | 733 | 136 |  | 0.071599 | 2.9608 | 3.6469 | 10.3669 | 11.1728 | -0.21657 | 40.3518 | 679.0478 | 113.3333 | 792.3811 | 1257.9843 | 1
253 | 12 | 551 | 221 |  | 0.071599 | 2.9608 | 3.6469 | 10.3669 | 12.1728 | 0.045234 | 41.3751 | 521.7701 | 184.1667 | 705.9368 | 1120.7453 | 1
253 | 13 | 677 | 162 |  | 0.071599 | 2.9608 | 3.6469 | 10.3669 | 13.1728 | 0.30703 | 39.2958 | 612.586 | 135 | 747.586 | 1186.8675 | 1
253 | 14 | 189 | 299 |  | 0.071599 | 2.9608 | 3.6469 | 10.3669 | 14.1728 | 0.56883 | 34.4982 | 151.7617 | 249.1667 | 400.9283 | 636.5138 | 1
253 | 15 | 66 | 231 |  | 0.071599 | 2.9608 | 3.6469 | 10.3669 | 15.1728 | 0.83063 | 27.6918 | 42.7844 | 192.5 | 235.2844 | 373.5375 | 1
253 | 16 | 0 | 118 |  | 0.071599 | 2.9608 | 3.6469 | 10.3669 | 16.1728 | 1.0924 | 19.5882 | 0 | 98.3333 | 98.3333 | 156.114 | 1
253 | 17 | 0 | 65 |  | 0.071599 | 2.9608 | 3.6469 | 10.3669 | 17.1728 | 1.3542 | 10.7678 | 0 | 54.1667 | 54.1667 | 85.995 | 0
253 | 18 | 0 | 18 |  | 0.071599 | 2.9608 | 3.6469 | 10.3669 | 18.1728 | 1.616 | 1.6932 | 0 | 15 | 15 | 23.814 | 0
253 | 19 | 0 | 1 |  | 0.071599 | 2.9608 | 3.6469 | 10.3669 | 19.1728 | 1.8778 | -7.2311 | 0 | 0.83333 | 0.83333 | 1.323 | 0
253 | 20 | 0 | 0 |  | 0.071599 | 2.9608 | 3.6469 | 10.3669 | 20.1728 | 2.1396 | -15.5951 | 0 | 0 | 0 | 0 | 0
253 | 21 | 0 | 0 |  | 0.071599 | 2.9608 | 3.6469 | 10.3669 | 21.1728 | 2.4014 | -22.9298 | 0 | 0 | 0 | 0 | 0
253 | 22 | 0 | 0 |  | 0.071599 | 2.9608 | 3.6469 | 10.3669 | 22.1728 | 2.6632 | -28.6816 | 0 | 0 | 0 | 0 | 0
253 | 23 | 0 | 0 |  | 0.071599 | 2.9608 | 3.6469 | 10.3669 | 23.1728 | 2.925 | -32.2555 | 0 | 0 | 0 | 0 | 0
253 | 24 | 0 | 0 |  | 0.071599 | 2.9608 | 3.6469 | 10.3669 | 24.1728 | 3.1868 | -33.1753 | 0 | 0 | 0 | 0 | 0
254 | 1 | 0 | 0 |  | 0.064834 | 2.9781 | 4.0144 | 10.7344 | 1.1789 | -2.833 | -31.6603 | 0 | 0 | 0 | 0 | 0
254 | 2 | 0 | 0 |  | 0.064834 | 2.9781 | 4.0144 | 10.7344 | 2.1789 | -2.5712 | -27.2373 | 0 | 0 | 0 | 0 | 0
254 | 3 | 0 | 0 |  | 0.064834 | 2.9781 | 4.0144 | 10.7344 | 3.1789 | -2.3094 | -20.8407 | 0 | 0 | 0 | 0 | 0
254 | 4 | 0 | 0 |  | 0.064834 | 2.9781 | 4.0144 | 10.7344 | 4.1789 | -2.0476 | -13.0681 | 0 | 0 | 0 | 0 | 0
254 | 5 | 0 | 0 |  | 0.064834 | 2.9781 | 4.0144 | 10.7344 | 5.1789 | -1.7858 | -4.4464 | 0 | 0 | 0 | 0 | 0
254 | 6 | 0 | 5 |  | 0.064834 | 2.9781 | 4.0144 | 10.7344 | 6.1789 | -1.524 | 4.58 | 0 | 4.1667 | 4.1667 | 6.615 | 0
254 | 7 | 0 | 48 |  | 0.064834 | 2.9781 | 4.0144 | 10.7344 | 7.1789 | -1.2622 | 13.6091 | 0 | 40 | 40 | 63.504 | 1
254 | 8 | 0 | 80 |  | 0.064834 | 2.9781 | 4.0144 | 10.7344 | 8.1789 | -1.0004 | 22.2234 | 0 | 66.6667 | 66.6667 | 105.84 | 1
254 | 9 | 155 | 202 |  | 0.064834 | 2.9781 | 4.0144 | 10.7344 | 9.1789 | -0.73856 | 29.9258 | 109.4002 | 168.3333 | 277.7335 | 440.9298 | 1
254 | 10 | 3 | 176 |  | 0.064834 | 2.9781 | 4.0144 | 10.7344 | 10.1789 | -0.47676 | 36.0897 | 2.5291 | 146.6667 | 149.1958 | 236.8632 | 1
254 | 11 | 5 | 206 |  | 0.064834 | 2.9781 | 4.0144 | 10.7344 | 11.1789 | -0.21496 | 39.9854 | 4.6226 | 171.6667 | 176.2893 | 279.8769 | 1
254 | 12 | 5 | 220 |  | 0.064834 | 2.9781 | 4.0144 | 10.7344 | 12.1789 | 0.046838 | 40.9844 | 4.7235 | 183.3333 | 188.0569 | 298.5591 | 1
254 | 13 | 5 | 218 |  | 0.064834 | 2.9781 | 4.0144 | 10.7344 | 13.1789 | 0.30864 | 38.8975 | 4.511 | 181.6667 | 186.1777 | 295.5757 | 1
254 | 14 | 4 | 198 |  | 0.064834 | 2.9781 | 4.0144 | 10.7344 | 14.1789 | 0.57044 | 34.106 | 3.1997 | 165 | 168.1997 | 267.0339 | 1
254 | 15 | 66 | 228 |  | 0.064834 | 2.9781 | 4.0144 | 10.7344 | 15.1789 | 0.83224 | 27.311 | 42.5596 | 190 | 232.5596 | 369.2116 | 1
254 | 16 | 27 | 175 |  | 0.064834 | 2.9781 | 4.0144 | 10.7344 | 16.1789 | 1.094 | 19.2176 | 12.0828 | 145.8333 | 157.9161 | 250.7076 | 1
254 | 17 | 8 | 98 |  | 0.064834 | 2.9781 | 4.0144 | 10.7344 | 17.1789 | 1.3558 | 10.4033 | 1.7711 | 81.6667 | 83.4377 | 132.4657 | 0
254 | 18 | 46 | 41 |  | 0.064834 | 2.9781 | 4.0144 | 10.7344 | 18.1789 | 1.6176 | 1.3293 | 0 | 34.1667 | 34.1667 | 54.243 | 0
254 | 19 | 0 | 2 |  | 0.064834 | 2.9781 | 4.0144 | 10.7344 | 19.1789 | 1.8794 | -7.5995 | 0 | 1.6667 | 1.6667 | 2.646 | 0
254 | 20 | 0 | 0 |  | 0.064834 | 2.9781 | 4.0144 | 10.7344 | 20.1789 | 2.1412 | -15.9722 | 0 | 0 | 0 | 0 | 0
254 | 21 | 0 | 0 |  | 0.064834 | 2.9781 | 4.0144 | 10.7344 | 21.1789 | 2.403 | -23.3178 | 0 | 0 | 0 | 0 | 0
254 | 22 | 0 | 0 |  | 0.064834 | 2.9781 | 4.0144 | 10.7344 | 22.1789 | 2.6648 | -29.0782 | 0 | 0 | 0 | 0 | 0
254 | 23 | 0 | 0 |  | 0.064834 | 2.9781 | 4.0144 | 10.7344 | 23.1789 | 2.9266 | -32.6526 | 0 | 0 | 0 | 0 | 0
254 | 24 | 0 | 0 |  | 0.064834 | 2.9781 | 4.0144 | 10.7344 | 24.1789 | 3.1884 | -33.5596 | 0 | 0 | 0 | 0 | 0
255 | 1 | 0 | 0 |  | 0.058053 | 2.9953 | 4.3835 | 11.1035 | 1.1851 | -2.8313 | -32.0195 | 0 | 0 | 0 | 0 | 0
255 | 2 | 0 | 0 |  | 0.058053 | 2.9953 | 4.3835 | 11.1035 | 2.1851 | -2.5695 | -27.5644 | 0 | 0 | 0 | 0 | 0
255 | 3 | 0 | 0 |  | 0.058053 | 2.9953 | 4.3835 | 11.1035 | 3.1851 | -2.3077 | -21.1372 | 0 | 0 | 0 | 0 | 0
255 | 4 | 0 | 0 |  | 0.058053 | 2.9953 | 4.3835 | 11.1035 | 4.1851 | -2.0459 | -13.3407 | 0 | 0 | 0 | 0 | 0
255 | 5 | 0 | 0 |  | 0.058053 | 2.9953 | 4.3835 | 11.1035 | 5.1851 | -1.7841 | -4.7041 | 0 | 0 | 0 | 0 | 0
255 | 6 | 0 | 8 |  | 0.058053 | 2.9953 | 4.3835 | 11.1035 | 6.1851 | -1.5223 | 4.3273 | 0 | 6.6667 | 6.6667 | 10.584 | 0
255 | 7 | 214 | 46 |  | 0.058053 | 2.9953 | 4.3835 | 11.1035 | 7.1851 | -1.2605 | 13.3512 | 64.967 | 38.3333 | 103.3003 | 163.9996 | 1
255 | 8 | 103 | 156 |  | 0.058053 | 2.9953 | 4.3835 | 11.1035 | 8.1851 | -0.99875 | 21.9498 | 53.6654 | 130 | 183.6654 | 291.5872 | 1
255 | 9 | 458 | 156 |  | 0.058053 | 2.9953 | 4.3835 | 11.1035 | 9.1851 | -0.73695 | 29.6261 | 322.6518 | 130 | 452.6518 | 718.6301 | 1
255 | 10 | 192 | 255 |  | 0.058053 | 2.9953 | 4.3835 | 11.1035 | 10.1851 | -0.47515 | 35.7563 | 161.5588 | 212.5 | 374.0588 | 593.8558 | 1
255 | 11 | 193 | 304 |  | 0.058053 | 2.9953 | 4.3835 | 11.1035 | 11.1851 | -0.21335 | 39.6178 | 178.0629 | 253.3333 | 431.3962 | 684.8846 | 1
255 | 12 | 78 | 304 |  | 0.058053 | 2.9953 | 4.3835 | 11.1035 | 12.1851 | 0.048448 | 40.5926 | 73.5079 | 253.3333 | 326.8413 | 518.8932 | 1
255 | 13 | 350 | 294 |  | 0.058053 | 2.9953 | 4.3835 | 11.1035 | 13.1851 | 0.31025 | 38.4982 | 314.83 | 245 | 559.83 | 888.786 | 1
255 | 14 | 587 | 190 |  | 0.058053 | 2.9953 | 4.3835 | 11.1035 | 14.1851 | 0.57205 | 33.7126 | 467.7469 | 158.3333 | 626.0803 | 993.965 | 1
255 | 15 | 662 | 118 |  | 0.058053 | 2.9953 | 4.3835 | 11.1035 | 15.1851 | 0.83385 | 26.929 | 424.6023 | 98.3333 | 522.9356 | 830.2126 | 1
255 | 16 | 498 | 125 |  | 0.058053 | 2.9953 | 4.3835 | 11.1035 | 16.1851 | 1.0956 | 18.8459 | 220.9915 | 104.1667 | 325.1581 | 516.2211 | 1
255 | 17 | 291 | 96 |  | 0.058053 | 2.9953 | 4.3835 | 11.1035 | 17.1851 | 1.3574 | 10.0376 | 63.2651 | 80 | 143.2651 | 227.4477 | 0
255 | 18 | 48 | 38 |  | 0.058053 | 2.9953 | 4.3835 | 11.1035 | 18.1851 | 1.6192 | 0.96433 | 0 | 31.6667 | 31.6667 | 50.274 | 0
255 | 19 | 0 | 1 |  | 0.058053 | 2.9953 | 4.3835 | 11.1035 | 19.1851 | 1.881 | -7.9689 | 0 | 0.83333 | 0.83333 | 1.323 | 0
255 | 20 | 0 | 0 |  | 0.058053 | 2.9953 | 4.3835 | 11.1035 | 20.1851 | 2.1428 | -16.3504 | 0 | 0 | 0 | 0 | 0
255 | 21 | 0 | 0 |  | 0.058053 | 2.9953 | 4.3835 | 11.1035 | 21.1851 | 2.4046 | -23.7067 | 0 | 0 | 0 | 0 | 0
255 | 22 | 0 | 0 |  | 0.058053 | 2.9953 | 4.3835 | 11.1035 | 22.1851 | 2.6664 | -29.4758 | 0 | 0 | 0 | 0 | 0
255 | 23 | 0 | 0 |  | 0.058053 | 2.9953 | 4.3835 | 11.1035 | 23.1851 | 2.9282 | -33.0507 | 0 | 0 | 0 | 0 | 0
255 | 24 | 0 | 0 |  | 0.058053 | 2.9953 | 4.3835 | 11.1035 | 24.1851 | 3.19 | -33.9447 | 0 | 0 | 0 | 0 | 0
256 | 1 | 0 | 0 |  | 0.051258 | 3.0125 | 4.7539 | 11.4739 | 1.1912 | -2.8297 | -32.3791 | 0 | 0 | 0 | 0 | 0
256 | 2 | 0 | 0 |  | 0.051258 | 3.0125 | 4.7539 | 11.4739 | 2.1912 | -2.5679 | -27.8916 | 0 | 0 | 0 | 0 | 0
256 | 3 | 0 | 0 |  | 0.051258 | 3.0125 | 4.7539 | 11.4739 | 3.1912 | -2.3061 | -21.4337 | 0 | 0 | 0 | 0 | 0
256 | 4 | 0 | 0 |  | 0.051258 | 3.0125 | 4.7539 | 11.4739 | 4.1912 | -2.0443 | -13.6134 | 0 | 0 | 0 | 0 | 0
256 | 5 | 0 | 0 |  | 0.051258 | 3.0125 | 4.7539 | 11.4739 | 5.1912 | -1.7825 | -4.9622 | 0 | 0 | 0 | 0 | 0
256 | 6 | 0 | 7 |  | 0.051258 | 3.0125 | 4.7539 | 11.4739 | 6.1912 | -1.5207 | 4.074 | 0 | 5.8333 | 5.8333 | 9.261 | 0
256 | 7 | 23 | 53 |  | 0.051258 | 3.0125 | 4.7539 | 11.4739 | 7.1912 | -1.2589 | 13.0925 | 6.9573 | 44.1667 | 51.1239 | 81.1644 | 1
256 | 8 | 106 | 126 |  | 0.051258 | 3.0125 | 4.7539 | 11.4739 | 8.1912 | -0.99713 | 21.675 | 55.1034 | 105 | 160.1034 | 254.1802 | 1
256 | 9 | 148 | 202 |  | 0.051258 | 3.0125 | 4.7539 | 11.4739 | 9.1912 | -0.73533 | 29.3252 | 104.0613 | 168.3333 | 272.3947 | 432.4538 | 1
256 | 10 | 115 | 296 |  | 0.051258 | 3.0125 | 4.7539 | 11.4739 | 10.1912 | -0.47353 | 35.4217 | 96.5794 | 246.6667 | 343.246 | 544.9374 | 1
256 | 11 | 194 | 301 |  | 0.051258 | 3.0125 | 4.7539 | 11.4739 | 11.1912 | -0.21174 | 39.2491 | 178.6038 | 250.8333 | 429.4371 | 681.7744 | 1
256 | 12 | 199 | 322 |  | 0.051258 | 3.0125 | 4.7539 | 11.4739 | 12.1912 | 0.050064 | 40.1999 | 187.0723 | 268.3333 | 455.4056 | 723.002 | 1
256 | 13 | 526 | 224 |  | 0.051258 | 3.0125 | 4.7539 | 11.4739 | 13.1912 | 0.31186 | 38.0981 | 471.7001 | 186.6667 | 658.3668 | 1045.2231 | 1
256 | 14 | 654 | 146 |  | 0.051258 | 3.0125 | 4.7539 | 11.4739 | 14.1912 | 0.57366 | 33.3184 | 519.0848 | 121.6667 | 640.7515 | 1017.2571 | 1
256 | 15 | 646 | 117 |  | 0.051258 | 3.0125 | 4.7539 | 11.4739 | 15.1912 | 0.83546 | 26.546 | 412.0857 | 97.5 | 509.5857 | 809.0183 | 1
256 | 16 | 502 | 115 |  | 0.051258 | 3.0125 | 4.7539 | 11.4739 | 16.1912 | 1.0973 | 18.4732 | 220.8668 | 95.8333 | 316.7001 | 502.7931 | 1
256 | 17 | 272 | 95 |  | 0.051258 | 3.0125 | 4.7539 | 11.4739 | 17.1912 | 1.3591 | 9.6709 | 58.0466 | 79.1667 | 137.2133 | 217.8398 | 0
256 | 18 | 24 | 36 |  | 0.051258 | 3.0125 | 4.7539 | 11.4739 | 18.1912 | 1.6209 | 0.5985 | 0 | 30 | 30 | 47.628 | 0
256 | 19 | 0 | 1 |  | 0.051258 | 3.0125 | 4.7539 | 11.4739 | 19.1912 | 1.8827 | -8.3392 | 0 | 0.83333 | 0.83333 | 1.323 | 0
256 | 20 | 0 | 0 |  | 0.051258 | 3.0125 | 4.7539 | 11.4739 | 20.1912 | 2.1445 | -16.7293 | 0 | 0 | 0 | 0 | 0
256 | 21 | 0 | 0 |  | 0.051258 | 3.0125 | 4.7539 | 11.4739 | 21.1912 | 2.4063 | -24.0965 | 0 | 0 | 0 | 0 | 0
256 | 22 | 0 | 0 |  | 0.051258 | 3.0125 | 4.7539 | 11.4739 | 22.1912 | 2.6681 | -29.8744 | 0 | 0 | 0 | 0 | 0
256 | 23 | 0 | 0 |  | 0.051258 | 3.0125 | 4.7539 | 11.4739 | 23.1912 | 2.9299 | -33.4496 | 0 | 0 | 0 | 0 | 0
256 | 24 | 0 | 0 |  | 0.051258 | 3.0125 | 4.7539 | 11.4739 | 24.1912 | 3.1917 | -34.3305 | 0 | 0 | 0 | 0 | 0
257 | 1 | 0 | 0 |  | 0.044449 | 3.0297 | 5.1251 | 11.8451 | 1.1974 | -2.8281 | -32.739 | 0 | 0 | 0 | 0 | 0
257 | 2 | 0 | 0 |  | 0.044449 | 3.0297 | 5.1251 | 11.8451 | 2.1974 | -2.5663 | -28.2189 | 0 | 0 | 0 | 0 | 0
257 | 3 | 0 | 0 |  | 0.044449 | 3.0297 | 5.1251 | 11.8451 | 3.1974 | -2.3045 | -21.7303 | 0 | 0 | 0 | 0 | 0
257 | 4 | 0 | 0 |  | 0.044449 | 3.0297 | 5.1251 | 11.8451 | 4.1974 | -2.0427 | -13.8862 | 0 | 0 | 0 | 0 | 0
257 | 5 | 0 | 0 |  | 0.044449 | 3.0297 | 5.1251 | 11.8451 | 5.1974 | -1.7809 | -5.2205 | 0 | 0 | 0 | 0 | 0
257 | 6 | 0 | 6 |  | 0.044449 | 3.0297 | 5.1251 | 11.8451 | 6.1974 | -1.5191 | 3.8202 | 0 | 5 | 5 | 7.938 | 0
257 | 7 | 196 | 45 |  | 0.044449 | 3.0297 | 5.1251 | 11.8451 | 7.1974 | -1.2573 | 12.8329 | 59.0706 | 37.5 | 96.5706 | 153.3154 | 1
257 | 8 | 373 | 103 |  | 0.044449 | 3.0297 | 5.1251 | 11.8451 | 8.1974 | -0.99551 | 21.3992 | 193.4519 | 85.8333 | 279.2852 | 443.3932 | 1
257 | 9 | 555 | 118 |  | 0.044449 | 3.0297 | 5.1251 | 11.8451 | 9.1974 | -0.73371 | 29.0231 | 389.4537 | 98.3333 | 487.787 | 774.4107 | 1
257 | 10 | 616 | 141 |  | 0.044449 | 3.0297 | 5.1251 | 11.8451 | 10.1974 | -0.47191 | 35.0859 | 516.2977 | 117.5 | 633.7977 | 1006.2172 | 1
257 | 11 | 538 | 200 |  | 0.044449 | 3.0297 | 5.1251 | 11.8451 | 11.1974 | -0.21012 | 38.8794 | 494.2187 | 166.6667 | 660.8854 | 1049.2217 | 1
257 | 12 | 636 | 188 |  | 0.044449 | 3.0297 | 5.1251 | 11.8451 | 12.1974 | 0.051684 | 39.8064 | 596.3542 | 156.6667 | 753.0209 | 1195.4959 | 1
257 | 13 | 727 | 142 |  | 0.044449 | 3.0297 | 5.1251 | 11.8451 | 13.1974 | 0.31348 | 37.6971 | 649.9182 | 118.3333 | 768.2516 | 1219.6762 | 1
257 | 14 | 523 | 197 |  | 0.044449 | 3.0297 | 5.1251 | 11.8451 | 14.1974 | 0.57528 | 32.9233 | 413.4454 | 164.1667 | 577.6121 | 917.017 | 1
257 | 15 | 575 | 141 |  | 0.044449 | 3.0297 | 5.1251 | 11.8451 | 15.1974 | 0.83708 | 26.1621 | 364.7656 | 117.5 | 482.2656 | 765.6449 | 1
257 | 16 | 490 | 117 |  | 0.044449 | 3.0297 | 5.1251 | 11.8451 | 16.1974 | 1.0989 | 18.0996 | 213.7181 | 97.5 | 311.2181 | 494.0898 | 1
257 | 17 | 147 | 98 |  | 0.044449 | 3.0297 | 5.1251 | 11.8451 | 17.1974 | 1.3607 | 9.3034 | 30.78 | 81.6667 | 112.4467 | 178.5203 | 0
257 | 18 | 0 | 20 |  | 0.044449 | 3.0297 | 5.1251 | 11.8451 | 18.1974 | 1.6225 | 0.23193 | 0 | 16.6667 | 16.6667 | 26.46 | 0
257 | 19 | 0 | 0 |  | 0.044449 | 3.0297 | 5.1251 | 11.8451 | 19.1974 | 1.8843 | -8.7101 | 0 | 0 | 0 | 0 | 0
257 | 20 | 0 | 0 |  | 0.044449 | 3.0297 | 5.1251 | 11.8451 | 20.1974 | 2.1461 | -17.1089 | 0 | 0 | 0 | 0 | 0
257 | 21 | 0 | 0 |  | 0.044449 | 3.0297 | 5.1251 | 11.8451 | 21.1974 | 2.4079 | -24.487 | 0 | 0 | 0 | 0 | 0
257 | 22 | 0 | 0 |  | 0.044449 | 3.0297 | 5.1251 | 11.8451 | 22.1974 | 2.6697 | -30.2736 | 0 | 0 | 0 | 0 | 0
257 | 23 | 0 | 0 |  | 0.044449 | 3.0297 | 5.1251 | 11.8451 | 23.1974 | 2.9315 | -33.8492 | 0 | 0 | 0 | 0 | 0
257 | 24 | 0 | 0 |  | 0.044449 | 3.0297 | 5.1251 | 11.8451 | 24.1974 | 3.1933 | -34.7169 | 0 | 0 | 0 | 0 | 0
258 | 1 | 0 | 0 |  | 0.03763 | 3.0469 | 5.4967 | 12.2167 | 1.2036 | -2.8265 | -33.0991 | 0 | 0 | 0 | 0 | 0
258 | 2 | 0 | 0 |  | 0.03763 | 3.0469 | 5.4967 | 12.2167 | 2.2036 | -2.5647 | -28.5462 | 0 | 0 | 0 | 0 | 0
258 | 3 | 0 | 0 |  | 0.03763 | 3.0469 | 5.4967 | 12.2167 | 3.2036 | -2.3029 | -22.0268 | 0 | 0 | 0 | 0 | 0
258 | 4 | 0 | 0 |  | 0.03763 | 3.0469 | 5.4967 | 12.2167 | 4.2036 | -2.0411 | -14.1591 | 0 | 0 | 0 | 0 | 0
258 | 5 | 0 | 0 |  | 0.03763 | 3.0469 | 5.4967 | 12.2167 | 5.2036 | -1.7793 | -5.4791 | 0 | 0 | 0 | 0 | 0
258 | 6 | 0 | 3 |  | 0.03763 | 3.0469 | 5.4967 | 12.2167 | 6.2036 | -1.5175 | 3.5659 | 0 | 2.5 | 2.5 | 3.969 | 0
258 | 7 | 0 | 41 |  | 0.03763 | 3.0469 | 5.4967 | 12.2167 | 7.2036 | -1.2557 | 12.5726 | 0 | 34.1667 | 34.1667 | 54.243 | 1
258 | 8 | 14 | 115 |  | 0.03763 | 3.0469 | 5.4967 | 12.2167 | 8.2036 | -0.99389 | 21.1224 | 7.2437 | 95.8333 | 103.077 | 163.645 | 1
258 | 9 | 0 | 127 |  | 0.03763 | 3.0469 | 5.4967 | 12.2167 | 9.2036 | -0.73209 | 28.7198 | 0 | 105.8333 | 105.8333 | 168.021 | 1
258 | 10 | 65 | 237 |  | 0.03763 | 3.0469 | 5.4967 | 12.2167 | 10.2036 | -0.47029 | 34.749 | 54.3677 | 197.5 | 251.8677 | 399.8652 | 1
258 | 11 | 70 | 279 |  | 0.03763 | 3.0469 | 5.4967 | 12.2167 | 11.2036 | -0.20849 | 38.5088 | 64.1591 | 232.5 | 296.6591 | 470.9759 | 1
258 | 12 | 72 | 298 |  | 0.03763 | 3.0469 | 5.4967 | 12.2167 | 12.2036 | 0.053305 | 39.4122 | 67.3355 | 248.3333 | 315.6689 | 501.1559 | 1
258 | 13 | 71 | 294 |  | 0.03763 | 3.0469 | 5.4967 | 12.2167 | 13.2036 | 0.3151 | 37.2955 | 63.2702 | 245 | 308.2702 | 489.4097 | 1
258 | 14 | 68 | 266 |  | 0.03763 | 3.0469 | 5.4967 | 12.2167 | 14.2036 | 0.5769 | 32.5275 | 53.5365 | 221.6667 | 275.2032 | 436.9126 | 1
258 | 15 | 18 | 239 |  | 0.03763 | 3.0469 | 5.4967 | 12.2167 | 15.2036 | 0.8387 | 25.7774 | 11.3546 | 199.1667 | 210.5212 | 334.2235 | 1
258 | 16 | 24 | 162 |  | 0.03763 | 3.0469 | 5.4967 | 12.2167 | 16.2036 | 1.1005 | 17.7252 | 10.3756 | 135 | 145.3756 | 230.7983 | 1
258 | 17 | 3 | 87 |  | 0.03763 | 3.0469 | 5.4967 | 12.2167 | 17.2036 | 1.3623 | 8.9353 | 0.61606 | 72.5 | 73.1161 | 116.079 | 0
258 | 18 | 0 | 18 |  | 0.03763 | 3.0469 | 5.4967 | 12.2167 | 18.2036 | 1.6241 | -0.13526 | 0 | 15 | 15 | 23.814 | 0
258 | 19 | 0 | 0 |  | 0.03763 | 3.0469 | 5.4967 | 12.2167 | 19.2036 | 1.8859 | -9.0816 | 0 | 0 | 0 | 0 | 0
258 | 20 | 0 | 0 |  | 0.03763 | 3.0469 | 5.4967 | 12.2167 | 20.2036 | 2.1477 | -17.4891 | 0 | 0 | 0 | 0 | 0
258 | 21 | 0 | 0 |  | 0.03763 | 3.0469 | 5.4967 | 12.2167 | 21.2036 | 2.4095 | -24.8781 | 0 | 0 | 0 | 0 | 0
258 | 22 | 0 | 0 |  | 0.03763 | 3.0469 | 5.4967 | 12.2167 | 22.2036 | 2.6713 | -30.6736 | 0 | 0 | 0 | 0 | 0
258 | 23 | 0 | 0 |  | 0.03763 | 3.0469 | 5.4967 | 12.2167 | 23.2036 | 2.9331 | -34.2495 | 0 | 0 | 0 | 0 | 0
258 | 24 | 0 | 0 |  | 0.03763 | 3.0469 | 5.4967 | 12.2167 | 24.2036 | 3.1949 | -35.1037 | 0 | 0 | 0 | 0 | 0
259 | 1 | 0 | 0 |  | 0.030801 | 3.0641 | 5.8683 | 12.5883 | 1.2098 | -2.8249 | -33.4594 | 0 | 0 | 0 | 0 | 0
259 | 2 | 0 | 0 |  | 0.030801 | 3.0641 | 5.8683 | 12.5883 | 2.2098 | -2.5631 | -28.8735 | 0 | 0 | 0 | 0 | 0
259 | 3 | 0 | 0 |  | 0.030801 | 3.0641 | 5.8683 | 12.5883 | 3.2098 | -2.3013 | -22.3232 | 0 | 0 | 0 | 0 | 0
259 | 4 | 0 | 0 |  | 0.030801 | 3.0641 | 5.8683 | 12.5883 | 4.2098 | -2.0395 | -14.432 | 0 | 0 | 0 | 0 | 0
259 | 5 | 0 | 0 |  | 0.030801 | 3.0641 | 5.8683 | 12.5883 | 5.2098 | -1.7777 | -5.7379 | 0 | 0 | 0 | 0 | 0
259 | 6 | 0 | 3 |  | 0.030801 | 3.0641 | 5.8683 | 12.5883 | 6.2098 | -1.5159 | 3.3112 | 0 | 2.5 | 2.5 | 3.969 | 0
259 | 7 | 35 | 53 |  | 0.030801 | 3.0641 | 5.8683 | 12.5883 | 7.2098 | -1.2541 | 12.3115 | 10.4689 | 44.1667 | 54.6356 | 86.7394 | 0
259 | 8 | 322 | 110 |  | 0.030801 | 3.0641 | 5.8683 | 12.5883 | 8.2098 | -0.99227 | 20.8446 | 166.1982 | 91.6667 | 257.8648 | 409.3862 | 1
259 | 9 | 563 | 113 |  | 0.030801 | 3.0641 | 5.8683 | 12.5883 | 9.2098 | -0.73047 | 28.4154 | 393.4303 | 94.1667 | 487.597 | 774.1089 | 1
259 | 10 | 694 | 109 |  | 0.030801 | 3.0641 | 5.8683 | 12.5883 | 10.2098 | -0.46867 | 34.411 | 579.2568 | 90.8333 | 670.0901 | 1063.8351 | 1
259 | 11 | 665 | 144 |  | 0.030801 | 3.0641 | 5.8683 | 12.5883 | 11.2098 | -0.20687 | 38.1373 | 608.1064 | 120 | 728.1064 | 1155.9417 | 1
259 | 12 | 729 | 135 |  | 0.030801 | 3.0641 | 5.8683 | 12.5883 | 12.2098 | 0.054927 | 39.0173 | 679.9519 | 112.5 | 792.4519 | 1258.0967 | 1
259 | 13 | 365 | 271 |  | 0.030801 | 3.0641 | 5.8683 | 12.5883 | 13.2098 | 0.31673 | 36.8934 | 324.2067 | 225.8333 | 550.0401 | 873.2436 | 1
259 | 14 | 199 | 273 |  | 0.030801 | 3.0641 | 5.8683 | 12.5883 | 14.2098 | 0.57853 | 32.1311 | 156.0228 | 227.5 | 383.5228 | 608.8807 | 1
259 | 15 | 119 | 255 |  | 0.030801 | 3.0641 | 5.8683 | 12.5883 | 15.2098 | 0.84033 | 25.3922 | 74.6378 | 212.5 | 287.1378 | 455.86 | 1
259 | 16 | 84 | 184 |  | 0.030801 | 3.0641 | 5.8683 | 12.5883 | 16.2098 | 1.1021 | 17.3503 | 35.9898 | 153.3333 | 189.3231 | 300.5694 | 1
259 | 17 | 3 | 84 |  | 0.030801 | 3.0641 | 5.8683 | 12.5883 | 17.2098 | 1.3639 | 8.5666 | 0.6039 | 70 | 70.6039 | 112.0908 | 0
259 | 18 | 0 | 16 |  | 0.030801 | 3.0641 | 5.8683 | 12.5883 | 18.2098 | 1.6257 | -0.50289 | 0 | 13.3333 | 13.3333 | 21.168 | 0
259 | 19 | 0 | 0 |  | 0.030801 | 3.0641 | 5.8683 | 12.5883 | 19.2098 | 1.8875 | -9.4534 | 0 | 0 | 0 | 0 | 0
259 | 20 | 0 | 0 |  | 0.030801 | 3.0641 | 5.8683 | 12.5883 | 20.2098 | 2.1493 | -17.8696 | 0 | 0 | 0 | 0 | 0
259 | 21 | 0 | 0 |  | 0.030801 | 3.0641 | 5.8683 | 12.5883 | 21.2098 | 2.4111 | -25.2696 | 0 | 0 | 0 | 0 | 0
259 | 22 | 0 | 0 |  | 0.030801 | 3.0641 | 5.8683 | 12.5883 | 22.2098 | 2.6729 | -31.074 | 0 | 0 | 0 | 0 | 0
259 | 23 | 0 | 0 |  | 0.030801 | 3.0641 | 5.8683 | 12.5883 | 23.2098 | 2.9347 | -34.6504 | 0 | 0 | 0 | 0 | 0
259 | 24 | 0 | 0 |  | 0.030801 | 3.0641 | 5.8683 | 12.5883 | 24.2098 | 3.1965 | -35.4909 | 0 | 0 | 0 | 0 | 0
260 | 1 | 0 | 0 |  | 0.023964 | 3.0813 | 6.2396 | 12.9596 | 1.216 | -2.8232 | -33.8198 | 0 | 0 | 0 | 0 | 0
260 | 2 | 0 | 0 |  | 0.023964 | 3.0813 | 6.2396 | 12.9596 | 2.216 | -2.5614 | -29.2006 | 0 | 0 | 0 | 0 | 0
260 | 3 | 0 | 0 |  | 0.023964 | 3.0813 | 6.2396 | 12.9596 | 3.216 | -2.2996 | -22.6195 | 0 | 0 | 0 | 0 | 0
260 | 4 | 0 | 0 |  | 0.023964 | 3.0813 | 6.2396 | 12.9596 | 4.216 | -2.0378 | -14.7049 | 0 | 0 | 0 | 0 | 0
260 | 5 | 0 | 0 |  | 0.023964 | 3.0813 | 6.2396 | 12.9596 | 5.216 | -1.776 | -5.9969 | 0 | 0 | 0 | 0 | 0
260 | 6 | 0 | 3 |  | 0.023964 | 3.0813 | 6.2396 | 12.9596 | 6.216 | -1.5142 | 3.0559 | 0 | 2.5 | 2.5 | 3.969 | 0
260 | 7 | 0 | 37 |  | 0.023964 | 3.0813 | 6.2396 | 12.9596 | 7.216 | -1.2525 | 12.0497 | 0 | 30.8333 | 30.8333 | 48.951 | 0
260 | 8 | 9 | 112 |  | 0.023964 | 3.0813 | 6.2396 | 12.9596 | 8.216 | -0.99065 | 20.5658 | 4.6337 | 93.3333 | 97.967 | 155.5324 | 1
260 | 9 | 29 | 185 |  | 0.023964 | 3.0813 | 6.2396 | 12.9596 | 9.216 | -0.72885 | 28.1099 | 20.2217 | 154.1667 | 174.3884 | 276.859 | 1
260 | 10 | 40 | 246 |  | 0.023964 | 3.0813 | 6.2396 | 12.9596 | 10.216 | -0.46705 | 34.0721 | 33.3143 | 205 | 238.3143 | 378.3477 | 1
260 | 11 | 70 | 274 |  | 0.023964 | 3.0813 | 6.2396 | 12.9596 | 11.216 | -0.20525 | 37.7651 | 63.86 | 228.3333 | 292.1933 | 463.8861 | 1
260 | 12 | 72 | 293 |  | 0.023964 | 3.0813 | 6.2396 | 12.9596 | 12.216 | 0.056547 | 38.622 | 66.9724 | 244.1667 | 311.1391 | 493.9644 | 1
260 | 13 | 205 | 298 |  | 0.023964 | 3.0813 | 6.2396 | 12.9596 | 13.216 | 0.31835 | 36.4908 | 181.4865 | 248.3333 | 429.8199 | 682.382 | 1
260 | 14 | 187 | 276 |  | 0.023964 | 3.0813 | 6.2396 | 12.9596 | 14.216 | 0.58015 | 31.7343 | 145.9956 | 230 | 375.9956 | 596.9307 | 1
260 | 15 | 344 | 190 |  | 0.023964 | 3.0813 | 6.2396 | 12.9596 | 15.216 | 0.84194 | 25.0065 | 214.5099 | 158.3333 | 372.8432 | 591.9258 | 1
260 | 16 | 137 | 159 |  | 0.023964 | 3.0813 | 6.2396 | 12.9596 | 16.216 | 1.1037 | 16.9749 | 58.1646 | 132.5 | 190.6646 | 302.6991 | 1
260 | 17 | 2 | 81 |  | 0.023964 | 3.0813 | 6.2396 | 12.9596 | 17.216 | 1.3655 | 8.1975 | 0.39448 | 67.5 | 67.8945 | 107.7893 | 0
260 | 18 | 0 | 19 |  | 0.023964 | 3.0813 | 6.2396 | 12.9596 | 18.216 | 1.6273 | -0.87084 | 0 | 15.8333 | 15.8333 | 25.137 | 0
260 | 19 | 0 | 0 |  | 0.023964 | 3.0813 | 6.2396 | 12.9596 | 19.216 | 1.8891 | -9.8255 | 0 | 0 | 0 | 0 | 0
260 | 20 | 0 | 0 |  | 0.023964 | 3.0813 | 6.2396 | 12.9596 | 20.216 | 2.1509 | -18.2504 | 0 | 0 | 0 | 0 | 0
260 | 21 | 0 | 0 |  | 0.023964 | 3.0813 | 6.2396 | 12.9596 | 21.216 | 2.4127 | -25.6614 | 0 | 0 | 0 | 0 | 0
260 | 22 | 0 | 0 |  | 0.023964 | 3.0813 | 6.2396 | 12.9596 | 22.216 | 2.6745 | -31.4748 | 0 | 0 | 0 | 0 | 0
260 | 23 | 0 | 0 |  | 0.023964 | 3.0813 | 6.2396 | 12.9596 | 23.216 | 2.9363 | -35.0516 | 0 | 0 | 0 | 0 | 0
260 | 24 | 0 | 0 |  | 0.023964 | 3.0813 | 6.2396 | 12.9596 | 24.216 | 3.1981 | -35.8784 | 0 | 0 | 0 | 0 | 0
261 | 1 | 0 | 0 |  | 0.017121 | 3.0986 | 6.61 | 13.33 | 1.2222 | -2.8216 | -34.1801 | 0 | 0 | 0 | 0 | 0
261 | 2 | 0 | 0 |  | 0.017121 | 3.0986 | 6.61 | 13.33 | 2.2222 | -2.5598 | -29.5276 | 0 | 0 | 0 | 0 | 0
261 | 3 | 0 | 0 |  | 0.017121 | 3.0986 | 6.61 | 13.33 | 3.2222 | -2.298 | -22.9156 | 0 | 0 | 0 | 0 | 0
261 | 4 | 0 | 0 |  | 0.017121 | 3.0986 | 6.61 | 13.33 | 4.2222 | -2.0362 | -14.9778 | 0 | 0 | 0 | 0 | 0
261 | 5 | 0 | 0 |  | 0.017121 | 3.0986 | 6.61 | 13.33 | 5.2222 | -1.7744 | -6.2561 | 0 | 0 | 0 | 0 | 0
261 | 6 | 0 | 4 |  | 0.017121 | 3.0986 | 6.61 | 13.33 | 6.2222 | -1.5126 | 2.8002 | 0 | 3.3333 | 3.3333 | 5.292 | 0
261 | 7 | 87 | 51 |  | 0.017121 | 3.0986 | 6.61 | 13.33 | 7.2222 | -1.2508 | 11.7872 | 25.8188 | 42.5 | 68.3188 | 108.463 | 0
261 | 8 | 331 | 103 |  | 0.017121 | 3.0986 | 6.61 | 13.33 | 8.2222 | -0.98903 | 20.2861 | 169.9794 | 85.8333 | 255.8127 | 406.1283 | 1
261 | 9 | 545 | 115 |  | 0.017121 | 3.0986 | 6.61 | 13.33 | 9.2222 | -0.72723 | 27.8034 | 379.1844 | 95.8333 | 475.0178 | 754.1382 | 1
261 | 10 | 681 | 110 |  | 0.017121 | 3.0986 | 6.61 | 13.33 | 10.2222 | -0.46544 | 33.7322 | 565.9145 | 91.6667 | 657.5811 | 1043.9758 | 1
261 | 11 | 723 | 122 |  | 0.017121 | 3.0986 | 6.61 | 13.33 | 11.2222 | -0.20364 | 37.3922 | 657.9858 | 101.6667 | 759.6525 | 1206.0243 | 1
261 | 12 | 753 | 120 |  | 0.017121 | 3.0986 | 6.61 | 13.33 | 12.2222 | 0.058163 | 38.2262 | 698.4669 | 100 | 798.4669 | 1267.6461 | 1
261 | 13 | 725 | 128 |  | 0.017121 | 3.0986 | 6.61 | 13.33 | 13.2222 | 0.31996 | 36.088 | 639.6802 | 106.6667 | 746.3469 | 1184.9004 | 1
261 | 14 | 182 | 274 |  | 0.017121 | 3.0986 | 6.61 | 13.33 | 14.2222 | 0.58176 | 31.3372 | 141.4827 | 228.3333 | 369.8161 | 587.12 | 1
261 | 15 | 44 | 215 |  | 0.017121 | 3.0986 | 6.61 | 13.33 | 15.2222 | 0.84356 | 24.6205 | 27.2761 | 179.1667 | 206.4427 | 327.7485 | 1
261 | 16 | 22 | 152 |  | 0.017121 | 3.0986 | 6.61 | 13.33 | 16.2222 | 1.1054 | 16.5992 | 9.2542 | 126.6667 | 135.9209 | 215.788 | 1
261 | 17 | 0 | 49 |  | 0.017121 | 3.0986 | 6.61 | 13.33 | 17.2222 | 1.3672 | 7.8282 | 0 | 40.8333 | 40.8333 | 64.827 | 0
261 | 18 | 0 | 8 |  | 0.017121 | 3.0986 | 6.61 | 13.33 | 18.2222 | 1.629 | -1.2389 | 0 | 6.6667 | 6.6667 | 10.584 | 0
261 | 19 | 0 | 0 |  | 0.017121 | 3.0986 | 6.61 | 13.33 | 19.2222 | 1.8908 | -10.1978 | 0 | 0 | 0 | 0 | 0
261 | 20 | 0 | 0 |  | 0.017121 | 3.0986 | 6.61 | 13.33 | 20.2222 | 2.1526 | -18.6313 | 0 | 0 | 0 | 0 | 0
261 | 21 | 0 | 0 |  | 0.017121 | 3.0986 | 6.61 | 13.33 | 21.2222 | 2.4144 | -26.0534 | 0 | 0 | 0 | 0 | 0
261 | 22 | 0 | 0 |  | 0.017121 | 3.0986 | 6.61 | 13.33 | 22.2222 | 2.6762 | -31.8758 | 0 | 0 | 0 | 0 | 0
261 | 23 | 0 | 0 |  | 0.017121 | 3.0986 | 6.61 | 13.33 | 23.2222 | 2.938 | -35.4531 | 0 | 0 | 0 | 0 | 0
261 | 24 | 0 | 0 |  | 0.017121 | 3.0986 | 6.61 | 13.33 | 24.2222 | 3.1998 | -36.2661 | 0 | 0 | 0 | 0 | 0
262 | 1 | 0 | 0 |  | 0.010275 | 3.1158 | 6.9793 | 13.6993 | 1.2283 | -2.82 | -34.5404 | 0 | 0 | 0 | 0 | 0
262 | 2 | 0 | 0 |  | 0.010275 | 3.1158 | 6.9793 | 13.6993 | 2.2283 | -2.5582 | -29.8544 | 0 | 0 | 0 | 0 | 0
262 | 3 | 0 | 0 |  | 0.010275 | 3.1158 | 6.9793 | 13.6993 | 3.2283 | -2.2964 | -23.2116 | 0 | 0 | 0 | 0 | 0
262 | 4 | 0 | 0 |  | 0.010275 | 3.1158 | 6.9793 | 13.6993 | 4.2283 | -2.0346 | -15.2506 | 0 | 0 | 0 | 0 | 0
262 | 5 | 0 | 0 |  | 0.010275 | 3.1158 | 6.9793 | 13.6993 | 5.2283 | -1.7728 | -6.5155 | 0 | 0 | 0 | 0 | 0
262 | 6 | 0 | 2 |  | 0.010275 | 3.1158 | 6.9793 | 13.6993 | 6.2283 | -1.511 | 2.544 | 0 | 1.6667 | 1.6667 | 2.646 | 0
262 | 7 | 0 | 34 |  | 0.010275 | 3.1158 | 6.9793 | 13.6993 | 7.2283 | -1.2492 | 11.5239 | 0 | 28.3333 | 28.3333 | 44.982 | 0
262 | 8 | 0 | 69 |  | 0.010275 | 3.1158 | 6.9793 | 13.6993 | 8.2283 | -0.98742 | 20.0055 | 0 | 57.5 | 57.5 | 91.287 | 1
262 | 9 | 38 | 176 |  | 0.010275 | 3.1158 | 6.9793 | 13.6993 | 9.2283 | -0.72562 | 27.4959 | 26.3782 | 146.6667 | 173.0449 | 274.726 | 1
262 | 10 | 40 | 241 |  | 0.010275 | 3.1158 | 6.9793 | 13.6993 | 10.2283 | -0.46382 | 33.3914 | 33.1643 | 200.8333 | 233.9977 | 371.4947 | 1
262 | 11 | 4 | 192 |  | 0.010275 | 3.1158 | 6.9793 | 13.6993 | 11.2283 | -0.20203 | 37.0187 | 3.6313 | 160 | 163.6313 | 259.781 | 1
262 | 12 | 5 | 205 |  | 0.010275 | 3.1158 | 6.9793 | 13.6993 | 12.2283 | 0.059774 | 37.8301 | 4.6247 | 170.8333 | 175.458 | 278.5572 | 1
262 | 13 | 70 | 283 |  | 0.010275 | 3.1158 | 6.9793 | 13.6993 | 13.2283 | 0.32157 | 35.685 | 61.5504 | 235.8333 | 297.3837 | 472.1264 | 1
262 | 14 | 47 | 266 |  | 0.010275 | 3.1158 | 6.9793 | 13.6993 | 14.2283 | 0.58337 | 30.94 | 36.3776 | 221.6667 | 258.0443 | 409.6711 | 1
262 | 15 | 178 | 215 |  | 0.010275 | 3.1158 | 6.9793 | 13.6993 | 15.2283 | 0.84517 | 24.2343 | 109.6866 | 179.1667 | 288.8533 | 458.5835 | 1
262 | 16 | 221 | 154 |  | 0.010275 | 3.1158 | 6.9793 | 13.6993 | 16.2283 | 1.107 | 16.2234 | 92.0946 | 128.3333 | 220.4279 | 349.9514 | 1
262 | 17 | 195 | 86 |  | 0.010275 | 3.1158 | 6.9793 | 13.6993 | 17.2283 | 1.3688 | 7.4588 | 36.8724 | 71.6667 | 108.5391 | 172.3167 | 0
262 | 18 | 0 | 22 |  | 0.010275 | 3.1158 | 6.9793 | 13.6993 | 18.2283 | 1.6306 | -1.6071 | 0 | 18.3333 | 18.3333 | 29.106 | 0
262 | 19 | 0 | 0 |  | 0.010275 | 3.1158 | 6.9793 | 13.6993 | 19.2283 | 1.8924 | -10.5699 | 0 | 0 | 0 | 0 | 0
262 | 20 | 0 | 0 |  | 0.010275 | 3.1158 | 6.9793 | 13.6993 | 20.2283 | 2.1542 | -19.0121 | 0 | 0 | 0 | 0 | 0
262 | 21 | 0 | 0 |  | 0.010275 | 3.1158 | 6.9793 | 13.6993 | 21.2283 | 2.416 | -26.4454 | 0 | 0 | 0 | 0 | 0
262 | 22 | 0 | 0 |  | 0.010275 | 3.1158 | 6.9793 | 13.6993 | 22.2283 | 2.6778 | -32.277 | 0 | 0 | 0 | 0 | 0
262 | 23 | 0 | 0 |  | 0.010275 | 3.1158 | 6.9793 | 13.6993 | 23.2283 | 2.9396 | -35.8548 | 0 | 0 | 0 | 0 | 0
262 | 24 | 0 | 0 |  | 0.010275 | 3.1158 | 6.9793 | 13.6993 | 24.2283 | 3.2014 | -36.6539 | 0 | 0 | 0 | 0 | 0
263 | 1 | 0 | 0 |  | 0.0034251 | 3.133 | 7.3469 | 14.0669 | 1.2344 | -2.8184 | -34.9005 | 0 | 0 | 0 | 0 | 0
263 | 2 | 0 | 0 |  | 0.0034251 | 3.133 | 7.3469 | 14.0669 | 2.2344 | -2.5566 | -30.1809 | 0 | 0 | 0 | 0 | 0
263 | 3 | 0 | 0 |  | 0.0034251 | 3.133 | 7.3469 | 14.0669 | 3.2344 | -2.2948 | -23.5073 | 0 | 0 | 0 | 0 | 0
263 | 4 | 0 | 0 |  | 0.0034251 | 3.133 | 7.3469 | 14.0669 | 4.2344 | -2.033 | -15.5233 | 0 | 0 | 0 | 0 | 0
263 | 5 | 0 | 0 |  | 0.0034251 | 3.133 | 7.3469 | 14.0669 | 5.2344 | -1.7712 | -6.7751 | 0 | 0 | 0 | 0 | 0
263 | 6 | 0 | 3 |  | 0.0034251 | 3.133 | 7.3469 | 14.0669 | 6.2344 | -1.5094 | 2.2874 | 0 | 2.5 | 2.5 | 3.969 | 0
263 | 7 | 42 | 48 |  | 0.0034251 | 3.133 | 7.3469 | 14.0669 | 7.2344 | -1.2476 | 11.26 | 12.3624 | 40 | 52.3624 | 83.1305 | 0
263 | 8 | 261 | 104 |  | 0.0034251 | 3.133 | 7.3469 | 14.0669 | 8.2344 | -0.98582 | 19.724 | 133.3187 | 86.6667 | 219.9853 | 349.2487 | 1
263 | 9 | 155 | 181 |  | 0.0034251 | 3.133 | 7.3469 | 14.0669 | 9.2344 | -0.72402 | 27.1876 | 107.3431 | 150.8333 | 258.1764 | 409.8809 | 1
263 | 10 | 66 | 227 |  | 0.0034251 | 3.133 | 7.3469 | 14.0669 | 10.2344 | -0.46222 | 33.0498 | 54.5931 | 189.1667 | 243.7597 | 386.9929 | 1
263 | 11 | 85 | 259 |  | 0.0034251 | 3.133 | 7.3469 | 14.0669 | 11.2344 | -0.20042 | 36.6447 | 76.9691 | 215.8333 | 292.8024 | 464.8531 | 1
263 | 12 | 72 | 285 |  | 0.0034251 | 3.133 | 7.3469 | 14.0669 | 12.2344 | 0.061378 | 37.4338 | 66.402 | 237.5 | 303.902 | 482.4749 | 1
263 | 13 | 72 | 280 |  | 0.0034251 | 3.133 | 7.3469 | 14.0669 | 13.2344 | 0.32318 | 35.282 | 63.088 | 233.3333 | 296.4213 | 470.5985 | 1
263 | 14 | 4 | 180 |  | 0.0034251 | 3.133 | 7.3469 | 14.0669 | 14.2344 | 0.58498 | 30.5427 | 3.0823 | 150 | 153.0823 | 243.0334 | 1
263 | 15 | 178 | 315 |  | 0.0034251 | 3.133 | 7.3469 | 14.0669 | 15.2344 | 0.84678 | 23.8481 | 109.0244 | 262.5 | 371.5244 | 589.8322 | 1
263 | 16 | 142 | 148 |  | 0.0034251 | 3.133 | 7.3469 | 14.0669 | 16.2344 | 1.1086 | 15.8475 | 58.6136 | 123.3333 | 181.9469 | 288.8589 | 1
263 | 17 | 212 | 79 |  | 0.0034251 | 3.133 | 7.3469 | 14.0669 | 17.2344 | 1.3704 | 7.0895 | 39.2215 | 65.8333 | 105.0548 | 166.785 | 0
263 | 18 | 0 | 17 |  | 0.0034251 | 3.133 | 7.3469 | 14.0669 | 18.2344 | 1.6322 | -1.975 | 0 | 14.1667 | 14.1667 | 22.491 | 0
263 | 19 | 0 | 0 |  | 0.0034251 | 3.133 | 7.3469 | 14.0669 | 19.2344 | 1.894 | -10.9419 | 0 | 0 | 0 | 0 | 0
263 | 20 | 0 | 0 |  | 0.0034251 | 3.133 | 7.3469 | 14.0669 | 20.2344 | 2.1558 | -19.3928 | 0 | 0 | 0 | 0 | 0
263 | 21 | 0 | 0 |  | 0.0034251 | 3.133 | 7.3469 | 14.0669 | 21.2344 | 2.4176 | -26.8372 | 0 | 0 | 0 | 0 | 0
263 | 22 | 0 | 0 |  | 0.0034251 | 3.133 | 7.3469 | 14.0669 | 22.2344 | 2.6794 | -32.6782 | 0 | 0 | 0 | 0 | 0
263 | 23 | 0 | 0 |  | 0.0034251 | 3.133 | 7.3469 | 14.0669 | 23.2344 | 2.9412 | -36.2566 | 0 | 0 | 0 | 0 | 0
263 | 24 | 0 | 0 |  | 0.0034251 | 3.133 | 7.3469 | 14.0669 | 24.2344 | 3.203 | -37.0418 | 0 | 0 | 0 | 0 | 0
264 | 1 | 0 | 0 |  | -0.0034251 | 3.1502 | 7.7125 | 14.4325 | 1.2405 | -2.8168 | -35.2604 | 0 | 0 | 0 | 0 | 0
264 | 2 | 0 | 0 |  | -0.0034251 | 3.1502 | 7.7125 | 14.4325 | 2.2405 | -2.555 | -30.5071 | 0 | 0 | 0 | 0 | 0
264 | 3 | 0 | 0 |  | -0.0034251 | 3.1502 | 7.7125 | 14.4325 | 3.2405 | -2.2932 | -23.8027 | 0 | 0 | 0 | 0 | 0
264 | 4 | 0 | 0 |  | -0.0034251 | 3.1502 | 7.7125 | 14.4325 | 4.2405 | -2.0314 | -15.796 | 0 | 0 | 0 | 0 | 0
264 | 5 | 0 | 0 |  | -0.0034251 | 3.1502 | 7.7125 | 14.4325 | 5.2405 | -1.7696 | -7.0348 | 0 | 0 | 0 | 0 | 0
264 | 6 | 0 | 1 |  | -0.0034251 | 3.1502 | 7.7125 | 14.4325 | 6.2405 | -1.5078 | 2.0304 | 0 | 0.83333 | 0.83333 | 1.323 | 0
264 | 7 | 0 | 31 |  | -0.0034251 | 3.1502 | 7.7125 | 14.4325 | 7.2405 | -1.246 | 10.9954 | 0 | 25.8333 | 25.8333 | 41.013 | 0
264 | 8 | 11 | 103 |  | -0.0034251 | 3.1502 | 7.7125 | 14.4325 | 8.2405 | -0.98422 | 19.4417 | 5.6032 | 85.8333 | 91.4366 | 145.1647 | 1
264 | 9 | 11 | 183 |  | -0.0034251 | 3.1502 | 7.7125 | 14.4325 | 9.2405 | -0.72242 | 26.8783 | 7.5996 | 152.5 | 160.0996 | 254.1741 | 1
264 | 10 | 51 | 231 |  | -0.0034251 | 3.1502 | 7.7125 | 14.4325 | 10.2405 | -0.46062 | 32.7075 | 42.0843 | 192.5 | 234.5843 | 372.426 | 1
264 | 11 | 85 | 256 |  | -0.0034251 | 3.1502 | 7.7125 | 14.4325 | 11.2405 | -0.19883 | 36.2703 | 76.7694 | 213.3333 | 290.1027 | 460.5671 | 1
264 | 12 | 87 | 274 |  | -0.0034251 | 3.1502 | 7.7125 | 14.4325 | 12.2405 | 0.062974 | 37.0374 | 79.998 | 228.3333 | 308.3314 | 489.5069 | 1
264 | 13 | 208 | 286 |  | -0.0034251 | 3.1502 | 7.7125 | 14.4325 | 13.2405 | 0.32477 | 34.879 | 181.6074 | 238.3333 | 419.9407 | 666.6979 | 1
264 | 14 | 131 | 295 |  | -0.0034251 | 3.1502 | 7.7125 | 14.4325 | 14.2405 | 0.58657 | 30.1455 | 100.4922 | 245.8333 | 346.3255 | 549.8264 | 1
264 | 15 | 48 | 206 |  | -0.0034251 | 3.1502 | 7.7125 | 14.4325 | 15.2405 | 0.84837 | 23.462 | 29.2201 | 171.6667 | 200.8868 | 318.9278 | 1
264 | 16 | 21 | 143 |  | -0.0034251 | 3.1502 | 7.7125 | 14.4325 | 16.2405 | 1.1102 | 15.4718 | 8.5851 | 119.1667 | 127.7517 | 202.8186 | 1
264 | 17 | 0 | 69 |  | -0.0034251 | 3.1502 | 7.7125 | 14.4325 | 17.2405 | 1.372 | 6.7204 | 0 | 57.5 | 57.5 | 91.287 | 0
264 | 18 | 0 | 11 |  | -0.0034251 | 3.1502 | 7.7125 | 14.4325 | 18.2405 | 1.6338 | -2.3427 | 0 | 9.1667 | 9.1667 | 14.553 | 0
264 | 19 | 0 | 0 |  | -0.0034251 | 3.1502 | 7.7125 | 14.4325 | 19.2405 | 1.8956 | -11.3136 | 0 | 0 | 0 | 0 | 0
264 | 20 | 0 | 0 |  | -0.0034251 | 3.1502 | 7.7125 | 14.4325 | 20.2405 | 2.1574 | -19.7731 | 0 | 0 | 0 | 0 | 0
264 | 21 | 0 | 0 |  | -0.0034251 | 3.1502 | 7.7125 | 14.4325 | 21.2405 | 2.4192 | -27.2288 | 0 | 0 | 0 | 0 | 0
264 | 22 | 0 | 0 |  | -0.0034251 | 3.1502 | 7.7125 | 14.4325 | 22.2405 | 2.681 | -33.0793 | 0 | 0 | 0 | 0 | 0
264 | 23 | 0 | 0 |  | -0.0034251 | 3.1502 | 7.7125 | 14.4325 | 23.2405 | 2.9428 | -36.6584 | 0 | 0 | 0 | 0 | 0
264 | 24 | 0 | 0 |  | -0.0034251 | 3.1502 | 7.7125 | 14.4325 | 24.2405 | 3.2046 | -37.4295 | 0 | 0 | 0 | 0 | 0
265 | 1 | 0 | 0 |  | -0.010275 | 3.1674 | 8.0757 | 14.7957 | 1.2466 | -2.8152 | -35.6199 | 0 | 0 | 0 | 0 | 0
265 | 2 | 0 | 0 |  | -0.010275 | 3.1674 | 8.0757 | 14.7957 | 2.2466 | -2.5534 | -30.8329 | 0 | 0 | 0 | 0 | 0
265 | 3 | 0 | 0 |  | -0.010275 | 3.1674 | 8.0757 | 14.7957 | 3.2466 | -2.2916 | -24.0978 | 0 | 0 | 0 | 0 | 0
265 | 4 | 0 | 0 |  | -0.010275 | 3.1674 | 8.0757 | 14.7957 | 4.2466 | -2.0298 | -16.0685 | 0 | 0 | 0 | 0 | 0
265 | 5 | 0 | 0 |  | -0.010275 | 3.1674 | 8.0757 | 14.7957 | 5.2466 | -1.768 | -7.2946 | 0 | 0 | 0 | 0 | 0
265 | 6 | 0 | 1 |  | -0.010275 | 3.1674 | 8.0757 | 14.7957 | 6.2466 | -1.5062 | 1.773 | 0 | 0.83333 | 0.83333 | 1.323 | 0
265 | 7 | 0 | 29 |  | -0.010275 | 3.1674 | 8.0757 | 14.7957 | 7.2466 | -1.2444 | 10.7302 | 0 | 24.1667 | 24.1667 | 38.367 | 0
265 | 8 | 7 | 101 |  | -0.010275 | 3.1674 | 8.0757 | 14.7957 | 8.2466 | -0.98264 | 19.1587 | 3.5556 | 84.1667 | 87.7222 | 139.2678 | 1
265 | 9 | 26 | 174 |  | -0.010275 | 3.1674 | 8.0757 | 14.7957 | 9.2466 | -0.72084 | 26.5683 | 17.9182 | 145 | 162.9182 | 258.6489 | 1
265 | 10 | 40 | 234 |  | -0.010275 | 3.1674 | 8.0757 | 14.7957 | 10.2466 | -0.45904 | 32.3646 | 32.926 | 195 | 227.926 | 361.8554 | 1
265 | 11 | 70 | 262 |  | -0.010275 | 3.1674 | 8.0757 | 14.7957 | 11.2466 | -0.19724 | 35.8955 | 63.0542 | 218.3333 | 281.3875 | 446.7308 | 1
265 | 12 | 73 | 280 |  | -0.010275 | 3.1674 | 8.0757 | 14.7957 | 12.2466 | 0.064558 | 36.6411 | 66.922 | 233.3333 | 300.2554 | 476.6854 | 1
265 | 13 | 86 | 266 |  | -0.010275 | 3.1674 | 8.0757 | 14.7957 | 13.2466 | 0.32636 | 34.4762 | 74.8168 | 221.6667 | 296.4835 | 470.6972 | 1
265 | 14 | 45 | 259 |  | -0.010275 | 3.1674 | 8.0757 | 14.7957 | 14.2466 | 0.58816 | 29.7485 | 34.3633 | 215.8333 | 250.1966 | 397.2122 | 1
265 | 15 | 48 | 202 |  | -0.010275 | 3.1674 | 8.0757 | 14.7957 | 15.2466 | 0.84996 | 23.0761 | 29.0393 | 168.3333 | 197.3726 | 313.3487 | 1
265 | 16 | 15 | 142 |  | -0.010275 | 3.1674 | 8.0757 | 14.7957 | 16.2466 | 1.1118 | 15.0964 | 6.0726 | 118.3333 | 124.406 | 197.5069 | 1
265 | 17 | 0 | 66 |  | -0.010275 | 3.1674 | 8.0757 | 14.7957 | 17.2466 | 1.3736 | 6.3516 | 0 | 55 | 55 | 87.318 | 0
265 | 18 | 0 | 10 |  | -0.010275 | 3.1674 | 8.0757 | 14.7957 | 18.2466 | 1.6354 | -2.71 | 0 | 8.3333 | 8.3333 | 13.23 | 0
265 | 19 | 0 | 0 |  | -0.010275 | 3.1674 | 8.0757 | 14.7957 | 19.2466 | 1.8972 | -11.6847 | 0 | 0 | 0 | 0 | 0
265 | 20 | 0 | 0 |  | -0.010275 | 3.1674 | 8.0757 | 14.7957 | 20.2466 | 2.159 | -20.1529 | 0 | 0 | 0 | 0 | 0
265 | 21 | 0 | 0 |  | -0.010275 | 3.1674 | 8.0757 | 14.7957 | 21.2466 | 2.4208 | -27.62 | 0 | 0 | 0 | 0 | 0
265 | 22 | 0 | 0 |  | -0.010275 | 3.1674 | 8.0757 | 14.7957 | 22.2466 | 2.6826 | -33.48 | 0 | 0 | 0 | 0 | 0
265 | 23 | 0 | 0 |  | -0.010275 | 3.1674 | 8.0757 | 14.7957 | 23.2466 | 2.9444 | -37.06 | 0 | 0 | 0 | 0 | 0
265 | 24 | 0 | 0 |  | -0.010275 | 3.1674 | 8.0757 | 14.7957 | 24.2466 | 3.2062 | -37.817 | 0 | 0 | 0 | 0 | 0
266 | 1 | 0 | 0 |  | -0.017121 | 3.1846 | 8.436 | 15.156 | 1.2526 | -2.8137 | -35.9791 | 0 | 0 | 0 | 0 | 0
266 | 2 | 0 | 0 |  | -0.017121 | 3.1846 | 8.436 | 15.156 | 2.2526 | -2.5519 | -31.1583 | 0 | 0 | 0 | 0 | 0
266 | 3 | 0 | 0 |  | -0.017121 | 3.1846 | 8.436 | 15.156 | 3.2526 | -2.2901 | -24.3925 | 0 | 0 | 0 | 0 | 0
266 | 4 | 0 | 0 |  | -0.017121 | 3.1846 | 8.436 | 15.156 | 4.2526 | -2.0283 | -16.3408 | 0 | 0 | 0 | 0 | 0
266 | 5 | 0 | 0 |  | -0.017121 | 3.1846 | 8.436 | 15.156 | 5.2526 | -1.7665 | -7.5545 | 0 | 0 | 0 | 0 | 0
266 | 6 | 0 | 2 |  | -0.017121 | 3.1846 | 8.436 | 15.156 | 6.2526 | -1.5047 | 1.5152 | 0 | 1.6667 | 1.6667 | 2.646 | 0
266 | 7 | 12 | 40 |  | -0.017121 | 3.1846 | 8.436 | 15.156 | 7.2526 | -1.2429 | 10.4644 | 3.4864 | 33.3333 | 36.8197 | 58.455 | 0
266 | 8 | 62 | 114 |  | -0.017121 | 3.1846 | 8.436 | 15.156 | 8.2526 | -0.98107 | 18.8748 | 31.4002 | 95 | 126.4002 | 200.673 | 1
266 | 9 | 274 | 162 |  | -0.017121 | 3.1846 | 8.436 | 15.156 | 9.2526 | -0.71927 | 26.2574 | 188.3511 | 135 | 323.3511 | 513.3523 | 1
266 | 10 | 356 | 196 |  | -0.017121 | 3.1846 | 8.436 | 15.156 | 10.2526 | -0.45747 | 32.0211 | 292.3027 | 163.3333 | 455.636 | 723.3677 | 1
266 | 11 | 499 | 203 |  | -0.017121 | 3.1846 | 8.436 | 15.156 | 11.2526 | -0.19567 | 35.5205 | 448.2677 | 169.1667 | 617.4344 | 980.2388 | 1
266 | 12 | 589 | 169 |  | -0.017121 | 3.1846 | 8.436 | 15.156 | 12.2526 | 0.066131 | 36.2448 | 538.2986 | 140.8333 | 679.1319 | 1078.1899 | 1
266 | 13 | 579 | 168 |  | -0.017121 | 3.1846 | 8.436 | 15.156 | 13.2526 | 0.32793 | 34.0737 | 501.8627 | 140 | 641.8627 | 1019.0213 | 1
266 | 14 | 629 | 139 |  | -0.017121 | 3.1846 | 8.436 | 15.156 | 14.2526 | 0.58973 | 29.352 | 478.11 | 115.8333 | 593.9434 | 942.9445 | 1
266 | 15 | 536 | 134 |  | -0.017121 | 3.1846 | 8.436 | 15.156 | 15.2526 | 0.85153 | 22.6906 | 322.2418 | 111.6667 | 433.9085 | 688.8731 | 1
266 | 16 | 405 | 110 |  | -0.017121 | 3.1846 | 8.436 | 15.156 | 16.2526 | 1.1133 | 14.7214 | 162.3495 | 91.6667 | 254.0162 | 403.2761 | 1
266 | 17 | 204 | 72 |  | -0.017121 | 3.1846 | 8.436 | 15.156 | 17.2526 | 1.3751 | 5.9833 | 35.2432 | 60 | 95.2432 | 151.2081 | 0
266 | 18 | 0 | 16 |  | -0.017121 | 3.1846 | 8.436 | 15.156 | 18.2526 | 1.6369 | -3.0767 | 0 | 13.3333 | 13.3333 | 21.168 | 0
266 | 19 | 0 | 0 |  | -0.017121 | 3.1846 | 8.436 | 15.156 | 19.2526 | 1.8987 | -12.0553 | 0 | 0 | 0 | 0 | 0
266 | 20 | 0 | 0 |  | -0.017121 | 3.1846 | 8.436 | 15.156 | 20.2526 | 2.1605 | -20.5321 | 0 | 0 | 0 | 0 | 0
266 | 21 | 0 | 0 |  | -0.017121 | 3.1846 | 8.436 | 15.156 | 21.2526 | 2.4223 | -28.0106 | 0 | 0 | 0 | 0 | 0
266 | 22 | 0 | 0 |  | -0.017121 | 3.1846 | 8.436 | 15.156 | 22.2526 | 2.6841 | -33.8804 | 0 | 0 | 0 | 0 | 0
266 | 23 | 0 | 0 |  | -0.017121 | 3.1846 | 8.436 | 15.156 | 23.2526 | 2.9459 | -37.4613 | 0 | 0 | 0 | 0 | 0
266 | 24 | 0 | 0 |  | -0.017121 | 3.1846 | 8.436 | 15.156 | 24.2526 | 3.2077 | -38.2043 | 0 | 0 | 0 | 0 | 0
267 | 1 | 0 | 0 |  | -0.023964 | 3.2018 | 8.7931 | 15.5131 | 1.2586 | -2.8121 | -36.3378 | 0 | 0 | 0 | 0 | 0
267 | 2 | 0 | 0 |  | -0.023964 | 3.2018 | 8.7931 | 15.5131 | 2.2586 | -2.5503 | -31.4832 | 0 | 0 | 0 | 0 | 0
267 | 3 | 0 | 0 |  | -0.023964 | 3.2018 | 8.7931 | 15.5131 | 3.2586 | -2.2885 | -24.6869 | 0 | 0 | 0 | 0 | 0
267 | 4 | 0 | 0 |  | -0.023964 | 3.2018 | 8.7931 | 15.5131 | 4.2586 | -2.0267 | -16.613 | 0 | 0 | 0 | 0 | 0
267 | 5 | 0 | 0 |  | -0.023964 | 3.2018 | 8.7931 | 15.5131 | 5.2586 | -1.7649 | -7.8146 | 0 | 0 | 0 | 0 | 0
267 | 6 | 0 | 1 |  | -0.023964 | 3.2018 | 8.7931 | 15.5131 | 6.2586 | -1.5031 | 1.2571 | 0 | 0.83333 | 0.83333 | 1.323 | 0
267 | 7 | 0 | 16 |  | -0.023964 | 3.2018 | 8.7931 | 15.5131 | 7.2586 | -1.2413 | 10.198 | 0 | 13.3333 | 13.3333 | 21.168 | 0
267 | 8 | 0 | 62 |  | -0.023964 | 3.2018 | 8.7931 | 15.5131 | 8.2586 | -0.97951 | 18.5903 | 0 | 51.6667 | 51.6667 | 82.026 | 1
267 | 9 | 0 | 112 |  | -0.023964 | 3.2018 | 8.7931 | 15.5131 | 9.2586 | -0.71771 | 25.9459 | 0 | 93.3333 | 93.3333 | 148.176 | 1
267 | 10 | 0 | 156 |  | -0.023964 | 3.2018 | 8.7931 | 15.5131 | 10.2586 | -0.45591 | 31.677 | 0 | 130 | 130 | 206.388 | 1
267 | 11 | 2 | 185 |  | -0.023964 | 3.2018 | 8.7931 | 15.5131 | 11.2586 | -0.19411 | 35.1454 | 1.7917 | 154.1667 | 155.9584 | 247.5995 | 1
267 | 12 | 4 | 196 |  | -0.023964 | 3.2018 | 8.7931 | 15.5131 | 12.2586 | 0.067689 | 35.8488 | 3.6442 | 163.3333 | 166.9776 | 265.0936 | 1
267 | 13 | 4 | 192 |  | -0.023964 | 3.2018 | 8.7931 | 15.5131 | 13.2586 | 0.32949 | 33.6717 | 3.4542 | 160 | 163.4542 | 259.4999 | 1
267 | 14 | 1 | 172 |  | -0.023964 | 3.2018 | 8.7931 | 15.5131 | 14.2586 | 0.59129 | 28.9559 | 0.75657 | 143.3333 | 144.0899 | 228.7571 | 1
267 | 15 | 46 | 196 |  | -0.023964 | 3.2018 | 8.7931 | 15.5131 | 15.2586 | 0.85309 | 22.3056 | 27.48 | 163.3333 | 190.8134 | 302.9353 | 1
267 | 16 | 240 | 131 |  | -0.023964 | 3.2018 | 8.7931 | 15.5131 | 16.2586 | 1.1149 | 14.347 | 95.2507 | 109.1667 | 204.4174 | 324.5331 | 1
267 | 17 | 145 | 71 |  | -0.023964 | 3.2018 | 8.7931 | 15.5131 | 17.2586 | 1.3767 | 5.6157 | 24.4597 | 59.1667 | 83.6264 | 132.7652 | 0
267 | 18 | 0 | 14 |  | -0.023964 | 3.2018 | 8.7931 | 15.5131 | 18.2586 | 1.6385 | -3.4427 | 0 | 11.6667 | 11.6667 | 18.522 | 0
267 | 19 | 0 | 0 |  | -0.023964 | 3.2018 | 8.7931 | 15.5131 | 19.2586 | 1.9003 | -12.425 | 0 | 0 | 0 | 0 | 0
267 | 20 | 0 | 0 |  | -0.023964 | 3.2018 | 8.7931 | 15.5131 | 20.2586 | 2.1621 | -20.9105 | 0 | 0 | 0 | 0 | 0
267 | 21 | 0 | 0 |  | -0.023964 | 3.2018 | 8.7931 | 15.5131 | 21.2586 | 2.4239 | -28.4006 | 0 | 0 | 0 | 0 | 0
267 | 22 | 0 | 0 |  | -0.023964 | 3.2018 | 8.7931 | 15.5131 | 22.2586 | 2.6857 | -34.2803 | 0 | 0 | 0 | 0 | 0
267 | 23 | 0 | 0 |  | -0.023964 | 3.2018 | 8.7931 | 15.5131 | 23.2586 | 2.9475 | -37.8623 | 0 | 0 | 0 | 0 | 0
267 | 24 | 0 | 0 |  | -0.023964 | 3.2018 | 8.7931 | 15.5131 | 24.2586 | 3.2093 | -38.5912 | 0 | 0 | 0 | 0 | 0
268 | 1 | 0 | 0 |  | -0.030801 | 3.2191 | 9.1465 | 15.8665 | 1.2644 | -2.8106 | -36.696 | 0 | 0 | 0 | 0 | 0
268 | 2 | 0 | 0 |  | -0.030801 | 3.2191 | 9.1465 | 15.8665 | 2.2644 | -2.5488 | -31.8075 | 0 | 0 | 0 | 0 | 0
268 | 3 | 0 | 0 |  | -0.030801 | 3.2191 | 9.1465 | 15.8665 | 3.2644 | -2.287 | -24.9808 | 0 | 0 | 0 | 0 | 0
268 | 4 | 0 | 0 |  | -0.030801 | 3.2191 | 9.1465 | 15.8665 | 4.2644 | -2.0252 | -16.885 | 0 | 0 | 0 | 0 | 0
268 | 5 | 0 | 0 |  | -0.030801 | 3.2191 | 9.1465 | 15.8665 | 5.2644 | -1.7634 | -8.0747 | 0 | 0 | 0 | 0 | 0
268 | 6 | 0 | 1 |  | -0.030801 | 3.2191 | 9.1465 | 15.8665 | 6.2644 | -1.5016 | 0.99861 | 0 | 0.83333 | 0.83333 | 1.323 | 0
268 | 7 | 42 | 39 |  | -0.030801 | 3.2191 | 9.1465 | 15.8665 | 7.2644 | -1.2398 | 9.931 | 12.0905 | 32.5 | 44.5905 | 70.7918 | 0
268 | 8 | 264 | 105 |  | -0.030801 | 3.2191 | 9.1465 | 15.8665 | 8.2644 | -0.97797 | 18.305 | 132.8943 | 87.5 | 220.3943 | 349.898 | 1
268 | 9 | 516 | 116 |  | -0.030801 | 3.2191 | 9.1465 | 15.8665 | 9.2644 | -0.71617 | 25.6337 | 352.8371 | 96.6667 | 449.5038 | 713.6322 | 1
268 | 10 | 336 | 203 |  | -0.030801 | 3.2191 | 9.1465 | 15.8665 | 10.2644 | -0.45437 | 31.3325 | 274.4413 | 169.1667 | 443.6079 | 704.2719 | 1
268 | 11 | 340 | 249 |  | -0.030801 | 3.2191 | 9.1465 | 15.8665 | 11.2644 | -0.19257 | 34.7702 | 303.7268 | 207.5 | 511.2268 | 811.6236 | 1
268 | 12 | 96 | 260 |  | -0.030801 | 3.2191 | 9.1465 | 15.8665 | 12.2644 | 0.069231 | 35.4531 | 87.1825 | 216.6667 | 303.8492 | 482.391 | 1
268 | 13 | 89 | 258 |  | -0.030801 | 3.2191 | 9.1465 | 15.8665 | 13.2644 | 0.33103 | 33.2702 | 76.5659 | 215 | 291.5659 | 462.89 | 1
268 | 14 | 46 | 250 |  | -0.030801 | 3.2191 | 9.1465 | 15.8665 | 14.2644 | 0.59283 | 28.5604 | 34.6377 | 208.3333 | 242.971 | 385.7408 | 1
268 | 15 | 171 | 199 |  | -0.030801 | 3.2191 | 9.1465 | 15.8665 | 15.2644 | 0.85463 | 21.9213 | 101.5007 | 165.8333 | 267.3341 | 424.4196 | 1
268 | 16 | 388 | 110 |  | -0.030801 | 3.2191 | 9.1465 | 15.8665 | 16.2644 | 1.1164 | 13.9733 | 152.4411 | 91.6667 | 244.1078 | 387.5456 | 1
268 | 17 | 136 | 74 |  | -0.030801 | 3.2191 | 9.1465 | 15.8665 | 17.2644 | 1.3782 | 5.2489 | 22.3888 | 61.6667 | 84.0555 | 133.4465 | 0
268 | 18 | 0 | 13 |  | -0.030801 | 3.2191 | 9.1465 | 15.8665 | 18.2644 | 1.64 | -3.8078 | 0 | 10.8333 | 10.8333 | 17.199 | 0
268 | 19 | 0 | 0 |  | -0.030801 | 3.2191 | 9.1465 | 15.8665 | 19.2644 | 1.9018 | -12.7939 | 0 | 0 | 0 | 0 | 0
268 | 20 | 0 | 0 |  | -0.030801 | 3.2191 | 9.1465 | 15.8665 | 20.2644 | 2.1636 | -21.2881 | 0 | 0 | 0 | 0 | 0
268 | 21 | 0 | 0 |  | -0.030801 | 3.2191 | 9.1465 | 15.8665 | 21.2644 | 2.4254 | -28.7898 | 0 | 0 | 0 | 0 | 0
268 | 22 | 0 | 0 |  | -0.030801 | 3.2191 | 9.1465 | 15.8665 | 22.2644 | 2.6872 | -34.6795 | 0 | 0 | 0 | 0 | 0
268 | 23 | 0 | 0 |  | -0.030801 | 3.2191 | 9.1465 | 15.8665 | 23.2644 | 2.949 | -38.2627 | 0 | 0 | 0 | 0 | 0
268 | 24 | 0 | 0 |  | -0.030801 | 3.2191 | 9.1465 | 15.8665 | 24.2644 | 3.2108 | -38.9777 | 0 | 0 | 0 | 0 | 0
269 | 1 | 0 | 0 |  | -0.03763 | 3.2363 | 9.4959 | 16.2159 | 1.2703 | -2.809 | -37.0536 | 0 | 0 | 0 | 0 | 0
269 | 2 | 0 | 0 |  | -0.03763 | 3.2363 | 9.4959 | 16.2159 | 2.2703 | -2.5472 | -32.1313 | 0 | 0 | 0 | 0 | 0
269 | 3 | 0 | 0 |  | -0.03763 | 3.2363 | 9.4959 | 16.2159 | 3.2703 | -2.2854 | -25.2743 | 0 | 0 | 0 | 0 | 0
269 | 4 | 0 | 0 |  | -0.03763 | 3.2363 | 9.4959 | 16.2159 | 4.2703 | -2.0236 | -17.1567 | 0 | 0 | 0 | 0 | 0
269 | 5 | 0 | 0 |  | -0.03763 | 3.2363 | 9.4959 | 16.2159 | 5.2703 | -1.7618 | -8.3348 | 0 | 0 | 0 | 0 | 0
269 | 6 | 0 | 0 |  | -0.03763 | 3.2363 | 9.4959 | 16.2159 | 6.2703 | -1.5 | 0.73982 | 0 | 0 | 0 | 0 | 0
269 | 7 | 0 | 14 |  | -0.03763 | 3.2363 | 9.4959 | 16.2159 | 7.2703 | -1.2382 | 9.6636 | 0 | 11.6667 | 11.6667 | 18.522 | 0
269 | 8 | 0 | 59 |  | -0.03763 | 3.2363 | 9.4959 | 16.2159 | 8.2703 | -0.97644 | 18.0191 | 0 | 49.1667 | 49.1667 | 78.057 | 1
269 | 9 | 0 | 109 |  | -0.03763 | 3.2363 | 9.4959 | 16.2159 | 9.2703 | -0.71464 | 25.3208 | 0 | 90.8333 | 90.8333 | 144.207 | 1
269 | 10 | 0 | 151 |  | -0.03763 | 3.2363 | 9.4959 | 16.2159 | 10.2703 | -0.45284 | 30.9877 | 0 | 125.8333 | 125.8333 | 199.773 | 1
269 | 11 | 1 | 181 |  | -0.03763 | 3.2363 | 9.4959 | 16.2159 | 11.2703 | -0.19104 | 34.3951 | 0.89074 | 150.8333 | 151.7241 | 240.8771 | 1
269 | 12 | 4 | 193 |  | -0.03763 | 3.2363 | 9.4959 | 16.2159 | 12.2703 | 0.070755 | 35.0578 | 3.6208 | 160.8333 | 164.4542 | 261.0874 | 1
269 | 13 | 3 | 188 |  | -0.03763 | 3.2363 | 9.4959 | 16.2159 | 13.2703 | 0.33255 | 32.8694 | 2.571 | 156.6667 | 159.2377 | 252.8057 | 1
269 | 14 | 1 | 168 |  | -0.03763 | 3.2363 | 9.4959 | 16.2159 | 14.2703 | 0.59435 | 28.1657 | 0.7494 | 140 | 140.7494 | 223.4537 | 1
269 | 15 | 0 | 131 |  | -0.03763 | 3.2363 | 9.4959 | 16.2159 | 15.2703 | 0.85615 | 21.5378 | 0 | 109.1667 | 109.1667 | 173.313 | 1
269 | 16 | 0 | 84 |  | -0.03763 | 3.2363 | 9.4959 | 16.2159 | 16.2703 | 1.118 | 13.6005 | 0 | 70 | 70 | 111.132 | 1
269 | 17 | 0 | 34 |  | -0.03763 | 3.2363 | 9.4959 | 16.2159 | 17.2703 | 1.3798 | 4.883 | 0 | 28.3333 | 28.3333 | 44.982 | 0
269 | 18 | 0 | 4 |  | -0.03763 | 3.2363 | 9.4959 | 16.2159 | 18.2703 | 1.6416 | -4.1719 | 0 | 3.3333 | 3.3333 | 5.292 | 0
269 | 19 | 0 | 0 |  | -0.03763 | 3.2363 | 9.4959 | 16.2159 | 19.2703 | 1.9034 | -13.1616 | 0 | 0 | 0 | 0 | 0
269 | 20 | 0 | 0 |  | -0.03763 | 3.2363 | 9.4959 | 16.2159 | 20.2703 | 2.1652 | -21.6645 | 0 | 0 | 0 | 0 | 0
269 | 21 | 0 | 0 |  | -0.03763 | 3.2363 | 9.4959 | 16.2159 | 21.2703 | 2.4269 | -29.1779 | 0 | 0 | 0 | 0 | 0
269 | 22 | 0 | 0 |  | -0.03763 | 3.2363 | 9.4959 | 16.2159 | 22.2703 | 2.6887 | -35.078 | 0 | 0 | 0 | 0 | 0
269 | 23 | 0 | 0 |  | -0.03763 | 3.2363 | 9.4959 | 16.2159 | 23.2703 | 2.9505 | -38.6626 | 0 | 0 | 0 | 0 | 0
269 | 24 | 0 | 0 |  | -0.03763 | 3.2363 | 9.4959 | 16.2159 | 24.2703 | 3.2123 | -39.3636 | 0 | 0 | 0 | 0 | 0
270 | 1 | 0 | 0 |  | -0.044449 | 3.2535 | 9.8408 | 16.5608 | 1.276 | -2.8075 | -37.4106 | 0 | 0 | 0 | 0 | 0
270 | 2 | 0 | 0 |  | -0.044449 | 3.2535 | 9.8408 | 16.5608 | 2.276 | -2.5457 | -32.4544 | 0 | 0 | 0 | 0 | 0
270 | 3 | 0 | 0 |  | -0.044449 | 3.2535 | 9.8408 | 16.5608 | 3.276 | -2.2839 | -25.5673 | 0 | 0 | 0 | 0 | 0
270 | 4 | 0 | 0 |  | -0.044449 | 3.2535 | 9.8408 | 16.5608 | 4.276 | -2.0221 | -17.4283 | 0 | 0 | 0 | 0 | 0
270 | 5 | 0 | 0 |  | -0.044449 | 3.2535 | 9.8408 | 16.5608 | 5.276 | -1.7603 | -8.595 | 0 | 0 | 0 | 0 | 0
270 | 6 | 0 | 0 |  | -0.044449 | 3.2535 | 9.8408 | 16.5608 | 6.276 | -1.4985 | 0.48074 | 0 | 0 | 0 | 0 | 0
270 | 7 | 0 | 21 |  | -0.044449 | 3.2535 | 9.8408 | 16.5608 | 7.276 | -1.2367 | 9.3956 | 0 | 17.5 | 17.5 | 27.783 | 0
270 | 8 | 7 | 90 |  | -0.044449 | 3.2535 | 9.8408 | 16.5608 | 8.276 | -0.97494 | 17.7326 | 3.5012 | 75 | 78.5012 | 124.6286 | 1
270 | 9 | 10 | 168 |  | -0.044449 | 3.2535 | 9.8408 | 16.5608 | 9.276 | -0.71314 | 25.0075 | 6.8001 | 140 | 146.8001 | 233.0598 | 1
270 | 10 | 180 | 221 |  | -0.044449 | 3.2535 | 9.8408 | 16.5608 | 10.276 | -0.45134 | 30.6426 | 146.2188 | 184.1667 | 330.3855 | 524.52 | 1
270 | 11 | 72 | 248 |  | -0.044449 | 3.2535 | 9.8408 | 16.5608 | 11.276 | -0.18954 | 34.0201 | 63.9447 | 206.6667 | 270.6113 | 429.6226 | 1
270 | 12 | 503 | 211 |  | -0.044449 | 3.2535 | 9.8408 | 16.5608 | 12.276 | 0.07226 | 34.6631 | 453.818 | 175.8333 | 629.6514 | 999.6345 | 1
270 | 13 | 681 | 144 |  | -0.044449 | 3.2535 | 9.8408 | 16.5608 | 13.276 | 0.33406 | 32.4693 | 581.3509 | 120 | 701.3509 | 1113.4647 | 1
270 | 14 | 636 | 129 |  | -0.044449 | 3.2535 | 9.8408 | 16.5608 | 14.276 | 0.59586 | 27.772 | 474.3149 | 107.5 | 581.8149 | 923.6893 | 1
270 | 15 | 536 | 125 |  | -0.044449 | 3.2535 | 9.8408 | 16.5608 | 15.276 | 0.85766 | 21.1553 | 314.0385 | 104.1667 | 418.2051 | 663.9425 | 1
270 | 16 | 426 | 98 |  | -0.044449 | 3.2535 | 9.8408 | 16.5608 | 16.276 | 1.1195 | 13.2286 | 163.9725 | 81.6667 | 245.6392 | 389.9768 | 1
270 | 17 | 179 | 62 |  | -0.044449 | 3.2535 | 9.8408 | 16.5608 | 17.276 | 1.3813 | 4.5181 | 28.0193 | 51.6667 | 79.686 | 126.5095 | 0
270 | 18 | 0 | 10 |  | -0.044449 | 3.2535 | 9.8408 | 16.5608 | 18.276 | 1.6431 | -4.5348 | 0 | 8.3333 | 8.3333 | 13.23 | 0
270 | 19 | 0 | 0 |  | -0.044449 | 3.2535 | 9.8408 | 16.5608 | 19.276 | 1.9049 | -13.5282 | 0 | 0 | 0 | 0 | 0
270 | 20 | 0 | 0 |  | -0.044449 | 3.2535 | 9.8408 | 16.5608 | 20.276 | 2.1667 | -22.0397 | 0 | 0 | 0 | 0 | 0
270 | 21 | 0 | 0 |  | -0.044449 | 3.2535 | 9.8408 | 16.5608 | 21.276 | 2.4285 | -29.565 | 0 | 0 | 0 | 0 | 0
270 | 22 | 0 | 0 |  | -0.044449 | 3.2535 | 9.8408 | 16.5608 | 22.276 | 2.6903 | -35.4755 | 0 | 0 | 0 | 0 | 0
270 | 23 | 0 | 0 |  | -0.044449 | 3.2535 | 9.8408 | 16.5608 | 23.276 | 2.9521 | -39.0617 | 0 | 0 | 0 | 0 | 0
270 | 24 | 0 | 0 |  | -0.044449 | 3.2535 | 9.8408 | 16.5608 | 24.276 | 3.2139 | -39.7489 | 0 | 0 | 0 | 0 | 0
271 | 1 | 0 | 0 |  | -0.051258 | 3.2707 | 10.1808 | 16.9008 | 1.2817 | -2.806 | -37.7668 | 0 | 0 | 0 | 0 | 0
271 | 2 | 0 | 0 |  | -0.051258 | 3.2707 | 10.1808 | 16.9008 | 2.2817 | -2.5443 | -32.7768 | 0 | 0 | 0 | 0 | 0
271 | 3 | 0 | 0 |  | -0.051258 | 3.2707 | 10.1808 | 16.9008 | 3.2817 | -2.2825 | -25.8598 | 0 | 0 | 0 | 0 | 0
271 | 4 | 0 | 0 |  | -0.051258 | 3.2707 | 10.1808 | 16.9008 | 4.2817 | -2.0207 | -17.6995 | 0 | 0 | 0 | 0 | 0
271 | 5 | 0 | 0 |  | -0.051258 | 3.2707 | 10.1808 | 16.9008 | 5.2817 | -1.7589 | -8.8552 | 0 | 0 | 0 | 0 | 0
271 | 6 | 0 | 0 |  | -0.051258 | 3.2707 | 10.1808 | 16.9008 | 6.2817 | -1.4971 | 0.22137 | 0 | 0 | 0 | 0 | 0
271 | 7 | 4 | 32 |  | -0.051258 | 3.2707 | 10.1808 | 16.9008 | 7.2817 | -1.2353 | 9.1271 | 1.1347 | 26.6667 | 27.8013 | 44.1374 | 0
271 | 8 | 188 | 102 |  | -0.051258 | 3.2707 | 10.1808 | 16.9008 | 8.2817 | -0.97345 | 17.4456 | 93.7213 | 85 | 178.7213 | 283.7379 | 1
271 | 9 | 492 | 119 |  | -0.051258 | 3.2707 | 10.1808 | 16.9008 | 9.2817 | -0.71165 | 24.6936 | 333.6009 | 99.1667 | 432.7676 | 687.0618 | 1
271 | 10 | 656 | 109 |  | -0.051258 | 3.2707 | 10.1808 | 16.9008 | 10.2817 | -0.44986 | 30.2973 | 531.3793 | 90.8333 | 622.2126 | 987.8247 | 1
271 | 11 | 715 | 114 |  | -0.051258 | 3.2707 | 10.1808 | 16.9008 | 11.2817 | -0.18806 | 33.6453 | 633.1037 | 95 | 728.1037 | 1155.9374 | 1
271 | 12 | 757 | 112 |  | -0.051258 | 3.2707 | 10.1808 | 16.9008 | 12.2817 | 0.073744 | 34.269 | 680.6952 | 93.3333 | 774.0286 | 1228.8477 | 1
271 | 13 | 756 | 107 |  | -0.051258 | 3.2707 | 10.1808 | 16.9008 | 13.2817 | 0.33554 | 32.0702 | 642.8397 | 89.1667 | 732.0064 | 1162.1334 | 1
271 | 14 | 718 | 103 |  | -0.051258 | 3.2707 | 10.1808 | 16.9008 | 14.2817 | 0.59734 | 27.3792 | 532.8559 | 85.8333 | 618.6892 | 982.231 | 1
271 | 15 | 590 | 109 |  | -0.051258 | 3.2707 | 10.1808 | 16.9008 | 15.2817 | 0.85914 | 20.7738 | 343.4032 | 90.8333 | 434.2365 | 689.3939 | 1
271 | 16 | 229 | 120 |  | -0.051258 | 3.2707 | 10.1808 | 16.9008 | 16.2817 | 1.1209 | 12.8579 | 87.2325 | 100 | 187.2325 | 297.2504 | 1
271 | 17 | 88 | 74 |  | -0.051258 | 3.2707 | 10.1808 | 16.9008 | 17.2817 | 1.3827 | 4.1545 | 13.421 | 61.6667 | 75.0876 | 119.2091 | 0
271 | 18 | 0 | 9 |  | -0.051258 | 3.2707 | 10.1808 | 16.9008 | 18.2817 | 1.6445 | -4.8964 | 0 | 7.5 | 7.5 | 11.907 | 0
271 | 19 | 0 | 0 |  | -0.051258 | 3.2707 | 10.1808 | 16.9008 | 19.2817 | 1.9063 | -13.8934 | 0 | 0 | 0 | 0 | 0
271 | 20 | 0 | 0 |  | -0.051258 | 3.2707 | 10.1808 | 16.9008 | 20.2817 | 2.1681 | -22.4136 | 0 | 0 | 0 | 0 | 0
271 | 21 | 0 | 0 |  | -0.051258 | 3.2707 | 10.1808 | 16.9008 | 21.2817 | 2.4299 | -29.9509 | 0 | 0 | 0 | 0 | 0
271 | 22 | 0 | 0 |  | -0.051258 | 3.2707 | 10.1808 | 16.9008 | 22.2817 | 2.6917 | -35.872 | 0 | 0 | 0 | 0 | 0
271 | 23 | 0 | 0 |  | -0.051258 | 3.2707 | 10.1808 | 16.9008 | 23.2817 | 2.9535 | -39.4601 | 0 | 0 | 0 | 0 | 0
271 | 24 | 0 | 0 |  | -0.051258 | 3.2707 | 10.1808 | 16.9008 | 24.2817 | 3.2153 | -40.1334 | 0 | 0 | 0 | 0 | 0
272 | 1 | 0 | 0 |  | -0.058053 | 3.2879 | 10.5156 | 17.2356 | 1.2873 | -2.8046 | -38.1222 | 0 | 0 | 0 | 0 | 0
272 | 2 | 0 | 0 |  | -0.058053 | 3.2879 | 10.5156 | 17.2356 | 2.2873 | -2.5428 | -33.0985 | 0 | 0 | 0 | 0 | 0
272 | 3 | 0 | 0 |  | -0.058053 | 3.2879 | 10.5156 | 17.2356 | 3.2873 | -2.281 | -26.1517 | 0 | 0 | 0 | 0 | 0
272 | 4 | 0 | 0 |  | -0.058053 | 3.2879 | 10.5156 | 17.2356 | 4.2873 | -2.0192 | -17.9705 | 0 | 0 | 0 | 0 | 0
272 | 5 | 0 | 0 |  | -0.058053 | 3.2879 | 10.5156 | 17.2356 | 5.2873 | -1.7574 | -9.1154 | 0 | 0 | 0 | 0 | 0
272 | 6 | 0 | 0 |  | -0.058053 | 3.2879 | 10.5156 | 17.2356 | 6.2873 | -1.4956 | -0.038242 | 0 | 0 | 0 | 0 | 0
272 | 7 | 16 | 32 |  | -0.058053 | 3.2879 | 10.5156 | 17.2356 | 7.2873 | -1.2338 | 8.8582 | 4.5153 | 26.6667 | 31.182 | 49.5045 | 0
272 | 8 | 248 | 97 |  | -0.058053 | 3.2879 | 10.5156 | 17.2356 | 8.2873 | -0.97199 | 17.158 | 123.2115 | 80.8333 | 204.0448 | 323.9415 | 1
272 | 9 | 503 | 111 |  | -0.058053 | 3.2879 | 10.5156 | 17.2356 | 9.2873 | -0.71019 | 24.3794 | 340.0546 | 92.5 | 432.5546 | 686.7237 | 1
272 | 10 | 643 | 111 |  | -0.058053 | 3.2879 | 10.5156 | 17.2356 | 10.2873 | -0.44839 | 29.9518 | 519.3439 | 92.5 | 611.8439 | 971.3633 | 1
272 | 11 | 361 | 226 |  | -0.058053 | 3.2879 | 10.5156 | 17.2356 | 11.2873 | -0.1866 | 33.2708 | 318.6754 | 188.3333 | 507.0088 | 804.9271 | 1
272 | 12 | 662 | 156 |  | -0.058053 | 3.2879 | 10.5156 | 17.2356 | 12.2873 | 0.075204 | 33.8757 | 593.2467 | 130 | 723.2467 | 1148.2264 | 1
272 | 13 | 722 | 116 |  | -0.058053 | 3.2879 | 10.5156 | 17.2356 | 13.2873 | 0.337 | 31.6721 | 611.4859 | 96.6667 | 708.1526 | 1124.263 | 1
272 | 14 | 684 | 110 |  | -0.058053 | 3.2879 | 10.5156 | 17.2356 | 14.2873 | 0.5988 | 26.9876 | 505.1217 | 91.6667 | 596.7883 | 947.4612 | 1
272 | 15 | 576 | 111 |  | -0.058053 | 3.2879 | 10.5156 | 17.2356 | 15.2873 | 0.8606 | 20.3935 | 333.0315 | 92.5 | 425.5315 | 675.5738 | 1
272 | 16 | 222 | 118 |  | -0.058053 | 3.2879 | 10.5156 | 17.2356 | 16.2873 | 1.1224 | 12.4885 | 83.6831 | 98.3333 | 182.0164 | 288.9692 | 0
272 | 17 | 0 | 47 |  | -0.058053 | 3.2879 | 10.5156 | 17.2356 | 17.2873 | 1.3842 | 3.7923 | 0 | 39.1667 | 39.1667 | 62.181 | 0
272 | 18 | 0 | 4 |  | -0.058053 | 3.2879 | 10.5156 | 17.2356 | 18.2873 | 1.646 | -5.2566 | 0 | 3.3333 | 3.3333 | 5.292 | 0
272 | 19 | 0 | 0 |  | -0.058053 | 3.2879 | 10.5156 | 17.2356 | 19.2873 | 1.9078 | -14.257 | 0 | 0 | 0 | 0 | 0
272 | 20 | 0 | 0 |  | -0.058053 | 3.2879 | 10.5156 | 17.2356 | 20.2873 | 2.1696 | -22.786 | 0 | 0 | 0 | 0 | 0
272 | 21 | 0 | 0 |  | -0.058053 | 3.2879 | 10.5156 | 17.2356 | 21.2873 | 2.4314 | -30.3353 | 0 | 0 | 0 | 0 | 0
272 | 22 | 0 | 0 |  | -0.058053 | 3.2879 | 10.5156 | 17.2356 | 22.2873 | 2.6932 | -36.2674 | 0 | 0 | 0 | 0 | 0
272 | 23 | 0 | 0 |  | -0.058053 | 3.2879 | 10.5156 | 17.2356 | 23.2873 | 2.955 | -39.8575 | 0 | 0 | 0 | 0 | 0
272 | 24 | 0 | 0 |  | -0.058053 | 3.2879 | 10.5156 | 17.2356 | 24.2873 | 3.2168 | -40.5171 | 0 | 0 | 0 | 0 | 0
273 | 1 | 0 | 0 |  | -0.064834 | 3.3051 | 10.8447 | 17.5647 | 1.2927 | -2.8032 | -38.4768 | 0 | 0 | 0 | 0 | 0
273 | 2 | 0 | 0 |  | -0.064834 | 3.3051 | 10.8447 | 17.5647 | 2.2927 | -2.5414 | -33.4194 | 0 | 0 | 0 | 0 | 0
273 | 3 | 0 | 0 |  | -0.064834 | 3.3051 | 10.8447 | 17.5647 | 3.2927 | -2.2796 | -26.4431 | 0 | 0 | 0 | 0 | 0
273 | 4 | 0 | 0 |  | -0.064834 | 3.3051 | 10.8447 | 17.5647 | 4.2927 | -2.0178 | -18.2411 | 0 | 0 | 0 | 0 | 0
273 | 5 | 0 | 0 |  | -0.064834 | 3.3051 | 10.8447 | 17.5647 | 5.2927 | -1.756 | -9.3755 | 0 | 0 | 0 | 0 | 0
273 | 6 | 0 | 0 |  | -0.064834 | 3.3051 | 10.8447 | 17.5647 | 6.2927 | -1.4942 | -0.29809 | 0 | 0 | 0 | 0 | 0
273 | 7 | 0 | 17 |  | -0.064834 | 3.3051 | 10.8447 | 17.5647 | 7.2927 | -1.2324 | 8.5888 | 0 | 14.1667 | 14.1667 | 22.491 | 0
273 | 8 | 5 | 84 |  | -0.064834 | 3.3051 | 10.8447 | 17.5647 | 8.2927 | -0.97056 | 16.8699 | 2.4754 | 70 | 72.4754 | 115.062 | 1
273 | 9 | 144 | 158 |  | -0.064834 | 3.3051 | 10.8447 | 17.5647 | 9.2927 | -0.70876 | 24.0647 | 97.0579 | 131.6667 | 228.7246 | 363.1231 | 1
273 | 10 | 64 | 202 |  | -0.064834 | 3.3051 | 10.8447 | 17.5647 | 10.2927 | -0.44696 | 29.6063 | 51.5395 | 168.3333 | 219.8729 | 349.0702 | 1
273 | 11 | 46 | 254 |  | -0.064834 | 3.3051 | 10.8447 | 17.5647 | 11.2927 | -0.18516 | 32.8968 | 40.4807 | 211.6667 | 252.1473 | 400.3091 | 1
273 | 12 | 48 | 272 |  | -0.064834 | 3.3051 | 10.8447 | 17.5647 | 12.2927 | 0.07664 | 33.4832 | 42.8664 | 226.6667 | 269.5331 | 427.9107 | 1
273 | 13 | 48 | 265 |  | -0.064834 | 3.3051 | 10.8447 | 17.5647 | 13.2927 | 0.33844 | 31.2752 | 40.4891 | 220.8333 | 261.3224 | 414.8755 | 1
273 | 14 | 44 | 233 |  | -0.064834 | 3.3051 | 10.8447 | 17.5647 | 14.2927 | 0.60024 | 26.5972 | 32.3316 | 194.1667 | 226.4983 | 359.5886 | 1
273 | 15 | 45 | 177 |  | -0.064834 | 3.3051 | 10.8447 | 17.5647 | 15.2927 | 0.86204 | 20.0146 | 25.8442 | 147.5 | 173.3442 | 275.2013 | 1
273 | 16 | 10 | 117 |  | -0.064834 | 3.3051 | 10.8447 | 17.5647 | 16.2927 | 1.1238 | 12.1205 | 3.7298 | 97.5 | 101.2298 | 160.7125 | 0
273 | 17 | 6 | 55 |  | -0.064834 | 3.3051 | 10.8447 | 17.5647 | 17.2927 | 1.3856 | 3.4316 | 0.86717 | 45.8333 | 46.7005 | 74.1417 | 0
273 | 18 | 0 | 2 |  | -0.064834 | 3.3051 | 10.8447 | 17.5647 | 18.2927 | 1.6474 | -5.6151 | 0 | 1.6667 | 1.6667 | 2.646 | 0
273 | 19 | 0 | 0 |  | -0.064834 | 3.3051 | 10.8447 | 17.5647 | 19.2927 | 1.9092 | -14.619 | 0 | 0 | 0 | 0 | 0
273 | 20 | 0 | 0 |  | -0.064834 | 3.3051 | 10.8447 | 17.5647 | 20.2927 | 2.171 | -23.1567 | 0 | 0 | 0 | 0 | 0
273 | 21 | 0 | 0 |  | -0.064834 | 3.3051 | 10.8447 | 17.5647 | 21.2927 | 2.4328 | -30.7182 | 0 | 0 | 0 | 0 | 0
273 | 22 | 0 | 0 |  | -0.064834 | 3.3051 | 10.8447 | 17.5647 | 22.2927 | 2.6946 | -36.6614 | 0 | 0 | 0 | 0 | 0
273 | 23 | 0 | 0 |  | -0.064834 | 3.3051 | 10.8447 | 17.5647 | 23.2927 | 2.9564 | -40.2538 | 0 | 0 | 0 | 0 | 0
273 | 24 | 0 | 0 |  | -0.064834 | 3.3051 | 10.8447 | 17.5647 | 24.2927 | 3.2182 | -40.9 | 0 | 0 | 0 | 0 | 0
274 | 1 | 0 | 0 |  | -0.071599 | 3.3223 | 11.1678 | 17.8878 | 1.2981 | -2.8017 | -38.8304 | 0 | 0 | 0 | 0 | 0
274 | 2 | 0 | 0 |  | -0.071599 | 3.3223 | 11.1678 | 17.8878 | 2.2981 | -2.5399 | -33.7396 | 0 | 0 | 0 | 0 | 0
274 | 3 | 0 | 0 |  | -0.071599 | 3.3223 | 11.1678 | 17.8878 | 3.2981 | -2.2781 | -26.7338 | 0 | 0 | 0 | 0 | 0
274 | 4 | 0 | 0 |  | -0.071599 | 3.3223 | 11.1678 | 17.8878 | 4.2981 | -2.0163 | -18.5114 | 0 | 0 | 0 | 0 | 0
274 | 5 | 0 | 0 |  | -0.071599 | 3.3223 | 11.1678 | 17.8878 | 5.2981 | -1.7545 | -9.6357 | 0 | 0 | 0 | 0 | 0
274 | 6 | 0 | 0 |  | -0.071599 | 3.3223 | 11.1678 | 17.8878 | 6.2981 | -1.4927 | -0.55815 | 0 | 0 | 0 | 0 | 0
274 | 7 | 0 | 21 |  | -0.071599 | 3.3223 | 11.1678 | 17.8878 | 7.2981 | -1.2309 | 8.3191 | 0 | 17.5 | 17.5 | 27.783 | 0
274 | 8 | 72 | 91 |  | -0.071599 | 3.3223 | 11.1678 | 17.8878 | 8.2981 | -0.96915 | 16.5814 | 35.5186 | 75.8333 | 111.3519 | 176.7823 | 1
274 | 9 | 10 | 158 |  | -0.071599 | 3.3223 | 11.1678 | 17.8878 | 9.2981 | -0.70735 | 23.7498 | 6.7193 | 131.6667 | 138.386 | 219.7016 | 1
274 | 10 | 287 | 209 |  | -0.071599 | 3.3223 | 11.1678 | 17.8878 | 10.2981 | -0.44555 | 29.2608 | 230.4263 | 174.1667 | 404.593 | 642.3318 | 1
274 | 11 | 334 | 233 |  | -0.071599 | 3.3223 | 11.1678 | 17.8878 | 11.2981 | -0.18375 | 32.5232 | 292.9955 | 194.1667 | 487.1622 | 773.4186 | 1
274 | 12 | 204 | 265 |  | -0.071599 | 3.3223 | 11.1678 | 17.8878 | 12.2981 | 0.07805 | 33.0917 | 181.5443 | 220.8333 | 402.3777 | 638.8148 | 1
274 | 13 | 130 | 298 |  | -0.071599 | 3.3223 | 11.1678 | 17.8878 | 13.2981 | 0.33985 | 30.8795 | 109.2114 | 248.3333 | 357.5447 | 567.638 | 1
274 | 14 | 124 | 263 |  | -0.071599 | 3.3223 | 11.1678 | 17.8878 | 14.2981 | 0.60165 | 26.2083 | 90.6591 | 219.1667 | 309.8258 | 491.8794 | 1
274 | 15 | 418 | 160 |  | -0.071599 | 3.3223 | 11.1678 | 17.8878 | 15.2981 | 0.86345 | 19.6372 | 238.4487 | 133.3333 | 371.7821 | 590.2412 | 1
274 | 16 | 368 | 95 |  | -0.071599 | 3.3223 | 11.1678 | 17.8878 | 16.2981 | 1.1252 | 11.7541 | 135.8016 | 79.1667 | 214.9682 | 341.2836 | 0
274 | 17 | 73 | 51 |  | -0.071599 | 3.3223 | 11.1678 | 17.8878 | 17.2981 | 1.387 | 3.0725 | 10.2618 | 42.5 | 52.7618 | 83.7646 | 0
274 | 18 | 0 | 6 |  | -0.071599 | 3.3223 | 11.1678 | 17.8878 | 18.2981 | 1.6488 | -5.9719 | 0 | 5 | 5 | 7.938 | 0
274 | 19 | 0 | 0 |  | -0.071599 | 3.3223 | 11.1678 | 17.8878 | 19.2981 | 1.9106 | -14.9793 | 0 | 0 | 0 | 0 | 0
274 | 20 | 0 | 0 |  | -0.071599 | 3.3223 | 11.1678 | 17.8878 | 20.2981 | 2.1724 | -23.5257 | 0 | 0 | 0 | 0 | 0
274 | 21 | 0 | 0 |  | -0.071599 | 3.3223 | 11.1678 | 17.8878 | 21.2981 | 2.4342 | -31.0995 | 0 | 0 | 0 | 0 | 0
274 | 22 | 0 | 0 |  | -0.071599 | 3.3223 | 11.1678 | 17.8878 | 22.2981 | 2.696 | -37.0541 | 0 | 0 | 0 | 0 | 0
274 | 23 | 0 | 0 |  | -0.071599 | 3.3223 | 11.1678 | 17.8878 | 23.2981 | 2.9578 | -40.6491 | 0 | 0 | 0 | 0 | 0
274 | 24 | 0 | 0 |  | -0.071599 | 3.3223 | 11.1678 | 17.8878 | 24.2981 | 3.2196 | -41.2818 | 0 | 0 | 0 | 0 | 0
275 | 1 | 0 | 0 |  | -0.078346 | 3.3396 | 11.4844 | 18.2044 | 1.3034 | -2.8004 | -39.1831 | 0 | 0 | 0 | 0 | 0
275 | 2 | 0 | 0 |  | -0.078346 | 3.3396 | 11.4844 | 18.2044 | 2.3034 | -2.5386 | -34.0588 | 0 | 0 | 0 | 0 | 0
275 | 3 | 0 | 0 |  | -0.078346 | 3.3396 | 11.4844 | 18.2044 | 3.3034 | -2.2768 | -27.0239 | 0 | 0 | 0 | 0 | 0
275 | 4 | 0 | 0 |  | -0.078346 | 3.3396 | 11.4844 | 18.2044 | 4.3034 | -2.015 | -18.7814 | 0 | 0 | 0 | 0 | 0
275 | 5 | 0 | 0 |  | -0.078346 | 3.3396 | 11.4844 | 18.2044 | 5.3034 | -1.7532 | -9.8957 | 0 | 0 | 0 | 0 | 0
275 | 6 | 0 | 0 |  | -0.078346 | 3.3396 | 11.4844 | 18.2044 | 6.3034 | -1.4914 | -0.81839 | 0 | 0 | 0 | 0 | 0
275 | 7 | 5 | 27 |  | -0.078346 | 3.3396 | 11.4844 | 18.2044 | 7.3034 | -1.2296 | 8.0491 | 1.3882 | 22.5 | 23.8882 | 37.9249 | 0
275 | 8 | 216 | 96 |  | -0.078346 | 3.3396 | 11.4844 | 18.2044 | 8.3034 | -0.96777 | 16.2926 | 106.1645 | 80 | 186.1645 | 295.5548 | 1
275 | 9 | 473 | 111 |  | -0.078346 | 3.3396 | 11.4844 | 18.2044 | 9.3034 | -0.70597 | 23.4346 | 316.8193 | 92.5 | 409.3193 | 649.8354 | 1
275 | 10 | 323 | 188 |  | -0.078346 | 3.3396 | 11.4844 | 18.2044 | 10.3034 | -0.44417 | 28.9154 | 258.5328 | 156.6667 | 415.1995 | 659.1707 | 1
275 | 11 | 329 | 231 |  | -0.078346 | 3.3396 | 11.4844 | 18.2044 | 11.3034 | -0.18237 | 32.1503 | 287.6812 | 192.5 | 480.1812 | 762.3356 | 1
275 | 12 | 338 | 246 |  | -0.078346 | 3.3396 | 11.4844 | 18.2044 | 12.3034 | 0.079432 | 32.7013 | 299.7263 | 205 | 504.7263 | 801.3035 | 1
275 | 13 | 206 | 251 |  | -0.078346 | 3.3396 | 11.4844 | 18.2044 | 13.3034 | 0.34123 | 30.4853 | 172.3457 | 209.1667 | 381.5123 | 605.689 | 1
275 | 14 | 334 | 204 |  | -0.078346 | 3.3396 | 11.4844 | 18.2044 | 14.3034 | 0.60303 | 25.8209 | 242.9594 | 170 | 412.9594 | 655.6143 | 1
275 | 15 | 90 | 152 |  | -0.078346 | 3.3396 | 11.4844 | 18.2044 | 15.3034 | 0.86483 | 19.2614 | 50.9929 | 126.6667 | 177.6596 | 282.0523 | 1
275 | 16 | 233 | 119 |  | -0.078346 | 3.3396 | 11.4844 | 18.2044 | 16.3034 | 1.1266 | 11.3894 | 85.0645 | 99.1667 | 184.2312 | 292.4854 | 0
275 | 17 | 8 | 49 |  | -0.078346 | 3.3396 | 11.4844 | 18.2044 | 17.3034 | 1.3884 | 2.7153 | 1.0931 | 40.8333 | 41.9265 | 66.5625 | 0
275 | 18 | 0 | 4 |  | -0.078346 | 3.3396 | 11.4844 | 18.2044 | 18.3034 | 1.6502 | -6.3269 | 0 | 3.3333 | 3.3333 | 5.292 | 0
275 | 19 | 0 | 0 |  | -0.078346 | 3.3396 | 11.4844 | 18.2044 | 19.3034 | 1.912 | -15.3375 | 0 | 0 | 0 | 0 | 0
275 | 20 | 0 | 0 |  | -0.078346 | 3.3396 | 11.4844 | 18.2044 | 20.3034 | 2.1738 | -23.8927 | 0 | 0 | 0 | 0 | 0
275 | 21 | 0 | 0 |  | -0.078346 | 3.3396 | 11.4844 | 18.2044 | 21.3034 | 2.4356 | -31.479 | 0 | 0 | 0 | 0 | 0
275 | 22 | 0 | 0 |  | -0.078346 | 3.3396 | 11.4844 | 18.2044 | 22.3034 | 2.6974 | -37.4452 | 0 | 0 | 0 | 0 | 0
275 | 23 | 0 | 0 |  | -0.078346 | 3.3396 | 11.4844 | 18.2044 | 23.3034 | 2.9592 | -41.043 | 0 | 0 | 0 | 0 | 0
275 | 24 | 0 | 0 |  | -0.078346 | 3.3396 | 11.4844 | 18.2044 | 24.3034 | 3.221 | -41.6626 | 0 | 0 | 0 | 0 | 0
276 | 1 | 0 | 0 |  | -0.085073 | 3.3568 | 11.7943 | 18.5143 | 1.3086 | -2.799 | -39.5346 | 0 | 0 | 0 | 0 | 0
276 | 2 | 0 | 0 |  | -0.085073 | 3.3568 | 11.7943 | 18.5143 | 2.3086 | -2.5372 | -34.3771 | 0 | 0 | 0 | 0 | 0
276 | 3 | 0 | 0 |  | -0.085073 | 3.3568 | 11.7943 | 18.5143 | 3.3086 | -2.2754 | -27.3133 | 0 | 0 | 0 | 0 | 0
276 | 4 | 0 | 0 |  | -0.085073 | 3.3568 | 11.7943 | 18.5143 | 4.3086 | -2.0136 | -19.051 | 0 | 0 | 0 | 0 | 0
276 | 5 | 0 | 0 |  | -0.085073 | 3.3568 | 11.7943 | 18.5143 | 5.3086 | -1.7518 | -10.1557 | 0 | 0 | 0 | 0 | 0
276 | 6 | 0 | 0 |  | -0.085073 | 3.3568 | 11.7943 | 18.5143 | 6.3086 | -1.49 | -1.0788 | 0 | 0 | 0 | 0 | 0
276 | 7 | 0 | 24 |  | -0.085073 | 3.3568 | 11.7943 | 18.5143 | 7.3086 | -1.2282 | 7.7787 | 0 | 20 | 20 | 31.752 | 0
276 | 8 | 132 | 88 |  | -0.085073 | 3.3568 | 11.7943 | 18.5143 | 8.3086 | -0.96641 | 16.0034 | 64.6342 | 73.3333 | 137.9676 | 219.0373 | 1
276 | 9 | 271 | 137 |  | -0.085073 | 3.3568 | 11.7943 | 18.5143 | 9.3086 | -0.70461 | 23.1193 | 180.9314 | 114.1667 | 295.098 | 468.4976 | 1
276 | 10 | 526 | 145 |  | -0.085073 | 3.3568 | 11.7943 | 18.5143 | 10.3086 | -0.44281 | 28.5703 | 419.6964 | 120.8333 | 540.5298 | 858.145 | 1
276 | 11 | 634 | 131 |  | -0.085073 | 3.3568 | 11.7943 | 18.5143 | 11.3086 | -0.18102 | 31.778 | 552.564 | 109.1667 | 661.7306 | 1050.5636 | 1
276 | 12 | 660 | 132 |  | -0.085073 | 3.3568 | 11.7943 | 18.5143 | 12.3086 | 0.080784 | 32.312 | 583.1592 | 110 | 693.1592 | 1100.4595 | 1
276 | 13 | 517 | 178 |  | -0.085073 | 3.3568 | 11.7943 | 18.5143 | 13.3086 | 0.34258 | 30.0925 | 430.7386 | 148.3333 | 579.0719 | 919.3346 | 1
276 | 14 | 351 | 194 |  | -0.085073 | 3.3568 | 11.7943 | 18.5143 | 14.3086 | 0.60438 | 25.4352 | 254.024 | 161.6667 | 415.6907 | 659.9505 | 1
276 | 15 | 485 | 126 |  | -0.085073 | 3.3568 | 11.7943 | 18.5143 | 15.3086 | 0.86618 | 18.8874 | 272.9228 | 105 | 377.9228 | 599.9902 | 1
276 | 16 | 112 | 111 |  | -0.085073 | 3.3568 | 11.7943 | 18.5143 | 16.3086 | 1.128 | 11.0265 | 40.4497 | 92.5 | 132.9497 | 211.0709 | 0
276 | 17 | 0 | 23 |  | -0.085073 | 3.3568 | 11.7943 | 18.5143 | 17.3086 | 1.3898 | 2.3599 | 0 | 19.1667 | 19.1667 | 30.429 | 0
276 | 18 | 0 | 1 |  | -0.085073 | 3.3568 | 11.7943 | 18.5143 | 18.3086 | 1.6516 | -6.6798 | 0 | 0.83333 | 0.83333 | 1.323 | 0
276 | 19 | 0 | 0 |  | -0.085073 | 3.3568 | 11.7943 | 18.5143 | 19.3086 | 1.9134 | -15.6937 | 0 | 0 | 0 | 0 | 0
276 | 20 | 0 | 0 |  | -0.085073 | 3.3568 | 11.7943 | 18.5143 | 20.3086 | 2.1752 | -24.2577 | 0 | 0 | 0 | 0 | 0
276 | 21 | 0 | 0 |  | -0.085073 | 3.3568 | 11.7943 | 18.5143 | 21.3086 | 2.437 | -31.8565 | 0 | 0 | 0 | 0 | 0
276 | 22 | 0 | 0 |  | -0.085073 | 3.3568 | 11.7943 | 18.5143 | 22.3086 | 2.6988 | -37.8346 | 0 | 0 | 0 | 0 | 0
276 | 23 | 0 | 0 |  | -0.085073 | 3.3568 | 11.7943 | 18.5143 | 23.3086 | 2.9606 | -41.4356 | 0 | 0 | 0 | 0 | 0
276 | 24 | 0 | 0 |  | -0.085073 | 3.3568 | 11.7943 | 18.5143 | 24.3086 | 3.2224 | -42.0421 | 0 | 0 | 0 | 0 | 0
277 | 1 | 0 | 0 |  | -0.091779 | 3.374 | 12.0971 | 18.8171 | 1.3136 | -2.7977 | -39.8851 | 0 | 0 | 0 | 0 | 0
277 | 2 | 0 | 0 |  | -0.091779 | 3.374 | 12.0971 | 18.8171 | 2.3136 | -2.5359 | -34.6945 | 0 | 0 | 0 | 0 | 0
277 | 3 | 0 | 0 |  | -0.091779 | 3.374 | 12.0971 | 18.8171 | 3.3136 | -2.2741 | -27.602 | 0 | 0 | 0 | 0 | 0
277 | 4 | 0 | 0 |  | -0.091779 | 3.374 | 12.0971 | 18.8171 | 4.3136 | -2.0123 | -19.3202 | 0 | 0 | 0 | 0 | 0
277 | 5 | 0 | 0 |  | -0.091779 | 3.374 | 12.0971 | 18.8171 | 5.3136 | -1.7505 | -10.4156 | 0 | 0 | 0 | 0 | 0
277 | 6 | 0 | 0 |  | -0.091779 | 3.374 | 12.0971 | 18.8171 | 6.3136 | -1.4887 | -1.3393 | 0 | 0 | 0 | 0 | 0
277 | 7 | 0 | 9 |  | -0.091779 | 3.374 | 12.0971 | 18.8171 | 7.3136 | -1.2269 | 7.5081 | 0 | 7.5 | 7.5 | 11.907 | 0
277 | 8 | 9 | 74 |  | -0.091779 | 3.374 | 12.0971 | 18.8171 | 8.3136 | -0.96509 | 15.7139 | 4.3899 | 61.6667 | 66.0566 | 104.8714 | 1
277 | 9 | 144 | 146 |  | -0.091779 | 3.374 | 12.0971 | 18.8171 | 9.3136 | -0.70329 | 22.8038 | 95.823 | 121.6667 | 217.4896 | 345.2865 | 1
277 | 10 | 46 | 198 |  | -0.091779 | 3.374 | 12.0971 | 18.8171 | 10.3136 | -0.44149 | 28.2254 | 36.5862 | 165 | 201.5862 | 320.0382 | 1
277 | 11 | 2 | 165 |  | -0.091779 | 3.374 | 12.0971 | 18.8171 | 11.3136 | -0.17969 | 31.4066 | 1.7373 | 137.5 | 139.2373 | 221.0532 | 1
277 | 12 | 72 | 244 |  | -0.091779 | 3.374 | 12.0971 | 18.8171 | 12.3136 | 0.082105 | 31.9241 | 63.3856 | 203.3333 | 266.7189 | 423.443 | 1
277 | 13 | 203 | 245 |  | -0.091779 | 3.374 | 12.0971 | 18.8171 | 13.3136 | 0.3439 | 29.7013 | 168.4192 | 204.1667 | 372.5859 | 591.5174 | 1
277 | 14 | 325 | 200 |  | -0.091779 | 3.374 | 12.0971 | 18.8171 | 14.3136 | 0.6057 | 25.0513 | 233.9999 | 166.6667 | 400.6666 | 636.0982 | 1
277 | 15 | 312 | 146 |  | -0.091779 | 3.374 | 12.0971 | 18.8171 | 15.3136 | 0.8675 | 18.5152 | 174.3683 | 121.6667 | 296.035 | 469.9851 | 1
277 | 16 | 20 | 101 |  | -0.091779 | 3.374 | 12.0971 | 18.8171 | 16.3136 | 1.1293 | 10.6656 | 7.145 | 84.1667 | 91.3117 | 144.9664 | 0
277 | 17 | 0 | 43 |  | -0.091779 | 3.374 | 12.0971 | 18.8171 | 17.3136 | 1.3911 | 2.0067 | 0 | 35.8333 | 35.8333 | 56.889 | 0
277 | 18 | 0 | 2 |  | -0.091779 | 3.374 | 12.0971 | 18.8171 | 18.3136 | 1.6529 | -7.0305 | 0 | 1.6667 | 1.6667 | 2.646 | 0
277 | 19 | 0 | 0 |  | -0.091779 | 3.374 | 12.0971 | 18.8171 | 19.3136 | 1.9147 | -16.0477 | 0 | 0 | 0 | 0 | 0
277 | 20 | 0 | 0 |  | -0.091779 | 3.374 | 12.0971 | 18.8171 | 20.3136 | 2.1765 | -24.6204 | 0 | 0 | 0 | 0 | 0
277 | 21 | 0 | 0 |  | -0.091779 | 3.374 | 12.0971 | 18.8171 | 21.3136 | 2.4383 | -32.232 | 0 | 0 | 0 | 0 | 0
277 | 22 | 0 | 0 |  | -0.091779 | 3.374 | 12.0971 | 18.8171 | 22.3136 | 2.7001 | -38.2222 | 0 | 0 | 0 | 0 | 0
277 | 23 | 0 | 0 |  | -0.091779 | 3.374 | 12.0971 | 18.8171 | 23.3136 | 2.9619 | -41.8267 | 0 | 0 | 0 | 0 | 0
277 | 24 | 0 | 0 |  | -0.091779 | 3.374 | 12.0971 | 18.8171 | 24.3136 | 3.2237 | -42.4205 | 0 | 0 | 0 | 0 | 0
278 | 1 | 0 | 0 |  | -0.098461 | 3.3912 | 12.3923 | 19.1123 | 1.3185 | -2.7964 | -40.2343 | 0 | 0 | 0 | 0 | 0
278 | 2 | 0 | 0 |  | -0.098461 | 3.3912 | 12.3923 | 19.1123 | 2.3185 | -2.5346 | -35.0108 | 0 | 0 | 0 | 0 | 0
278 | 3 | 0 | 0 |  | -0.098461 | 3.3912 | 12.3923 | 19.1123 | 3.3185 | -2.2728 | -27.89 | 0 | 0 | 0 | 0 | 0
278 | 4 | 0 | 0 |  | -0.098461 | 3.3912 | 12.3923 | 19.1123 | 4.3185 | -2.011 | -19.589 | 0 | 0 | 0 | 0 | 0
278 | 5 | 0 | 0 |  | -0.098461 | 3.3912 | 12.3923 | 19.1123 | 5.3185 | -1.7492 | -10.6753 | 0 | 0 | 0 | 0 | 0
278 | 6 | 0 | 0 |  | -0.098461 | 3.3912 | 12.3923 | 19.1123 | 6.3185 | -1.4874 | -1.5999 | 0 | 0 | 0 | 0 | 0
278 | 7 | 0 | 8 |  | -0.098461 | 3.3912 | 12.3923 | 19.1123 | 7.3185 | -1.2256 | 7.2372 | 0 | 6.6667 | 6.6667 | 10.584 | 0
278 | 8 | 0 | 46 |  | -0.098461 | 3.3912 | 12.3923 | 19.1123 | 8.3185 | -0.9638 | 15.4242 | 0 | 38.3333 | 38.3333 | 60.858 | 1
278 | 9 | 0 | 94 |  | -0.098461 | 3.3912 | 12.3923 | 19.1123 | 9.3185 | -0.70201 | 22.4884 | 0 | 78.3333 | 78.3333 | 124.362 | 1
278 | 10 | 46 | 194 |  | -0.098461 | 3.3912 | 12.3923 | 19.1123 | 10.3185 | -0.44021 | 27.8809 | 36.4671 | 161.6667 | 198.1337 | 314.5571 | 1
278 | 11 | 1 | 162 |  | -0.098461 | 3.3912 | 12.3923 | 19.1123 | 11.3185 | -0.17841 | 31.0361 | 0.86573 | 135 | 135.8657 | 215.7004 | 1
278 | 12 | 1 | 174 |  | -0.098461 | 3.3912 | 12.3923 | 19.1123 | 12.3185 | 0.083393 | 31.5375 | 0.87711 | 145 | 145.8771 | 231.5945 | 1
278 | 13 | 1 | 169 |  | -0.098461 | 3.3912 | 12.3923 | 19.1123 | 13.3185 | 0.34519 | 29.3119 | 0.82614 | 140.8333 | 141.6595 | 224.8986 | 1
278 | 14 | 66 | 204 |  | -0.098461 | 3.3912 | 12.3923 | 19.1123 | 14.3185 | 0.60699 | 24.6693 | 47.2744 | 170 | 217.2744 | 344.9449 | 1
278 | 15 | 14 | 171 |  | -0.098461 | 3.3912 | 12.3923 | 19.1123 | 15.3185 | 0.86879 | 18.1451 | 7.7704 | 142.5 | 150.2704 | 238.5692 | 1
278 | 16 | 0 | 64 |  | -0.098461 | 3.3912 | 12.3923 | 19.1123 | 16.3185 | 1.1306 | 10.3068 | 0 | 53.3333 | 53.3333 | 84.672 | 0
278 | 17 | 0 | 19 |  | -0.098461 | 3.3912 | 12.3923 | 19.1123 | 17.3185 | 1.3924 | 1.6556 | 0 | 15.8333 | 15.8333 | 25.137 | 0
278 | 18 | 0 | 1 |  | -0.098461 | 3.3912 | 12.3923 | 19.1123 | 18.3185 | 1.6542 | -7.3789 | 0 | 0.83333 | 0.83333 | 1.323 | 0
278 | 19 | 0 | 0 |  | -0.098461 | 3.3912 | 12.3923 | 19.1123 | 19.3185 | 1.916 | -16.3993 | 0 | 0 | 0 | 0 | 0
278 | 20 | 0 | 0 |  | -0.098461 | 3.3912 | 12.3923 | 19.1123 | 20.3185 | 2.1778 | -24.9808 | 0 | 0 | 0 | 0 | 0
278 | 21 | 0 | 0 |  | -0.098461 | 3.3912 | 12.3923 | 19.1123 | 21.3185 | 2.4396 | -32.6052 | 0 | 0 | 0 | 0 | 0
278 | 22 | 0 | 0 |  | -0.098461 | 3.3912 | 12.3923 | 19.1123 | 22.3185 | 2.7014 | -38.6078 | 0 | 0 | 0 | 0 | 0
278 | 23 | 0 | 0 |  | -0.098461 | 3.3912 | 12.3923 | 19.1123 | 23.3185 | 2.9632 | -42.2162 | 0 | 0 | 0 | 0 | 0
278 | 24 | 0 | 0 |  | -0.098461 | 3.3912 | 12.3923 | 19.1123 | 24.3185 | 3.225 | -42.7975 | 0 | 0 | 0 | 0 | 0
279 | 1 | 0 | 0 |  | -0.10512 | 3.4084 | 12.6796 | 19.3996 | 1.3233 | -2.7951 | -40.5824 | 0 | 0 | 0 | 0 | 0
279 | 2 | 0 | 0 |  | -0.10512 | 3.4084 | 12.6796 | 19.3996 | 2.3233 | -2.5333 | -35.3262 | 0 | 0 | 0 | 0 | 0
279 | 3 | 0 | 0 |  | -0.10512 | 3.4084 | 12.6796 | 19.3996 | 3.3233 | -2.2715 | -28.1773 | 0 | 0 | 0 | 0 | 0
279 | 4 | 0 | 0 |  | -0.10512 | 3.4084 | 12.6796 | 19.3996 | 4.3233 | -2.0097 | -19.8573 | 0 | 0 | 0 | 0 | 0
279 | 5 | 0 | 0 |  | -0.10512 | 3.4084 | 12.6796 | 19.3996 | 5.3233 | -1.7479 | -10.9349 | 0 | 0 | 0 | 0 | 0
279 | 6 | 0 | 0 |  | -0.10512 | 3.4084 | 12.6796 | 19.3996 | 6.3233 | -1.4861 | -1.8607 | 0 | 0 | 0 | 0 | 0
279 | 7 | 0 | 22 |  | -0.10512 | 3.4084 | 12.6796 | 19.3996 | 7.3233 | -1.2244 | 6.9661 | 0 | 18.3333 | 18.3333 | 29.106 | 0
279 | 8 | 195 | 88 |  | -0.10512 | 3.4084 | 12.6796 | 19.3996 | 8.3233 | -0.96255 | 15.1343 | 94.3554 | 73.3333 | 167.6887 | 266.2226 | 1
279 | 9 | 461 | 97 |  | -0.10512 | 3.4084 | 12.6796 | 19.3996 | 9.3233 | -0.70075 | 22.1729 | 304.6757 | 80.8333 | 385.5091 | 612.0342 | 1
279 | 10 | 182 | 193 |  | -0.10512 | 3.4084 | 12.6796 | 19.3996 | 10.3233 | -0.43895 | 27.5368 | 143.8043 | 160.8333 | 304.6376 | 483.6427 | 1
279 | 11 | 69 | 223 |  | -0.10512 | 3.4084 | 12.6796 | 19.3996 | 11.3233 | -0.17715 | 30.6665 | 59.5305 | 185.8333 | 245.3639 | 389.5397 | 1
279 | 12 | 47 | 253 |  | -0.10512 | 3.4084 | 12.6796 | 19.3996 | 12.3233 | 0.084647 | 31.1525 | 41.0703 | 210.8333 | 251.9037 | 399.9223 | 1
279 | 13 | 46 | 245 |  | -0.10512 | 3.4084 | 12.6796 | 19.3996 | 13.3233 | 0.34645 | 28.9243 | 37.8398 | 204.1667 | 242.0065 | 384.2095 | 1
279 | 14 | 45 | 212 |  | -0.10512 | 3.4084 | 12.6796 | 19.3996 | 14.3233 | 0.60825 | 24.2893 | 32.065 | 176.6667 | 208.7317 | 331.3824 | 1
279 | 15 | 41 | 158 |  | -0.10512 | 3.4084 | 12.6796 | 19.3996 | 15.3233 | 0.87004 | 17.7771 | 22.5988 | 131.6667 | 154.2655 | 244.9119 | 1
279 | 16 | 7 | 99 |  | -0.10512 | 3.4084 | 12.6796 | 19.3996 | 16.3233 | 1.1318 | 9.9502 | 2.4465 | 82.5 | 84.9465 | 134.8611 | 0
279 | 17 | 12 | 42 |  | -0.10512 | 3.4084 | 12.6796 | 19.3996 | 17.3233 | 1.3936 | 1.3069 | 1.4549 | 35 | 36.4549 | 57.8759 | 0
279 | 18 | 0 | 2 |  | -0.10512 | 3.4084 | 12.6796 | 19.3996 | 18.3233 | 1.6554 | -7.7249 | 0 | 1.6667 | 1.6667 | 2.646 | 0
279 | 19 | 0 | 0 |  | -0.10512 | 3.4084 | 12.6796 | 19.3996 | 19.3233 | 1.9172 | -16.7484 | 0 | 0 | 0 | 0 | 0
279 | 20 | 0 | 0 |  | -0.10512 | 3.4084 | 12.6796 | 19.3996 | 20.3233 | 2.179 | -25.3387 | 0 | 0 | 0 | 0 | 0
279 | 21 | 0 | 0 |  | -0.10512 | 3.4084 | 12.6796 | 19.3996 | 21.3233 | 2.4408 | -32.9761 | 0 | 0 | 0 | 0 | 0
279 | 22 | 0 | 0 |  | -0.10512 | 3.4084 | 12.6796 | 19.3996 | 22.3233 | 2.7026 | -38.9914 | 0 | 0 | 0 | 0 | 0
279 | 23 | 0 | 0 |  | -0.10512 | 3.4084 | 12.6796 | 19.3996 | 23.3233 | 2.9644 | -42.6039 | 0 | 0 | 0 | 0 | 0
279 | 24 | 0 | 0 |  | -0.10512 | 3.4084 | 12.6796 | 19.3996 | 24.3233 | 3.2262 | -43.173 | 0 | 0 | 0 | 0 | 0
280 | 1 | 0 | 0 |  | -0.11175 | 3.4256 | 12.9588 | 19.6788 | 1.328 | -2.7939 | -40.9291 | 0 | 0 | 0 | 0 | 0
280 | 2 | 0 | 0 |  | -0.11175 | 3.4256 | 12.9588 | 19.6788 | 2.328 | -2.5321 | -35.6404 | 0 | 0 | 0 | 0 | 0
280 | 3 | 0 | 0 |  | -0.11175 | 3.4256 | 12.9588 | 19.6788 | 3.328 | -2.2703 | -28.4637 | 0 | 0 | 0 | 0 | 0
280 | 4 | 0 | 0 |  | -0.11175 | 3.4256 | 12.9588 | 19.6788 | 4.328 | -2.0085 | -20.1251 | 0 | 0 | 0 | 0 | 0
280 | 5 | 0 | 0 |  | -0.11175 | 3.4256 | 12.9588 | 19.6788 | 5.328 | -1.7467 | -11.1943 | 0 | 0 | 0 | 0 | 0
280 | 6 | 0 | 0 |  | -0.11175 | 3.4256 | 12.9588 | 19.6788 | 6.328 | -1.4849 | -2.1214 | 0 | 0 | 0 | 0 | 0
280 | 7 | 0 | 12 |  | -0.11175 | 3.4256 | 12.9588 | 19.6788 | 7.328 | -1.2231 | 6.6949 | 0 | 10 | 10 | 15.876 | 0
280 | 8 | 0 | 70 |  | -0.11175 | 3.4256 | 12.9588 | 19.6788 | 8.328 | -0.96133 | 14.8443 | 0 | 58.3333 | 58.3333 | 92.61 | 1
280 | 9 | 0 | 91 |  | -0.11175 | 3.4256 | 12.9588 | 19.6788 | 9.328 | -0.69953 | 21.8576 | 0 | 75.8333 | 75.8333 | 120.393 | 1
280 | 10 | 66 | 182 |  | -0.11175 | 3.4256 | 12.9588 | 19.6788 | 10.328 | -0.43773 | 27.1933 | 51.9728 | 151.6667 | 203.6394 | 323.298 | 1
280 | 11 | 1 | 160 |  | -0.11175 | 3.4256 | 12.9588 | 19.6788 | 11.328 | -0.17593 | 30.2981 | 0.85976 | 133.3333 | 134.1931 | 213.045 | 1
280 | 12 | 3 | 170 |  | -0.11175 | 3.4256 | 12.9588 | 19.6788 | 12.328 | 0.085865 | 30.7691 | 2.6116 | 141.6667 | 144.2783 | 229.0562 | 1
280 | 13 | 1 | 166 |  | -0.11175 | 3.4256 | 12.9588 | 19.6788 | 13.328 | 0.34766 | 28.5387 | 0.81906 | 138.3333 | 139.1524 | 220.9183 | 1
280 | 14 | 0 | 143 |  | -0.11175 | 3.4256 | 12.9588 | 19.6788 | 14.328 | 0.60946 | 23.9115 | 0 | 119.1667 | 119.1667 | 189.189 | 1
280 | 15 | 0 | 106 |  | -0.11175 | 3.4256 | 12.9588 | 19.6788 | 15.328 | 0.87126 | 17.4114 | 0 | 88.3333 | 88.3333 | 140.238 | 1
280 | 16 | 0 | 60 |  | -0.11175 | 3.4256 | 12.9588 | 19.6788 | 16.328 | 1.1331 | 9.596 | 0 | 50 | 50 | 79.38 | 0
280 | 17 | 0 | 16 |  | -0.11175 | 3.4256 | 12.9588 | 19.6788 | 17.328 | 1.3949 | 0.96069 | 0 | 13.3333 | 13.3333 | 21.168 | 0
280 | 18 | 0 | 0 |  | -0.11175 | 3.4256 | 12.9588 | 19.6788 | 18.328 | 1.6567 | -8.0683 | 0 | 0 | 0 | 0 | 0
280 | 19 | 0 | 0 |  | -0.11175 | 3.4256 | 12.9588 | 19.6788 | 19.328 | 1.9185 | -17.0948 | 0 | 0 | 0 | 0 | 0
280 | 20 | 0 | 0 |  | -0.11175 | 3.4256 | 12.9588 | 19.6788 | 20.328 | 2.1803 | -25.694 | 0 | 0 | 0 | 0 | 0
280 | 21 | 0 | 0 |  | -0.11175 | 3.4256 | 12.9588 | 19.6788 | 21.328 | 2.4421 | -33.3445 | 0 | 0 | 0 | 0 | 0
280 | 22 | 0 | 0 |  | -0.11175 | 3.4256 | 12.9588 | 19.6788 | 22.328 | 2.7039 | -39.3729 | 0 | 0 | 0 | 0 | 0
280 | 23 | 0 | 0 |  | -0.11175 | 3.4256 | 12.9588 | 19.6788 | 23.328 | 2.9657 | -42.9899 | 0 | 0 | 0 | 0 | 0
280 | 24 | 0 | 0 |  | -0.11175 | 3.4256 | 12.9588 | 19.6788 | 24.328 | 3.2275 | -43.5471 | 0 | 0 | 0 | 0 | 0
281 | 1 | 0 | 0 |  | -0.11835 | 3.4428 | 13.2293 | 19.9493 | 1.3325 | -2.7927 | -41.2744 | 0 | 0 | 0 | 0 | 0
281 | 2 | 0 | 0 |  | -0.11835 | 3.4428 | 13.2293 | 19.9493 | 2.3325 | -2.5309 | -35.9535 | 0 | 0 | 0 | 0 | 0
281 | 3 | 0 | 0 |  | -0.11835 | 3.4428 | 13.2293 | 19.9493 | 3.3325 | -2.2691 | -28.7493 | 0 | 0 | 0 | 0 | 0
281 | 4 | 0 | 0 |  | -0.11835 | 3.4428 | 13.2293 | 19.9493 | 4.3325 | -2.0073 | -20.3925 | 0 | 0 | 0 | 0 | 0
281 | 5 | 0 | 0 |  | -0.11835 | 3.4428 | 13.2293 | 19.9493 | 5.3325 | -1.7456 | -11.4535 | 0 | 0 | 0 | 0 | 0
281 | 6 | 0 | 0 |  | -0.11835 | 3.4428 | 13.2293 | 19.9493 | 6.3325 | -1.4838 | -2.3822 | 0 | 0 | 0 | 0 | 0
281 | 7 | 0 | 11 |  | -0.11835 | 3.4428 | 13.2293 | 19.9493 | 7.3325 | -1.222 | 6.4236 | 0 | 9.1667 | 9.1667 | 14.553 | 0
281 | 8 | 0 | 68 |  | -0.11835 | 3.4428 | 13.2293 | 19.9493 | 8.3325 | -0.96015 | 14.5542 | 0 | 56.6667 | 56.6667 | 89.964 | 1
281 | 9 | 22 | 136 |  | -0.11835 | 3.4428 | 13.2293 | 19.9493 | 9.3325 | -0.69835 | 21.5425 | 14.4365 | 113.3333 | 127.7698 | 202.8474 | 1
281 | 10 | 49 | 188 |  | -0.11835 | 3.4428 | 13.2293 | 19.9493 | 10.3325 | -0.43655 | 26.8504 | 38.4533 | 156.6667 | 195.12 | 309.7725 | 1
281 | 11 | 46 | 231 |  | -0.11835 | 3.4428 | 13.2293 | 19.9493 | 11.3325 | -0.17475 | 29.9308 | 39.4098 | 192.5 | 231.9098 | 368.18 | 1
281 | 12 | 49 | 248 |  | -0.11835 | 3.4428 | 13.2293 | 19.9493 | 12.3325 | 0.087045 | 30.3874 | 42.4938 | 206.6667 | 249.1605 | 395.5672 | 1
281 | 13 | 5 | 163 |  | -0.11835 | 3.4428 | 13.2293 | 19.9493 | 13.3325 | 0.34884 | 28.1552 | 4.0775 | 135.8333 | 139.9109 | 222.1225 | 1
281 | 14 | 0 | 143 |  | -0.11835 | 3.4428 | 13.2293 | 19.9493 | 14.3325 | 0.61064 | 23.536 | 0 | 119.1667 | 119.1667 | 189.189 | 1
281 | 15 | 0 | 106 |  | -0.11835 | 3.4428 | 13.2293 | 19.9493 | 15.3325 | 0.87244 | 17.0481 | 0 | 88.3333 | 88.3333 | 140.238 | 1
281 | 16 | 11 | 92 |  | -0.11835 | 3.4428 | 13.2293 | 19.9493 | 16.3325 | 1.1342 | 9.2444 | 3.7605 | 76.6667 | 80.4272 | 127.6862 | 0
281 | 17 | 0 | 15 |  | -0.11835 | 3.4428 | 13.2293 | 19.9493 | 17.3325 | 1.396 | 0.61708 | 0 | 12.5 | 12.5 | 19.845 | 0
281 | 18 | 0 | 1 |  | -0.11835 | 3.4428 | 13.2293 | 19.9493 | 18.3325 | 1.6578 | -8.409 | 0 | 0.83333 | 0.83333 | 1.323 | 0
281 | 19 | 0 | 0 |  | -0.11835 | 3.4428 | 13.2293 | 19.9493 | 19.3325 | 1.9196 | -17.4385 | 0 | 0 | 0 | 0 | 0
281 | 20 | 0 | 0 |  | -0.11835 | 3.4428 | 13.2293 | 19.9493 | 20.3325 | 2.1814 | -26.0465 | 0 | 0 | 0 | 0 | 0
281 | 21 | 0 | 0 |  | -0.11835 | 3.4428 | 13.2293 | 19.9493 | 21.3325 | 2.4432 | -33.7103 | 0 | 0 | 0 | 0 | 0
281 | 22 | 0 | 0 |  | -0.11835 | 3.4428 | 13.2293 | 19.9493 | 22.3325 | 2.705 | -39.752 | 0 | 0 | 0 | 0 | 0
281 | 23 | 0 | 0 |  | -0.11835 | 3.4428 | 13.2293 | 19.9493 | 23.3325 | 2.9668 | -43.374 | 0 | 0 | 0 | 0 | 0
281 | 24 | 0 | 0 |  | -0.11835 | 3.4428 | 13.2293 | 19.9493 | 24.3325 | 3.2286 | -43.9195 | 0 | 0 | 0 | 0 | 0
282 | 1 | 0 | 0 |  | -0.12493 | 3.4601 | 13.491 | 20.211 | 1.3368 | -2.7916 | -41.6183 | 0 | 0 | 0 | 0 | 0
282 | 2 | 0 | 0 |  | -0.12493 | 3.4601 | 13.491 | 20.211 | 2.3368 | -2.5298 | -36.2654 | 0 | 0 | 0 | 0 | 0
282 | 3 | 0 | 0 |  | -0.12493 | 3.4601 | 13.491 | 20.211 | 3.3368 | -2.268 | -29.034 | 0 | 0 | 0 | 0 | 0
282 | 4 | 0 | 0 |  | -0.12493 | 3.4601 | 13.491 | 20.211 | 4.3368 | -2.0062 | -20.6593 | 0 | 0 | 0 | 0 | 0
282 | 5 | 0 | 0 |  | -0.12493 | 3.4601 | 13.491 | 20.211 | 5.3368 | -1.7444 | -11.7125 | 0 | 0 | 0 | 0 | 0
282 | 6 | 0 | 0 |  | -0.12493 | 3.4601 | 13.491 | 20.211 | 6.3368 | -1.4826 | -2.6429 | 0 | 0 | 0 | 0 | 0
282 | 7 | 0 | 10 |  | -0.12493 | 3.4601 | 13.491 | 20.211 | 7.3368 | -1.2208 | 6.1522 | 0 | 8.3333 | 8.3333 | 13.23 | 0
282 | 8 | 0 | 65 |  | -0.12493 | 3.4601 | 13.491 | 20.211 | 8.3368 | -0.95901 | 14.2642 | 0 | 54.1667 | 54.1667 | 85.995 | 1
282 | 9 | 145 | 132 |  | -0.12493 | 3.4601 | 13.491 | 20.211 | 9.3368 | -0.69721 | 21.2276 | 94.8007 | 110 | 204.8007 | 325.1415 | 1
282 | 10 | 136 | 205 |  | -0.12493 | 3.4601 | 13.491 | 20.211 | 10.3368 | -0.43541 | 26.5082 | 106.3548 | 170.8333 | 277.1881 | 440.0639 | 1
282 | 11 | 125 | 258 |  | -0.12493 | 3.4601 | 13.491 | 20.211 | 11.3368 | -0.17361 | 29.5649 | 106.7095 | 215 | 321.7095 | 510.746 | 1
282 | 12 | 72 | 230 |  | -0.12493 | 3.4601 | 13.491 | 20.211 | 12.3368 | 0.088187 | 30.0075 | 62.1994 | 191.6667 | 253.8661 | 403.0378 | 1
282 | 13 | 45 | 235 |  | -0.12493 | 3.4601 | 13.491 | 20.211 | 13.3368 | 0.34999 | 27.7739 | 36.5373 | 195.8333 | 232.3706 | 368.9116 | 1
282 | 14 | 0 | 139 |  | -0.12493 | 3.4601 | 13.491 | 20.211 | 14.3368 | 0.61179 | 23.1629 | 0 | 115.8333 | 115.8333 | 183.897 | 1
282 | 15 | 0 | 102 |  | -0.12493 | 3.4601 | 13.491 | 20.211 | 15.3368 | 0.87359 | 16.6873 | 0 | 85 | 85 | 134.946 | 1
282 | 16 | 9 | 88 |  | -0.12493 | 3.4601 | 13.491 | 20.211 | 16.3368 | 1.1354 | 8.8954 | 3.0428 | 73.3333 | 76.3762 | 121.2548 | 0
282 | 17 | 0 | 14 |  | -0.12493 | 3.4601 | 13.491 | 20.211 | 17.3368 | 1.3972 | 0.27623 | 0 | 11.6667 | 11.6667 | 18.522 | 0
282 | 18 | 0 | 0 |  | -0.12493 | 3.4601 | 13.491 | 20.211 | 18.3368 | 1.659 | -8.7469 | 0 | 0 | 0 | 0 | 0
282 | 19 | 0 | 0 |  | -0.12493 | 3.4601 | 13.491 | 20.211 | 19.3368 | 1.9208 | -17.7792 | 0 | 0 | 0 | 0 | 0
282 | 20 | 0 | 0 |  | -0.12493 | 3.4601 | 13.491 | 20.211 | 20.3368 | 2.1826 | -26.3961 | 0 | 0 | 0 | 0 | 0
282 | 21 | 0 | 0 |  | -0.12493 | 3.4601 | 13.491 | 20.211 | 21.3368 | 2.4444 | -34.0733 | 0 | 0 | 0 | 0 | 0
282 | 22 | 0 | 0 |  | -0.12493 | 3.4601 | 13.491 | 20.211 | 22.3368 | 2.7062 | -40.1286 | 0 | 0 | 0 | 0 | 0
282 | 23 | 0 | 0 |  | -0.12493 | 3.4601 | 13.491 | 20.211 | 23.3368 | 2.968 | -43.756 | 0 | 0 | 0 | 0 | 0
282 | 24 | 0 | 0 |  | -0.12493 | 3.4601 | 13.491 | 20.211 | 24.3368 | 3.2298 | -44.2903 | 0 | 0 | 0 | 0 | 0
283 | 1 | 0 | 0 |  | -0.13147 | 3.4773 | 13.7434 | 20.4634 | 1.3411 | -2.7905 | -41.9606 | 0 | 0 | 0 | 0 | 0
283 | 2 | 0 | 0 |  | -0.13147 | 3.4773 | 13.7434 | 20.4634 | 2.3411 | -2.5287 | -36.5761 | 0 | 0 | 0 | 0 | 0
283 | 3 | 0 | 0 |  | -0.13147 | 3.4773 | 13.7434 | 20.4634 | 3.3411 | -2.2669 | -29.3179 | 0 | 0 | 0 | 0 | 0
283 | 4 | 0 | 0 |  | -0.13147 | 3.4773 | 13.7434 | 20.4634 | 4.3411 | -2.0051 | -20.9256 | 0 | 0 | 0 | 0 | 0
283 | 5 | 0 | 0 |  | -0.13147 | 3.4773 | 13.7434 | 20.4634 | 5.3411 | -1.7433 | -11.9712 | 0 | 0 | 0 | 0 | 0
283 | 6 | 0 | 0 |  | -0.13147 | 3.4773 | 13.7434 | 20.4634 | 6.3411 | -1.4815 | -2.9035 | 0 | 0 | 0 | 0 | 0
283 | 7 | 0 | 6 |  | -0.13147 | 3.4773 | 13.7434 | 20.4634 | 7.3411 | -1.2197 | 5.8808 | 0 | 5 | 5 | 7.938 | 0
283 | 8 | 0 | 39 |  | -0.13147 | 3.4773 | 13.7434 | 20.4634 | 8.3411 | -0.95791 | 13.9742 | 0 | 32.5 | 32.5 | 51.597 | 1
283 | 9 | 0 | 85 |  | -0.13147 | 3.4773 | 13.7434 | 20.4634 | 9.3411 | -0.69611 | 20.913 | 0 | 70.8333 | 70.8333 | 112.455 | 1
283 | 10 | 172 | 185 |  | -0.13147 | 3.4773 | 13.7434 | 20.4634 | 10.3411 | -0.43431 | 26.1668 | 134.03 | 154.1667 | 288.1967 | 457.541 | 1
283 | 11 | 130 | 251 |  | -0.13147 | 3.4773 | 13.7434 | 20.4634 | 11.3411 | -0.17251 | 29.2003 | 110.5765 | 209.1667 | 319.7432 | 507.6242 | 1
283 | 12 | 74 | 226 |  | -0.13147 | 3.4773 | 13.7434 | 20.4634 | 12.3411 | 0.089289 | 29.6296 | 63.6786 | 188.3333 | 252.0119 | 400.0942 | 1
283 | 13 | 47 | 230 |  | -0.13147 | 3.4773 | 13.7434 | 20.4634 | 13.3411 | 0.35109 | 27.395 | 37.9933 | 191.6667 | 229.6599 | 364.6081 | 1
283 | 14 | 0 | 136 |  | -0.13147 | 3.4773 | 13.7434 | 20.4634 | 14.3411 | 0.61289 | 22.7923 | 0 | 113.3333 | 113.3333 | 179.928 | 1
283 | 15 | 0 | 100 |  | -0.13147 | 3.4773 | 13.7434 | 20.4634 | 15.3411 | 0.87469 | 16.3292 | 0 | 83.3333 | 83.3333 | 132.3 | 1
283 | 16 | 0 | 55 |  | -0.13147 | 3.4773 | 13.7434 | 20.4634 | 16.3411 | 1.1365 | 8.5491 | 0 | 45.8333 | 45.8333 | 72.765 | 0
283 | 17 | 0 | 12 |  | -0.13147 | 3.4773 | 13.7434 | 20.4634 | 17.3411 | 1.3983 | -0.061743 | 0 | 10 | 10 | 15.876 | 0
283 | 18 | 0 | 0 |  | -0.13147 | 3.4773 | 13.7434 | 20.4634 | 18.3411 | 1.6601 | -9.0817 | 0 | 0 | 0 | 0 | 0
283 | 19 | 0 | 0 |  | -0.13147 | 3.4773 | 13.7434 | 20.4634 | 19.3411 | 1.9219 | -18.1169 | 0 | 0 | 0 | 0 | 0
283 | 20 | 0 | 0 |  | -0.13147 | 3.4773 | 13.7434 | 20.4634 | 20.3411 | 2.1837 | -26.7426 | 0 | 0 | 0 | 0 | 0
283 | 21 | 0 | 0 |  | -0.13147 | 3.4773 | 13.7434 | 20.4634 | 21.3411 | 2.4455 | -34.4334 | 0 | 0 | 0 | 0 | 0
283 | 22 | 0 | 0 |  | -0.13147 | 3.4773 | 13.7434 | 20.4634 | 22.3411 | 2.7073 | -40.5027 | 0 | 0 | 0 | 0 | 0
283 | 23 | 0 | 0 |  | -0.13147 | 3.4773 | 13.7434 | 20.4634 | 23.3411 | 2.9691 | -44.1359 | 0 | 0 | 0 | 0 | 0
283 | 24 | 0 | 0 |  | -0.13147 | 3.4773 | 13.7434 | 20.4634 | 24.3411 | 3.2309 | -44.6593 | 0 | 0 | 0 | 0 | 0
284 | 1 | 0 | 0 |  | -0.13797 | 3.4945 | 13.9864 | 20.7064 | 1.3451 | -2.7894 | -42.3014 | 0 | 0 | 0 | 0 | 0
284 | 2 | 0 | 0 |  | -0.13797 | 3.4945 | 13.9864 | 20.7064 | 2.3451 | -2.5276 | -36.8855 | 0 | 0 | 0 | 0 | 0
284 | 3 | 0 | 0 |  | -0.13797 | 3.4945 | 13.9864 | 20.7064 | 3.3451 | -2.2658 | -29.6008 | 0 | 0 | 0 | 0 | 0
284 | 4 | 0 | 0 |  | -0.13797 | 3.4945 | 13.9864 | 20.7064 | 4.3451 | -2.004 | -21.1913 | 0 | 0 | 0 | 0 | 0
284 | 5 | 0 | 0 |  | -0.13797 | 3.4945 | 13.9864 | 20.7064 | 5.3451 | -1.7422 | -12.2296 | 0 | 0 | 0 | 0 | 0
284 | 6 | 0 | 0 |  | -0.13797 | 3.4945 | 13.9864 | 20.7064 | 6.3451 | -1.4804 | -3.1641 | 0 | 0 | 0 | 0 | 0
284 | 7 | 0 | 16 |  | -0.13797 | 3.4945 | 13.9864 | 20.7064 | 7.3451 | -1.2186 | 5.6094 | 0 | 13.3333 | 13.3333 | 21.168 | 0
284 | 8 | 171 | 77 |  | -0.13797 | 3.4945 | 13.9864 | 20.7064 | 8.3451 | -0.95685 | 13.6843 | 80.9629 | 64.1667 | 145.1296 | 230.4077 | 1
284 | 9 | 455 | 96 |  | -0.13797 | 3.4945 | 13.9864 | 20.7064 | 9.3451 | -0.69505 | 20.5989 | 295.2345 | 80 | 375.2345 | 595.7222 | 1
284 | 10 | 593 | 111 |  | -0.13797 | 3.4945 | 13.9864 | 20.7064 | 10.3451 | -0.43325 | 25.8263 | 460.4251 | 92.5 | 552.9251 | 877.8238 | 1
284 | 11 | 702 | 99 |  | -0.13797 | 3.4945 | 13.9864 | 20.7064 | 11.3451 | -0.17145 | 28.8372 | 594.9263 | 82.5 | 677.4263 | 1075.4819 | 1
284 | 12 | 711 | 104 |  | -0.13797 | 3.4945 | 13.9864 | 20.7064 | 12.3451 | 0.090349 | 29.2537 | 609.4302 | 86.6667 | 696.0969 | 1105.1235 | 1
284 | 13 | 643 | 119 |  | -0.13797 | 3.4945 | 13.9864 | 20.7064 | 13.3451 | 0.35215 | 27.0184 | 517.48 | 99.1667 | 616.6467 | 978.9883 | 1
284 | 14 | 66 | 188 |  | -0.13797 | 3.4945 | 13.9864 | 20.7064 | 14.3451 | 0.61395 | 22.4244 | 45.8024 | 156.6667 | 202.4691 | 321.4399 | 1
284 | 15 | 154 | 149 |  | -0.13797 | 3.4945 | 13.9864 | 20.7064 | 15.3451 | 0.87575 | 15.9739 | 81.9671 | 124.1667 | 206.1338 | 327.258 | 1
284 | 16 | 245 | 83 |  | -0.13797 | 3.4945 | 13.9864 | 20.7064 | 16.3451 | 1.1375 | 8.2058 | 81.0083 | 69.1667 | 150.175 | 238.4179 | 0
284 | 17 | 0 | 27 |  | -0.13797 | 3.4945 | 13.9864 | 20.7064 | 17.3451 | 1.3993 | -0.39671 | 0 | 22.5 | 22.5 | 35.721 | 0
284 | 18 | 0 | 0 |  | -0.13797 | 3.4945 | 13.9864 | 20.7064 | 18.3451 | 1.6611 | -9.4135 | 0 | 0 | 0 | 0 | 0
284 | 19 | 0 | 0 |  | -0.13797 | 3.4945 | 13.9864 | 20.7064 | 19.3451 | 1.9229 | -18.4514 | 0 | 0 | 0 | 0 | 0
284 | 20 | 0 | 0 |  | -0.13797 | 3.4945 | 13.9864 | 20.7064 | 20.3451 | 2.1847 | -27.086 | 0 | 0 | 0 | 0 | 0
284 | 21 | 0 | 0 |  | -0.13797 | 3.4945 | 13.9864 | 20.7064 | 21.3451 | 2.4465 | -34.7905 | 0 | 0 | 0 | 0 | 0
284 | 22 | 0 | 0 |  | -0.13797 | 3.4945 | 13.9864 | 20.7064 | 22.3451 | 2.7083 | -40.8741 | 0 | 0 | 0 | 0 | 0
284 | 23 | 0 | 0 |  | -0.13797 | 3.4945 | 13.9864 | 20.7064 | 23.3451 | 2.9701 | -44.5135 | 0 | 0 | 0 | 0 | 0
284 | 24 | 0 | 0 |  | -0.13797 | 3.4945 | 13.9864 | 20.7064 | 24.3451 | 3.2319 | -45.0264 | 0 | 0 | 0 | 0 | 0
285 | 1 | 0 | 0 |  | -0.14445 | 3.5117 | 14.2195 | 20.9395 | 1.349 | -2.7884 | -42.6406 | 0 | 0 | 0 | 0 | 0
285 | 2 | 0 | 0 |  | -0.14445 | 3.5117 | 14.2195 | 20.9395 | 2.349 | -2.5266 | -37.1936 | 0 | 0 | 0 | 0 | 0
285 | 3 | 0 | 0 |  | -0.14445 | 3.5117 | 14.2195 | 20.9395 | 3.349 | -2.2648 | -29.8828 | 0 | 0 | 0 | 0 | 0
285 | 4 | 0 | 0 |  | -0.14445 | 3.5117 | 14.2195 | 20.9395 | 4.349 | -2.003 | -21.4564 | 0 | 0 | 0 | 0 | 0
285 | 5 | 0 | 0 |  | -0.14445 | 3.5117 | 14.2195 | 20.9395 | 5.349 | -1.7412 | -12.4877 | 0 | 0 | 0 | 0 | 0
285 | 6 | 0 | 0 |  | -0.14445 | 3.5117 | 14.2195 | 20.9395 | 6.349 | -1.4794 | -3.4245 | 0 | 0 | 0 | 0 | 0
285 | 7 | 0 | 14 |  | -0.14445 | 3.5117 | 14.2195 | 20.9395 | 7.349 | -1.2176 | 5.3381 | 0 | 11.6667 | 11.6667 | 18.522 | 0
285 | 8 | 170 | 74 |  | -0.14445 | 3.5117 | 14.2195 | 20.9395 | 8.349 | -0.95583 | 13.3947 | 80.1161 | 61.6667 | 141.7828 | 225.0943 | 1
285 | 9 | 457 | 94 |  | -0.14445 | 3.5117 | 14.2195 | 20.9395 | 9.349 | -0.69403 | 20.2853 | 295.3798 | 78.3333 | 373.7131 | 593.3069 | 1
285 | 10 | 65 | 169 |  | -0.14445 | 3.5117 | 14.2195 | 20.9395 | 10.349 | -0.43223 | 25.4868 | 50.2833 | 140.8333 | 191.1167 | 303.4168 | 1
285 | 11 | 195 | 216 |  | -0.14445 | 3.5117 | 14.2195 | 20.9395 | 11.349 | -0.17043 | 28.4758 | 164.6448 | 180 | 344.6448 | 547.1582 | 1
285 | 12 | 131 | 267 |  | -0.14445 | 3.5117 | 14.2195 | 20.9395 | 12.349 | 0.091366 | 28.88 | 111.8417 | 222.5 | 334.3417 | 530.8009 | 1
285 | 13 | 71 | 214 |  | -0.14445 | 3.5117 | 14.2195 | 20.9395 | 13.349 | 0.35317 | 26.6444 | 56.8859 | 178.3333 | 235.2192 | 373.4341 | 1
285 | 14 | 389 | 178 |  | -0.14445 | 3.5117 | 14.2195 | 20.9395 | 14.349 | 0.61496 | 22.0592 | 268.52 | 148.3333 | 416.8533 | 661.7964 | 1
285 | 15 | 524 | 94 |  | -0.14445 | 3.5117 | 14.2195 | 20.9395 | 15.349 | 0.87676 | 15.6215 | 276.9507 | 78.3333 | 355.284 | 564.0489 | 1
285 | 16 | 327 | 73 |  | -0.14445 | 3.5117 | 14.2195 | 20.9395 | 16.349 | 1.1386 | 7.8654 | 106.9224 | 60.8333 | 167.7557 | 266.329 | 0
285 | 17 | 29 | 27 |  | -0.14445 | 3.5117 | 14.2195 | 20.9395 | 17.349 | 1.4004 | -0.72853 | 2.8815 | 22.5 | 25.3815 | 40.2957 | 0
285 | 18 | 0 | 0 |  | -0.14445 | 3.5117 | 14.2195 | 20.9395 | 18.349 | 1.6622 | -9.742 | 0 | 0 | 0 | 0 | 0
285 | 19 | 0 | 0 |  | -0.14445 | 3.5117 | 14.2195 | 20.9395 | 19.349 | 1.924 | -18.7826 | 0 | 0 | 0 | 0 | 0
285 | 20 | 0 | 0 |  | -0.14445 | 3.5117 | 14.2195 | 20.9395 | 20.349 | 2.1858 | -27.426 | 0 | 0 | 0 | 0 | 0
285 | 21 | 0 | 0 |  | -0.14445 | 3.5117 | 14.2195 | 20.9395 | 21.349 | 2.4476 | -35.1445 | 0 | 0 | 0 | 0 | 0
285 | 22 | 0 | 0 |  | -0.14445 | 3.5117 | 14.2195 | 20.9395 | 22.349 | 2.7094 | -41.2426 | 0 | 0 | 0 | 0 | 0
285 | 23 | 0 | 0 |  | -0.14445 | 3.5117 | 14.2195 | 20.9395 | 23.349 | 2.9712 | -44.8888 | 0 | 0 | 0 | 0 | 0
285 | 24 | 0 | 0 |  | -0.14445 | 3.5117 | 14.2195 | 20.9395 | 24.349 | 3.233 | -45.3916 | 0 | 0 | 0 | 0 | 0
286 | 1 | 0 | 0 |  | -0.15088 | 3.5289 | 14.4424 | 21.1624 | 1.3527 | -2.7875 | -42.9781 | 0 | 0 | 0 | 0 | 0
286 | 2 | 0 | 0 |  | -0.15088 | 3.5289 | 14.4424 | 21.1624 | 2.3527 | -2.5257 | -37.5004 | 0 | 0 | 0 | 0 | 0
286 | 3 | 0 | 0 |  | -0.15088 | 3.5289 | 14.4424 | 21.1624 | 3.3527 | -2.2639 | -30.1638 | 0 | 0 | 0 | 0 | 0
286 | 4 | 0 | 0 |  | -0.15088 | 3.5289 | 14.4424 | 21.1624 | 4.3527 | -2.0021 | -21.7208 | 0 | 0 | 0 | 0 | 0
286 | 5 | 0 | 0 |  | -0.15088 | 3.5289 | 14.4424 | 21.1624 | 5.3527 | -1.7403 | -12.7455 | 0 | 0 | 0 | 0 | 0
286 | 6 | 0 | 0 |  | -0.15088 | 3.5289 | 14.4424 | 21.1624 | 6.3527 | -1.4785 | -3.6848 | 0 | 0 | 0 | 0 | 0
286 | 7 | 0 | 5 |  | -0.15088 | 3.5289 | 14.4424 | 21.1624 | 7.3527 | -1.2167 | 5.0669 | 0 | 4.1667 | 4.1667 | 6.615 | 0
286 | 8 | 0 | 56 |  | -0.15088 | 3.5289 | 14.4424 | 21.1624 | 8.3527 | -0.95486 | 13.1053 | 0 | 46.6667 | 46.6667 | 74.088 | 1
286 | 9 | 138 | 123 |  | -0.15088 | 3.5289 | 14.4424 | 21.1624 | 9.3527 | -0.69306 | 19.9722 | 88.8426 | 102.5 | 191.3426 | 303.7755 | 1
286 | 10 | 368 | 166 |  | -0.15088 | 3.5289 | 14.4424 | 21.1624 | 10.3527 | -0.43126 | 25.1484 | 283.6225 | 138.3333 | 421.9559 | 669.8972 | 1
286 | 11 | 358 | 184 |  | -0.15088 | 3.5289 | 14.4424 | 21.1624 | 11.3527 | -0.16946 | 28.116 | 301.138 | 153.3333 | 454.4713 | 721.5187 | 1
286 | 12 | 335 | 213 |  | -0.15088 | 3.5289 | 14.4424 | 21.1624 | 12.3527 | 0.092339 | 28.5086 | 284.8665 | 177.5 | 462.3665 | 734.0531 | 1
286 | 13 | 196 | 220 |  | -0.15088 | 3.5289 | 14.4424 | 21.1624 | 13.3527 | 0.35414 | 26.2731 | 156.3352 | 183.3333 | 339.6685 | 539.2578 | 1
286 | 14 | 117 | 218 |  | -0.15088 | 3.5289 | 14.4424 | 21.1624 | 14.3527 | 0.61594 | 21.697 | 80.3325 | 181.6667 | 261.9992 | 415.9499 | 1
286 | 15 | 381 | 117 |  | -0.15088 | 3.5289 | 14.4424 | 21.1624 | 15.3527 | 0.87774 | 15.2722 | 199.9627 | 97.5 | 297.4627 | 472.2517 | 1
286 | 16 | 260 | 83 |  | -0.15088 | 3.5289 | 14.4424 | 21.1624 | 16.3527 | 1.1395 | 7.5283 | 84.072 | 69.1667 | 153.2386 | 243.2816 | 0
286 | 17 | 15 | 26 |  | -0.15088 | 3.5289 | 14.4424 | 21.1624 | 17.3527 | 1.4013 | -1.0571 | 1.4383 | 21.6667 | 23.1049 | 36.6814 | 0
286 | 18 | 0 | 0 |  | -0.15088 | 3.5289 | 14.4424 | 21.1624 | 18.3527 | 1.6631 | -10.0671 | 0 | 0 | 0 | 0 | 0
286 | 19 | 0 | 0 |  | -0.15088 | 3.5289 | 14.4424 | 21.1624 | 19.3527 | 1.9249 | -19.1103 | 0 | 0 | 0 | 0 | 0
286 | 20 | 0 | 0 |  | -0.15088 | 3.5289 | 14.4424 | 21.1624 | 20.3527 | 2.1867 | -27.7626 | 0 | 0 | 0 | 0 | 0
286 | 21 | 0 | 0 |  | -0.15088 | 3.5289 | 14.4424 | 21.1624 | 21.3527 | 2.4485 | -35.4951 | 0 | 0 | 0 | 0 | 0
286 | 22 | 0 | 0 |  | -0.15088 | 3.5289 | 14.4424 | 21.1624 | 22.3527 | 2.7103 | -41.6082 | 0 | 0 | 0 | 0 | 0
286 | 23 | 0 | 0 |  | -0.15088 | 3.5289 | 14.4424 | 21.1624 | 23.3527 | 2.9721 | -45.2615 | 0 | 0 | 0 | 0 | 0
286 | 24 | 0 | 0 |  | -0.15088 | 3.5289 | 14.4424 | 21.1624 | 24.3527 | 3.2339 | -45.7547 | 0 | 0 | 0 | 0 | 0
287 | 1 | 0 | 0 |  | -0.15728 | 3.5461 | 14.655 | 21.375 | 1.3562 | -2.7865 | -43.3138 | 0 | 0 | 0 | 0 | 0
287 | 2 | 0 | 0 |  | -0.15728 | 3.5461 | 14.655 | 21.375 | 2.3562 | -2.5247 | -37.8057 | 0 | 0 | 0 | 0 | 0
287 | 3 | 0 | 0 |  | -0.15728 | 3.5461 | 14.655 | 21.375 | 3.3562 | -2.2629 | -30.4438 | 0 | 0 | 0 | 0 | 0
287 | 4 | 0 | 0 |  | -0.15728 | 3.5461 | 14.655 | 21.375 | 4.3562 | -2.0011 | -21.9846 | 0 | 0 | 0 | 0 | 0
287 | 5 | 0 | 0 |  | -0.15728 | 3.5461 | 14.655 | 21.375 | 5.3562 | -1.7393 | -13.0028 | 0 | 0 | 0 | 0 | 0
287 | 6 | 0 | 0 |  | -0.15728 | 3.5461 | 14.655 | 21.375 | 6.3562 | -1.4775 | -3.9448 | 0 | 0 | 0 | 0 | 0
287 | 7 | 0 | 12 |  | -0.15728 | 3.5461 | 14.655 | 21.375 | 7.3562 | -1.2157 | 4.7959 | 0 | 10 | 10 | 15.876 | 0
287 | 8 | 154 | 71 |  | -0.15728 | 3.5461 | 14.655 | 21.375 | 8.3562 | -0.95393 | 12.8162 | 71.8821 | 59.1667 | 131.0488 | 208.053 | 1
287 | 9 | 452 | 91 |  | -0.15728 | 3.5461 | 14.655 | 21.375 | 9.3562 | -0.69213 | 19.6598 | 289.8191 | 75.8333 | 365.6524 | 580.5098 | 1
287 | 10 | 575 | 110 |  | -0.15728 | 3.5461 | 14.655 | 21.375 | 10.3562 | -0.43033 | 24.8112 | 441.4888 | 91.6667 | 533.1554 | 846.4376 | 1
287 | 11 | 691 | 97 |  | -0.15728 | 3.5461 | 14.655 | 21.375 | 11.3562 | -0.16853 | 27.758 | 579.0441 | 80.8333 | 659.8775 | 1047.6215 | 1
287 | 12 | 703 | 101 |  | -0.15728 | 3.5461 | 14.655 | 21.375 | 12.3562 | 0.093266 | 28.1395 | 595.3922 | 84.1667 | 679.5589 | 1078.8677 | 1
287 | 13 | 218 | 208 |  | -0.15728 | 3.5461 | 14.655 | 21.375 | 13.3562 | 0.35507 | 25.9045 | 173.1026 | 173.3333 | 346.4359 | 550.0017 | 1
287 | 14 | 64 | 179 |  | -0.15728 | 3.5461 | 14.655 | 21.375 | 14.3562 | 0.61686 | 21.3377 | 43.708 | 149.1667 | 192.8747 | 306.2079 | 1
287 | 15 | 17 | 141 |  | -0.15728 | 3.5461 | 14.655 | 21.375 | 15.3562 | 0.87866 | 14.926 | 8.8599 | 117.5 | 126.3599 | 200.609 | 1
287 | 16 | 3 | 75 |  | -0.15728 | 3.5461 | 14.655 | 21.375 | 16.3562 | 1.1405 | 7.1944 | 0.95931 | 62.5 | 63.4593 | 100.748 | 0
287 | 17 | 0 | 9 |  | -0.15728 | 3.5461 | 14.655 | 21.375 | 17.3562 | 1.4023 | -1.3823 | 0 | 7.5 | 7.5 | 11.907 | 0
287 | 18 | 0 | 0 |  | -0.15728 | 3.5461 | 14.655 | 21.375 | 18.3562 | 1.6641 | -10.3887 | 0 | 0 | 0 | 0 | 0
287 | 19 | 0 | 0 |  | -0.15728 | 3.5461 | 14.655 | 21.375 | 19.3562 | 1.9259 | -19.4345 | 0 | 0 | 0 | 0 | 0
287 | 20 | 0 | 0 |  | -0.15728 | 3.5461 | 14.655 | 21.375 | 20.3562 | 2.1877 | -28.0957 | 0 | 0 | 0 | 0 | 0
287 | 21 | 0 | 0 |  | -0.15728 | 3.5461 | 14.655 | 21.375 | 21.3562 | 2.4495 | -35.8423 | 0 | 0 | 0 | 0 | 0
287 | 22 | 0 | 0 |  | -0.15728 | 3.5461 | 14.655 | 21.375 | 22.3562 | 2.7113 | -41.9708 | 0 | 0 | 0 | 0 | 0
287 | 23 | 0 | 0 |  | -0.15728 | 3.5461 | 14.655 | 21.375 | 23.3562 | 2.9731 | -45.6318 | 0 | 0 | 0 | 0 | 0
287 | 24 | 0 | 0 |  | -0.15728 | 3.5461 | 14.655 | 21.375 | 24.3562 | 3.2349 | -46.1158 | 0 | 0 | 0 | 0 | 0
288 | 1 | 0 | 0 |  | -0.16363 | 3.5633 | 14.8568 | 21.5768 | 1.3596 | -2.7856 | -43.6478 | 0 | 0 | 0 | 0 | 0
288 | 2 | 0 | 0 |  | -0.16363 | 3.5633 | 14.8568 | 21.5768 | 2.3596 | -2.5238 | -38.1096 | 0 | 0 | 0 | 0 | 0
288 | 3 | 0 | 0 |  | -0.16363 | 3.5633 | 14.8568 | 21.5768 | 3.3596 | -2.262 | -30.7227 | 0 | 0 | 0 | 0 | 0
288 | 4 | 0 | 0 |  | -0.16363 | 3.5633 | 14.8568 | 21.5768 | 4.3596 | -2.0002 | -22.2477 | 0 | 0 | 0 | 0 | 0
288 | 5 | 0 | 0 |  | -0.16363 | 3.5633 | 14.8568 | 21.5768 | 5.3596 | -1.7384 | -13.2597 | 0 | 0 | 0 | 0 | 0
288 | 6 | 0 | 0 |  | -0.16363 | 3.5633 | 14.8568 | 21.5768 | 6.3596 | -1.4766 | -4.2046 | 0 | 0 | 0 | 0 | 0
288 | 7 | 0 | 8 |  | -0.16363 | 3.5633 | 14.8568 | 21.5768 | 7.3596 | -1.2149 | 4.5252 | 0 | 6.6667 | 6.6667 | 10.584 | 0
288 | 8 | 0 | 52 |  | -0.16363 | 3.5633 | 14.8568 | 21.5768 | 8.3596 | -0.95305 | 12.5275 | 0 | 43.3333 | 43.3333 | 68.796 | 1
288 | 9 | 18 | 118 |  | -0.16363 | 3.5633 | 14.8568 | 21.5768 | 9.3596 | -0.69125 | 19.3481 | 11.4941 | 98.3333 | 109.8275 | 174.3621 | 1
288 | 10 | 25 | 177 |  | -0.16363 | 3.5633 | 14.8568 | 21.5768 | 10.3596 | -0.42945 | 24.4753 | 19.1218 | 147.5 | 166.6218 | 264.5287 | 1
288 | 11 | 45 | 210 |  | -0.16363 | 3.5633 | 14.8568 | 21.5768 | 11.3596 | -0.16765 | 27.402 | 37.5647 | 175 | 212.5647 | 337.4677 | 1
288 | 12 | 47 | 226 |  | -0.16363 | 3.5633 | 14.8568 | 21.5768 | 12.3596 | 0.094147 | 27.7729 | 39.6447 | 188.3333 | 227.978 | 361.9379 | 1
288 | 13 | 46 | 217 |  | -0.16363 | 3.5633 | 14.8568 | 21.5768 | 13.3596 | 0.35595 | 25.5388 | 36.3617 | 180.8333 | 217.195 | 344.8189 | 1
288 | 14 | 0 | 127 |  | -0.16363 | 3.5633 | 14.8568 | 21.5768 | 14.3596 | 0.61775 | 20.9816 | 0 | 105.8333 | 105.8333 | 168.021 | 1
288 | 15 | 0 | 90 |  | -0.16363 | 3.5633 | 14.8568 | 21.5768 | 15.3596 | 0.87954 | 14.583 | 0 | 75 | 75 | 119.07 | 1
288 | 16 | 0 | 45 |  | -0.16363 | 3.5633 | 14.8568 | 21.5768 | 16.3596 | 1.1413 | 6.8638 | 0 | 37.5 | 37.5 | 59.535 | 0
288 | 17 | 0 | 8 |  | -0.16363 | 3.5633 | 14.8568 | 21.5768 | 17.3596 | 1.4031 | -1.7039 | 0 | 6.6667 | 6.6667 | 10.584 | 0
288 | 18 | 0 | 0 |  | -0.16363 | 3.5633 | 14.8568 | 21.5768 | 18.3596 | 1.6649 | -10.7068 | 0 | 0 | 0 | 0 | 0
288 | 19 | 0 | 0 |  | -0.16363 | 3.5633 | 14.8568 | 21.5768 | 19.3596 | 1.9267 | -19.755 | 0 | 0 | 0 | 0 | 0
288 | 20 | 0 | 0 |  | -0.16363 | 3.5633 | 14.8568 | 21.5768 | 20.3596 | 2.1885 | -28.425 | 0 | 0 | 0 | 0 | 0
288 | 21 | 0 | 0 |  | -0.16363 | 3.5633 | 14.8568 | 21.5768 | 21.3596 | 2.4503 | -36.186 | 0 | 0 | 0 | 0 | 0
288 | 22 | 0 | 0 |  | -0.16363 | 3.5633 | 14.8568 | 21.5768 | 22.3596 | 2.7121 | -42.3301 | 0 | 0 | 0 | 0 | 0
288 | 23 | 0 | 0 |  | -0.16363 | 3.5633 | 14.8568 | 21.5768 | 23.3596 | 2.9739 | -45.9993 | 0 | 0 | 0 | 0 | 0
288 | 24 | 0 | 0 |  | -0.16363 | 3.5633 | 14.8568 | 21.5768 | 24.3596 | 3.2357 | -46.4746 | 0 | 0 | 0 | 0 | 0
289 | 1 | 0 | 0 |  | -0.16995 | 3.5806 | 15.0477 | 21.7677 | 1.3628 | -2.7848 | -43.9798 | 0 | 0 | 0 | 0 | 0
289 | 2 | 0 | 0 |  | -0.16995 | 3.5806 | 15.0477 | 21.7677 | 2.3628 | -2.523 | -38.4121 | 0 | 0 | 0 | 0 | 0
289 | 3 | 0 | 0 |  | -0.16995 | 3.5806 | 15.0477 | 21.7677 | 3.3628 | -2.2612 | -31.0005 | 0 | 0 | 0 | 0 | 0
289 | 4 | 0 | 0 |  | -0.16995 | 3.5806 | 15.0477 | 21.7677 | 4.3628 | -1.9994 | -22.51 | 0 | 0 | 0 | 0 | 0
289 | 5 | 0 | 0 |  | -0.16995 | 3.5806 | 15.0477 | 21.7677 | 5.3628 | -1.7376 | -13.5162 | 0 | 0 | 0 | 0 | 0
289 | 6 | 0 | 0 |  | -0.16995 | 3.5806 | 15.0477 | 21.7677 | 6.3628 | -1.4758 | -4.464 | 0 | 0 | 0 | 0 | 0
289 | 7 | 0 | 4 |  | -0.16995 | 3.5806 | 15.0477 | 21.7677 | 7.3628 | -1.214 | 4.2548 | 0 | 3.3333 | 3.3333 | 5.292 | 0
289 | 8 | 0 | 31 |  | -0.16995 | 3.5806 | 15.0477 | 21.7677 | 8.3628 | -0.95222 | 12.2392 | 0 | 25.8333 | 25.8333 | 41.013 | 0
289 | 9 | 137 | 116 |  | -0.16995 | 3.5806 | 15.0477 | 21.7677 | 9.3628 | -0.69042 | 19.0373 | 87.1184 | 96.6667 | 183.7851 | 291.7772 | 1
289 | 10 | 47 | 166 |  | -0.16995 | 3.5806 | 15.0477 | 21.7677 | 10.3628 | -0.42862 | 24.1407 | 35.8096 | 138.3333 | 174.1429 | 276.4693 | 1
289 | 11 | 413 | 185 |  | -0.16995 | 3.5806 | 15.0477 | 21.7677 | 11.3628 | -0.16682 | 27.0479 | 343.4274 | 154.1667 | 497.5941 | 789.9804 | 1
289 | 12 | 656 | 119 |  | -0.16995 | 3.5806 | 15.0477 | 21.7677 | 12.3628 | 0.09498 | 27.4089 | 551.0852 | 99.1667 | 650.2518 | 1032.3398 | 1
289 | 13 | 706 | 93 |  | -0.16995 | 3.5806 | 15.0477 | 21.7677 | 13.3628 | 0.35678 | 25.1761 | 555.552 | 77.5 | 633.052 | 1005.0333 | 1
289 | 14 | 646 | 91 |  | -0.16995 | 3.5806 | 15.0477 | 21.7677 | 14.3628 | 0.61858 | 20.6287 | 436.4781 | 75.8333 | 512.3114 | 813.3456 | 1
289 | 15 | 76 | 117 |  | -0.16995 | 3.5806 | 15.0477 | 21.7677 | 15.3628 | 0.88038 | 14.2435 | 39.0591 | 97.5 | 136.5591 | 216.8012 | 1
289 | 16 | 2 | 70 |  | -0.16995 | 3.5806 | 15.0477 | 21.7677 | 16.3628 | 1.1422 | 6.5368 | 0.62548 | 58.3333 | 58.9588 | 93.603 | 0
289 | 17 | 0 | 12 |  | -0.16995 | 3.5806 | 15.0477 | 21.7677 | 17.3628 | 1.404 | -2.022 | 0 | 10 | 10 | 15.876 | 0
289 | 18 | 0 | 0 |  | -0.16995 | 3.5806 | 15.0477 | 21.7677 | 18.3628 | 1.6658 | -11.021 | 0 | 0 | 0 | 0 | 0
289 | 19 | 0 | 0 |  | -0.16995 | 3.5806 | 15.0477 | 21.7677 | 19.3628 | 1.9276 | -20.0716 | 0 | 0 | 0 | 0 | 0
289 | 20 | 0 | 0 |  | -0.16995 | 3.5806 | 15.0477 | 21.7677 | 20.3628 | 2.1894 | -28.7505 | 0 | 0 | 0 | 0 | 0
289 | 21 | 0 | 0 |  | -0.16995 | 3.5806 | 15.0477 | 21.7677 | 21.3628 | 2.4512 | -36.5259 | 0 | 0 | 0 | 0 | 0
289 | 22 | 0 | 0 |  | -0.16995 | 3.5806 | 15.0477 | 21.7677 | 22.3628 | 2.713 | -42.6861 | 0 | 0 | 0 | 0 | 0
289 | 23 | 0 | 0 |  | -0.16995 | 3.5806 | 15.0477 | 21.7677 | 23.3628 | 2.9748 | -46.364 | 0 | 0 | 0 | 0 | 0
289 | 24 | 0 | 0 |  | -0.16995 | 3.5806 | 15.0477 | 21.7677 | 24.3628 | 3.2366 | -46.8311 | 0 | 0 | 0 | 0 | 0
290 | 1 | 0 | 0 |  | -0.17621 | 3.5978 | 15.2274 | 21.9474 | 1.3658 | -2.784 | -44.3099 | 0 | 0 | 0 | 0 | 0
290 | 2 | 0 | 0 |  | -0.17621 | 3.5978 | 15.2274 | 21.9474 | 2.3658 | -2.5222 | -38.713 | 0 | 0 | 0 | 0 | 0
290 | 3 | 0 | 0 |  | -0.17621 | 3.5978 | 15.2274 | 21.9474 | 3.3658 | -2.2604 | -31.2772 | 0 | 0 | 0 | 0 | 0
290 | 4 | 0 | 0 |  | -0.17621 | 3.5978 | 15.2274 | 21.9474 | 4.3658 | -1.9986 | -22.7716 | 0 | 0 | 0 | 0 | 0
290 | 5 | 0 | 0 |  | -0.17621 | 3.5978 | 15.2274 | 21.9474 | 5.3658 | -1.7368 | -13.7721 | 0 | 0 | 0 | 0 | 0
290 | 6 | 0 | 0 |  | -0.17621 | 3.5978 | 15.2274 | 21.9474 | 6.3658 | -1.475 | -4.7231 | 0 | 0 | 0 | 0 | 0
290 | 7 | 0 | 3 |  | -0.17621 | 3.5978 | 15.2274 | 21.9474 | 7.3658 | -1.2132 | 3.9847 | 0 | 2.5 | 2.5 | 3.969 | 0
290 | 8 | 58 | 52 |  | -0.17621 | 3.5978 | 15.2274 | 21.9474 | 8.3658 | -0.95143 | 11.9516 | 26.6648 | 43.3333 | 69.9981 | 111.129 | 0
290 | 9 | 191 | 121 |  | -0.17621 | 3.5978 | 15.2274 | 21.9474 | 9.3658 | -0.68963 | 18.7274 | 120.9421 | 100.8333 | 221.7755 | 352.0907 | 1
290 | 10 | 495 | 128 |  | -0.17621 | 3.5978 | 15.2274 | 21.9474 | 10.3658 | -0.42784 | 23.8076 | 375.6624 | 106.6667 | 482.3291 | 765.7457 | 1
290 | 11 | 72 | 190 |  | -0.17621 | 3.5978 | 15.2274 | 21.9474 | 11.3658 | -0.16604 | 26.696 | 59.6374 | 158.3333 | 217.9708 | 346.0504 | 1
290 | 12 | 195 | 216 |  | -0.17621 | 3.5978 | 15.2274 | 21.9474 | 12.3658 | 0.095764 | 27.0476 | 163.1425 | 180 | 343.1425 | 544.773 | 1
290 | 13 | 124 | 239 |  | -0.17621 | 3.5978 | 15.2274 | 21.9474 | 13.3658 | 0.35756 | 24.8165 | 97.1338 | 199.1667 | 296.3005 | 470.4066 | 1
290 | 14 | 442 | 156 |  | -0.17621 | 3.5978 | 15.2274 | 21.9474 | 14.3658 | 0.61936 | 20.2792 | 297.049 | 130 | 427.049 | 677.983 | 1
290 | 15 | 433 | 98 |  | -0.17621 | 3.5978 | 15.2274 | 21.9474 | 15.3658 | 0.88116 | 13.9074 | 220.9902 | 81.6667 | 302.6569 | 480.4981 | 1
290 | 16 | 278 | 65 |  | -0.17621 | 3.5978 | 15.2274 | 21.9474 | 16.3658 | 1.143 | 6.2135 | 85.9843 | 54.1667 | 140.151 | 222.5038 | 0
290 | 17 | 0 | 20 |  | -0.17621 | 3.5978 | 15.2274 | 21.9474 | 17.3658 | 1.4048 | -2.3363 | 0 | 16.6667 | 16.6667 | 26.46 | 0
290 | 18 | 0 | 0 |  | -0.17621 | 3.5978 | 15.2274 | 21.9474 | 18.3658 | 1.6666 | -11.3314 | 0 | 0 | 0 | 0 | 0
290 | 19 | 0 | 0 |  | -0.17621 | 3.5978 | 15.2274 | 21.9474 | 19.3658 | 1.9284 | -20.3843 | 0 | 0 | 0 | 0 | 0
290 | 20 | 0 | 0 |  | -0.17621 | 3.5978 | 15.2274 | 21.9474 | 20.3658 | 2.1902 | -29.0721 | 0 | 0 | 0 | 0 | 0
290 | 21 | 0 | 0 |  | -0.17621 | 3.5978 | 15.2274 | 21.9474 | 21.3658 | 2.452 | -36.8621 | 0 | 0 | 0 | 0 | 0
290 | 22 | 0 | 0 |  | -0.17621 | 3.5978 | 15.2274 | 21.9474 | 22.3658 | 2.7138 | -43.0386 | 0 | 0 | 0 | 0 | 0
290 | 23 | 0 | 0 |  | -0.17621 | 3.5978 | 15.2274 | 21.9474 | 23.3658 | 2.9756 | -46.7258 | 0 | 0 | 0 | 0 | 0
290 | 24 | 0 | 0 |  | -0.17621 | 3.5978 | 15.2274 | 21.9474 | 24.3658 | 3.2374 | -47.1853 | 0 | 0 | 0 | 0 | 0
291 | 1 | 0 | 0 |  | -0.18244 | 3.615 | 15.3957 | 22.1157 | 1.3686 | -2.7833 | -44.638 | 0 | 0 | 0 | 0 | 0
291 | 2 | 0 | 0 |  | -0.18244 | 3.615 | 15.3957 | 22.1157 | 2.3686 | -2.5215 | -39.0123 | 0 | 0 | 0 | 0 | 0
291 | 3 | 0 | 0 |  | -0.18244 | 3.615 | 15.3957 | 22.1157 | 3.3686 | -2.2597 | -31.5527 | 0 | 0 | 0 | 0 | 0
291 | 4 | 0 | 0 |  | -0.18244 | 3.615 | 15.3957 | 22.1157 | 4.3686 | -1.9979 | -23.0323 | 0 | 0 | 0 | 0 | 0
291 | 5 | 0 | 0 |  | -0.18244 | 3.615 | 15.3957 | 22.1157 | 5.3686 | -1.7361 | -14.0275 | 0 | 0 | 0 | 0 | 0
291 | 6 | 0 | 0 |  | -0.18244 | 3.615 | 15.3957 | 22.1157 | 6.3686 | -1.4743 | -4.9818 | 0 | 0 | 0 | 0 | 0
291 | 7 | 0 | 5 |  | -0.18244 | 3.615 | 15.3957 | 22.1157 | 7.3686 | -1.2125 | 3.7151 | 0 | 4.1667 | 4.1667 | 6.615 | 0
291 | 8 | 0 | 45 |  | -0.18244 | 3.615 | 15.3957 | 22.1157 | 8.3686 | -0.9507 | 11.6645 | 0 | 37.5 | 37.5 | 59.535 | 0
291 | 9 | 16 | 110 |  | -0.18244 | 3.615 | 15.3957 | 22.1157 | 9.3686 | -0.6889 | 18.4185 | 10.0876 | 91.6667 | 101.7543 | 161.5451 | 1
291 | 10 | 23 | 168 |  | -0.18244 | 3.615 | 15.3957 | 22.1157 | 10.3686 | -0.4271 | 23.476 | 17.3856 | 140 | 157.3856 | 249.8654 | 1
291 | 11 | 43 | 200 |  | -0.18244 | 3.615 | 15.3957 | 22.1157 | 11.3686 | -0.1653 | 26.3463 | 35.4766 | 166.6667 | 202.1432 | 320.9226 | 1
291 | 12 | 45 | 215 |  | -0.18244 | 3.615 | 15.3957 | 22.1157 | 12.3686 | 0.096498 | 26.6891 | 37.4933 | 179.1667 | 216.6599 | 343.9693 | 1
291 | 13 | 191 | 204 |  | -0.18244 | 3.615 | 15.3957 | 22.1157 | 13.3686 | 0.3583 | 24.4602 | 148.9386 | 170 | 318.9386 | 506.3469 | 1
291 | 14 | 47 | 172 |  | -0.18244 | 3.615 | 15.3957 | 22.1157 | 14.3686 | 0.6201 | 19.9331 | 31.4183 | 143.3333 | 174.7516 | 277.4357 | 1
291 | 15 | 15 | 128 |  | -0.18244 | 3.615 | 15.3957 | 22.1157 | 15.3686 | 0.8819 | 13.575 | 7.6026 | 106.6667 | 114.2693 | 181.414 | 1
291 | 16 | 0 | 64 |  | -0.18244 | 3.615 | 15.3957 | 22.1157 | 16.3686 | 1.1437 | 5.8939 | 0 | 53.3333 | 53.3333 | 84.672 | 0
291 | 17 | 0 | 10 |  | -0.18244 | 3.615 | 15.3957 | 22.1157 | 17.3686 | 1.4055 | -2.6467 | 0 | 8.3333 | 8.3333 | 13.23 | 0
291 | 18 | 0 | 0 |  | -0.18244 | 3.615 | 15.3957 | 22.1157 | 18.3686 | 1.6673 | -11.6379 | 0 | 0 | 0 | 0 | 0
291 | 19 | 0 | 0 |  | -0.18244 | 3.615 | 15.3957 | 22.1157 | 19.3686 | 1.9291 | -20.6929 | 0 | 0 | 0 | 0 | 0
291 | 20 | 0 | 0 |  | -0.18244 | 3.615 | 15.3957 | 22.1157 | 20.3686 | 2.1909 | -29.3896 | 0 | 0 | 0 | 0 | 0
291 | 21 | 0 | 0 |  | -0.18244 | 3.615 | 15.3957 | 22.1157 | 21.3686 | 2.4527 | -37.1943 | 0 | 0 | 0 | 0 | 0
291 | 22 | 0 | 0 |  | -0.18244 | 3.615 | 15.3957 | 22.1157 | 22.3686 | 2.7145 | -43.3876 | 0 | 0 | 0 | 0 | 0
291 | 23 | 0 | 0 |  | -0.18244 | 3.615 | 15.3957 | 22.1157 | 23.3686 | 2.9763 | -47.0846 | 0 | 0 | 0 | 0 | 0
291 | 24 | 0 | 0 |  | -0.18244 | 3.615 | 15.3957 | 22.1157 | 24.3686 | 3.2381 | -47.537 | 0 | 0 | 0 | 0 | 0
292 | 1 | 0 | 0 |  | -0.18861 | 3.6322 | 15.5522 | 22.2722 | 1.3712 | -2.7826 | -44.964 | 0 | 0 | 0 | 0 | 0
292 | 2 | 0 | 0 |  | -0.18861 | 3.6322 | 15.5522 | 22.2722 | 2.3712 | -2.5208 | -39.31 | 0 | 0 | 0 | 0 | 0
292 | 3 | 0 | 0 |  | -0.18861 | 3.6322 | 15.5522 | 22.2722 | 3.3712 | -2.259 | -31.827 | 0 | 0 | 0 | 0 | 0
292 | 4 | 0 | 0 |  | -0.18861 | 3.6322 | 15.5522 | 22.2722 | 4.3712 | -1.9972 | -23.2922 | 0 | 0 | 0 | 0 | 0
292 | 5 | 0 | 0 |  | -0.18861 | 3.6322 | 15.5522 | 22.2722 | 5.3712 | -1.7354 | -14.2823 | 0 | 0 | 0 | 0 | 0
292 | 6 | 0 | 0 |  | -0.18861 | 3.6322 | 15.5522 | 22.2722 | 6.3712 | -1.4736 | -5.24 | 0 | 0 | 0 | 0 | 0
292 | 7 | 0 | 5 |  | -0.18861 | 3.6322 | 15.5522 | 22.2722 | 7.3712 | -1.2118 | 3.4459 | 0 | 4.1667 | 4.1667 | 6.615 | 0
292 | 8 | 0 | 43 |  | -0.18861 | 3.6322 | 15.5522 | 22.2722 | 8.3712 | -0.95002 | 11.3781 | 0 | 35.8333 | 35.8333 | 56.889 | 0
292 | 9 | 18 | 106 |  | -0.18861 | 3.6322 | 15.5522 | 22.2722 | 9.3712 | -0.68822 | 18.1107 | 11.2989 | 88.3333 | 99.6323 | 158.1762 | 1
292 | 10 | 31 | 161 |  | -0.18861 | 3.6322 | 15.5522 | 22.2722 | 10.3712 | -0.42642 | 23.1462 | 23.3385 | 134.1667 | 157.5052 | 250.0553 | 1
292 | 11 | 44 | 195 |  | -0.18861 | 3.6322 | 15.5522 | 22.2722 | 11.3712 | -0.16462 | 25.9989 | 36.1575 | 162.5 | 198.6575 | 315.3886 | 1
292 | 12 | 47 | 211 |  | -0.18861 | 3.6322 | 15.5522 | 22.2722 | 12.3712 | 0.097181 | 26.3335 | 38.9976 | 175.8333 | 214.831 | 341.0657 | 1
292 | 13 | 45 | 202 |  | -0.18861 | 3.6322 | 15.5522 | 22.2722 | 13.3712 | 0.35898 | 24.1071 | 34.9309 | 168.3333 | 203.2642 | 322.7022 | 1
292 | 14 | 17 | 180 |  | -0.18861 | 3.6322 | 15.5522 | 22.2722 | 14.3712 | 0.62078 | 19.5906 | 11.3036 | 150 | 161.3036 | 256.0856 | 1
292 | 15 | 17 | 124 |  | -0.18861 | 3.6322 | 15.5522 | 22.2722 | 15.3712 | 0.88258 | 13.2463 | 8.5571 | 103.3333 | 111.8904 | 177.6372 | 1
292 | 16 | 0 | 61 |  | -0.18861 | 3.6322 | 15.5522 | 22.2722 | 16.3712 | 1.1444 | 5.5781 | 0 | 50.8333 | 50.8333 | 80.703 | 0
292 | 17 | 0 | 9 |  | -0.18861 | 3.6322 | 15.5522 | 22.2722 | 17.3712 | 1.4062 | -2.9531 | 0 | 7.5 | 7.5 | 11.907 | 0
292 | 18 | 0 | 0 |  | -0.18861 | 3.6322 | 15.5522 | 22.2722 | 18.3712 | 1.668 | -11.9402 | 0 | 0 | 0 | 0 | 0
292 | 19 | 0 | 0 |  | -0.18861 | 3.6322 | 15.5522 | 22.2722 | 19.3712 | 1.9298 | -20.9974 | 0 | 0 | 0 | 0 | 0
292 | 20 | 0 | 0 |  | -0.18861 | 3.6322 | 15.5522 | 22.2722 | 20.3712 | 2.1916 | -29.7028 | 0 | 0 | 0 | 0 | 0
292 | 21 | 0 | 0 |  | -0.18861 | 3.6322 | 15.5522 | 22.2722 | 21.3712 | 2.4534 | -37.5225 | 0 | 0 | 0 | 0 | 0
292 | 22 | 0 | 0 |  | -0.18861 | 3.6322 | 15.5522 | 22.2722 | 22.3712 | 2.7152 | -43.7329 | 0 | 0 | 0 | 0 | 0
292 | 23 | 0 | 0 |  | -0.18861 | 3.6322 | 15.5522 | 22.2722 | 23.3712 | 2.977 | -47.4403 | 0 | 0 | 0 | 0 | 0
292 | 24 | 0 | 0 |  | -0.18861 | 3.6322 | 15.5522 | 22.2722 | 24.3712 | 3.2388 | -47.8861 | 0 | 0 | 0 | 0 | 0
293 | 1 | 0 | 0 |  | -0.19474 | 3.6494 | 15.6969 | 22.4169 | 1.3736 | -2.782 | -45.2879 | 0 | 0 | 0 | 0 | 0
293 | 2 | 0 | 0 |  | -0.19474 | 3.6494 | 15.6969 | 22.4169 | 2.3736 | -2.5202 | -39.606 | 0 | 0 | 0 | 0 | 0
293 | 3 | 0 | 0 |  | -0.19474 | 3.6494 | 15.6969 | 22.4169 | 3.3736 | -2.2584 | -32.1001 | 0 | 0 | 0 | 0 | 0
293 | 4 | 0 | 0 |  | -0.19474 | 3.6494 | 15.6969 | 22.4169 | 4.3736 | -1.9966 | -23.5513 | 0 | 0 | 0 | 0 | 0
293 | 5 | 0 | 0 |  | -0.19474 | 3.6494 | 15.6969 | 22.4169 | 5.3736 | -1.7348 | -14.5365 | 0 | 0 | 0 | 0 | 0
293 | 6 | 0 | 0 |  | -0.19474 | 3.6494 | 15.6969 | 22.4169 | 6.3736 | -1.473 | -5.4977 | 0 | 0 | 0 | 0 | 0
293 | 7 | 0 | 4 |  | -0.19474 | 3.6494 | 15.6969 | 22.4169 | 7.3736 | -1.2112 | 3.1773 | 0 | 3.3333 | 3.3333 | 5.292 | 0
293 | 8 | 0 | 26 |  | -0.19474 | 3.6494 | 15.6969 | 22.4169 | 8.3736 | -0.94939 | 11.0925 | 0 | 21.6667 | 21.6667 | 34.398 | 0
293 | 9 | 0 | 68 |  | -0.19474 | 3.6494 | 15.6969 | 22.4169 | 9.3736 | -0.68759 | 17.804 | 0 | 56.6667 | 56.6667 | 89.964 | 1
293 | 10 | 0 | 106 |  | -0.19474 | 3.6494 | 15.6969 | 22.4169 | 10.3736 | -0.42579 | 22.8181 | 0 | 88.3333 | 88.3333 | 140.238 | 1
293 | 11 | 0 | 133 |  | -0.19474 | 3.6494 | 15.6969 | 22.4169 | 11.3736 | -0.16399 | 25.6539 | 0 | 110.8333 | 110.8333 | 175.959 | 1
293 | 12 | 0 | 143 |  | -0.19474 | 3.6494 | 15.6969 | 22.4169 | 12.3736 | 0.097812 | 25.9809 | 0 | 119.1667 | 119.1667 | 189.189 | 1
293 | 13 | 0 | 137 |  | -0.19474 | 3.6494 | 15.6969 | 22.4169 | 13.3736 | 0.35961 | 23.7575 | 0 | 114.1667 | 114.1667 | 181.251 | 1
293 | 14 | 0 | 114 |  | -0.19474 | 3.6494 | 15.6969 | 22.4169 | 14.3736 | 0.62141 | 19.2518 | 0 | 95 | 95 | 150.822 | 1
293 | 15 | 0 | 79 |  | -0.19474 | 3.6494 | 15.6969 | 22.4169 | 15.3736 | 0.88321 | 12.9215 | 0 | 65.8333 | 65.8333 | 104.517 | 1
293 | 16 | 0 | 58 |  | -0.19474 | 3.6494 | 15.6969 | 22.4169 | 16.3736 | 1.145 | 5.2663 | 0 | 48.3333 | 48.3333 | 76.734 | 0
293 | 17 | 0 | 9 |  | -0.19474 | 3.6494 | 15.6969 | 22.4169 | 17.3736 | 1.4068 | -3.2555 | 0 | 7.5 | 7.5 | 11.907 | 0
293 | 18 | 0 | 0 |  | -0.19474 | 3.6494 | 15.6969 | 22.4169 | 18.3736 | 1.6686 | -12.2383 | 0 | 0 | 0 | 0 | 0
293 | 19 | 0 | 0 |  | -0.19474 | 3.6494 | 15.6969 | 22.4169 | 19.3736 | 1.9304 | -21.2975 | 0 | 0 | 0 | 0 | 0
293 | 20 | 0 | 0 |  | -0.19474 | 3.6494 | 15.6969 | 22.4169 | 20.3736 | 2.1922 | -30.0118 | 0 | 0 | 0 | 0 | 0
293 | 21 | 0 | 0 |  | -0.19474 | 3.6494 | 15.6969 | 22.4169 | 21.3736 | 2.454 | -37.8464 | 0 | 0 | 0 | 0 | 0
293 | 22 | 0 | 0 |  | -0.19474 | 3.6494 | 15.6969 | 22.4169 | 22.3736 | 2.7158 | -44.0743 | 0 | 0 | 0 | 0 | 0
293 | 23 | 0 | 0 |  | -0.19474 | 3.6494 | 15.6969 | 22.4169 | 23.3736 | 2.9776 | -47.7927 | 0 | 0 | 0 | 0 | 0
293 | 24 | 0 | 0 |  | -0.19474 | 3.6494 | 15.6969 | 22.4169 | 24.3736 | 3.2394 | -48.2327 | 0 | 0 | 0 | 0 | 0
294 | 1 | 0 | 0 |  | -0.20082 | 3.6666 | 15.8294 | 22.5494 | 1.3758 | -2.7814 | -45.6096 | 0 | 0 | 0 | 0 | 0
294 | 2 | 0 | 0 |  | -0.20082 | 3.6666 | 15.8294 | 22.5494 | 2.3758 | -2.5196 | -39.9003 | 0 | 0 | 0 | 0 | 0
294 | 3 | 0 | 0 |  | -0.20082 | 3.6666 | 15.8294 | 22.5494 | 3.3758 | -2.2578 | -32.3719 | 0 | 0 | 0 | 0 | 0
294 | 4 | 0 | 0 |  | -0.20082 | 3.6666 | 15.8294 | 22.5494 | 4.3758 | -1.996 | -23.8094 | 0 | 0 | 0 | 0 | 0
294 | 5 | 0 | 0 |  | -0.20082 | 3.6666 | 15.8294 | 22.5494 | 5.3758 | -1.7342 | -14.79 | 0 | 0 | 0 | 0 | 0
294 | 6 | 0 | 0 |  | -0.20082 | 3.6666 | 15.8294 | 22.5494 | 6.3758 | -1.4724 | -5.7548 | 0 | 0 | 0 | 0 | 0
294 | 7 | 0 | 2 |  | -0.20082 | 3.6666 | 15.8294 | 22.5494 | 7.3758 | -1.2106 | 2.9093 | 0 | 1.6667 | 1.6667 | 2.646 | 0
294 | 8 | 0 | 24 |  | -0.20082 | 3.6666 | 15.8294 | 22.5494 | 8.3758 | -0.94881 | 10.8078 | 0 | 20 | 20 | 31.752 | 0
294 | 9 | 25 | 99 |  | -0.20082 | 3.6666 | 15.8294 | 22.5494 | 9.3758 | -0.68701 | 17.4987 | 15.5529 | 82.5 | 98.0529 | 155.6687 | 1
294 | 10 | 161 | 156 |  | -0.20082 | 3.6666 | 15.8294 | 22.5494 | 10.3758 | -0.42521 | 22.4918 | 120.2201 | 130 | 250.2201 | 397.2494 | 1
294 | 11 | 332 | 170 |  | -0.20082 | 3.6666 | 15.8294 | 22.5494 | 11.3758 | -0.16341 | 25.3115 | 270.638 | 141.6667 | 412.3046 | 654.5749 | 1
294 | 12 | 479 | 153 |  | -0.20082 | 3.6666 | 15.8294 | 22.5494 | 12.3758 | 0.09839 | 25.6314 | 394.1434 | 127.5 | 521.6434 | 828.161 | 1
294 | 13 | 427 | 167 |  | -0.20082 | 3.6666 | 15.8294 | 22.5494 | 13.3758 | 0.36019 | 23.4114 | 328.4488 | 139.1667 | 467.6155 | 742.3863 | 1
294 | 14 | 186 | 161 |  | -0.20082 | 3.6666 | 15.8294 | 22.5494 | 14.3758 | 0.62199 | 18.9167 | 122.3684 | 134.1667 | 256.535 | 407.275 | 1
294 | 15 | 139 | 117 |  | -0.20082 | 3.6666 | 15.8294 | 22.5494 | 15.3758 | 0.88379 | 12.6006 | 69.0152 | 97.5 | 166.5152 | 264.3595 | 1
294 | 16 | 0 | 56 |  | -0.20082 | 3.6666 | 15.8294 | 22.5494 | 16.3758 | 1.1456 | 4.9586 | 0 | 46.6667 | 46.6667 | 74.088 | 0
294 | 17 | 0 | 10 |  | -0.20082 | 3.6666 | 15.8294 | 22.5494 | 17.3758 | 1.4074 | -3.5536 | 0 | 8.3333 | 8.3333 | 13.23 | 0
294 | 18 | 0 | 0 |  | -0.20082 | 3.6666 | 15.8294 | 22.5494 | 18.3758 | 1.6692 | -12.5322 | 0 | 0 | 0 | 0 | 0
294 | 19 | 0 | 0 |  | -0.20082 | 3.6666 | 15.8294 | 22.5494 | 19.3758 | 1.931 | -21.5933 | 0 | 0 | 0 | 0 | 0
294 | 20 | 0 | 0 |  | -0.20082 | 3.6666 | 15.8294 | 22.5494 | 20.3758 | 2.1928 | -30.3163 | 0 | 0 | 0 | 0 | 0
294 | 21 | 0 | 0 |  | -0.20082 | 3.6666 | 15.8294 | 22.5494 | 21.3758 | 2.4546 | -38.1661 | 0 | 0 | 0 | 0 | 0
294 | 22 | 0 | 0 |  | -0.20082 | 3.6666 | 15.8294 | 22.5494 | 22.3758 | 2.7164 | -44.4118 | 0 | 0 | 0 | 0 | 0
294 | 23 | 0 | 0 |  | -0.20082 | 3.6666 | 15.8294 | 22.5494 | 23.3758 | 2.9782 | -48.1418 | 0 | 0 | 0 | 0 | 0
294 | 24 | 0 | 0 |  | -0.20082 | 3.6666 | 15.8294 | 22.5494 | 24.3758 | 3.24 | -48.5764 | 0 | 0 | 0 | 0 | 0
295 | 1 | 0 | 0 |  | -0.20684 | 3.6838 | 15.9497 | 22.6697 | 1.3778 | -2.7809 | -45.929 | 0 | 0 | 0 | 0 | 0
295 | 2 | 0 | 0 |  | -0.20684 | 3.6838 | 15.9497 | 22.6697 | 2.3778 | -2.5191 | -40.1928 | 0 | 0 | 0 | 0 | 0
295 | 3 | 0 | 0 |  | -0.20684 | 3.6838 | 15.9497 | 22.6697 | 3.3778 | -2.2573 | -32.6424 | 0 | 0 | 0 | 0 | 0
295 | 4 | 0 | 0 |  | -0.20684 | 3.6838 | 15.9497 | 22.6697 | 4.3778 | -1.9955 | -24.0665 | 0 | 0 | 0 | 0 | 0
295 | 5 | 0 | 0 |  | -0.20684 | 3.6838 | 15.9497 | 22.6697 | 5.3778 | -1.7337 | -15.0427 | 0 | 0 | 0 | 0 | 0
295 | 6 | 0 | 0 |  | -0.20684 | 3.6838 | 15.9497 | 22.6697 | 6.3778 | -1.4719 | -6.0113 | 0 | 0 | 0 | 0 | 0
295 | 7 | 0 | 5 |  | -0.20684 | 3.6838 | 15.9497 | 22.6697 | 7.3778 | -1.2101 | 2.6421 | 0 | 4.1667 | 4.1667 | 6.615 | 0
295 | 8 | 137 | 48 |  | -0.20684 | 3.6838 | 15.9497 | 22.6697 | 8.3778 | -0.94828 | 10.5239 | 61.2853 | 40 | 101.2853 | 160.8006 | 0
295 | 9 | 315 | 88 |  | -0.20684 | 3.6838 | 15.9497 | 22.6697 | 9.3778 | -0.68648 | 17.1947 | 195.0704 | 73.3333 | 268.4037 | 426.1178 | 1
295 | 10 | 415 | 121 |  | -0.20684 | 3.6838 | 15.9497 | 22.6697 | 10.3778 | -0.42468 | 22.1675 | 308.5962 | 100.8333 | 409.4295 | 650.0103 | 1
295 | 11 | 555 | 123 |  | -0.20684 | 3.6838 | 15.9497 | 22.6697 | 11.3778 | -0.16288 | 24.9717 | 450.5866 | 102.5 | 553.0866 | 878.0802 | 1
295 | 12 | 666 | 99 |  | -0.20684 | 3.6838 | 15.9497 | 22.6697 | 12.3778 | 0.098915 | 25.2851 | 545.7245 | 82.5 | 628.2245 | 997.3692 | 1
295 | 13 | 595 | 112 |  | -0.20684 | 3.6838 | 15.9497 | 22.6697 | 13.3778 | 0.36071 | 23.069 | 455.5957 | 93.3333 | 548.9291 | 871.4798 | 1
295 | 14 | 463 | 132 |  | -0.20684 | 3.6838 | 15.9497 | 22.6697 | 14.3778 | 0.62251 | 18.5856 | 303.0011 | 110 | 413.0011 | 655.6805 | 1
295 | 15 | 353 | 96 |  | -0.20684 | 3.6838 | 15.9497 | 22.6697 | 15.3778 | 0.88431 | 12.2838 | 174.0848 | 80 | 254.0848 | 403.3851 | 0
295 | 16 | 193 | 60 |  | -0.20684 | 3.6838 | 15.9497 | 22.6697 | 16.3778 | 1.1461 | 4.6551 | 56.5262 | 50 | 106.5262 | 169.121 | 0
295 | 17 | 0 | 12 |  | -0.20684 | 3.6838 | 15.9497 | 22.6697 | 17.3778 | 1.4079 | -3.8475 | 0 | 10 | 10 | 15.876 | 0
295 | 18 | 0 | 0 |  | -0.20684 | 3.6838 | 15.9497 | 22.6697 | 18.3778 | 1.6697 | -12.8215 | 0 | 0 | 0 | 0 | 0
295 | 19 | 0 | 0 |  | -0.20684 | 3.6838 | 15.9497 | 22.6697 | 19.3778 | 1.9315 | -21.8845 | 0 | 0 | 0 | 0 | 0
295 | 20 | 0 | 0 |  | -0.20684 | 3.6838 | 15.9497 | 22.6697 | 20.3778 | 2.1933 | -30.6163 | 0 | 0 | 0 | 0 | 0
295 | 21 | 0 | 0 |  | -0.20684 | 3.6838 | 15.9497 | 22.6697 | 21.3778 | 2.4551 | -38.4813 | 0 | 0 | 0 | 0 | 0
295 | 22 | 0 | 0 |  | -0.20684 | 3.6838 | 15.9497 | 22.6697 | 22.3778 | 2.7169 | -44.7453 | 0 | 0 | 0 | 0 | 0
295 | 23 | 0 | 0 |  | -0.20684 | 3.6838 | 15.9497 | 22.6697 | 23.3778 | 2.9787 | -48.4874 | 0 | 0 | 0 | 0 | 0
295 | 24 | 0 | 0 |  | -0.20684 | 3.6838 | 15.9497 | 22.6697 | 24.3778 | 3.2405 | -48.9174 | 0 | 0 | 0 | 0 | 0
296 | 1 | 0 | 0 |  | -0.21281 | 3.7011 | 16.0574 | 22.7774 | 1.3796 | -2.7804 | -46.2461 | 0 | 0 | 0 | 0 | 0
296 | 2 | 0 | 0 |  | -0.21281 | 3.7011 | 16.0574 | 22.7774 | 2.3796 | -2.5186 | -40.4835 | 0 | 0 | 0 | 0 | 0
296 | 3 | 0 | 0 |  | -0.21281 | 3.7011 | 16.0574 | 22.7774 | 3.3796 | -2.2568 | -32.9115 | 0 | 0 | 0 | 0 | 0
296 | 4 | 0 | 0 |  | -0.21281 | 3.7011 | 16.0574 | 22.7774 | 4.3796 | -1.995 | -24.3226 | 0 | 0 | 0 | 0 | 0
296 | 5 | 0 | 0 |  | -0.21281 | 3.7011 | 16.0574 | 22.7774 | 5.3796 | -1.7332 | -15.2947 | 0 | 0 | 0 | 0 | 0
296 | 6 | 0 | 0 |  | -0.21281 | 3.7011 | 16.0574 | 22.7774 | 6.3796 | -1.4714 | -6.2671 | 0 | 0 | 0 | 0 | 0
296 | 7 | 0 | 4 |  | -0.21281 | 3.7011 | 16.0574 | 22.7774 | 7.3796 | -1.2096 | 2.3755 | 0 | 3.3333 | 3.3333 | 5.292 | 0
296 | 8 | 112 | 48 |  | -0.21281 | 3.7011 | 16.0574 | 22.7774 | 8.3796 | -0.94781 | 10.2411 | 49.8135 | 40 | 89.8135 | 142.5879 | 0
296 | 9 | 354 | 84 |  | -0.21281 | 3.7011 | 16.0574 | 22.7774 | 9.3796 | -0.68601 | 16.8921 | 218.2063 | 70 | 288.2063 | 457.5564 | 1
296 | 10 | 87 | 131 |  | -0.21281 | 3.7011 | 16.0574 | 22.7774 | 10.3796 | -0.42421 | 21.8453 | 64.4221 | 109.1667 | 173.5888 | 275.5896 | 1
296 | 11 | 42 | 186 |  | -0.21281 | 3.7011 | 16.0574 | 22.7774 | 11.3796 | -0.16241 | 24.6346 | 33.9593 | 155 | 188.9593 | 299.9917 | 1
296 | 12 | 44 | 201 |  | -0.21281 | 3.7011 | 16.0574 | 22.7774 | 12.3796 | 0.099385 | 24.9422 | 35.9028 | 167.5 | 203.4028 | 322.9223 | 1
296 | 13 | 43 | 192 |  | -0.21281 | 3.7011 | 16.0574 | 22.7774 | 13.3796 | 0.36118 | 22.7303 | 32.776 | 160 | 192.776 | 306.0512 | 1
296 | 14 | 0 | 109 |  | -0.21281 | 3.7011 | 16.0574 | 22.7774 | 14.3796 | 0.62298 | 18.2585 | 0 | 90.8333 | 90.8333 | 144.207 | 1
296 | 15 | 0 | 73 |  | -0.21281 | 3.7011 | 16.0574 | 22.7774 | 15.3796 | 0.88478 | 11.9711 | 0 | 60.8333 | 60.8333 | 96.579 | 0
296 | 16 | 0 | 32 |  | -0.21281 | 3.7011 | 16.0574 | 22.7774 | 16.3796 | 1.1466 | 4.3558 | 0 | 26.6667 | 26.6667 | 42.336 | 0
296 | 17 | 0 | 4 |  | -0.21281 | 3.7011 | 16.0574 | 22.7774 | 17.3796 | 1.4084 | -4.1369 | 0 | 3.3333 | 3.3333 | 5.292 | 0
296 | 18 | 0 | 0 |  | -0.21281 | 3.7011 | 16.0574 | 22.7774 | 18.3796 | 1.6702 | -13.1064 | 0 | 0 | 0 | 0 | 0
296 | 19 | 0 | 0 |  | -0.21281 | 3.7011 | 16.0574 | 22.7774 | 19.3796 | 1.932 | -22.1711 | 0 | 0 | 0 | 0 | 0
296 | 20 | 0 | 0 |  | -0.21281 | 3.7011 | 16.0574 | 22.7774 | 20.3796 | 2.1938 | -30.9116 | 0 | 0 | 0 | 0 | 0
296 | 21 | 0 | 0 |  | -0.21281 | 3.7011 | 16.0574 | 22.7774 | 21.3796 | 2.4556 | -38.792 | 0 | 0 | 0 | 0 | 0
296 | 22 | 0 | 0 |  | -0.21281 | 3.7011 | 16.0574 | 22.7774 | 22.3796 | 2.7174 | -45.0746 | 0 | 0 | 0 | 0 | 0
296 | 23 | 0 | 0 |  | -0.21281 | 3.7011 | 16.0574 | 22.7774 | 23.3796 | 2.9792 | -48.8294 | 0 | 0 | 0 | 0 | 0
296 | 24 | 0 | 0 |  | -0.21281 | 3.7011 | 16.0574 | 22.7774 | 24.3796 | 3.241 | -49.2555 | 0 | 0 | 0 | 0 | 0
297 | 1 | 0 | 0 |  | -0.21872 | 3.7183 | 16.1526 | 22.8726 | 1.3812 | -2.78 | -46.5608 | 0 | 0 | 0 | 0 | 0
297 | 2 | 0 | 0 |  | -0.21872 | 3.7183 | 16.1526 | 22.8726 | 2.3812 | -2.5182 | -40.7723 | 0 | 0 | 0 | 0 | 0
297 | 3 | 0 | 0 |  | -0.21872 | 3.7183 | 16.1526 | 22.8726 | 3.3812 | -2.2564 | -33.1791 | 0 | 0 | 0 | 0 | 0
297 | 4 | 0 | 0 |  | -0.21872 | 3.7183 | 16.1526 | 22.8726 | 4.3812 | -1.9946 | -24.5777 | 0 | 0 | 0 | 0 | 0
297 | 5 | 0 | 0 |  | -0.21872 | 3.7183 | 16.1526 | 22.8726 | 5.3812 | -1.7328 | -15.5459 | 0 | 0 | 0 | 0 | 0
297 | 6 | 0 | 0 |  | -0.21872 | 3.7183 | 16.1526 | 22.8726 | 6.3812 | -1.471 | -6.5222 | 0 | 0 | 0 | 0 | 0
297 | 7 | 0 | 2 |  | -0.21872 | 3.7183 | 16.1526 | 22.8726 | 7.3812 | -1.2092 | 2.1099 | 0 | 1.6667 | 1.6667 | 2.646 | 0
297 | 8 | 12 | 41 |  | -0.21872 | 3.7183 | 16.1526 | 22.8726 | 8.3812 | -0.9474 | 9.9594 | 5.3059 | 34.1667 | 39.4726 | 62.6667 | 0
297 | 9 | 211 | 94 |  | -0.21872 | 3.7183 | 16.1526 | 22.8726 | 9.3812 | -0.6856 | 16.5912 | 129.4503 | 78.3333 | 207.7837 | 329.8774 | 1
297 | 10 | 302 | 132 |  | -0.21872 | 3.7183 | 16.1526 | 22.8726 | 10.3812 | -0.4238 | 21.5253 | 222.6789 | 110 | 332.6789 | 528.161 | 1
297 | 11 | 175 | 186 |  | -0.21872 | 3.7183 | 16.1526 | 22.8726 | 11.3812 | -0.162 | 24.3003 | 140.9162 | 155 | 295.9162 | 469.7966 | 1
297 | 12 | 477 | 166 |  | -0.21872 | 3.7183 | 16.1526 | 22.8726 | 12.3812 | 0.0998 | 24.6027 | 387.5847 | 138.3333 | 525.9181 | 834.9475 | 1
297 | 13 | 639 | 98 |  | -0.21872 | 3.7183 | 16.1526 | 22.8726 | 13.3812 | 0.3616 | 22.3954 | 484.862 | 81.6667 | 566.5287 | 899.421 | 1
297 | 14 | 573 | 94 |  | -0.21872 | 3.7183 | 16.1526 | 22.8726 | 14.3812 | 0.6234 | 17.9355 | 371.0789 | 78.3333 | 449.4123 | 713.4869 | 1
297 | 15 | 448 | 82 |  | -0.21872 | 3.7183 | 16.1526 | 22.8726 | 15.3812 | 0.8852 | 11.6627 | 217.9954 | 68.3333 | 286.3288 | 454.5756 | 0
297 | 16 | 213 | 54 |  | -0.21872 | 3.7183 | 16.1526 | 22.8726 | 16.3812 | 1.147 | 4.061 | 61.0723 | 45 | 106.0723 | 168.4004 | 0
297 | 17 | 0 | 10 |  | -0.21872 | 3.7183 | 16.1526 | 22.8726 | 17.3812 | 1.4088 | -4.4218 | 0 | 8.3333 | 8.3333 | 13.23 | 0
297 | 18 | 0 | 0 |  | -0.21872 | 3.7183 | 16.1526 | 22.8726 | 18.3812 | 1.6706 | -13.3866 | 0 | 0 | 0 | 0 | 0
297 | 19 | 0 | 0 |  | -0.21872 | 3.7183 | 16.1526 | 22.8726 | 19.3812 | 1.9324 | -22.4529 | 0 | 0 | 0 | 0 | 0
297 | 20 | 0 | 0 |  | -0.21872 | 3.7183 | 16.1526 | 22.8726 | 20.3812 | 2.1942 | -31.2022 | 0 | 0 | 0 | 0 | 0
297 | 21 | 0 | 0 |  | -0.21872 | 3.7183 | 16.1526 | 22.8726 | 21.3812 | 2.456 | -39.098 | 0 | 0 | 0 | 0 | 0
297 | 22 | 0 | 0 |  | -0.21872 | 3.7183 | 16.1526 | 22.8726 | 22.3812 | 2.7178 | -45.3995 | 0 | 0 | 0 | 0 | 0
297 | 23 | 0 | 0 |  | -0.21872 | 3.7183 | 16.1526 | 22.8726 | 23.3812 | 2.9796 | -49.1678 | 0 | 0 | 0 | 0 | 0
297 | 24 | 0 | 0 |  | -0.21872 | 3.7183 | 16.1526 | 22.8726 | 24.3812 | 3.2414 | -49.5906 | 0 | 0 | 0 | 0 | 0
298 | 1 | 0 | 0 |  | -0.22457 | 3.7355 | 16.2349 | 22.9549 | 1.3826 | -2.7796 | -46.8731 | 0 | 0 | 0 | 0 | 0
298 | 2 | 0 | 0 |  | -0.22457 | 3.7355 | 16.2349 | 22.9549 | 2.3826 | -2.5178 | -41.0592 | 0 | 0 | 0 | 0 | 0
298 | 3 | 0 | 0 |  | -0.22457 | 3.7355 | 16.2349 | 22.9549 | 3.3826 | -2.256 | -33.4453 | 0 | 0 | 0 | 0 | 0
298 | 4 | 0 | 0 |  | -0.22457 | 3.7355 | 16.2349 | 22.9549 | 4.3826 | -1.9942 | -24.8317 | 0 | 0 | 0 | 0 | 0
298 | 5 | 0 | 0 |  | -0.22457 | 3.7355 | 16.2349 | 22.9549 | 5.3826 | -1.7324 | -15.7962 | 0 | 0 | 0 | 0 | 0
298 | 6 | 0 | 0 |  | -0.22457 | 3.7355 | 16.2349 | 22.9549 | 6.3826 | -1.4706 | -6.7764 | 0 | 0 | 0 | 0 | 0
298 | 7 | 0 | 3 |  | -0.22457 | 3.7355 | 16.2349 | 22.9549 | 7.3826 | -1.2088 | 1.8451 | 0 | 2.5 | 2.5 | 3.969 | 0
298 | 8 | 86 | 46 |  | -0.22457 | 3.7355 | 16.2349 | 22.9549 | 8.3826 | -0.94704 | 9.6789 | 37.7993 | 38.3333 | 76.1326 | 120.8681 | 0
298 | 9 | 390 | 77 |  | -0.22457 | 3.7355 | 16.2349 | 22.9549 | 9.3826 | -0.68524 | 16.2919 | 238.1311 | 64.1667 | 302.2978 | 479.9279 | 1
298 | 10 | 575 | 83 |  | -0.22457 | 3.7355 | 16.2349 | 22.9549 | 10.3826 | -0.42344 | 21.2075 | 422.1628 | 69.1667 | 491.3295 | 780.0347 | 1
298 | 11 | 648 | 91 |  | -0.22457 | 3.7355 | 16.2349 | 22.9549 | 11.3826 | -0.16164 | 23.969 | 519.6403 | 75.8333 | 595.4737 | 945.374 | 1
298 | 12 | 685 | 89 |  | -0.22457 | 3.7355 | 16.2349 | 22.9549 | 12.3826 | 0.10016 | 24.2667 | 554.2549 | 74.1667 | 628.4216 | 997.6822 | 1
298 | 13 | 665 | 89 |  | -0.22457 | 3.7355 | 16.2349 | 22.9549 | 13.3826 | 0.36196 | 22.0645 | 502.3117 | 74.1667 | 576.4784 | 915.2171 | 1
298 | 14 | 584 | 90 |  | -0.22457 | 3.7355 | 16.2349 | 22.9549 | 14.3826 | 0.62376 | 17.6167 | 376.2437 | 75 | 451.2437 | 716.3945 | 1
298 | 15 | 444 | 80 |  | -0.22457 | 3.7355 | 16.2349 | 22.9549 | 15.3826 | 0.88556 | 11.3587 | 214.6267 | 66.6667 | 281.2934 | 446.5814 | 0
298 | 16 | 202 | 52 |  | -0.22457 | 3.7355 | 16.2349 | 22.9549 | 16.3826 | 1.1474 | 3.7707 | 57.3155 | 43.3333 | 100.6488 | 159.7901 | 0
298 | 17 | 0 | 9 |  | -0.22457 | 3.7355 | 16.2349 | 22.9549 | 17.3826 | 1.4092 | -4.7021 | 0 | 7.5 | 7.5 | 11.907 | 0
298 | 18 | 0 | 0 |  | -0.22457 | 3.7355 | 16.2349 | 22.9549 | 18.3826 | 1.671 | -13.6621 | 0 | 0 | 0 | 0 | 0
298 | 19 | 0 | 0 |  | -0.22457 | 3.7355 | 16.2349 | 22.9549 | 19.3826 | 1.9328 | -22.7299 | 0 | 0 | 0 | 0 | 0
298 | 20 | 0 | 0 |  | -0.22457 | 3.7355 | 16.2349 | 22.9549 | 20.3826 | 2.1946 | -31.4878 | 0 | 0 | 0 | 0 | 0
298 | 21 | 0 | 0 |  | -0.22457 | 3.7355 | 16.2349 | 22.9549 | 21.3826 | 2.4564 | -39.3993 | 0 | 0 | 0 | 0 | 0
298 | 22 | 0 | 0 |  | -0.22457 | 3.7355 | 16.2349 | 22.9549 | 22.3826 | 2.7182 | -45.7201 | 0 | 0 | 0 | 0 | 0
298 | 23 | 0 | 0 |  | -0.22457 | 3.7355 | 16.2349 | 22.9549 | 23.3826 | 2.98 | -49.5024 | 0 | 0 | 0 | 0 | 0
298 | 24 | 0 | 0 |  | -0.22457 | 3.7355 | 16.2349 | 22.9549 | 24.3826 | 3.2418 | -49.9226 | 0 | 0 | 0 | 0 | 0
299 | 1 | 0 | 0 |  | -0.23036 | 3.7527 | 16.3042 | 23.0242 | 1.3837 | -2.7793 | -47.1828 | 0 | 0 | 0 | 0 | 0
299 | 2 | 0 | 0 |  | -0.23036 | 3.7527 | 16.3042 | 23.0242 | 2.3837 | -2.5175 | -41.3441 | 0 | 0 | 0 | 0 | 0
299 | 3 | 0 | 0 |  | -0.23036 | 3.7527 | 16.3042 | 23.0242 | 3.3837 | -2.2557 | -33.71 | 0 | 0 | 0 | 0 | 0
299 | 4 | 0 | 0 |  | -0.23036 | 3.7527 | 16.3042 | 23.0242 | 4.3837 | -1.9939 | -25.0845 | 0 | 0 | 0 | 0 | 0
299 | 5 | 0 | 0 |  | -0.23036 | 3.7527 | 16.3042 | 23.0242 | 5.3837 | -1.7321 | -16.0455 | 0 | 0 | 0 | 0 | 0
299 | 6 | 0 | 0 |  | -0.23036 | 3.7527 | 16.3042 | 23.0242 | 6.3837 | -1.4703 | -7.0298 | 0 | 0 | 0 | 0 | 0
299 | 7 | 0 | 2 |  | -0.23036 | 3.7527 | 16.3042 | 23.0242 | 7.3837 | -1.2085 | 1.5813 | 0 | 1.6667 | 1.6667 | 2.646 | 0
299 | 8 | 59 | 41 |  | -0.23036 | 3.7527 | 16.3042 | 23.0242 | 8.3837 | -0.94674 | 9.3997 | 25.7751 | 34.1667 | 59.9418 | 95.1636 | 0
299 | 9 | 13 | 90 |  | -0.23036 | 3.7527 | 16.3042 | 23.0242 | 9.3837 | -0.68494 | 15.9943 | 7.8995 | 75 | 82.8995 | 131.6113 | 1
299 | 10 | 19 | 146 |  | -0.23036 | 3.7527 | 16.3042 | 23.0242 | 10.3837 | -0.42314 | 20.8921 | 13.8896 | 121.6667 | 135.5563 | 215.2092 | 1
299 | 11 | 41 | 177 |  | -0.23036 | 3.7527 | 16.3042 | 23.0242 | 11.3837 | -0.16134 | 23.6408 | 32.7423 | 147.5 | 180.2423 | 286.1526 | 1
299 | 12 | 43 | 192 |  | -0.23036 | 3.7527 | 16.3042 | 23.0242 | 12.3837 | 0.10046 | 23.9344 | 34.6463 | 160 | 194.6463 | 309.0205 | 1
299 | 13 | 0 | 125 |  | -0.23036 | 3.7527 | 16.3042 | 23.0242 | 13.3837 | 0.36226 | 21.7377 | 0 | 104.1667 | 104.1667 | 165.375 | 1
299 | 14 | 0 | 103 |  | -0.23036 | 3.7527 | 16.3042 | 23.0242 | 14.3837 | 0.62406 | 17.3022 | 0 | 85.8333 | 85.8333 | 136.269 | 1
299 | 15 | 0 | 68 |  | -0.23036 | 3.7527 | 16.3042 | 23.0242 | 15.3837 | 0.88586 | 11.0592 | 0 | 56.6667 | 56.6667 | 89.964 | 0
299 | 16 | 0 | 43 |  | -0.23036 | 3.7527 | 16.3042 | 23.0242 | 16.3837 | 1.1477 | 3.485 | 0 | 35.8333 | 35.8333 | 56.889 | 0
299 | 17 | 0 | 3 |  | -0.23036 | 3.7527 | 16.3042 | 23.0242 | 17.3837 | 1.4095 | -4.9776 | 0 | 2.5 | 2.5 | 3.969 | 0
299 | 18 | 0 | 0 |  | -0.23036 | 3.7527 | 16.3042 | 23.0242 | 18.3837 | 1.6713 | -13.9327 | 0 | 0 | 0 | 0 | 0
299 | 19 | 0 | 0 |  | -0.23036 | 3.7527 | 16.3042 | 23.0242 | 19.3837 | 1.9331 | -23.0019 | 0 | 0 | 0 | 0 | 0
299 | 20 | 0 | 0 |  | -0.23036 | 3.7527 | 16.3042 | 23.0242 | 20.3837 | 2.1949 | -31.7685 | 0 | 0 | 0 | 0 | 0
299 | 21 | 0 | 0 |  | -0.23036 | 3.7527 | 16.3042 | 23.0242 | 21.3837 | 2.4567 | -39.6956 | 0 | 0 | 0 | 0 | 0
299 | 22 | 0 | 0 |  | -0.23036 | 3.7527 | 16.3042 | 23.0242 | 22.3837 | 2.7185 | -46.0361 | 0 | 0 | 0 | 0 | 0
299 | 23 | 0 | 0 |  | -0.23036 | 3.7527 | 16.3042 | 23.0242 | 23.3837 | 2.9803 | -49.8331 | 0 | 0 | 0 | 0 | 0
299 | 24 | 0 | 0 |  | -0.23036 | 3.7527 | 16.3042 | 23.0242 | 24.3837 | 3.2421 | -50.2515 | 0 | 0 | 0 | 0 | 0
300 | 1 | 0 | 0 |  | -0.2361 | 3.7699 | 16.3605 | 23.0805 | 1.3847 | -2.7791 | -47.4899 | 0 | 0 | 0 | 0 | 0
300 | 2 | 0 | 0 |  | -0.2361 | 3.7699 | 16.3605 | 23.0805 | 2.3847 | -2.5173 | -41.6269 | 0 | 0 | 0 | 0 | 0
300 | 3 | 0 | 0 |  | -0.2361 | 3.7699 | 16.3605 | 23.0805 | 3.3847 | -2.2555 | -33.9732 | 0 | 0 | 0 | 0 | 0
300 | 4 | 0 | 0 |  | -0.2361 | 3.7699 | 16.3605 | 23.0805 | 4.3847 | -1.9937 | -25.3361 | 0 | 0 | 0 | 0 | 0
300 | 5 | 0 | 0 |  | -0.2361 | 3.7699 | 16.3605 | 23.0805 | 5.3847 | -1.7319 | -16.2938 | 0 | 0 | 0 | 0 | 0
300 | 6 | 0 | 0 |  | -0.2361 | 3.7699 | 16.3605 | 23.0805 | 6.3847 | -1.4701 | -7.2822 | 0 | 0 | 0 | 0 | 0
300 | 7 | 0 | 1 |  | -0.2361 | 3.7699 | 16.3605 | 23.0805 | 7.3847 | -1.2083 | 1.3186 | 0 | 0.83333 | 0.83333 | 1.323 | 0
300 | 8 | 0 | 17 |  | -0.2361 | 3.7699 | 16.3605 | 23.0805 | 8.3847 | -0.94649 | 9.1218 | 0 | 14.1667 | 14.1667 | 22.491 | 0
300 | 9 | 0 | 56 |  | -0.2361 | 3.7699 | 16.3605 | 23.0805 | 9.3847 | -0.68469 | 15.6986 | 0 | 46.6667 | 46.6667 | 74.088 | 1
300 | 10 | 0 | 93 |  | -0.2361 | 3.7699 | 16.3605 | 23.0805 | 10.3847 | -0.42289 | 20.5792 | 0 | 77.5 | 77.5 | 123.039 | 1
300 | 11 | 0 | 118 |  | -0.2361 | 3.7699 | 16.3605 | 23.0805 | 11.3847 | -0.16109 | 23.3157 | 0 | 98.3333 | 98.3333 | 156.114 | 1
300 | 12 | 65 | 178 |  | -0.2361 | 3.7699 | 16.3605 | 23.0805 | 12.3847 | 0.10071 | 23.6058 | 52.1521 | 148.3333 | 200.4854 | 318.2907 | 1
300 | 13 | 0 | 122 |  | -0.2361 | 3.7699 | 16.3605 | 23.0805 | 13.3847 | 0.36251 | 21.415 | 0 | 101.6667 | 101.6667 | 161.406 | 1
300 | 14 | 0 | 100 |  | -0.2361 | 3.7699 | 16.3605 | 23.0805 | 14.3847 | 0.62431 | 16.9922 | 0 | 83.3333 | 83.3333 | 132.3 | 1
300 | 15 | 0 | 65 |  | -0.2361 | 3.7699 | 16.3605 | 23.0805 | 15.3847 | 0.88611 | 10.7642 | 0 | 54.1667 | 54.1667 | 85.995 | 0
300 | 16 | 0 | 26 |  | -0.2361 | 3.7699 | 16.3605 | 23.0805 | 16.3847 | 1.1479 | 3.2039 | 0 | 21.6667 | 21.6667 | 34.398 | 0
300 | 17 | 0 | 2 |  | -0.2361 | 3.7699 | 16.3605 | 23.0805 | 17.3847 | 1.4097 | -5.2484 | 0 | 1.6667 | 1.6667 | 2.646 | 0
300 | 18 | 0 | 0 |  | -0.2361 | 3.7699 | 16.3605 | 23.0805 | 18.3847 | 1.6715 | -14.1984 | 0 | 0 | 0 | 0 | 0
300 | 19 | 0 | 0 |  | -0.2361 | 3.7699 | 16.3605 | 23.0805 | 19.3847 | 1.9333 | -23.269 | 0 | 0 | 0 | 0 | 0
300 | 20 | 0 | 0 |  | -0.2361 | 3.7699 | 16.3605 | 23.0805 | 20.3847 | 2.1951 | -32.044 | 0 | 0 | 0 | 0 | 0
300 | 21 | 0 | 0 |  | -0.2361 | 3.7699 | 16.3605 | 23.0805 | 21.3847 | 2.4569 | -39.9869 | 0 | 0 | 0 | 0 | 0
300 | 22 | 0 | 0 |  | -0.2361 | 3.7699 | 16.3605 | 23.0805 | 22.3847 | 2.7187 | -46.3475 | 0 | 0 | 0 | 0 | 0
300 | 23 | 0 | 0 |  | -0.2361 | 3.7699 | 16.3605 | 23.0805 | 23.3847 | 2.9805 | -50.1598 | 0 | 0 | 0 | 0 | 0
300 | 24 | 0 | 0 |  | -0.2361 | 3.7699 | 16.3605 | 23.0805 | 24.3847 | 3.2423 | -50.577 | 0 | 0 | 0 | 0 | 0
301 | 1 | 0 | 0 |  | -0.24176 | 3.7871 | 16.4036 | 23.1236 | 1.3854 | -2.7789 | -47.7943 | 0 | 0 | 0 | 0 | 0
301 | 2 | 0 | 0 |  | -0.24176 | 3.7871 | 16.4036 | 23.1236 | 2.3854 | -2.5171 | -41.9077 | 0 | 0 | 0 | 0 | 0
301 | 3 | 0 | 0 |  | -0.24176 | 3.7871 | 16.4036 | 23.1236 | 3.3854 | -2.2553 | -34.2347 | 0 | 0 | 0 | 0 | 0
301 | 4 | 0 | 0 |  | -0.24176 | 3.7871 | 16.4036 | 23.1236 | 4.3854 | -1.9935 | -25.5864 | 0 | 0 | 0 | 0 | 0
301 | 5 | 0 | 0 |  | -0.24176 | 3.7871 | 16.4036 | 23.1236 | 5.3854 | -1.7317 | -16.5411 | 0 | 0 | 0 | 0 | 0
301 | 6 | 0 | 0 |  | -0.24176 | 3.7871 | 16.4036 | 23.1236 | 6.3854 | -1.4699 | -7.5336 | 0 | 0 | 0 | 0 | 0
301 | 7 | 0 | 1 |  | -0.24176 | 3.7871 | 16.4036 | 23.1236 | 7.3854 | -1.2081 | 1.057 | 0 | 0.83333 | 0.83333 | 1.323 | 0
301 | 8 | 0 | 16 |  | -0.24176 | 3.7871 | 16.4036 | 23.1236 | 8.3854 | -0.9463 | 8.8454 | 0 | 13.3333 | 13.3333 | 21.168 | 0
301 | 9 | 15 | 84 |  | -0.24176 | 3.7871 | 16.4036 | 23.1236 | 9.3854 | -0.6845 | 15.4048 | 9.0258 | 70 | 79.0258 | 125.4614 | 1
301 | 10 | 18 | 140 |  | -0.24176 | 3.7871 | 16.4036 | 23.1236 | 10.3854 | -0.4227 | 20.2689 | 13.0442 | 116.6667 | 129.7108 | 205.9289 | 1
301 | 11 | 182 | 170 |  | -0.24176 | 3.7871 | 16.4036 | 23.1236 | 11.3854 | -0.1609 | 22.9939 | 144.1353 | 141.6667 | 285.802 | 453.7393 | 1
301 | 12 | 67 | 176 |  | -0.24176 | 3.7871 | 16.4036 | 23.1236 | 12.3854 | 0.1009 | 23.2811 | 53.5309 | 146.6667 | 200.1975 | 317.8336 | 1
301 | 13 | 187 | 175 |  | -0.24176 | 3.7871 | 16.4036 | 23.1236 | 13.3854 | 0.3627 | 21.0966 | 139.3607 | 145.8333 | 285.194 | 452.774 | 1
301 | 14 | 107 | 167 |  | -0.24176 | 3.7871 | 16.4036 | 23.1236 | 14.3854 | 0.62449 | 16.6866 | 67.8853 | 139.1667 | 207.052 | 328.7158 | 1
301 | 15 | 236 | 93 |  | -0.24176 | 3.7871 | 16.4036 | 23.1236 | 15.3854 | 0.88629 | 10.4739 | 111.8907 | 77.5 | 189.3907 | 300.6766 | 0
301 | 16 | 58 | 51 |  | -0.24176 | 3.7871 | 16.4036 | 23.1236 | 16.3854 | 1.1481 | 2.9277 | 15.9606 | 42.5 | 58.4606 | 92.812 | 0
301 | 17 | 0 | 6 |  | -0.24176 | 3.7871 | 16.4036 | 23.1236 | 17.3854 | 1.4099 | -5.5142 | 0 | 5 | 5 | 7.938 | 0
301 | 18 | 0 | 0 |  | -0.24176 | 3.7871 | 16.4036 | 23.1236 | 18.3854 | 1.6717 | -14.459 | 0 | 0 | 0 | 0 | 0
301 | 19 | 0 | 0 |  | -0.24176 | 3.7871 | 16.4036 | 23.1236 | 19.3854 | 1.9335 | -23.5308 | 0 | 0 | 0 | 0 | 0
301 | 20 | 0 | 0 |  | -0.24176 | 3.7871 | 16.4036 | 23.1236 | 20.3854 | 2.1953 | -32.3144 | 0 | 0 | 0 | 0 | 0
301 | 21 | 0 | 0 |  | -0.24176 | 3.7871 | 16.4036 | 23.1236 | 21.3854 | 2.4571 | -40.2732 | 0 | 0 | 0 | 0 | 0
301 | 22 | 0 | 0 |  | -0.24176 | 3.7871 | 16.4036 | 23.1236 | 22.3854 | 2.7189 | -46.6541 | 0 | 0 | 0 | 0 | 0
301 | 23 | 0 | 0 |  | -0.24176 | 3.7871 | 16.4036 | 23.1236 | 23.3854 | 2.9807 | -50.4824 | 0 | 0 | 0 | 0 | 0
301 | 24 | 0 | 0 |  | -0.24176 | 3.7871 | 16.4036 | 23.1236 | 24.3854 | 3.2425 | -50.8993 | 0 | 0 | 0 | 0 | 0
302 | 1 | 0 | 0 |  | -0.24737 | 3.8043 | 16.4334 | 23.1534 | 1.3859 | -2.7788 | -48.096 | 0 | 0 | 0 | 0 | 0
302 | 2 | 0 | 0 |  | -0.24737 | 3.8043 | 16.4334 | 23.1534 | 2.3859 | -2.517 | -42.1863 | 0 | 0 | 0 | 0 | 0
302 | 3 | 0 | 0 |  | -0.24737 | 3.8043 | 16.4334 | 23.1534 | 3.3859 | -2.2552 | -34.4946 | 0 | 0 | 0 | 0 | 0
302 | 4 | 0 | 0 |  | -0.24737 | 3.8043 | 16.4334 | 23.1534 | 4.3859 | -1.9934 | -25.8354 | 0 | 0 | 0 | 0 | 0
302 | 5 | 0 | 0 |  | -0.24737 | 3.8043 | 16.4334 | 23.1534 | 5.3859 | -1.7316 | -16.7873 | 0 | 0 | 0 | 0 | 0
302 | 6 | 0 | 0 |  | -0.24737 | 3.8043 | 16.4334 | 23.1534 | 6.3859 | -1.4698 | -7.784 | 0 | 0 | 0 | 0 | 0
302 | 7 | 0 | 1 |  | -0.24737 | 3.8043 | 16.4334 | 23.1534 | 7.3859 | -1.208 | 0.79661 | 0 | 0.83333 | 0.83333 | 1.323 | 0
302 | 8 | 17 | 34 |  | -0.24737 | 3.8043 | 16.4334 | 23.1534 | 8.3859 | -0.94617 | 8.5705 | 7.2885 | 28.3333 | 35.6219 | 56.5533 | 0
302 | 9 | 104 | 86 |  | -0.24737 | 3.8043 | 16.4334 | 23.1534 | 9.3859 | -0.68437 | 15.1131 | 62.2679 | 71.6667 | 133.9345 | 212.6345 | 1
302 | 10 | 410 | 124 |  | -0.24737 | 3.8043 | 16.4334 | 23.1534 | 10.3859 | -0.42257 | 19.9613 | 295.809 | 103.3333 | 399.1424 | 633.6784 | 1
302 | 11 | 613 | 93 |  | -0.24737 | 3.8043 | 16.4334 | 23.1534 | 11.3859 | -0.16077 | 22.6754 | 483.4359 | 77.5 | 560.9359 | 890.5419 | 1
302 | 12 | 627 | 97 |  | -0.24737 | 3.8043 | 16.4334 | 23.1534 | 12.3859 | 0.10103 | 22.9603 | 498.8506 | 80.8333 | 579.6839 | 920.3061 | 1
302 | 13 | 607 | 96 |  | -0.24737 | 3.8043 | 16.4334 | 23.1534 | 13.3859 | 0.36283 | 20.7826 | 450.3556 | 80 | 530.3556 | 841.9925 | 1
302 | 14 | 526 | 95 |  | -0.24737 | 3.8043 | 16.4334 | 23.1534 | 14.3859 | 0.62462 | 16.3857 | 332.0442 | 79.1667 | 411.2109 | 652.8384 | 1
302 | 15 | 405 | 77 |  | -0.24737 | 3.8043 | 16.4334 | 23.1534 | 15.3859 | 0.88642 | 10.1884 | 190.8098 | 64.1667 | 254.9765 | 404.8007 | 0
302 | 16 | 85 | 44 |  | -0.24737 | 3.8043 | 16.4334 | 23.1534 | 16.3859 | 1.1482 | 2.6563 | 23.1597 | 36.6667 | 59.8264 | 94.9803 | 0
302 | 17 | 0 | 4 |  | -0.24737 | 3.8043 | 16.4334 | 23.1534 | 17.3859 | 1.41 | -5.7751 | 0 | 3.3333 | 3.3333 | 5.292 | 0
302 | 18 | 0 | 0 |  | -0.24737 | 3.8043 | 16.4334 | 23.1534 | 18.3859 | 1.6718 | -14.7146 | 0 | 0 | 0 | 0 | 0
302 | 19 | 0 | 0 |  | -0.24737 | 3.8043 | 16.4334 | 23.1534 | 19.3859 | 1.9336 | -23.7875 | 0 | 0 | 0 | 0 | 0
302 | 20 | 0 | 0 |  | -0.24737 | 3.8043 | 16.4334 | 23.1534 | 20.3859 | 2.1954 | -32.5795 | 0 | 0 | 0 | 0 | 0
302 | 21 | 0 | 0 |  | -0.24737 | 3.8043 | 16.4334 | 23.1534 | 21.3859 | 2.4572 | -40.5542 | 0 | 0 | 0 | 0 | 0
302 | 22 | 0 | 0 |  | -0.24737 | 3.8043 | 16.4334 | 23.1534 | 22.3859 | 2.719 | -46.9558 | 0 | 0 | 0 | 0 | 0
302 | 23 | 0 | 0 |  | -0.24737 | 3.8043 | 16.4334 | 23.1534 | 23.3859 | 2.9808 | -50.8007 | 0 | 0 | 0 | 0 | 0
302 | 24 | 0 | 0 |  | -0.24737 | 3.8043 | 16.4334 | 23.1534 | 24.3859 | 3.2426 | -51.2181 | 0 | 0 | 0 | 0 | 0
303 | 1 | 0 | 0 |  | -0.2529 | 3.8216 | 16.4498 | 23.1698 | 1.3862 | -2.7787 | -48.3949 | 0 | 0 | 0 | 0 | 0
303 | 2 | 0 | 0 |  | -0.2529 | 3.8216 | 16.4498 | 23.1698 | 2.3862 | -2.5169 | -42.4628 | 0 | 0 | 0 | 0 | 0
303 | 3 | 0 | 0 |  | -0.2529 | 3.8216 | 16.4498 | 23.1698 | 3.3862 | -2.2551 | -34.7527 | 0 | 0 | 0 | 0 | 0
303 | 4 | 0 | 0 |  | -0.2529 | 3.8216 | 16.4498 | 23.1698 | 4.3862 | -1.9933 | -26.0831 | 0 | 0 | 0 | 0 | 0
303 | 5 | 0 | 0 |  | -0.2529 | 3.8216 | 16.4498 | 23.1698 | 5.3862 | -1.7315 | -17.0323 | 0 | 0 | 0 | 0 | 0
303 | 6 | 0 | 0 |  | -0.2529 | 3.8216 | 16.4498 | 23.1698 | 6.3862 | -1.4697 | -8.0331 | 0 | 0 | 0 | 0 | 0
303 | 7 | 0 | 1 |  | -0.2529 | 3.8216 | 16.4498 | 23.1698 | 7.3862 | -1.2079 | 0.53756 | 0 | 0.83333 | 0.83333 | 1.323 | 0
303 | 8 | 0 | 28 |  | -0.2529 | 3.8216 | 16.4498 | 23.1698 | 8.3862 | -0.9461 | 8.2973 | 0 | 23.3333 | 23.3333 | 37.044 | 0
303 | 9 | 79 | 88 |  | -0.2529 | 3.8216 | 16.4498 | 23.1698 | 9.3862 | -0.6843 | 14.8235 | 47.062 | 73.3333 | 120.3954 | 191.1397 | 1
303 | 10 | 21 | 133 |  | -0.2529 | 3.8216 | 16.4498 | 23.1698 | 10.3862 | -0.4225 | 19.6564 | 15.0841 | 110.8333 | 125.9174 | 199.9065 | 1
303 | 11 | 38 | 165 |  | -0.2529 | 3.8216 | 16.4498 | 23.1698 | 11.3862 | -0.1607 | 22.3604 | 29.8427 | 137.5 | 167.3427 | 265.6732 | 1
303 | 12 | 0 | 123 |  | -0.2529 | 3.8216 | 16.4498 | 23.1698 | 12.3862 | 0.1011 | 22.6436 | 0 | 102.5 | 102.5 | 162.729 | 1
303 | 13 | 0 | 116 |  | -0.2529 | 3.8216 | 16.4498 | 23.1698 | 13.3862 | 0.3629 | 20.473 | 0 | 96.6667 | 96.6667 | 153.468 | 1
303 | 14 | 0 | 94 |  | -0.2529 | 3.8216 | 16.4498 | 23.1698 | 14.3862 | 0.6247 | 16.0894 | 0 | 78.3333 | 78.3333 | 124.362 | 1
303 | 15 | 0 | 60 |  | -0.2529 | 3.8216 | 16.4498 | 23.1698 | 15.3862 | 0.8865 | 9.9077 | 0 | 50 | 50 | 79.38 | 0
303 | 16 | 0 | 22 |  | -0.2529 | 3.8216 | 16.4498 | 23.1698 | 16.3862 | 1.1483 | 2.39 | 0 | 18.3333 | 18.3333 | 29.106 | 0
303 | 17 | 0 | 2 |  | -0.2529 | 3.8216 | 16.4498 | 23.1698 | 17.3862 | 1.4101 | -6.0308 | 0 | 1.6667 | 1.6667 | 2.646 | 0
303 | 18 | 0 | 0 |  | -0.2529 | 3.8216 | 16.4498 | 23.1698 | 18.3862 | 1.6719 | -14.9649 | 0 | 0 | 0 | 0 | 0
303 | 19 | 0 | 0 |  | -0.2529 | 3.8216 | 16.4498 | 23.1698 | 19.3862 | 1.9337 | -24.0388 | 0 | 0 | 0 | 0 | 0
303 | 20 | 0 | 0 |  | -0.2529 | 3.8216 | 16.4498 | 23.1698 | 20.3862 | 2.1955 | -32.8392 | 0 | 0 | 0 | 0 | 0
303 | 21 | 0 | 0 |  | -0.2529 | 3.8216 | 16.4498 | 23.1698 | 21.3862 | 2.4573 | -40.8299 | 0 | 0 | 0 | 0 | 0
303 | 22 | 0 | 0 |  | -0.2529 | 3.8216 | 16.4498 | 23.1698 | 22.3862 | 2.7191 | -47.2525 | 0 | 0 | 0 | 0 | 0
303 | 23 | 0 | 0 |  | -0.2529 | 3.8216 | 16.4498 | 23.1698 | 23.3862 | 2.9809 | -51.1147 | 0 | 0 | 0 | 0 | 0
303 | 24 | 0 | 0 |  | -0.2529 | 3.8216 | 16.4498 | 23.1698 | 24.3862 | 3.2427 | -51.5334 | 0 | 0 | 0 | 0 | 0
304 | 1 | 0 | 0 |  | -0.25837 | 3.8388 | 16.4528 | 23.1728 | 1.3862 | -2.7787 | -48.6909 | 0 | 0 | 0 | 0 | 0
304 | 2 | 0 | 0 |  | -0.25837 | 3.8388 | 16.4528 | 23.1728 | 2.3862 | -2.5169 | -42.7369 | 0 | 0 | 0 | 0 | 0
304 | 3 | 0 | 0 |  | -0.25837 | 3.8388 | 16.4528 | 23.1728 | 3.3862 | -2.2551 | -35.0091 | 0 | 0 | 0 | 0 | 0
304 | 4 | 0 | 0 |  | -0.25837 | 3.8388 | 16.4528 | 23.1728 | 4.3862 | -1.9933 | -26.3293 | 0 | 0 | 0 | 0 | 0
304 | 5 | 0 | 0 |  | -0.25837 | 3.8388 | 16.4528 | 23.1728 | 5.3862 | -1.7315 | -17.276 | 0 | 0 | 0 | 0 | 0
304 | 6 | 0 | 0 |  | -0.25837 | 3.8388 | 16.4528 | 23.1728 | 6.3862 | -1.4697 | -8.2811 | 0 | 0 | 0 | 0 | 0
304 | 7 | 0 | 0 |  | -0.25837 | 3.8388 | 16.4528 | 23.1728 | 7.3862 | -1.2079 | 0.27989 | 0 | 0 | 0 | 0 | 0
304 | 8 | 0 | 12 |  | -0.25837 | 3.8388 | 16.4528 | 23.1728 | 8.3862 | -0.94609 | 8.0258 | 0 | 10 | 10 | 15.876 | 0
304 | 9 | 0 | 50 |  | -0.25837 | 3.8388 | 16.4528 | 23.1728 | 9.3862 | -0.68429 | 14.5362 | 0 | 41.6667 | 41.6667 | 66.15 | 1
304 | 10 | 0 | 85 |  | -0.25837 | 3.8388 | 16.4528 | 23.1728 | 10.3862 | -0.42249 | 19.3544 | 0 | 70.8333 | 70.8333 | 112.455 | 1
304 | 11 | 0 | 111 |  | -0.25837 | 3.8388 | 16.4528 | 23.1728 | 11.3862 | -0.16069 | 22.0489 | 0 | 92.5 | 92.5 | 146.853 | 1
304 | 12 | 0 | 121 |  | -0.25837 | 3.8388 | 16.4528 | 23.1728 | 12.3862 | 0.10111 | 22.331 | 0 | 100.8333 | 100.8333 | 160.083 | 1
304 | 13 | 0 | 114 |  | -0.25837 | 3.8388 | 16.4528 | 23.1728 | 13.3862 | 0.36291 | 20.1679 | 0 | 95 | 95 | 150.822 | 1
304 | 14 | 0 | 92 |  | -0.25837 | 3.8388 | 16.4528 | 23.1728 | 14.3862 | 0.62471 | 15.798 | 0 | 76.6667 | 76.6667 | 121.716 | 1
304 | 15 | 0 | 58 |  | -0.25837 | 3.8388 | 16.4528 | 23.1728 | 15.3862 | 0.88651 | 9.632 | 0 | 48.3333 | 48.3333 | 76.734 | 0
304 | 16 | 0 | 20 |  | -0.25837 | 3.8388 | 16.4528 | 23.1728 | 16.3862 | 1.1483 | 2.1287 | 0 | 16.6667 | 16.6667 | 26.46 | 0
304 | 17 | 0 | 1 |  | -0.25837 | 3.8388 | 16.4528 | 23.1728 | 17.3862 | 1.4101 | -6.2814 | 0 | 0.83333 | 0.83333 | 1.323 | 0
304 | 18 | 0 | 0 |  | -0.25837 | 3.8388 | 16.4528 | 23.1728 | 18.3862 | 1.6719 | -15.21 | 0 | 0 | 0 | 0 | 0
304 | 19 | 0 | 0 |  | -0.25837 | 3.8388 | 16.4528 | 23.1728 | 19.3862 | 1.9337 | -24.2847 | 0 | 0 | 0 | 0 | 0
304 | 20 | 0 | 0 |  | -0.25837 | 3.8388 | 16.4528 | 23.1728 | 20.3862 | 2.1955 | -33.0934 | 0 | 0 | 0 | 0 | 0
304 | 21 | 0 | 0 |  | -0.25837 | 3.8388 | 16.4528 | 23.1728 | 21.3862 | 2.4573 | -41.1002 | 0 | 0 | 0 | 0 | 0
304 | 22 | 0 | 0 |  | -0.25837 | 3.8388 | 16.4528 | 23.1728 | 22.3862 | 2.7191 | -47.5441 | 0 | 0 | 0 | 0 | 0
304 | 23 | 0 | 0 |  | -0.25837 | 3.8388 | 16.4528 | 23.1728 | 23.3862 | 2.9809 | -51.4243 | 0 | 0 | 0 | 0 | 0
304 | 24 | 0 | 0 |  | -0.25837 | 3.8388 | 16.4528 | 23.1728 | 24.3862 | 3.2427 | -51.845 | 0 | 0 | 0 | 0 | 0
305 | 1 | 0 | 0 |  | -0.26377 | 3.856 | 16.4422 | 23.1622 | 1.386 | -2.7787 | -48.9839 | 0 | 0 | 0 | 0 | 0
305 | 2 | 0 | 0 |  | -0.26377 | 3.856 | 16.4422 | 23.1622 | 2.386 | -2.5169 | -43.0088 | 0 | 0 | 0 | 0 | 0
305 | 3 | 0 | 0 |  | -0.26377 | 3.856 | 16.4422 | 23.1622 | 3.386 | -2.2551 | -35.2637 | 0 | 0 | 0 | 0 | 0
305 | 4 | 0 | 0 |  | -0.26377 | 3.856 | 16.4422 | 23.1622 | 4.386 | -1.9933 | -26.5741 | 0 | 0 | 0 | 0 | 0
305 | 5 | 0 | 0 |  | -0.26377 | 3.856 | 16.4422 | 23.1622 | 5.386 | -1.7315 | -17.5185 | 0 | 0 | 0 | 0 | 0
305 | 6 | 0 | 0 |  | -0.26377 | 3.856 | 16.4422 | 23.1622 | 6.386 | -1.4697 | -8.5277 | 0 | 0 | 0 | 0 | 0
305 | 7 | 0 | 0 |  | -0.26377 | 3.856 | 16.4422 | 23.1622 | 7.386 | -1.2079 | 0.023707 | 0 | 0 | 0 | 0 | 0
305 | 8 | 0 | 12 |  | -0.26377 | 3.856 | 16.4422 | 23.1622 | 8.386 | -0.94613 | 7.7561 | 0 | 10 | 10 | 15.876 | 0
305 | 9 | 0 | 48 |  | -0.26377 | 3.856 | 16.4422 | 23.1622 | 9.386 | -0.68433 | 14.2512 | 0 | 40 | 40 | 63.504 | 1
305 | 10 | 0 | 84 |  | -0.26377 | 3.856 | 16.4422 | 23.1622 | 10.386 | -0.42253 | 19.0555 | 0 | 70 | 70 | 111.132 | 1
305 | 11 | 0 | 109 |  | -0.26377 | 3.856 | 16.4422 | 23.1622 | 11.386 | -0.16074 | 21.7412 | 0 | 90.8333 | 90.8333 | 144.207 | 1
305 | 12 | 68 | 163 |  | -0.26377 | 3.856 | 16.4422 | 23.1622 | 12.386 | 0.10106 | 22.0226 | 53.4268 | 135.8333 | 189.2601 | 300.4693 | 1
305 | 13 | 39 | 165 |  | -0.26377 | 3.856 | 16.4422 | 23.1622 | 13.386 | 0.36286 | 19.8675 | 28.557 | 137.5 | 166.057 | 263.6321 | 1
305 | 14 | 28 | 136 |  | -0.26377 | 3.856 | 16.4422 | 23.1622 | 14.386 | 0.62466 | 15.5115 | 17.4166 | 113.3333 | 130.7499 | 207.5786 | 1
305 | 15 | 8 | 89 |  | -0.26377 | 3.856 | 16.4422 | 23.1622 | 15.386 | 0.88646 | 9.3614 | 3.7006 | 74.1667 | 77.8672 | 123.622 | 0
305 | 16 | 0 | 31 |  | -0.26377 | 3.856 | 16.4422 | 23.1622 | 16.386 | 1.1483 | 1.8725 | 0 | 25.8333 | 25.8333 | 41.013 | 0
305 | 17 | 0 | 1 |  | -0.26377 | 3.856 | 16.4422 | 23.1622 | 17.386 | 1.4101 | -6.5267 | 0 | 0.83333 | 0.83333 | 1.323 | 0
305 | 18 | 0 | 0 |  | -0.26377 | 3.856 | 16.4422 | 23.1622 | 18.386 | 1.6719 | -15.4497 | 0 | 0 | 0 | 0 | 0
305 | 19 | 0 | 0 |  | -0.26377 | 3.856 | 16.4422 | 23.1622 | 19.386 | 1.9337 | -24.5252 | 0 | 0 | 0 | 0 | 0
305 | 20 | 0 | 0 |  | -0.26377 | 3.856 | 16.4422 | 23.1622 | 20.386 | 2.1955 | -33.342 | 0 | 0 | 0 | 0 | 0
305 | 21 | 0 | 0 |  | -0.26377 | 3.856 | 16.4422 | 23.1622 | 21.386 | 2.4573 | -41.3649 | 0 | 0 | 0 | 0 | 0
305 | 22 | 0 | 0 |  | -0.26377 | 3.856 | 16.4422 | 23.1622 | 22.386 | 2.7191 | -47.8305 | 0 | 0 | 0 | 0 | 0
305 | 23 | 0 | 0 |  | -0.26377 | 3.856 | 16.4422 | 23.1622 | 23.386 | 2.9809 | -51.7293 | 0 | 0 | 0 | 0 | 0
305 | 24 | 0 | 0 |  | -0.26377 | 3.856 | 16.4422 | 23.1622 | 24.386 | 3.2427 | -52.1529 | 0 | 0 | 0 | 0 | 0
306 | 1 | 0 | 0 |  | -0.26909 | 3.8732 | 16.4181 | 23.1381 | 1.3856 | -2.7788 | -49.2739 | 0 | 0 | 0 | 0 | 0
306 | 2 | 0 | 0 |  | -0.26909 | 3.8732 | 16.4181 | 23.1381 | 2.3856 | -2.517 | -43.2782 | 0 | 0 | 0 | 0 | 0
306 | 3 | 0 | 0 |  | -0.26909 | 3.8732 | 16.4181 | 23.1381 | 3.3856 | -2.2552 | -35.5163 | 0 | 0 | 0 | 0 | 0
306 | 4 | 0 | 0 |  | -0.26909 | 3.8732 | 16.4181 | 23.1381 | 4.3856 | -1.9934 | -26.8173 | 0 | 0 | 0 | 0 | 0
306 | 5 | 0 | 0 |  | -0.26909 | 3.8732 | 16.4181 | 23.1381 | 5.3856 | -1.7316 | -17.7595 | 0 | 0 | 0 | 0 | 0
306 | 6 | 0 | 0 |  | -0.26909 | 3.8732 | 16.4181 | 23.1381 | 6.3856 | -1.4698 | -8.7729 | 0 | 0 | 0 | 0 | 0
306 | 7 | 0 | 0 |  | -0.26909 | 3.8732 | 16.4181 | 23.1381 | 7.3856 | -1.208 | -0.23092 | 0 | 0 | 0 | 0 | 0
306 | 8 | 0 | 11 |  | -0.26909 | 3.8732 | 16.4181 | 23.1381 | 8.3856 | -0.94624 | 7.4884 | 0 | 9.1667 | 9.1667 | 14.553 | 0
306 | 9 | 0 | 47 |  | -0.26909 | 3.8732 | 16.4181 | 23.1381 | 9.3856 | -0.68444 | 13.9686 | 0 | 39.1667 | 39.1667 | 62.181 | 1
306 | 10 | 0 | 83 |  | -0.26909 | 3.8732 | 16.4181 | 23.1381 | 10.3856 | -0.42264 | 18.7596 | 0 | 69.1667 | 69.1667 | 109.809 | 1
306 | 11 | 172 | 233 |  | -0.26909 | 3.8732 | 16.4181 | 23.1381 | 11.3856 | -0.16084 | 21.4372 | 133.3823 | 194.1667 | 327.549 | 520.0168 | 1
306 | 12 | 0 | 117 |  | -0.26909 | 3.8732 | 16.4181 | 23.1381 | 12.3856 | 0.10096 | 21.7186 | 0 | 97.5 | 97.5 | 154.791 | 1
306 | 13 | 0 | 111 |  | -0.26909 | 3.8732 | 16.4181 | 23.1381 | 13.3856 | 0.36276 | 19.5719 | 0 | 92.5 | 92.5 | 146.853 | 1
306 | 14 | 0 | 89 |  | -0.26909 | 3.8732 | 16.4181 | 23.1381 | 14.3856 | 0.62456 | 15.2299 | 0 | 74.1667 | 74.1667 | 117.747 | 1
306 | 15 | 0 | 55 |  | -0.26909 | 3.8732 | 16.4181 | 23.1381 | 15.3856 | 0.88636 | 9.0958 | 0 | 45.8333 | 45.8333 | 72.765 | 0
306 | 16 | 0 | 18 |  | -0.26909 | 3.8732 | 16.4181 | 23.1381 | 16.3856 | 1.1482 | 1.6216 | 0 | 15 | 15 | 23.814 | 0
306 | 17 | 0 | 1 |  | -0.26909 | 3.8732 | 16.4181 | 23.1381 | 17.3856 | 1.41 | -6.7667 | 0 | 0.83333 | 0.83333 | 1.323 | 0
306 | 18 | 0 | 0 |  | -0.26909 | 3.8732 | 16.4181 | 23.1381 | 18.3856 | 1.6718 | -15.6839 | 0 | 0 | 0 | 0 | 0
306 | 19 | 0 | 0 |  | -0.26909 | 3.8732 | 16.4181 | 23.1381 | 19.3856 | 1.9336 | -24.76 | 0 | 0 | 0 | 0 | 0
306 | 20 | 0 | 0 |  | -0.26909 | 3.8732 | 16.4181 | 23.1381 | 20.3856 | 2.1954 | -33.585 | 0 | 0 | 0 | 0 | 0
306 | 21 | 0 | 0 |  | -0.26909 | 3.8732 | 16.4181 | 23.1381 | 21.3856 | 2.4572 | -41.624 | 0 | 0 | 0 | 0 | 0
306 | 22 | 0 | 0 |  | -0.26909 | 3.8732 | 16.4181 | 23.1381 | 22.3856 | 2.719 | -48.1116 | 0 | 0 | 0 | 0 | 0
306 | 23 | 0 | 0 |  | -0.26909 | 3.8732 | 16.4181 | 23.1381 | 23.3856 | 2.9808 | -52.0297 | 0 | 0 | 0 | 0 | 0
306 | 24 | 0 | 0 |  | -0.26909 | 3.8732 | 16.4181 | 23.1381 | 24.3856 | 3.2426 | -52.457 | 0 | 0 | 0 | 0 | 0
307 | 1 | 0 | 0 |  | -0.27434 | 3.8904 | 16.3804 | 23.1004 | 1.385 | -2.779 | -49.5609 | 0 | 0 | 0 | 0 | 0
307 | 2 | 0 | 0 |  | -0.27434 | 3.8904 | 16.3804 | 23.1004 | 2.385 | -2.5172 | -43.5452 | 0 | 0 | 0 | 0 | 0
307 | 3 | 0 | 0 |  | -0.27434 | 3.8904 | 16.3804 | 23.1004 | 3.385 | -2.2554 | -35.7671 | 0 | 0 | 0 | 0 | 0
307 | 4 | 0 | 0 |  | -0.27434 | 3.8904 | 16.3804 | 23.1004 | 4.385 | -1.9936 | -27.0589 | 0 | 0 | 0 | 0 | 0
307 | 5 | 0 | 0 |  | -0.27434 | 3.8904 | 16.3804 | 23.1004 | 5.385 | -1.7318 | -17.9991 | 0 | 0 | 0 | 0 | 0
307 | 6 | 0 | 0 |  | -0.27434 | 3.8904 | 16.3804 | 23.1004 | 6.385 | -1.47 | -9.0167 | 0 | 0 | 0 | 0 | 0
307 | 7 | 0 | 0 |  | -0.27434 | 3.8904 | 16.3804 | 23.1004 | 7.385 | -1.2082 | -0.48389 | 0 | 0 | 0 | 0 | 0
307 | 8 | 0 | 11 |  | -0.27434 | 3.8904 | 16.3804 | 23.1004 | 8.385 | -0.9464 | 7.2227 | 0 | 9.1667 | 9.1667 | 14.553 | 0
307 | 9 | 0 | 45 |  | -0.27434 | 3.8904 | 16.3804 | 23.1004 | 9.385 | -0.6846 | 13.6887 | 0 | 37.5 | 37.5 | 59.535 | 1
307 | 10 | 0 | 80 |  | -0.27434 | 3.8904 | 16.3804 | 23.1004 | 10.385 | -0.4228 | 18.4669 | 0 | 66.6667 | 66.6667 | 105.84 | 1
307 | 11 | 0 | 105 |  | -0.27434 | 3.8904 | 16.3804 | 23.1004 | 11.385 | -0.161 | 21.137 | 0 | 87.5 | 87.5 | 138.915 | 1
307 | 12 | 67 | 158 |  | -0.27434 | 3.8904 | 16.3804 | 23.1004 | 12.385 | 0.10079 | 21.419 | 52.2065 | 131.6667 | 183.8731 | 291.917 | 1
307 | 13 | 38 | 160 |  | -0.27434 | 3.8904 | 16.3804 | 23.1004 | 13.385 | 0.36259 | 19.281 | 27.5865 | 133.3333 | 160.9198 | 255.4763 | 1
307 | 14 | 27 | 131 |  | -0.27434 | 3.8904 | 16.3804 | 23.1004 | 14.385 | 0.62439 | 14.9534 | 16.6354 | 109.1667 | 125.8021 | 199.7234 | 1
307 | 15 | 7 | 84 |  | -0.27434 | 3.8904 | 16.3804 | 23.1004 | 15.385 | 0.88619 | 8.8355 | 3.2003 | 70 | 73.2003 | 116.2128 | 0
307 | 16 | 0 | 27 |  | -0.27434 | 3.8904 | 16.3804 | 23.1004 | 16.385 | 1.148 | 1.376 | 0 | 22.5 | 22.5 | 35.721 | 0
307 | 17 | 0 | 1 |  | -0.27434 | 3.8904 | 16.3804 | 23.1004 | 17.385 | 1.4098 | -7.0012 | 0 | 0.83333 | 0.83333 | 1.323 | 0
307 | 18 | 0 | 0 |  | -0.27434 | 3.8904 | 16.3804 | 23.1004 | 18.385 | 1.6716 | -15.9126 | 0 | 0 | 0 | 0 | 0
307 | 19 | 0 | 0 |  | -0.27434 | 3.8904 | 16.3804 | 23.1004 | 19.385 | 1.9334 | -24.9892 | 0 | 0 | 0 | 0 | 0
307 | 20 | 0 | 0 |  | -0.27434 | 3.8904 | 16.3804 | 23.1004 | 20.385 | 2.1952 | -33.8223 | 0 | 0 | 0 | 0 | 0
307 | 21 | 0 | 0 |  | -0.27434 | 3.8904 | 16.3804 | 23.1004 | 21.385 | 2.457 | -41.8774 | 0 | 0 | 0 | 0 | 0
307 | 22 | 0 | 0 |  | -0.27434 | 3.8904 | 16.3804 | 23.1004 | 22.385 | 2.7188 | -48.3873 | 0 | 0 | 0 | 0 | 0
307 | 23 | 0 | 0 |  | -0.27434 | 3.8904 | 16.3804 | 23.1004 | 23.385 | 2.9806 | -52.3252 | 0 | 0 | 0 | 0 | 0
307 | 24 | 0 | 0 |  | -0.27434 | 3.8904 | 16.3804 | 23.1004 | 24.385 | 3.2424 | -52.7573 | 0 | 0 | 0 | 0 | 0
308 | 1 | 0 | 0 |  | -0.27952 | 3.9076 | 16.3291 | 23.0491 | 1.3842 | -2.7792 | -49.8446 | 0 | 0 | 0 | 0 | 0
308 | 2 | 0 | 0 |  | -0.27952 | 3.9076 | 16.3291 | 23.0491 | 2.3842 | -2.5174 | -43.8097 | 0 | 0 | 0 | 0 | 0
308 | 3 | 0 | 0 |  | -0.27952 | 3.9076 | 16.3291 | 23.0491 | 3.3842 | -2.2556 | -36.0158 | 0 | 0 | 0 | 0 | 0
308 | 4 | 0 | 0 |  | -0.27952 | 3.9076 | 16.3291 | 23.0491 | 4.3842 | -1.9938 | -27.2989 | 0 | 0 | 0 | 0 | 0
308 | 5 | 0 | 0 |  | -0.27952 | 3.9076 | 16.3291 | 23.0491 | 5.3842 | -1.732 | -18.2372 | 0 | 0 | 0 | 0 | 0
308 | 6 | 0 | 0 |  | -0.27952 | 3.9076 | 16.3291 | 23.0491 | 6.3842 | -1.4702 | -9.259 | 0 | 0 | 0 | 0 | 0
308 | 7 | 0 | 0 |  | -0.27952 | 3.9076 | 16.3291 | 23.0491 | 7.3842 | -1.2084 | -0.73512 | 0 | 0 | 0 | 0 | 0
308 | 8 | 0 | 10 |  | -0.27952 | 3.9076 | 16.3291 | 23.0491 | 8.3842 | -0.94663 | 6.959 | 0 | 8.3333 | 8.3333 | 13.23 | 0
308 | 9 | 0 | 44 |  | -0.27952 | 3.9076 | 16.3291 | 23.0491 | 9.3842 | -0.68483 | 13.4114 | 0 | 36.6667 | 36.6667 | 58.212 | 1
308 | 10 | 0 | 79 |  | -0.27952 | 3.9076 | 16.3291 | 23.0491 | 10.3842 | -0.42303 | 18.1776 | 0 | 65.8333 | 65.8333 | 104.517 | 1
308 | 11 | 0 | 104 |  | -0.27952 | 3.9076 | 16.3291 | 23.0491 | 11.3842 | -0.16123 | 20.8409 | 0 | 86.6667 | 86.6667 | 137.592 | 1
308 | 12 | 0 | 114 |  | -0.27952 | 3.9076 | 16.3291 | 23.0491 | 12.3842 | 0.10057 | 21.1239 | 0 | 95 | 95 | 150.822 | 1
308 | 13 | 0 | 107 |  | -0.27952 | 3.9076 | 16.3291 | 23.0491 | 13.3842 | 0.36237 | 18.9951 | 0 | 89.1667 | 89.1667 | 141.561 | 1
308 | 14 | 30 | 128 |  | -0.27952 | 3.9076 | 16.3291 | 23.0491 | 14.3842 | 0.62417 | 14.6821 | 18.3979 | 106.6667 | 125.0646 | 198.5526 | 1
308 | 15 | 7 | 82 |  | -0.27952 | 3.9076 | 16.3291 | 23.0491 | 15.3842 | 0.88597 | 8.5805 | 3.1822 | 68.3333 | 71.5155 | 113.538 | 0
308 | 16 | 0 | 25 |  | -0.27952 | 3.9076 | 16.3291 | 23.0491 | 16.3842 | 1.1478 | 1.1358 | 0 | 20.8333 | 20.8333 | 33.075 | 0
308 | 17 | 0 | 1 |  | -0.27952 | 3.9076 | 16.3291 | 23.0491 | 17.3842 | 1.4096 | -7.2303 | 0 | 0.83333 | 0.83333 | 1.323 | 0
308 | 18 | 0 | 0 |  | -0.27952 | 3.9076 | 16.3291 | 23.0491 | 18.3842 | 1.6714 | -16.1357 | 0 | 0 | 0 | 0 | 0
308 | 19 | 0 | 0 |  | -0.27952 | 3.9076 | 16.3291 | 23.0491 | 19.3842 | 1.9332 | -25.2127 | 0 | 0 | 0 | 0 | 0
308 | 20 | 0 | 0 |  | -0.27952 | 3.9076 | 16.3291 | 23.0491 | 20.3842 | 2.195 | -34.0537 | 0 | 0 | 0 | 0 | 0
308 | 21 | 0 | 0 |  | -0.27952 | 3.9076 | 16.3291 | 23.0491 | 21.3842 | 2.4568 | -42.125 | 0 | 0 | 0 | 0 | 0
308 | 22 | 0 | 0 |  | -0.27952 | 3.9076 | 16.3291 | 23.0491 | 22.3842 | 2.7186 | -48.6574 | 0 | 0 | 0 | 0 | 0
308 | 23 | 0 | 0 |  | -0.27952 | 3.9076 | 16.3291 | 23.0491 | 23.3842 | 2.9804 | -52.616 | 0 | 0 | 0 | 0 | 0
308 | 24 | 0 | 0 |  | -0.27952 | 3.9076 | 16.3291 | 23.0491 | 24.3842 | 3.2422 | -53.0535 | 0 | 0 | 0 | 0 | 0
309 | 1 | 0 | 0 |  | -0.28461 | 3.9248 | 16.2642 | 22.9842 | 1.3831 | -2.7795 | -50.125 | 0 | 0 | 0 | 0 | 0
309 | 2 | 0 | 0 |  | -0.28461 | 3.9248 | 16.2642 | 22.9842 | 2.3831 | -2.5177 | -44.0717 | 0 | 0 | 0 | 0 | 0
309 | 3 | 0 | 0 |  | -0.28461 | 3.9248 | 16.2642 | 22.9842 | 3.3831 | -2.2559 | -36.2625 | 0 | 0 | 0 | 0 | 0
309 | 4 | 0 | 0 |  | -0.28461 | 3.9248 | 16.2642 | 22.9842 | 4.3831 | -1.9941 | -27.5371 | 0 | 0 | 0 | 0 | 0
309 | 5 | 0 | 0 |  | -0.28461 | 3.9248 | 16.2642 | 22.9842 | 5.3831 | -1.7323 | -18.4738 | 0 | 0 | 0 | 0 | 0
309 | 6 | 0 | 0 |  | -0.28461 | 3.9248 | 16.2642 | 22.9842 | 6.3831 | -1.4705 | -9.4996 | 0 | 0 | 0 | 0 | 0
309 | 7 | 0 | 0 |  | -0.28461 | 3.9248 | 16.2642 | 22.9842 | 7.3831 | -1.2087 | -0.98452 | 0 | 0 | 0 | 0 | 0
309 | 8 | 0 | 9 |  | -0.28461 | 3.9248 | 16.2642 | 22.9842 | 8.3831 | -0.94691 | 6.6977 | 0 | 7.5 | 7.5 | 11.907 | 0
309 | 9 | 0 | 42 |  | -0.28461 | 3.9248 | 16.2642 | 22.9842 | 9.3831 | -0.68511 | 13.1368 | 0 | 35 | 35 | 55.566 | 1
309 | 10 | 0 | 77 |  | -0.28461 | 3.9248 | 16.2642 | 22.9842 | 10.3831 | -0.42331 | 17.8916 | 0 | 64.1667 | 64.1667 | 101.871 | 1
309 | 11 | 0 | 102 |  | -0.28461 | 3.9248 | 16.2642 | 22.9842 | 11.3831 | -0.16151 | 20.5488 | 0 | 85 | 85 | 134.946 | 1
309 | 12 | 0 | 112 |  | -0.28461 | 3.9248 | 16.2642 | 22.9842 | 12.3831 | 0.10029 | 20.8335 | 0 | 93.3333 | 93.3333 | 148.176 | 1
309 | 13 | 0 | 106 |  | -0.28461 | 3.9248 | 16.2642 | 22.9842 | 13.3831 | 0.36209 | 18.7143 | 0 | 88.3333 | 88.3333 | 140.238 | 1
309 | 14 | 0 | 84 |  | -0.28461 | 3.9248 | 16.2642 | 22.9842 | 14.3831 | 0.62389 | 14.416 | 0 | 70 | 70 | 111.132 | 1
309 | 15 | 0 | 51 |  | -0.28461 | 3.9248 | 16.2642 | 22.9842 | 15.3831 | 0.88569 | 8.3308 | 0 | 42.5 | 42.5 | 67.473 | 0
309 | 16 | 0 | 15 |  | -0.28461 | 3.9248 | 16.2642 | 22.9842 | 16.3831 | 1.1475 | 0.90105 | 0 | 12.5 | 12.5 | 19.845 | 0
309 | 17 | 0 | 0 |  | -0.28461 | 3.9248 | 16.2642 | 22.9842 | 17.3831 | 1.4093 | -7.4538 | 0 | 0 | 0 | 0 | 0
309 | 18 | 0 | 0 |  | -0.28461 | 3.9248 | 16.2642 | 22.9842 | 18.3831 | 1.6711 | -16.3531 | 0 | 0 | 0 | 0 | 0
309 | 19 | 0 | 0 |  | -0.28461 | 3.9248 | 16.2642 | 22.9842 | 19.3831 | 1.9329 | -25.4304 | 0 | 0 | 0 | 0 | 0
309 | 20 | 0 | 0 |  | -0.28461 | 3.9248 | 16.2642 | 22.9842 | 20.3831 | 2.1947 | -34.2793 | 0 | 0 | 0 | 0 | 0
309 | 21 | 0 | 0 |  | -0.28461 | 3.9248 | 16.2642 | 22.9842 | 21.3831 | 2.4565 | -42.3668 | 0 | 0 | 0 | 0 | 0
309 | 22 | 0 | 0 |  | -0.28461 | 3.9248 | 16.2642 | 22.9842 | 22.3831 | 2.7183 | -48.9219 | 0 | 0 | 0 | 0 | 0
309 | 23 | 0 | 0 |  | -0.28461 | 3.9248 | 16.2642 | 22.9842 | 23.3831 | 2.9801 | -52.9017 | 0 | 0 | 0 | 0 | 0
309 | 24 | 0 | 0 |  | -0.28461 | 3.9248 | 16.2642 | 22.9842 | 24.3831 | 3.2419 | -53.3456 | 0 | 0 | 0 | 0 | 0
310 | 1 | 0 | 0 |  | -0.28963 | 3.9421 | 16.1858 | 22.9058 | 1.3818 | -2.7798 | -50.4022 | 0 | 0 | 0 | 0 | 0
310 | 2 | 0 | 0 |  | -0.28963 | 3.9421 | 16.1858 | 22.9058 | 2.3818 | -2.518 | -44.3309 | 0 | 0 | 0 | 0 | 0
310 | 3 | 0 | 0 |  | -0.28963 | 3.9421 | 16.1858 | 22.9058 | 3.3818 | -2.2562 | -36.5071 | 0 | 0 | 0 | 0 | 0
310 | 4 | 0 | 0 |  | -0.28963 | 3.9421 | 16.1858 | 22.9058 | 4.3818 | -1.9944 | -27.7735 | 0 | 0 | 0 | 0 | 0
310 | 5 | 0 | 0 |  | -0.28963 | 3.9421 | 16.1858 | 22.9058 | 5.3818 | -1.7327 | -18.7086 | 0 | 0 | 0 | 0 | 0
310 | 6 | 0 | 0 |  | -0.28963 | 3.9421 | 16.1858 | 22.9058 | 6.3818 | -1.4709 | -9.7386 | 0 | 0 | 0 | 0 | 0
310 | 7 | 0 | 0 |  | -0.28963 | 3.9421 | 16.1858 | 22.9058 | 7.3818 | -1.2091 | -1.232 | 0 | 0 | 0 | 0 | 0
310 | 8 | 0 | 14 |  | -0.28963 | 3.9421 | 16.1858 | 22.9058 | 8.3818 | -0.94725 | 6.4386 | 0 | 11.6667 | 11.6667 | 18.522 | 0
310 | 9 | 9 | 64 |  | -0.28963 | 3.9421 | 16.1858 | 22.9058 | 9.3818 | -0.68545 | 12.8651 | 5.1696 | 53.3333 | 58.5029 | 92.8792 | 1
310 | 10 | 15 | 116 |  | -0.28963 | 3.9421 | 16.1858 | 22.9058 | 10.3818 | -0.42365 | 17.6092 | 10.4392 | 96.6667 | 107.1059 | 170.0413 | 1
310 | 11 | 36 | 147 |  | -0.28963 | 3.9421 | 16.1858 | 22.9058 | 11.3818 | -0.16185 | 20.2609 | 27.4523 | 122.5 | 149.9523 | 238.0643 | 1
310 | 12 | 39 | 161 |  | -0.28963 | 3.9421 | 16.1858 | 22.9058 | 12.3818 | 0.099945 | 20.5479 | 30.0186 | 134.1667 | 164.1853 | 260.6605 | 1
310 | 13 | 38 | 153 |  | -0.28963 | 3.9421 | 16.1858 | 22.9058 | 13.3818 | 0.36174 | 18.4385 | 27.2419 | 127.5 | 154.7419 | 245.6683 | 1
310 | 14 | 132 | 130 |  | -0.28963 | 3.9421 | 16.1858 | 22.9058 | 14.3818 | 0.62354 | 14.1553 | 80.2189 | 108.3333 | 188.5522 | 299.3455 | 1
310 | 15 | 10 | 77 |  | -0.28963 | 3.9421 | 16.1858 | 22.9058 | 15.3818 | 0.88534 | 8.0866 | 4.4962 | 64.1667 | 68.6629 | 109.0092 | 0
310 | 16 | 0 | 22 |  | -0.28963 | 3.9421 | 16.1858 | 22.9058 | 16.3818 | 1.1471 | 0.67186 | 0 | 18.3333 | 18.3333 | 29.106 | 0
310 | 17 | 0 | 0 |  | -0.28963 | 3.9421 | 16.1858 | 22.9058 | 17.3818 | 1.4089 | -7.6717 | 0 | 0 | 0 | 0 | 0
310 | 18 | 0 | 0 |  | -0.28963 | 3.9421 | 16.1858 | 22.9058 | 18.3818 | 1.6707 | -16.5647 | 0 | 0 | 0 | 0 | 0
310 | 19 | 0 | 0 |  | -0.28963 | 3.9421 | 16.1858 | 22.9058 | 19.3818 | 1.9325 | -25.6422 | 0 | 0 | 0 | 0 | 0
310 | 20 | 0 | 0 |  | -0.28963 | 3.9421 | 16.1858 | 22.9058 | 20.3818 | 2.1943 | -34.4988 | 0 | 0 | 0 | 0 | 0
310 | 21 | 0 | 0 |  | -0.28963 | 3.9421 | 16.1858 | 22.9058 | 21.3818 | 2.4561 | -42.6025 | 0 | 0 | 0 | 0 | 0
310 | 22 | 0 | 0 |  | -0.28963 | 3.9421 | 16.1858 | 22.9058 | 22.3818 | 2.7179 | -49.1807 | 0 | 0 | 0 | 0 | 0
310 | 23 | 0 | 0 |  | -0.28963 | 3.9421 | 16.1858 | 22.9058 | 23.3818 | 2.9797 | -53.1823 | 0 | 0 | 0 | 0 | 0
310 | 24 | 0 | 0 |  | -0.28963 | 3.9421 | 16.1858 | 22.9058 | 24.3818 | 3.2415 | -53.6335 | 0 | 0 | 0 | 0 | 0
311 | 1 | 0 | 0 |  | -0.29457 | 3.9593 | 16.0937 | 22.8137 | 1.3802 | -2.7802 | -50.6759 | 0 | 0 | 0 | 0 | 0
311 | 2 | 0 | 0 |  | -0.29457 | 3.9593 | 16.0937 | 22.8137 | 2.3802 | -2.5185 | -44.5875 | 0 | 0 | 0 | 0 | 0
311 | 3 | 0 | 0 |  | -0.29457 | 3.9593 | 16.0937 | 22.8137 | 3.3802 | -2.2567 | -36.7494 | 0 | 0 | 0 | 0 | 0
311 | 4 | 0 | 0 |  | -0.29457 | 3.9593 | 16.0937 | 22.8137 | 4.3802 | -1.9949 | -28.008 | 0 | 0 | 0 | 0 | 0
311 | 5 | 0 | 0 |  | -0.29457 | 3.9593 | 16.0937 | 22.8137 | 5.3802 | -1.7331 | -18.9417 | 0 | 0 | 0 | 0 | 0
311 | 6 | 0 | 0 |  | -0.29457 | 3.9593 | 16.0937 | 22.8137 | 6.3802 | -1.4713 | -9.9757 | 0 | 0 | 0 | 0 | 0
311 | 7 | 0 | 0 |  | -0.29457 | 3.9593 | 16.0937 | 22.8137 | 7.3802 | -1.2095 | -1.4775 | 0 | 0 | 0 | 0 | 0
311 | 8 | 0 | 8 |  | -0.29457 | 3.9593 | 16.0937 | 22.8137 | 8.3802 | -0.94765 | 6.1819 | 0 | 6.6667 | 6.6667 | 10.584 | 0
311 | 9 | 6 | 62 |  | -0.29457 | 3.9593 | 16.0937 | 22.8137 | 9.3802 | -0.68585 | 12.5964 | 3.428 | 51.6667 | 55.0947 | 87.4683 | 1
311 | 10 | 15 | 114 |  | -0.29457 | 3.9593 | 16.0937 | 22.8137 | 10.3802 | -0.42406 | 17.3304 | 10.3917 | 95 | 105.3917 | 167.3199 | 1
311 | 11 | 150 | 151 |  | -0.29457 | 3.9593 | 16.0937 | 22.8137 | 11.3802 | -0.16226 | 19.9773 | 113.9083 | 125.8333 | 239.7417 | 380.6139 | 1
311 | 12 | 61 | 151 |  | -0.29457 | 3.9593 | 16.0937 | 22.8137 | 12.3802 | 0.099544 | 20.267 | 46.7635 | 125.8333 | 172.5968 | 274.0148 | 1
311 | 13 | 37 | 150 |  | -0.29457 | 3.9593 | 16.0937 | 22.8137 | 13.3802 | 0.36134 | 18.1679 | 26.4168 | 125 | 151.4168 | 240.3894 | 1
311 | 14 | 0 | 81 |  | -0.29457 | 3.9593 | 16.0937 | 22.8137 | 14.3802 | 0.62314 | 13.8999 | 0 | 67.5 | 67.5 | 107.163 | 1
311 | 15 | 0 | 48 |  | -0.29457 | 3.9593 | 16.0937 | 22.8137 | 15.3802 | 0.88494 | 7.848 | 0 | 40 | 40 | 63.504 | 0
311 | 16 | 0 | 13 |  | -0.29457 | 3.9593 | 16.0937 | 22.8137 | 16.3802 | 1.1467 | 0.44829 | 0 | 10.8333 | 10.8333 | 17.199 | 0
311 | 17 | 0 | 0 |  | -0.29457 | 3.9593 | 16.0937 | 22.8137 | 17.3802 | 1.4085 | -7.8838 | 0 | 0 | 0 | 0 | 0
311 | 18 | 0 | 0 |  | -0.29457 | 3.9593 | 16.0937 | 22.8137 | 18.3802 | 1.6703 | -16.7706 | 0 | 0 | 0 | 0 | 0
311 | 19 | 0 | 0 |  | -0.29457 | 3.9593 | 16.0937 | 22.8137 | 19.3802 | 1.9321 | -25.8481 | 0 | 0 | 0 | 0 | 0
311 | 20 | 0 | 0 |  | -0.29457 | 3.9593 | 16.0937 | 22.8137 | 20.3802 | 2.1939 | -34.7124 | 0 | 0 | 0 | 0 | 0
311 | 21 | 0 | 0 |  | -0.29457 | 3.9593 | 16.0937 | 22.8137 | 21.3802 | 2.4557 | -42.8322 | 0 | 0 | 0 | 0 | 0
311 | 22 | 0 | 0 |  | -0.29457 | 3.9593 | 16.0937 | 22.8137 | 22.3802 | 2.7175 | -49.4336 | 0 | 0 | 0 | 0 | 0
311 | 23 | 0 | 0 |  | -0.29457 | 3.9593 | 16.0937 | 22.8137 | 23.3802 | 2.9793 | -53.4578 | 0 | 0 | 0 | 0 | 0
311 | 24 | 0 | 0 |  | -0.29457 | 3.9593 | 16.0937 | 22.8137 | 24.3802 | 3.2411 | -53.9172 | 0 | 0 | 0 | 0 | 0
312 | 1 | 0 | 0 |  | -0.29942 | 3.9765 | 15.9881 | 22.7081 | 1.3785 | -2.7807 | -50.9461 | 0 | 0 | 0 | 0 | 0
312 | 2 | 0 | 0 |  | -0.29942 | 3.9765 | 15.9881 | 22.7081 | 2.3785 | -2.5189 | -44.8413 | 0 | 0 | 0 | 0 | 0
312 | 3 | 0 | 0 |  | -0.29942 | 3.9765 | 15.9881 | 22.7081 | 3.3785 | -2.2571 | -36.9895 | 0 | 0 | 0 | 0 | 0
312 | 4 | 0 | 0 |  | -0.29942 | 3.9765 | 15.9881 | 22.7081 | 4.3785 | -1.9953 | -28.2406 | 0 | 0 | 0 | 0 | 0
312 | 5 | 0 | 0 |  | -0.29942 | 3.9765 | 15.9881 | 22.7081 | 5.3785 | -1.7335 | -19.173 | 0 | 0 | 0 | 0 | 0
312 | 6 | 0 | 0 |  | -0.29942 | 3.9765 | 15.9881 | 22.7081 | 6.3785 | -1.4717 | -10.211 | 0 | 0 | 0 | 0 | 0
312 | 7 | 0 | 0 |  | -0.29942 | 3.9765 | 15.9881 | 22.7081 | 7.3785 | -1.2099 | -1.7208 | 0 | 0 | 0 | 0 | 0
312 | 8 | 0 | 8 |  | -0.29942 | 3.9765 | 15.9881 | 22.7081 | 8.3785 | -0.94811 | 5.9278 | 0 | 6.6667 | 6.6667 | 10.584 | 0
312 | 9 | 0 | 38 |  | -0.29942 | 3.9765 | 15.9881 | 22.7081 | 9.3785 | -0.68632 | 12.3308 | 0 | 31.6667 | 31.6667 | 50.274 | 0
312 | 10 | 0 | 73 |  | -0.29942 | 3.9765 | 15.9881 | 22.7081 | 10.3785 | -0.42452 | 17.0554 | 0 | 60.8333 | 60.8333 | 96.579 | 1
312 | 11 | 0 | 97 |  | -0.29942 | 3.9765 | 15.9881 | 22.7081 | 11.3785 | -0.16272 | 19.698 | 0 | 80.8333 | 80.8333 | 128.331 | 1
312 | 12 | 0 | 107 |  | -0.29942 | 3.9765 | 15.9881 | 22.7081 | 12.3785 | 0.099083 | 19.991 | 0 | 89.1667 | 89.1667 | 141.561 | 1
312 | 13 | 0 | 101 |  | -0.29942 | 3.9765 | 15.9881 | 22.7081 | 13.3785 | 0.36088 | 17.9026 | 0 | 84.1667 | 84.1667 | 133.623 | 1
312 | 14 | 0 | 80 |  | -0.29942 | 3.9765 | 15.9881 | 22.7081 | 14.3785 | 0.62268 | 13.6501 | 0 | 66.6667 | 66.6667 | 105.84 | 1
312 | 15 | 0 | 47 |  | -0.29942 | 3.9765 | 15.9881 | 22.7081 | 15.3785 | 0.88448 | 7.6149 | 0 | 39.1667 | 39.1667 | 62.181 | 0
312 | 16 | 0 | 12 |  | -0.29942 | 3.9765 | 15.9881 | 22.7081 | 16.3785 | 1.1463 | 0.23041 | 0 | 10 | 10 | 15.876 | 0
312 | 17 | 0 | 0 |  | -0.29942 | 3.9765 | 15.9881 | 22.7081 | 17.3785 | 1.4081 | -8.0902 | 0 | 0 | 0 | 0 | 0
312 | 18 | 0 | 0 |  | -0.29942 | 3.9765 | 15.9881 | 22.7081 | 18.3785 | 1.6699 | -16.9706 | 0 | 0 | 0 | 0 | 0
312 | 19 | 0 | 0 |  | -0.29942 | 3.9765 | 15.9881 | 22.7081 | 19.3785 | 1.9317 | -26.048 | 0 | 0 | 0 | 0 | 0
312 | 20 | 0 | 0 |  | -0.29942 | 3.9765 | 15.9881 | 22.7081 | 20.3785 | 2.1935 | -34.9198 | 0 | 0 | 0 | 0 | 0
312 | 21 | 0 | 0 |  | -0.29942 | 3.9765 | 15.9881 | 22.7081 | 21.3785 | 2.4553 | -43.0557 | 0 | 0 | 0 | 0 | 0
312 | 22 | 0 | 0 |  | -0.29942 | 3.9765 | 15.9881 | 22.7081 | 22.3785 | 2.7171 | -49.6806 | 0 | 0 | 0 | 0 | 0
312 | 23 | 0 | 0 |  | -0.29942 | 3.9765 | 15.9881 | 22.7081 | 23.3785 | 2.9789 | -53.7279 | 0 | 0 | 0 | 0 | 0
312 | 24 | 0 | 0 |  | -0.29942 | 3.9765 | 15.9881 | 22.7081 | 24.3785 | 3.2407 | -54.1964 | 0 | 0 | 0 | 0 | 0
313 | 1 | 0 | 0 |  | -0.30419 | 3.9937 | 15.8691 | 22.5891 | 1.3765 | -2.7812 | -51.2128 | 0 | 0 | 0 | 0 | 0
313 | 2 | 0 | 0 |  | -0.30419 | 3.9937 | 15.8691 | 22.5891 | 2.3765 | -2.5194 | -45.0923 | 0 | 0 | 0 | 0 | 0
313 | 3 | 0 | 0 |  | -0.30419 | 3.9937 | 15.8691 | 22.5891 | 3.3765 | -2.2576 | -37.2273 | 0 | 0 | 0 | 0 | 0
313 | 4 | 0 | 0 |  | -0.30419 | 3.9937 | 15.8691 | 22.5891 | 4.3765 | -1.9958 | -28.4712 | 0 | 0 | 0 | 0 | 0
313 | 5 | 0 | 0 |  | -0.30419 | 3.9937 | 15.8691 | 22.5891 | 5.3765 | -1.734 | -19.4024 | 0 | 0 | 0 | 0 | 0
313 | 6 | 0 | 0 |  | -0.30419 | 3.9937 | 15.8691 | 22.5891 | 6.3765 | -1.4722 | -10.4443 | 0 | 0 | 0 | 0 | 0
313 | 7 | 0 | 0 |  | -0.30419 | 3.9937 | 15.8691 | 22.5891 | 7.3765 | -1.2104 | -1.962 | 0 | 0 | 0 | 0 | 0
313 | 8 | 0 | 7 |  | -0.30419 | 3.9937 | 15.8691 | 22.5891 | 8.3765 | -0.94863 | 5.6763 | 0 | 5.8333 | 5.8333 | 9.261 | 0
313 | 9 | 0 | 37 |  | -0.30419 | 3.9937 | 15.8691 | 22.5891 | 9.3765 | -0.68683 | 12.0683 | 0 | 30.8333 | 30.8333 | 48.951 | 0
313 | 10 | 0 | 71 |  | -0.30419 | 3.9937 | 15.8691 | 22.5891 | 10.3765 | -0.42504 | 16.7841 | 0 | 59.1667 | 59.1667 | 93.933 | 1
313 | 11 | 0 | 95 |  | -0.30419 | 3.9937 | 15.8691 | 22.5891 | 11.3765 | -0.16324 | 19.4232 | 0 | 79.1667 | 79.1667 | 125.685 | 1
313 | 12 | 0 | 105 |  | -0.30419 | 3.9937 | 15.8691 | 22.5891 | 12.3765 | 0.098563 | 19.7201 | 0 | 87.5 | 87.5 | 138.915 | 1
313 | 13 | 0 | 99 |  | -0.30419 | 3.9937 | 15.8691 | 22.5891 | 13.3765 | 0.36036 | 17.6427 | 0 | 82.5 | 82.5 | 130.977 | 1
313 | 14 | 0 | 77 |  | -0.30419 | 3.9937 | 15.8691 | 22.5891 | 14.3765 | 0.62216 | 13.4058 | 0 | 64.1667 | 64.1667 | 101.871 | 1
313 | 15 | 7 | 71 |  | -0.30419 | 3.9937 | 15.8691 | 22.5891 | 15.3765 | 0.88396 | 7.3876 | 3.099 | 59.1667 | 62.2656 | 98.8529 | 0
313 | 16 | 0 | 12 |  | -0.30419 | 3.9937 | 15.8691 | 22.5891 | 16.3765 | 1.1458 | 0.018284 | 0 | 10 | 10 | 15.876 | 0
313 | 17 | 0 | 0 |  | -0.30419 | 3.9937 | 15.8691 | 22.5891 | 17.3765 | 1.4076 | -8.2908 | 0 | 0 | 0 | 0 | 0
313 | 18 | 0 | 0 |  | -0.30419 | 3.9937 | 15.8691 | 22.5891 | 18.3765 | 1.6694 | -17.1647 | 0 | 0 | 0 | 0 | 0
313 | 19 | 0 | 0 |  | -0.30419 | 3.9937 | 15.8691 | 22.5891 | 19.3765 | 1.9312 | -26.2419 | 0 | 0 | 0 | 0 | 0
313 | 20 | 0 | 0 |  | -0.30419 | 3.9937 | 15.8691 | 22.5891 | 20.3765 | 2.193 | -35.121 | 0 | 0 | 0 | 0 | 0
313 | 21 | 0 | 0 |  | -0.30419 | 3.9937 | 15.8691 | 22.5891 | 21.3765 | 2.4548 | -43.273 | 0 | 0 | 0 | 0 | 0
313 | 22 | 0 | 0 |  | -0.30419 | 3.9937 | 15.8691 | 22.5891 | 22.3765 | 2.7166 | -49.9216 | 0 | 0 | 0 | 0 | 0
313 | 23 | 0 | 0 |  | -0.30419 | 3.9937 | 15.8691 | 22.5891 | 23.3765 | 2.9784 | -53.9926 | 0 | 0 | 0 | 0 | 0
313 | 24 | 0 | 0 |  | -0.30419 | 3.9937 | 15.8691 | 22.5891 | 24.3765 | 3.2402 | -54.4712 | 0 | 0 | 0 | 0 | 0
314 | 1 | 0 | 0 |  | -0.30888 | 4.0109 | 15.7366 | 22.4566 | 1.3743 | -2.7818 | -51.4758 | 0 | 0 | 0 | 0 | 0
314 | 2 | 0 | 0 |  | -0.30888 | 4.0109 | 15.7366 | 22.4566 | 2.3743 | -2.52 | -45.3403 | 0 | 0 | 0 | 0 | 0
314 | 3 | 0 | 0 |  | -0.30888 | 4.0109 | 15.7366 | 22.4566 | 3.3743 | -2.2582 | -37.4627 | 0 | 0 | 0 | 0 | 0
314 | 4 | 0 | 0 |  | -0.30888 | 4.0109 | 15.7366 | 22.4566 | 4.3743 | -1.9964 | -28.6997 | 0 | 0 | 0 | 0 | 0
314 | 5 | 0 | 0 |  | -0.30888 | 4.0109 | 15.7366 | 22.4566 | 5.3743 | -1.7346 | -19.6299 | 0 | 0 | 0 | 0 | 0
314 | 6 | 0 | 0 |  | -0.30888 | 4.0109 | 15.7366 | 22.4566 | 6.3743 | -1.4728 | -10.6755 | 0 | 0 | 0 | 0 | 0
314 | 7 | 0 | 0 |  | -0.30888 | 4.0109 | 15.7366 | 22.4566 | 7.3743 | -1.211 | -2.2008 | 0 | 0 | 0 | 0 | 0
314 | 8 | 0 | 7 |  | -0.30888 | 4.0109 | 15.7366 | 22.4566 | 8.3743 | -0.94921 | 5.4274 | 0 | 5.8333 | 5.8333 | 9.261 | 0
314 | 9 | 0 | 35 |  | -0.30888 | 4.0109 | 15.7366 | 22.4566 | 9.3743 | -0.68741 | 11.8091 | 0 | 29.1667 | 29.1667 | 46.305 | 0
314 | 10 | 0 | 69 |  | -0.30888 | 4.0109 | 15.7366 | 22.4566 | 10.3743 | -0.42561 | 16.5168 | 0 | 57.5 | 57.5 | 91.287 | 1
314 | 11 | 0 | 93 |  | -0.30888 | 4.0109 | 15.7366 | 22.4566 | 11.3743 | -0.16381 | 19.153 | 0 | 77.5 | 77.5 | 123.039 | 1
314 | 12 | 0 | 103 |  | -0.30888 | 4.0109 | 15.7366 | 22.4566 | 12.3743 | 0.097985 | 19.4542 | 0 | 85.8333 | 85.8333 | 136.269 | 1
314 | 13 | 0 | 97 |  | -0.30888 | 4.0109 | 15.7366 | 22.4566 | 13.3743 | 0.35978 | 17.3882 | 0 | 80.8333 | 80.8333 | 128.331 | 1
314 | 14 | 0 | 76 |  | -0.30888 | 4.0109 | 15.7366 | 22.4566 | 14.3743 | 0.62158 | 13.1672 | 0 | 63.3333 | 63.3333 | 100.548 | 1
314 | 15 | 0 | 44 |  | -0.30888 | 4.0109 | 15.7366 | 22.4566 | 15.3743 | 0.88338 | 7.166 | 0 | 36.6667 | 36.6667 | 58.212 | 0
314 | 16 | 0 | 11 |  | -0.30888 | 4.0109 | 15.7366 | 22.4566 | 16.3743 | 1.1452 | -0.18802 | 0 | 9.1667 | 9.1667 | 14.553 | 0
314 | 17 | 0 | 0 |  | -0.30888 | 4.0109 | 15.7366 | 22.4566 | 17.3743 | 1.407 | -8.4854 | 0 | 0 | 0 | 0 | 0
314 | 18 | 0 | 0 |  | -0.30888 | 4.0109 | 15.7366 | 22.4566 | 18.3743 | 1.6688 | -17.3528 | 0 | 0 | 0 | 0 | 0
314 | 19 | 0 | 0 |  | -0.30888 | 4.0109 | 15.7366 | 22.4566 | 19.3743 | 1.9306 | -26.4297 | 0 | 0 | 0 | 0 | 0
314 | 20 | 0 | 0 |  | -0.30888 | 4.0109 | 15.7366 | 22.4566 | 20.3743 | 2.1924 | -35.316 | 0 | 0 | 0 | 0 | 0
314 | 21 | 0 | 0 |  | -0.30888 | 4.0109 | 15.7366 | 22.4566 | 21.3743 | 2.4542 | -43.484 | 0 | 0 | 0 | 0 | 0
314 | 22 | 0 | 0 |  | -0.30888 | 4.0109 | 15.7366 | 22.4566 | 22.3743 | 2.716 | -50.1565 | 0 | 0 | 0 | 0 | 0
314 | 23 | 0 | 0 |  | -0.30888 | 4.0109 | 15.7366 | 22.4566 | 23.3743 | 2.9778 | -54.2519 | 0 | 0 | 0 | 0 | 0
314 | 24 | 0 | 0 |  | -0.30888 | 4.0109 | 15.7366 | 22.4566 | 24.3743 | 3.2396 | -54.7414 | 0 | 0 | 0 | 0 | 0
315 | 1 | 0 | 0 |  | -0.31347 | 4.0281 | 15.5909 | 22.3109 | 1.3718 | -2.7824 | -51.735 | 0 | 0 | 0 | 0 | 0
315 | 2 | 0 | 0 |  | -0.31347 | 4.0281 | 15.5909 | 22.3109 | 2.3718 | -2.5206 | -45.5853 | 0 | 0 | 0 | 0 | 0
315 | 3 | 0 | 0 |  | -0.31347 | 4.0281 | 15.5909 | 22.3109 | 3.3718 | -2.2588 | -37.6956 | 0 | 0 | 0 | 0 | 0
315 | 4 | 0 | 0 |  | -0.31347 | 4.0281 | 15.5909 | 22.3109 | 4.3718 | -1.997 | -28.9261 | 0 | 0 | 0 | 0 | 0
315 | 5 | 0 | 0 |  | -0.31347 | 4.0281 | 15.5909 | 22.3109 | 5.3718 | -1.7352 | -19.8553 | 0 | 0 | 0 | 0 | 0
315 | 6 | 0 | 0 |  | -0.31347 | 4.0281 | 15.5909 | 22.3109 | 6.3718 | -1.4734 | -10.9047 | 0 | 0 | 0 | 0 | 0
315 | 7 | 0 | 0 |  | -0.31347 | 4.0281 | 15.5909 | 22.3109 | 7.3718 | -1.2116 | -2.4373 | 0 | 0 | 0 | 0 | 0
315 | 8 | 0 | 17 |  | -0.31347 | 4.0281 | 15.5909 | 22.3109 | 8.3718 | -0.94985 | 5.1815 | 0 | 14.1667 | 14.1667 | 22.491 | 0
315 | 9 | 0 | 54 |  | -0.31347 | 4.0281 | 15.5909 | 22.3109 | 9.3718 | -0.68805 | 11.5533 | 0 | 45 | 45 | 71.442 | 0
315 | 10 | 13 | 104 |  | -0.31347 | 4.0281 | 15.5909 | 22.3109 | 10.3718 | -0.42625 | 16.2535 | 8.8436 | 86.6667 | 95.5102 | 151.632 | 1
315 | 11 | 0 | 91 |  | -0.31347 | 4.0281 | 15.5909 | 22.3109 | 11.3718 | -0.16445 | 18.8875 | 0 | 75.8333 | 75.8333 | 120.393 | 1
315 | 12 | 0 | 101 |  | -0.31347 | 4.0281 | 15.5909 | 22.3109 | 12.3718 | 0.097349 | 19.1936 | 0 | 84.1667 | 84.1667 | 133.623 | 1
315 | 13 | 0 | 95 |  | -0.31347 | 4.0281 | 15.5909 | 22.3109 | 13.3718 | 0.35915 | 17.1392 | 0 | 79.1667 | 79.1667 | 125.685 | 1
315 | 14 | 0 | 74 |  | -0.31347 | 4.0281 | 15.5909 | 22.3109 | 14.3718 | 0.62095 | 12.9343 | 0 | 61.6667 | 61.6667 | 97.902 | 1
315 | 15 | 0 | 42 |  | -0.31347 | 4.0281 | 15.5909 | 22.3109 | 15.3718 | 0.88275 | 6.9502 | 0 | 35 | 35 | 55.566 | 0
315 | 16 | 0 | 10 |  | -0.31347 | 4.0281 | 15.5909 | 22.3109 | 16.3718 | 1.1445 | -0.38844 | 0 | 8.3333 | 8.3333 | 13.23 | 0
315 | 17 | 0 | 0 |  | -0.31347 | 4.0281 | 15.5909 | 22.3109 | 17.3718 | 1.4063 | -8.6742 | 0 | 0 | 0 | 0 | 0
315 | 18 | 0 | 0 |  | -0.31347 | 4.0281 | 15.5909 | 22.3109 | 18.3718 | 1.6681 | -17.5348 | 0 | 0 | 0 | 0 | 0
315 | 19 | 0 | 0 |  | -0.31347 | 4.0281 | 15.5909 | 22.3109 | 19.3718 | 1.9299 | -26.6113 | 0 | 0 | 0 | 0 | 0
315 | 20 | 0 | 0 |  | -0.31347 | 4.0281 | 15.5909 | 22.3109 | 20.3718 | 2.1917 | -35.5048 | 0 | 0 | 0 | 0 | 0
315 | 21 | 0 | 0 |  | -0.31347 | 4.0281 | 15.5909 | 22.3109 | 21.3718 | 2.4535 | -43.6887 | 0 | 0 | 0 | 0 | 0
315 | 22 | 0 | 0 |  | -0.31347 | 4.0281 | 15.5909 | 22.3109 | 22.3718 | 2.7153 | -50.3852 | 0 | 0 | 0 | 0 | 0
315 | 23 | 0 | 0 |  | -0.31347 | 4.0281 | 15.5909 | 22.3109 | 23.3718 | 2.9771 | -54.5055 | 0 | 0 | 0 | 0 | 0
315 | 24 | 0 | 0 |  | -0.31347 | 4.0281 | 15.5909 | 22.3109 | 24.3718 | 3.2389 | -55.0069 | 0 | 0 | 0 | 0 | 0
316 | 1 | 0 | 0 |  | -0.31798 | 4.0453 | 15.4319 | 22.1519 | 1.3692 | -2.7831 | -51.9904 | 0 | 0 | 0 | 0 | 0
316 | 2 | 0 | 0 |  | -0.31798 | 4.0453 | 15.4319 | 22.1519 | 2.3692 | -2.5213 | -45.8273 | 0 | 0 | 0 | 0 | 0
316 | 3 | 0 | 0 |  | -0.31798 | 4.0453 | 15.4319 | 22.1519 | 3.3692 | -2.2595 | -37.926 | 0 | 0 | 0 | 0 | 0
316 | 4 | 0 | 0 |  | -0.31798 | 4.0453 | 15.4319 | 22.1519 | 4.3692 | -1.9977 | -29.1502 | 0 | 0 | 0 | 0 | 0
316 | 5 | 0 | 0 |  | -0.31798 | 4.0453 | 15.4319 | 22.1519 | 5.3692 | -1.7359 | -20.0785 | 0 | 0 | 0 | 0 | 0
316 | 6 | 0 | 0 |  | -0.31798 | 4.0453 | 15.4319 | 22.1519 | 6.3692 | -1.4741 | -11.1316 | 0 | 0 | 0 | 0 | 0
316 | 7 | 0 | 0 |  | -0.31798 | 4.0453 | 15.4319 | 22.1519 | 7.3692 | -1.2123 | -2.6712 | 0 | 0 | 0 | 0 | 0
316 | 8 | 0 | 9 |  | -0.31798 | 4.0453 | 15.4319 | 22.1519 | 8.3692 | -0.95054 | 4.9384 | 0 | 7.5 | 7.5 | 11.907 | 0
316 | 9 | 132 | 65 |  | -0.31798 | 4.0453 | 15.4319 | 22.1519 | 9.3692 | -0.68874 | 11.301 | 73.4029 | 54.1667 | 127.5696 | 202.5295 | 0
316 | 10 | 438 | 76 |  | -0.31798 | 4.0453 | 15.4319 | 22.1519 | 10.3692 | -0.42694 | 15.9944 | 296.6115 | 63.3333 | 359.9448 | 571.4484 | 1
316 | 11 | 431 | 100 |  | -0.31798 | 4.0453 | 15.4319 | 22.1519 | 11.3692 | -0.16514 | 18.6267 | 320.6391 | 83.3333 | 403.9724 | 641.3466 | 1
316 | 12 | 348 | 121 |  | -0.31798 | 4.0453 | 15.4319 | 22.1519 | 12.3692 | 0.096656 | 18.9382 | 261.6178 | 100.8333 | 362.4511 | 575.4274 | 1
316 | 13 | 153 | 144 |  | -0.31798 | 4.0453 | 15.4319 | 22.1519 | 13.3692 | 0.35846 | 16.8959 | 107.1246 | 120 | 227.1246 | 360.583 | 1
316 | 14 | 287 | 98 |  | -0.31798 | 4.0453 | 15.4319 | 22.1519 | 14.3692 | 0.62025 | 12.7072 | 170.0808 | 81.6667 | 251.7475 | 399.6743 | 1
316 | 15 | 72 | 72 |  | -0.31798 | 4.0453 | 15.4319 | 22.1519 | 15.3692 | 0.88205 | 6.7403 | 31.4258 | 60 | 91.4258 | 145.1477 | 0
316 | 16 | 17 | 25 |  | -0.31798 | 4.0453 | 15.4319 | 22.1519 | 16.3692 | 1.1439 | -0.58293 | 4.1202 | 20.8333 | 24.9535 | 39.6162 | 0
316 | 17 | 0 | 0 |  | -0.31798 | 4.0453 | 15.4319 | 22.1519 | 17.3692 | 1.4057 | -8.8569 | 0 | 0 | 0 | 0 | 0
316 | 18 | 0 | 0 |  | -0.31798 | 4.0453 | 15.4319 | 22.1519 | 18.3692 | 1.6675 | -17.7108 | 0 | 0 | 0 | 0 | 0
316 | 19 | 0 | 0 |  | -0.31798 | 4.0453 | 15.4319 | 22.1519 | 19.3692 | 1.9293 | -26.7867 | 0 | 0 | 0 | 0 | 0
316 | 20 | 0 | 0 |  | -0.31798 | 4.0453 | 15.4319 | 22.1519 | 20.3692 | 2.1911 | -35.6872 | 0 | 0 | 0 | 0 | 0
316 | 21 | 0 | 0 |  | -0.31798 | 4.0453 | 15.4319 | 22.1519 | 21.3692 | 2.4529 | -43.887 | 0 | 0 | 0 | 0 | 0
316 | 22 | 0 | 0 |  | -0.31798 | 4.0453 | 15.4319 | 22.1519 | 22.3692 | 2.7146 | -50.6076 | 0 | 0 | 0 | 0 | 0
316 | 23 | 0 | 0 |  | -0.31798 | 4.0453 | 15.4319 | 22.1519 | 23.3692 | 2.9764 | -54.7534 | 0 | 0 | 0 | 0 | 0
316 | 24 | 0 | 0 |  | -0.31798 | 4.0453 | 15.4319 | 22.1519 | 24.3692 | 3.2382 | -55.2677 | 0 | 0 | 0 | 0 | 0
317 | 1 | 0 | 0 |  | -0.3224 | 4.0626 | 15.2598 | 21.9798 | 1.3663 | -2.7839 | -52.242 | 0 | 0 | 0 | 0 | 0
317 | 2 | 0 | 0 |  | -0.3224 | 4.0626 | 15.2598 | 21.9798 | 2.3663 | -2.5221 | -46.0662 | 0 | 0 | 0 | 0 | 0
317 | 3 | 0 | 0 |  | -0.3224 | 4.0626 | 15.2598 | 21.9798 | 3.3663 | -2.2603 | -38.1538 | 0 | 0 | 0 | 0 | 0
317 | 4 | 0 | 0 |  | -0.3224 | 4.0626 | 15.2598 | 21.9798 | 4.3663 | -1.9985 | -29.372 | 0 | 0 | 0 | 0 | 0
317 | 5 | 0 | 0 |  | -0.3224 | 4.0626 | 15.2598 | 21.9798 | 5.3663 | -1.7367 | -20.2995 | 0 | 0 | 0 | 0 | 0
317 | 6 | 0 | 0 |  | -0.3224 | 4.0626 | 15.2598 | 21.9798 | 6.3663 | -1.4749 | -11.3561 | 0 | 0 | 0 | 0 | 0
317 | 7 | 0 | 0 |  | -0.3224 | 4.0626 | 15.2598 | 21.9798 | 7.3663 | -1.2131 | -2.9026 | 0 | 0 | 0 | 0 | 0
317 | 8 | 0 | 15 |  | -0.3224 | 4.0626 | 15.2598 | 21.9798 | 8.3663 | -0.95129 | 4.6984 | 0 | 12.5 | 12.5 | 19.845 | 0
317 | 9 | 170 | 63 |  | -0.3224 | 4.0626 | 15.2598 | 21.9798 | 9.3663 | -0.68949 | 11.0523 | 94.02 | 52.5 | 146.52 | 232.6151 | 0
317 | 10 | 262 | 89 |  | -0.3224 | 4.0626 | 15.2598 | 21.9798 | 10.3663 | -0.42769 | 15.7395 | 176.6245 | 74.1667 | 250.7912 | 398.156 | 1
317 | 11 | 494 | 91 |  | -0.3224 | 4.0626 | 15.2598 | 21.9798 | 11.3663 | -0.16589 | 18.3708 | 366.0306 | 75.8333 | 441.864 | 701.5032 | 1
317 | 12 | 194 | 138 |  | -0.3224 | 4.0626 | 15.2598 | 21.9798 | 12.3663 | 0.095905 | 18.6882 | 145.2955 | 115 | 260.2955 | 413.2451 | 1
317 | 13 | 128 | 149 |  | -0.3224 | 4.0626 | 15.2598 | 21.9798 | 13.3663 | 0.3577 | 16.6582 | 89.2895 | 124.1667 | 213.4561 | 338.883 | 1
317 | 14 | 106 | 119 |  | -0.3224 | 4.0626 | 15.2598 | 21.9798 | 14.3663 | 0.6195 | 12.4859 | 62.5758 | 99.1667 | 161.7425 | 256.7824 | 0
317 | 15 | 85 | 67 |  | -0.3224 | 4.0626 | 15.2598 | 21.9798 | 15.3663 | 0.8813 | 6.5363 | 36.9364 | 55.8333 | 92.7697 | 147.2812 | 0
317 | 16 | 0 | 23 |  | -0.3224 | 4.0626 | 15.2598 | 21.9798 | 16.3663 | 1.1431 | -0.77141 | 0 | 19.1667 | 19.1667 | 30.429 | 0
317 | 17 | 0 | 0 |  | -0.3224 | 4.0626 | 15.2598 | 21.9798 | 17.3663 | 1.4049 | -9.0336 | 0 | 0 | 0 | 0 | 0
317 | 18 | 0 | 0 |  | -0.3224 | 4.0626 | 15.2598 | 21.9798 | 18.3663 | 1.6667 | -17.8806 | 0 | 0 | 0 | 0 | 0
317 | 19 | 0 | 0 |  | -0.3224 | 4.0626 | 15.2598 | 21.9798 | 19.3663 | 1.9285 | -26.9558 | 0 | 0 | 0 | 0 | 0
317 | 20 | 0 | 0 |  | -0.3224 | 4.0626 | 15.2598 | 21.9798 | 20.3663 | 2.1903 | -35.8632 | 0 | 0 | 0 | 0 | 0
317 | 21 | 0 | 0 |  | -0.3224 | 4.0626 | 15.2598 | 21.9798 | 21.3663 | 2.4521 | -44.0787 | 0 | 0 | 0 | 0 | 0
317 | 22 | 0 | 0 |  | -0.3224 | 4.0626 | 15.2598 | 21.9798 | 22.3663 | 2.7139 | -50.8236 | 0 | 0 | 0 | 0 | 0
317 | 23 | 0 | 0 |  | -0.3224 | 4.0626 | 15.2598 | 21.9798 | 23.3663 | 2.9757 | -54.9955 | 0 | 0 | 0 | 0 | 0
317 | 24 | 0 | 0 |  | -0.3224 | 4.0626 | 15.2598 | 21.9798 | 24.3663 | 3.2375 | -55.5235 | 0 | 0 | 0 | 0 | 0
318 | 1 | 0 | 0 |  | -0.32672 | 4.0798 | 15.0748 | 21.7948 | 1.3632 | -2.7847 | -52.4895 | 0 | 0 | 0 | 0 | 0
318 | 2 | 0 | 0 |  | -0.32672 | 4.0798 | 15.0748 | 21.7948 | 2.3632 | -2.5229 | -46.3018 | 0 | 0 | 0 | 0 | 0
318 | 3 | 0 | 0 |  | -0.32672 | 4.0798 | 15.0748 | 21.7948 | 3.3632 | -2.2611 | -38.3789 | 0 | 0 | 0 | 0 | 0
318 | 4 | 0 | 0 |  | -0.32672 | 4.0798 | 15.0748 | 21.7948 | 4.3632 | -1.9993 | -29.5914 | 0 | 0 | 0 | 0 | 0
318 | 5 | 0 | 0 |  | -0.32672 | 4.0798 | 15.0748 | 21.7948 | 5.3632 | -1.7375 | -20.5183 | 0 | 0 | 0 | 0 | 0
318 | 6 | 0 | 0 |  | -0.32672 | 4.0798 | 15.0748 | 21.7948 | 6.3632 | -1.4757 | -11.5783 | 0 | 0 | 0 | 0 | 0
318 | 7 | 0 | 0 |  | -0.32672 | 4.0798 | 15.0748 | 21.7948 | 7.3632 | -1.2139 | -3.1313 | 0 | 0 | 0 | 0 | 0
318 | 8 | 0 | 14 |  | -0.32672 | 4.0798 | 15.0748 | 21.7948 | 8.3632 | -0.9521 | 4.4615 | 0 | 11.6667 | 11.6667 | 18.522 | 0
318 | 9 | 169 | 61 |  | -0.32672 | 4.0798 | 15.0748 | 21.7948 | 9.3632 | -0.6903 | 10.8073 | 92.9581 | 50.8333 | 143.7915 | 228.2834 | 0
318 | 10 | 447 | 70 |  | -0.32672 | 4.0798 | 15.0748 | 21.7948 | 10.3632 | -0.4285 | 15.4889 | 299.9857 | 58.3333 | 358.319 | 568.8672 | 1
318 | 11 | 425 | 109 |  | -0.32672 | 4.0798 | 15.0748 | 21.7948 | 11.3632 | -0.1667 | 18.1198 | 313.6505 | 90.8333 | 404.4839 | 642.1586 | 1
318 | 12 | 331 | 122 |  | -0.32672 | 4.0798 | 15.0748 | 21.7948 | 12.3632 | 0.095098 | 18.4436 | 246.9812 | 101.6667 | 348.6479 | 553.5134 | 1
318 | 13 | 499 | 93 |  | -0.32672 | 4.0798 | 15.0748 | 21.7948 | 13.3632 | 0.3569 | 16.4264 | 346.8295 | 77.5 | 424.3295 | 673.6656 | 1
318 | 14 | 268 | 97 |  | -0.32672 | 4.0798 | 15.0748 | 21.7948 | 14.3632 | 0.6187 | 12.2707 | 157.6193 | 80.8333 | 238.4526 | 378.5674 | 0
318 | 15 | 305 | 57 |  | -0.32672 | 4.0798 | 15.0748 | 21.7948 | 15.3632 | 0.8805 | 6.3384 | 131.9738 | 47.5 | 179.4738 | 284.9326 | 0
318 | 16 | 0 | 23 |  | -0.32672 | 4.0798 | 15.0748 | 21.7948 | 16.3632 | 1.1423 | -0.95384 | 0 | 19.1667 | 19.1667 | 30.429 | 0
318 | 17 | 0 | 0 |  | -0.32672 | 4.0798 | 15.0748 | 21.7948 | 17.3632 | 1.4041 | -9.2042 | 0 | 0 | 0 | 0 | 0
318 | 18 | 0 | 0 |  | -0.32672 | 4.0798 | 15.0748 | 21.7948 | 18.3632 | 1.6659 | -18.0443 | 0 | 0 | 0 | 0 | 0
318 | 19 | 0 | 0 |  | -0.32672 | 4.0798 | 15.0748 | 21.7948 | 19.3632 | 1.9277 | -27.1187 | 0 | 0 | 0 | 0 | 0
318 | 20 | 0 | 0 |  | -0.32672 | 4.0798 | 15.0748 | 21.7948 | 20.3632 | 2.1895 | -36.0327 | 0 | 0 | 0 | 0 | 0
318 | 21 | 0 | 0 |  | -0.32672 | 4.0798 | 15.0748 | 21.7948 | 21.3632 | 2.4513 | -44.264 | 0 | 0 | 0 | 0 | 0
318 | 22 | 0 | 0 |  | -0.32672 | 4.0798 | 15.0748 | 21.7948 | 22.3632 | 2.7131 | -51.0332 | 0 | 0 | 0 | 0 | 0
318 | 23 | 0 | 0 |  | -0.32672 | 4.0798 | 15.0748 | 21.7948 | 23.3632 | 2.9749 | -55.2317 | 0 | 0 | 0 | 0 | 0
318 | 24 | 0 | 0 |  | -0.32672 | 4.0798 | 15.0748 | 21.7948 | 24.3632 | 3.2367 | -55.7744 | 0 | 0 | 0 | 0 | 0
319 | 1 | 0 | 0 |  | -0.33095 | 4.097 | 14.8769 | 21.5969 | 1.3599 | -2.7856 | -52.7329 | 0 | 0 | 0 | 0 | 0
319 | 2 | 0 | 0 |  | -0.33095 | 4.097 | 14.8769 | 21.5969 | 2.3599 | -2.5238 | -46.5341 | 0 | 0 | 0 | 0 | 0
319 | 3 | 0 | 0 |  | -0.33095 | 4.097 | 14.8769 | 21.5969 | 3.3599 | -2.262 | -38.6012 | 0 | 0 | 0 | 0 | 0
319 | 4 | 0 | 0 |  | -0.33095 | 4.097 | 14.8769 | 21.5969 | 4.3599 | -2.0002 | -29.8084 | 0 | 0 | 0 | 0 | 0
319 | 5 | 0 | 0 |  | -0.33095 | 4.097 | 14.8769 | 21.5969 | 5.3599 | -1.7384 | -20.7346 | 0 | 0 | 0 | 0 | 0
319 | 6 | 0 | 0 |  | -0.33095 | 4.097 | 14.8769 | 21.5969 | 6.3599 | -1.4766 | -11.798 | 0 | 0 | 0 | 0 | 0
319 | 7 | 0 | 0 |  | -0.33095 | 4.097 | 14.8769 | 21.5969 | 7.3599 | -1.2148 | -3.3572 | 0 | 0 | 0 | 0 | 0
319 | 8 | 0 | 4 |  | -0.33095 | 4.097 | 14.8769 | 21.5969 | 8.3599 | -0.95296 | 4.2278 | 0 | 3.3333 | 3.3333 | 5.292 | 0
319 | 9 | 0 | 29 |  | -0.33095 | 4.097 | 14.8769 | 21.5969 | 9.3599 | -0.69116 | 10.5661 | 0 | 24.1667 | 24.1667 | 38.367 | 0
319 | 10 | 0 | 61 |  | -0.33095 | 4.097 | 14.8769 | 21.5969 | 10.3599 | -0.42936 | 15.2428 | 0 | 50.8333 | 50.8333 | 80.703 | 1
319 | 11 | 0 | 85 |  | -0.33095 | 4.097 | 14.8769 | 21.5969 | 11.3599 | -0.16757 | 17.8739 | 0 | 70.8333 | 70.8333 | 112.455 | 1
319 | 12 | 0 | 95 |  | -0.33095 | 4.097 | 14.8769 | 21.5969 | 12.3599 | 0.094234 | 18.2045 | 0 | 79.1667 | 79.1667 | 125.685 | 1
319 | 13 | 0 | 89 |  | -0.33095 | 4.097 | 14.8769 | 21.5969 | 13.3599 | 0.35603 | 16.2003 | 0 | 74.1667 | 74.1667 | 117.747 | 1
319 | 14 | 0 | 69 |  | -0.33095 | 4.097 | 14.8769 | 21.5969 | 14.3599 | 0.61783 | 12.0614 | 0 | 57.5 | 57.5 | 91.287 | 0
319 | 15 | 0 | 38 |  | -0.33095 | 4.097 | 14.8769 | 21.5969 | 15.3599 | 0.87963 | 6.1465 | 0 | 31.6667 | 31.6667 | 50.274 | 0
319 | 16 | 0 | 8 |  | -0.33095 | 4.097 | 14.8769 | 21.5969 | 16.3599 | 1.1414 | -1.1302 | 0 | 6.6667 | 6.6667 | 10.584 | 0
319 | 17 | 0 | 0 |  | -0.33095 | 4.097 | 14.8769 | 21.5969 | 17.3599 | 1.4032 | -9.3686 | 0 | 0 | 0 | 0 | 0
319 | 18 | 0 | 0 |  | -0.33095 | 4.097 | 14.8769 | 21.5969 | 18.3599 | 1.665 | -18.2017 | 0 | 0 | 0 | 0 | 0
319 | 19 | 0 | 0 |  | -0.33095 | 4.097 | 14.8769 | 21.5969 | 19.3599 | 1.9268 | -27.2752 | 0 | 0 | 0 | 0 | 0
319 | 20 | 0 | 0 |  | -0.33095 | 4.097 | 14.8769 | 21.5969 | 20.3599 | 2.1886 | -36.1958 | 0 | 0 | 0 | 0 | 0
319 | 21 | 0 | 0 |  | -0.33095 | 4.097 | 14.8769 | 21.5969 | 21.3599 | 2.4504 | -44.4426 | 0 | 0 | 0 | 0 | 0
319 | 22 | 0 | 0 |  | -0.33095 | 4.097 | 14.8769 | 21.5969 | 22.3599 | 2.7122 | -51.2363 | 0 | 0 | 0 | 0 | 0
319 | 23 | 0 | 0 |  | -0.33095 | 4.097 | 14.8769 | 21.5969 | 23.3599 | 2.974 | -55.4618 | 0 | 0 | 0 | 0 | 0
319 | 24 | 0 | 0 |  | -0.33095 | 4.097 | 14.8769 | 21.5969 | 24.3599 | 3.2358 | -56.0203 | 0 | 0 | 0 | 0 | 0
320 | 1 | 0 | 0 |  | -0.33508 | 4.1142 | 14.6663 | 21.3863 | 1.3564 | -2.7865 | -52.9722 | 0 | 0 | 0 | 0 | 0
320 | 2 | 0 | 0 |  | -0.33508 | 4.1142 | 14.6663 | 21.3863 | 2.3564 | -2.5247 | -46.7631 | 0 | 0 | 0 | 0 | 0
320 | 3 | 0 | 0 |  | -0.33508 | 4.1142 | 14.6663 | 21.3863 | 3.3564 | -2.2629 | -38.8207 | 0 | 0 | 0 | 0 | 0
320 | 4 | 0 | 0 |  | -0.33508 | 4.1142 | 14.6663 | 21.3863 | 4.3564 | -2.0011 | -30.0228 | 0 | 0 | 0 | 0 | 0
320 | 5 | 0 | 0 |  | -0.33508 | 4.1142 | 14.6663 | 21.3863 | 5.3564 | -1.7393 | -20.9485 | 0 | 0 | 0 | 0 | 0
320 | 6 | 0 | 0 |  | -0.33508 | 4.1142 | 14.6663 | 21.3863 | 6.3564 | -1.4775 | -12.0151 | 0 | 0 | 0 | 0 | 0
320 | 7 | 0 | 0 |  | -0.33508 | 4.1142 | 14.6663 | 21.3863 | 7.3564 | -1.2157 | -3.5802 | 0 | 0 | 0 | 0 | 0
320 | 8 | 0 | 10 |  | -0.33508 | 4.1142 | 14.6663 | 21.3863 | 8.3564 | -0.95388 | 3.9974 | 0 | 8.3333 | 8.3333 | 13.23 | 0
320 | 9 | 177 | 41 |  | -0.33508 | 4.1142 | 14.6663 | 21.3863 | 9.3564 | -0.69208 | 10.3287 | 96.3014 | 34.1667 | 130.4681 | 207.1311 | 0
320 | 10 | 130 | 92 |  | -0.33508 | 4.1142 | 14.6663 | 21.3863 | 10.3564 | -0.43028 | 15.0012 | 86.4672 | 76.6667 | 163.1339 | 258.9914 | 1
320 | 11 | 377 | 117 |  | -0.33508 | 4.1142 | 14.6663 | 21.3863 | 11.3564 | -0.16848 | 17.6331 | 276.0471 | 97.5 | 373.5471 | 593.0434 | 1
320 | 12 | 568 | 81 |  | -0.33508 | 4.1142 | 14.6663 | 21.3863 | 12.3564 | 0.093315 | 17.9711 | 420.7561 | 67.5 | 488.2561 | 775.1554 | 1
320 | 13 | 496 | 89 |  | -0.33508 | 4.1142 | 14.6663 | 21.3863 | 13.3564 | 0.35511 | 15.9802 | 342.3352 | 74.1667 | 416.5019 | 661.2384 | 1
320 | 14 | 261 | 94 |  | -0.33508 | 4.1142 | 14.6663 | 21.3863 | 14.3564 | 0.61691 | 11.8581 | 152.4082 | 78.3333 | 230.7416 | 366.3253 | 0
320 | 15 | 60 | 66 |  | -0.33508 | 4.1142 | 14.6663 | 21.3863 | 15.3564 | 0.87871 | 5.9608 | 25.7551 | 55 | 80.7551 | 128.2068 | 0
320 | 16 | 0 | 22 |  | -0.33508 | 4.1142 | 14.6663 | 21.3863 | 16.3564 | 1.1405 | -1.3003 | 0 | 18.3333 | 18.3333 | 29.106 | 0
320 | 17 | 0 | 0 |  | -0.33508 | 4.1142 | 14.6663 | 21.3863 | 17.3564 | 1.4023 | -9.5268 | 0 | 0 | 0 | 0 | 0
320 | 18 | 0 | 0 |  | -0.33508 | 4.1142 | 14.6663 | 21.3863 | 18.3564 | 1.6641 | -18.3529 | 0 | 0 | 0 | 0 | 0
320 | 19 | 0 | 0 |  | -0.33508 | 4.1142 | 14.6663 | 21.3863 | 19.3564 | 1.9259 | -27.4254 | 0 | 0 | 0 | 0 | 0
320 | 20 | 0 | 0 |  | -0.33508 | 4.1142 | 14.6663 | 21.3863 | 20.3564 | 2.1877 | -36.3524 | 0 | 0 | 0 | 0 | 0
320 | 21 | 0 | 0 |  | -0.33508 | 4.1142 | 14.6663 | 21.3863 | 21.3564 | 2.4495 | -44.6146 | 0 | 0 | 0 | 0 | 0
320 | 22 | 0 | 0 |  | -0.33508 | 4.1142 | 14.6663 | 21.3863 | 22.3564 | 2.7113 | -51.4328 | 0 | 0 | 0 | 0 | 0
320 | 23 | 0 | 0 |  | -0.33508 | 4.1142 | 14.6663 | 21.3863 | 23.3564 | 2.9731 | -55.6859 | 0 | 0 | 0 | 0 | 0
320 | 24 | 0 | 0 |  | -0.33508 | 4.1142 | 14.6663 | 21.3863 | 24.3564 | 3.2349 | -56.2609 | 0 | 0 | 0 | 0 | 0
321 | 1 | 0 | 0 |  | -0.33912 | 4.1314 | 14.4432 | 21.1632 | 1.3527 | -2.7875 | -53.2072 | 0 | 0 | 0 | 0 | 0
321 | 2 | 0 | 0 |  | -0.33912 | 4.1314 | 14.4432 | 21.1632 | 2.3527 | -2.5257 | -46.9886 | 0 | 0 | 0 | 0 | 0
321 | 3 | 0 | 0 |  | -0.33912 | 4.1314 | 14.4432 | 21.1632 | 3.3527 | -2.2639 | -39.0373 | 0 | 0 | 0 | 0 | 0
321 | 4 | 0 | 0 |  | -0.33912 | 4.1314 | 14.4432 | 21.1632 | 4.3527 | -2.0021 | -30.2346 | 0 | 0 | 0 | 0 | 0
321 | 5 | 0 | 0 |  | -0.33912 | 4.1314 | 14.4432 | 21.1632 | 5.3527 | -1.7403 | -21.1598 | 0 | 0 | 0 | 0 | 0
321 | 6 | 0 | 0 |  | -0.33912 | 4.1314 | 14.4432 | 21.1632 | 6.3527 | -1.4785 | -12.2295 | 0 | 0 | 0 | 0 | 0
321 | 7 | 0 | 0 |  | -0.33912 | 4.1314 | 14.4432 | 21.1632 | 7.3527 | -1.2167 | -3.8002 | 0 | 0 | 0 | 0 | 0
321 | 8 | 0 | 10 |  | -0.33912 | 4.1314 | 14.4432 | 21.1632 | 8.3527 | -0.95486 | 3.7705 | 0 | 8.3333 | 8.3333 | 13.23 | 0
321 | 9 | 144 | 55 |  | -0.33912 | 4.1314 | 14.4432 | 21.1632 | 9.3527 | -0.69306 | 10.0954 | 77.921 | 45.8333 | 123.7543 | 196.4724 | 0
321 | 10 | 422 | 68 |  | -0.33912 | 4.1314 | 14.4432 | 21.1632 | 10.3527 | -0.43126 | 14.7642 | 279.4445 | 56.6667 | 336.1112 | 533.6101 | 1
321 | 11 | 299 | 108 |  | -0.33912 | 4.1314 | 14.4432 | 21.1632 | 11.3527 | -0.16946 | 17.3976 | 218.0892 | 90 | 308.0892 | 489.1224 | 1
321 | 12 | 150 | 141 |  | -0.33912 | 4.1314 | 14.4432 | 21.1632 | 12.3527 | 0.092342 | 17.7434 | 110.7227 | 117.5 | 228.2227 | 362.3264 | 1
321 | 13 | 123 | 140 |  | -0.33912 | 4.1314 | 14.4432 | 21.1632 | 13.3527 | 0.35414 | 15.7661 | 84.6071 | 116.6667 | 201.2738 | 319.5422 | 1
321 | 14 | 23 | 100 |  | -0.33912 | 4.1314 | 14.4432 | 21.1632 | 14.3527 | 0.61594 | 11.6611 | 13.385 | 83.3333 | 96.7183 | 153.55 | 0
321 | 15 | 1 | 57 |  | -0.33912 | 4.1314 | 14.4432 | 21.1632 | 15.3527 | 0.87774 | 5.7812 | 0.42765 | 47.5 | 47.9276 | 76.0899 | 0
321 | 16 | 0 | 12 |  | -0.33912 | 4.1314 | 14.4432 | 21.1632 | 16.3527 | 1.1395 | -1.4643 | 0 | 10 | 10 | 15.876 | 0
321 | 17 | 0 | 0 |  | -0.33912 | 4.1314 | 14.4432 | 21.1632 | 17.3527 | 1.4013 | -9.6789 | 0 | 0 | 0 | 0 | 0
321 | 18 | 0 | 0 |  | -0.33912 | 4.1314 | 14.4432 | 21.1632 | 18.3527 | 1.6631 | -18.4978 | 0 | 0 | 0 | 0 | 0
321 | 19 | 0 | 0 |  | -0.33912 | 4.1314 | 14.4432 | 21.1632 | 19.3527 | 1.9249 | -27.5691 | 0 | 0 | 0 | 0 | 0
321 | 20 | 0 | 0 |  | -0.33912 | 4.1314 | 14.4432 | 21.1632 | 20.3527 | 2.1867 | -36.5024 | 0 | 0 | 0 | 0 | 0
321 | 21 | 0 | 0 |  | -0.33912 | 4.1314 | 14.4432 | 21.1632 | 21.3527 | 2.4485 | -44.7799 | 0 | 0 | 0 | 0 | 0
321 | 22 | 0 | 0 |  | -0.33912 | 4.1314 | 14.4432 | 21.1632 | 22.3527 | 2.7103 | -51.6226 | 0 | 0 | 0 | 0 | 0
321 | 23 | 0 | 0 |  | -0.33912 | 4.1314 | 14.4432 | 21.1632 | 23.3527 | 2.9721 | -55.9038 | 0 | 0 | 0 | 0 | 0
321 | 24 | 0 | 0 |  | -0.33912 | 4.1314 | 14.4432 | 21.1632 | 24.3527 | 3.2339 | -56.4963 | 0 | 0 | 0 | 0 | 0
322 | 1 | 0 | 0 |  | -0.34306 | 4.1486 | 14.2078 | 20.9278 | 1.3488 | -2.7885 | -53.4379 | 0 | 0 | 0 | 0 | 0
322 | 2 | 0 | 0 |  | -0.34306 | 4.1486 | 14.2078 | 20.9278 | 2.3488 | -2.5267 | -47.2106 | 0 | 0 | 0 | 0 | 0
322 | 3 | 0 | 0 |  | -0.34306 | 4.1486 | 14.2078 | 20.9278 | 3.3488 | -2.2649 | -39.251 | 0 | 0 | 0 | 0 | 0
322 | 4 | 0 | 0 |  | -0.34306 | 4.1486 | 14.2078 | 20.9278 | 4.3488 | -2.0031 | -30.4437 | 0 | 0 | 0 | 0 | 0
322 | 5 | 0 | 0 |  | -0.34306 | 4.1486 | 14.2078 | 20.9278 | 5.3488 | -1.7413 | -21.3685 | 0 | 0 | 0 | 0 | 0
322 | 6 | 0 | 0 |  | -0.34306 | 4.1486 | 14.2078 | 20.9278 | 6.3488 | -1.4795 | -12.4411 | 0 | 0 | 0 | 0 | 0
322 | 7 | 0 | 0 |  | -0.34306 | 4.1486 | 14.2078 | 20.9278 | 7.3488 | -1.2177 | -4.0172 | 0 | 0 | 0 | 0 | 0
322 | 8 | 0 | 8 |  | -0.34306 | 4.1486 | 14.2078 | 20.9278 | 8.3488 | -0.95588 | 3.5471 | 0 | 6.6667 | 6.6667 | 10.584 | 0
322 | 9 | 67 | 43 |  | -0.34306 | 4.1486 | 14.2078 | 20.9278 | 9.3488 | -0.69408 | 9.8662 | 36.0582 | 35.8333 | 71.8915 | 114.135 | 0
322 | 10 | 85 | 97 |  | -0.34306 | 4.1486 | 14.2078 | 20.9278 | 10.3488 | -0.43228 | 14.532 | 56.039 | 80.8333 | 136.8724 | 217.2986 | 1
322 | 11 | 30 | 119 |  | -0.34306 | 4.1486 | 14.2078 | 20.9278 | 11.3488 | -0.17048 | 17.1674 | 21.7985 | 99.1667 | 120.9651 | 192.0443 | 1
322 | 12 | 40 | 131 |  | -0.34306 | 4.1486 | 14.2078 | 20.9278 | 12.3488 | 0.091315 | 17.5214 | 29.4237 | 109.1667 | 138.5904 | 220.0261 | 1
322 | 13 | 28 | 126 |  | -0.34306 | 4.1486 | 14.2078 | 20.9278 | 13.3488 | 0.35311 | 15.558 | 19.1968 | 105 | 124.1968 | 197.1749 | 1
322 | 14 | 19 | 98 |  | -0.34306 | 4.1486 | 14.2078 | 20.9278 | 14.3488 | 0.61491 | 11.4702 | 11.0209 | 81.6667 | 92.6876 | 147.1508 | 0
322 | 15 | 0 | 55 |  | -0.34306 | 4.1486 | 14.2078 | 20.9278 | 15.3488 | 0.87671 | 5.6079 | 0 | 45.8333 | 45.8333 | 72.765 | 0
322 | 16 | 0 | 11 |  | -0.34306 | 4.1486 | 14.2078 | 20.9278 | 16.3488 | 1.1385 | -1.622 | 0 | 9.1667 | 9.1667 | 14.553 | 0
322 | 17 | 0 | 0 |  | -0.34306 | 4.1486 | 14.2078 | 20.9278 | 17.3488 | 1.4003 | -9.8246 | 0 | 0 | 0 | 0 | 0
322 | 18 | 0 | 0 |  | -0.34306 | 4.1486 | 14.2078 | 20.9278 | 18.3488 | 1.6621 | -18.6364 | 0 | 0 | 0 | 0 | 0
322 | 19 | 0 | 0 |  | -0.34306 | 4.1486 | 14.2078 | 20.9278 | 19.3488 | 1.9239 | -27.7065 | 0 | 0 | 0 | 0 | 0
322 | 20 | 0 | 0 |  | -0.34306 | 4.1486 | 14.2078 | 20.9278 | 20.3488 | 2.1857 | -36.6458 | 0 | 0 | 0 | 0 | 0
322 | 21 | 0 | 0 |  | -0.34306 | 4.1486 | 14.2078 | 20.9278 | 21.3488 | 2.4475 | -44.9384 | 0 | 0 | 0 | 0 | 0
322 | 22 | 0 | 0 |  | -0.34306 | 4.1486 | 14.2078 | 20.9278 | 22.3488 | 2.7093 | -51.8057 | 0 | 0 | 0 | 0 | 0
322 | 23 | 0 | 0 |  | -0.34306 | 4.1486 | 14.2078 | 20.9278 | 23.3488 | 2.9711 | -56.1153 | 0 | 0 | 0 | 0 | 0
322 | 24 | 0 | 0 |  | -0.34306 | 4.1486 | 14.2078 | 20.9278 | 24.3488 | 3.2329 | -56.7264 | 0 | 0 | 0 | 0 | 0
323 | 1 | 0 | 0 |  | -0.34689 | 4.1658 | 13.9603 | 20.6803 | 1.3447 | -2.7896 | -53.6642 | 0 | 0 | 0 | 0 | 0
323 | 2 | 0 | 0 |  | -0.34689 | 4.1658 | 13.9603 | 20.6803 | 2.3447 | -2.5278 | -47.429 | 0 | 0 | 0 | 0 | 0
323 | 3 | 0 | 0 |  | -0.34689 | 4.1658 | 13.9603 | 20.6803 | 3.3447 | -2.266 | -39.4615 | 0 | 0 | 0 | 0 | 0
323 | 4 | 0 | 0 |  | -0.34689 | 4.1658 | 13.9603 | 20.6803 | 4.3447 | -2.0042 | -30.65 | 0 | 0 | 0 | 0 | 0
323 | 5 | 0 | 0 |  | -0.34689 | 4.1658 | 13.9603 | 20.6803 | 5.3447 | -1.7424 | -21.5744 | 0 | 0 | 0 | 0 | 0
323 | 6 | 0 | 0 |  | -0.34689 | 4.1658 | 13.9603 | 20.6803 | 6.3447 | -1.4806 | -12.6499 | 0 | 0 | 0 | 0 | 0
323 | 7 | 0 | 0 |  | -0.34689 | 4.1658 | 13.9603 | 20.6803 | 7.3447 | -1.2188 | -4.2309 | 0 | 0 | 0 | 0 | 0
323 | 8 | 0 | 3 |  | -0.34689 | 4.1658 | 13.9603 | 20.6803 | 8.3447 | -0.95696 | 3.3274 | 0 | 2.5 | 2.5 | 3.969 | 0
323 | 9 | 0 | 24 |  | -0.34689 | 4.1658 | 13.9603 | 20.6803 | 9.3447 | -0.69516 | 9.6412 | 0 | 20 | 20 | 31.752 | 0
323 | 10 | 0 | 55 |  | -0.34689 | 4.1658 | 13.9603 | 20.6803 | 10.3447 | -0.43336 | 14.3046 | 0 | 45.8333 | 45.8333 | 72.765 | 1
323 | 11 | 0 | 78 |  | -0.34689 | 4.1658 | 13.9603 | 20.6803 | 11.3447 | -0.17156 | 16.9425 | 0 | 65 | 65 | 103.194 | 1
323 | 12 | 0 | 88 |  | -0.34689 | 4.1658 | 13.9603 | 20.6803 | 12.3447 | 0.090235 | 17.3053 | 0 | 73.3333 | 73.3333 | 116.424 | 1
323 | 13 | 0 | 83 |  | -0.34689 | 4.1658 | 13.9603 | 20.6803 | 13.3447 | 0.35203 | 15.3561 | 0 | 69.1667 | 69.1667 | 109.809 | 1
323 | 14 | 0 | 64 |  | -0.34689 | 4.1658 | 13.9603 | 20.6803 | 14.3447 | 0.61383 | 11.2856 | 0 | 53.3333 | 53.3333 | 84.672 | 0
323 | 15 | 0 | 34 |  | -0.34689 | 4.1658 | 13.9603 | 20.6803 | 15.3447 | 0.87563 | 5.4409 | 0 | 28.3333 | 28.3333 | 44.982 | 0
323 | 16 | 0 | 7 |  | -0.34689 | 4.1658 | 13.9603 | 20.6803 | 16.3447 | 1.1374 | -1.7735 | 0 | 5.8333 | 5.8333 | 9.261 | 0
323 | 17 | 0 | 0 |  | -0.34689 | 4.1658 | 13.9603 | 20.6803 | 17.3447 | 1.3992 | -9.9641 | 0 | 0 | 0 | 0 | 0
323 | 18 | 0 | 0 |  | -0.34689 | 4.1658 | 13.9603 | 20.6803 | 18.3447 | 1.661 | -18.7687 | 0 | 0 | 0 | 0 | 0
323 | 19 | 0 | 0 |  | -0.34689 | 4.1658 | 13.9603 | 20.6803 | 19.3447 | 1.9228 | -27.8374 | 0 | 0 | 0 | 0 | 0
323 | 20 | 0 | 0 |  | -0.34689 | 4.1658 | 13.9603 | 20.6803 | 20.3447 | 2.1846 | -36.7827 | 0 | 0 | 0 | 0 | 0
323 | 21 | 0 | 0 |  | -0.34689 | 4.1658 | 13.9603 | 20.6803 | 21.3447 | 2.4464 | -45.0902 | 0 | 0 | 0 | 0 | 0
323 | 22 | 0 | 0 |  | -0.34689 | 4.1658 | 13.9603 | 20.6803 | 22.3447 | 2.7082 | -51.982 | 0 | 0 | 0 | 0 | 0
323 | 23 | 0 | 0 |  | -0.34689 | 4.1658 | 13.9603 | 20.6803 | 23.3447 | 2.97 | -56.3205 | 0 | 0 | 0 | 0 | 0
323 | 24 | 0 | 0 |  | -0.34689 | 4.1658 | 13.9603 | 20.6803 | 24.3447 | 3.2318 | -56.9509 | 0 | 0 | 0 | 0 | 0
324 | 1 | 0 | 0 |  | -0.35063 | 4.1831 | 13.7008 | 20.4208 | 1.3403 | -2.7907 | -53.8859 | 0 | 0 | 0 | 0 | 0
324 | 2 | 0 | 0 |  | -0.35063 | 4.1831 | 13.7008 | 20.4208 | 2.3403 | -2.5289 | -47.6437 | 0 | 0 | 0 | 0 | 0
324 | 3 | 0 | 0 |  | -0.35063 | 4.1831 | 13.7008 | 20.4208 | 3.3403 | -2.2671 | -39.6689 | 0 | 0 | 0 | 0 | 0
324 | 4 | 0 | 0 |  | -0.35063 | 4.1831 | 13.7008 | 20.4208 | 4.3403 | -2.0053 | -30.8534 | 0 | 0 | 0 | 0 | 0
324 | 5 | 0 | 0 |  | -0.35063 | 4.1831 | 13.7008 | 20.4208 | 5.3403 | -1.7435 | -21.7775 | 0 | 0 | 0 | 0 | 0
324 | 6 | 0 | 0 |  | -0.35063 | 4.1831 | 13.7008 | 20.4208 | 6.3403 | -1.4817 | -12.8556 | 0 | 0 | 0 | 0 | 0
324 | 7 | 0 | 0 |  | -0.35063 | 4.1831 | 13.7008 | 20.4208 | 7.3403 | -1.2199 | -4.4414 | 0 | 0 | 0 | 0 | 0
324 | 8 | 0 | 7 |  | -0.35063 | 4.1831 | 13.7008 | 20.4208 | 8.3403 | -0.95809 | 3.1114 | 0 | 5.8333 | 5.8333 | 9.261 | 0
324 | 9 | 173 | 44 |  | -0.35063 | 4.1831 | 13.7008 | 20.4208 | 9.3403 | -0.6963 | 9.4205 | 92.1023 | 36.6667 | 128.769 | 204.4336 | 0
324 | 10 | 406 | 67 |  | -0.35063 | 4.1831 | 13.7008 | 20.4208 | 10.3403 | -0.4345 | 14.0821 | 265.3518 | 55.8333 | 321.1852 | 509.9136 | 1
324 | 11 | 537 | 72 |  | -0.35063 | 4.1831 | 13.7008 | 20.4208 | 11.3403 | -0.1727 | 16.7232 | 387.2858 | 60 | 447.2858 | 710.111 | 1
324 | 12 | 548 | 83 |  | -0.35063 | 4.1831 | 13.7008 | 20.4208 | 12.3403 | 0.089103 | 17.0951 | 400.3989 | 69.1667 | 469.5655 | 745.4822 | 1
324 | 13 | 529 | 81 |  | -0.35063 | 4.1831 | 13.7008 | 20.4208 | 13.3403 | 0.3509 | 15.1604 | 360.4016 | 67.5 | 427.9016 | 679.3365 | 1
324 | 14 | 459 | 69 |  | -0.35063 | 4.1831 | 13.7008 | 20.4208 | 14.3403 | 0.6127 | 11.1073 | 264.5986 | 57.5 | 322.0986 | 511.3637 | 0
324 | 15 | 265 | 53 |  | -0.35063 | 4.1831 | 13.7008 | 20.4208 | 15.3403 | 0.8745 | 5.2802 | 112.1839 | 44.1667 | 156.3506 | 248.2222 | 0
324 | 16 | 0 | 18 |  | -0.35063 | 4.1831 | 13.7008 | 20.4208 | 16.3403 | 1.1363 | -1.9186 | 0 | 15 | 15 | 23.814 | 0
324 | 17 | 0 | 0 |  | -0.35063 | 4.1831 | 13.7008 | 20.4208 | 17.3403 | 1.3981 | -10.0973 | 0 | 0 | 0 | 0 | 0
324 | 18 | 0 | 0 |  | -0.35063 | 4.1831 | 13.7008 | 20.4208 | 18.3403 | 1.6599 | -18.8946 | 0 | 0 | 0 | 0 | 0
324 | 19 | 0 | 0 |  | -0.35063 | 4.1831 | 13.7008 | 20.4208 | 19.3403 | 1.9217 | -27.9618 | 0 | 0 | 0 | 0 | 0
324 | 20 | 0 | 0 |  | -0.35063 | 4.1831 | 13.7008 | 20.4208 | 20.3403 | 2.1835 | -36.9129 | 0 | 0 | 0 | 0 | 0
324 | 21 | 0 | 0 |  | -0.35063 | 4.1831 | 13.7008 | 20.4208 | 21.3403 | 2.4453 | -45.2351 | 0 | 0 | 0 | 0 | 0
324 | 22 | 0 | 0 |  | -0.35063 | 4.1831 | 13.7008 | 20.4208 | 22.3403 | 2.7071 | -52.1515 | 0 | 0 | 0 | 0 | 0
324 | 23 | 0 | 0 |  | -0.35063 | 4.1831 | 13.7008 | 20.4208 | 23.3403 | 2.9689 | -56.5193 | 0 | 0 | 0 | 0 | 0
324 | 24 | 0 | 0 |  | -0.35063 | 4.1831 | 13.7008 | 20.4208 | 24.3403 | 3.2307 | -57.1699 | 0 | 0 | 0 | 0 | 0
325 | 1 | 0 | 0 |  | -0.35426 | 4.2003 | 13.4296 | 20.1496 | 1.3358 | -2.7919 | -54.103 | 0 | 0 | 0 | 0 | 0
325 | 2 | 0 | 0 |  | -0.35426 | 4.2003 | 13.4296 | 20.1496 | 2.3358 | -2.5301 | -47.8546 | 0 | 0 | 0 | 0 | 0
325 | 3 | 0 | 0 |  | -0.35426 | 4.2003 | 13.4296 | 20.1496 | 3.3358 | -2.2683 | -39.8731 | 0 | 0 | 0 | 0 | 0
325 | 4 | 0 | 0 |  | -0.35426 | 4.2003 | 13.4296 | 20.1496 | 4.3358 | -2.0065 | -31.0539 | 0 | 0 | 0 | 0 | 0
325 | 5 | 0 | 0 |  | -0.35426 | 4.2003 | 13.4296 | 20.1496 | 5.3358 | -1.7447 | -21.9777 | 0 | 0 | 0 | 0 | 0
325 | 6 | 0 | 0 |  | -0.35426 | 4.2003 | 13.4296 | 20.1496 | 6.3358 | -1.4829 | -13.0584 | 0 | 0 | 0 | 0 | 0
325 | 7 | 0 | 0 |  | -0.35426 | 4.2003 | 13.4296 | 20.1496 | 7.3358 | -1.2211 | -4.6486 | 0 | 0 | 0 | 0 | 0
325 | 8 | 0 | 4 |  | -0.35426 | 4.2003 | 13.4296 | 20.1496 | 8.3358 | -0.95928 | 2.8992 | 0 | 3.3333 | 3.3333 | 5.292 | 0
325 | 9 | 0 | 22 |  | -0.35426 | 4.2003 | 13.4296 | 20.1496 | 9.3358 | -0.69748 | 9.2043 | 0 | 18.3333 | 18.3333 | 29.106 | 0
325 | 10 | 21 | 80 |  | -0.35426 | 4.2003 | 13.4296 | 20.1496 | 10.3358 | -0.43568 | 13.8647 | 13.6664 | 66.6667 | 80.3331 | 127.5368 | 1
325 | 11 | 18 | 117 |  | -0.35426 | 4.2003 | 13.4296 | 20.1496 | 11.3358 | -0.17388 | 16.5094 | 12.9343 | 97.5 | 110.4343 | 175.3255 | 1
325 | 12 | 0 | 86 |  | -0.35426 | 4.2003 | 13.4296 | 20.1496 | 12.3358 | 0.087919 | 16.891 | 0 | 71.6667 | 71.6667 | 113.778 | 1
325 | 13 | 0 | 81 |  | -0.35426 | 4.2003 | 13.4296 | 20.1496 | 13.3358 | 0.34972 | 14.9709 | 0 | 67.5 | 67.5 | 107.163 | 1
325 | 14 | 0 | 62 |  | -0.35426 | 4.2003 | 13.4296 | 20.1496 | 14.3358 | 0.61152 | 10.9353 | 0 | 51.6667 | 51.6667 | 82.026 | 0
325 | 15 | 0 | 32 |  | -0.35426 | 4.2003 | 13.4296 | 20.1496 | 15.3358 | 0.87332 | 5.1259 | 0 | 26.6667 | 26.6667 | 42.336 | 0
325 | 16 | 0 | 6 |  | -0.35426 | 4.2003 | 13.4296 | 20.1496 | 16.3358 | 1.1351 | -2.0573 | 0 | 5 | 5 | 7.938 | 0
325 | 17 | 0 | 0 |  | -0.35426 | 4.2003 | 13.4296 | 20.1496 | 17.3358 | 1.3969 | -10.224 | 0 | 0 | 0 | 0 | 0
325 | 18 | 0 | 0 |  | -0.35426 | 4.2003 | 13.4296 | 20.1496 | 18.3358 | 1.6587 | -19.0141 | 0 | 0 | 0 | 0 | 0
325 | 19 | 0 | 0 |  | -0.35426 | 4.2003 | 13.4296 | 20.1496 | 19.3358 | 1.9205 | -28.0797 | 0 | 0 | 0 | 0 | 0
325 | 20 | 0 | 0 |  | -0.35426 | 4.2003 | 13.4296 | 20.1496 | 20.3358 | 2.1823 | -37.0364 | 0 | 0 | 0 | 0 | 0
325 | 21 | 0 | 0 |  | -0.35426 | 4.2003 | 13.4296 | 20.1496 | 21.3358 | 2.4441 | -45.3733 | 0 | 0 | 0 | 0 | 0
325 | 22 | 0 | 0 |  | -0.35426 | 4.2003 | 13.4296 | 20.1496 | 22.3358 | 2.7059 | -52.314 | 0 | 0 | 0 | 0 | 0
325 | 23 | 0 | 0 |  | -0.35426 | 4.2003 | 13.4296 | 20.1496 | 23.3358 | 2.9677 | -56.7115 | 0 | 0 | 0 | 0 | 0
325 | 24 | 0 | 0 |  | -0.35426 | 4.2003 | 13.4296 | 20.1496 | 24.3358 | 3.2295 | -57.3833 | 0 | 0 | 0 | 0 | 0
326 | 1 | 0 | 0 |  | -0.35778 | 4.2175 | 13.147 | 19.867 | 1.3311 | -2.7931 | -54.3154 | 0 | 0 | 0 | 0 | 0
326 | 2 | 0 | 0 |  | -0.35778 | 4.2175 | 13.147 | 19.867 | 2.3311 | -2.5313 | -48.0617 | 0 | 0 | 0 | 0 | 0
326 | 3 | 0 | 0 |  | -0.35778 | 4.2175 | 13.147 | 19.867 | 3.3311 | -2.2695 | -40.0739 | 0 | 0 | 0 | 0 | 0
326 | 4 | 0 | 0 |  | -0.35778 | 4.2175 | 13.147 | 19.867 | 4.3311 | -2.0077 | -31.2513 | 0 | 0 | 0 | 0 | 0
326 | 5 | 0 | 0 |  | -0.35778 | 4.2175 | 13.147 | 19.867 | 5.3311 | -1.7459 | -22.1749 | 0 | 0 | 0 | 0 | 0
326 | 6 | 0 | 0 |  | -0.35778 | 4.2175 | 13.147 | 19.867 | 6.3311 | -1.4841 | -13.2579 | 0 | 0 | 0 | 0 | 0
326 | 7 | 0 | 0 |  | -0.35778 | 4.2175 | 13.147 | 19.867 | 7.3311 | -1.2223 | -4.8522 | 0 | 0 | 0 | 0 | 0
326 | 8 | 0 | 3 |  | -0.35778 | 4.2175 | 13.147 | 19.867 | 8.3311 | -0.96051 | 2.691 | 0 | 2.5 | 2.5 | 3.969 | 0
326 | 9 | 0 | 33 |  | -0.35778 | 4.2175 | 13.147 | 19.867 | 9.3311 | -0.69871 | 8.9925 | 0 | 27.5 | 27.5 | 43.659 | 0
326 | 10 | 0 | 51 |  | -0.35778 | 4.2175 | 13.147 | 19.867 | 10.3311 | -0.43691 | 13.6523 | 0 | 42.5 | 42.5 | 67.473 | 1
326 | 11 | 0 | 75 |  | -0.35778 | 4.2175 | 13.147 | 19.867 | 11.3311 | -0.17511 | 16.3013 | 0 | 62.5 | 62.5 | 99.225 | 1
326 | 12 | 0 | 85 |  | -0.35778 | 4.2175 | 13.147 | 19.867 | 12.3311 | 0.086686 | 16.6929 | 0 | 70.8333 | 70.8333 | 112.455 | 1
326 | 13 | 0 | 80 |  | -0.35778 | 4.2175 | 13.147 | 19.867 | 13.3311 | 0.34849 | 14.7878 | 0 | 66.6667 | 66.6667 | 105.84 | 1
326 | 14 | 21 | 92 |  | -0.35778 | 4.2175 | 13.147 | 19.867 | 14.3311 | 0.61028 | 10.7698 | 12.0373 | 76.6667 | 88.7039 | 140.8264 | 0
326 | 15 | 0 | 49 |  | -0.35778 | 4.2175 | 13.147 | 19.867 | 15.3311 | 0.87208 | 4.9781 | 0 | 40.8333 | 40.8333 | 64.827 | 0
326 | 16 | 0 | 9 |  | -0.35778 | 4.2175 | 13.147 | 19.867 | 16.3311 | 1.1339 | -2.1897 | 0 | 7.5 | 7.5 | 11.907 | 0
326 | 17 | 0 | 0 |  | -0.35778 | 4.2175 | 13.147 | 19.867 | 17.3311 | 1.3957 | -10.3445 | 0 | 0 | 0 | 0 | 0
326 | 18 | 0 | 0 |  | -0.35778 | 4.2175 | 13.147 | 19.867 | 18.3311 | 1.6575 | -19.1271 | 0 | 0 | 0 | 0 | 0
326 | 19 | 0 | 0 |  | -0.35778 | 4.2175 | 13.147 | 19.867 | 19.3311 | 1.9193 | -28.1912 | 0 | 0 | 0 | 0 | 0
326 | 20 | 0 | 0 |  | -0.35778 | 4.2175 | 13.147 | 19.867 | 20.3311 | 2.1811 | -37.1533 | 0 | 0 | 0 | 0 | 0
326 | 21 | 0 | 0 |  | -0.35778 | 4.2175 | 13.147 | 19.867 | 21.3311 | 2.4429 | -45.5045 | 0 | 0 | 0 | 0 | 0
326 | 22 | 0 | 0 |  | -0.35778 | 4.2175 | 13.147 | 19.867 | 22.3311 | 2.7047 | -52.4696 | 0 | 0 | 0 | 0 | 0
326 | 23 | 0 | 0 |  | -0.35778 | 4.2175 | 13.147 | 19.867 | 23.3311 | 2.9665 | -56.897 | 0 | 0 | 0 | 0 | 0
326 | 24 | 0 | 0 |  | -0.35778 | 4.2175 | 13.147 | 19.867 | 24.3311 | 3.2283 | -57.5909 | 0 | 0 | 0 | 0 | 0
327 | 1 | 0 | 0 |  | -0.3612 | 4.2347 | 12.8531 | 19.5731 | 1.3262 | -2.7944 | -54.523 | 0 | 0 | 0 | 0 | 0
327 | 2 | 0 | 0 |  | -0.3612 | 4.2347 | 12.8531 | 19.5731 | 2.3262 | -2.5326 | -48.2648 | 0 | 0 | 0 | 0 | 0
327 | 3 | 0 | 0 |  | -0.3612 | 4.2347 | 12.8531 | 19.5731 | 3.3262 | -2.2708 | -40.2714 | 0 | 0 | 0 | 0 | 0
327 | 4 | 0 | 0 |  | -0.3612 | 4.2347 | 12.8531 | 19.5731 | 4.3262 | -2.009 | -31.4456 | 0 | 0 | 0 | 0 | 0
327 | 5 | 0 | 0 |  | -0.3612 | 4.2347 | 12.8531 | 19.5731 | 5.3262 | -1.7472 | -22.369 | 0 | 0 | 0 | 0 | 0
327 | 6 | 0 | 0 |  | -0.3612 | 4.2347 | 12.8531 | 19.5731 | 6.3262 | -1.4854 | -13.4543 | 0 | 0 | 0 | 0 | 0
327 | 7 | 0 | 0 |  | -0.3612 | 4.2347 | 12.8531 | 19.5731 | 7.3262 | -1.2236 | -5.0523 | 0 | 0 | 0 | 0 | 0
327 | 8 | 0 | 5 |  | -0.3612 | 4.2347 | 12.8531 | 19.5731 | 8.3262 | -0.96179 | 2.4868 | 0 | 4.1667 | 4.1667 | 6.615 | 0
327 | 9 | 94 | 41 |  | -0.3612 | 4.2347 | 12.8531 | 19.5731 | 9.3262 | -0.69999 | 8.7853 | 49.2465 | 34.1667 | 83.4132 | 132.4267 | 0
327 | 10 | 221 | 75 |  | -0.3612 | 4.2347 | 12.8531 | 19.5731 | 10.3262 | -0.43819 | 13.4451 | 142.6154 | 62.5 | 205.1154 | 325.6413 | 1
327 | 11 | 386 | 89 |  | -0.3612 | 4.2347 | 12.8531 | 19.5731 | 11.3262 | -0.1764 | 16.099 | 275.4013 | 74.1667 | 349.568 | 554.9741 | 1
327 | 12 | 146 | 129 |  | -0.3612 | 4.2347 | 12.8531 | 19.5731 | 12.3262 | 0.085404 | 16.5009 | 105.6635 | 107.5 | 213.1635 | 338.4184 | 1
327 | 13 | 119 | 128 |  | -0.3612 | 4.2347 | 12.8531 | 19.5731 | 13.3262 | 0.3472 | 14.611 | 80.3683 | 106.6667 | 187.0349 | 296.9367 | 1
327 | 14 | 95 | 100 |  | -0.3612 | 4.2347 | 12.8531 | 19.5731 | 14.3262 | 0.609 | 10.6108 | 54.3109 | 83.3333 | 137.6442 | 218.5239 | 0
327 | 15 | 192 | 51 |  | -0.3612 | 4.2347 | 12.8531 | 19.5731 | 15.3262 | 0.8708 | 4.8367 | 80.5972 | 42.5 | 123.0972 | 195.4291 | 0
327 | 16 | 0 | 9 |  | -0.3612 | 4.2347 | 12.8531 | 19.5731 | 16.3262 | 1.1326 | -2.3156 | 0 | 7.5 | 7.5 | 11.907 | 0
327 | 17 | 0 | 0 |  | -0.3612 | 4.2347 | 12.8531 | 19.5731 | 17.3262 | 1.3944 | -10.4585 | 0 | 0 | 0 | 0 | 0
327 | 18 | 0 | 0 |  | -0.3612 | 4.2347 | 12.8531 | 19.5731 | 18.3262 | 1.6562 | -19.2338 | 0 | 0 | 0 | 0 | 0
327 | 19 | 0 | 0 |  | -0.3612 | 4.2347 | 12.8531 | 19.5731 | 19.3262 | 1.918 | -28.2961 | 0 | 0 | 0 | 0 | 0
327 | 20 | 0 | 0 |  | -0.3612 | 4.2347 | 12.8531 | 19.5731 | 20.3262 | 2.1798 | -37.2635 | 0 | 0 | 0 | 0 | 0
327 | 21 | 0 | 0 |  | -0.3612 | 4.2347 | 12.8531 | 19.5731 | 21.3262 | 2.4416 | -45.6288 | 0 | 0 | 0 | 0 | 0
327 | 22 | 0 | 0 |  | -0.3612 | 4.2347 | 12.8531 | 19.5731 | 22.3262 | 2.7034 | -52.6181 | 0 | 0 | 0 | 0 | 0
327 | 23 | 0 | 0 |  | -0.3612 | 4.2347 | 12.8531 | 19.5731 | 23.3262 | 2.9652 | -57.0758 | 0 | 0 | 0 | 0 | 0
327 | 24 | 0 | 0 |  | -0.3612 | 4.2347 | 12.8531 | 19.5731 | 24.3262 | 3.227 | -57.7926 | 0 | 0 | 0 | 0 | 0
328 | 1 | 0 | 0 |  | -0.36452 | 4.2519 | 12.5483 | 19.2683 | 1.3211 | -2.7957 | -54.7257 | 0 | 0 | 0 | 0 | 0
328 | 2 | 0 | 0 |  | -0.36452 | 4.2519 | 12.5483 | 19.2683 | 2.3211 | -2.5339 | -48.4639 | 0 | 0 | 0 | 0 | 0
328 | 3 | 0 | 0 |  | -0.36452 | 4.2519 | 12.5483 | 19.2683 | 3.3211 | -2.2721 | -40.4654 | 0 | 0 | 0 | 0 | 0
328 | 4 | 0 | 0 |  | -0.36452 | 4.2519 | 12.5483 | 19.2683 | 4.3211 | -2.0103 | -31.6367 | 0 | 0 | 0 | 0 | 0
328 | 5 | 0 | 0 |  | -0.36452 | 4.2519 | 12.5483 | 19.2683 | 5.3211 | -1.7485 | -22.5599 | 0 | 0 | 0 | 0 | 0
328 | 6 | 0 | 0 |  | -0.36452 | 4.2519 | 12.5483 | 19.2683 | 6.3211 | -1.4867 | -13.6472 | 0 | 0 | 0 | 0 | 0
328 | 7 | 0 | 0 |  | -0.36452 | 4.2519 | 12.5483 | 19.2683 | 7.3211 | -1.2249 | -5.2487 | 0 | 0 | 0 | 0 | 0
328 | 8 | 0 | 2 |  | -0.36452 | 4.2519 | 12.5483 | 19.2683 | 8.3211 | -0.96312 | 2.2867 | 0 | 1.6667 | 1.6667 | 2.646 | 0
328 | 9 | 16 | 37 |  | -0.36452 | 4.2519 | 12.5483 | 19.2683 | 9.3211 | -0.70132 | 8.5828 | 8.3382 | 30.8333 | 39.1715 | 62.1887 | 0
328 | 10 | 11 | 76 |  | -0.36452 | 4.2519 | 12.5483 | 19.2683 | 10.3211 | -0.43953 | 13.2432 | 7.0692 | 63.3333 | 70.4025 | 111.7711 | 1
328 | 11 | 131 | 114 |  | -0.36452 | 4.2519 | 12.5483 | 19.2683 | 11.3211 | -0.17773 | 15.9025 | 93.1424 | 95 | 188.1424 | 298.6949 | 1
328 | 12 | 45 | 118 |  | -0.36452 | 4.2519 | 12.5483 | 19.2683 | 12.3211 | 0.084074 | 16.3152 | 32.4695 | 98.3333 | 130.8028 | 207.6626 | 1
328 | 13 | 0 | 77 |  | -0.36452 | 4.2519 | 12.5483 | 19.2683 | 13.3211 | 0.34587 | 14.4407 | 0 | 64.1667 | 64.1667 | 101.871 | 1
328 | 14 | 0 | 58 |  | -0.36452 | 4.2519 | 12.5483 | 19.2683 | 14.3211 | 0.60767 | 10.4583 | 0 | 48.3333 | 48.3333 | 76.734 | 0
328 | 15 | 0 | 47 |  | -0.36452 | 4.2519 | 12.5483 | 19.2683 | 15.3211 | 0.86947 | 4.7018 | 0 | 39.1667 | 39.1667 | 62.181 | 0
328 | 16 | 0 | 11 |  | -0.36452 | 4.2519 | 12.5483 | 19.2683 | 16.3211 | 1.1313 | -2.4351 | 0 | 9.1667 | 9.1667 | 14.553 | 0
328 | 17 | 0 | 0 |  | -0.36452 | 4.2519 | 12.5483 | 19.2683 | 17.3211 | 1.3931 | -10.566 | 0 | 0 | 0 | 0 | 0
328 | 18 | 0 | 0 |  | -0.36452 | 4.2519 | 12.5483 | 19.2683 | 18.3211 | 1.6549 | -19.334 | 0 | 0 | 0 | 0 | 0
328 | 19 | 0 | 0 |  | -0.36452 | 4.2519 | 12.5483 | 19.2683 | 19.3211 | 1.9167 | -28.3945 | 0 | 0 | 0 | 0 | 0
328 | 20 | 0 | 0 |  | -0.36452 | 4.2519 | 12.5483 | 19.2683 | 20.3211 | 2.1785 | -37.367 | 0 | 0 | 0 | 0 | 0
328 | 21 | 0 | 0 |  | -0.36452 | 4.2519 | 12.5483 | 19.2683 | 21.3211 | 2.4403 | -45.7463 | 0 | 0 | 0 | 0 | 0
328 | 22 | 0 | 0 |  | -0.36452 | 4.2519 | 12.5483 | 19.2683 | 22.3211 | 2.7021 | -52.7597 | 0 | 0 | 0 | 0 | 0
328 | 23 | 0 | 0 |  | -0.36452 | 4.2519 | 12.5483 | 19.2683 | 23.3211 | 2.9639 | -57.2479 | 0 | 0 | 0 | 0 | 0
328 | 24 | 0 | 0 |  | -0.36452 | 4.2519 | 12.5483 | 19.2683 | 24.3211 | 3.2257 | -57.9884 | 0 | 0 | 0 | 0 | 0
329 | 1 | 0 | 0 |  | -0.36772 | 4.2691 | 12.2327 | 18.9527 | 1.3159 | -2.7971 | -54.9235 | 0 | 0 | 0 | 0 | 0
329 | 2 | 0 | 0 |  | -0.36772 | 4.2691 | 12.2327 | 18.9527 | 2.3159 | -2.5353 | -48.6589 | 0 | 0 | 0 | 0 | 0
329 | 3 | 0 | 0 |  | -0.36772 | 4.2691 | 12.2327 | 18.9527 | 3.3159 | -2.2735 | -40.6558 | 0 | 0 | 0 | 0 | 0
329 | 4 | 0 | 0 |  | -0.36772 | 4.2691 | 12.2327 | 18.9527 | 4.3159 | -2.0117 | -31.8245 | 0 | 0 | 0 | 0 | 0
329 | 5 | 0 | 0 |  | -0.36772 | 4.2691 | 12.2327 | 18.9527 | 5.3159 | -1.7499 | -22.7476 | 0 | 0 | 0 | 0 | 0
329 | 6 | 0 | 0 |  | -0.36772 | 4.2691 | 12.2327 | 18.9527 | 6.3159 | -1.4881 | -13.8368 | 0 | 0 | 0 | 0 | 0
329 | 7 | 0 | 0 |  | -0.36772 | 4.2691 | 12.2327 | 18.9527 | 7.3159 | -1.2263 | -5.4413 | 0 | 0 | 0 | 0 | 0
329 | 8 | 0 | 1 |  | -0.36772 | 4.2691 | 12.2327 | 18.9527 | 8.3159 | -0.9645 | 2.0908 | 0 | 0.83333 | 0.83333 | 1.323 | 0
329 | 9 | 0 | 29 |  | -0.36772 | 4.2691 | 12.2327 | 18.9527 | 9.3159 | -0.7027 | 8.3851 | 0 | 24.1667 | 24.1667 | 38.367 | 0
329 | 10 | 0 | 48 |  | -0.36772 | 4.2691 | 12.2327 | 18.9527 | 10.3159 | -0.4409 | 13.0467 | 0 | 40 | 40 | 63.504 | 1
329 | 11 | 0 | 72 |  | -0.36772 | 4.2691 | 12.2327 | 18.9527 | 11.3159 | -0.1791 | 15.7118 | 0 | 60 | 60 | 95.256 | 1
329 | 12 | 56 | 114 |  | -0.36772 | 4.2691 | 12.2327 | 18.9527 | 12.3159 | 0.082697 | 16.1358 | 40.2884 | 95 | 135.2884 | 214.7839 | 1
329 | 13 | 0 | 77 |  | -0.36772 | 4.2691 | 12.2327 | 18.9527 | 13.3159 | 0.3445 | 14.277 | 0 | 64.1667 | 64.1667 | 101.871 | 1
329 | 14 | 0 | 58 |  | -0.36772 | 4.2691 | 12.2327 | 18.9527 | 14.3159 | 0.6063 | 10.3124 | 0 | 48.3333 | 48.3333 | 76.734 | 0
329 | 15 | 0 | 29 |  | -0.36772 | 4.2691 | 12.2327 | 18.9527 | 15.3159 | 0.86809 | 4.5735 | 0 | 24.1667 | 24.1667 | 38.367 | 0
329 | 16 | 0 | 8 |  | -0.36772 | 4.2691 | 12.2327 | 18.9527 | 16.3159 | 1.1299 | -2.548 | 0 | 6.6667 | 6.6667 | 10.584 | 0
329 | 17 | 0 | 0 |  | -0.36772 | 4.2691 | 12.2327 | 18.9527 | 17.3159 | 1.3917 | -10.6672 | 0 | 0 | 0 | 0 | 0
329 | 18 | 0 | 0 |  | -0.36772 | 4.2691 | 12.2327 | 18.9527 | 18.3159 | 1.6535 | -19.4278 | 0 | 0 | 0 | 0 | 0
329 | 19 | 0 | 0 |  | -0.36772 | 4.2691 | 12.2327 | 18.9527 | 19.3159 | 1.9153 | -28.4864 | 0 | 0 | 0 | 0 | 0
329 | 20 | 0 | 0 |  | -0.36772 | 4.2691 | 12.2327 | 18.9527 | 20.3159 | 2.1771 | -37.4638 | 0 | 0 | 0 | 0 | 0
329 | 21 | 0 | 0 |  | -0.36772 | 4.2691 | 12.2327 | 18.9527 | 21.3159 | 2.4389 | -45.8568 | 0 | 0 | 0 | 0 | 0
329 | 22 | 0 | 0 |  | -0.36772 | 4.2691 | 12.2327 | 18.9527 | 22.3159 | 2.7007 | -52.8941 | 0 | 0 | 0 | 0 | 0
329 | 23 | 0 | 0 |  | -0.36772 | 4.2691 | 12.2327 | 18.9527 | 23.3159 | 2.9625 | -57.4131 | 0 | 0 | 0 | 0 | 0
329 | 24 | 0 | 0 |  | -0.36772 | 4.2691 | 12.2327 | 18.9527 | 24.3159 | 3.2243 | -58.1781 | 0 | 0 | 0 | 0 | 0
330 | 1 | 0 | 0 |  | -0.37081 | 4.2863 | 11.9067 | 18.6267 | 1.3104 | -2.7985 | -55.1162 | 0 | 0 | 0 | 0 | 0
330 | 2 | 0 | 0 |  | -0.37081 | 4.2863 | 11.9067 | 18.6267 | 2.3104 | -2.5367 | -48.8497 | 0 | 0 | 0 | 0 | 0
330 | 3 | 0 | 0 |  | -0.37081 | 4.2863 | 11.9067 | 18.6267 | 3.3104 | -2.2749 | -40.8426 | 0 | 0 | 0 | 0 | 0
330 | 4 | 0 | 0 |  | -0.37081 | 4.2863 | 11.9067 | 18.6267 | 4.3104 | -2.0131 | -32.0089 | 0 | 0 | 0 | 0 | 0
330 | 5 | 0 | 0 |  | -0.37081 | 4.2863 | 11.9067 | 18.6267 | 5.3104 | -1.7513 | -22.9319 | 0 | 0 | 0 | 0 | 0
330 | 6 | 0 | 0 |  | -0.37081 | 4.2863 | 11.9067 | 18.6267 | 6.3104 | -1.4895 | -14.0228 | 0 | 0 | 0 | 0 | 0
330 | 7 | 0 | 0 |  | -0.37081 | 4.2863 | 11.9067 | 18.6267 | 7.3104 | -1.2277 | -5.6301 | 0 | 0 | 0 | 0 | 0
330 | 8 | 0 | 1 |  | -0.37081 | 4.2863 | 11.9067 | 18.6267 | 8.3104 | -0.96592 | 1.8993 | 0 | 0.83333 | 0.83333 | 1.323 | 0
330 | 9 | 0 | 17 |  | -0.37081 | 4.2863 | 11.9067 | 18.6267 | 9.3104 | -0.70412 | 8.1922 | 0 | 14.1667 | 14.1667 | 22.491 | 0
330 | 10 | 16 | 72 |  | -0.37081 | 4.2863 | 11.9067 | 18.6267 | 10.3104 | -0.44232 | 12.8557 | 10.1996 | 60 | 70.1996 | 111.4488 | 1
330 | 11 | 16 | 107 |  | -0.37081 | 4.2863 | 11.9067 | 18.6267 | 11.3104 | -0.18053 | 15.5272 | 11.3002 | 89.1667 | 100.4668 | 159.5012 | 1
330 | 12 | 38 | 117 |  | -0.37081 | 4.2863 | 11.9067 | 18.6267 | 12.3104 | 0.081274 | 15.9628 | 27.2611 | 97.5 | 124.7611 | 198.0707 | 1
330 | 13 | 27 | 113 |  | -0.37081 | 4.2863 | 11.9067 | 18.6267 | 13.3104 | 0.34307 | 14.1197 | 18.0933 | 94.1667 | 112.2599 | 178.2239 | 1
330 | 14 | 0 | 57 |  | -0.37081 | 4.2863 | 11.9067 | 18.6267 | 14.3104 | 0.60487 | 10.173 | 0 | 47.5 | 47.5 | 75.411 | 0
330 | 15 | 0 | 45 |  | -0.37081 | 4.2863 | 11.9067 | 18.6267 | 15.3104 | 0.86667 | 4.4517 | 0 | 37.5 | 37.5 | 59.535 | 0
330 | 16 | 0 | 5 |  | -0.37081 | 4.2863 | 11.9067 | 18.6267 | 16.3104 | 1.1285 | -2.6545 | 0 | 4.1667 | 4.1667 | 6.615 | 0
330 | 17 | 0 | 0 |  | -0.37081 | 4.2863 | 11.9067 | 18.6267 | 17.3104 | 1.3903 | -10.7619 | 0 | 0 | 0 | 0 | 0
330 | 18 | 0 | 0 |  | -0.37081 | 4.2863 | 11.9067 | 18.6267 | 18.3104 | 1.6521 | -19.5152 | 0 | 0 | 0 | 0 | 0
330 | 19 | 0 | 0 |  | -0.37081 | 4.2863 | 11.9067 | 18.6267 | 19.3104 | 1.9139 | -28.5717 | 0 | 0 | 0 | 0 | 0
330 | 20 | 0 | 0 |  | -0.37081 | 4.2863 | 11.9067 | 18.6267 | 20.3104 | 2.1757 | -37.5539 | 0 | 0 | 0 | 0 | 0
330 | 21 | 0 | 0 |  | -0.37081 | 4.2863 | 11.9067 | 18.6267 | 21.3104 | 2.4375 | -45.9604 | 0 | 0 | 0 | 0 | 0
330 | 22 | 0 | 0 |  | -0.37081 | 4.2863 | 11.9067 | 18.6267 | 22.3104 | 2.6993 | -53.0214 | 0 | 0 | 0 | 0 | 0
330 | 23 | 0 | 0 |  | -0.37081 | 4.2863 | 11.9067 | 18.6267 | 23.3104 | 2.9611 | -57.5713 | 0 | 0 | 0 | 0 | 0
330 | 24 | 0 | 0 |  | -0.37081 | 4.2863 | 11.9067 | 18.6267 | 24.3104 | 3.2229 | -58.3617 | 0 | 0 | 0 | 0 | 0
331 | 1 | 0 | 0 |  | -0.3738 | 4.3036 | 11.5706 | 18.2906 | 1.3048 | -2.8 | -55.3037 | 0 | 0 | 0 | 0 | 0
331 | 2 | 0 | 0 |  | -0.3738 | 4.3036 | 11.5706 | 18.2906 | 2.3048 | -2.5382 | -49.0362 | 0 | 0 | 0 | 0 | 0
331 | 3 | 0 | 0 |  | -0.3738 | 4.3036 | 11.5706 | 18.2906 | 3.3048 | -2.2764 | -41.0256 | 0 | 0 | 0 | 0 | 0
331 | 4 | 0 | 0 |  | -0.3738 | 4.3036 | 11.5706 | 18.2906 | 4.3048 | -2.0146 | -32.1898 | 0 | 0 | 0 | 0 | 0
331 | 5 | 0 | 0 |  | -0.3738 | 4.3036 | 11.5706 | 18.2906 | 5.3048 | -1.7528 | -23.1127 | 0 | 0 | 0 | 0 | 0
331 | 6 | 0 | 0 |  | -0.3738 | 4.3036 | 11.5706 | 18.2906 | 6.3048 | -1.491 | -14.2052 | 0 | 0 | 0 | 0 | 0
331 | 7 | 0 | 0 |  | -0.3738 | 4.3036 | 11.5706 | 18.2906 | 7.3048 | -1.2292 | -5.8149 | 0 | 0 | 0 | 0 | 0
331 | 8 | 0 | 3 |  | -0.3738 | 4.3036 | 11.5706 | 18.2906 | 8.3048 | -0.96739 | 1.7122 | 0 | 2.5 | 2.5 | 3.969 | 0
331 | 9 | 0 | 26 |  | -0.3738 | 4.3036 | 11.5706 | 18.2906 | 9.3048 | -0.70559 | 8.0044 | 0 | 21.6667 | 21.6667 | 34.398 | 0
331 | 10 | 10 | 72 |  | -0.3738 | 4.3036 | 11.5706 | 18.2906 | 10.3048 | -0.44379 | 12.6702 | 6.3496 | 60 | 66.3496 | 105.3366 | 1
331 | 11 | 17 | 106 |  | -0.3738 | 4.3036 | 11.5706 | 18.2906 | 11.3048 | -0.18199 | 15.3486 | 11.9676 | 88.3333 | 100.301 | 159.2378 | 1
331 | 12 | 38 | 116 |  | -0.3738 | 4.3036 | 11.5706 | 18.2906 | 12.3048 | 0.079808 | 15.7961 | 27.1863 | 96.6667 | 123.853 | 196.629 | 1
331 | 13 | 27 | 111 |  | -0.3738 | 4.3036 | 11.5706 | 18.2906 | 13.3048 | 0.34161 | 13.9691 | 18.0503 | 92.5 | 110.5503 | 175.5097 | 1
331 | 14 | 18 | 85 |  | -0.3738 | 4.3036 | 11.5706 | 18.2906 | 14.3048 | 0.60341 | 10.0404 | 10.1966 | 70.8333 | 81.0299 | 128.6431 | 0
331 | 15 | 0 | 44 |  | -0.3738 | 4.3036 | 11.5706 | 18.2906 | 15.3048 | 0.86521 | 4.3365 | 0 | 36.6667 | 36.6667 | 58.212 | 0
331 | 16 | 0 | 12 |  | -0.3738 | 4.3036 | 11.5706 | 18.2906 | 16.3048 | 1.127 | -2.7544 | 0 | 10 | 10 | 15.876 | 0
331 | 17 | 0 | 0 |  | -0.3738 | 4.3036 | 11.5706 | 18.2906 | 17.3048 | 1.3888 | -10.8501 | 0 | 0 | 0 | 0 | 0
331 | 18 | 0 | 0 |  | -0.3738 | 4.3036 | 11.5706 | 18.2906 | 18.3048 | 1.6506 | -19.5961 | 0 | 0 | 0 | 0 | 0
331 | 19 | 0 | 0 |  | -0.3738 | 4.3036 | 11.5706 | 18.2906 | 19.3048 | 1.9124 | -28.6506 | 0 | 0 | 0 | 0 | 0
331 | 20 | 0 | 0 |  | -0.3738 | 4.3036 | 11.5706 | 18.2906 | 20.3048 | 2.1742 | -37.6373 | 0 | 0 | 0 | 0 | 0
331 | 21 | 0 | 0 |  | -0.3738 | 4.3036 | 11.5706 | 18.2906 | 21.3048 | 2.436 | -46.057 | 0 | 0 | 0 | 0 | 0
331 | 22 | 0 | 0 |  | -0.3738 | 4.3036 | 11.5706 | 18.2906 | 22.3048 | 2.6978 | -53.1415 | 0 | 0 | 0 | 0 | 0
331 | 23 | 0 | 0 |  | -0.3738 | 4.3036 | 11.5706 | 18.2906 | 23.3048 | 2.9596 | -57.7226 | 0 | 0 | 0 | 0 | 0
331 | 24 | 0 | 0 |  | -0.3738 | 4.3036 | 11.5706 | 18.2906 | 24.3048 | 3.2214 | -58.5391 | 0 | 0 | 0 | 0 | 0
332 | 1 | 0 | 0 |  | -0.37666 | 4.3208 | 11.2247 | 17.9447 | 1.2991 | -2.8015 | -55.4859 | 0 | 0 | 0 | 0 | 0
332 | 2 | 0 | 0 |  | -0.37666 | 4.3208 | 11.2247 | 17.9447 | 2.2991 | -2.5397 | -49.2183 | 0 | 0 | 0 | 0 | 0
332 | 3 | 0 | 0 |  | -0.37666 | 4.3208 | 11.2247 | 17.9447 | 3.2991 | -2.2779 | -41.2048 | 0 | 0 | 0 | 0 | 0
332 | 4 | 0 | 0 |  | -0.37666 | 4.3208 | 11.2247 | 17.9447 | 4.2991 | -2.0161 | -32.3672 | 0 | 0 | 0 | 0 | 0
332 | 5 | 0 | 0 |  | -0.37666 | 4.3208 | 11.2247 | 17.9447 | 5.2991 | -1.7543 | -23.29 | 0 | 0 | 0 | 0 | 0
332 | 6 | 0 | 0 |  | -0.37666 | 4.3208 | 11.2247 | 17.9447 | 6.2991 | -1.4925 | -14.3838 | 0 | 0 | 0 | 0 | 0
332 | 7 | 0 | 0 |  | -0.37666 | 4.3208 | 11.2247 | 17.9447 | 7.2991 | -1.2307 | -5.9957 | 0 | 0 | 0 | 0 | 0
332 | 8 | 0 | 2 |  | -0.37666 | 4.3208 | 11.2247 | 17.9447 | 8.2991 | -0.9689 | 1.5297 | 0 | 1.6667 | 1.6667 | 2.646 | 0
332 | 9 | 38 | 33 |  | -0.37666 | 4.3208 | 11.2247 | 17.9447 | 9.2991 | -0.7071 | 7.8216 | 19.3975 | 27.5 | 46.8975 | 74.4545 | 0
332 | 10 | 285 | 73 |  | -0.37666 | 4.3208 | 11.2247 | 17.9447 | 10.2991 | -0.4453 | 12.4903 | 180.261 | 60.8333 | 241.0944 | 382.7614 | 0
332 | 11 | 493 | 68 |  | -0.37666 | 4.3208 | 11.2247 | 17.9447 | 11.2991 | -0.1835 | 15.1761 | 345.9677 | 56.6667 | 402.6344 | 639.2223 | 1
332 | 12 | 555 | 69 |  | -0.37666 | 4.3208 | 11.2247 | 17.9447 | 12.2991 | 0.078298 | 15.636 | 396.0126 | 57.5 | 453.5126 | 719.9967 | 1
332 | 13 | 409 | 83 |  | -0.37666 | 4.3208 | 11.2247 | 17.9447 | 13.2991 | 0.3401 | 13.8252 | 272.8116 | 69.1667 | 341.9783 | 542.9247 | 1
332 | 14 | 236 | 79 |  | -0.37666 | 4.3208 | 11.2247 | 17.9447 | 14.2991 | 0.6019 | 9.9144 | 133.4307 | 65.8333 | 199.264 | 316.3515 | 0
332 | 15 | 220 | 46 |  | -0.37666 | 4.3208 | 11.2247 | 17.9447 | 15.2991 | 0.8637 | 4.228 | 91.4215 | 38.3333 | 129.7548 | 205.9987 | 0
332 | 16 | 0 | 12 |  | -0.37666 | 4.3208 | 11.2247 | 17.9447 | 16.2991 | 1.1255 | -2.8478 | 0 | 10 | 10 | 15.876 | 0
332 | 17 | 0 | 0 |  | -0.37666 | 4.3208 | 11.2247 | 17.9447 | 17.2991 | 1.3873 | -10.9319 | 0 | 0 | 0 | 0 | 0
332 | 18 | 0 | 0 |  | -0.37666 | 4.3208 | 11.2247 | 17.9447 | 18.2991 | 1.6491 | -19.6705 | 0 | 0 | 0 | 0 | 0
332 | 19 | 0 | 0 |  | -0.37666 | 4.3208 | 11.2247 | 17.9447 | 19.2991 | 1.9109 | -28.7229 | 0 | 0 | 0 | 0 | 0
332 | 20 | 0 | 0 |  | -0.37666 | 4.3208 | 11.2247 | 17.9447 | 20.2991 | 2.1727 | -37.7141 | 0 | 0 | 0 | 0 | 0
332 | 21 | 0 | 0 |  | -0.37666 | 4.3208 | 11.2247 | 17.9447 | 21.2991 | 2.4345 | -46.1466 | 0 | 0 | 0 | 0 | 0
332 | 22 | 0 | 0 |  | -0.37666 | 4.3208 | 11.2247 | 17.9447 | 22.2991 | 2.6963 | -53.2545 | 0 | 0 | 0 | 0 | 0
332 | 23 | 0 | 0 |  | -0.37666 | 4.3208 | 11.2247 | 17.9447 | 23.2991 | 2.9581 | -57.8667 | 0 | 0 | 0 | 0 | 0
332 | 24 | 0 | 0 |  | -0.37666 | 4.3208 | 11.2247 | 17.9447 | 24.2991 | 3.2199 | -58.7102 | 0 | 0 | 0 | 0 | 0
333 | 1 | 0 | 0 |  | -0.37942 | 4.338 | 10.8692 | 17.5892 | 1.2932 | -2.803 | -55.6628 | 0 | 0 | 0 | 0 | 0
333 | 2 | 0 | 0 |  | -0.37942 | 4.338 | 10.8692 | 17.5892 | 2.2932 | -2.5412 | -49.396 | 0 | 0 | 0 | 0 | 0
333 | 3 | 0 | 0 |  | -0.37942 | 4.338 | 10.8692 | 17.5892 | 3.2932 | -2.2794 | -41.3802 | 0 | 0 | 0 | 0 | 0
333 | 4 | 0 | 0 |  | -0.37942 | 4.338 | 10.8692 | 17.5892 | 4.2932 | -2.0176 | -32.5409 | 0 | 0 | 0 | 0 | 0
333 | 5 | 0 | 0 |  | -0.37942 | 4.338 | 10.8692 | 17.5892 | 5.2932 | -1.7558 | -23.4637 | 0 | 0 | 0 | 0 | 0
333 | 6 | 0 | 0 |  | -0.37942 | 4.338 | 10.8692 | 17.5892 | 6.2932 | -1.494 | -14.5587 | 0 | 0 | 0 | 0 | 0
333 | 7 | 0 | 0 |  | -0.37942 | 4.338 | 10.8692 | 17.5892 | 7.2932 | -1.2322 | -6.1723 | 0 | 0 | 0 | 0 | 0
333 | 8 | 0 | 2 |  | -0.37942 | 4.338 | 10.8692 | 17.5892 | 8.2932 | -0.97045 | 1.3517 | 0 | 1.6667 | 1.6667 | 2.646 | 0
333 | 9 | 102 | 33 |  | -0.37942 | 4.338 | 10.8692 | 17.5892 | 9.2932 | -0.70865 | 7.6439 | 51.8054 | 27.5 | 79.3054 | 125.9053 | 0
333 | 10 | 310 | 69 |  | -0.37942 | 4.338 | 10.8692 | 17.5892 | 10.2932 | -0.44685 | 12.3161 | 195.3272 | 57.5 | 252.8272 | 401.3884 | 0
333 | 11 | 519 | 64 |  | -0.37942 | 4.338 | 10.8692 | 17.5892 | 11.2932 | -0.18505 | 15.0098 | 363.096 | 53.3333 | 416.4294 | 661.1233 | 1
333 | 12 | 546 | 72 |  | -0.37942 | 4.338 | 10.8692 | 17.5892 | 12.2932 | 0.076747 | 15.4823 | 388.5974 | 60 | 448.5974 | 712.1932 | 1
333 | 13 | 510 | 74 |  | -0.37942 | 4.338 | 10.8692 | 17.5892 | 13.2932 | 0.33855 | 13.688 | 339.4519 | 61.6667 | 401.1186 | 636.8158 | 1
333 | 14 | 434 | 63 |  | -0.37942 | 4.338 | 10.8692 | 17.5892 | 14.2932 | 0.60035 | 9.7952 | 244.939 | 52.5 | 297.439 | 472.2142 | 0
333 | 15 | 227 | 45 |  | -0.37942 | 4.338 | 10.8692 | 17.5892 | 15.2932 | 0.86215 | 4.1262 | 94.1972 | 37.5 | 131.6972 | 209.0824 | 0
333 | 16 | 0 | 12 |  | -0.37942 | 4.338 | 10.8692 | 17.5892 | 16.2932 | 1.1239 | -2.9347 | 0 | 10 | 10 | 15.876 | 0
333 | 17 | 0 | 0 |  | -0.37942 | 4.338 | 10.8692 | 17.5892 | 17.2932 | 1.3857 | -11.0071 | 0 | 0 | 0 | 0 | 0
333 | 18 | 0 | 0 |  | -0.37942 | 4.338 | 10.8692 | 17.5892 | 18.2932 | 1.6475 | -19.7385 | 0 | 0 | 0 | 0 | 0
333 | 19 | 0 | 0 |  | -0.37942 | 4.338 | 10.8692 | 17.5892 | 19.2932 | 1.9093 | -28.7887 | 0 | 0 | 0 | 0 | 0
333 | 20 | 0 | 0 |  | -0.37942 | 4.338 | 10.8692 | 17.5892 | 20.2932 | 2.1711 | -37.7841 | 0 | 0 | 0 | 0 | 0
333 | 21 | 0 | 0 |  | -0.37942 | 4.338 | 10.8692 | 17.5892 | 21.2932 | 2.4329 | -46.2293 | 0 | 0 | 0 | 0 | 0
333 | 22 | 0 | 0 |  | -0.37942 | 4.338 | 10.8692 | 17.5892 | 22.2932 | 2.6947 | -53.3602 | 0 | 0 | 0 | 0 | 0
333 | 23 | 0 | 0 |  | -0.37942 | 4.338 | 10.8692 | 17.5892 | 23.2932 | 2.9565 | -58.0038 | 0 | 0 | 0 | 0 | 0
333 | 24 | 0 | 0 |  | -0.37942 | 4.338 | 10.8692 | 17.5892 | 24.2932 | 3.2183 | -58.8748 | 0 | 0 | 0 | 0 | 0
334 | 1 | 0 | 0 |  | -0.38206 | 4.3552 | 10.5046 | 17.2246 | 1.2871 | -2.8046 | -55.8343 | 0 | 0 | 0 | 0 | 0
334 | 2 | 0 | 0 |  | -0.38206 | 4.3552 | 10.5046 | 17.2246 | 2.2871 | -2.5428 | -49.5691 | 0 | 0 | 0 | 0 | 0
334 | 3 | 0 | 0 |  | -0.38206 | 4.3552 | 10.5046 | 17.2246 | 3.2871 | -2.281 | -41.5515 | 0 | 0 | 0 | 0 | 0
334 | 4 | 0 | 0 |  | -0.38206 | 4.3552 | 10.5046 | 17.2246 | 4.2871 | -2.0192 | -32.7109 | 0 | 0 | 0 | 0 | 0
334 | 5 | 0 | 0 |  | -0.38206 | 4.3552 | 10.5046 | 17.2246 | 5.2871 | -1.7574 | -23.6336 | 0 | 0 | 0 | 0 | 0
334 | 6 | 0 | 0 |  | -0.38206 | 4.3552 | 10.5046 | 17.2246 | 6.2871 | -1.4956 | -14.7296 | 0 | 0 | 0 | 0 | 0
334 | 7 | 0 | 0 |  | -0.38206 | 4.3552 | 10.5046 | 17.2246 | 7.2871 | -1.2338 | -6.3447 | 0 | 0 | 0 | 0 | 0
334 | 8 | 0 | 1 |  | -0.38206 | 4.3552 | 10.5046 | 17.2246 | 8.2871 | -0.97204 | 1.1784 | 0 | 0.83333 | 0.83333 | 1.323 | 0
334 | 9 | 92 | 32 |  | -0.38206 | 4.3552 | 10.5046 | 17.2246 | 9.2871 | -0.71024 | 7.4715 | 46.4947 | 26.6667 | 73.1614 | 116.151 | 0
334 | 10 | 227 | 81 |  | -0.38206 | 4.3552 | 10.5046 | 17.2246 | 10.2871 | -0.44844 | 12.1477 | 142.4963 | 67.5 | 209.9963 | 333.3902 | 0
334 | 11 | 504 | 65 |  | -0.38206 | 4.3552 | 10.5046 | 17.2246 | 11.2871 | -0.18664 | 14.8498 | 351.5506 | 54.1667 | 405.7172 | 644.1167 | 1
334 | 12 | 520 | 76 |  | -0.38206 | 4.3552 | 10.5046 | 17.2246 | 12.2871 | 0.075156 | 15.3353 | 369.186 | 63.3333 | 432.5194 | 686.6677 | 1
334 | 13 | 500 | 74 |  | -0.38206 | 4.3552 | 10.5046 | 17.2246 | 13.2871 | 0.33696 | 13.5575 | 332.1225 | 61.6667 | 393.7891 | 625.1796 | 1
334 | 14 | 411 | 64 |  | -0.38206 | 4.3552 | 10.5046 | 17.2246 | 14.2871 | 0.59876 | 9.6828 | 231.5791 | 53.3333 | 284.9124 | 452.3269 | 0
334 | 15 | 203 | 44 |  | -0.38206 | 4.3552 | 10.5046 | 17.2246 | 15.2871 | 0.86055 | 4.031 | 84.1365 | 36.6667 | 120.8031 | 191.787 | 0
334 | 16 | 0 | 6 |  | -0.38206 | 4.3552 | 10.5046 | 17.2246 | 16.2871 | 1.1224 | -3.0149 | 0 | 5 | 5 | 7.938 | 0
334 | 17 | 0 | 0 |  | -0.38206 | 4.3552 | 10.5046 | 17.2246 | 17.2871 | 1.3842 | -11.0759 | 0 | 0 | 0 | 0 | 0
334 | 18 | 0 | 0 |  | -0.38206 | 4.3552 | 10.5046 | 17.2246 | 18.2871 | 1.646 | -19.8 | 0 | 0 | 0 | 0 | 0
334 | 19 | 0 | 0 |  | -0.38206 | 4.3552 | 10.5046 | 17.2246 | 19.2871 | 1.9078 | -28.848 | 0 | 0 | 0 | 0 | 0
334 | 20 | 0 | 0 |  | -0.38206 | 4.3552 | 10.5046 | 17.2246 | 20.2871 | 2.1696 | -37.8475 | 0 | 0 | 0 | 0 | 0
334 | 21 | 0 | 0 |  | -0.38206 | 4.3552 | 10.5046 | 17.2246 | 21.2871 | 2.4314 | -46.3051 | 0 | 0 | 0 | 0 | 0
334 | 22 | 0 | 0 |  | -0.38206 | 4.3552 | 10.5046 | 17.2246 | 22.2871 | 2.6932 | -53.4588 | 0 | 0 | 0 | 0 | 0
334 | 23 | 0 | 0 |  | -0.38206 | 4.3552 | 10.5046 | 17.2246 | 23.2871 | 2.9549 | -58.1336 | 0 | 0 | 0 | 0 | 0
334 | 24 | 0 | 0 |  | -0.38206 | 4.3552 | 10.5046 | 17.2246 | 24.2871 | 3.2167 | -59.033 | 0 | 0 | 0 | 0 | 0
335 | 1 | 0 | 0 |  | -0.38458 | 4.3724 | 10.1311 | 16.8511 | 1.2809 | -2.8063 | -56.0002 | 0 | 0 | 0 | 0 | 0
335 | 2 | 0 | 0 |  | -0.38458 | 4.3724 | 10.1311 | 16.8511 | 2.2809 | -2.5445 | -49.7376 | 0 | 0 | 0 | 0 | 0
335 | 3 | 0 | 0 |  | -0.38458 | 4.3724 | 10.1311 | 16.8511 | 3.2809 | -2.2827 | -41.7187 | 0 | 0 | 0 | 0 | 0
335 | 4 | 0 | 0 |  | -0.38458 | 4.3724 | 10.1311 | 16.8511 | 4.2809 | -2.0209 | -32.877 | 0 | 0 | 0 | 0 | 0
335 | 5 | 0 | 0 |  | -0.38458 | 4.3724 | 10.1311 | 16.8511 | 5.2809 | -1.7591 | -23.7997 | 0 | 0 | 0 | 0 | 0
335 | 6 | 0 | 0 |  | -0.38458 | 4.3724 | 10.1311 | 16.8511 | 6.2809 | -1.4973 | -14.8966 | 0 | 0 | 0 | 0 | 0
335 | 7 | 0 | 0 |  | -0.38458 | 4.3724 | 10.1311 | 16.8511 | 7.2809 | -1.2355 | -6.5127 | 0 | 0 | 0 | 0 | 0
335 | 8 | 0 | 0 |  | -0.38458 | 4.3724 | 10.1311 | 16.8511 | 8.2809 | -0.97367 | 1.0099 | 0 | 0 | 0 | 0 | 0
335 | 9 | 0 | 12 |  | -0.38458 | 4.3724 | 10.1311 | 16.8511 | 9.2809 | -0.71187 | 7.3044 | 0 | 10 | 10 | 15.876 | 0
335 | 10 | 0 | 38 |  | -0.38458 | 4.3724 | 10.1311 | 16.8511 | 10.2809 | -0.45007 | 11.9852 | 0 | 31.6667 | 31.6667 | 50.274 | 0
335 | 11 | 0 | 61 |  | -0.38458 | 4.3724 | 10.1311 | 16.8511 | 11.2809 | -0.18827 | 14.6961 | 0 | 50.8333 | 50.8333 | 80.703 | 1
335 | 12 | 181 | 120 |  | -0.38458 | 4.3724 | 10.1311 | 16.8511 | 12.2809 | 0.073527 | 15.195 | 128.2034 | 100 | 228.2034 | 362.2958 | 1
335 | 13 | 334 | 88 |  | -0.38458 | 4.3724 | 10.1311 | 16.8511 | 13.2809 | 0.33533 | 13.4338 | 221.4356 | 73.3333 | 294.7689 | 467.9752 | 1
335 | 14 | 328 | 70 |  | -0.38458 | 4.3724 | 10.1311 | 16.8511 | 14.2809 | 0.59713 | 9.5771 | 184.5381 | 58.3333 | 242.8714 | 385.5826 | 0
335 | 15 | 109 | 49 |  | -0.38458 | 4.3724 | 10.1311 | 16.8511 | 15.2809 | 0.85892 | 3.9426 | 45.1316 | 40.8333 | 85.965 | 136.478 | 0
335 | 16 | 0 | 3 |  | -0.38458 | 4.3724 | 10.1311 | 16.8511 | 16.2809 | 1.1207 | -3.0886 | 0 | 2.5 | 2.5 | 3.969 | 0
335 | 17 | 0 | 0 |  | -0.38458 | 4.3724 | 10.1311 | 16.8511 | 17.2809 | 1.3825 | -11.1382 | 0 | 0 | 0 | 0 | 0
335 | 18 | 0 | 0 |  | -0.38458 | 4.3724 | 10.1311 | 16.8511 | 18.2809 | 1.6443 | -19.8551 | 0 | 0 | 0 | 0 | 0
335 | 19 | 0 | 0 |  | -0.38458 | 4.3724 | 10.1311 | 16.8511 | 19.2809 | 1.9061 | -28.9008 | 0 | 0 | 0 | 0 | 0
335 | 20 | 0 | 0 |  | -0.38458 | 4.3724 | 10.1311 | 16.8511 | 20.2809 | 2.1679 | -37.9042 | 0 | 0 | 0 | 0 | 0
335 | 21 | 0 | 0 |  | -0.38458 | 4.3724 | 10.1311 | 16.8511 | 21.2809 | 2.4297 | -46.3739 | 0 | 0 | 0 | 0 | 0
335 | 22 | 0 | 0 |  | -0.38458 | 4.3724 | 10.1311 | 16.8511 | 22.2809 | 2.6915 | -53.55 | 0 | 0 | 0 | 0 | 0
335 | 23 | 0 | 0 |  | -0.38458 | 4.3724 | 10.1311 | 16.8511 | 23.2809 | 2.9533 | -58.2563 | 0 | 0 | 0 | 0 | 0
335 | 24 | 0 | 0 |  | -0.38458 | 4.3724 | 10.1311 | 16.8511 | 24.2809 | 3.2151 | -59.1846 | 0 | 0 | 0 | 0 | 0
336 | 1 | 0 | 0 |  | -0.38699 | 4.3896 | 9.749 | 16.469 | 1.2745 | -2.8079 | -56.1606 | 0 | 0 | 0 | 0 | 0
336 | 2 | 0 | 0 |  | -0.38699 | 4.3896 | 9.749 | 16.469 | 2.2745 | -2.5461 | -49.9014 | 0 | 0 | 0 | 0 | 0
336 | 3 | 0 | 0 |  | -0.38699 | 4.3896 | 9.749 | 16.469 | 3.2745 | -2.2843 | -41.8818 | 0 | 0 | 0 | 0 | 0
336 | 4 | 0 | 0 |  | -0.38699 | 4.3896 | 9.749 | 16.469 | 4.2745 | -2.0225 | -33.0393 | 0 | 0 | 0 | 0 | 0
336 | 5 | 0 | 0 |  | -0.38699 | 4.3896 | 9.749 | 16.469 | 5.2745 | -1.7607 | -23.9619 | 0 | 0 | 0 | 0 | 0
336 | 6 | 0 | 0 |  | -0.38699 | 4.3896 | 9.749 | 16.469 | 6.2745 | -1.4989 | -15.0595 | 0 | 0 | 0 | 0 | 0
336 | 7 | 0 | 0 |  | -0.38699 | 4.3896 | 9.749 | 16.469 | 7.2745 | -1.2371 | -6.6763 | 0 | 0 | 0 | 0 | 0
336 | 8 | 0 | 0 |  | -0.38699 | 4.3896 | 9.749 | 16.469 | 8.2745 | -0.97534 | 0.84629 | 0 | 0 | 0 | 0 | 0
336 | 9 | 0 | 18 |  | -0.38699 | 4.3896 | 9.749 | 16.469 | 9.2745 | -0.71354 | 7.1427 | 0 | 15 | 15 | 23.814 | 0
336 | 10 | 0 | 59 |  | -0.38699 | 4.3896 | 9.749 | 16.469 | 10.2745 | -0.45174 | 11.8286 | 0 | 49.1667 | 49.1667 | 78.057 | 0
336 | 11 | 8 | 93 |  | -0.38699 | 4.3896 | 9.749 | 16.469 | 11.2745 | -0.18994 | 14.5488 | 5.5484 | 77.5 | 83.0484 | 131.8477 | 1
336 | 12 | 18 | 106 |  | -0.38699 | 4.3896 | 9.749 | 16.469 | 12.2745 | 0.07186 | 15.0613 | 12.7209 | 88.3333 | 101.0542 | 160.4337 | 1
336 | 13 | 16 | 100 |  | -0.38699 | 4.3896 | 9.749 | 16.469 | 13.2745 | 0.33366 | 13.317 | 10.5888 | 83.3333 | 93.9221 | 149.1108 | 1
336 | 14 | 4 | 76 |  | -0.38699 | 4.3896 | 9.749 | 16.469 | 14.2745 | 0.59546 | 9.4783 | 2.2475 | 63.3333 | 65.5808 | 104.1161 | 0
336 | 15 | 0 | 35 |  | -0.38699 | 4.3896 | 9.749 | 16.469 | 15.2745 | 0.85726 | 3.8609 | 0 | 29.1667 | 29.1667 | 46.305 | 0
336 | 16 | 0 | 5 |  | -0.38699 | 4.3896 | 9.749 | 16.469 | 16.2745 | 1.1191 | -3.1556 | 0 | 4.1667 | 4.1667 | 6.615 | 0
336 | 17 | 0 | 0 |  | -0.38699 | 4.3896 | 9.749 | 16.469 | 17.2745 | 1.3809 | -11.1941 | 0 | 0 | 0 | 0 | 0
336 | 18 | 0 | 0 |  | -0.38699 | 4.3896 | 9.749 | 16.469 | 18.2745 | 1.6427 | -19.9037 | 0 | 0 | 0 | 0 | 0
336 | 19 | 0 | 0 |  | -0.38699 | 4.3896 | 9.749 | 16.469 | 19.2745 | 1.9045 | -28.9471 | 0 | 0 | 0 | 0 | 0
336 | 20 | 0 | 0 |  | -0.38699 | 4.3896 | 9.749 | 16.469 | 20.2745 | 2.1663 | -37.9543 | 0 | 0 | 0 | 0 | 0
336 | 21 | 0 | 0 |  | -0.38699 | 4.3896 | 9.749 | 16.469 | 21.2745 | 2.4281 | -46.4358 | 0 | 0 | 0 | 0 | 0
336 | 22 | 0 | 0 |  | -0.38699 | 4.3896 | 9.749 | 16.469 | 22.2745 | 2.6899 | -53.6341 | 0 | 0 | 0 | 0 | 0
336 | 23 | 0 | 0 |  | -0.38699 | 4.3896 | 9.749 | 16.469 | 23.2745 | 2.9517 | -58.3716 | 0 | 0 | 0 | 0 | 0
336 | 24 | 0 | 0 |  | -0.38699 | 4.3896 | 9.749 | 16.469 | 24.2745 | 3.2135 | -59.3295 | 0 | 0 | 0 | 0 | 0
337 | 1 | 0 | 0 |  | -0.38927 | 4.4068 | 9.3588 | 16.0788 | 1.268 | -2.8096 | -56.3152 | 0 | 0 | 0 | 0 | 0
337 | 2 | 0 | 0 |  | -0.38927 | 4.4068 | 9.3588 | 16.0788 | 2.268 | -2.5478 | -50.0603 | 0 | 0 | 0 | 0 | 0
337 | 3 | 0 | 0 |  | -0.38927 | 4.4068 | 9.3588 | 16.0788 | 3.268 | -2.286 | -42.0407 | 0 | 0 | 0 | 0 | 0
337 | 4 | 0 | 0 |  | -0.38927 | 4.4068 | 9.3588 | 16.0788 | 4.268 | -2.0242 | -33.1975 | 0 | 0 | 0 | 0 | 0
337 | 5 | 0 | 0 |  | -0.38927 | 4.4068 | 9.3588 | 16.0788 | 5.268 | -1.7624 | -24.1202 | 0 | 0 | 0 | 0 | 0
337 | 6 | 0 | 0 |  | -0.38927 | 4.4068 | 9.3588 | 16.0788 | 6.268 | -1.5006 | -15.2182 | 0 | 0 | 0 | 0 | 0
337 | 7 | 0 | 0 |  | -0.38927 | 4.4068 | 9.3588 | 16.0788 | 7.268 | -1.2388 | -6.8355 | 0 | 0 | 0 | 0 | 0
337 | 8 | 0 | 0 |  | -0.38927 | 4.4068 | 9.3588 | 16.0788 | 8.268 | -0.97704 | 0.68764 | 0 | 0 | 0 | 0 | 0
337 | 9 | 0 | 17 |  | -0.38927 | 4.4068 | 9.3588 | 16.0788 | 9.268 | -0.71524 | 6.9865 | 0 | 14.1667 | 14.1667 | 22.491 | 0
337 | 10 | 0 | 58 |  | -0.38927 | 4.4068 | 9.3588 | 16.0788 | 10.268 | -0.45344 | 11.678 | 0 | 48.3333 | 48.3333 | 76.734 | 0
337 | 11 | 8 | 92 |  | -0.38927 | 4.4068 | 9.3588 | 16.0788 | 11.268 | -0.19164 | 14.408 | 5.5334 | 76.6667 | 82.2001 | 130.5009 | 1
337 | 12 | 18 | 105 |  | -0.38927 | 4.4068 | 9.3588 | 16.0788 | 12.268 | 0.070157 | 14.9345 | 12.6937 | 87.5 | 100.1937 | 159.0676 | 1
337 | 13 | 16 | 100 |  | -0.38927 | 4.4068 | 9.3588 | 16.0788 | 13.268 | 0.33196 | 13.2071 | 10.5713 | 83.3333 | 93.9046 | 149.083 | 1
337 | 14 | 4 | 75 |  | -0.38927 | 4.4068 | 9.3588 | 16.0788 | 14.268 | 0.59376 | 9.3864 | 2.2448 | 62.5 | 64.7448 | 102.7889 | 0
337 | 15 | 0 | 34 |  | -0.38927 | 4.4068 | 9.3588 | 16.0788 | 15.268 | 0.85556 | 3.7859 | 0 | 28.3333 | 28.3333 | 44.982 | 0
337 | 16 | 0 | 5 |  | -0.38927 | 4.4068 | 9.3588 | 16.0788 | 16.268 | 1.1174 | -3.2161 | 0 | 4.1667 | 4.1667 | 6.615 | 0
337 | 17 | 0 | 0 |  | -0.38927 | 4.4068 | 9.3588 | 16.0788 | 17.268 | 1.3792 | -11.2434 | 0 | 0 | 0 | 0 | 0
337 | 18 | 0 | 0 |  | -0.38927 | 4.4068 | 9.3588 | 16.0788 | 18.268 | 1.641 | -19.946 | 0 | 0 | 0 | 0 | 0
337 | 19 | 0 | 0 |  | -0.38927 | 4.4068 | 9.3588 | 16.0788 | 19.268 | 1.9028 | -28.987 | 0 | 0 | 0 | 0 | 0
337 | 20 | 0 | 0 |  | -0.38927 | 4.4068 | 9.3588 | 16.0788 | 20.268 | 2.1646 | -37.9978 | 0 | 0 | 0 | 0 | 0
337 | 21 | 0 | 0 |  | -0.38927 | 4.4068 | 9.3588 | 16.0788 | 21.268 | 2.4264 | -46.4908 | 0 | 0 | 0 | 0 | 0
337 | 22 | 0 | 0 |  | -0.38927 | 4.4068 | 9.3588 | 16.0788 | 22.268 | 2.6882 | -53.7108 | 0 | 0 | 0 | 0 | 0
337 | 23 | 0 | 0 |  | -0.38927 | 4.4068 | 9.3588 | 16.0788 | 23.268 | 2.95 | -58.4796 | 0 | 0 | 0 | 0 | 0
337 | 24 | 0 | 0 |  | -0.38927 | 4.4068 | 9.3588 | 16.0788 | 24.268 | 3.2117 | -59.4677 | 0 | 0 | 0 | 0 | 0
338 | 1 | 0 | 0 |  | -0.39144 | 4.4241 | 8.9608 | 15.6808 | 1.2613 | -2.8114 | -56.464 | 0 | 0 | 0 | 0 | 0
338 | 2 | 0 | 0 |  | -0.39144 | 4.4241 | 8.9608 | 15.6808 | 2.2613 | -2.5496 | -50.2144 | 0 | 0 | 0 | 0 | 0
338 | 3 | 0 | 0 |  | -0.39144 | 4.4241 | 8.9608 | 15.6808 | 3.2613 | -2.2878 | -42.1952 | 0 | 0 | 0 | 0 | 0
338 | 4 | 0 | 0 |  | -0.39144 | 4.4241 | 8.9608 | 15.6808 | 4.2613 | -2.026 | -33.3517 | 0 | 0 | 0 | 0 | 0
338 | 5 | 0 | 0 |  | -0.39144 | 4.4241 | 8.9608 | 15.6808 | 5.2613 | -1.7642 | -24.2743 | 0 | 0 | 0 | 0 | 0
338 | 6 | 0 | 0 |  | -0.39144 | 4.4241 | 8.9608 | 15.6808 | 6.2613 | -1.5024 | -15.3726 | 0 | 0 | 0 | 0 | 0
338 | 7 | 0 | 0 |  | -0.39144 | 4.4241 | 8.9608 | 15.6808 | 7.2613 | -1.2406 | -6.99 | 0 | 0 | 0 | 0 | 0
338 | 8 | 0 | 0 |  | -0.39144 | 4.4241 | 8.9608 | 15.6808 | 8.2613 | -0.97878 | 0.53402 | 0 | 0 | 0 | 0 | 0
338 | 9 | 0 | 16 |  | -0.39144 | 4.4241 | 8.9608 | 15.6808 | 9.2613 | -0.71698 | 6.8358 | 0 | 13.3333 | 13.3333 | 21.168 | 0
338 | 10 | 95 | 57 |  | -0.39144 | 4.4241 | 8.9608 | 15.6808 | 10.2613 | -0.45518 | 11.5335 | 58.7989 | 47.5 | 106.2989 | 168.7601 | 0
338 | 11 | 112 | 92 |  | -0.39144 | 4.4241 | 8.9608 | 15.6808 | 11.2613 | -0.19338 | 14.2737 | 77.2662 | 76.6667 | 153.9329 | 244.3838 | 1
338 | 12 | 19 | 103 |  | -0.39144 | 4.4241 | 8.9608 | 15.6808 | 12.2613 | 0.068421 | 14.8144 | 13.3718 | 85.8333 | 99.2051 | 157.4981 | 1
338 | 13 | 16 | 99 |  | -0.39144 | 4.4241 | 8.9608 | 15.6808 | 13.2613 | 0.33022 | 13.1041 | 10.5551 | 82.5 | 93.0551 | 147.7343 | 1
338 | 14 | 4 | 74 |  | -0.39144 | 4.4241 | 8.9608 | 15.6808 | 14.2613 | 0.59202 | 9.3013 | 2.2425 | 61.6667 | 63.9092 | 101.4622 | 0
338 | 15 | 151 | 40 |  | -0.39144 | 4.4241 | 8.9608 | 15.6808 | 15.2613 | 0.85382 | 3.7177 | 62.4126 | 33.3333 | 95.746 | 152.0063 | 0
338 | 16 | 0 | 8 |  | -0.39144 | 4.4241 | 8.9608 | 15.6808 | 16.2613 | 1.1156 | -3.27 | 0 | 6.6667 | 6.6667 | 10.584 | 0
338 | 17 | 0 | 0 |  | -0.39144 | 4.4241 | 8.9608 | 15.6808 | 17.2613 | 1.3774 | -11.2863 | 0 | 0 | 0 | 0 | 0
338 | 18 | 0 | 0 |  | -0.39144 | 4.4241 | 8.9608 | 15.6808 | 18.2613 | 1.6392 | -19.9818 | 0 | 0 | 0 | 0 | 0
338 | 19 | 0 | 0 |  | -0.39144 | 4.4241 | 8.9608 | 15.6808 | 19.2613 | 1.901 | -29.0204 | 0 | 0 | 0 | 0 | 0
338 | 20 | 0 | 0 |  | -0.39144 | 4.4241 | 8.9608 | 15.6808 | 20.2613 | 2.1628 | -38.0346 | 0 | 0 | 0 | 0 | 0
338 | 21 | 0 | 0 |  | -0.39144 | 4.4241 | 8.9608 | 15.6808 | 21.2613 | 2.4246 | -46.5389 | 0 | 0 | 0 | 0 | 0
338 | 22 | 0 | 0 |  | -0.39144 | 4.4241 | 8.9608 | 15.6808 | 22.2613 | 2.6864 | -53.7803 | 0 | 0 | 0 | 0 | 0
338 | 23 | 0 | 0 |  | -0.39144 | 4.4241 | 8.9608 | 15.6808 | 23.2613 | 2.9482 | -58.5803 | 0 | 0 | 0 | 0 | 0
338 | 24 | 0 | 0 |  | -0.39144 | 4.4241 | 8.9608 | 15.6808 | 24.2613 | 3.21 | -59.5991 | 0 | 0 | 0 | 0 | 0
339 | 1 | 0 | 0 |  | -0.39349 | 4.4413 | 8.5554 | 15.2754 | 1.2546 | -2.8131 | -56.6069 | 0 | 0 | 0 | 0 | 0
339 | 2 | 0 | 0 |  | -0.39349 | 4.4413 | 8.5554 | 15.2754 | 2.2546 | -2.5513 | -50.3635 | 0 | 0 | 0 | 0 | 0
339 | 3 | 0 | 0 |  | -0.39349 | 4.4413 | 8.5554 | 15.2754 | 3.2546 | -2.2895 | -42.3453 | 0 | 0 | 0 | 0 | 0
339 | 4 | 0 | 0 |  | -0.39349 | 4.4413 | 8.5554 | 15.2754 | 4.2546 | -2.0277 | -33.5017 | 0 | 0 | 0 | 0 | 0
339 | 5 | 0 | 0 |  | -0.39349 | 4.4413 | 8.5554 | 15.2754 | 5.2546 | -1.7659 | -24.4243 | 0 | 0 | 0 | 0 | 0
339 | 6 | 0 | 0 |  | -0.39349 | 4.4413 | 8.5554 | 15.2754 | 6.2546 | -1.5041 | -15.5227 | 0 | 0 | 0 | 0 | 0
339 | 7 | 0 | 0 |  | -0.39349 | 4.4413 | 8.5554 | 15.2754 | 7.2546 | -1.2423 | -7.1398 | 0 | 0 | 0 | 0 | 0
339 | 8 | 0 | 0 |  | -0.39349 | 4.4413 | 8.5554 | 15.2754 | 8.2546 | -0.98055 | 0.38554 | 0 | 0 | 0 | 0 | 0
339 | 9 | 27 | 26 |  | -0.39349 | 4.4413 | 8.5554 | 15.2754 | 9.2546 | -0.71875 | 6.6908 | 13.3252 | 21.6667 | 34.9918 | 55.553 | 0
339 | 10 | 176 | 71 |  | -0.39349 | 4.4413 | 8.5554 | 15.2754 | 10.2546 | -0.45695 | 11.3951 | 108.5733 | 59.1667 | 167.74 | 266.304 | 0
339 | 11 | 398 | 71 |  | -0.39349 | 4.4413 | 8.5554 | 15.2754 | 11.2546 | -0.19515 | 14.146 | 273.8827 | 59.1667 | 333.0494 | 528.7492 | 1
339 | 12 | 380 | 94 |  | -0.39349 | 4.4413 | 8.5554 | 15.2754 | 12.2546 | 0.066651 | 14.7012 | 266.9235 | 78.3333 | 345.2568 | 548.1297 | 1
339 | 13 | 364 | 91 |  | -0.39349 | 4.4413 | 8.5554 | 15.2754 | 13.2546 | 0.32845 | 13.0081 | 239.7918 | 75.8333 | 315.6251 | 501.0864 | 1
339 | 14 | 328 | 67 |  | -0.39349 | 4.4413 | 8.5554 | 15.2754 | 14.2546 | 0.59025 | 9.2232 | 183.7253 | 55.8333 | 239.5586 | 380.3233 | 0
339 | 15 | 139 | 42 |  | -0.39349 | 4.4413 | 8.5554 | 15.2754 | 15.2546 | 0.85205 | 3.6563 | 57.4432 | 35 | 92.4432 | 146.7628 | 0
339 | 16 | 0 | 8 |  | -0.39349 | 4.4413 | 8.5554 | 15.2754 | 16.2546 | 1.1138 | -3.3172 | 0 | 6.6667 | 6.6667 | 10.584 | 0
339 | 17 | 0 | 0 |  | -0.39349 | 4.4413 | 8.5554 | 15.2754 | 17.2546 | 1.3756 | -11.3227 | 0 | 0 | 0 | 0 | 0
339 | 18 | 0 | 0 |  | -0.39349 | 4.4413 | 8.5554 | 15.2754 | 18.2546 | 1.6374 | -20.0113 | 0 | 0 | 0 | 0 | 0
339 | 19 | 0 | 0 |  | -0.39349 | 4.4413 | 8.5554 | 15.2754 | 19.2546 | 1.8992 | -29.0475 | 0 | 0 | 0 | 0 | 0
339 | 20 | 0 | 0 |  | -0.39349 | 4.4413 | 8.5554 | 15.2754 | 20.2546 | 2.161 | -38.065 | 0 | 0 | 0 | 0 | 0
339 | 21 | 0 | 0 |  | -0.39349 | 4.4413 | 8.5554 | 15.2754 | 21.2546 | 2.4228 | -46.5801 | 0 | 0 | 0 | 0 | 0
339 | 22 | 0 | 0 |  | -0.39349 | 4.4413 | 8.5554 | 15.2754 | 22.2546 | 2.6846 | -53.8426 | 0 | 0 | 0 | 0 | 0
339 | 23 | 0 | 0 |  | -0.39349 | 4.4413 | 8.5554 | 15.2754 | 23.2546 | 2.9464 | -58.6735 | 0 | 0 | 0 | 0 | 0
339 | 24 | 0 | 0 |  | -0.39349 | 4.4413 | 8.5554 | 15.2754 | 24.2546 | 3.2082 | -59.7236 | 0 | 0 | 0 | 0 | 0
340 | 1 | 0 | 0 |  | -0.39541 | 4.4585 | 8.1429 | 14.8629 | 1.2477 | -2.8149 | -56.7438 | 0 | 0 | 0 | 0 | 0
340 | 2 | 0 | 0 |  | -0.39541 | 4.4585 | 8.1429 | 14.8629 | 2.2477 | -2.5531 | -50.5074 | 0 | 0 | 0 | 0 | 0
340 | 3 | 0 | 0 |  | -0.39541 | 4.4585 | 8.1429 | 14.8629 | 3.2477 | -2.2913 | -42.4908 | 0 | 0 | 0 | 0 | 0
340 | 4 | 0 | 0 |  | -0.39541 | 4.4585 | 8.1429 | 14.8629 | 4.2477 | -2.0295 | -33.6474 | 0 | 0 | 0 | 0 | 0
340 | 5 | 0 | 0 |  | -0.39541 | 4.4585 | 8.1429 | 14.8629 | 5.2477 | -1.7677 | -24.57 | 0 | 0 | 0 | 0 | 0
340 | 6 | 0 | 0 |  | -0.39541 | 4.4585 | 8.1429 | 14.8629 | 6.2477 | -1.5059 | -15.6683 | 0 | 0 | 0 | 0 | 0
340 | 7 | 0 | 0 |  | -0.39541 | 4.4585 | 8.1429 | 14.8629 | 7.2477 | -1.2441 | -7.2849 | 0 | 0 | 0 | 0 | 0
340 | 8 | 0 | 0 |  | -0.39541 | 4.4585 | 8.1429 | 14.8629 | 8.2477 | -0.98235 | 0.24226 | 0 | 0 | 0 | 0 | 0
340 | 9 | 0 | 15 |  | -0.39541 | 4.4585 | 8.1429 | 14.8629 | 9.2477 | -0.72055 | 6.5515 | 0 | 12.5 | 12.5 | 19.845 | 0
340 | 10 | 0 | 34 |  | -0.39541 | 4.4585 | 8.1429 | 14.8629 | 10.2477 | -0.45875 | 11.263 | 0 | 28.3333 | 28.3333 | 44.982 | 0
340 | 11 | 18 | 86 |  | -0.39541 | 4.4585 | 8.1429 | 14.8629 | 11.2477 | -0.19695 | 14.0249 | 12.3569 | 71.6667 | 84.0236 | 133.3958 | 1
340 | 12 | 17 | 102 |  | -0.39541 | 4.4585 | 8.1429 | 14.8629 | 12.2477 | 0.064852 | 14.5948 | 11.9198 | 85 | 96.9198 | 153.8699 | 1
340 | 13 | 15 | 97 |  | -0.39541 | 4.4585 | 8.1429 | 14.8629 | 13.2477 | 0.32665 | 12.919 | 9.8689 | 80.8333 | 90.7023 | 143.9989 | 1
340 | 14 | 3 | 73 |  | -0.39541 | 4.4585 | 8.1429 | 14.8629 | 14.2477 | 0.58845 | 9.152 | 1.6792 | 60.8333 | 62.5125 | 99.2449 | 0
340 | 15 | 0 | 32 |  | -0.39541 | 4.4585 | 8.1429 | 14.8629 | 15.2477 | 0.85025 | 3.6016 | 0 | 26.6667 | 26.6667 | 42.336 | 0
340 | 16 | 0 | 4 |  | -0.39541 | 4.4585 | 8.1429 | 14.8629 | 16.2477 | 1.112 | -3.3579 | 0 | 3.3333 | 3.3333 | 5.292 | 0
340 | 17 | 0 | 0 |  | -0.39541 | 4.4585 | 8.1429 | 14.8629 | 17.2477 | 1.3738 | -11.3527 | 0 | 0 | 0 | 0 | 0
340 | 18 | 0 | 0 |  | -0.39541 | 4.4585 | 8.1429 | 14.8629 | 18.2477 | 1.6356 | -20.0344 | 0 | 0 | 0 | 0 | 0
340 | 19 | 0 | 0 |  | -0.39541 | 4.4585 | 8.1429 | 14.8629 | 19.2477 | 1.8974 | -29.0682 | 0 | 0 | 0 | 0 | 0
340 | 20 | 0 | 0 |  | -0.39541 | 4.4585 | 8.1429 | 14.8629 | 20.2477 | 2.1592 | -38.0888 | 0 | 0 | 0 | 0 | 0
340 | 21 | 0 | 0 |  | -0.39541 | 4.4585 | 8.1429 | 14.8629 | 21.2477 | 2.421 | -46.6145 | 0 | 0 | 0 | 0 | 0
340 | 22 | 0 | 0 |  | -0.39541 | 4.4585 | 8.1429 | 14.8629 | 22.2477 | 2.6828 | -53.8976 | 0 | 0 | 0 | 0 | 0
340 | 23 | 0 | 0 |  | -0.39541 | 4.4585 | 8.1429 | 14.8629 | 23.2477 | 2.9446 | -58.7593 | 0 | 0 | 0 | 0 | 0
340 | 24 | 0 | 0 |  | -0.39541 | 4.4585 | 8.1429 | 14.8629 | 24.2477 | 3.2064 | -59.8411 | 0 | 0 | 0 | 0 | 0
341 | 1 | 0 | 0 |  | -0.39722 | 4.4757 | 7.7237 | 14.4437 | 1.2407 | -2.8168 | -56.8747 | 0 | 0 | 0 | 0 | 0
341 | 2 | 0 | 0 |  | -0.39722 | 4.4757 | 7.7237 | 14.4437 | 2.2407 | -2.555 | -50.6463 | 0 | 0 | 0 | 0 | 0
341 | 3 | 0 | 0 |  | -0.39722 | 4.4757 | 7.7237 | 14.4437 | 3.2407 | -2.2932 | -42.6318 | 0 | 0 | 0 | 0 | 0
341 | 4 | 0 | 0 |  | -0.39722 | 4.4757 | 7.7237 | 14.4437 | 4.2407 | -2.0314 | -33.7888 | 0 | 0 | 0 | 0 | 0
341 | 5 | 0 | 0 |  | -0.39722 | 4.4757 | 7.7237 | 14.4437 | 5.2407 | -1.7696 | -24.7114 | 0 | 0 | 0 | 0 | 0
341 | 6 | 0 | 0 |  | -0.39722 | 4.4757 | 7.7237 | 14.4437 | 6.2407 | -1.5078 | -15.8095 | 0 | 0 | 0 | 0 | 0
341 | 7 | 0 | 0 |  | -0.39722 | 4.4757 | 7.7237 | 14.4437 | 7.2407 | -1.246 | -7.4251 | 0 | 0 | 0 | 0 | 0
341 | 8 | 0 | 0 |  | -0.39722 | 4.4757 | 7.7237 | 14.4437 | 8.2407 | -0.98418 | 0.10428 | 0 | 0 | 0 | 0 | 0
341 | 9 | 0 | 15 |  | -0.39722 | 4.4757 | 7.7237 | 14.4437 | 9.2407 | -0.72238 | 6.418 | 0 | 12.5 | 12.5 | 19.845 | 0
341 | 10 | 0 | 54 |  | -0.39722 | 4.4757 | 7.7237 | 14.4437 | 10.2407 | -0.46058 | 11.1371 | 0 | 45 | 45 | 71.442 | 0
341 | 11 | 8 | 87 |  | -0.39722 | 4.4757 | 7.7237 | 14.4437 | 11.2407 | -0.19878 | 13.9104 | 5.4793 | 72.5 | 77.9793 | 123.8 | 1
341 | 12 | 18 | 101 |  | -0.39722 | 4.4757 | 7.7237 | 14.4437 | 12.2407 | 0.063023 | 14.4955 | 12.5997 | 84.1667 | 96.7663 | 153.6262 | 1
341 | 13 | 104 | 103 |  | -0.39722 | 4.4757 | 7.7237 | 14.4437 | 13.2407 | 0.32482 | 12.837 | 68.3465 | 85.8333 | 154.1799 | 244.7759 | 1
341 | 14 | 262 | 79 |  | -0.39722 | 4.4757 | 7.7237 | 14.4437 | 14.2407 | 0.58662 | 9.0877 | 146.5691 | 65.8333 | 212.4025 | 337.2101 | 0
341 | 15 | 68 | 48 |  | -0.39722 | 4.4757 | 7.7237 | 14.4437 | 15.2407 | 0.84842 | 3.5538 | 28.1099 | 40 | 68.1099 | 108.1313 | 0
341 | 16 | 0 | 8 |  | -0.39722 | 4.4757 | 7.7237 | 14.4437 | 16.2407 | 1.1102 | -3.3919 | 0 | 6.6667 | 6.6667 | 10.584 | 0
341 | 17 | 0 | 0 |  | -0.39722 | 4.4757 | 7.7237 | 14.4437 | 17.2407 | 1.372 | -11.3763 | 0 | 0 | 0 | 0 | 0
341 | 18 | 0 | 0 |  | -0.39722 | 4.4757 | 7.7237 | 14.4437 | 18.2407 | 1.6338 | -20.0512 | 0 | 0 | 0 | 0 | 0
341 | 19 | 0 | 0 |  | -0.39722 | 4.4757 | 7.7237 | 14.4437 | 19.2407 | 1.8956 | -29.0825 | 0 | 0 | 0 | 0 | 0
341 | 20 | 0 | 0 |  | -0.39722 | 4.4757 | 7.7237 | 14.4437 | 20.2407 | 2.1574 | -38.1061 | 0 | 0 | 0 | 0 | 0
341 | 21 | 0 | 0 |  | -0.39722 | 4.4757 | 7.7237 | 14.4437 | 21.2407 | 2.4192 | -46.6421 | 0 | 0 | 0 | 0 | 0
341 | 22 | 0 | 0 |  | -0.39722 | 4.4757 | 7.7237 | 14.4437 | 22.2407 | 2.681 | -53.9454 | 0 | 0 | 0 | 0 | 0
341 | 23 | 0 | 0 |  | -0.39722 | 4.4757 | 7.7237 | 14.4437 | 23.2407 | 2.9428 | -58.8376 | 0 | 0 | 0 | 0 | 0
341 | 24 | 0 | 0 |  | -0.39722 | 4.4757 | 7.7237 | 14.4437 | 24.2407 | 3.2046 | -59.9516 | 0 | 0 | 0 | 0 | 0
342 | 1 | 0 | 0 |  | -0.3989 | 4.4929 | 7.2982 | 14.0182 | 1.2336 | -2.8186 | -56.9995 | 0 | 0 | 0 | 0 | 0
342 | 2 | 0 | 0 |  | -0.3989 | 4.4929 | 7.2982 | 14.0182 | 2.2336 | -2.5568 | -50.7799 | 0 | 0 | 0 | 0 | 0
342 | 3 | 0 | 0 |  | -0.3989 | 4.4929 | 7.2982 | 14.0182 | 3.2336 | -2.295 | -42.7681 | 0 | 0 | 0 | 0 | 0
342 | 4 | 0 | 0 |  | -0.3989 | 4.4929 | 7.2982 | 14.0182 | 4.2336 | -2.0332 | -33.9258 | 0 | 0 | 0 | 0 | 0
342 | 5 | 0 | 0 |  | -0.3989 | 4.4929 | 7.2982 | 14.0182 | 5.2336 | -1.7714 | -24.8484 | 0 | 0 | 0 | 0 | 0
342 | 6 | 0 | 0 |  | -0.3989 | 4.4929 | 7.2982 | 14.0182 | 6.2336 | -1.5096 | -15.946 | 0 | 0 | 0 | 0 | 0
342 | 7 | 0 | 0 |  | -0.3989 | 4.4929 | 7.2982 | 14.0182 | 7.2336 | -1.2478 | -7.5604 | 0 | 0 | 0 | 0 | 0
342 | 8 | 0 | 0 |  | -0.3989 | 4.4929 | 7.2982 | 14.0182 | 8.2336 | -0.98603 | -0.028346 | 0 | 0 | 0 | 0 | 0
342 | 9 | 0 | 9 |  | -0.3989 | 4.4929 | 7.2982 | 14.0182 | 9.2336 | -0.72423 | 6.2903 | 0 | 7.5 | 7.5 | 11.907 | 0
342 | 10 | 0 | 33 |  | -0.3989 | 4.4929 | 7.2982 | 14.0182 | 10.2336 | -0.46243 | 11.0176 | 0 | 27.5 | 27.5 | 43.659 | 0
342 | 11 | 0 | 55 |  | -0.3989 | 4.4929 | 7.2982 | 14.0182 | 11.2336 | -0.20063 | 13.8028 | 0 | 45.8333 | 45.8333 | 72.765 | 1
342 | 12 | 0 | 65 |  | -0.3989 | 4.4929 | 7.2982 | 14.0182 | 12.2336 | 0.061166 | 14.4031 | 0 | 54.1667 | 54.1667 | 85.995 | 1
342 | 13 | 0 | 62 |  | -0.3989 | 4.4929 | 7.2982 | 14.0182 | 13.2336 | 0.32297 | 12.7621 | 0 | 51.6667 | 51.6667 | 82.026 | 1
342 | 14 | 0 | 45 |  | -0.3989 | 4.4929 | 7.2982 | 14.0182 | 14.2336 | 0.58476 | 9.0305 | 0 | 37.5 | 37.5 | 59.535 | 0
342 | 15 | 0 | 20 |  | -0.3989 | 4.4929 | 7.2982 | 14.0182 | 15.2336 | 0.84656 | 3.5127 | 0 | 16.6667 | 16.6667 | 26.46 | 0
342 | 16 | 0 | 3 |  | -0.3989 | 4.4929 | 7.2982 | 14.0182 | 16.2336 | 1.1084 | -3.4194 | 0 | 2.5 | 2.5 | 3.969 | 0
342 | 17 | 0 | 0 |  | -0.3989 | 4.4929 | 7.2982 | 14.0182 | 17.2336 | 1.3702 | -11.3934 | 0 | 0 | 0 | 0 | 0
342 | 18 | 0 | 0 |  | -0.3989 | 4.4929 | 7.2982 | 14.0182 | 18.2336 | 1.632 | -20.0617 | 0 | 0 | 0 | 0 | 0
342 | 19 | 0 | 0 |  | -0.3989 | 4.4929 | 7.2982 | 14.0182 | 19.2336 | 1.8938 | -29.0906 | 0 | 0 | 0 | 0 | 0
342 | 20 | 0 | 0 |  | -0.3989 | 4.4929 | 7.2982 | 14.0182 | 20.2336 | 2.1556 | -38.1169 | 0 | 0 | 0 | 0 | 0
342 | 21 | 0 | 0 |  | -0.3989 | 4.4929 | 7.2982 | 14.0182 | 21.2336 | 2.4174 | -46.6629 | 0 | 0 | 0 | 0 | 0
342 | 22 | 0 | 0 |  | -0.3989 | 4.4929 | 7.2982 | 14.0182 | 22.2336 | 2.6792 | -53.9859 | 0 | 0 | 0 | 0 | 0
342 | 23 | 0 | 0 |  | -0.3989 | 4.4929 | 7.2982 | 14.0182 | 23.2336 | 2.941 | -58.9084 | 0 | 0 | 0 | 0 | 0
342 | 24 | 0 | 0 |  | -0.3989 | 4.4929 | 7.2982 | 14.0182 | 24.2336 | 3.2028 | -60.055 | 0 | 0 | 0 | 0 | 0
343 | 1 | 0 | 0 |  | -0.40045 | 4.5101 | 6.8669 | 13.5869 | 1.2264 | -2.8205 | -57.118 | 0 | 0 | 0 | 0 | 0
343 | 2 | 0 | 0 |  | -0.40045 | 4.5101 | 6.8669 | 13.5869 | 2.2264 | -2.5587 | -50.9081 | 0 | 0 | 0 | 0 | 0
343 | 3 | 0 | 0 |  | -0.40045 | 4.5101 | 6.8669 | 13.5869 | 3.2264 | -2.2969 | -42.8996 | 0 | 0 | 0 | 0 | 0
343 | 4 | 0 | 0 |  | -0.40045 | 4.5101 | 6.8669 | 13.5869 | 4.2264 | -2.0351 | -34.0582 | 0 | 0 | 0 | 0 | 0
343 | 5 | 0 | 0 |  | -0.40045 | 4.5101 | 6.8669 | 13.5869 | 5.2264 | -1.7733 | -24.9808 | 0 | 0 | 0 | 0 | 0
343 | 6 | 0 | 0 |  | -0.40045 | 4.5101 | 6.8669 | 13.5869 | 6.2264 | -1.5115 | -16.0778 | 0 | 0 | 0 | 0 | 0
343 | 7 | 0 | 0 |  | -0.40045 | 4.5101 | 6.8669 | 13.5869 | 7.2264 | -1.2497 | -7.6907 | 0 | 0 | 0 | 0 | 0
343 | 8 | 0 | 0 |  | -0.40045 | 4.5101 | 6.8669 | 13.5869 | 8.2264 | -0.98791 | -0.15553 | 0 | 0 | 0 | 0 | 0
343 | 9 | 8 | 24 |  | -0.40045 | 4.5101 | 6.8669 | 13.5869 | 9.2264 | -0.72611 | 6.1685 | 3.8803 | 20 | 23.8803 | 37.9124 | 0
343 | 10 | 149 | 66 |  | -0.40045 | 4.5101 | 6.8669 | 13.5869 | 10.2264 | -0.46431 | 10.9044 | 90.8012 | 55 | 145.8012 | 231.474 | 0
343 | 11 | 250 | 87 |  | -0.40045 | 4.5101 | 6.8669 | 13.5869 | 11.2264 | -0.20252 | 13.7019 | 170.499 | 72.5 | 242.999 | 385.7853 | 1
343 | 12 | 438 | 75 |  | -0.40045 | 4.5101 | 6.8669 | 13.5869 | 12.2264 | 0.059284 | 14.3177 | 305.666 | 62.5 | 368.166 | 584.5004 | 1
343 | 13 | 355 | 89 |  | -0.40045 | 4.5101 | 6.8669 | 13.5869 | 13.2264 | 0.32108 | 12.6942 | 232.8576 | 74.1667 | 307.0243 | 487.4318 | 1
343 | 14 | 332 | 64 |  | -0.40045 | 4.5101 | 6.8669 | 13.5869 | 14.2264 | 0.58288 | 8.9801 | 185.6084 | 53.3333 | 238.9418 | 379.344 | 0
343 | 15 | 139 | 41 |  | -0.40045 | 4.5101 | 6.8669 | 13.5869 | 15.2264 | 0.84468 | 3.4784 | 57.5242 | 34.1667 | 91.6909 | 145.5685 | 0
343 | 16 | 0 | 7 |  | -0.40045 | 4.5101 | 6.8669 | 13.5869 | 16.2264 | 1.1065 | -3.4403 | 0 | 5.8333 | 5.8333 | 9.261 | 0
343 | 17 | 0 | 0 |  | -0.40045 | 4.5101 | 6.8669 | 13.5869 | 17.2264 | 1.3683 | -11.4041 | 0 | 0 | 0 | 0 | 0
343 | 18 | 0 | 0 |  | -0.40045 | 4.5101 | 6.8669 | 13.5869 | 18.2264 | 1.6301 | -20.0659 | 0 | 0 | 0 | 0 | 0
343 | 19 | 0 | 0 |  | -0.40045 | 4.5101 | 6.8669 | 13.5869 | 19.2264 | 1.8919 | -29.0923 | 0 | 0 | 0 | 0 | 0
343 | 20 | 0 | 0 |  | -0.40045 | 4.5101 | 6.8669 | 13.5869 | 20.2264 | 2.1537 | -38.1213 | 0 | 0 | 0 | 0 | 0
343 | 21 | 0 | 0 |  | -0.40045 | 4.5101 | 6.8669 | 13.5869 | 21.2264 | 2.4155 | -46.6769 | 0 | 0 | 0 | 0 | 0
343 | 22 | 0 | 0 |  | -0.40045 | 4.5101 | 6.8669 | 13.5869 | 22.2264 | 2.6773 | -54.0193 | 0 | 0 | 0 | 0 | 0
343 | 23 | 0 | 0 |  | -0.40045 | 4.5101 | 6.8669 | 13.5869 | 23.2264 | 2.9391 | -58.9717 | 0 | 0 | 0 | 0 | 0
343 | 24 | 0 | 0 |  | -0.40045 | 4.5101 | 6.8669 | 13.5869 | 24.2264 | 3.2009 | -60.1512 | 0 | 0 | 0 | 0 | 0
344 | 1 | 0 | 0 |  | -0.40189 | 4.5273 | 6.43 | 13.15 | 1.2192 | -2.8224 | -57.2301 | 0 | 0 | 0 | 0 | 0
344 | 2 | 0 | 0 |  | -0.40189 | 4.5273 | 6.43 | 13.15 | 2.2192 | -2.5606 | -51.0309 | 0 | 0 | 0 | 0 | 0
344 | 3 | 0 | 0 |  | -0.40189 | 4.5273 | 6.43 | 13.15 | 3.2192 | -2.2988 | -43.0263 | 0 | 0 | 0 | 0 | 0
344 | 4 | 0 | 0 |  | -0.40189 | 4.5273 | 6.43 | 13.15 | 4.2192 | -2.037 | -34.186 | 0 | 0 | 0 | 0 | 0
344 | 5 | 0 | 0 |  | -0.40189 | 4.5273 | 6.43 | 13.15 | 5.2192 | -1.7752 | -25.1087 | 0 | 0 | 0 | 0 | 0
344 | 6 | 0 | 0 |  | -0.40189 | 4.5273 | 6.43 | 13.15 | 6.2192 | -1.5134 | -16.2049 | 0 | 0 | 0 | 0 | 0
344 | 7 | 0 | 0 |  | -0.40189 | 4.5273 | 6.43 | 13.15 | 7.2192 | -1.2516 | -7.8159 | 0 | 0 | 0 | 0 | 0
344 | 8 | 0 | 0 |  | -0.40189 | 4.5273 | 6.43 | 13.15 | 8.2192 | -0.98982 | -0.2772 | 0 | 0 | 0 | 0 | 0
344 | 9 | 0 | 24 |  | -0.40189 | 4.5273 | 6.43 | 13.15 | 9.2192 | -0.72802 | 6.0528 | 0 | 20 | 20 | 31.752 | 0
344 | 10 | 0 | 51 |  | -0.40189 | 4.5273 | 6.43 | 13.15 | 10.2192 | -0.46622 | 10.7977 | 0 | 42.5 | 42.5 | 67.473 | 0
344 | 11 | 8 | 84 |  | -0.40189 | 4.5273 | 6.43 | 13.15 | 11.2192 | -0.20442 | 13.6078 | 5.4452 | 70 | 75.4452 | 119.7769 | 1
344 | 12 | 18 | 99 |  | -0.40189 | 4.5273 | 6.43 | 13.15 | 12.2192 | 0.057378 | 14.2394 | 12.5449 | 82.5 | 95.0449 | 150.8933 | 1
344 | 13 | 349 | 85 |  | -0.40189 | 4.5273 | 6.43 | 13.15 | 13.2192 | 0.31918 | 12.6334 | 228.7515 | 70.8333 | 299.5848 | 475.6209 | 1
344 | 14 | 285 | 73 |  | -0.40189 | 4.5273 | 6.43 | 13.15 | 14.2192 | 0.58098 | 8.9368 | 159.3184 | 60.8333 | 220.1518 | 349.513 | 0
344 | 15 | 138 | 40 |  | -0.40189 | 4.5273 | 6.43 | 13.15 | 15.2192 | 0.84278 | 3.4509 | 57.1598 | 33.3333 | 90.4932 | 143.667 | 0
344 | 16 | 0 | 7 |  | -0.40189 | 4.5273 | 6.43 | 13.15 | 16.2192 | 1.1046 | -3.4547 | 0 | 5.8333 | 5.8333 | 9.261 | 0
344 | 17 | 0 | 0 |  | -0.40189 | 4.5273 | 6.43 | 13.15 | 17.2192 | 1.3664 | -11.4085 | 0 | 0 | 0 | 0 | 0
344 | 18 | 0 | 0 |  | -0.40189 | 4.5273 | 6.43 | 13.15 | 18.2192 | 1.6282 | -20.0639 | 0 | 0 | 0 | 0 | 0
344 | 19 | 0 | 0 |  | -0.40189 | 4.5273 | 6.43 | 13.15 | 19.2192 | 1.89 | -29.0879 | 0 | 0 | 0 | 0 | 0
344 | 20 | 0 | 0 |  | -0.40189 | 4.5273 | 6.43 | 13.15 | 20.2192 | 2.1518 | -38.1194 | 0 | 0 | 0 | 0 | 0
344 | 21 | 0 | 0 |  | -0.40189 | 4.5273 | 6.43 | 13.15 | 21.2192 | 2.4136 | -46.6843 | 0 | 0 | 0 | 0 | 0
344 | 22 | 0 | 0 |  | -0.40189 | 4.5273 | 6.43 | 13.15 | 22.2192 | 2.6754 | -54.0454 | 0 | 0 | 0 | 0 | 0
344 | 23 | 0 | 0 |  | -0.40189 | 4.5273 | 6.43 | 13.15 | 23.2192 | 2.9372 | -59.0275 | 0 | 0 | 0 | 0 | 0
344 | 24 | 0 | 0 |  | -0.40189 | 4.5273 | 6.43 | 13.15 | 24.2192 | 3.199 | -60.2402 | 0 | 0 | 0 | 0 | 0
345 | 1 | 0 | 0 |  | -0.40319 | 4.5446 | 5.9881 | 12.7081 | 1.2118 | -2.8243 | -57.3359 | 0 | 0 | 0 | 0 | 0
345 | 2 | 0 | 0 |  | -0.40319 | 4.5446 | 5.9881 | 12.7081 | 2.2118 | -2.5625 | -51.1482 | 0 | 0 | 0 | 0 | 0
345 | 3 | 0 | 0 |  | -0.40319 | 4.5446 | 5.9881 | 12.7081 | 3.2118 | -2.3007 | -43.148 | 0 | 0 | 0 | 0 | 0
345 | 4 | 0 | 0 |  | -0.40319 | 4.5446 | 5.9881 | 12.7081 | 4.2118 | -2.0389 | -34.3092 | 0 | 0 | 0 | 0 | 0
345 | 5 | 0 | 0 |  | -0.40319 | 4.5446 | 5.9881 | 12.7081 | 5.2118 | -1.7771 | -25.2319 | 0 | 0 | 0 | 0 | 0
345 | 6 | 0 | 0 |  | -0.40319 | 4.5446 | 5.9881 | 12.7081 | 6.2118 | -1.5153 | -16.3271 | 0 | 0 | 0 | 0 | 0
345 | 7 | 0 | 0 |  | -0.40319 | 4.5446 | 5.9881 | 12.7081 | 7.2118 | -1.2535 | -7.9359 | 0 | 0 | 0 | 0 | 0
345 | 8 | 0 | 0 |  | -0.40319 | 4.5446 | 5.9881 | 12.7081 | 8.2118 | -0.99175 | -0.39329 | 0 | 0 | 0 | 0 | 0
345 | 9 | 0 | 22 |  | -0.40319 | 4.5446 | 5.9881 | 12.7081 | 9.2118 | -0.72995 | 5.9431 | 0 | 18.3333 | 18.3333 | 29.106 | 0
345 | 10 | 46 | 79 |  | -0.40319 | 4.5446 | 5.9881 | 12.7081 | 10.2118 | -0.46815 | 10.6975 | 27.8799 | 65.8333 | 93.7133 | 148.7792 | 0
345 | 11 | 333 | 79 |  | -0.40319 | 4.5446 | 5.9881 | 12.7081 | 11.2118 | -0.20635 | 13.5206 | 226.2387 | 65.8333 | 292.072 | 463.6935 | 1
345 | 12 | 15 | 99 |  | -0.40319 | 4.5446 | 5.9881 | 12.7081 | 12.2118 | 0.055449 | 14.1681 | 10.4414 | 82.5 | 92.9414 | 147.5538 | 1
345 | 13 | 20 | 93 |  | -0.40319 | 4.5446 | 5.9881 | 12.7081 | 13.2118 | 0.31725 | 12.5797 | 13.101 | 77.5 | 90.601 | 143.8381 | 1
345 | 14 | 61 | 80 |  | -0.40319 | 4.5446 | 5.9881 | 12.7081 | 14.2118 | 0.57905 | 8.9005 | 34.1021 | 66.6667 | 100.7687 | 159.9805 | 0
345 | 15 | 0 | 31 |  | -0.40319 | 4.5446 | 5.9881 | 12.7081 | 15.2118 | 0.84085 | 3.4302 | 0 | 25.8333 | 25.8333 | 41.013 | 0
345 | 16 | 0 | 4 |  | -0.40319 | 4.5446 | 5.9881 | 12.7081 | 16.2118 | 1.1026 | -3.4624 | 0 | 3.3333 | 3.3333 | 5.292 | 0
345 | 17 | 0 | 0 |  | -0.40319 | 4.5446 | 5.9881 | 12.7081 | 17.2118 | 1.3644 | -11.4066 | 0 | 0 | 0 | 0 | 0
345 | 18 | 0 | 0 |  | -0.40319 | 4.5446 | 5.9881 | 12.7081 | 18.2118 | 1.6262 | -20.0556 | 0 | 0 | 0 | 0 | 0
345 | 19 | 0 | 0 |  | -0.40319 | 4.5446 | 5.9881 | 12.7081 | 19.2118 | 1.888 | -29.0772 | 0 | 0 | 0 | 0 | 0
345 | 20 | 0 | 0 |  | -0.40319 | 4.5446 | 5.9881 | 12.7081 | 20.2118 | 2.1498 | -38.1111 | 0 | 0 | 0 | 0 | 0
345 | 21 | 0 | 0 |  | -0.40319 | 4.5446 | 5.9881 | 12.7081 | 21.2118 | 2.4116 | -46.685 | 0 | 0 | 0 | 0 | 0
345 | 22 | 0 | 0 |  | -0.40319 | 4.5446 | 5.9881 | 12.7081 | 22.2118 | 2.6734 | -54.0644 | 0 | 0 | 0 | 0 | 0
345 | 23 | 0 | 0 |  | -0.40319 | 4.5446 | 5.9881 | 12.7081 | 23.2118 | 2.9352 | -59.0757 | 0 | 0 | 0 | 0 | 0
345 | 24 | 0 | 0 |  | -0.40319 | 4.5446 | 5.9881 | 12.7081 | 24.2118 | 3.197 | -60.3219 | 0 | 0 | 0 | 0 | 0
346 | 1 | 0 | 0 |  | -0.40437 | 4.5618 | 5.5415 | 12.2615 | 1.2044 | -2.8263 | -57.4353 | 0 | 0 | 0 | 0 | 0
346 | 2 | 0 | 0 |  | -0.40437 | 4.5618 | 5.5415 | 12.2615 | 2.2044 | -2.5645 | -51.26 | 0 | 0 | 0 | 0 | 0
346 | 3 | 0 | 0 |  | -0.40437 | 4.5618 | 5.5415 | 12.2615 | 3.2044 | -2.3027 | -43.2648 | 0 | 0 | 0 | 0 | 0
346 | 4 | 0 | 0 |  | -0.40437 | 4.5618 | 5.5415 | 12.2615 | 4.2044 | -2.0409 | -34.4276 | 0 | 0 | 0 | 0 | 0
346 | 5 | 0 | 0 |  | -0.40437 | 4.5618 | 5.5415 | 12.2615 | 5.2044 | -1.7791 | -25.3503 | 0 | 0 | 0 | 0 | 0
346 | 6 | 0 | 0 |  | -0.40437 | 4.5618 | 5.5415 | 12.2615 | 6.2044 | -1.5173 | -16.4444 | 0 | 0 | 0 | 0 | 0
346 | 7 | 0 | 0 |  | -0.40437 | 4.5618 | 5.5415 | 12.2615 | 7.2044 | -1.2555 | -8.0507 | 0 | 0 | 0 | 0 | 0
346 | 8 | 0 | 0 |  | -0.40437 | 4.5618 | 5.5415 | 12.2615 | 8.2044 | -0.9937 | -0.50372 | 0 | 0 | 0 | 0 | 0
346 | 9 | 0 | 8 |  | -0.40437 | 4.5618 | 5.5415 | 12.2615 | 9.2044 | -0.7319 | 5.8395 | 0 | 6.6667 | 6.6667 | 10.584 | 0
346 | 10 | 0 | 49 |  | -0.40437 | 4.5618 | 5.5415 | 12.2615 | 10.2044 | -0.4701 | 10.6039 | 0 | 40.8333 | 40.8333 | 64.827 | 0
346 | 11 | 0 | 53 |  | -0.40437 | 4.5618 | 5.5415 | 12.2615 | 11.2044 | -0.2083 | 13.4403 | 0 | 44.1667 | 44.1667 | 70.119 | 1
346 | 12 | 0 | 64 |  | -0.40437 | 4.5618 | 5.5415 | 12.2615 | 12.2044 | 0.053501 | 14.104 | 0 | 53.3333 | 53.3333 | 84.672 | 1
346 | 13 | 0 | 61 |  | -0.40437 | 4.5618 | 5.5415 | 12.2615 | 13.2044 | 0.3153 | 12.5331 | 0 | 50.8333 | 50.8333 | 80.703 | 1
346 | 14 | 0 | 44 |  | -0.40437 | 4.5618 | 5.5415 | 12.2615 | 14.2044 | 0.5771 | 8.8712 | 0 | 36.6667 | 36.6667 | 58.212 | 0
346 | 15 | 0 | 19 |  | -0.40437 | 4.5618 | 5.5415 | 12.2615 | 15.2044 | 0.8389 | 3.4163 | 0 | 15.8333 | 15.8333 | 25.137 | 0
346 | 16 | 0 | 2 |  | -0.40437 | 4.5618 | 5.5415 | 12.2615 | 16.2044 | 1.1007 | -3.4637 | 0 | 1.6667 | 1.6667 | 2.646 | 0
346 | 17 | 0 | 0 |  | -0.40437 | 4.5618 | 5.5415 | 12.2615 | 17.2044 | 1.3625 | -11.3983 | 0 | 0 | 0 | 0 | 0
346 | 18 | 0 | 0 |  | -0.40437 | 4.5618 | 5.5415 | 12.2615 | 18.2044 | 1.6243 | -20.0412 | 0 | 0 | 0 | 0 | 0
346 | 19 | 0 | 0 |  | -0.40437 | 4.5618 | 5.5415 | 12.2615 | 19.2044 | 1.8861 | -29.0604 | 0 | 0 | 0 | 0 | 0
346 | 20 | 0 | 0 |  | -0.40437 | 4.5618 | 5.5415 | 12.2615 | 20.2044 | 2.1479 | -38.0966 | 0 | 0 | 0 | 0 | 0
346 | 21 | 0 | 0 |  | -0.40437 | 4.5618 | 5.5415 | 12.2615 | 21.2044 | 2.4097 | -46.6791 | 0 | 0 | 0 | 0 | 0
346 | 22 | 0 | 0 |  | -0.40437 | 4.5618 | 5.5415 | 12.2615 | 22.2044 | 2.6715 | -54.0763 | 0 | 0 | 0 | 0 | 0
346 | 23 | 0 | 0 |  | -0.40437 | 4.5618 | 5.5415 | 12.2615 | 23.2044 | 2.9333 | -59.1164 | 0 | 0 | 0 | 0 | 0
346 | 24 | 0 | 0 |  | -0.40437 | 4.5618 | 5.5415 | 12.2615 | 24.2044 | 3.1951 | -60.3963 | 0 | 0 | 0 | 0 | 0
347 | 1 | 0 | 0 |  | -0.40543 | 4.579 | 5.0907 | 11.8107 | 1.1968 | -2.8283 | -57.528 | 0 | 0 | 0 | 0 | 0
347 | 2 | 0 | 0 |  | -0.40543 | 4.579 | 5.0907 | 11.8107 | 2.1968 | -2.5665 | -51.366 | 0 | 0 | 0 | 0 | 0
347 | 3 | 0 | 0 |  | -0.40543 | 4.579 | 5.0907 | 11.8107 | 3.1968 | -2.3047 | -43.3764 | 0 | 0 | 0 | 0 | 0
347 | 4 | 0 | 0 |  | -0.40543 | 4.579 | 5.0907 | 11.8107 | 4.1968 | -2.0429 | -34.5411 | 0 | 0 | 0 | 0 | 0
347 | 5 | 0 | 0 |  | -0.40543 | 4.579 | 5.0907 | 11.8107 | 5.1968 | -1.7811 | -25.4639 | 0 | 0 | 0 | 0 | 0
347 | 6 | 0 | 0 |  | -0.40543 | 4.579 | 5.0907 | 11.8107 | 6.1968 | -1.5193 | -16.5567 | 0 | 0 | 0 | 0 | 0
347 | 7 | 0 | 0 |  | -0.40543 | 4.579 | 5.0907 | 11.8107 | 7.1968 | -1.2575 | -8.1601 | 0 | 0 | 0 | 0 | 0
347 | 8 | 0 | 0 |  | -0.40543 | 4.579 | 5.0907 | 11.8107 | 8.1968 | -0.99566 | -0.60844 | 0 | 0 | 0 | 0 | 0
347 | 9 | 0 | 12 |  | -0.40543 | 4.579 | 5.0907 | 11.8107 | 9.1968 | -0.73386 | 5.7421 | 0 | 10 | 10 | 15.876 | 0
347 | 10 | 0 | 48 |  | -0.40543 | 4.579 | 5.0907 | 11.8107 | 10.1968 | -0.47207 | 10.5169 | 0 | 40 | 40 | 63.504 | 0
347 | 11 | 7 | 81 |  | -0.40543 | 4.579 | 5.0907 | 11.8107 | 11.1968 | -0.21027 | 13.3669 | 4.7399 | 67.5 | 72.2399 | 114.688 | 1
347 | 12 | 16 | 96 |  | -0.40543 | 4.579 | 5.0907 | 11.8107 | 12.1968 | 0.051534 | 14.047 | 11.1147 | 80 | 91.1147 | 144.6537 | 1
347 | 13 | 15 | 92 |  | -0.40543 | 4.579 | 5.0907 | 11.8107 | 13.1968 | 0.31333 | 12.4937 | 9.8177 | 76.6667 | 86.4844 | 137.3026 | 0
347 | 14 | 3 | 69 |  | -0.40543 | 4.579 | 5.0907 | 11.8107 | 14.1968 | 0.57513 | 8.8488 | 1.6782 | 57.5 | 59.1782 | 93.9513 | 0
347 | 15 | 0 | 30 |  | -0.40543 | 4.579 | 5.0907 | 11.8107 | 15.1968 | 0.83693 | 3.4091 | 0 | 25 | 25 | 39.69 | 0
347 | 16 | 0 | 4 |  | -0.40543 | 4.579 | 5.0907 | 11.8107 | 16.1968 | 1.0987 | -3.4585 | 0 | 3.3333 | 3.3333 | 5.292 | 0
347 | 17 | 0 | 0 |  | -0.40543 | 4.579 | 5.0907 | 11.8107 | 17.1968 | 1.3605 | -11.3838 | 0 | 0 | 0 | 0 | 0
347 | 18 | 0 | 0 |  | -0.40543 | 4.579 | 5.0907 | 11.8107 | 18.1968 | 1.6223 | -20.0207 | 0 | 0 | 0 | 0 | 0
347 | 19 | 0 | 0 |  | -0.40543 | 4.579 | 5.0907 | 11.8107 | 19.1968 | 1.8841 | -29.0375 | 0 | 0 | 0 | 0 | 0
347 | 20 | 0 | 0 |  | -0.40543 | 4.579 | 5.0907 | 11.8107 | 20.1968 | 2.1459 | -38.0758 | 0 | 0 | 0 | 0 | 0
347 | 21 | 0 | 0 |  | -0.40543 | 4.579 | 5.0907 | 11.8107 | 21.1968 | 2.4077 | -46.6666 | 0 | 0 | 0 | 0 | 0
347 | 22 | 0 | 0 |  | -0.40543 | 4.579 | 5.0907 | 11.8107 | 22.1968 | 2.6695 | -54.0811 | 0 | 0 | 0 | 0 | 0
347 | 23 | 0 | 0 |  | -0.40543 | 4.579 | 5.0907 | 11.8107 | 23.1968 | 2.9313 | -59.1496 | 0 | 0 | 0 | 0 | 0
347 | 24 | 0 | 0 |  | -0.40543 | 4.579 | 5.0907 | 11.8107 | 24.1968 | 3.1931 | -60.4633 | 0 | 0 | 0 | 0 | 0
348 | 1 | 0 | 0 |  | -0.40636 | 4.5962 | 4.636 | 11.356 | 1.1893 | -2.8302 | -57.6142 | 0 | 0 | 0 | 0 | 0
348 | 2 | 0 | 0 |  | -0.40636 | 4.5962 | 4.636 | 11.356 | 2.1893 | -2.5684 | -51.4663 | 0 | 0 | 0 | 0 | 0
348 | 3 | 0 | 0 |  | -0.40636 | 4.5962 | 4.636 | 11.356 | 3.1893 | -2.3066 | -43.4828 | 0 | 0 | 0 | 0 | 0
348 | 4 | 0 | 0 |  | -0.40636 | 4.5962 | 4.636 | 11.356 | 4.1893 | -2.0448 | -34.6497 | 0 | 0 | 0 | 0 | 0
348 | 5 | 0 | 0 |  | -0.40636 | 4.5962 | 4.636 | 11.356 | 5.1893 | -1.783 | -25.5726 | 0 | 0 | 0 | 0 | 0
348 | 6 | 0 | 0 |  | -0.40636 | 4.5962 | 4.636 | 11.356 | 6.1893 | -1.5212 | -16.6639 | 0 | 0 | 0 | 0 | 0
348 | 7 | 0 | 0 |  | -0.40636 | 4.5962 | 4.636 | 11.356 | 7.1893 | -1.2594 | -8.2642 | 0 | 0 | 0 | 0 | 0
348 | 8 | 0 | 0 |  | -0.40636 | 4.5962 | 4.636 | 11.356 | 8.1893 | -0.99765 | -0.70737 | 0 | 0 | 0 | 0 | 0
348 | 9 | 0 | 12 |  | -0.40636 | 4.5962 | 4.636 | 11.356 | 9.1893 | -0.73585 | 5.6509 | 0 | 10 | 10 | 15.876 | 0
348 | 10 | 0 | 47 |  | -0.40636 | 4.5962 | 4.636 | 11.356 | 10.1893 | -0.47405 | 10.4365 | 0 | 39.1667 | 39.1667 | 62.181 | 0
348 | 11 | 7 | 82 |  | -0.40636 | 4.5962 | 4.636 | 11.356 | 11.1893 | -0.21225 | 13.3006 | 4.7328 | 68.3333 | 73.0661 | 115.9997 | 1
348 | 12 | 22 | 96 |  | -0.40636 | 4.5962 | 4.636 | 11.356 | 12.1893 | 0.04955 | 13.9971 | 15.2699 | 80 | 95.2699 | 151.2506 | 1
348 | 13 | 20 | 92 |  | -0.40636 | 4.5962 | 4.636 | 11.356 | 13.1893 | 0.31135 | 12.4614 | 13.0876 | 76.6667 | 89.7543 | 142.4939 | 0
348 | 14 | 4 | 70 |  | -0.40636 | 4.5962 | 4.636 | 11.356 | 14.1893 | 0.57315 | 8.8335 | 2.2388 | 58.3333 | 60.5721 | 96.1643 | 0
348 | 15 | 0 | 30 |  | -0.40636 | 4.5962 | 4.636 | 11.356 | 15.1893 | 0.83495 | 3.4087 | 0 | 25 | 25 | 39.69 | 0
348 | 16 | 0 | 4 |  | -0.40636 | 4.5962 | 4.636 | 11.356 | 16.1893 | 1.0967 | -3.4467 | 0 | 3.3333 | 3.3333 | 5.292 | 0
348 | 17 | 0 | 0 |  | -0.40636 | 4.5962 | 4.636 | 11.356 | 17.1893 | 1.3585 | -11.363 | 0 | 0 | 0 | 0 | 0
348 | 18 | 0 | 0 |  | -0.40636 | 4.5962 | 4.636 | 11.356 | 18.1893 | 1.6203 | -19.994 | 0 | 0 | 0 | 0 | 0
348 | 19 | 0 | 0 |  | -0.40636 | 4.5962 | 4.636 | 11.356 | 19.1893 | 1.8821 | -29.0086 | 0 | 0 | 0 | 0 | 0
348 | 20 | 0 | 0 |  | -0.40636 | 4.5962 | 4.636 | 11.356 | 20.1893 | 2.1439 | -38.0488 | 0 | 0 | 0 | 0 | 0
348 | 21 | 0 | 0 |  | -0.40636 | 4.5962 | 4.636 | 11.356 | 21.1893 | 2.4057 | -46.6476 | 0 | 0 | 0 | 0 | 0
348 | 22 | 0 | 0 |  | -0.40636 | 4.5962 | 4.636 | 11.356 | 22.1893 | 2.6675 | -54.0788 | 0 | 0 | 0 | 0 | 0
348 | 23 | 0 | 0 |  | -0.40636 | 4.5962 | 4.636 | 11.356 | 23.1893 | 2.9293 | -59.1752 | 0 | 0 | 0 | 0 | 0
348 | 24 | 0 | 0 |  | -0.40636 | 4.5962 | 4.636 | 11.356 | 24.1893 | 3.1911 | -60.5228 | 0 | 0 | 0 | 0 | 0
349 | 1 | 0 | 0 |  | -0.40716 | 4.6134 | 4.1779 | 10.8979 | 1.1816 | -2.8322 | -57.6936 | 0 | 0 | 0 | 0 | 0
349 | 2 | 0 | 0 |  | -0.40716 | 4.6134 | 4.1779 | 10.8979 | 2.1816 | -2.5704 | -51.5608 | 0 | 0 | 0 | 0 | 0
349 | 3 | 0 | 0 |  | -0.40716 | 4.6134 | 4.1779 | 10.8979 | 3.1816 | -2.3086 | -43.584 | 0 | 0 | 0 | 0 | 0
349 | 4 | 0 | 0 |  | -0.40716 | 4.6134 | 4.1779 | 10.8979 | 4.1816 | -2.0468 | -34.7534 | 0 | 0 | 0 | 0 | 0
349 | 5 | 0 | 0 |  | -0.40716 | 4.6134 | 4.1779 | 10.8979 | 5.1816 | -1.785 | -25.6763 | 0 | 0 | 0 | 0 | 0
349 | 6 | 0 | 0 |  | -0.40716 | 4.6134 | 4.1779 | 10.8979 | 6.1816 | -1.5232 | -16.7659 | 0 | 0 | 0 | 0 | 0
349 | 7 | 0 | 0 |  | -0.40716 | 4.6134 | 4.1779 | 10.8979 | 7.1816 | -1.2614 | -8.3628 | 0 | 0 | 0 | 0 | 0
349 | 8 | 0 | 0 |  | -0.40716 | 4.6134 | 4.1779 | 10.8979 | 8.1816 | -0.99965 | -0.80047 | 0 | 0 | 0 | 0 | 0
349 | 9 | 0 | 20 |  | -0.40716 | 4.6134 | 4.1779 | 10.8979 | 9.1816 | -0.73785 | 5.5659 | 0 | 16.6667 | 16.6667 | 26.46 | 0
349 | 10 | 152 | 61 |  | -0.40716 | 4.6134 | 4.1779 | 10.8979 | 10.1816 | -0.47605 | 10.3629 | 91.2533 | 50.8333 | 142.0866 | 225.5767 | 0
349 | 11 | 379 | 66 |  | -0.40716 | 4.6134 | 4.1779 | 10.8979 | 11.1816 | -0.21425 | 13.2412 | 255.8939 | 55 | 310.8939 | 493.5752 | 1
349 | 12 | 362 | 89 |  | -0.40716 | 4.6134 | 4.1779 | 10.8979 | 12.1816 | 0.047551 | 13.9544 | 251.0814 | 74.1667 | 325.2481 | 516.3639 | 1
349 | 13 | 193 | 97 |  | -0.40716 | 4.6134 | 4.1779 | 10.8979 | 13.1816 | 0.30935 | 12.4363 | 126.2867 | 80.8333 | 207.1201 | 328.8238 | 0
349 | 14 | 8 | 68 |  | -0.40716 | 4.6134 | 4.1779 | 10.8979 | 14.1816 | 0.57115 | 8.8251 | 4.4806 | 56.6667 | 61.1473 | 97.0774 | 0
349 | 15 | 140 | 37 |  | -0.40716 | 4.6134 | 4.1779 | 10.8979 | 15.1816 | 0.83295 | 3.415 | 58.4145 | 30.8333 | 89.2479 | 141.6899 | 0
349 | 16 | 0 | 7 |  | -0.40716 | 4.6134 | 4.1779 | 10.8979 | 16.1816 | 1.0947 | -3.4285 | 0 | 5.8333 | 5.8333 | 9.261 | 0
349 | 17 | 0 | 0 |  | -0.40716 | 4.6134 | 4.1779 | 10.8979 | 17.1816 | 1.3565 | -11.336 | 0 | 0 | 0 | 0 | 0
349 | 18 | 0 | 0 |  | -0.40716 | 4.6134 | 4.1779 | 10.8979 | 18.1816 | 1.6183 | -19.9614 | 0 | 0 | 0 | 0 | 0
349 | 19 | 0 | 0 |  | -0.40716 | 4.6134 | 4.1779 | 10.8979 | 19.1816 | 1.8801 | -28.9737 | 0 | 0 | 0 | 0 | 0
349 | 20 | 0 | 0 |  | -0.40716 | 4.6134 | 4.1779 | 10.8979 | 20.1816 | 2.1419 | -38.0158 | 0 | 0 | 0 | 0 | 0
349 | 21 | 0 | 0 |  | -0.40716 | 4.6134 | 4.1779 | 10.8979 | 21.1816 | 2.4037 | -46.6221 | 0 | 0 | 0 | 0 | 0
349 | 22 | 0 | 0 |  | -0.40716 | 4.6134 | 4.1779 | 10.8979 | 22.1816 | 2.6655 | -54.0696 | 0 | 0 | 0 | 0 | 0
349 | 23 | 0 | 0 |  | -0.40716 | 4.6134 | 4.1779 | 10.8979 | 23.1816 | 2.9273 | -59.1933 | 0 | 0 | 0 | 0 | 0
349 | 24 | 0 | 0 |  | -0.40716 | 4.6134 | 4.1779 | 10.8979 | 24.1816 | 3.1891 | -60.5749 | 0 | 0 | 0 | 0 | 0
350 | 1 | 0 | 0 |  | -0.40783 | 4.6306 | 3.7169 | 10.4369 | 1.1739 | -2.8343 | -57.7663 | 0 | 0 | 0 | 0 | 0
350 | 2 | 0 | 0 |  | -0.40783 | 4.6306 | 3.7169 | 10.4369 | 2.1739 | -2.5725 | -51.6493 | 0 | 0 | 0 | 0 | 0
350 | 3 | 0 | 0 |  | -0.40783 | 4.6306 | 3.7169 | 10.4369 | 3.1739 | -2.3107 | -43.6798 | 0 | 0 | 0 | 0 | 0
350 | 4 | 0 | 0 |  | -0.40783 | 4.6306 | 3.7169 | 10.4369 | 4.1739 | -2.0489 | -34.8519 | 0 | 0 | 0 | 0 | 0
350 | 5 | 0 | 0 |  | -0.40783 | 4.6306 | 3.7169 | 10.4369 | 5.1739 | -1.7871 | -25.775 | 0 | 0 | 0 | 0 | 0
350 | 6 | 0 | 0 |  | -0.40783 | 4.6306 | 3.7169 | 10.4369 | 6.1739 | -1.5253 | -16.8627 | 0 | 0 | 0 | 0 | 0
350 | 7 | 0 | 0 |  | -0.40783 | 4.6306 | 3.7169 | 10.4369 | 7.1739 | -1.2635 | -8.456 | 0 | 0 | 0 | 0 | 0
350 | 8 | 0 | 0 |  | -0.40783 | 4.6306 | 3.7169 | 10.4369 | 8.1739 | -1.0017 | -0.88765 | 0 | 0 | 0 | 0 | 0
350 | 9 | 0 | 11 |  | -0.40783 | 4.6306 | 3.7169 | 10.4369 | 9.1739 | -0.73986 | 5.4873 | 0 | 9.1667 | 9.1667 | 14.553 | 0
350 | 10 | 0 | 46 |  | -0.40783 | 4.6306 | 3.7169 | 10.4369 | 10.1739 | -0.47806 | 10.2959 | 0 | 38.3333 | 38.3333 | 60.858 | 0
350 | 11 | 7 | 80 |  | -0.40783 | 4.6306 | 3.7169 | 10.4369 | 11.1739 | -0.21626 | 13.1889 | 4.7204 | 66.6667 | 71.387 | 113.3341 | 1
350 | 12 | 17 | 95 |  | -0.40783 | 4.6306 | 3.7169 | 10.4369 | 12.1739 | 0.04554 | 13.9189 | 11.7842 | 79.1667 | 90.9509 | 144.3936 | 1
350 | 13 | 15 | 91 |  | -0.40783 | 4.6306 | 3.7169 | 10.4369 | 13.1739 | 0.30734 | 12.4183 | 9.8157 | 75.8333 | 85.649 | 135.9764 | 0
350 | 14 | 5 | 69 |  | -0.40783 | 4.6306 | 3.7169 | 10.4369 | 14.1739 | 0.56914 | 8.8238 | 2.8028 | 57.5 | 60.3028 | 95.7367 | 0
350 | 15 | 31 | 42 |  | -0.40783 | 4.6306 | 3.7169 | 10.4369 | 15.1739 | 0.83094 | 3.4281 | 12.9612 | 35 | 47.9612 | 76.1431 | 0
350 | 16 | 0 | 7 |  | -0.40783 | 4.6306 | 3.7169 | 10.4369 | 16.1739 | 1.0927 | -3.4039 | 0 | 5.8333 | 5.8333 | 9.261 | 0
350 | 17 | 0 | 0 |  | -0.40783 | 4.6306 | 3.7169 | 10.4369 | 17.1739 | 1.3545 | -11.3028 | 0 | 0 | 0 | 0 | 0
350 | 18 | 0 | 0 |  | -0.40783 | 4.6306 | 3.7169 | 10.4369 | 18.1739 | 1.6163 | -19.9227 | 0 | 0 | 0 | 0 | 0
350 | 19 | 0 | 0 |  | -0.40783 | 4.6306 | 3.7169 | 10.4369 | 19.1739 | 1.8781 | -28.9328 | 0 | 0 | 0 | 0 | 0
350 | 20 | 0 | 0 |  | -0.40783 | 4.6306 | 3.7169 | 10.4369 | 20.1739 | 2.1399 | -37.9766 | 0 | 0 | 0 | 0 | 0
350 | 21 | 0 | 0 |  | -0.40783 | 4.6306 | 3.7169 | 10.4369 | 21.1739 | 2.4017 | -46.5903 | 0 | 0 | 0 | 0 | 0
350 | 22 | 0 | 0 |  | -0.40783 | 4.6306 | 3.7169 | 10.4369 | 22.1739 | 2.6635 | -54.0533 | 0 | 0 | 0 | 0 | 0
350 | 23 | 0 | 0 |  | -0.40783 | 4.6306 | 3.7169 | 10.4369 | 23.1739 | 2.9253 | -59.2039 | 0 | 0 | 0 | 0 | 0
350 | 24 | 0 | 0 |  | -0.40783 | 4.6306 | 3.7169 | 10.4369 | 24.1739 | 3.1871 | -60.6195 | 0 | 0 | 0 | 0 | 0
351 | 1 | 0 | 0 |  | -0.40838 | 4.6478 | 3.2534 | 9.9734 | 1.1662 | -2.8363 | -57.8322 | 0 | 0 | 0 | 0 | 0
351 | 2 | 0 | 0 |  | -0.40838 | 4.6478 | 3.2534 | 9.9734 | 2.1662 | -2.5745 | -51.7319 | 0 | 0 | 0 | 0 | 0
351 | 3 | 0 | 0 |  | -0.40838 | 4.6478 | 3.2534 | 9.9734 | 3.1662 | -2.3127 | -43.7702 | 0 | 0 | 0 | 0 | 0
351 | 4 | 0 | 0 |  | -0.40838 | 4.6478 | 3.2534 | 9.9734 | 4.1662 | -2.0509 | -34.9453 | 0 | 0 | 0 | 0 | 0
351 | 5 | 0 | 0 |  | -0.40838 | 4.6478 | 3.2534 | 9.9734 | 5.1662 | -1.7891 | -25.8685 | 0 | 0 | 0 | 0 | 0
351 | 6 | 0 | 0 |  | -0.40838 | 4.6478 | 3.2534 | 9.9734 | 6.1662 | -1.5273 | -16.9543 | 0 | 0 | 0 | 0 | 0
351 | 7 | 0 | 0 |  | -0.40838 | 4.6478 | 3.2534 | 9.9734 | 7.1662 | -1.2655 | -8.5435 | 0 | 0 | 0 | 0 | 0
351 | 8 | 0 | 0 |  | -0.40838 | 4.6478 | 3.2534 | 9.9734 | 8.1662 | -1.0037 | -0.96889 | 0 | 0 | 0 | 0 | 0
351 | 9 | 0 | 16 |  | -0.40838 | 4.6478 | 3.2534 | 9.9734 | 9.1662 | -0.74188 | 5.4151 | 0 | 13.3333 | 13.3333 | 21.168 | 0
351 | 10 | 0 | 45 |  | -0.40838 | 4.6478 | 3.2534 | 9.9734 | 10.1662 | -0.48008 | 10.2357 | 0 | 37.5 | 37.5 | 59.535 | 0
351 | 11 | 7 | 79 |  | -0.40838 | 4.6478 | 3.2534 | 9.9734 | 11.1662 | -0.21828 | 13.1437 | 4.7151 | 65.8333 | 70.5484 | 112.0026 | 1
351 | 12 | 17 | 95 |  | -0.40838 | 4.6478 | 3.2534 | 9.9734 | 12.1662 | 0.043517 | 13.8907 | 11.7789 | 79.1667 | 90.9455 | 144.3851 | 1
351 | 13 | 183 | 98 |  | -0.40838 | 4.6478 | 3.2534 | 9.9734 | 13.1662 | 0.30532 | 12.4075 | 119.7758 | 81.6667 | 201.4425 | 319.8101 | 0
351 | 14 | 170 | 71 |  | -0.40838 | 4.6478 | 3.2534 | 9.9734 | 14.1662 | 0.56712 | 8.8294 | 95.3891 | 59.1667 | 154.5558 | 245.3727 | 0
351 | 15 | 0 | 30 |  | -0.40838 | 4.6478 | 3.2534 | 9.9734 | 15.1662 | 0.82892 | 3.4478 | 0 | 25 | 25 | 39.69 | 0
351 | 16 | 0 | 2 |  | -0.40838 | 4.6478 | 3.2534 | 9.9734 | 16.1662 | 1.0907 | -3.3729 | 0 | 1.6667 | 1.6667 | 2.646 | 0
351 | 17 | 0 | 0 |  | -0.40838 | 4.6478 | 3.2534 | 9.9734 | 17.1662 | 1.3525 | -11.2635 | 0 | 0 | 0 | 0 | 0
351 | 18 | 0 | 0 |  | -0.40838 | 4.6478 | 3.2534 | 9.9734 | 18.1662 | 1.6143 | -19.8781 | 0 | 0 | 0 | 0 | 0
351 | 19 | 0 | 0 |  | -0.40838 | 4.6478 | 3.2534 | 9.9734 | 19.1662 | 1.8761 | -28.886 | 0 | 0 | 0 | 0 | 0
351 | 20 | 0 | 0 |  | -0.40838 | 4.6478 | 3.2534 | 9.9734 | 20.1662 | 2.1379 | -37.9315 | 0 | 0 | 0 | 0 | 0
351 | 21 | 0 | 0 |  | -0.40838 | 4.6478 | 3.2534 | 9.9734 | 21.1662 | 2.3997 | -46.5521 | 0 | 0 | 0 | 0 | 0
351 | 22 | 0 | 0 |  | -0.40838 | 4.6478 | 3.2534 | 9.9734 | 22.1662 | 2.6615 | -54.0302 | 0 | 0 | 0 | 0 | 0
351 | 23 | 0 | 0 |  | -0.40838 | 4.6478 | 3.2534 | 9.9734 | 23.1662 | 2.9233 | -59.2069 | 0 | 0 | 0 | 0 | 0
351 | 24 | 0 | 0 |  | -0.40838 | 4.6478 | 3.2534 | 9.9734 | 24.1662 | 3.1851 | -60.6566 | 0 | 0 | 0 | 0 | 0
352 | 1 | 0 | 0 |  | -0.40879 | 4.665 | 2.7877 | 9.5077 | 1.1585 | -2.8383 | -57.8911 | 0 | 0 | 0 | 0 | 0
352 | 2 | 0 | 0 |  | -0.40879 | 4.665 | 2.7877 | 9.5077 | 2.1585 | -2.5765 | -51.8084 | 0 | 0 | 0 | 0 | 0
352 | 3 | 0 | 0 |  | -0.40879 | 4.665 | 2.7877 | 9.5077 | 3.1585 | -2.3147 | -43.8551 | 0 | 0 | 0 | 0 | 0
352 | 4 | 0 | 0 |  | -0.40879 | 4.665 | 2.7877 | 9.5077 | 4.1585 | -2.0529 | -35.0334 | 0 | 0 | 0 | 0 | 0
352 | 5 | 0 | 0 |  | -0.40879 | 4.665 | 2.7877 | 9.5077 | 5.1585 | -1.7911 | -25.9568 | 0 | 0 | 0 | 0 | 0
352 | 6 | 0 | 0 |  | -0.40879 | 4.665 | 2.7877 | 9.5077 | 6.1585 | -1.5293 | -17.0405 | 0 | 0 | 0 | 0 | 0
352 | 7 | 0 | 0 |  | -0.40879 | 4.665 | 2.7877 | 9.5077 | 7.1585 | -1.2675 | -8.6254 | 0 | 0 | 0 | 0 | 0
352 | 8 | 0 | 0 |  | -0.40879 | 4.665 | 2.7877 | 9.5077 | 8.1585 | -1.0057 | -1.0441 | 0 | 0 | 0 | 0 | 0
352 | 9 | 0 | 10 |  | -0.40879 | 4.665 | 2.7877 | 9.5077 | 9.1585 | -0.74391 | 5.3493 | 0 | 8.3333 | 8.3333 | 13.23 | 0
352 | 10 | 0 | 44 |  | -0.40879 | 4.665 | 2.7877 | 9.5077 | 10.1585 | -0.48211 | 10.1823 | 0 | 36.6667 | 36.6667 | 58.212 | 0
352 | 11 | 6 | 78 |  | -0.40879 | 4.665 | 2.7877 | 9.5077 | 11.1585 | -0.22031 | 13.1055 | 4.0375 | 65 | 69.0375 | 109.6039 | 1
352 | 12 | 0 | 61 |  | -0.40879 | 4.665 | 2.7877 | 9.5077 | 12.1585 | 0.041485 | 13.8696 | 0 | 50.8333 | 50.8333 | 80.703 | 1
352 | 13 | 0 | 58 |  | -0.40879 | 4.665 | 2.7877 | 9.5077 | 13.1585 | 0.30328 | 12.4039 | 0 | 48.3333 | 48.3333 | 76.734 | 0
352 | 14 | 0 | 43 |  | -0.40879 | 4.665 | 2.7877 | 9.5077 | 14.1585 | 0.56508 | 8.842 | 0 | 35.8333 | 35.8333 | 56.889 | 0
352 | 15 | 0 | 19 |  | -0.40879 | 4.665 | 2.7877 | 9.5077 | 15.1585 | 0.82688 | 3.4742 | 0 | 15.8333 | 15.8333 | 25.137 | 0
352 | 16 | 0 | 2 |  | -0.40879 | 4.665 | 2.7877 | 9.5077 | 16.1585 | 1.0887 | -3.3356 | 0 | 1.6667 | 1.6667 | 2.646 | 0
352 | 17 | 0 | 0 |  | -0.40879 | 4.665 | 2.7877 | 9.5077 | 17.1585 | 1.3505 | -11.2181 | 0 | 0 | 0 | 0 | 0
352 | 18 | 0 | 0 |  | -0.40879 | 4.665 | 2.7877 | 9.5077 | 18.1585 | 1.6123 | -19.8276 | 0 | 0 | 0 | 0 | 0
352 | 19 | 0 | 0 |  | -0.40879 | 4.665 | 2.7877 | 9.5077 | 19.1585 | 1.8741 | -28.8334 | 0 | 0 | 0 | 0 | 0
352 | 20 | 0 | 0 |  | -0.40879 | 4.665 | 2.7877 | 9.5077 | 20.1585 | 2.1359 | -37.8804 | 0 | 0 | 0 | 0 | 0
352 | 21 | 0 | 0 |  | -0.40879 | 4.665 | 2.7877 | 9.5077 | 21.1585 | 2.3977 | -46.5076 | 0 | 0 | 0 | 0 | 0
352 | 22 | 0 | 0 |  | -0.40879 | 4.665 | 2.7877 | 9.5077 | 22.1585 | 2.6595 | -54.0002 | 0 | 0 | 0 | 0 | 0
352 | 23 | 0 | 0 |  | -0.40879 | 4.665 | 2.7877 | 9.5077 | 23.1585 | 2.9213 | -59.2025 | 0 | 0 | 0 | 0 | 0
352 | 24 | 0 | 0 |  | -0.40879 | 4.665 | 2.7877 | 9.5077 | 24.1585 | 3.1831 | -60.6861 | 0 | 0 | 0 | 0 | 0
353 | 1 | 0 | 0 |  | -0.40908 | 4.6823 | 2.3204 | 9.0404 | 1.1507 | -2.8403 | -57.9431 | 0 | 0 | 0 | 0 | 0
353 | 2 | 0 | 0 |  | -0.40908 | 4.6823 | 2.3204 | 9.0404 | 2.1507 | -2.5785 | -51.8787 | 0 | 0 | 0 | 0 | 0
353 | 3 | 0 | 0 |  | -0.40908 | 4.6823 | 2.3204 | 9.0404 | 3.1507 | -2.3167 | -43.9344 | 0 | 0 | 0 | 0 | 0
353 | 4 | 0 | 0 |  | -0.40908 | 4.6823 | 2.3204 | 9.0404 | 4.1507 | -2.0549 | -35.1162 | 0 | 0 | 0 | 0 | 0
353 | 5 | 0 | 0 |  | -0.40908 | 4.6823 | 2.3204 | 9.0404 | 5.1507 | -1.7931 | -26.0398 | 0 | 0 | 0 | 0 | 0
353 | 6 | 0 | 0 |  | -0.40908 | 4.6823 | 2.3204 | 9.0404 | 6.1507 | -1.5314 | -17.1212 | 0 | 0 | 0 | 0 | 0
353 | 7 | 0 | 0 |  | -0.40908 | 4.6823 | 2.3204 | 9.0404 | 7.1507 | -1.2696 | -8.7016 | 0 | 0 | 0 | 0 | 0
353 | 8 | 0 | 0 |  | -0.40908 | 4.6823 | 2.3204 | 9.0404 | 8.1507 | -1.0078 | -1.1133 | 0 | 0 | 0 | 0 | 0
353 | 9 | 0 | 10 |  | -0.40908 | 4.6823 | 2.3204 | 9.0404 | 9.1507 | -0.74595 | 5.29 | 0 | 8.3333 | 8.3333 | 13.23 | 0
353 | 10 | 0 | 44 |  | -0.40908 | 4.6823 | 2.3204 | 9.0404 | 10.1507 | -0.48415 | 10.1358 | 0 | 36.6667 | 36.6667 | 58.212 | 0
353 | 11 | 5 | 77 |  | -0.40908 | 4.6823 | 2.3204 | 9.0404 | 11.1507 | -0.22235 | 13.0744 | 3.3616 | 64.1667 | 67.5283 | 107.2079 | 1
353 | 12 | 15 | 93 |  | -0.40908 | 4.6823 | 2.3204 | 9.0404 | 12.1507 | 0.039446 | 13.8557 | 10.3876 | 77.5 | 87.8876 | 139.5304 | 1
353 | 13 | 14 | 90 |  | -0.40908 | 4.6823 | 2.3204 | 9.0404 | 13.1507 | 0.30125 | 12.4074 | 9.1706 | 75 | 84.1706 | 133.6293 | 0
353 | 14 | 69 | 75 |  | -0.40908 | 4.6823 | 2.3204 | 9.0404 | 14.1507 | 0.56305 | 8.8615 | 38.8118 | 62.5 | 101.3118 | 160.8425 | 0
353 | 15 | 6 | 39 |  | -0.40908 | 4.6823 | 2.3204 | 9.0404 | 15.1507 | 0.82484 | 3.5072 | 2.5269 | 32.5 | 35.0269 | 55.6087 | 0
353 | 16 | 0 | 5 |  | -0.40908 | 4.6823 | 2.3204 | 9.0404 | 16.1507 | 1.0866 | -3.2919 | 0 | 4.1667 | 4.1667 | 6.615 | 0
353 | 17 | 0 | 0 |  | -0.40908 | 4.6823 | 2.3204 | 9.0404 | 17.1507 | 1.3484 | -11.1667 | 0 | 0 | 0 | 0 | 0
353 | 18 | 0 | 0 |  | -0.40908 | 4.6823 | 2.3204 | 9.0404 | 18.1507 | 1.6102 | -19.7712 | 0 | 0 | 0 | 0 | 0
353 | 19 | 0 | 0 |  | -0.40908 | 4.6823 | 2.3204 | 9.0404 | 19.1507 | 1.872 | -28.775 | 0 | 0 | 0 | 0 | 0
353 | 20 | 0 | 0 |  | -0.40908 | 4.6823 | 2.3204 | 9.0404 | 20.1507 | 2.1338 | -37.8235 | 0 | 0 | 0 | 0 | 0
353 | 21 | 0 | 0 |  | -0.40908 | 4.6823 | 2.3204 | 9.0404 | 21.1507 | 2.3956 | -46.4569 | 0 | 0 | 0 | 0 | 0
353 | 22 | 0 | 0 |  | -0.40908 | 4.6823 | 2.3204 | 9.0404 | 22.1507 | 2.6574 | -53.9634 | 0 | 0 | 0 | 0 | 0
353 | 23 | 0 | 0 |  | -0.40908 | 4.6823 | 2.3204 | 9.0404 | 23.1507 | 2.9192 | -59.1907 | 0 | 0 | 0 | 0 | 0
353 | 24 | 0 | 0 |  | -0.40908 | 4.6823 | 2.3204 | 9.0404 | 24.1507 | 3.181 | -60.708 | 0 | 0 | 0 | 0 | 0
354 | 1 | 0 | 0 |  | -0.40924 | 4.6995 | 1.8519 | 8.5719 | 1.1429 | -2.8424 | -57.9881 | 0 | 0 | 0 | 0 | 0
354 | 2 | 0 | 0 |  | -0.40924 | 4.6995 | 1.8519 | 8.5719 | 2.1429 | -2.5806 | -51.9428 | 0 | 0 | 0 | 0 | 0
354 | 3 | 0 | 0 |  | -0.40924 | 4.6995 | 1.8519 | 8.5719 | 3.1429 | -2.3188 | -44.0081 | 0 | 0 | 0 | 0 | 0
354 | 4 | 0 | 0 |  | -0.40924 | 4.6995 | 1.8519 | 8.5719 | 4.1429 | -2.057 | -35.1936 | 0 | 0 | 0 | 0 | 0
354 | 5 | 0 | 0 |  | -0.40924 | 4.6995 | 1.8519 | 8.5719 | 5.1429 | -1.7952 | -26.1174 | 0 | 0 | 0 | 0 | 0
354 | 6 | 0 | 0 |  | -0.40924 | 4.6995 | 1.8519 | 8.5719 | 6.1429 | -1.5334 | -17.1964 | 0 | 0 | 0 | 0 | 0
354 | 7 | 0 | 0 |  | -0.40924 | 4.6995 | 1.8519 | 8.5719 | 7.1429 | -1.2716 | -8.772 | 0 | 0 | 0 | 0 | 0
354 | 8 | 0 | 0 |  | -0.40924 | 4.6995 | 1.8519 | 8.5719 | 8.1429 | -1.0098 | -1.1763 | 0 | 0 | 0 | 0 | 0
354 | 9 | 0 | 6 |  | -0.40924 | 4.6995 | 1.8519 | 8.5719 | 9.1429 | -0.748 | 5.2372 | 0 | 5 | 5 | 7.938 | 0
354 | 10 | 0 | 27 |  | -0.40924 | 4.6995 | 1.8519 | 8.5719 | 10.1429 | -0.4862 | 10.0961 | 0 | 22.5 | 22.5 | 35.721 | 0
354 | 11 | 14 | 76 |  | -0.40924 | 4.6995 | 1.8519 | 8.5719 | 11.1429 | -0.2244 | 13.0505 | 9.4056 | 63.3333 | 72.7389 | 115.4803 | 1
354 | 12 | 0 | 61 |  | -0.40924 | 4.6995 | 1.8519 | 8.5719 | 12.1429 | 0.037402 | 13.8491 | 0 | 50.8333 | 50.8333 | 80.703 | 1
354 | 13 | 0 | 59 |  | -0.40924 | 4.6995 | 1.8519 | 8.5719 | 13.1429 | 0.2992 | 12.4181 | 0 | 49.1667 | 49.1667 | 78.057 | 0
354 | 14 | 6 | 69 |  | -0.40924 | 4.6995 | 1.8519 | 8.5719 | 14.1429 | 0.561 | 8.8879 | 3.3798 | 57.5 | 60.8798 | 96.6528 | 0
354 | 15 | 0 | 19 |  | -0.40924 | 4.6995 | 1.8519 | 8.5719 | 15.1429 | 0.8228 | 3.5469 | 0 | 15.8333 | 15.8333 | 25.137 | 0
354 | 16 | 0 | 3 |  | -0.40924 | 4.6995 | 1.8519 | 8.5719 | 16.1429 | 1.0846 | -3.2419 | 0 | 2.5 | 2.5 | 3.969 | 0
354 | 17 | 0 | 0 |  | -0.40924 | 4.6995 | 1.8519 | 8.5719 | 17.1429 | 1.3464 | -11.1093 | 0 | 0 | 0 | 0 | 0
354 | 18 | 0 | 0 |  | -0.40924 | 4.6995 | 1.8519 | 8.5719 | 18.1429 | 1.6082 | -19.7091 | 0 | 0 | 0 | 0 | 0
354 | 19 | 0 | 0 |  | -0.40924 | 4.6995 | 1.8519 | 8.5719 | 19.1429 | 1.87 | -28.711 | 0 | 0 | 0 | 0 | 0
354 | 20 | 0 | 0 |  | -0.40924 | 4.6995 | 1.8519 | 8.5719 | 20.1429 | 2.1318 | -37.7607 | 0 | 0 | 0 | 0 | 0
354 | 21 | 0 | 0 |  | -0.40924 | 4.6995 | 1.8519 | 8.5719 | 21.1429 | 2.3936 | -46.4001 | 0 | 0 | 0 | 0 | 0
354 | 22 | 0 | 0 |  | -0.40924 | 4.6995 | 1.8519 | 8.5719 | 22.1429 | 2.6554 | -53.9199 | 0 | 0 | 0 | 0 | 0
354 | 23 | 0 | 0 |  | -0.40924 | 4.6995 | 1.8519 | 8.5719 | 23.1429 | 2.9172 | -59.1714 | 0 | 0 | 0 | 0 | 0
354 | 24 | 0 | 0 |  | -0.40924 | 4.6995 | 1.8519 | 8.5719 | 24.1429 | 3.179 | -60.7223 | 0 | 0 | 0 | 0 | 0
355 | 1 | 0 | 0 |  | -0.40928 | 4.7167 | 1.3826 | 8.1026 | 1.135 | -2.8444 | -58.026 | 0 | 0 | 0 | 0 | 0
355 | 2 | 0 | 0 |  | -0.40928 | 4.7167 | 1.3826 | 8.1026 | 2.135 | -2.5826 | -52.0007 | 0 | 0 | 0 | 0 | 0
355 | 3 | 0 | 0 |  | -0.40928 | 4.7167 | 1.3826 | 8.1026 | 3.135 | -2.3208 | -44.076 | 0 | 0 | 0 | 0 | 0
355 | 4 | 0 | 0 |  | -0.40928 | 4.7167 | 1.3826 | 8.1026 | 4.135 | -2.059 | -35.2656 | 0 | 0 | 0 | 0 | 0
355 | 5 | 0 | 0 |  | -0.40928 | 4.7167 | 1.3826 | 8.1026 | 5.135 | -1.7972 | -26.1897 | 0 | 0 | 0 | 0 | 0
355 | 6 | 0 | 0 |  | -0.40928 | 4.7167 | 1.3826 | 8.1026 | 6.135 | -1.5354 | -17.2661 | 0 | 0 | 0 | 0 | 0
355 | 7 | 0 | 0 |  | -0.40928 | 4.7167 | 1.3826 | 8.1026 | 7.135 | -1.2736 | -8.8366 | 0 | 0 | 0 | 0 | 0
355 | 8 | 0 | 0 |  | -0.40928 | 4.7167 | 1.3826 | 8.1026 | 8.135 | -1.0118 | -1.2332 | 0 | 0 | 0 | 0 | 0
355 | 9 | 0 | 10 |  | -0.40928 | 4.7167 | 1.3826 | 8.1026 | 9.135 | -0.75004 | 5.1909 | 0 | 8.3333 | 8.3333 | 13.23 | 0
355 | 10 | 0 | 43 |  | -0.40928 | 4.7167 | 1.3826 | 8.1026 | 10.135 | -0.48824 | 10.0633 | 0 | 35.8333 | 35.8333 | 56.889 | 0
355 | 11 | 6 | 78 |  | -0.40928 | 4.7167 | 1.3826 | 8.1026 | 11.135 | -0.22644 | 13.0337 | 4.0285 | 65 | 69.0285 | 109.5897 | 1
355 | 12 | 20 | 93 |  | -0.40928 | 4.7167 | 1.3826 | 8.1026 | 12.135 | 0.035354 | 13.8497 | 13.85 | 77.5 | 91.35 | 145.0272 | 1
355 | 13 | 19 | 90 |  | -0.40928 | 4.7167 | 1.3826 | 8.1026 | 13.135 | 0.29715 | 12.4359 | 12.4627 | 75 | 87.4627 | 138.8557 | 0
355 | 14 | 62 | 78 |  | -0.40928 | 4.7167 | 1.3826 | 8.1026 | 14.135 | 0.55895 | 8.9213 | 34.9806 | 65 | 99.9806 | 158.7293 | 0
355 | 15 | 118 | 42 |  | -0.40928 | 4.7167 | 1.3826 | 8.1026 | 15.135 | 0.82075 | 3.5931 | 49.9815 | 35 | 84.9815 | 134.9166 | 0
355 | 16 | 0 | 7 |  | -0.40928 | 4.7167 | 1.3826 | 8.1026 | 16.135 | 1.0826 | -3.1857 | 0 | 5.8333 | 5.8333 | 9.261 | 0
355 | 17 | 0 | 0 |  | -0.40928 | 4.7167 | 1.3826 | 8.1026 | 17.135 | 1.3444 | -11.046 | 0 | 0 | 0 | 0 | 0
355 | 18 | 0 | 0 |  | -0.40928 | 4.7167 | 1.3826 | 8.1026 | 18.135 | 1.6062 | -19.6413 | 0 | 0 | 0 | 0 | 0
355 | 19 | 0 | 0 |  | -0.40928 | 4.7167 | 1.3826 | 8.1026 | 19.135 | 1.868 | -28.6413 | 0 | 0 | 0 | 0 | 0
355 | 20 | 0 | 0 |  | -0.40928 | 4.7167 | 1.3826 | 8.1026 | 20.135 | 2.1297 | -37.6922 | 0 | 0 | 0 | 0 | 0
355 | 21 | 0 | 0 |  | -0.40928 | 4.7167 | 1.3826 | 8.1026 | 21.135 | 2.3915 | -46.3371 | 0 | 0 | 0 | 0 | 0
355 | 22 | 0 | 0 |  | -0.40928 | 4.7167 | 1.3826 | 8.1026 | 22.135 | 2.6533 | -53.8696 | 0 | 0 | 0 | 0 | 0
355 | 23 | 0 | 0 |  | -0.40928 | 4.7167 | 1.3826 | 8.1026 | 23.135 | 2.9151 | -59.1447 | 0 | 0 | 0 | 0 | 0
355 | 24 | 0 | 0 |  | -0.40928 | 4.7167 | 1.3826 | 8.1026 | 24.135 | 3.1769 | -60.729 | 0 | 0 | 0 | 0 | 0
356 | 1 | 0 | 0 |  | -0.40918 | 4.7339 | 0.91301 | 7.633 | 1.1272 | -2.8465 | -58.0568 | 0 | 0 | 0 | 0 | 0
356 | 2 | 0 | 0 |  | -0.40918 | 4.7339 | 0.91301 | 7.633 | 2.1272 | -2.5847 | -52.0521 | 0 | 0 | 0 | 0 | 0
356 | 3 | 0 | 0 |  | -0.40918 | 4.7339 | 0.91301 | 7.633 | 3.1272 | -2.3229 | -44.1381 | 0 | 0 | 0 | 0 | 0
356 | 4 | 0 | 0 |  | -0.40918 | 4.7339 | 0.91301 | 7.633 | 4.1272 | -2.0611 | -35.3321 | 0 | 0 | 0 | 0 | 0
356 | 5 | 0 | 0 |  | -0.40918 | 4.7339 | 0.91301 | 7.633 | 5.1272 | -1.7993 | -26.2564 | 0 | 0 | 0 | 0 | 0
356 | 6 | 0 | 0 |  | -0.40918 | 4.7339 | 0.91301 | 7.633 | 6.1272 | -1.5375 | -17.3302 | 0 | 0 | 0 | 0 | 0
356 | 7 | 0 | 0 |  | -0.40918 | 4.7339 | 0.91301 | 7.633 | 7.1272 | -1.2757 | -8.8953 | 0 | 0 | 0 | 0 | 0
356 | 8 | 0 | 0 |  | -0.40918 | 4.7339 | 0.91301 | 7.633 | 8.1272 | -1.0139 | -1.2839 | 0 | 0 | 0 | 0 | 0
356 | 9 | 0 | 9 |  | -0.40918 | 4.7339 | 0.91301 | 7.633 | 9.1272 | -0.75209 | 5.1512 | 0 | 7.5 | 7.5 | 11.907 | 0
356 | 10 | 0 | 27 |  | -0.40918 | 4.7339 | 0.91301 | 7.633 | 10.1272 | -0.49029 | 10.0375 | 0 | 22.5 | 22.5 | 35.721 | 0
356 | 11 | 0 | 49 |  | -0.40918 | 4.7339 | 0.91301 | 7.633 | 11.1272 | -0.22849 | 13.0241 | 0 | 40.8333 | 40.8333 | 64.827 | 1
356 | 12 | 0 | 61 |  | -0.40918 | 4.7339 | 0.91301 | 7.633 | 12.1272 | 0.033305 | 13.8575 | 0 | 50.8333 | 50.8333 | 80.703 | 1
356 | 13 | 0 | 59 |  | -0.40918 | 4.7339 | 0.91301 | 7.633 | 13.1272 | 0.2951 | 12.4609 | 0 | 49.1667 | 49.1667 | 78.057 | 0
356 | 14 | 0 | 44 |  | -0.40918 | 4.7339 | 0.91301 | 7.633 | 14.1272 | 0.5569 | 8.9615 | 0 | 36.6667 | 36.6667 | 58.212 | 0
356 | 15 | 0 | 31 |  | -0.40918 | 4.7339 | 0.91301 | 7.633 | 15.1272 | 0.8187 | 3.6459 | 0 | 25.8333 | 25.8333 | 41.013 | 0
356 | 16 | 0 | 4 |  | -0.40918 | 4.7339 | 0.91301 | 7.633 | 16.1272 | 1.0805 | -3.1234 | 0 | 3.3333 | 3.3333 | 5.292 | 0
356 | 17 | 0 | 0 |  | -0.40918 | 4.7339 | 0.91301 | 7.633 | 17.1272 | 1.3423 | -10.9768 | 0 | 0 | 0 | 0 | 0
356 | 18 | 0 | 0 |  | -0.40918 | 4.7339 | 0.91301 | 7.633 | 18.1272 | 1.6041 | -19.5678 | 0 | 0 | 0 | 0 | 0
356 | 19 | 0 | 0 |  | -0.40918 | 4.7339 | 0.91301 | 7.633 | 19.1272 | 1.8659 | -28.566 | 0 | 0 | 0 | 0 | 0
356 | 20 | 0 | 0 |  | -0.40918 | 4.7339 | 0.91301 | 7.633 | 20.1272 | 2.1277 | -37.618 | 0 | 0 | 0 | 0 | 0
356 | 21 | 0 | 0 |  | -0.40918 | 4.7339 | 0.91301 | 7.633 | 21.1272 | 2.3895 | -46.2682 | 0 | 0 | 0 | 0 | 0
356 | 22 | 0 | 0 |  | -0.40918 | 4.7339 | 0.91301 | 7.633 | 22.1272 | 2.6513 | -53.8128 | 0 | 0 | 0 | 0 | 0
356 | 23 | 0 | 0 |  | -0.40918 | 4.7339 | 0.91301 | 7.633 | 23.1272 | 2.9131 | -59.1107 | 0 | 0 | 0 | 0 | 0
356 | 24 | 0 | 0 |  | -0.40918 | 4.7339 | 0.91301 | 7.633 | 24.1272 | 3.1749 | -60.7281 | 0 | 0 | 0 | 0 | 0
357 | 1 | 0 | 0 |  | -0.40895 | 4.7511 | 0.44349 | 7.1635 | 1.1194 | -2.8485 | -58.0804 | 0 | 0 | 0 | 0 | 0
357 | 2 | 0 | 0 |  | -0.40895 | 4.7511 | 0.44349 | 7.1635 | 2.1194 | -2.5867 | -52.0972 | 0 | 0 | 0 | 0 | 0
357 | 3 | 0 | 0 |  | -0.40895 | 4.7511 | 0.44349 | 7.1635 | 3.1194 | -2.3249 | -44.1944 | 0 | 0 | 0 | 0 | 0
357 | 4 | 0 | 0 |  | -0.40895 | 4.7511 | 0.44349 | 7.1635 | 4.1194 | -2.0631 | -35.3929 | 0 | 0 | 0 | 0 | 0
357 | 5 | 0 | 0 |  | -0.40895 | 4.7511 | 0.44349 | 7.1635 | 5.1194 | -1.8013 | -26.3177 | 0 | 0 | 0 | 0 | 0
357 | 6 | 0 | 0 |  | -0.40895 | 4.7511 | 0.44349 | 7.1635 | 6.1194 | -1.5395 | -17.3886 | 0 | 0 | 0 | 0 | 0
357 | 7 | 0 | 0 |  | -0.40895 | 4.7511 | 0.44349 | 7.1635 | 7.1194 | -1.2777 | -8.9482 | 0 | 0 | 0 | 0 | 0
357 | 8 | 0 | 0 |  | -0.40895 | 4.7511 | 0.44349 | 7.1635 | 8.1194 | -1.0159 | -1.3283 | 0 | 0 | 0 | 0 | 0
357 | 9 | 0 | 9 |  | -0.40895 | 4.7511 | 0.44349 | 7.1635 | 9.1194 | -0.75414 | 5.118 | 0 | 7.5 | 7.5 | 11.907 | 0
357 | 10 | 0 | 43 |  | -0.40895 | 4.7511 | 0.44349 | 7.1635 | 10.1194 | -0.49234 | 10.0185 | 0 | 35.8333 | 35.8333 | 56.889 | 0
357 | 11 | 85 | 84 |  | -0.40895 | 4.7511 | 0.44349 | 7.1635 | 11.1194 | -0.23054 | 13.0216 | 57.0231 | 70 | 127.0231 | 201.6619 | 1
357 | 12 | 238 | 89 |  | -0.40895 | 4.7511 | 0.44349 | 7.1635 | 12.1194 | 0.031257 | 13.8726 | 164.8972 | 74.1667 | 239.0639 | 379.5378 | 1
357 | 13 | 24 | 89 |  | -0.40895 | 4.7511 | 0.44349 | 7.1635 | 13.1194 | 0.29306 | 12.4929 | 15.772 | 74.1667 | 89.9386 | 142.7866 | 0
357 | 14 | 175 | 72 |  | -0.40895 | 4.7511 | 0.44349 | 7.1635 | 14.1194 | 0.55486 | 9.0085 | 99.094 | 60 | 159.094 | 252.5776 | 0
357 | 15 | 0 | 32 |  | -0.40895 | 4.7511 | 0.44349 | 7.1635 | 15.1194 | 0.81665 | 3.7052 | 0 | 26.6667 | 26.6667 | 42.336 | 0
357 | 16 | 0 | 4 |  | -0.40895 | 4.7511 | 0.44349 | 7.1635 | 16.1194 | 1.0785 | -3.0548 | 0 | 3.3333 | 3.3333 | 5.292 | 0
357 | 17 | 0 | 0 |  | -0.40895 | 4.7511 | 0.44349 | 7.1635 | 17.1194 | 1.3403 | -10.9017 | 0 | 0 | 0 | 0 | 0
357 | 18 | 0 | 0 |  | -0.40895 | 4.7511 | 0.44349 | 7.1635 | 18.1194 | 1.6021 | -19.4887 | 0 | 0 | 0 | 0 | 0
357 | 19 | 0 | 0 |  | -0.40895 | 4.7511 | 0.44349 | 7.1635 | 19.1194 | 1.8639 | -28.4852 | 0 | 0 | 0 | 0 | 0
357 | 20 | 0 | 0 |  | -0.40895 | 4.7511 | 0.44349 | 7.1635 | 20.1194 | 2.1257 | -37.5383 | 0 | 0 | 0 | 0 | 0
357 | 21 | 0 | 0 |  | -0.40895 | 4.7511 | 0.44349 | 7.1635 | 21.1194 | 2.3875 | -46.1934 | 0 | 0 | 0 | 0 | 0
357 | 22 | 0 | 0 |  | -0.40895 | 4.7511 | 0.44349 | 7.1635 | 22.1194 | 2.6493 | -53.7494 | 0 | 0 | 0 | 0 | 0
357 | 23 | 0 | 0 |  | -0.40895 | 4.7511 | 0.44349 | 7.1635 | 23.1194 | 2.911 | -59.0694 | 0 | 0 | 0 | 0 | 0
357 | 24 | 0 | 0 |  | -0.40895 | 4.7511 | 0.44349 | 7.1635 | 24.1194 | 3.1728 | -60.7195 | 0 | 0 | 0 | 0 | 0
358 | 1 | 0 | 0 |  | -0.4086 | 4.7683 | -0.025476 | 6.6945 | 1.1116 | -2.8506 | -58.0969 | 0 | 0 | 0 | 0 | 0
358 | 2 | 0 | 0 |  | -0.4086 | 4.7683 | -0.025476 | 6.6945 | 2.1116 | -2.5888 | -52.1357 | 0 | 0 | 0 | 0 | 0
358 | 3 | 0 | 0 |  | -0.4086 | 4.7683 | -0.025476 | 6.6945 | 3.1116 | -2.327 | -44.2447 | 0 | 0 | 0 | 0 | 0
358 | 4 | 0 | 0 |  | -0.4086 | 4.7683 | -0.025476 | 6.6945 | 4.1116 | -2.0652 | -35.4481 | 0 | 0 | 0 | 0 | 0
358 | 5 | 0 | 0 |  | -0.4086 | 4.7683 | -0.025476 | 6.6945 | 5.1116 | -1.8034 | -26.3733 | 0 | 0 | 0 | 0 | 0
358 | 6 | 0 | 0 |  | -0.4086 | 4.7683 | -0.025476 | 6.6945 | 6.1116 | -1.5416 | -17.4413 | 0 | 0 | 0 | 0 | 0
358 | 7 | 0 | 0 |  | -0.4086 | 4.7683 | -0.025476 | 6.6945 | 7.1116 | -1.2798 | -8.995 | 0 | 0 | 0 | 0 | 0
358 | 8 | 0 | 0 |  | -0.4086 | 4.7683 | -0.025476 | 6.6945 | 8.1116 | -1.018 | -1.3664 | 0 | 0 | 0 | 0 | 0
358 | 9 | 0 | 9 |  | -0.4086 | 4.7683 | -0.025476 | 6.6945 | 9.1116 | -0.75619 | 5.0915 | 0 | 7.5 | 7.5 | 11.907 | 0
358 | 10 | 0 | 27 |  | -0.4086 | 4.7683 | -0.025476 | 6.6945 | 10.1116 | -0.49439 | 10.0065 | 0 | 22.5 | 22.5 | 35.721 | 0
358 | 11 | 14 | 76 |  | -0.4086 | 4.7683 | -0.025476 | 6.6945 | 11.1116 | -0.23259 | 13.0262 | 9.39 | 63.3333 | 72.7233 | 115.4556 | 1
358 | 12 | 16 | 94 |  | -0.4086 | 4.7683 | -0.025476 | 6.6945 | 12.1116 | 0.02921 | 13.8949 | 11.0904 | 78.3333 | 89.4238 | 141.9692 | 1
358 | 13 | 16 | 91 |  | -0.4086 | 4.7683 | -0.025476 | 6.6945 | 13.1116 | 0.29101 | 12.5321 | 10.5266 | 75.8333 | 86.3599 | 137.105 | 1
358 | 14 | 6 | 69 |  | -0.4086 | 4.7683 | -0.025476 | 6.6945 | 14.1116 | 0.55281 | 9.0624 | 3.4044 | 57.5 | 60.9044 | 96.6918 | 0
358 | 15 | 0 | 20 |  | -0.4086 | 4.7683 | -0.025476 | 6.6945 | 15.1116 | 0.81461 | 3.7709 | 0 | 16.6667 | 16.6667 | 26.46 | 0
358 | 16 | 0 | 3 |  | -0.4086 | 4.7683 | -0.025476 | 6.6945 | 16.1116 | 1.0764 | -2.9802 | 0 | 2.5 | 2.5 | 3.969 | 0
358 | 17 | 0 | 0 |  | -0.4086 | 4.7683 | -0.025476 | 6.6945 | 17.1116 | 1.3382 | -10.8209 | 0 | 0 | 0 | 0 | 0
358 | 18 | 0 | 0 |  | -0.4086 | 4.7683 | -0.025476 | 6.6945 | 18.1116 | 1.6 | -19.404 | 0 | 0 | 0 | 0 | 0
358 | 19 | 0 | 0 |  | -0.4086 | 4.7683 | -0.025476 | 6.6945 | 19.1116 | 1.8618 | -28.3989 | 0 | 0 | 0 | 0 | 0
358 | 20 | 0 | 0 |  | -0.4086 | 4.7683 | -0.025476 | 6.6945 | 20.1116 | 2.1236 | -37.453 | 0 | 0 | 0 | 0 | 0
358 | 21 | 0 | 0 |  | -0.4086 | 4.7683 | -0.025476 | 6.6945 | 21.1116 | 2.3854 | -46.1126 | 0 | 0 | 0 | 0 | 0
358 | 22 | 0 | 0 |  | -0.4086 | 4.7683 | -0.025476 | 6.6945 | 22.1116 | 2.6472 | -53.6795 | 0 | 0 | 0 | 0 | 0
358 | 23 | 0 | 0 |  | -0.4086 | 4.7683 | -0.025476 | 6.6945 | 23.1116 | 2.909 | -59.0208 | 0 | 0 | 0 | 0 | 0
358 | 24 | 0 | 0 |  | -0.4086 | 4.7683 | -0.025476 | 6.6945 | 24.1116 | 3.1708 | -60.7033 | 0 | 0 | 0 | 0 | 0
359 | 1 | 0 | 0 |  | -0.40812 | 4.7855 | -0.49346 | 6.2265 | 1.1038 | -2.8526 | -58.106 | 0 | 0 | 0 | 0 | 0
359 | 2 | 0 | 0 |  | -0.40812 | 4.7855 | -0.49346 | 6.2265 | 2.1038 | -2.5908 | -52.1678 | 0 | 0 | 0 | 0 | 0
359 | 3 | 0 | 0 |  | -0.40812 | 4.7855 | -0.49346 | 6.2265 | 3.1038 | -2.329 | -44.289 | 0 | 0 | 0 | 0 | 0
359 | 4 | 0 | 0 |  | -0.40812 | 4.7855 | -0.49346 | 6.2265 | 4.1038 | -2.0672 | -35.4976 | 0 | 0 | 0 | 0 | 0
359 | 5 | 0 | 0 |  | -0.40812 | 4.7855 | -0.49346 | 6.2265 | 5.1038 | -1.8054 | -26.4232 | 0 | 0 | 0 | 0 | 0
359 | 6 | 0 | 0 |  | -0.40812 | 4.7855 | -0.49346 | 6.2265 | 6.1038 | -1.5436 | -17.4882 | 0 | 0 | 0 | 0 | 0
359 | 7 | 0 | 0 |  | -0.40812 | 4.7855 | -0.49346 | 6.2265 | 7.1038 | -1.2818 | -9.0359 | 0 | 0 | 0 | 0 | 0
359 | 8 | 0 | 0 |  | -0.40812 | 4.7855 | -0.49346 | 6.2265 | 8.1038 | -1.02 | -1.3983 | 0 | 0 | 0 | 0 | 0
359 | 9 | 0 | 9 |  | -0.40812 | 4.7855 | -0.49346 | 6.2265 | 9.1038 | -0.75823 | 5.0717 | 0 | 7.5 | 7.5 | 11.907 | 0
359 | 10 | 0 | 27 |  | -0.40812 | 4.7855 | -0.49346 | 6.2265 | 10.1038 | -0.49643 | 10.0014 | 0 | 22.5 | 22.5 | 35.721 | 0
359 | 11 | 8 | 78 |  | -0.40812 | 4.7855 | -0.49346 | 6.2265 | 11.1038 | -0.23463 | 13.0381 | 5.3652 | 65 | 70.3652 | 111.7119 | 1
359 | 12 | 21 | 93 |  | -0.40812 | 4.7855 | -0.49346 | 6.2265 | 12.1038 | 0.027168 | 13.9243 | 14.5645 | 77.5 | 92.0645 | 146.1616 | 1
359 | 13 | 16 | 92 |  | -0.40812 | 4.7855 | -0.49346 | 6.2265 | 13.1038 | 0.28897 | 12.5783 | 10.54 | 76.6667 | 87.2066 | 138.4492 | 1
359 | 14 | 7 | 70 |  | -0.40812 | 4.7855 | -0.49346 | 6.2265 | 14.1038 | 0.55077 | 9.1231 | 3.9804 | 58.3333 | 62.3137 | 98.9292 | 0
359 | 15 | 0 | 33 |  | -0.40812 | 4.7855 | -0.49346 | 6.2265 | 15.1038 | 0.81257 | 3.8431 | 0 | 27.5 | 27.5 | 43.659 | 0
359 | 16 | 0 | 6 |  | -0.40812 | 4.7855 | -0.49346 | 6.2265 | 16.1038 | 1.0744 | -2.8995 | 0 | 5 | 5 | 7.938 | 0
359 | 17 | 0 | 0 |  | -0.40812 | 4.7855 | -0.49346 | 6.2265 | 17.1038 | 1.3362 | -10.7344 | 0 | 0 | 0 | 0 | 0
359 | 18 | 0 | 0 |  | -0.40812 | 4.7855 | -0.49346 | 6.2265 | 18.1038 | 1.598 | -19.3139 | 0 | 0 | 0 | 0 | 0
359 | 19 | 0 | 0 |  | -0.40812 | 4.7855 | -0.49346 | 6.2265 | 19.1038 | 1.8598 | -28.3073 | 0 | 0 | 0 | 0 | 0
359 | 20 | 0 | 0 |  | -0.40812 | 4.7855 | -0.49346 | 6.2265 | 20.1038 | 2.1216 | -37.3622 | 0 | 0 | 0 | 0 | 0
359 | 21 | 0 | 0 |  | -0.40812 | 4.7855 | -0.49346 | 6.2265 | 21.1038 | 2.3834 | -46.0261 | 0 | 0 | 0 | 0 | 0
359 | 22 | 0 | 0 |  | -0.40812 | 4.7855 | -0.49346 | 6.2265 | 22.1038 | 2.6452 | -53.6032 | 0 | 0 | 0 | 0 | 0
359 | 23 | 0 | 0 |  | -0.40812 | 4.7855 | -0.49346 | 6.2265 | 23.1038 | 2.907 | -58.965 | 0 | 0 | 0 | 0 | 0
359 | 24 | 0 | 0 |  | -0.40812 | 4.7855 | -0.49346 | 6.2265 | 24.1038 | 3.1688 | -60.6795 | 0 | 0 | 0 | 0 | 0
360 | 1 | 0 | 0 |  | -0.40751 | 4.8028 | -0.96001 | 5.76 | 1.096 | -2.8547 | -58.1079 | 0 | 0 | 0 | 0 | 0
360 | 2 | 0 | 0 |  | -0.40751 | 4.8028 | -0.96001 | 5.76 | 2.096 | -2.5929 | -52.1932 | 0 | 0 | 0 | 0 | 0
360 | 3 | 0 | 0 |  | -0.40751 | 4.8028 | -0.96001 | 5.76 | 3.096 | -2.3311 | -44.3273 | 0 | 0 | 0 | 0 | 0
360 | 4 | 0 | 0 |  | -0.40751 | 4.8028 | -0.96001 | 5.76 | 4.096 | -2.0693 | -35.5413 | 0 | 0 | 0 | 0 | 0
360 | 5 | 0 | 0 |  | -0.40751 | 4.8028 | -0.96001 | 5.76 | 5.096 | -1.8075 | -26.4674 | 0 | 0 | 0 | 0 | 0
360 | 6 | 0 | 0 |  | -0.40751 | 4.8028 | -0.96001 | 5.76 | 6.096 | -1.5457 | -17.5293 | 0 | 0 | 0 | 0 | 0
360 | 7 | 0 | 0 |  | -0.40751 | 4.8028 | -0.96001 | 5.76 | 7.096 | -1.2839 | -9.0707 | 0 | 0 | 0 | 0 | 0
360 | 8 | 0 | 0 |  | -0.40751 | 4.8028 | -0.96001 | 5.76 | 8.096 | -1.0221 | -1.4237 | 0 | 0 | 0 | 0 | 0
360 | 9 | 0 | 12 |  | -0.40751 | 4.8028 | -0.96001 | 5.76 | 9.096 | -0.76027 | 5.0586 | 0 | 10 | 10 | 15.876 | 0
360 | 10 | 201 | 36 |  | -0.40751 | 4.8028 | -0.96001 | 5.76 | 10.096 | -0.49847 | 10.0034 | 118.8351 | 30 | 148.8351 | 236.2906 | 0
360 | 11 | 8 | 77 |  | -0.40751 | 4.8028 | -0.96001 | 5.76 | 11.096 | -0.23667 | 13.0571 | 5.3655 | 64.1667 | 69.5322 | 110.3892 | 1
360 | 12 | 91 | 105 |  | -0.40751 | 4.8028 | -0.96001 | 5.76 | 12.096 | 0.025133 | 13.961 | 63.1569 | 87.5 | 150.6569 | 239.1828 | 1
360 | 13 | 353 | 83 |  | -0.40751 | 4.8028 | -0.96001 | 5.76 | 13.096 | 0.28693 | 12.6316 | 232.8621 | 69.1667 | 302.0288 | 479.5009 | 1
360 | 14 | 6 | 71 |  | -0.40751 | 4.8028 | -0.96001 | 5.76 | 14.096 | 0.54873 | 9.1905 | 3.4196 | 59.1667 | 62.5863 | 99.3619 | 0
360 | 15 | 0 | 33 |  | -0.40751 | 4.8028 | -0.96001 | 5.76 | 15.096 | 0.81053 | 3.9216 | 0 | 27.5 | 27.5 | 43.659 | 0
360 | 16 | 0 | 5 |  | -0.40751 | 4.8028 | -0.96001 | 5.76 | 16.096 | 1.0723 | -2.8129 | 0 | 4.1667 | 4.1667 | 6.615 | 0
360 | 17 | 0 | 0 |  | -0.40751 | 4.8028 | -0.96001 | 5.76 | 17.096 | 1.3341 | -10.6422 | 0 | 0 | 0 | 0 | 0
360 | 18 | 0 | 0 |  | -0.40751 | 4.8028 | -0.96001 | 5.76 | 18.096 | 1.5959 | -19.2184 | 0 | 0 | 0 | 0 | 0
360 | 19 | 0 | 0 |  | -0.40751 | 4.8028 | -0.96001 | 5.76 | 19.096 | 1.8577 | -28.2104 | 0 | 0 | 0 | 0 | 0
360 | 20 | 0 | 0 |  | -0.40751 | 4.8028 | -0.96001 | 5.76 | 20.096 | 2.1195 | -37.2661 | 0 | 0 | 0 | 0 | 0
360 | 21 | 0 | 0 |  | -0.40751 | 4.8028 | -0.96001 | 5.76 | 21.096 | 2.3813 | -45.9339 | 0 | 0 | 0 | 0 | 0
360 | 22 | 0 | 0 |  | -0.40751 | 4.8028 | -0.96001 | 5.76 | 22.096 | 2.6431 | -53.5205 | 0 | 0 | 0 | 0 | 0
360 | 23 | 0 | 0 |  | -0.40751 | 4.8028 | -0.96001 | 5.76 | 23.096 | 2.9049 | -58.902 | 0 | 0 | 0 | 0 | 0
360 | 24 | 0 | 0 |  | -0.40751 | 4.8028 | -0.96001 | 5.76 | 24.096 | 3.1667 | -60.6481 | 0 | 0 | 0 | 0 | 0
361 | 1 | 0 | 0 |  | -0.40677 | 4.82 | -1.4247 | 5.2953 | 1.0883 | -2.8567 | -58.1025 | 0 | 0 | 0 | 0 | 0
361 | 2 | 0 | 0 |  | -0.40677 | 4.82 | -1.4247 | 5.2953 | 2.0883 | -2.5949 | -52.2119 | 0 | 0 | 0 | 0 | 0
361 | 3 | 0 | 0 |  | -0.40677 | 4.82 | -1.4247 | 5.2953 | 3.0883 | -2.3331 | -44.3594 | 0 | 0 | 0 | 0 | 0
361 | 4 | 0 | 0 |  | -0.40677 | 4.82 | -1.4247 | 5.2953 | 4.0883 | -2.0713 | -35.5791 | 0 | 0 | 0 | 0 | 0
361 | 5 | 0 | 0 |  | -0.40677 | 4.82 | -1.4247 | 5.2953 | 5.0883 | -1.8095 | -26.5058 | 0 | 0 | 0 | 0 | 0
361 | 6 | 0 | 0 |  | -0.40677 | 4.82 | -1.4247 | 5.2953 | 6.0883 | -1.5477 | -17.5645 | 0 | 0 | 0 | 0 | 0
361 | 7 | 0 | 0 |  | -0.40677 | 4.82 | -1.4247 | 5.2953 | 7.0883 | -1.2859 | -9.0994 | 0 | 0 | 0 | 0 | 0
361 | 8 | 0 | 0 |  | -0.40677 | 4.82 | -1.4247 | 5.2953 | 8.0883 | -1.0241 | -1.4428 | 0 | 0 | 0 | 0 | 0
361 | 9 | 0 | 9 |  | -0.40677 | 4.82 | -1.4247 | 5.2953 | 9.0883 | -0.76229 | 5.0521 | 0 | 7.5 | 7.5 | 11.907 | 0
361 | 10 | 0 | 42 |  | -0.40677 | 4.82 | -1.4247 | 5.2953 | 10.0883 | -0.50049 | 10.0123 | 0 | 35 | 35 | 55.566 | 0
361 | 11 | 7 | 77 |  | -0.40677 | 4.82 | -1.4247 | 5.2953 | 11.0883 | -0.23869 | 13.0832 | 4.6956 | 64.1667 | 68.8623 | 109.3258 | 1
361 | 12 | 17 | 94 |  | -0.40677 | 4.82 | -1.4247 | 5.2953 | 12.0883 | 0.023105 | 14.0049 | 11.8083 | 78.3333 | 90.1416 | 143.1088 | 1
361 | 13 | 106 | 99 |  | -0.40677 | 4.82 | -1.4247 | 5.2953 | 13.0883 | 0.2849 | 12.6918 | 70.031 | 82.5 | 152.531 | 242.1583 | 1
361 | 14 | 96 | 74 |  | -0.40677 | 4.82 | -1.4247 | 5.2953 | 14.0883 | 0.5467 | 9.2647 | 54.8464 | 61.6667 | 116.5131 | 184.9762 | 0
361 | 15 | 0 | 34 |  | -0.40677 | 4.82 | -1.4247 | 5.2953 | 15.0883 | 0.8085 | 4.0065 | 0 | 28.3333 | 28.3333 | 44.982 | 0
361 | 16 | 0 | 5 |  | -0.40677 | 4.82 | -1.4247 | 5.2953 | 16.0883 | 1.0703 | -2.7203 | 0 | 4.1667 | 4.1667 | 6.615 | 0
361 | 17 | 0 | 0 |  | -0.40677 | 4.82 | -1.4247 | 5.2953 | 17.0883 | 1.3321 | -10.5444 | 0 | 0 | 0 | 0 | 0
361 | 18 | 0 | 0 |  | -0.40677 | 4.82 | -1.4247 | 5.2953 | 18.0883 | 1.5939 | -19.1175 | 0 | 0 | 0 | 0 | 0
361 | 19 | 0 | 0 |  | -0.40677 | 4.82 | -1.4247 | 5.2953 | 19.0883 | 1.8557 | -28.1083 | 0 | 0 | 0 | 0 | 0
361 | 20 | 0 | 0 |  | -0.40677 | 4.82 | -1.4247 | 5.2953 | 20.0883 | 2.1175 | -37.1646 | 0 | 0 | 0 | 0 | 0
361 | 21 | 0 | 0 |  | -0.40677 | 4.82 | -1.4247 | 5.2953 | 21.0883 | 2.3793 | -45.836 | 0 | 0 | 0 | 0 | 0
361 | 22 | 0 | 0 |  | -0.40677 | 4.82 | -1.4247 | 5.2953 | 22.0883 | 2.6411 | -53.4316 | 0 | 0 | 0 | 0 | 0
361 | 23 | 0 | 0 |  | -0.40677 | 4.82 | -1.4247 | 5.2953 | 23.0883 | 2.9029 | -58.832 | 0 | 0 | 0 | 0 | 0
361 | 24 | 0 | 0 |  | -0.40677 | 4.82 | -1.4247 | 5.2953 | 24.0883 | 3.1647 | -60.609 | 0 | 0 | 0 | 0 | 0
362 | 1 | 0 | 0 |  | -0.40591 | 4.8372 | -1.8871 | 4.8329 | 1.0805 | -2.8587 | -58.0897 | 0 | 0 | 0 | 0 | 0
362 | 2 | 0 | 0 |  | -0.40591 | 4.8372 | -1.8871 | 4.8329 | 2.0805 | -2.5969 | -52.224 | 0 | 0 | 0 | 0 | 0
362 | 3 | 0 | 0 |  | -0.40591 | 4.8372 | -1.8871 | 4.8329 | 3.0805 | -2.3351 | -44.3853 | 0 | 0 | 0 | 0 | 0
362 | 4 | 0 | 0 |  | -0.40591 | 4.8372 | -1.8871 | 4.8329 | 4.0805 | -2.0733 | -35.6111 | 0 | 0 | 0 | 0 | 0
362 | 5 | 0 | 0 |  | -0.40591 | 4.8372 | -1.8871 | 4.8329 | 5.0805 | -1.8115 | -26.5384 | 0 | 0 | 0 | 0 | 0
362 | 6 | 0 | 0 |  | -0.40591 | 4.8372 | -1.8871 | 4.8329 | 6.0805 | -1.5497 | -17.5938 | 0 | 0 | 0 | 0 | 0
362 | 7 | 0 | 0 |  | -0.40591 | 4.8372 | -1.8871 | 4.8329 | 7.0805 | -1.2879 | -9.1219 | 0 | 0 | 0 | 0 | 0
362 | 8 | 0 | 0 |  | -0.40591 | 4.8372 | -1.8871 | 4.8329 | 8.0805 | -1.0261 | -1.4555 | 0 | 0 | 0 | 0 | 0
362 | 9 | 0 | 6 |  | -0.40591 | 4.8372 | -1.8871 | 4.8329 | 9.0805 | -0.76431 | 5.0524 | 0 | 5 | 5 | 7.938 | 0
362 | 10 | 0 | 27 |  | -0.40591 | 4.8372 | -1.8871 | 4.8329 | 10.0805 | -0.50251 | 10.0282 | 0 | 22.5 | 22.5 | 35.721 | 0
362 | 11 | 0 | 50 |  | -0.40591 | 4.8372 | -1.8871 | 4.8329 | 11.0805 | -0.24071 | 13.1165 | 0 | 41.6667 | 41.6667 | 66.15 | 1
362 | 12 | 0 | 62 |  | -0.40591 | 4.8372 | -1.8871 | 4.8329 | 12.0805 | 0.021087 | 14.0558 | 0 | 51.6667 | 51.6667 | 82.026 | 1
362 | 13 | 0 | 61 |  | -0.40591 | 4.8372 | -1.8871 | 4.8329 | 13.0805 | 0.28289 | 12.7591 | 0 | 50.8333 | 50.8333 | 80.703 | 1
362 | 14 | 0 | 46 |  | -0.40591 | 4.8372 | -1.8871 | 4.8329 | 14.0805 | 0.54469 | 9.3455 | 0 | 38.3333 | 38.3333 | 60.858 | 0
362 | 15 | 0 | 22 |  | -0.40591 | 4.8372 | -1.8871 | 4.8329 | 15.0805 | 0.80649 | 4.0976 | 0 | 18.3333 | 18.3333 | 29.106 | 0
362 | 16 | 0 | 3 |  | -0.40591 | 4.8372 | -1.8871 | 4.8329 | 16.0805 | 1.0683 | -2.6218 | 0 | 2.5 | 2.5 | 3.969 | 0
362 | 17 | 0 | 0 |  | -0.40591 | 4.8372 | -1.8871 | 4.8329 | 17.0805 | 1.3301 | -10.4412 | 0 | 0 | 0 | 0 | 0
362 | 18 | 0 | 0 |  | -0.40591 | 4.8372 | -1.8871 | 4.8329 | 18.0805 | 1.5919 | -19.0114 | 0 | 0 | 0 | 0 | 0
362 | 19 | 0 | 0 |  | -0.40591 | 4.8372 | -1.8871 | 4.8329 | 19.0805 | 1.8537 | -28.001 | 0 | 0 | 0 | 0 | 0
362 | 20 | 0 | 0 |  | -0.40591 | 4.8372 | -1.8871 | 4.8329 | 20.0805 | 2.1155 | -37.058 | 0 | 0 | 0 | 0 | 0
362 | 21 | 0 | 0 |  | -0.40591 | 4.8372 | -1.8871 | 4.8329 | 21.0805 | 2.3773 | -45.7326 | 0 | 0 | 0 | 0 | 0
362 | 22 | 0 | 0 |  | -0.40591 | 4.8372 | -1.8871 | 4.8329 | 22.0805 | 2.6391 | -53.3365 | 0 | 0 | 0 | 0 | 0
362 | 23 | 0 | 0 |  | -0.40591 | 4.8372 | -1.8871 | 4.8329 | 23.0805 | 2.9009 | -58.7549 | 0 | 0 | 0 | 0 | 0
362 | 24 | 0 | 0 |  | -0.40591 | 4.8372 | -1.8871 | 4.8329 | 24.0805 | 3.1627 | -60.5624 | 0 | 0 | 0 | 0 | 0
363 | 1 | 0 | 0 |  | -0.40492 | 4.8544 | -2.3468 | 4.3732 | 1.0729 | -2.8607 | -58.0695 | 0 | 0 | 0 | 0 | 0
363 | 2 | 0 | 0 |  | -0.40492 | 4.8544 | -2.3468 | 4.3732 | 2.0729 | -2.5989 | -52.2292 | 0 | 0 | 0 | 0 | 0
363 | 3 | 0 | 0 |  | -0.40492 | 4.8544 | -2.3468 | 4.3732 | 3.0729 | -2.3371 | -44.405 | 0 | 0 | 0 | 0 | 0
363 | 4 | 0 | 0 |  | -0.40492 | 4.8544 | -2.3468 | 4.3732 | 4.0729 | -2.0753 | -35.6371 | 0 | 0 | 0 | 0 | 0
363 | 5 | 0 | 0 |  | -0.40492 | 4.8544 | -2.3468 | 4.3732 | 5.0729 | -1.8135 | -26.5652 | 0 | 0 | 0 | 0 | 0
363 | 6 | 0 | 0 |  | -0.40492 | 4.8544 | -2.3468 | 4.3732 | 6.0729 | -1.5517 | -17.6171 | 0 | 0 | 0 | 0 | 0
363 | 7 | 0 | 0 |  | -0.40492 | 4.8544 | -2.3468 | 4.3732 | 7.0729 | -1.2899 | -9.1383 | 0 | 0 | 0 | 0 | 0
363 | 8 | 0 | 0 |  | -0.40492 | 4.8544 | -2.3468 | 4.3732 | 8.0729 | -1.0281 | -1.4618 | 0 | 0 | 0 | 0 | 0
363 | 9 | 0 | 6 |  | -0.40492 | 4.8544 | -2.3468 | 4.3732 | 9.0729 | -0.76632 | 5.0594 | 0 | 5 | 5 | 7.938 | 0
363 | 10 | 0 | 26 |  | -0.40492 | 4.8544 | -2.3468 | 4.3732 | 10.0729 | -0.50452 | 10.051 | 0 | 21.6667 | 21.6667 | 34.398 | 0
363 | 11 | 0 | 49 |  | -0.40492 | 4.8544 | -2.3468 | 4.3732 | 11.0729 | -0.24272 | 13.157 | 0 | 40.8333 | 40.8333 | 64.827 | 1
363 | 12 | 0 | 62 |  | -0.40492 | 4.8544 | -2.3468 | 4.3732 | 12.0729 | 0.019082 | 14.114 | 0 | 51.6667 | 51.6667 | 82.026 | 1
363 | 13 | 0 | 61 |  | -0.40492 | 4.8544 | -2.3468 | 4.3732 | 13.0729 | 0.28088 | 12.8333 | 0 | 50.8333 | 50.8333 | 80.703 | 1
363 | 14 | 8 | 72 |  | -0.40492 | 4.8544 | -2.3468 | 4.3732 | 14.0729 | 0.54268 | 9.4329 | 4.5946 | 60 | 64.5946 | 102.5503 | 0
363 | 15 | 0 | 35 |  | -0.40492 | 4.8544 | -2.3468 | 4.3732 | 15.0729 | 0.80448 | 4.195 | 0 | 29.1667 | 29.1667 | 46.305 | 0
363 | 16 | 0 | 10 |  | -0.40492 | 4.8544 | -2.3468 | 4.3732 | 16.0729 | 1.0663 | -2.5176 | 0 | 8.3333 | 8.3333 | 13.23 | 0
363 | 17 | 0 | 0 |  | -0.40492 | 4.8544 | -2.3468 | 4.3732 | 17.0729 | 1.3281 | -10.3324 | 0 | 0 | 0 | 0 | 0
363 | 18 | 0 | 0 |  | -0.40492 | 4.8544 | -2.3468 | 4.3732 | 18.0729 | 1.5899 | -18.9001 | 0 | 0 | 0 | 0 | 0
363 | 19 | 0 | 0 |  | -0.40492 | 4.8544 | -2.3468 | 4.3732 | 19.0729 | 1.8517 | -27.8887 | 0 | 0 | 0 | 0 | 0
363 | 20 | 0 | 0 |  | -0.40492 | 4.8544 | -2.3468 | 4.3732 | 20.0729 | 2.1135 | -36.9462 | 0 | 0 | 0 | 0 | 0
363 | 21 | 0 | 0 |  | -0.40492 | 4.8544 | -2.3468 | 4.3732 | 21.0729 | 2.3753 | -45.6237 | 0 | 0 | 0 | 0 | 0
363 | 22 | 0 | 0 |  | -0.40492 | 4.8544 | -2.3468 | 4.3732 | 22.0729 | 2.6371 | -53.2353 | 0 | 0 | 0 | 0 | 0
363 | 23 | 0 | 0 |  | -0.40492 | 4.8544 | -2.3468 | 4.3732 | 23.0729 | 2.8989 | -58.6708 | 0 | 0 | 0 | 0 | 0
363 | 24 | 0 | 0 |  | -0.40492 | 4.8544 | -2.3468 | 4.3732 | 24.0729 | 3.1607 | -60.5082 | 0 | 0 | 0 | 0 | 0
364 | 1 | 0 | 0 |  | -0.4038 | 4.8716 | -2.8033 | 3.9167 | 1.0653 | -2.8627 | -58.042 | 0 | 0 | 0 | 0 | 0
364 | 2 | 0 | 0 |  | -0.4038 | 4.8716 | -2.8033 | 3.9167 | 2.0653 | -2.6009 | -52.2277 | 0 | 0 | 0 | 0 | 0
364 | 3 | 0 | 0 |  | -0.4038 | 4.8716 | -2.8033 | 3.9167 | 3.0653 | -2.3391 | -44.4184 | 0 | 0 | 0 | 0 | 0
364 | 4 | 0 | 0 |  | -0.4038 | 4.8716 | -2.8033 | 3.9167 | 4.0653 | -2.0773 | -35.657 | 0 | 0 | 0 | 0 | 0
364 | 5 | 0 | 0 |  | -0.4038 | 4.8716 | -2.8033 | 3.9167 | 5.0653 | -1.8155 | -26.5859 | 0 | 0 | 0 | 0 | 0
364 | 6 | 0 | 0 |  | -0.4038 | 4.8716 | -2.8033 | 3.9167 | 6.0653 | -1.5537 | -17.6344 | 0 | 0 | 0 | 0 | 0
364 | 7 | 0 | 0 |  | -0.4038 | 4.8716 | -2.8033 | 3.9167 | 7.0653 | -1.2919 | -9.1486 | 0 | 0 | 0 | 0 | 0
364 | 8 | 0 | 0 |  | -0.4038 | 4.8716 | -2.8033 | 3.9167 | 8.0653 | -1.0301 | -1.4616 | 0 | 0 | 0 | 0 | 0
364 | 9 | 0 | 9 |  | -0.4038 | 4.8716 | -2.8033 | 3.9167 | 9.0653 | -0.76831 | 5.0731 | 0 | 7.5 | 7.5 | 11.907 | 0
364 | 10 | 0 | 43 |  | -0.4038 | 4.8716 | -2.8033 | 3.9167 | 10.0653 | -0.50651 | 10.0809 | 0 | 35.8333 | 35.8333 | 56.889 | 0
364 | 11 | 7 | 78 |  | -0.4038 | 4.8716 | -2.8033 | 3.9167 | 11.0653 | -0.24471 | 13.2045 | 4.7018 | 65 | 69.7018 | 110.6586 | 1
364 | 12 | 0 | 62 |  | -0.4038 | 4.8716 | -2.8033 | 3.9167 | 12.0653 | 0.01709 | 14.1792 | 0 | 51.6667 | 51.6667 | 82.026 | 1
364 | 13 | 0 | 61 |  | -0.4038 | 4.8716 | -2.8033 | 3.9167 | 13.0653 | 0.27889 | 12.9145 | 0 | 50.8333 | 50.8333 | 80.703 | 1
364 | 14 | 0 | 47 |  | -0.4038 | 4.8716 | -2.8033 | 3.9167 | 14.0653 | 0.54069 | 9.5269 | 0 | 39.1667 | 39.1667 | 62.181 | 0
364 | 15 | 0 | 22 |  | -0.4038 | 4.8716 | -2.8033 | 3.9167 | 15.0653 | 0.80249 | 4.2985 | 0 | 18.3333 | 18.3333 | 29.106 | 0
364 | 16 | 0 | 4 |  | -0.4038 | 4.8716 | -2.8033 | 3.9167 | 16.0653 | 1.0643 | -2.4076 | 0 | 3.3333 | 3.3333 | 5.292 | 0
364 | 17 | 0 | 0 |  | -0.4038 | 4.8716 | -2.8033 | 3.9167 | 17.0653 | 1.3261 | -10.2184 | 0 | 0 | 0 | 0 | 0
364 | 18 | 0 | 0 |  | -0.4038 | 4.8716 | -2.8033 | 3.9167 | 18.0653 | 1.5879 | -18.7837 | 0 | 0 | 0 | 0 | 0
364 | 19 | 0 | 0 |  | -0.4038 | 4.8716 | -2.8033 | 3.9167 | 19.0653 | 1.8497 | -27.7714 | 0 | 0 | 0 | 0 | 0
364 | 20 | 0 | 0 |  | -0.4038 | 4.8716 | -2.8033 | 3.9167 | 20.0653 | 2.1115 | -36.8293 | 0 | 0 | 0 | 0 | 0
364 | 21 | 0 | 0 |  | -0.4038 | 4.8716 | -2.8033 | 3.9167 | 21.0653 | 2.3733 | -45.5095 | 0 | 0 | 0 | 0 | 0
364 | 22 | 0 | 0 |  | -0.4038 | 4.8716 | -2.8033 | 3.9167 | 22.0653 | 2.6351 | -53.128 | 0 | 0 | 0 | 0 | 0
364 | 23 | 0 | 0 |  | -0.4038 | 4.8716 | -2.8033 | 3.9167 | 23.0653 | 2.8969 | -58.5799 | 0 | 0 | 0 | 0 | 0
364 | 24 | 0 | 0 |  | -0.4038 | 4.8716 | -2.8033 | 3.9167 | 24.0653 | 3.1587 | -60.4465 | 0 | 0 | 0 | 0 | 0
365 | 1 | 0 | 0 |  | -0.40255 | 4.8888 | -3.2562 | 3.4638 | 1.0577 | -2.8647 | -58.007 | 0 | 0 | 0 | 0 | 0
365 | 2 | 0 | 0 |  | -0.40255 | 4.8888 | -3.2562 | 3.4638 | 2.0577 | -2.6029 | -52.2193 | 0 | 0 | 0 | 0 | 0
365 | 3 | 0 | 0 |  | -0.40255 | 4.8888 | -3.2562 | 3.4638 | 3.0577 | -2.3411 | -44.4254 | 0 | 0 | 0 | 0 | 0
365 | 4 | 0 | 0 |  | -0.40255 | 4.8888 | -3.2562 | 3.4638 | 4.0577 | -2.0793 | -35.6709 | 0 | 0 | 0 | 0 | 0
365 | 5 | 0 | 0 |  | -0.40255 | 4.8888 | -3.2562 | 3.4638 | 5.0577 | -1.8175 | -26.6007 | 0 | 0 | 0 | 0 | 0
365 | 6 | 0 | 0 |  | -0.40255 | 4.8888 | -3.2562 | 3.4638 | 6.0577 | -1.5557 | -17.6457 | 0 | 0 | 0 | 0 | 0
365 | 7 | 0 | 0 |  | -0.40255 | 4.8888 | -3.2562 | 3.4638 | 7.0577 | -1.2939 | -9.1525 | 0 | 0 | 0 | 0 | 0
365 | 8 | 0 | 0 |  | -0.40255 | 4.8888 | -3.2562 | 3.4638 | 8.0577 | -1.0321 | -1.4549 | 0 | 0 | 0 | 0 | 0
365 | 9 | 0 | 15 |  | -0.40255 | 4.8888 | -3.2562 | 3.4638 | 9.0577 | -0.77028 | 5.0936 | 0 | 12.5 | 12.5 | 19.845 | 0
365 | 10 | 247 | 36 |  | -0.40255 | 4.8888 | -3.2562 | 3.4638 | 10.0577 | -0.50849 | 10.1177 | 145.8423 | 30 | 175.8423 | 279.1672 | 0
365 | 11 | 291 | 71 |  | -0.40255 | 4.8888 | -3.2562 | 3.4638 | 11.0577 | -0.24669 | 13.2592 | 195.5979 | 59.1667 | 254.7646 | 404.4642 | 1
365 | 12 | 410 | 75 |  | -0.40255 | 4.8888 | -3.2562 | 3.4638 | 12.0577 | 0.015114 | 14.2516 | 286.0816 | 62.5 | 348.5816 | 553.4082 | 1
365 | 13 | 343 | 80 |  | -0.40255 | 4.8888 | -3.2562 | 3.4638 | 13.0577 | 0.27691 | 13.0025 | 228.2722 | 66.6667 | 294.9389 | 468.2449 | 1
365 | 14 | 277 | 75 |  | -0.40255 | 4.8888 | -3.2562 | 3.4638 | 14.0577 | 0.53871 | 9.6275 | 160.0021 | 62.5 | 222.5021 | 353.2443 | 0
365 | 15 | 173 | 45 |  | -0.40255 | 4.8888 | -3.2562 | 3.4638 | 15.0577 | 0.80051 | 4.4081 | 76.1329 | 37.5 | 113.6329 | 180.4035 | 0
365 | 16 | 0 | 6 |  | -0.40255 | 4.8888 | -3.2562 | 3.4638 | 16.0577 | 1.0623 | -2.2919 | 0 | 5 | 5 | 7.938 | 0
365 | 17 | 0 | 0 |  | -0.40255 | 4.8888 | -3.2562 | 3.4638 | 17.0577 | 1.3241 | -10.099 | 0 | 0 | 0 | 0 | 0
365 | 18 | 0 | 0 |  | -0.40255 | 4.8888 | -3.2562 | 3.4638 | 18.0577 | 1.5859 | -18.6623 | 0 | 0 | 0 | 0 | 0
365 | 19 | 0 | 0 |  | -0.40255 | 4.8888 | -3.2562 | 3.4638 | 19.0577 | 1.8477 | -27.6492 | 0 | 0 | 0 | 0 | 0
365 | 20 | 0 | 0 |  | -0.40255 | 4.8888 | -3.2562 | 3.4638 | 20.0577 | 2.1095 | -36.7075 | 0 | 0 | 0 | 0 | 0
365 | 21 | 0 | 0 |  | -0.40255 | 4.8888 | -3.2562 | 3.4638 | 21.0577 | 2.3713 | -45.3899 | 0 | 0 | 0 | 0 | 0
365 | 22 | 0 | 0 |  | -0.40255 | 4.8888 | -3.2562 | 3.4638 | 22.0577 | 2.6331 | -53.0148 | 0 | 0 | 0 | 0 | 0
365 | 23 | 0 | 0 |  | -0.40255 | 4.8888 | -3.2562 | 3.4638 | 23.0577 | 2.8949 | -58.4821 | 0 | 0 | 0 | 0 | 0
365 | 24 | 0 | 0 |  | -0.40255 | 4.8888 | -3.2562 | 3.4638 | 24.0577 | 3.1567 | -60.3773 | 0 | 0 | 0 | 0 | 0