## Energy Demand
Energy Demand - Case Study, Mabie Farm Park
Month | Day in Month | Energy Required for Space Heating (kWh) |  | Energy Required for Heating Hot Water (kWh) | Total Energy Required (kWh) | Load Profile (kWh)
|  | Visitor Centor | Outdoor Toilet
January | 31 | 3852.2968 | 909.9469 | 42.8736 | 4805.1173 | 6.4585 | Operating Hours | 24 | Hrs
February | 28 | 9157.3183 | 1441.1443 | 102.08 | 10700.5426 | 15.9234
March | 31 | 8024.5412 | 1289.1898 | 181.7024 | 9495.4334 | 12.7627
April | 30 | 5780.6919 | 789.7822 | 326.1475 | 6896.6215 | 9.5786
May | 31 | 1573.3297 | 0 | 653.312 | 2226.6417 | 2.9928
June | 30 | 0 | 0 | 1539.2569 | 1539.2569 | 2.1379 |  |  |  | 3852.2968
July | 31 | 0 | 0 | 1580.1984 | 1580.1984 | 2.1239 |  |  |  | 9157.3183
August | 31 | 0 | 0 | 1265.792 | 1265.792 | 1.7013 |  |  |  | 8024.5412
September | 30 | 0 | 0 | 624.4531 | 624.4531 | 0.8673 |  |  |  | 5780.6919
October | 31 | 3951.0481 | 645.2473 | 181.7024 | 4777.9978 | 6.422 |  |  |  | 1573.3297
November | 30 | 1983.1396 | 498.749 | 41.7628 | 2523.6513 | 3.5051 |  |  |  | -383.472
December | 31 | 4170.1907 | 990.679 | 42.8736 | 5203.7433 | 6.9943 |  |  |  | -2370.1067
| sum | 38492.5563 | 6564.7384 | 6582.1546 | 51639.4493 |  |  |  |  | -2256.9673
-793.6015
3951.0481
1983.1396
4170.1907

## Boiler Sizing
Boiler Sizing | [5 empty] | Calculation Reference Sheet
[8 empty] | Month | Total Heating Energy Required (kWh) | Heating Load Profile (kW) | Maximum Energy Supplied by Boiler (kWh) | Secondary Fuel Source Demand (kWh) | Total Energy Supplied by Biomass Boiler (kWh) | Real Energy Consumed by Biomass Boiler (kWh)
Boiler capacity | 8 | kW |  |  |  | 8 | 2.64 | January | 4805.1173 | 6.4585 | 5952 | 0 | 4805.1173 | 6006.3966
Turn-down ratio | 33 | % |  |  |  | 8 | 2.64 | February | 10700.5426 | 15.9234 | 5376 | 5324.5426 | 5376 | 6720
Boiler Efficiency | 80 | % |  |  |  | 8 | 2.64 | March | 9495.4334 | 12.7627 | 5952 | 3543.4334 | 5952 | 7440
Minimum power output | 2.64 | kW |  |  |  | 8 | 2.64 | April | 6896.6215 | 9.5786 | 5760 | 1136.6215 | 5760 | 7200
[6 empty] | 8 | 2.64 | May | 2226.6417 | 2.9928 | 5952 | 0 | 2226.6417 | 2783.3021
Capital Cost* | 3280 | GBP |  |  |  | 8 | 2.64 | June | 1539.2569 | 2.1379 | 5760 | 0 | 1539.2569 | 1924.0711
[6 empty] | 8 | 2.64 | July | 1580.1984 | 2.1239 | 5952 | 0 | 1580.1984 | 1975.248
[6 empty] | 8 | 2.64 | August | 1265.792 | 1.7013 | 5952 | 0 | 1265.792 | 1582.24
Power Supply by Secondary Fuel | 10004.5975 | kWh |  |  |  | 8 | 2.64 | September | 624.4531 | 0.8673 | 5760 | 0 | 624.4531 | 780.5663
[6 empty] | 8 | 2.64 | October | 4777.9978 | 6.422 | 5952 | 0 | 4777.9978 | 5972.4972
[6 empty] | 8 | 2.64 | November | 2523.6513 | 3.5051 | 5760 | 0 | 2523.6513 | 3154.5642
[6 empty] | 8 | 2.64 | December | 5203.7433 | 6.9943 | 5952 | 0 | 5203.7433 | 6504.6791
[8 empty] | Sum | 51639.4493 | 71.4678 | 70080 | 10004.5975 | 41634.8517 | 52043.5647
*1Capital Cost / kW | 410 | GBP
64549.3116
| Total Energy Supplied by Biomass Boiler (kWh) |  | Heating Load Profile (kW) | Real Energy *Consumed by Biomass Boiler (kWh)
*caused by boiler eff.
January | 4805.1173 |  | 6.4585 | 6006.3966
February | 10700.5426 |  | 15.9234 | 6720
March | 9495.4334 |  | 12.7627 | 7440
April | 6896.6215 |  | 9.5786 | 7200
May | 2226.6417 |  | 2.9928 | 2783.3021
June | 1539.2569 |  | 2.1379 | 1924.0711
July | 1580.1984 |  | 2.1239 | 1975.248
August | 1265.792 |  | 1.7013 | 1582.24
September | 624.4531 |  | 0.8673 | 780.5663
October | 4777.9978 |  | 6.422 | 5972.4972
November | 2523.6513 |  | 3.5051 | 3154.5642
December | 5203.7433 |  | 6.9943 | 6504.6791
Sum | 51639.4493 |  |  | 52043.5647

## Fuel Data
Fuel Data***
**(include delivery)
Type | Moisture content | Ash Content % |  |  |  |  | Density kg/m3 | Calorific Value |  | Fuel Cost** GBP/tonne | Total Cost pence/kWh
|  | ≤ 0.7% | ≤ 1.5% | ≤ 3.0% | ≤ 6.0% | ≤ 10.0% |  | MJ/kg | kWh/kg
Woodchip | ≤ 20% | 0.56 | 1.2 | 2.4 | 4.8 | 8 | 325 | 15.1 | 4.2 | 45 | 1.0714
| ≤ 30% | 0.49 | 1.05 | 2.1 | 4.2 | 7 | 371 | 12.9 | 3.6 | 80 | 2.2222 | according to http://www.biomassenergycentre.org.uk/portal/page?_pageid=75,59188&_dad=portal&_schema=PORTAL
| ≤ 40% | 0.42 | 0.9 | 1.8 | 3.6 | 6 | 433 | 10.7 | 3 | 45 | 1.5
| ≤ 55% | 0.315 | 0.675 | 1.35 | 2.7 | 4.5 | 578 | 7.4 | 2.1 | 45 | 2.1429
| ≤ 65% | 0.245 | 0.525 | 1.05 | 2.1 | 3.5 | 743 | 5.2 | 1.5 | 45 | 3
Pellet | ≤ 10% | 0.6 | 1.4 | 2.7 | 5.4 |  | 778 | 17.8 | 4.9 | 130 | 2.6531
| ≤ 15% | 0.6 | 1.3 | 2.6 | 5.1 |  | 824 | 16.6 | 4.6 | 130 | 2.8261
| ≤ 20% | 0.6 | 1.2 | 2.4 | 4.8 |  | 875 | 15.5 | 4.3 | 130 | 3.0233
*** When dealing with the supplier, the specifications of the fuel properties - according to CEN/TS 14961:2005 - are given
Woodchip | [5 empty] | Pellet
M20 | Moisture Content ≤ 20% |  | Dried |  |  | M10 | Moisture Content ≤ 10%
M30 | Moisture Content ≤ 30% |  | Suitable for Storage |  |  | M15 | Moisture Content ≤ 15%
M40 | Moisture Content ≤ 40% |  | Limited for Storage |  |  | M20 | Moisture Content ≤ 20%
M55 | Moisture Content ≤ 55%
M65 | Moisture Content ≤ 65%
A0.7 | Ash Content ≤ 0.7%
A1.5 | Ash Content ≤ 1.5%
A3.0 | Ash Content ≤ 3.0%
A6.0 | Ash Content ≤ 6.0%
A10.0 | Ash Content ≤10.0%
*** Reference - Group Project, 2008, MSc Renewable Energy System and the Environment, U. of Strathclyde.

## Fuel Cost Calculation
Fuel Cost Calculation
Selected Biomass Supply* : |  | Woodchip, M30, A0.7 |  |  | * Ex. Woodchip, M20, A0.7
Calorific Value** : |  | 3.6 |  | kWh/kg | **choose your data from Fuel Data sheet
Cost** : |  |  | 2.22 | pence/kWh
Real Energy Consumed for Space heating (kWh) |  | Biomass Consumption Tonnes |  | Biomass Cost GBP
January | 6006.3966 | 1.6684 |  | 133.342
February | 6720 | 1.8667 |  | 149.184
March | 7440 | 2.0667 |  | 165.168
April | 7200 | 2 |  | 159.84
May | 2783.3021 | 0.77314 |  | 61.7893
June | 1924.0711 | 0.53446 |  | 42.7144
July | 1975.248 | 0.54868 |  | 43.8505
August | 1582.24 | 0.43951 |  | 35.1257
September | 780.5663 | 0.21682 |  | 17.3286
October | 5972.4972 | 1.659 |  | 132.5894
November | 3154.5642 | 0.87627 |  | 70.0313
December | 6504.6791 | 1.8069 |  | 144.4039
Sum | 52043.5647 | 14.4565 |  | 1155.3671

## Cost Analysis
Cost Analysis
[12 empty] | Biomass Boiler | Heat Pump
[12 empty] | GBP/y | GBP/y
[11 empty] | Capital | 3280 | 6800
| Running costs or fuel costs for current and proposed system | [9 empty] | Expected life time | 10 | 10
Efficiency
| Current Heating system | [6 empty] | Kerosine Boiler | 90 | % | Capital Expense/year | 328 | 680
| Heating System Type: | Oil fired modern energy efficient condensing combination boiler | [5 empty] | Electricity Heater | 100 | % | Annual Fuel Cost | 1551.7993 | 1538.5972
| Heating area | fuel used |  |  | Energy Consumed (kWh) | cost |  |  |  |  | total payment | 1879.7993 | 2218.5972
| Visitor center | Kerosene | 3.17 | p/kWh | 42769.507 | 1355.7934
| Out door toilets | Electricity | 10.24 | p/kWh | 6564.7384 | 672.2292 | : Electricity | according to Energy Saving Trust |  |  | kWh supply | 51639.4493 | 43161.627
| Hot Water | Kerosene | 3.17 | p/kWh | 7313.5051 | 231.8381 |  |  |  |  | cost (p/kWh) | 3.6402 | 5.1402
| Annual Fuel Cost for the system |  |  |  |  | 2259.8607
Proposed Heating system
| Heating system Type: | Biomass Boiler (woodchip) + Conventional Boiler (kerosine)
| Heating Area | fuel used |  |  | Energy Consumed (kWh) | cost |  | Efficiency |  |  | Heat Pump
| whole building + Hot water | woodchip | 2.22 | p/kWh | 52043.5647 | 1155.3671 |  | Biomass Boiler | 80 | % | capital cost |  | 6800
|  | Kerosene | 3.17 | p/kWh | 12505.7469 | 396.4322 |  | Kerosine Boiler | 80 | % | O/M costs (approx. 1% of capital costs) |  | 68
| Annual Fuel Cost for the system |  |  |  |  | 1551.7993 |  |  |  |  | Annual running costs for present system |  | 2101.0926
[11 empty] | Annual running costs for GSHP |  | 1538.5972
[11 empty] | Annual savings |  | 562.4955
[11 empty] | Annual PAYBACK |  | 494.4955
[11 empty] | Pay back time (years) |  | 13.7514
| Capital Cost: | 3280 | GBP
| O/M Cost: | 98.4 | GBP/year
(3% of Capital Cost)
| Annual fuel costs for Conventional system | 2259.8607 | GBP
| Annual fuel costs for Biomass Boiler | 1551.7993 | GBP
| Annual Savings | 708.0614 | GBP
| Annual Payback | 609.6614 | GBP
| Payback Period | 5.38 | years

## Environmental Impact
Environmental Impacts
co2 SAVINGS
Current Heating system
Heating System Type: | Oil fired modern energy efficient condensing combination boiler
Heating area | rate of CO2 emmission for fuel |  |  | Energy Consumed (kWh) | CO2 emissions (tonnes)
visitor center | kerosene | 0.24 | kgCO2/kWh | 42769.507 | 10.2647
out door toilets | Electricity | 0.43 | kgCO2/kWh | 6564.7384 | 2.8228
Hot Water | kerosene | 0.24 | kgCO2/kWh | 7313.5051 | 1.7552
Annual CO2 emissions by the system |  |  |  |  | 13.0875
Proposed Heating system
Heating system Type: | Biomass Boiler
Heating Area | rate of CO2 emmission for fuel |  |  | Energy Consumed (kWh) | CO2 emissions (tonnes)
whole building | Woodchip | 0.04 | kgCO2/kWh | 52043.5647 | 2.0817
| kerosene | 0.24 | kgCO2/kWh | 12505.7469 | 3.0014
Annual CO2 emissions by the system |  |  |  |  | 5.0831
Annual CO2 savings by proposed heating system over current system |  |  |  |  | 8.0044 | tonnes

## Refference
Source: Forestry Commission
Table2: Capital Cost for Biomass Boiler
Source: carbon trust report
http://www.esru.strath.ac.uk/EandE/Web_sites/07-08/Biomass_feasibility/functions/fboiler.html