## Visitor Centre
| U value (W/m2K) | Area (m2) |  | Volume (m3) | 706
Walls | 0.3 | 158 |  | Air Changes per hour (ach) | Summer | 5
Floor | 0.25 | 295 |  |  | Winter | 2
Windows/ Doors | 2 | 30 |  | Heating Hours per day | 24
Roof | 0.2 | 328
Heat Losses
| Days in Month | Mean Outdoor Temperature (oC) | Mean Indoor Temperature (oC) | Floor Heat Losses (kWh) | Wall Heat Losses (kWh) | Windows/Doors Heat Losses (kWh) | Roof Heat Losses (kWh) | Ventilation Heat Losses (kWh) | Total Heat Losses (kWh)
January | 31 | 4.6 | 20 | 844.998 | 543.0902 | 687.456 | 751.6186 | 5338.7833 | 8165.9461
February | 28 | 5 | 20 | 743.4 | 477.792 | 604.8 | 661.248 | 11742.192 | 14229.432
March | 31 | 5.9 | 20 | 773.667 | 497.245 | 629.424 | 688.1702 | 12220.267 | 14808.7732
April | 30 | 7.8 | 21 | 700.92 | 450.4896 | 570.24 | 623.4624 | 11071.2096 | 13416.3216
May | 31 | 10.5 | 21 | 576.135 | 370.2888 | 468.72 | 512.4672 | 9100.1988 | 11027.8098
June | 30 | 13.1 | 23 | 525.69 | 337.8672 | 427.68 | 467.5968 | 8303.4072 | 10062.2412
July | 31 | 15.1 | 23 | 433.473 | 278.5982 | 352.656 | 385.5706 | 6846.8162 | 8297.114
August | 31 | 15.3 | 23 | 422.499 | 271.5451 | 343.728 | 375.8093 | 6673.4791 | 8087.0605
September | 30 | 13.3 | 21 | 408.87 | 262.7856 | 332.64 | 363.6864 | 6458.2056 | 7826.1876
October | 31 | 10.3 | 21 | 587.109 | 377.3419 | 477.648 | 522.2285 | 9273.5359 | 11237.8633
November | 30 | 7.2 | 20 | 679.68 | 436.8384 | 552.96 | 604.5696 | 4294.2874 | 6568.3354
December | 31 | 4.7 | 20 | 839.511 | 539.5637 | 682.992 | 746.7379 | 5304.1159 | 8112.9205
| South Facing | West Facing | North Facing
Area of Windows/Doors(m2) | 17 | 4 | 9 |  | Shading Coefficient | 0.87
Cooling Load Factor | 0.45 | 0.21 | 0.58
Solar Heat Gain
|  | South Facing Windows/Doors |  | West Facing Windows/Doors |  | North Facing Windows/Doors
| Days in Month | Average Solar Heat Gain Factor (W/m2) | Solar Heat Gain (kWh) | Average Solar Heat Gain Factor (W/m2) | Solar Heat Gain (kWh) | Average Solar Heat Gain Factor (W/m2) | Solar Heat Gain (kWh) | Total Solar Heat Gain (kWh)
January | 31 | 430 | 2129.2276 | 88.3333 | 48.0282 | 96.3636 | 325.5936 | 2502.8493
February | 28 | 590 | 2638.7726 | 115 | 56.4762 | 125.4545 | 382.8648 | 3078.1137
March | 31 | 624 | 3089.8558 | 137.3333 | 74.6702 | 149.8182 | 506.2059 | 3670.7319
April | 30 | 739 | 3541.2584 | 139.8333 | 73.5769 | 152.5455 | 498.7943 | 4113.6297
May | 31 | 833 | 4124.7594 | 138.8333 | 75.4858 | 151.4545 | 511.7349 | 4711.9801
June | 30 | 824 | 3948.575 | 137.3333 | 72.2615 | 149.8182 | 489.8767 | 4510.7132
July | 31 | 809 | 4005.9188 | 134.8333 | 73.3109 | 147.0909 | 496.991 | 4576.2208
August | 31 | 795 | 3936.5951 | 132.5 | 72.0423 | 144.5455 | 488.3904 | 4497.0278
September | 30 | 763 | 3656.2655 | 127.1667 | 66.912 | 138.7273 | 453.6115 | 4176.7891
October | 31 | 650 | 3218.5998 | 108.3333 | 58.9025 | 118.1818 | 399.3129 | 3676.8152
November | 30 | 515 | 2467.8594 | 85.8333 | 45.1634 | 93.6364 | 306.1729 | 2819.1958
December | 31 | 366 | 1812.3193 | 61 | 33.1666 | 66.5455 | 224.8439 | 2070.3298
Heat Emission Per Person (W) | 100
Casual Heat Gain
| Days in Month | People/Visitors per month | Average Number of People in Building at any one time | Heat Gain from People (kWh) | Heat Gain from Electrical Equipment (kWh) | Total Casual Heat Gain (kWh)
January | 31 | 220 | 2 | 148.8 | 1662 | 1810.8
February | 28 | 600 | 15 | 294 | 1700 | 1994
March | 31 | 1100 | 25 | 542.5 | 2571 | 3113.5
April | 30 | 2143 | 30 | 630 | 2892 | 3522
May | 31 | 4400 | 45 | 976.5 | 3766 | 4742.5
June | 30 | 10715 | 60 | 1260 | 4675 | 5935
July | 31 | 11000 | 60 | 1302 | 4789 | 6091
August | 31 | 8800 | 60 | 1302 | 4545 | 5847
September | 30 | 4286 | 30 | 630 | 3813 | 4443
October | 31 | 1100 | 20 | 434 | 3176 | 3610
November | 30 | 214.3 | 2 | 42 | 1724 | 1766
December | 31 | 220 | 2 | 43.4 | 1829 | 1872.4
Energy Balance
| Total Heat Losses (kWh) | Total Solar Heat Gain (kWh) | Total Casual Heat Gain (kWh) | Energy Required for Space Heating (kWh)
January | 8165.9461 | 2502.8493 | 1810.8 | 3852.2968
February | 14229.432 | 3078.1137 | 1994 | 9157.3183
March | 14808.7732 | 3670.7319 | 3113.5 | 8024.5412
April | 13416.3216 | 4113.6297 | 3522 | 5780.6919
May | 11027.8098 | 4711.9801 | 4742.5 | 1573.3297
June | 10062.2412 | 4510.7132 | 5935 | -383.472
July | 8297.114 | 4576.2208 | 6091 | -2370.1067
August | 8087.0605 | 4497.0278 | 5847 | -2256.9673
September | 7826.1876 | 4176.7891 | 4443 | -793.6015
October | 11237.8633 | 3676.8152 | 3610 | 3951.0481
November | 6568.3354 | 2819.1958 | 1766 | 1983.1396
December | 8112.9205 | 2070.3298 | 1872.4 | 4170.1907
|  |  | Total | 38492.5563

## Outdoor Toilets
| U value (W/m2K) | Area (m2) |  | Volume (m3) | 115
Walls | 0.3 | 58 |  | Air Changes per hour (ach) | Summer | 5
Floor | 0.25 | 48 |  |  | Winter | 2
Windows/ Doors | 2 | 9 |  | Heating Hours per day | 24
Roof | 0.2 | 62
Heat Losses
| Days in Month | Mean Outdoor Temperature (oC) | Mean Indoor Temperature (oC) | Floor Heat Losses (kWh) | Wall Heat Losses (kWh) | Windows/Doors Heat Losses (kWh) | Roof Heat Losses (kWh) | Ventilation Heat Losses (kWh) | Total Heat Losses (kWh)
January | 31 | 4.6 | 20 | 137.4912 | 199.3622 | 206.2368 | 142.0742 | 869.6318 | 1554.7963
February | 28 | 5 | 20 | 120.96 | 175.392 | 181.44 | 124.992 | 1912.68 | 2515.464
March | 31 | 5.9 | 20 | 125.8848 | 182.533 | 188.8272 | 130.081 | 1990.5534 | 2617.8793
April | 30 | 7.8 | 21 | 114.048 | 165.3696 | 171.072 | 117.8496 | 1803.384 | 2371.7232
May | 31 | 10.5 | 21 | 93.744 | 135.9288 | 140.616 | 96.8688 | 1482.327 | 1949.4846
June | 30 | 13.1 | 23 | 85.536 | 124.0272 | 128.304 | 88.3872 | 1352.538 | 1778.7924
July | 31 | 15.1 | 23 | 70.5312 | 102.2702 | 105.7968 | 72.8822 | 1115.2746 | 1466.7551
August | 31 | 15.3 | 23 | 68.7456 | 99.6811 | 103.1184 | 71.0371 | 1087.0398 | 1429.622
September | 30 | 13.3 | 21 | 66.528 | 96.4656 | 99.792 | 68.7456 | 1051.974 | 1383.5052
October | 31 | 10.3 | 21 | 95.5296 | 138.5179 | 143.2944 | 98.7139 | 1510.5618 | 1986.6176
November | 30 | 7.2 | 20 | 110.592 | 160.3584 | 165.888 | 114.2784 | 699.4944 | 1250.6112
December | 31 | 4.7 | 20 | 136.5984 | 198.0677 | 204.8976 | 141.1517 | 863.9849 | 1544.7002
| South Facing | West Facing | North Facing | East Facing
Area of Windows/Doors(m2) | 2 | 4 | 1 | 2 |  | Shading Coefficient | 0.87
Cooling Load Factor | 0.45 | 0.21 | 0.58 | 0.21
Solar Heat Gain
|  | South Facing Windows/Doors |  | West Facing Windows/Doors |  | North Facing Windows/Doors |  | East Facing Windows/Doors
| Days in Month | Average Solar Heat Gain Factor (W/m2) | Solar Heat Gain (kWh) | Average Solar Heat Gain Factor (W/m2) | Solar Heat Gain (kWh) | Average Solar Heat Gain Factor (W/m2) | Solar Heat Gain (kWh) | Average Solar Heat Gain Factor (W/m2) | Solar Heat Gain (kWh) | Total Solar Heat Gain (kWh)
January | 31 | 430 | 250.4974 | 71.6667 | 38.9663 | 78.1818 | 29.3512 | 71.6667 | 157.4346 | 476.2494
February | 28 | 590 | 310.4438 | 98.3333 | 48.2913 | 107.2727 | 36.3752 | 98.3333 | 267.7094 | 662.8197
March | 31 | 624 | 363.5124 | 104 | 56.5464 | 113.4545 | 42.5934 | 104 | 331.5373 | 794.1895
April | 30 | 739 | 416.6186 | 123.1667 | 64.8073 | 134.3636 | 48.8159 | 123.1667 | 449.9991 | 980.241
May | 31 | 833 | 485.2658 | 138.8333 | 75.4858 | 151.4545 | 56.8594 | 138.8333 | 590.8173 | 1208.4284
June | 30 | 824 | 464.5382 | 137.3333 | 72.2615 | 149.8182 | 54.4307 | 137.3333 | 559.4705 | 1150.701
July | 31 | 809 | 471.2846 | 134.8333 | 73.3109 | 147.0909 | 55.2212 | 134.8333 | 557.2631 | 1157.0798
August | 31 | 795 | 463.1288 | 132.5 | 72.0423 | 144.5455 | 54.2656 | 132.5 | 538.1427 | 1127.5794
September | 30 | 763 | 430.1489 | 127.1667 | 66.912 | 138.7273 | 50.4013 | 127.1667 | 479.7024 | 1027.1646
October | 31 | 650 | 378.6588 | 108.3333 | 58.9025 | 118.1818 | 44.3681 | 108.3333 | 359.741 | 841.6704
November | 30 | 515 | 290.3364 | 85.8333 | 45.1634 | 93.6364 | 34.0192 | 85.8333 | 218.5432 | 588.0622
December | 31 | 366 | 213.214 | 61 | 33.1666 | 66.5455 | 24.9827 | 61 | 114.0579 | 385.4212
Heat Emission Per Person (W) | 100
Casual Heat Gain
| Days in Month | People/Visitors per month | Average Number of People in Outdoor Toilets at any one time | Heat Gain from People (kWh) | Heat Gain from Electrical Equipment (kWh) | Total Casual Heat Gain (kWh)
January | 31 | 220 | 2 | 148.8 | 19.8 | 168.6
February | 28 | 600 | 4 | 268.8 | 142.7 | 411.5
March | 31 | 1100 | 5 | 372 | 162.5 | 534.5
April | 30 | 2143 | 5 | 360 | 241.7 | 601.7
May | 31 | 4400 | 7 | 520.8 | 241.7 | 762.5
June | 30 | 10715 | 8 | 576 | 241.7 | 817.7
July | 31 | 11000 | 8 | 595.2 | 241.7 | 836.9
August | 31 | 8800 | 8 | 595.2 | 241.7 | 836.9
September | 30 | 4286 | 6 | 432 | 241.7 | 673.7
October | 31 | 1100 | 4 | 297.6 | 202.1 | 499.7
November | 30 | 214.3 | 2 | 144 | 19.8 | 163.8
December | 31 | 220 | 2 | 148.8 | 19.8 | 168.6
Energy Balance
| Total Heat Losses (kWh) | Total Solar Heat Gain (kWh) | Total Casual Heat Gain (kWh) | Energy Required for Space Heating (kWh)
January | 1554.7963 | 476.2494 | 168.6 | 909.9469
February | 2515.464 | 662.8197 | 411.5 | 1441.1443
March | 2617.8793 | 794.1895 | 534.5 | 1289.1898
April | 2371.7232 | 980.241 | 601.7 | 789.7822
May | 1949.4846 | 1208.4284 | 762.5 | -21.4438
June | 1778.7924 | 1150.701 | 817.7 | -189.6086
July | 1466.7551 | 1157.0798 | 836.9 | -527.2247
August | 1429.622 | 1127.5794 | 836.9 | -534.8574
September | 1383.5052 | 1027.1646 | 673.7 | -317.3594
October | 1986.6176 | 841.6704 | 499.7 | 645.2473
November | 1250.6112 | 588.0622 | 163.8 | 498.749
December | 1544.7002 | 385.4212 | 168.6 | 990.679
|  |  | Total | 6564.7384

## Total Energy Consumption
| Visitor Centre | Outdoor Toilets | Total
| Energy Required for Space Heating (kWh) | Energy Required for Space Heating (kWh) | Energy Required for Space Heating (kWh)
January | 3852.2968 | 909.9469 | 4762.2437
February | 9157.3183 | 1441.1443 | 10598.4626
March | 8024.5412 | 1289.1898 | 9313.731
April | 5780.6919 | 789.7822 | 6570.474
May | 1573.3297 | -21.4438 | 1551.8859
June | -383.472 | -189.6086 | 0
July | -2370.1067 | -527.2247 | 0
August | -2256.9673 | -534.8574 | 0
September | -793.6015 | -317.3594 | 0
October | 3951.0481 | 645.2473 | 4596.2954
November | 1983.1396 | 498.749 | 2481.8886
December | 4170.1907 | 990.679 | 5160.8697
|  | Total | 45035.8509