## COP
HEAT PUMPS FOR DOMESTIC HEATING IN RURAL AREAS
Temperature Requirements for SPACE HEATING: |  |  |  | Temperature Requirement for Water Heating:
Type of Distribution system |  | Temperature required |  |  |  |  | Temperature required
Underfloor Heating |  | 30-45 | ° C | Domestic Hot water |  |  | 55 | ° C
Low Temp. Radiators |  | 45-55 | ° C | De-superheater |  |  | 75 | ° C
Conventional Radiators |  | 60-90 | ° C
Air Heating |  | 30-50 | ° C
Source Temperature |  | 8.4 | ° C | LIFT (output temp. - source temp.) |  |  | 46.6 | ° C
Earth Source (G & W) |  |  |  | difference between required output temperature of heat pump to source temperature
Air Teamperature for ASHP
Water Temperature for WSHP |  |  |  | COP of GSHP |  |  | 3.4805
Temperature to distribution system |  | 55 | ° C | varies with output temperature
Variation of COP for different heat pumps with temperature Lift
LIFT ( ° C )
TYPE OF HEAT PUMP | 20° C | 25° C | 30° C | 35° C | 40° C | 45° C | 50° C | 55° C | 60° C
Earth Source (G & W) | 9.26 | 7.15 | 5.8 | 4.8 | 4.15 | 3.6 | 3.2 | 2.9 | 2.6
High Efficiency ASHP | 7.5 | 5.9 | 4.75 | 3.9 | 3.4 | 3 | 2.25 | 2 | 1.9
Standard ASHP | 4.5 | 3.5 | 2.5 | 1.9 | 1.8 | 1.7 | 1.6 | 1.5 | 1.4
Source: Commercial Earth Energy Systems, Natural Resources Canada

## Source Temperature
Ground Temperature Estimation at different depths
Atmospheric Properties: |  | Ground temperature at a time of year (tyear)and at a depth (D)
Mean surface Temperature (Tmean) | ° C
(Average air temp). |  | T ( tyear ,D )= Tmean – Tamp
Amplitude of surface temperature (Tamp) | ° C
((max Air temp. - min air temp)/2)
Temperature shift (tshift) | day |  | Source: Kasuda, T and Archenbach, P.R., ASHRAE trascations, vol. 71, part 1, 1965
(day of year of min surface temperature)
Soil Properties: |  | time of year (tyear) |  | ° C | depth from surface | m
Thermal Diffusivity of soil (α) | m²/s | day | 1 | #DIV/0!
|  |  | 2 | #DIV/0!
|  |  | 3 | #DIV/0!
|  |  | 4 | #DIV/0!
5
source: RET Screen, GSHP Project model

## Economics
Heat Pump Economics
Earth Source capital costs (£/kW)
Type | ground coil | Heat pump | Total system
Horizontal | 250-350 | 350-650 | 600-1000
vertical | 450-600 | 350-650 | 800-1250
costs include installation and commissioning but exclude distribution system
source: Energy Savings Trust, UK
SIMPLE PAYBACK PERIOD
pump size | maximum energy can supply by the heat pump
capital cost | total cost of the heat pump including installation and commissioning of heat pump and ground heat exchanger
Annual O/M costs (approx. 1% of capital costs) | operation and maintenance costs of heat pump which is much lesser than any other technology, taken as 1% of capital cost
annual Running costs for the current system | it is the total costs for running the system to supply the demand
annual Running costs for the proposed system | it is the total costs for running the system to supply the demand
Annual Savings | it is the total money saved by proposed system over the current system, i.e. difference of their running costs
Annual payback | It the total money paid back for the capital cost for proposed heating system i.e. annual savings minus operations and maintenance costs
Total Pay back time for the proposed system | It is total number of years taken to pay back the capital costs of proposed heating system i.e. capital cost divided by annual pay back

## case study-1
CASE STUDY-1 | Mabie farm park, Dumfries and Galloway
Heat Pump Type: | Ground Source, Horizontal ground heat exchanger
Heating System: | Bi-Valent Heat Pump with High energy efficiency Oil (kerosene) fired Boiler
Distribution system | Low temperature radiators
temperature required for distribution is 45 - 55 deg. C, since there is also demand for hot water distribution temperature considered as 55 deg. C
SOURCE TEMPERATURE
MONTH | 1 m | 1.5 m | 2 m | 3 m
january | 6.647 | 8.6921 | 9.1869 | 8.7236
february | 5.168 | 7.6271 | 8.6704 | 8.7461
march | 4.5168 | 6.76 | 8.0846 | 8.6799
april | 4.8633 | 6.297 | 7.5643 | 8.5385
may | 6.1668 | 6.403 | 7.2701 | 8.3596
june | 8.0688 | 7.0442 | 7.2787 | 8.1915
july | 10.0604 | 8.0522 | 7.5907 | 8.0799
august | 11.6236 | 9.17 | 8.1296 | 8.0546
september | 12.2914 | 10.0636 | 8.7343 | 8.1233
october | 11.9062 | 10.5071 | 9.2485 | 8.2669
november | 10.5814 | 10.3858 | 9.5354 | 8.4462
december | 8.6663 | 9.7273 | 9.515 | 8.6129
| 8.38 | 8.3941 | 8.4007 | 8.4019
Demand and Supply
heating COP (COPh) | 3.4805 | heat pump size | 8 | kW
Month | Energy Required for Space Heating (kWh) | out door toilet heating (kWh)-electricity fuel | Monthly Hot Water Heat Requirement (kWh) | Total Heating demand (kWh) | Heating capacity of Heat Pump (kWh) | Heating Load on Heat Pump (kWh) | Energy consumed by the Heat Pump at (COPh=3.48) (kWh) | Heating load for Auxiliary heating system (kWh)
january | 3852.2968 | 909.9469 | 43 | 4805.2437 | 5840 | 4805.2437 | 1380.6125 | 0
february | 9157.3183 | 1441.1443 | 102 | 10700.4626 | 5840 | 5840 | 1677.9123 | 4860.4626
march | 8024.5412 | 1289.1898 | 182 | 9495.731 | 5840 | 5840 | 1677.9123 | 3655.731
april | 5780.6919 | 789.7822 | 326 | 6896.474 | 5840 | 5840 | 1677.9123 | 1056.474
may | 1573.3297 | 0 | 653 | 2226.3297 | 5840 | 2226.3297 | 639.6551 | 0
june | 0 | 0 | 1539 | 1539 | 5840 | 1539 | 442.1759 | 0
july | 0 | 0 | 1580 | 1580 | 5840 | 1580 | 453.9557 | 0
august | 0 | 0 | 1266 | 1266 | 5840 | 1266 | 363.7392 | 0
september | 0 | 0 | 624 | 624 | 5840 | 624 | 179.2838 | 0
october | 3951.0481 | 645.2473 | 182 | 4778.2954 | 5840 | 4778.2954 | 1372.8699 | 0
november | 1983.1396 | 498.749 | 42 | 2523.8886 | 5840 | 2523.8886 | 725.1479 | 0
december | 4170.1907 | 990.679 | 43 | 5203.8697 | 5840 | 5203.8697 | 1495.1433 | 0
Annual | 38492.5563 | 6564.7384 | 6582 | 51639.2947 | 70080 | 42066.627 | 12086.3201 | 9572.6677
COST ANALYSIS
Running costs or fuel costs for current and proposed system
Current Heating system
Heating System Type: | Oil fired modern energy efficient condensing combination boiler (efficiency of 90%)
heating area | fuel used | demand (kWh) | cost
visitor center | kerosene (0.0317 p/kWh) | 49582.0119 | 1571.7498
out door toilets | Electricity (0.1024 p/kWh) | 6564.7384 | 672.2292
Annual Running cost for the system |  |  | 2243.979
Proposed Heating system
Heating system Type: | Ground Source Heat Pump (COP=3.48)
Heating Area | energy supplied by and fuel used | demand (kWh) | cost
whole building | heat pump (electricity) | 12086.3201 | 1237.6392
| current boiler (kerosene) | 9572.6677 | 303.4536
Annual Running cost for the system |  |  | 1541.0927
SIMPLE PAYBACK PERIOD
Heat Pump Size kW | 8 |  | kW
Heat Pump Size 8 kW |  | GSHP | grant of £ 1,500 by EST
capital cost |  | 6400 | 4900
O/M costs (approx. 1% of capital costs) |  | 64 | 64
Annual running costs for present system |  | 2243.979 | 2243.979
Annual running costs for GSHP |  | 1541.0927 | 1541.0927
Annual savings |  | 702.8862 | 702.8862
Annual PAYBACK |  | 638.8862 | 638.8862
Pay back time (years) |  | 10.0174 | 7.6696
*EST- Energy Savings Trust
ENVIRONMENTAL IMPACTS
co2 SAVINGS
Current Heating system
Heating System Type: | Oil fired modern energy efficient condensing combination boiler
heating area | rate of CO2 emmission for fuel | demand (kWh) | CO2 emissions (tonnes)
visitor center | kerosene (0.24 kgCO2/kWh) | 45074.5563 | 10.8179
out door toilets | Electricity (0.43 kgCO2/kWh) | 6564.7384 | 2.8228
Annual CO2 emissions by the system |  |  | 13.6407
Proposed Heating system
Heating system Type: | Bi-Valent Ground Source Heat Pump
Heating Area | energy supplied by and fuel used | demand (kWh) | CO2 emissions (tonnes)
whole building | heat pump (electricity) | 12086.3201 | 5.1971
| current boiler (kerosene) | 9572.6677 | 2.2974
Annual CO2 emissions by the system |  |  | 7.4946
Annual CO2 savings by proposed heating system over current system |  |  | 6.1462 | tonnes