## Slide 1: Modelling inter-zone airflow in ESP-r
Notes: <number>

## Slide 2: Objectives
What is inter-zone air flow?
What modelling methodologies does ESP-r use?
How do I model inter-zone airflow?
How do I impose control?
Notes: <number>

## Slide 3: Outline
Introduction
  Flow modelling strategies
  Inter-zone air flow
  ESP-r methodologies
Demonstration and hands-on exercises
  Creating an air-flow network
  Running simulations and analyzing results
  Imposing control
Notes: <number>

## Slide 4: Integrated thermal and flow modelling
from supply fan
to extract fan
to zones
from zones
fluid flow node
air flow connection
air flow connection
hot water flow path
Building thermal
domain
Air
Plant domain
Water
Flow domain

## Slide 5: Where does fluid flow occur?
Openings and cracks and other opening in the envelope and interior partitions
  Inter-zone infiltration and ventilation
Mechanical air distribution systems
Hydronic heating/cooling equipment
Interior spaces (intra-zone convective flow)
Notes: <number>

## Slide 6: Why does fluid-flow matter?
Infiltration and ventilation affect:
  load and energy calculations
  thermal comfort assessment
  contaminant and moisture dispersal
Hydronic flows affect plant control.

## Slide 7: Levels of resolution
Scheduled air flow
Pressure-driven
network
Intra-zone CFD
Easy-to-use
Hard-to-use
Notes: <number>

## Slide 8: Integrated CFD
Solution of conservation equations for mass, energy, and momentum for all grid points
Limitation is large amount of computing resources needed
Used mainly to predict temperature and velocity fields inside large and complex enclosures such as atria

## Slide 9: Integrated CFD
Couples to building thermal domain
Couples to air-flow network
Resolves flow patterns within zones

## Slide 10: Inter-zone air flow
Flow modelling is used extensively in ESP-r for:
  natural ventilation in offices
  solar ventilation pre-heat
  mixed mode ventilation
  displacement ventilation, etc.
Examples can be seen in the realistic models section of the exemplars
Scheduled airflow is ignored when an air flow network is defined!

## Slide 11: Air flow network constituents
Nodes
Connecting components
Inter-nodal connections

## Slide 12: Nodes (1)
Points in the network where the pressure is calculated or known
Node pressures are network state variables
wind-induced pressure
internal fixed pressure
internal unknown pressure

## Slide 13: Nodes (2)
Internal, or boundary nodes
Pressure may be fixed, wind-induced, or unknown.
wind-induced pressure
internal fixed pressure
internal unknown pressure

## Slide 14: Components and connections (1)
Components
  describe the flow characteristics of the nodal connections
Connections
  flows through connections are usually a non-linear function of the pressure difference
Pi
Pj

## Slide 15: Components and connections (2)
Flow connections may or may not be represented in the thermal model
  for example: two zones may be connected by a door in the air flow model, but that door may be omitted in the building model
The height of the connection inlet and outlet is required to compute stack effect
Multiple connections can use the same component

## Slide 16: Stack effect
The pressure difference across the connection may not equal the pressure difference between the two nodes.
n
m
2
1
h1
hn
hm
h2
connection

## Slide 17: Solution
The flows are a function of nodal pressures and the component characteristics
  conservation of mass for each node
All the internal nodes are directly or indirectly linked to at least one boundary node
Pressure and mass flow computed for each node
Iteration may be required

## Slide 18: Defining airflow networks in ESP-r
Demonstration and exercise
Nodes
Components
Connections

## Slide 19: Unventilated performance

## Slide 20: Imposing control
Controls manipulate network characteristics in response to climate and building conditions
T
actuator
sensor

## Slide 21: Network controls
Comprise:
  Sensors
  Actuators
  Control laws
On/off and proportional laws control available
All connections using a given component can be actuated at once

## Slide 22: Effect of ventilation