ESP-r Training Course

## Required Information for Hands-on Modelling

## House Description

### Main Floor Geometry and Construction

The vertices of the house main floor are shown in Figure 1. Figure 2 shows the location and dimensions of the windows. The constructions of the exterior walls, floors, ceiling, and the windows are shown in Figures 3-6.

### Site Information

Latitude = 45.3

Longitude = 75.6 (site longitude difference = -0.6)

Terrain = isolated rural site

Ground reflectance = 0.2

(10,0,2.5)

Figure 1: Vertex points defining the zone.

x

y

z

1.5 m

0.5 m

0.5 m

w1

w2

w3

w4

w5

w6

w7

1.5 m

all windows are 2 x 1.5 m

Figure 2: Window locations and dimensions.

Figure 3: Exterior wall construction.

38 mm EPS

100 mm Light Mix Concrete

10 mm Synthetic Carpet

Figure 4: Floor construction.

13 mm Gypsum Plaster

200 mm Glass Fiber

Figure 5: Ceiling construction.

4 mm Clear Float

12.7 mm Air Gap

4 mm Clear Float

Figure 6: Window construction.

### Infiltration

0h00 – 7h00: 0.5 ach

7h00 – 20h00: 0.1 ach

20h00 – 24h00: 0.5 ach

### Internal Loads

These are non-HVAC related loads from people, lights, and equipment. The sensible loads are 70% radiative and 30% convective. The average hourly sensible and latent loads are constant throughout the week:

Sensible Load = 600 W

Latent Load = 150 W

### Foundation Type

The foundation type is a slab-on-grade. The floor slab sits directly on the ground.

### Thermostat Control Strategies

The heating and cooling capacities are set to 500  kW.

Two control strategies are to be modelled. The first is an ideal control with a heating setpoint:

Heat = ON if temperature is less than 21oC

Cooling = OFF (specify a zero maximum cooling capacity)

The second is an ideal control for heating with night setback:

From 0h00 – 6h00

Heat = ON if temperature is less than 16oC

Cooling = OFF (specify a zero maximum cooling capacity)

From 6h00 – 22h00

Heat = ON if temperature is less than 21oC

Cooling = OFF (specify a zero maximum cooling capacity)

From 22h00 – 24h00

Heat = ON if temperature is less than 16oC

Cooling = OFF (specify a zero maximum cooling capacity)