Solar hot water heating system

ESP-r plant modelling demonstration

# Solar heating system

In this exercise, we’ll implement a model for a simple solar heating system. This system, depicted in Figure 1, uses a solar collector to heat water stored in a buffer tank. The buffer tank is connected in series with a gas-fired tank, which supplies hot water to the space.

Figure 1: Solar hot-water heating system

# Components

This network will use the following ESP-r components:

| Name | Type | Catagory |
| --- | --- | --- |
| Buffer-tank | 2-node storage tank with immersed coil | Solar and others |
| Gas-fired-tank | 3-node tank for charging by residential fuel cell | Solar and others |
| Solar-collector | Simplified flat-plate solar collector, 1-node model | Solar and others |
| Pump-BT | Pressurized domestic WCH pump | Solar and others |
| Pump-GFT | Pressurized domestic WCH pump | Solar and others |
| Pump-RAD | Pressurized domestic WCH pump | Solar and others |
| Office-RAD | Domestic hot water radiator VO ~ 2 m^2 ; 2-node model | Wet central heating |
| Reception-RAD | Domestic hot water radiator VO ~ 2 m^2 ; 2-node model | Wet central heating |
| Junction | Water flow converger ; 1-node PP model | Primitive parts |

For this exercise, the default parameters for the water tank, pump and junction conponents will suffice. Make the following changes to collector and radiator components:

| Name | Input | Value | Units |
| --- | --- | --- | --- |
| Solar-collector | Collector area | 10.0 | m2 |
| Office-RAD | Nominal heat emission of radiator | 5000.0 | W |
| Reception-RAD | Nominal heat emission of radiator | 10000.0 | W |

# Connections

The components will be connected as follows. Take care when selecting the connected node.

| Component | Node |  | Component | Node | M.D. Ratio |
| --- | --- | --- | --- | --- | --- |
| Buffer-tank | Water node 2 | → | Pump-BT | Water node 1 | 1.0 |
| Pump-BT | Water node 1 | → | Solar-collector | Water node 1 | 1.0 |
| Solar-collector | Water node 1 | → | Buffer-tank | Water node 2 | 1.0 |
| Gas-tank | Water node 1 | → | Pump-GFT | Water node 1 | 0.5 |
| Pump-GFT | Water node 1 | → | Buffer-tank | Water node 1 | 1.0 |
| Buffer-tank | Water node 1 | → | Gas-tank | Water-node 1 | 1.0 |
| Gas-tank | Water node 1 | → | Pump-RAD | Water node 1 | 0.5 |
| Pump-RAD | Water node 1 | → | Office-RAD | Water node 1 | 0.5 |
| Pump-RAD | Water node 1 | → | Reception-RAD | Water node 1 | 0.5 |
| Office-RAD | Water node 2 | → | Junction | Water node 1 | 1.0 |
| Reception-RAD | Water node 2 | → | Junction | Water node 1 | 1.0 |
| Junction | Water node 1 | → | Gas-tank | Water node 1 | 1.0 |

# Containments

While containments can be defined for each component, only the following containments are necessary:

| Component | Containment type | Zone | Location |
| --- | --- | --- | --- |
| Buffer-tank | Zone (air/surface/const) temp. | Reception | Air point |
| Gas-fired-tank | Zone (air/surface/const) temp. | Reception | Air point |
| Reception-RAD | Zone (air/surface/const) temp. | Reception | Air point |
| Office-RAD | Zone (air/surface/const) temp. | Office | Air point |
| Solar-collector | Ambient air temperature | — | — |

# Controls

The network requires four plant controls:

### Buffer-tank pump

The buffer-tank pump will be activated whenever the temperature inside the tank is at least 5 °C greater than the solar collector, and deactivated when the difference falls to 1°C.

| Sensor | Output from a plant component: a) Solar collector, node 1 b) Buffer tank, node 1 |
| --- | --- |
| Actuator | Node within a plant-component: Pump-BT, node 1 |
| Period of validity | Jan 1  Dec 31 |
| Control type | Senses Dir. Normal solar radiation, actuates flow |
| Control law | On-off controller |
| Period start time | 0.0 h |
| Mode of operation | -1.0 (cooling) |
| Off-setpoint | 5 °C |
| On-setpoint | 1 °C |
| Output at high: | 0.1 kg/s |
| Output at low: | 0.0 kg/s |
| Sensor lag: | 0 s |
| Actuator lag: | 0 s |

### Gas-fired-tank burner

The tank burner will be activated whenever the tank temperature drops below 50 °C, and deactivated when it rises above 55 °C.

| Sensor | Output from a plant component (Gas-tank, node 1) |
| --- | --- |
| Actuator | Node within a plant-component: (Gas-tank, node 2) |
| Period of validity | Jan 1  Dec 31 |
| Control type | Senses db temperature, actuates variable. |
| Control law | On-off controller |
| Period start time | 0.0 h |
| Mode of operation | 1.0 (heating) |
| Off-setpoint | 55 °C |
| On-setpoint | 50 °C |
| Output at high: | 1.0 |
| Output at low: | 0. |
| Sensor lag: | 0 s |
| Actuator lag: | 0 s |

### Gas-fired--tank pump

The circulation pump between the buffer and gas-fired tanks will be activated whenever temperature in the buffer tank exceeds 60°C, and deactivated when the temperature drops below 55 °C.

| Sensor | Output from a plant component (Buffer-tank, node 1) |
| --- | --- |
| Actuator | Node within a plant-component: (Gas-tank-pump, node 1) |
| Period of validity | Jan 1  Dec 31 |
| Control type | Senses db temperature, actuates variable. |
| Control law | On-off controller |
| Period start time | 0.0 h |
| Mode of operation | -1.0 (cooling) |
| Off-setpoint | 55 °C |
| On-setpoint | 60 °C |
| Output at high: | 0.1 kg/s |
| Output at low: | 0. kg/s |
| Sensor lag: | 0 s |
| Actuator lag: | 0 s |

### Radiator pump

The pump supplying the radiators will be activated when the temperature in reception drops below 19°C, and deactivated whenever the temperature rises above 21°C.

| Sensor | Senses temperature in a specific zone (Reception, air point temperature) |
| --- | --- |
| Actuator | Node within a plant-component: (pump-rad, node 1) |
| Period of validity | Jan 1  Dec 31 |
| Control type | Senses db temperature, actuates variable. |
| Control law | On-off controller |
| Period start time | 0.0 h |
| Mode of operation | 1.0 (heating) |
| Off-setpoint | 21 °C |
| On-setpoint | 19 °C |
| Output at high: | 0.02 kg/s |
| Output at low: | 0.0 kg/s |
| Sensor lag: | 0 s |
| Actuator lag: | 0 s |