Electrical network with PV

ESP-r power modelling demonstration

# PV-electrical network

In this exercise, we’ll couple the pumps from our solar heating mechanical system to an electrical network that also includes photovoltaics and occupant-driven loads.  The network, depicted in Figure 1, features both AC and DC power.

Figure 1: Electrical network with PV and occupant loads

# PV-materials

The photovoltaic materials must first be added to the building fabric. In this exercise, we’ll add the PV to the large “w_roof” surface in the “roof_space” zone, depicted in Figure 2.  To do so, the west roof surface construction must be re-attributed from “roof” to “PVroof.”

Figure 2: West roof PV installation

# PV attributes

Under Embedded renewables section, select “Crystaline PV” and “WATSUN-PV_multic”. Enter in the component parameters as follows.

| Parameter | Value |
| --- | --- |
| Open circuit voltage at ref (V) | 20.37 |
| Short circuit current at ref (A) | 3.0200 |
| Voltage at maximum power point at ref (V) | 15.3200 |
| Current at maximum power point at ref (A) | 2.700 |
| Reference insolation (W/m2) | 1000.0 |
| Reference temperature. (K) | 298.0 |
| Temperature coefficient of Isc (/K) | -8.310E-05 |
| Temperature coefficient of Voc (/K) | 0.00355 |
| Coefficient of logarithm of irradiance for Voc (-) | 0.0054 |
| Number of series connected cells (not modules) (- | 36.0000 |
| Number of parallel connected branches. (-) | 1.0000 |
| Number of modules in surface. (-) | 188 |
| Load type (0-maximum power, 1-fixed V) | 0.0 |
| Load value - voltage (V) | 0.0 |
| # Shading treatment (0-def,1-prop,2-total,3-diff.) | 0.0 |
| Miscellaneous loss factor (-) | 0.0 |

Locate the material on the west roof surface, in the silica layer (node 3).

# “Electrifying” plant components

Before they can be coupled to the electrical network, the pumps in the plant component models must first be configured to compute power consumption. Turn the “electrical flag” for each component on, and enter the following data:

| Parameter | Value |
| --- | --- |
| Power factor | 1.0 |
| Load type | Resistive |
| Nominal power | 0.0 W |
| Operating voltage | 120. V |
| Phase | 1 |

# Electrical nodes

Add a new electrical network, and select a “balanced” type. Create two nodes, as follows:

| Name | Type | Voltage | Phase |
| --- | --- | --- | --- |
| PV-bus | DC | Calc-by-PV | 1 |
| AC-bus | 1-phase | Fixed | 1 |

# Hybrid components

Connect the three pumps (pump-GFT, pump-BT and pump-RAD) up to the AC-bus. Connect the PV array to the PV-bus. Configure each hybrid component as “1-phase”.

# Power-only components

### Occupant-driven loads

Select the “non-HVC electric loads” from the power-only components menu, and couple it to the AC-bus. Configure the component as follows:

| Parameter | Value |
| --- | --- |
| Number of data items | 1 |
| Scalar multiplier for loads | 1.0 |
| Number of string data items | 1 |
| non-HVAC electric loads input file | ../elec_loads/4UL.fcl |

### DC-AC converter

Select the DC-AC inverter from the power-only components menu, and configure it as follows. When prompted for the “node sending current to the PCU”, select PV-bus. When prompted for “node receiving current from the PCU”, select the AC-bus

| Parameter | Value |
| --- | --- |
| Number of data items | 6 |
| Operating mode of PCU | 1.0 |
| Nominal power | 5000. |
| non-HVAC electric loads input file | 0.8975E-05 |
| Set point voltage | 3.650 |
| Internal resistance constant (V2) | 2.0 |
| Auxiliary power (W) | 0.0 |
| Number of string data items | 0.0 |