## Costs
FINANCIAL ANALYSIS
Please note there are four worksheets in this document (see bottom of page)
Capital Costs
| Biomass System: |  | Fossil Fuel System
Costs: | Froling Turbomat 320 | Kob Pyrtec 350 | Current System | Oil System (300kW)
Boiler Costs (installed) | 70000 | 100000 | 0 | 15000
Fuel Feed System | 13855 | 13855 | 0 | 0
Bespoke Design Fuel Store | 10000 | 10000 | 0 | 0
Boilerhouse | 20500 | 20500 | 0 | 20500
Foundation Costs | 20000 | 20000 |  | 15000
Sub Total | 134355 | 164355 | 0 | 50500
Less funding @ 40% | 53742 | 65742
Total | 80613 | 98613 | 0 | 50500
Running Costs (per yr)
| Fuel | Maintenance | Total
Biomass System (scenario 1) | 9201.5 | 2000 | 11201.5
Biomass System (scenario 2) | 16060.22 | 2000 | 18060.22
Current System | 25913.36 | 8200 | 34113.36
Oil System | 23199.42 | 1000 | 24199.42
NPV Results (25yrs, 6% DF)
| PV Value | Lifetime Investment Costs
Kob Biomass System (scenario 1) | 12.7834 | 241805.764
Kob Biomass System (scenario 2) | 12.7834 | 329483.2246
Froling Biomass System (scenario 1) | 12.7834 | 223805.764
Froling Biomass System (scenario 2) | 12.7834 | 311483.2246
Current System | 12.7834 | 436083.2306
Oil System | 12.7834 | 359849.8047
Payback Period (compared to current heating portfolio)
| Capital Costs | Running Costs | Current Running Costs | PBP (years)
Kob Biomass System (scenario 1) | 98613 | 11201.5 | 34113.36 | 4.304
Kob Biomass System (scenario 2) | 98613 | 18060.22 | 34113.36 | 6.1429
Froling Biomass System (scenario 1) | 80613 | 11201.5 | 34113.36 | 3.5184
Froling Biomass System (scenario 2) | 80613 | 18060.22 | 34113.36 | 5.0216

## Fuel Cost Calculations
Current Fuel Costs (annual)
Fuel | Units (kWh) | Cost per Unit (£) | Costs (£)
Elec | 46750 | 0.0664 | 3104.2
Oil | 582500 | 0.0304 | 17708
LPG | 133888.8 | 0.0381 | 5101.1633
Total | 763138.8 |  | 25913.3633
Oil System Costs (annual)
Units | 763138.8
Cost per Unit (£) | 0.0304
Total Costs (£) | 23199.4195
Biomass Fuel Costs (annual)
Cost Chips | Units (kWh) | Chips @ 30% MC Cost per Unit (£) | Costs (£)
| 763138.8 | 0.016 | 12210.2208
|  | Total kWh required (boiler efficiency excluded) | No. Tonnes needed
Tonnes required | 30% MC = 3475 kWh tonne | 763138.8 | 219.6083
Scenario 1 Green Roundwood:
Cost Green Roundwood | 5420.5
Chipping Costs | 2200
Summer Oil Costs | 1581
Total | 9201.5
Scenario 2 Woodchips Purchased:
Transport | 3850
Cost Chips | 12210.22
Summer Oil Costs | 0 | since assumed to be included in previous demand
Total | 16060.22

## Conclusions
Financial Analysis Conclusions:
Capital Costs: From viewing the capital costs it can be seen that the biomass systems represent a larger initial outlay than the alternative fossil fuel system. Continuing to utilise the current system has no associated capital expenditure, this option is included to highlight the running cost benefits which could be incurred from biomass over the lifetime of the system. This is a bit misleading however since it should be taken into account that the current heating portfolio will require replacement (most likely in the next 5-10 years). The prospect of capital funding for a biomass system does, if only partially, close the gap between investing in a biomass or fossil fuel system. However it can be seen that the biomass proposals are well within the proposed budget set of £225-250,000.
Running Costs, Fuel: In terms of fuel the current system is the most expensive to run with annual costs calculated at £25,913.36. A 100% Oil system comprising of the new boiler and the present 335kW system in Kirkmichael House is the second most expensive at £23,199.42. It should be noted however that oil prices are highly volatile and can fluctuate significantly. Utilising biomass therefore is far cheaper in terms of fuel costs. The cheapest scenario is the purchase of green roundwood to dry and chip on site. However it is thought that due to the significant drying time and need to develop skills in these activities the more likely fuel costs, at least initially, will be those associated with scenario two, purchasing woodchips from a local supplier.
Running Costs, Maintenance: As regards maintenance the current system again fares worst. The £8200 annual value is also likely to increase as the system become older. Furthermore this figure does not take into account the extra staff time costs and difficulties associated with an unreliable heating system. The biomass maintenance costs are slightly higher than that for the oil system due to the need for activities such as disposing with ash and cleaning the grate.
Net Present Value (NPV) Calculations: By applying a discount rate it is possible to sum the additional savings/costs which would be accrued over the systems lifetime into one figure, this discounts these costs and savings dependant on how long it will take to realise them. From performing this analysis it can be shown that independent of what combination of system and fuel scenario is used biomass represents a better investment than either purchasing an equivalently sized oil system or sticking with the current heating portfolio. Even with no associated capital costs the current system is still significantly more expensive.
Pay Back Periods: When considering how long it will take for the reduced running costs of a biomass system, compared with the current arrangement, to pay off the additional capital investment required it can be seen that a biomass system is very competitive, ranging from approximately three and a half to six years. Most business investments will seek a payback period from 3-5 years however public sector bodies have more freedom to accept longer investment returns, in this context the range of payback periods suggested is highly acceptable.
Overall Conclusion: From a purely financial perspective replacing the current heating portfolio is essential. In doing this a biomass system represents the best value investment. It is possible to purchase a biomass system within the budget set out for the project.

## Assumptions,Calulations & Refs
Data / Info used: | Source/Explanation
Components of current heating system LPG, Oil, Elec. | from Barony College bills Elec wet system in Teaching Block, Oil in Kirkmichael House/Nith Cree, LPG in boilerhouse two and three.
Current Oil/LPG Fuel Costs | Oil at 3p/kWh, LPG 3.81 p/kWh taken as average from range of values in SDCS 2005
Current Fuel Costs Electricity 7.36p/kWh | Taken from energy bills based on observations suggesting a 60/40 night (5.2p/kWh) to day (8.8p/kWh) ratio.
Current System Maintenance £8200 | Oil at Kirkmichael £1000, LPG Systems £300, Electric wet system £6000 (repairs) + £900 pressurisation unit, from Pearl Edgar
Biomass O & M approx £2000 | estimated from 'Lanarkshire Biomass Project O & M Summery Site Info' (Econergy Ltd).
Costs green tonne roundwood £18.50 | Forestry Commission Scotland inc transport costs
Oil Boiler Costs (£15,000) | Based on 300kw system installed at Capenwray, www.lanchashire.gov.uk
Transport Costs £3850 | 17.5 per tonne delivery (Buccleuch Bioenergy) x 220 tonnes over six month heating season
Green Roundwood Costs at £5420.5 | 1 tonne green roundwood = .75 tonne at 30% MC (www.swwf.info). 220 tonnes rqd = 293 green tonnes. £18.50 per green tonne.
Chipping Costs £2200 | £10/odt (Scottish Executive), 220 tonnes required
Summer Oil Costs £1581 | six months (April-Sept) = 183 days or 4392 hours x 12kw constant demand at 3p/kWh Oil (SDCS 05)
Oil system maintenance £1000 | From Pearl Edgar. Based on current 335 kW system in place for Kirkmichael House
Boilerhouse Costs £20,500 | From costs at N. Lanarkshire project 'Palacerigg Country Park' to house 300kW system
Woodchip at 1.6p/kWh | From SDCS 2005 - at 30% MC £77/odt = 1.6p/kWh
Discount Rate at 6% | from Royal Commission on Environmental Pollution 'Biomass as a Renewable Energy Source'
Cost Kob System at £70,000 | From Supplier 3G Energi
Cost Froling System at £100,000 | From Supplier Highland Wood Energy
Fuel feed system £13,855 | From data supplied by 3G Energi 8x5m system
Calorific Value of chips at 30% MC - 3.475 mWh/tonne | Various inc. www.videncenter.dk, www.opet-chp.net
Additional Foundation Costs - Biomass £20,000 | Russell Merchant. It is thought that the proposed sight of the boilerhouse & fuel store could incur additional foundation costs, as was the case with the animal care centre. This is specific to this particular area and therefore may not be applicable should these be build elsewhere.
Additional Foundation Costs - Oil £15,000 | The foundation costs are likely to be lower since an oil system would not require a large fuel store to be constructed.
Assumptions | Explanation
No consideration of FF gas system | No mains gas on site (Pearl Edgar)
No consideration of FF Electric system | Electric wet system not an option as this is what is due to be replaced
No consideration of FF LPG system | Predicted LPG costs higher than oil (SDCS, 2005) so only oil alternative considered
Life New System 25 yrs | "expected life biomass system 20-30yrs" www.usewoodfuel.co.uk, average taken
Transport Distance (41.7km) | based on the average distance from Barony to 16 local suppliers
Funding at 40% | Support available from SBSS and LCBP Phase 1, the most likely funding streams
Include oil in green roundwood biomass scenario | Biomass heating recommendation to keep oil system to satisfy summer HW demand at 12kW (constant)
existing pipework utilised i.e. no additional pipework costs | Enforced assumption due to the complexity in estimating what % of current pipework is suitable and additional requirements needed
Fuel Scenario 1: Buy in green roundwood, dry and chip on site. | Group suggestions
Fuel Scenario 2: Buy in chips from local supplier away. | Group suggestions
Cost of decommissioning current system ignored | This will have to be done at some point anyway and will be the same whatever prospective system is selected
Bespoke Design Fuel Store £10,000 | Assumption estimated from N.Lanarkshire project boilerhouse costs
Efficiency of systems | Cannot calculate exact efficiency of current systems, although current demand figure intrinsically holds this. Since biomass and oil fuel costs are estimated through using current demand it is assumed that the inefficiencies of these systems is already taken into account. It is accepted the efficiency level will not be exactly correct however. Biomass is typically 90%.